{"text_format":"1","workbook":"xlsx","n_sheets":25,"sheets":["AER only","Instructions","Business & other details","Contents","2.1 Expenditure summary","2.2 Repex","2.3(a) Augex","2.3(b) Augex","2.5 Connections","2.6 Non-network","2.7 Vegetation management","2.8 Maintenance","2.9 Emergency Response","2.10 Overheads","2.11 Labour","2.12 Input tables","4.1 Public lighting","4.2 Metering","4.3 Fee-based services","4.4 Quoted services","5.2 Asset Age Profile","5.3 MD - Network level","5.4 MD & utilisation-Spatial","6.3 Sustained interruptionss","Amendments"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":1,"defined_names":657,"comments":3,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"AER only","index":0,"n_rows":98,"n_cols":40,"rows_kept":98,"cut":false,"hidden":true,"merged":[[81,4,81,11],[0,1,0,11],[3,28,3,38],[4,28,4,31],[4,34,4,38],[44,22,44,26],[45,1,45,5],[45,14,45,21],[45,22,45,26],[46,2,46,3],[46,34,48,34],[49,34,53,34],[57,34,58,34],[63,22,63,25]]}
[null,"Data in these columns used for data validation and database purposes."]
[null,"Date last modified:","2016-08-08","added new business names, improved column heading formatting"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"FOR ELECTRICITY BUSINESSES ONLY"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Feeder Types",null,null,null,"TasNetworks (D)","MAIFI flag","Feeder Names"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","long rural","EXTRA"]
[null,"dms_TradingName_List","dms_TradingNameFull_List","dms_ABN_List","dms_JurisdictionList","dms_Sector_List","dms_Segment_List","dms_FormControl_List","dms_RPT_List","dms_RPTMonth_List","dms_CRCPlength_List","dms_FRCPlength_List","dms_663_List","dms_DeterminationRef_List","dms_Addr1_List","dms_Addr2_List","dms_Suburb_List","dms_State_List","dms_PostCode_List","dms_PAddr1_List","dms_PAddr2_List","dms_PSuburb_List","dms_PState_List","dms_PPostCode_List","dms_ContactName1_List","dms_ContactPh1_List","dms_ContactEmail_List",null,"dms_CBD_flag","dms_Urban_flag","dms_ShortRural_flag","dms_LongRural_flag","dms_FeederType_5_flag","dms_MAIFI_flag_List","dms_FeederName_1","dms_FeederName_2","dms_FeederName_3","dms_FeederName_4","dms_FeederName_5"]
[null,"ActewAGL Distribution","ActewAGL Distribution",76670568688,"ACT","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","40 Bunda Street",null,"CANBERRA","ACT","2600","GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au",null,"NO","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"ActewAGL Distribution"]
[null,"ActewAGL Distribution (Tx Assets)","ActewAGL Distribution (Tx Assets)",76670568688,"ACT","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","40 Bunda Street",null,"CANBERRA","ACT","2600","GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"ActewAGL Distribution (Tx Assets)"]
[null,"ActewAGL Gas","ActewAGL Gas",76670568688,"ACT","Gas","Distribution","Weighted average price cap","Financial","June",5,5,"x",null,"40 Bunda Street",null,"CANBERRA","ACT","2600","GPO BOX 366",null,"CANBERRA","ACT",2601,"Philip Deamer","02 6248 3438","GasAAReview@actewagl.com.au",null,null,null,null,null,null,null,null,null,null,null,null,"ActewAGL Gas"]
[null,"AGN (SA)","AGN (SA)",78551685,"SA","Gas","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination",null,null,null,"SA",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"AGN (SA)"]
[null,"AGN (Victoria)","Australian Gas Networks Limited",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 10","81 Flinders Street","ADELAIDE","SA","5000",null,null,null,null,null,null,"08 8227 1500",null,null,null,null,null,null,null,null,null,null,null,null,null,"AGN (Victoria)"]
[null,"Amadeus","APT Pipelines (NT) Pty Ltd",39009737393,"NT","Gas","Transmission","Weighted average price cap","Financial","June",5,5,"x","n/a","Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","Alexandra Curran","02 9275 0020","alexandra.curran@apa.com.au",null,null,null,null,null,null,null,null,null,null,null,null,"Amadeus"]
[null,"APA GasNet","APA VTS Australia Limited",79096457868,"Vic","Gas","Transmission","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","PO Box R41",null,"ROYAL EXCHANGE","NSW","1225",null,"02 9693 0000",null,null,null,null,null,null,null,null,null,null,null,null,null,"APA GasNet"]
[null,"Ausgrid","Ausgrid",67505337385,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","570 George St",null,"SYDNEY","NSW",2000,null,null,null,null,null,"John Thomson","(02) 9269 2312","john.thomson@ausgrid.com.au",null,"YES","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Ausgrid"]
[null,"Ausgrid (Tx Assets)","Ausgrid (Tx Assets)",67505337385,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination",null,null,null,"NSW",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Ausgrid (Tx Assets)"]
[null,"AusNet (D)","AusNet Services (D)",91064651118,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 32","2 Southbank Boulevard","SOUTHBANK","Vic","3006","Locked Bag 14051",null,"MELBOURNE CITY MAIL CENTRE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,null,"YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"AusNet (D)"]
[null,"AusNet (Gas)","AusNet Gas Services",null,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"X",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AusNet (Gas)"]
[null,"AusNet (T)","AusNet (T)",78079798173,"Vic","Electricity","Transmission","Revenue cap","Financial","March",5,5,2,"transmission determination","Level 32","2 Southbank Boulevard","SOUTHBANK","Vic","3006",null,null,null,null,null,"Tom Hallam","03 9695 6617","Thomas.hallam@SP-Ausnet.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"AusNet (T)"]
[null,"Australian Distribution Co.","Australian Distribution Co.",11222333444,"-","Electricity","Distribution","Revenue cap","Financial","June",5,5,2,"distribution determination","123 Straight Street",null,"SYDNEY","NSW","2000","PO Box 123",null,"SYDNEY","NSW",2000,"Bob Smith","02 1234 5678","bob@auselec.net.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Australian Distribution Co."]
[null,"Australian Transmission Co.","Australian Transmission Co.",11222333444,"-","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","123 Straight Street",null,"SYDNEY","NSW","2000","PO Box 123",null,"SYDNEY","NSW",2000,"Bob Smith","02 1234 5678","bob@auselec.net.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Australian Transmission Co."]
[null,"CitiPower","CitiPower",76064651056,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","40 Market Street",null,"MELBOURNE","Vic","3000","Locked Bag 14090",null,"MELBOURNE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,"YES","YES","NO","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"CitiPower"]
[null,"Directlink","Directlink",16779340889,"Qld","Electricity","Transmission","Revenue cap","Financial","June",9,5,5,"transmission determination",null,null,null,"NSW",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Directlink"]
[null,"ElectraNet","ElectraNet",41094482416,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","52-55 East Terrace","Rymill Park","ADELAIDE","SA","5000","PO Box 7096","Hutt Street Post Office","ADELAIDE","SA",null,"Bill Jackson","08 8404 7969","jackson.bill@electranet.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"ElectraNet"]
[null,"Endeavour Energy","Endeavour Energy",59253130878,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","51 Huntingwood Drive",null,"HUNTINGWOOD","NSW","2148","PO Box 811",null,"SEVEN HILLS","NSW",null,"Jon Hocking","02 9853 4386 / 0407 348 156","Jon.Hocking@Endeavourenergy.com.au",null,"NO","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Endeavour Energy"]
[null,"Energex","Energex",40078849055,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","26 Reddacliff Street",null,"NEWSTEAD","Qld","4006","26 Reddacliff Street",null,"NEWSTEAD","QLD","4006","Nicola Roscoe","07 3664 5891","nicolaroscoe@energex.com.au",null,"YES","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"Energex"]
[null,"Ergon Energy","Ergon Energy",50087646062,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","22 Walker Street",null,"TOWNSVILLE","Qld","4810","Po Box 264",null,"FORTITUDE VALLEY","QLD",4006,"Jenny Doyle, Group Manager Regulatory Affairs","(07) 3851 6416","jenny.doyle@ergon.com.au",null,"NO","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Ergon Energy"]
[null,"Essential Energy","Essential Energy",37428185226,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","8 Buller Street",null,"PORT MACQUARIE","NSW",null,"PO Box 5730",null,"PORT MACQUARIE","NSW",null,"Catherine Waddell","02 6338 3553","catherine.waddell@essentialenergy.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Essential Energy"]
[null,"Jemena Electricity","Jemena Electricity",82064651083,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 16","567 Collins Street","MELBOURNE","VIC","3000","PO Box 16182",null,"MELBOURNE","VIC",8001,"Robert McMillan","03 9173 7000","robert.mcmillan@jemena.com.au",null,null,null,"YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"Jemena Electricity"]
[null,"JGN","Jemena Gas Networks",null,"NSW","Gas","Distribution","Weighted average price cap","Financial","June",5,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"JGN"]
[null,"Multinet Gas","Multinet Gas (DB No.1) Pty Ltd (ACN 086 026 986), Multinet Gas (DB No.2) Pty Ltd (ACN 086 230 122)",86026986,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Multinet Gas"]
[null,"Murraylink","Murraylink",79181207909,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Murraylink"]
[null,"Powercor Australia","Powercor Australia",89064651109,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","40 Market Street",null,"MELBOURNE","Vic","3000","Locked bag 14090",null,"MELBOURNE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Powercor Australia"]
[null,"Powerlink","Queensland Electricity Transmission Corporation Limited trading as Powerlink Queensland",82078849233,"Qld","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","33 Harold St",null,"VIRGINIA","Qld","4014","PO Box 1193",null,"VIRGINIA","QLD",4014,"Jennifer Harris","07 3860 2667","jharris@powerlink.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Powerlink"]
[null,"Roma to Brisbane Pipeline","APT Petroleum Pipelines Limited t/a Roma to Brisbane Pipeline","009 737 393","Qld","Gas","Transmission","Revenue cap","Financial","June",5,5,"x","n/a",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Roma to Brisbane Pipeline"]
[null,"SA Power Networks","SA Power Networks",13332330749,"SA","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","1 Anzac Highway",null,"KESWICK","SA","5035","GPO Box 77",null,"ADELAIDE","SA",null,"Damien O'Connor","08 8404 5066","damien.oconnor@sapowernetworks.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"SA Power Networks"]
[null,"TasNetworks (D)","TasNetworks (D)",24167357299,"Tas","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","21 Kirksway Place",null,"HOBART","Tas","7000","GPO Box 191",null,"HOBART","Tas",null,"Leigh Mayne","03 6270 3691","rrp2012@auroraenergy.com.au",null,null,null,"YES","YES","YES",null,"Critical Infrastructure","High density commercial","Urban","High density rural","Low density rural","TasNetworks (D)"]
[null,"TasNetworks (T)","TasNetworks (T)",24167357299,"Tas","Electricity","Transmission","Revenue cap","Financial","March",5,5,5,"transmission determination","1-7 Maria Street",null,"LENAH VALLEY","Tas","7008","PO Box 606",null,"MOONAH","Tas",null,"Heath Dillon","03 6274 3664","heath.dillon@transend.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"TasNetworks (T)"]
[null,"TransGrid","TransGrid",19622755774,"NSW","Electricity","Transmission","Revenue cap","Financial","June",5,4,5,"transmission determination","180 Thomas Street",null,"HAYMARKET","NSW","2000","PO Box A1000",null,"SYDNEY SOUTH","NSW",null,"Andrew Kingsmill","02 9284 3149","andrew.kingsmill@transgrid.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"TransGrid"]
[null,"United Energy","United Energy",70064651029,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 3","6 Nexus Court","MULGRAVE","Vic","3149","PO Box 449",null,"MOUNT WAVERLEY","VIC",3170,"Mathew Abraham","03 8846 9758","mathew.abraham@ue.com.au",null,null,null,"YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"United Energy"]
[null,"Western Power (D)","Western Power (D)",18540492861,"WA","Electricity","Distribution","Revenue cap","Financial","June",12,4,"x","distribution determination","363 Wellington Street",null,"PERTH","WA","6000","GPO Box L921",null,"PERTH","WA",6842,"Judy Hunter","08 9326 6239","judy.hunter@westernpower.com.au",null,null,null,"YES","YES","NO","NO","CBD","Urban","Short rural","Long rural",null,"Western Power (D)"]
[null,"Western Power (T)","Western Power (T)",18540492861,"WA","Electricity","Transmission","Revenue cap","Financial","June",12,4,"x","transmission determination","363 Wellington Street",null,"PERTH","WA","6000","GPO Box L921",null,"PERTH","WA",6842,"Judy Hunter","08 9326 6239","judy.hunter@westernpower.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Western Power (T)"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"For EB & Reset RINs only"]
[null,"The Reg Year Ending (dms_RYE) must be set to the last year of the regulatory period. For forecast data is is usually (FRCP_y5) for actual it is a single year (CRY). For historical actual data the RYE will need to be set manually in the business details sheet by setting the dms_Multiyear_flag to 1 and putting the correct value in 'dms_Specified_FinalYear. See cells C67:C68",null,null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"00\"),VALUE(LEFT(CRCP_y1,4)-1))","v":"2012-13"},null,null,null,null,null,null,"Drop down selector box for CA & Reset RINs.","For CA & Reset RINs only",null,null,null,null,null,null,null,"for DNSP only",null,null,null,null,null,null,null,null,null,null,null,"Reason for interruption","dms_Reason_Interruption_Detailed","dms_Reason_Interruption"]
[null,"dms_Model_List ","DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)",null,"dms_RYE_Formula_Result",null,null,null,null,null,null,null,null,"dms_0203_ProjectType","dms_020303_01_UOM","dms_020501_01_UOM","dms_020501_02_UOM","dms_020501_03_UOM","dms_020501_04_UOM","dms_020603_01_UOM","dms_040102_01_UOM","dms_040102_04_UOM","dms_030601_01_UOM","dms_030601_02_UOM","dms_030701_01_UOM","dms_030702_01_UOM","dms_030703_01_UOM",null,null,null,null,null,null,null,"Animal","Animal impact","Animal"]
[null,"ARR","ANNUAL REPORTING STATEMENT",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2016"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - single circuit","Circuit line length in km","0's","0's","0's","0's","0's","0's","days","minutes/customer","minutes/customer","Customer / km","%","km",null,null,null,null,null,null,null,null,"Animal nesting/burrowing, etc and other","Asset failure"]
[null,"CA","CATEGORY ANALYSIS",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2016"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - dual circuit","Circuit line length in km","0's","0's","0's","0's","0's","0's","0's","minutes/customer","minutes/customer","MWh/customer","Number of spans",null,null,null,null,null,null,null,null,null,"Other","Other"]
[null,"CPI","CPI",null,null,null,null,null,null,null,null,null,null,"New line on new route - other","Circuit line length in km","MVA added","MVA added","MVA added","MVA added","0's","0's","$0s","interruptions/customer","interruptions/customer","kVA / customer","Number of spans",null,null,null,null,null,null,null,null,"Asset failure","LV","Overloads"]
[null,"EB","ECONOMIC BENCHMARKING",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2016"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Line rebuild over existing route - single circuit","Circuit line length in km","0's","0's","0's","0's","0's","$0s","0's","interruptions/customer","interruptions/customer",null,"Number of spans",null,null,null,null,null,null,null,null,null,"Distribution substation","Planned"]
[null,"PTRM","POST TAX REVENUE MODEL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2023"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit","Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s","(per cent)",null,null,null,null,null,"Number of spans",null,null,null,null,null,null,null,null,null,"HV","Network business"]
[null,"Reset","REGULATORY REPORTING STATEMENT",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2023"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Reconductor - Single circuit","Number","net circuit km added","net circuit km added","net circuit km added","net circuit km added",null,null,null,null,null,null,"Years",null,null,null,null,null,null,null,null,null,"Zone substation","Third party"]
[null,"RFM","ROLL FORWARD MODEL",null,{"$f":"LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)","v":"2016"},"=LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)",null,null,null,null,null,null,null,"Reconductor - Dual circuit","Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s",null,null,null,null,null,null,"Years",null,null,null,null,null,null,null,null,null,"Subtransmission","Unknown"]
[null,"WACC","WEIGHTED AVERAGE COST OF CAPITAL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2023"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Other",null,"net circuit km added","net circuit km added","net circuit km added","net circuit km added",null,null,null,null,null,null,"Trees",null,null,null,null,null,null,null,null,"Other","insert description of 'other'","Vegetation"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"total spend $0s","total spend $0s","total spend $0s","total spend $0s",null,null,null,null,null,null,"Trees",null,null,null,null,null,null,null,null,"Overloads","Network error","Weather"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,"$0s",null,null,null,null,null,null,null,"Defects",null,null,null,null,null,null,null,null,"Planned","Switching and protection error","2 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,null,null,null,null,null,null,null,null,"Defects",null,null,null,null,null,null,null,null,"Network business","Fire","3 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,null,null,null,null,null,null,null,null,"Spans",null,null,null,null,null,null,null,null,null,"Other","4 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"$0s",null,null,null,null,null,null,null,null,null,"km",null,null,null,null,null,null,null,null,"Third party","Dig-in","5 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Spans",null,null,null,"",null,null,null,null,null,"Unauthorised access","6 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Vehicle impact","7 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Unknown"]
[null,"For all files either AER or business needs to be able to specify the type of submission","For PTRM & RFM templates we must provide a choice in case they change their form of control - otherwise it is drawn from the business specific lookup table above.",null,"These are indeces and lookup values for various dates. All step from the value placed in FRCP_y1 on the business and other details worksheet",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"for TNSP only",null,null,null,null,null,null,null,null,null,null,null,null,"Blow-in/Fall-in - NSP responsibility"]
[null,"dms_SourceList","dms_FormControl_Choices",null,"dms_FRCPlength_Num_List","dms_FinalYear_List","dms_CRCPlength_Num_List","dms_CFinalYear_List","dms_FRCP_years",null,"dms_CRCP_years",null,"dms_CRCP_index",null,null,null,null,null,null,null,null,null,"dms_030601_01_UOM",null,"dms_030701_01_UOM","dms_030702_01_UOM",null,null,null,null,null,null,null,null,"Unknown","Grow-in - NSP responsibility"]
[null,"After appeal","Revenue cap",null,1,"dms_FRCP_y1",1,"CRCP_y1",{"$f":"FRCP_y1","v":"2018-19"},"dms_FRCP_y1",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)-1)&\"-\"&TEXT(VALUE(MID(dms_FRCP_y1,3,2)),\"00\"),VALUE(LEFT(dms_FRCP_y1,4)-1))","v":"2017-18"},"dms_CRCP_yZ",1,null,null,null,null,null,null,null,null,null,"%",null,"Number of spans","km",null,null,null,null,null,null,null,null,"Vegetation","Blow-in/Fall-in - Other responsible party"]
[null,"Draft decision","Revenue yield",null,2,"dms_FRCP_y2",2,"CRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y1,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y1,4)+1))","v":"2019-20"},"dms_FRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yZ,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yZ,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yZ,4)-1))","v":"2016-17"},"dms_CRCP_yY",2,null,null,null,null,null,null,null,null,null,"number",null,"Years","%",null,null,null,null,null,null,null,null,null,"Grow-in - Other responsible party"]
[null,"Final decision","Weighted average price cap",null,3,"dms_FRCP_y3",3,"CRCP_y3",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y2,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y2,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y2,4)+1))","v":"2020-21"},"dms_FRCP_y3",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yY,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yY,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yY,4)-1))","v":"2015-16"},"dms_CRCP_yX",3,null,null,null,null,null,null,null,null,null,"number",null,"Trees","km"]
[null,"PTRM update 1",null,null,4,"dms_FRCP_y4",4,"CRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y3,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y3,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y3,4)+1))","v":"2021-22"},"dms_FRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yX,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yX,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yX,4)-1))","v":"2014-15"},"dms_CRCP_yW",4,null,null,null,null,null,null,null,null,null,"%",null,"Defects","number"]
[null,"PTRM update 2",null,null,5,"dms_FRCP_y5",5,"CRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y4,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y4,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y4,4)+1))","v":"2022-23"},"dms_FRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yW,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yW,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yW,4)-1))","v":"2013-14"},"dms_CRCP_yV",5,null,null,null,null,null,null,null,null,null,"number",null,"Number of spans",null,null,null,null,null,null,null,null,null,"Weather"]
[null,"PTRM update 3",null,null,6,"dms_FRCP_y6",6,"CRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y5,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y5,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y5,4)+1))","v":"2023-24"},"dms_FRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yV,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yV,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yV,4)-1))","v":"2012-13"},"dms_CRCP_yU",6,null,null,null,null,null,null,null,null,null,"number",null,"km",null,null,null,null,null,null,null,null,null,"2 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 4",null,null,7,"dms_FRCP_y7",7,"CRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y6,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y6,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y6,4)+1))","v":"2024-25"},"dms_FRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yU,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yU,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yU,4)-1))","v":"2011-12"},"dms_CRCP_yT",7,null,null,null,null,null,null,null,null,null,"%",null,"km",null,null,null,null,null,null,null,null,null,"3 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 5",null,null,8,"dms_FRCP_y8",8,"CRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y7,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y7,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y7,4)+1))","v":"2025-26"},"dms_FRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yT,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yT,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yT,4)-1))","v":"2010-11"},"dms_CRCP_yS",8,null,null,null,null,null,null,null,null,null,"number",null,"Number of spans",null,null,null,null,null,null,null,null,null,"4 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 6",null,null,9,"dms_FRCP_y9",9,"CRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y8,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y8,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y8,4)+1))","v":"2026-27"},"dms_FRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yS,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yS,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yS,4)-1))","v":"2009-10"},"dms_CRCP_yR",9,null,null,null,null,null,null,null,null,null,"number",null,null,null,null,null,null,null,null,null,null,null,"5 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 7",null,null,10,"dms_FRCP_y10",10,"CRCP_y10",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y9,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y9,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y9,4)+1))","v":"2027-28"},"dms_FRCP_y10",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yR,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yR,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yR,4)-1))","v":"2008-09"},"dms_CRCP_yQ",10,null,null,null,null,null,null,null,null,null,"%",null,null,null,null,null,null,null,null,null,null,null,"6 - STPIS Exclusion (3.3)(a)"]
[null,"Regulatory proposal",null,null,11,"dms_FRCP_y11",11,"CRCP_y11",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y10,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y10,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y10,4)+1))","v":"2028-29"},"dms_FRCP_y11",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yQ,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yQ,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yQ,4)-1))","v":"2007-08"},"dms_CRCP_yP",11,null,null,null,null,null,null,null,null,null,"number",null,null,null,null,null,null,null,null,null,null,null,"7 - STPIS Exclusion (3.3)(a)"]
[null,"Reporting",null,null,12,"dms_FRCP_y12",12,"CRCP_y12",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y11,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y11,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y11,4)+1))","v":"2029-30"},"dms_FRCP_y12",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yP,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yP,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yP,4)-1))","v":"2006-07"},"dms_CRCP_yO",12,null,null,null,null,null,null,null,null,null,"%"]
[null,"Revised regulatory proposal",null,null,13,"dms_FRCP_y13",13,"CRCP_y13",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y12,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y12,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y12,4)+1))","v":"2030-31"},"dms_FRCP_y13",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yO,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yO,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yO,4)-1))","v":"2005-06"},"dms_CRCP_yN",13,null,null,null,null,null,null,null,null,null,"number"]
[null,null,null,null,14,"dms_FRCP_y14",14,"CRCP_y14",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y13,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y13,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y13,4)+1))","v":"2031-32"},"dms_FRCP_y14",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yN,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yN,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yN,4)-1))","v":"2004-05"},"dms_CRCP_yM",14,null,null,null,null,null,null,null,null,null,"%"]
[null,null,null,null,15,"dms_FRCP_y15",15,"CRCP_y15",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y14,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y14,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y14,4)+1))","v":"2032-33"},"dms_FRCP_y15",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yM,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yM,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yM,4)-1))","v":"2003-04"},"dms_CRCP_yL",15,null,null,null,null,null,null,null,null,null,"number"]
[]
[null,null,null,null,"These are drop down lists for businesses to select the correct FRCP_y1 on the business and other details worksheet.\nThis also populates the column headings in the worksheets"]
[null,"dms_DataQuality_List",null,null,"dms_RCP_fyear_list","dms_CRY_ListF","dms_CRY_ListC","dms_RCP_cyear_list","dms_FRCP_fyear_list","dms_FRCP_ListF","dms_FRCP_ListC","dms_FRCP_cyear_list"]
[null,"Actual",null,null,"dms_fy1","2006-07",2007,"dms_cy1","dms_frcp_fy1","2016-17","2017","dms_crcp_cy1"]
[null,"Estimate",null,null,"dms_fy2","2007-08","2008","dms_cy2","dms_frcp_fy2","2017-18","2018","dms_crcp_cy2"]
[null,"Consolidated",null,null,"dms_fy3","2008-09","2009","dms_cy3","dms_frcp_fy3","2018-19","2019","dms_crcp_cy3"]
[null,"Recast",null,null,"dms_fy4","2009-10","2010","dms_cy4","dms_frcp_fy4","2019-20","2020","dms_crcp_cy4"]
[null,"Public",null,null,"dms_fy5","2010-11","2011","dms_cy5","dms_frcp_fy5","2020-21","2021","dms_crcp_cy5"]
[null,null,null,null,"dms_fy6","2011-12","2012","dms_cy6","dms_frcp_fy6","2021-22","2022","dms_crcp_cy6"]
[null,null,null,null,"dms_fy7","2012-13","2013","dms_cy7","dms_frcp_fy7","2022-23","2023","dms_crcp_cy7"]
[null,null,null,null,"dms_fy8","2013-14","2014","dms_cy8","dms_frcp_fy8","2023-24","2024","dms_crcp_cy8"]
[null,null,null,null,"dms_fy9","2014-15","2015","dms_cy9","dms_frcp_fy9","2024-25","2025","dms_crcp_cy9"]
[null,null,null,null,"dms_fy10","2015-16","2016","dms_cy10","dms_frcp_fy10","2025-26","2026","dms_crcp_cy10"]
[null,null,null,null,"dms_fy11","2016-17","2017","dms_cy11","dms_frcp_fy11","2026-27","2027","dms_crcp_cy11"]
[null,null,null,null,"dms_fy12","2017-18","2018","dms_cy12","dms_frcp_fy12","2027-28","2028","dms_crcp_cy12"]
[null,null,null,null,"dms_fy13","2018-19",2019,"dms_cy13","dms_frcp_fy13","2028-29","2029","dms_crcp_cy13"]
[null,null,null,null,"dms_fy14","2019-20","2020","dms_cy14","dms_frcp_fy14","2029-30","2030","dms_crcp_cy14"]
[null,null,null,null,"dms_fy15","2020-21","2021","dms_cy15","dms_frcp_fy15","2030-31","2031","dms_crcp_cy15"]

{"sheet":"Instructions","index":1,"n_rows":27,"n_cols":4,"rows_kept":27,"cut":false,"hidden":false,"merged":[[24,2,24,4],[25,2,25,3],[26,2,26,4],[8,2,8,4],[10,2,10,4],[12,2,12,4],[20,2,20,4],[22,2,22,4],[7,2,7,3],[1,1,1,5],[2,1,2,5],[3,2,3,4],[4,2,4,4],[5,2,5,4]]}
[]
[null,{"$f":"CONCATENATE(dms_Segment,\" Network Service Provider\")","v":"Distribution Network Service Provider"}]
[null,"Annual Reporting RIN Template"]
[null,null,{"$f":"CONCATENATE(\"This template is to be used by \",dms_TradingName,\" to fulfil its reporting obligations to the AER.\")","v":"This template is to be used by Energex to fulfil its reporting obligations to the AER."}]
[null,null,"INSTRUCTIONS"]
[null,null,"Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting."]
[]
[null,null,"Identifying CONFIDENTIAL INFORMATION:\n\nPlease use the macro at the top of each \nworksheet to identify confidential information. \n\n"]
[null,null,"-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential.\n\n-To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro"]
[]
[null,null,"UNITS OF MEASURE\n\nAll amounts are to be unrounded and reported in nominal terms on a one for one basis: that is 1000 is to be entered as '1000'.\n\n"]
[]
[null,null,"COLOUR CODING OF INPUT / NON-INPUT CELLS:"]
[null,null,null,"Yellow = Input cell (mandatory)"]
[null,null,null,"Darker yellow = input cell (mandatory)"]
[null,null,null,"Orange = input cell (if data available)"]
[null,null,null,"Grey = Not applicable/No inputs required"]
[null,null,null,"Leave coloured cells blank if no information exists. \nPLEASE DO NOT ENTER TEXT into cells that are to contain numeric data."]
[]
[]
[null,null,"WORKSHEET NAVIGATION\n\nMany tables in the worksheets have been \"grouped\" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin of excel (for Row groupings) or above the columns (for column groupings). \n\n\n\n"]
[]
[null,null,"RETURNING COMPLETED RESPONSES\n\nPlease return four (4) files to the AER: \n1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. \n\n2. An actual and an estimate version with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER.\n\n3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response.\n\n\nUse the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public. "]
[]
[null,null,"SUBMITTING AMENDED DATA TO THE AER\n\nIf an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. \n\nNSPs must identify the reason for the amendments in the Amendment Reason box on the  Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. \n\n."]
[null,null,"NSP may use Amended Data macro \nto highlight cells that contain amended data.\nNB: if data is also CONFIDENTIAL, re-apply \nthe Confidentiality macro after applying the \nAmended macro"]
[null,null,"Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER"]

{"sheet":"Business & other details","index":2,"n_rows":88,"n_cols":12,"rows_kept":88,"cut":false,"hidden":false,"merged":[[7,1,7,8],[11,1,11,8],[13,2,13,4],[14,2,14,4],[17,2,17,3],[17,4,17,7],[82,4,82,8],[18,4,18,7],[19,2,19,3],[19,4,19,7],[22,2,22,3],[22,4,22,7],[23,4,23,7],[24,2,24,3],[24,4,24,7],[32,1,32,8],[49,2,49,3],[51,2,51,8]]}
[null,{"$f":"IF(dms_DataQuality=\"backcast\",INDEX(dms_Worksheet_List,MATCH(dms_Model,dms_Model_List))&\" BACKCAST\",INDEX(dms_Worksheet_List,MATCH(dms_Model,dms_Model_List)))","v":"CATEGORY ANALYSIS"}]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"IF(SUM(dms_SingleYear_Model)>0,CRY,CONCATENATE(FRCP_y1,\" to \",dms_MultiYear_FinalYear_Result))","v":"2015-16"}]
[null,"BUSINESS & OTHER DETAILS"]
[]
[]
[null,"Instructions"]
[null,"Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells. "]
[]
[null,"SUBMISSION PARTICULARS INPUT SHEETS"]
[]
[null,"ENTITY DETAILS"]
[]
[null,"Short name","Energex",null,null,"Select business name from drop down list first"]
[null,"ACN / ABN",{"$f":"INDEX(dms_ABN_List,MATCH(dms_TradingName,dms_TradingName_List))","v":40078849055}]
[]
[]
[null,"Business address","Address 1",null,{"$f":"INDEX(dms_Addr1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"26 Reddacliff Street"}]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List)))","v":""}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_Suburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"NEWSTEAD"}]
[null,null,null,"State",{"$f":"INDEX(dms_State_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Qld"},"p/code",{"$f":"INDEX(dms_PostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"4006"}]
[]
[null,"Postal address","Address 1",null,{"$f":"INDEX(dms_PAddr1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"26 Reddacliff Street"}]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List)))","v":""}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_PSuburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"NEWSTEAD"}]
[null,null,null,"State",{"$f":"INDEX(dms_PState_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"QLD"},"p/code",{"$f":"INDEX(dms_PPostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"4006"}]
[]
[]
[null,"Contact name/s",{"$f":"INDEX(dms_ContactName1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Nicola Roscoe"},null,null,"Rachel Leaver"]
[null,"Contact phone/s",{"$f":"INDEX(dms_ContactPh1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"07 3664 5891"},null,null,"07 3664 4115"]
[null,"Contact email address/s",{"$f":"INDEX(dms_ContactEmail_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"nicolaroscoe@energex.com.au"},null,null,"rachelleaver@energex.com.au"]
[]
[null,"REGULATORY CONTROL PERIODS"]
[]
[null,"Forthcoming regulatory control period","2018-19",{"$f":"dms_FRCP_y2","v":"2019-20"},{"$f":"dms_FRCP_y3","v":"2020-21"},{"$f":"dms_FRCP_y4","v":"2021-22"},{"$f":"dms_FRCP_y5","v":"2022-23"},{"$f":"dms_FRCP_y6","v":"2023-24"},{"$f":"dms_FRCP_y7","v":"2024-25"},{"$f":"dms_FRCP_y8","v":"2025-26"},{"$f":"dms_FRCP_y9","v":"2026-27"},{"$f":"dms_FRCP_y10","v":"2027-28"}]
[]
[]
[null,"Current regulatory control period",{"$f":"dms_CRCP_FirstYear_Result","v":"2013-14"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+1)&\"-\"&TEXT(MID(CRCP_y1,3,2)+2,\"00\"),VALUE(LEFT(CRCP_y1,4)+1))","v":"2014-15"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y2,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y2,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y2,4)+1))","v":"2015-16"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y3,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y3,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y3,4)+1))","v":"2016-17"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y4,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y4,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y4,4)+1))","v":"2017-18"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y5,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y5,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y5,4)+1))","v":"2018-19"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y6,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y6,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y6,4)+1))","v":"2019-20"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y7,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y7,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y7,4)+1))","v":"2020-21"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y8,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y8,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y8,4)+1))","v":"2021-22"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y9,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y9,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y9,4)+1))","v":"2022-23"}]
[]
[]
[null,"Previous regulatory control period",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y2,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y2,3,2)),\"00\"),VALUE(LEFT(PRCP_y2,4)-1))","v":"2008-09"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y3,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y3,3,2)),\"00\"),VALUE(LEFT(PRCP_y3,4)-1))","v":"2009-10"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y4,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y4,3,2)),\"00\"),VALUE(LEFT(PRCP_y4,4)-1))","v":"2010-11"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y5,4)-1)&\"-\"&TEXT(VALUE(RIGHT(PRCP_y5,2)-1),\"00\"),VALUE(LEFT(PRCP_y5,4)-1))","v":"2011-12"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"00\"),VALUE(LEFT(CRCP_y1,4)-1))","v":"2012-13"}]
[]
[]
[null,"Current regulatory year","2015-16","CRY"]
[]
[]
[null,null,"DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)"]
[null,null,"APPLY NR 'CRY' IF AN ANNUAL RIN (EB, CA , ARR) - including multi year annual RINs eg. Recast CA. EB"]
[]
[null,"Source","Reporting",null,"Please select the correct submission type from the dropdown list."]
[null,"Data quality (actual, estimate, public, consolidated)","Public"]
[null,"Amended RIN submission - amendment reason"]
[null,"Submission Date","31/10/2016","dms_SubmissionDate","Please enter date this file submitted to AER (dd/mm/yyyy)"]
[null,"EBSS - First application of scheme in forthcoming period?","No"]
[null,"Sector",{"$f":"INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Electricity"},"dms_Sector","=INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Segment",{"$f":"INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Distribution"},"dms_Segment","=INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Regulatory Year Ending",{"$f":"IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))","v":"2016"},"dms_RYE","=IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))"]
[null,"Reporting Period Type",{"$f":"INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Financial"},"dms_RPT","=INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Model or RIN Type","CA","dms_Model","Drop down selection"]
[null,"Security Classification","Public","dms_Classification","Always Public"]
[null,"Template - version no.",5,"dms_TemplateNumber"]
[null,"Dollar $ real month",{"$f":"INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"June"},"dms_RPTMonth","=INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Dollar $ real  (the last month before the FRCP_y1)",{"$f":"CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)))","v":"June 2016"},"dms_DollarReal","=IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(CRY,2))&RIGHT(CRY,2)),CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2))))"]
[null,"Form of control",{"$f":"INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Revenue cap"},"dms_FormControl","=INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"RIN response - version no.",1,"dms_RINversion"]
[null,"Jurisdiction",{"$f":"INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))","v":"Qld"},"dms_Jurisdiction","=INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Backcast Multiyear EB, CA or ARR?",0,"dms_MultiYear_Flag","1=y, 0-n"]
[null,null,2013,"dms_Specified_FinalYear","The result here is returned to dms_CRCP_FinalYear_Result if dms_MultiYear_Flag is set to 1"]
[null,"Single Year Model T/F",{"$f":"IF(dms_Model=\"EB\",1,0)","v":0},"dms_EB"]
[null,null,{"$f":"IF(dms_Model=\"CA\",1,0)","v":1},"dms_CA","=dms_SingleYear_Model"]
[null,null,{"$f":"IF(dms_Model=\"ARR\",1,0)","v":0},"dms_ARR"]
[null,"Single Year Final Year Reference","CRY","dms_SingleYear_FinalYear_Ref","This is the reference for EB, CA & ARR RINs"]
[null,"Single Year Final Year Result",{"$f":"INDIRECT(dms_SingleYear_FinalYear_Ref)","v":"2015-16"},"dms_SingleYear_FinalYear_Result","=INDIRECT(dms_SingleYear_FinalYear_Ref)",null,null,null,"Formula errors OK"]
[null,"FRCP length in years",{"$f":"INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_FRCPlength_Num","=INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Multi Year Final Year Reference",{"$f":"INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))","v":"dms_FRCP_y5"},"dms_MultiYear_FinalYear_Ref","=INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))"]
[null,"Multi Year Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)","v":"2022-23"},"dms_MultiYear_FinalYear_Result","=IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)",null,null,null,"Formula errors OK"]
[null,"CRCP length in years",{"$f":"INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_CRCPlength_Num","=INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"CRCP Final Year Reference",{"$f":"INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))","v":"CRCP_y5"},"dms_CRCP_FinalYear_Ref","=INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))"]
[null,"CRCP First Year Result",{"$f":"INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))","v":"2013-14"},"dms_CRCP_FirstYear_Result","=INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))"]
[null,"CRCP Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)","v":"2015-16"},"dms_CRCP_FinalYear_Result","=IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)"]
[null,"Table 6.6.3 - Public lighting repair - no. business days",{"$f":"INDEX(dms_663_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_663"]
[null,"Distribution Determination Reference",{"$f":"INDEX(dms_DeterminationRef_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"2015-20 Distribution Determination"}]
[null,"Backcast templates only - unit of measure ","$0s","dms_Backcast_UOM","If the cover sheet is for Backcast data ensure to apply dms_Backcast_UOM named range to this field. Otherwise, do not apply this named range."]
[null,"EB/CA Unit of Measure for Monetary Values","$0s","dms_dollar_nom_UOM","If the cover sheet is attached to an EB files make sure this field is set"]
[]
[null,"discard this record?","NO","dms_DISCARD","If record is to be discarded from DB set this flag to YES"]
[]
[null,"USES NAMED RANGES FLAG","yes","dms_Defined_Names_Used"]

{"sheet":"Contents","index":3,"n_rows":27,"n_cols":19,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"CONTENTS"]
[]
[]
[null,null,null,null,"1. Business details",null,null,null,null,null,null,"2. Expenditure"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"4. Alternative control services",null,null,null,null,null,null,"5. Network information",null,null,null,null,null,null,"6. Service & quality"]

{"sheet":"2.1 Expenditure summary","index":4,"n_rows":126,"n_cols":3,"rows_kept":126,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.1 EXPENDITURE SUMMARY & RECONCILIATION"]
[]
[null,"There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.1.1 - STANDARD CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Replacement expenditure",185809461.97181317]
[null,"Connections",55282599.029999979]
[null,"Augmentation Expenditure",100768270.28]
[null,"Non-network",44924222.429999992]
[null,"capitalised network overheads",76244540.012482867]
[null,"capitalised corporate overheads",107859046.68751723]
[null,"Metering",0]
[null,"Public Lighting",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-15586937.355499998]
[null,"capcons (included in the above)",23966209.391209014]
[null,"TOTAL GROSS CAPEX \n(including capcons)",{"$f":"+SUM(C11:C26)","v":555301203.05631328}]
[]
[null,"2.1.2 - STANDARD CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Vegetation management",45360019.779999986]
[null,"Maintenance",63374143.719999984]
[null,"Emergency response",38441155.950000003]
[null,"Non-network",169475925.13111249]
[null,"network overheads",91600404.097189263]
[null,"corporate overheads",116096443.67579757]
[null,"Metering",0]
[null,"Public Lighting",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-175660470.17111248]
[null,"TOTAL OPEX",{"$f":"+SUM(C33:C48)","v":348687622.18298686}]
[]
[null,"2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Connections",4875954.9499999536]
[null,"capitalised network overheads",7176541.8152946606]
[null,"capitalised corporate overheads",9715985.206705343]
[null,"Metering",16099986.189999897]
[null,"Public lighting",6539658.5299999993]
[null,"Fee and quoted",7494264.6600000001]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-6424860.7139000082]
[null,"TOTAL CAPEX",{"$f":"+SUM(C54:C67)","v":45477530.638099842}]
[]
[null,"2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Connections",18167055.010000013]
[null,"network overheads",18415684.913908798]
[null,"corporate overheads",23630034.583104409]
[null,"Metering",15716978.179999989]
[null,"Public lighting",11845528.4]
[null,"Fee and quoted",25450855.749999996]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-31243808.140000001]
[null,"TOTAL OPEX",{"$f":"+SUM(C73:C86)","v":81982328.697013214}]
[]
[null,"2.1.5 - DUAL FUNCTION ASSETS CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Replacement expenditure"]
[null,"Connections"]
[null,"Augmentation Expenditure"]
[null,"Non-network"]
[null,"Capitalised network overheads"]
[null,"Capitalised corporate overheads"]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item"]
[null,"capcons (included in the above)"]
[null,"TOTAL GROSS CAPEX (including capcons)",{"$f":"SUM(C92:C105)","v":0}]
[]
[null,"2.1.6 - DUAL FUNCTION ASSETS OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Vegetation management"]
[null,"Maintenance"]
[null,"Emergency response"]
[null,"Non-network"]
[null,"Network overheads"]
[null,"Corporate overheads"]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item"]
[null,"TOTAL OPEX",{"$f":"SUM(C112:C125)","v":0}]

{"sheet":"2.2 Repex","index":5,"n_rows":172,"n_cols":7,"rows_kept":172,"cut":false,"hidden":false,"merged":[[151,1,154,1],[155,1,158,1],[166,1,169,1],[170,1,171,1],[159,1,165,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.2 REPEX"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY"]
[null,null,null,null,"EXPENDITURE ($0's)","ASSET REPLACEMENTS\n(0's)","ASSET FAILURES\n(0's)"]
[null,"ASSET GROUP","ASSET CATEGORY",null,{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole",null,1245046.3499999999,1401]
[null,null,"˂ = 1 kV; Wood",null,13051708.934274044,3220,2]
[null,null,"> 1 kV & < = 11 kV; Wood",null,13215197.363890463,2773,6]
[null,null,"˃ 11 kV & < = 22 kV; Wood"]
[null,null,"> 22 kV & < = 66 kV; Wood",null,1334125.3001038439,136]
[null,null,"> 66 kV & < = 132 kV; Wood",null,744062.26817321999,33]
[null,null,"> 132 kV; Wood"]
[null,null,"˂ = 1 kV; Concrete"]
[null,null,"> 1 kV & < = 11 kV; Concrete",null,444397.87752782402,39]
[null,null,"˃ 11 kV & < = 22 kV; Concrete"]
[null,null,"> 22 kV & < = 66 kV; Concrete"]
[null,null,"> 66 kV & < = 132 kV; Concrete"]
[null,null,"> 132 kV; Concrete"]
[null,null,"˂ = 1 kV; Steel",null,null,null,2]
[null,null,"> 1 kV & < = 11 kV; Steel"]
[null,null,"˃ 11 kV & < = 22 kV; Steel"]
[null,null,"> 22 kV & < = 66 kV; Steel"]
[null,null,"> 66 kV & < = 132 kV; Steel"]
[null,null,"> 132 kV; Steel"]
[null,null,"Other"]
[null,"POLE TOP STRUCTURES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,8872073.7613050025,5809,79]
[null,null,"> 1 kV & < = 11 kV",null,7572630.5986618511,7407,58]
[null,null,"˃ 11 kV & < = 22 kV"]
[null,null,"> 22 kV & < = 66 kV",null,174358.34349949702,159,7]
[null,null,"> 66 kV & < = 132 kV",null,3500.737887709,1]
[null,null,"> 132 kV"]
[null,null,"Other",null,178.275234985,-6]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",null,9148905.754286265,134.16200000000001,105]
[null,null,"> 1 kV & < = 11 kV",null,6593770.2016087705,219.46109999999999,114]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER"]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase"]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase"]
[null,null,"> 22 kV & < = 66 kV",null,136459.22105690298,12.649559999999999,2]
[null,null,"> 66 kV & < = 132 kV",null,419585.27703455399,0.88902000000000003]
[null,null,"> 132 kV"]
[null,null,"Other"]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,4781001.8345395355,23.257999999999999,69]
[null,null,"> 1 kV & < = 11 kV",null,3527860.7572710668,7.2024800000000004,38]
[null,null,"> 11 kV & < = 22 kV"]
[null,null,"> 22 kV & < = 33 kV",null,6997767.9139161995,11.128590000000001]
[null,null,"> 33 kV & < = 66 kV"]
[null,null,"> 66 kV & < = 132 kV",null,499.09829380100001]
[null,null,">  132 kV"]
[null,null,"Other"]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",null,12385322.527992124,31742.465600000003,388]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",null,1076984.5676514891,2760.2144000000003]
[null,null,"˂ = 11 kV ; Residential ; Complex Type"]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type"]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type"]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  "]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  "]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  "]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  "]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  "]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  "]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  "]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  "]
[null,null,"> 132 kV ; Commercial & Industrial  "]
[null,null,"> 132 kV ; Subdivision  "]
[null,null,"Other"]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,574692.47112966608,89,8]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase"]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase"]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,955785.71107180195,115,11]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,9968962.2111439109,560,44]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,null,null,4]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,null,null,2]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,2931064.1849443698,52]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,325930.15541572601,5]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",null,null,null,1]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",null,841084.95118695509,5]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",null,882050.35551193904,16,2]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",null,154413.625286189]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",null,7281397.7021014905,4]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",null,-1000900.0534409099]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",null,11708.089934827]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA"]
[null,null,"Other"]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  FUSE",null,3398205.2932015937,48,130]
[null,null,"˂ = 11 kV  ; Switch",null,14366414.084168285,2996,56]
[null,null,"˂ = 11 kV ;  Circuit Breaker",null,5066137.8073290875,75,3]
[null,null,"> 11 kV & < = 22 kV  ; Switch"]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker"]
[null,null,"> 22 kV & < = 33 kV ; Switch",null,2026022.3247466099,11]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",null,5226496.2038745601,4,4]
[null,null,"> 33 kV & < = 66 kV ; Switch"]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker"]
[null,null,"> 66 kV & < = 132 kV ; Switch",null,2081.5095793099999]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",null,19011.630450387998,null,1]
[null,null,"> 132 kV ; Switch"]
[null,null,"> 132 kV ; Circuit Breaker"]
[null,null,"Other",null,3769.3469365239998]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",null,290656.59852813801,118,633]
[null,null,"Luminaires ;  Minor Road",null,2270734.5842801761,1166,1478]
[null,null,"Brackets ; Major Road",null,254531.88876259699,56]
[null,null,"Brackets ; Minor Road",null,1434932.6189837931,1475]
[null,null,"Lamps ; Major Road",null,514.51735571699999,2,6528]
[null,null,"Lamps ; Minor Road",null,157.802513339,4,12671]
[null,null,"Poles / Columns ; Major Road",null,69138.938751566995,2]
[null,null,"Poles / Columns ; Minor Road",null,299444.38975658995,179]
[null,null,"Other",null,303.99105415399998,1]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",null,12047488.28768043,507,458]
[null,null,"Local Network Wiring Assets",null,null,null,1]
[null,null,"Communications Network Assets",null,6868979.4701153897,96,169]
[null,null,"Master Station Assets",null,null,null,""]
[null,null,"Communications Site Infrastructure",null,132630.36222313001,null,10]
[null,null,"Communications Linear Assets",null,3335404.9294129917,70.668000000000006,9]
[null,null,"AFLC",null,3783918.1337779691,25,35]
[null,null,"Other",null,865792.17983575095,18]
[null,"OTHER BY: \nDNSP DEFINED","Other non AER Asset Categories",null,9395068.7100000009,522]
[null,null,null,null,"","",""]
[null,null,null,null,"","",""]
[null,null,null,null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"","",""]
[]
[]
[null,"2.2.2 - SELECTED ASSET CHARACTERISTICS"]
[null,null,null,null,"ASSET VOLUMES CURRENTLY IN COMMISSION","ASSET REPLACEMENTS\n(0's)"]
[null,"ASSET GROUP","METRIC","UNITS",{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"TOTAL POLES BY: \nFEEDER TYPE","Total CBD poles","Number",0]
[null,null,"Total urban poles","Number",231989,3211.9832564515914]
[null,null,"Total rural long poles","Number",0]
[null,null,"Total rural short poles","Number",215885,2989.0167435484086]
[null,"OVERHEAD CONDUCTORS BY:\nCONDUCTOR LENGTH BY FEEDER TYPE","Conductors CBD","KM",0]
[null,null,"Conductors urban","KM",13274,138.73670870221187]
[null,null,"Conductors rural long","KM"]
[null,null,"Conductors rural short","KM",21855,228.42329129778818]
[null,"OVERHEAD CONDUCTORS BY: \nCONDUCTOR LENGTH MATERIAL TYPE","OH conductor LV ABC","KM",3224,33.696485524780101]
[null,null,"OH conductor steel","KM",860,8.9885166102080909]
[null,null,"OH conductor ACSR","KM",7360,76.924979361780871]
[null,null,"OH conductor AAAC","KM",164,1.7140892140396824]
[null,null,"OH conductor AAC","KM",16730,174.8580033590481]
[null,null,"OH conductor HDBC","KM",6791,70.977925930143186]
[null,null,"Other","KM"]
[null,"UNDERGROUND CABLES BY: \nCABLE LENGTH BY FEEDER TYPE","Cable CBD","KM",213,0.49014949980634098]
[null,null,"Cable urban","KM",12085,27.809655892768216]
[null,null,"Cable rural long","KM",0]
[null,null,"Cable rural short","KM",5775,13.289264607425443]
[null,"TRANSFORMERS BY: \nTOTAL MVA","Total MVA replaced","MVA",31022,270]
[null,null,"Total MVA disposed of","MVA",31022,182]

{"sheet":"2.3(a) Augex","index":6,"n_rows":129,"n_cols":34,"rows_kept":129,"cut":false,"hidden":false,"merged":[[6,1,6,3],[11,21,11,22],[10,11,10,22],[12,17,12,19],[72,11,72,13],[72,14,72,16],[71,1,71,10],[72,1,73,1],[72,2,73,2],[72,3,73,3],[72,4,73,4],[72,6,73,6],[11,3,12,3],[11,4,12,4],[11,5,12,5],[11,14,11,15],[73,7,73,10],[72,7,72,10],[71,11,71,22],[72,17,72,19],[72,21,72,22],[12,30,12,31],[71,23,71,24],[71,25,73,25],[71,26,73,26],[71,30,71,31],[73,23,73,24],[73,27,73,29],[73,30,73,31],[71,29,72,29],[71,27,71,28],[11,6,12,6],[11,16,11,19],[12,23,12,24],[10,30,10,31],[10,23,10,24],[10,25,12,25],[10,26,12,26],[10,27,10,28],[10,29,11,29],[11,7,11,8],[11,9,11,10],[11,11,11,13],[10,1,10,10],[11,1,12,1],[11,2,12,2],[12,27,12,29]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.3 AUGEX PROJECT DATA"]
[]
[]
[null,"There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped.  See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS. "]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTY CONTRACTS","LAND AND EASEMENTS"]
[null,"SUBSTATION ID","SUBSTATION TYPE\n(drop down)","PROJECT ID","PROJECT TYPE\n(drop down)","PROJECT TRIGGER\n(drop down)","VOLTAGE (KV)","SUBSTATION RATING\nNORMAL CYCLIC\n(MVA)",null,"SUBSTATION RATING\nN-1 EMERGENCY\n(MVA)",null,"TRANSFORMERS",null,null,"SWITCHGEAR",null,"CAPACITORS",null,null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"PRE","POST","PRE","POST","UNITS ADDED ","MVA ADDED","EXPENDITURE ($0's)","UNITS ADDED ","EXPENDITURE ($0's)","MVAR ADDED","EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,"MGP","Zone substation","C0062187","Substation upgrade - capacity","Demand growth","33/11",22.85,45,10.8,16.88,1,20,354694,13,493985,5.4,136357,null,null,2298687.5699999998,10826.83,2972520,2158738,3217757,{"$f":"SUM(N14,P14,R14,U14,W14,X14,Y14)","v":11632738.57},"2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,6464443]
[null,"NBR","Zone substation","C0065092","Substation upgrade - capacity","Other","33/11",68.75,55.63,46.89,40.5,1,25,629173,21,613730,10.8,272939,null,null,2617245.27,13450.42,1417020,600958,2199884,8350949.2699999996,"2006,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,1494975]
[null,"BGY","Zone substation","C0065225","New substation establishment","Demand growth","33/11",0,60,0,33.75,2,50,1325779,30,1264288,10.8,273015,null,null,3733060.19,14464.42,2992121,2071262,3969700,15629225.189999999,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2016",null,null,6053107]
[null,"GYN","Zone substation","C0065303","New substation establishment","Demand growth","33/11",0,27.82,0,0,1,25,639271,12,542942,5.4,136939,null,null,5541089.0099999998,17868,3670745,2974877,4783042,18288905.009999998,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2016",null,null,8080000.9100000001]
[null,"WMR","Zone substation","C0065333","New substation establishment","Other","33/11",0,9.6,0,0,1,8,353984,20,177330,1.79,50504,null,null,1566815.93,8171.37,2042567,1497518,2460461,8149179.9299999997,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,4441816.5599999996]
[null,"UMG","Zone substation","C0077354","Substation upgrade - capacity","Demand growth","33/11",55,82.5,31.25,62.5,1,25,659936,12,511156,5.4,136477,null,null,1272332.18,8134.25,1084885,604465,1647573,5916824.1799999997,"2006,2009,2010,2011,2012,2013,2014,2015,2016",null,null,1537397.8]
[null,"CNA ","Zone substation","C0094795","Substation upgrade - capacity","Demand growth","33/11",5.2,26.25,0,0,1,20,392468,18,828451,null,null,null,null,2094907.82,10454.58,2118353,1366751,2764558,9565488.8200000003,"2008,2009,2010,2011,2012,2013,2014,2015",null,null,4098522.49]
[null,"DBS","Zone substation","C0112644","New substation establishment","Demand growth","33/11",0,52.5,0,31.25,2,50,1272504,18,600542,5.4,136436,null,null,1683266.55,4765.17,1497231,1157274,2267035,8614288.5500000007,"2008,2009,2010,2011,2012,2013,2014,2015",null,null,3423534.14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N46,P46,R46,U46,W46,X46,Y46)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,22266828.600000001,"2003,2004,2005,2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016"]
[]
[]
[null,"AUG232_1","AUG232_2","AUG232_3","AUG232_4","AUG232_5","AUG232_6","ED_AUG232_00001","ED_AUG232_00002","ED_AUG232_00003","ED_AUG232_00004","ED_AUG232_00005","ED_AUG232_00006","ED_AUG232_00007","ED_AUG232_00008","ED_AUG232_00009","ED_AUG232_00010","ED_AUG232_00011","ED_AUG232_00012","ED_AUG232_00013","ED_AUG232_00014","ED_AUG232_00015","ED_AUG232_00016","ED_AUG232_00017","ED_AUG232_00018","ED_AUG232_00019","ED_AUG232_00020","ED_AUG232_00021"]
[null,"2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS."]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTY CONTRACTS","LAND AND EASEMENTS"]
[null,"LINE ID","PROJECT ID","PROJECT TYPE","PROJECT TRIGGER",null,"VOLTAGE (KV)","ROUTE LINE LENGTH ADDED",null,null,null,"POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS)",null,null,"OVERHEAD LINES",null,null,"UNDERGROUND CABLES",null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"KM ADDED",null,null,null,"POLES/TOWERS ADDED","POLES/TOWERS UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,"F3700, F3702","C0062187","New line on new route - single circuit","Demand growth",null,"Other",null,2.7,null,null,26,33,98647,2.4048330240000002,3.1286070000000001,39176,0.30459000000000003,null,108595,3037305.4,10826.83,2972520,2158738,3217757,{"$f":"SUM(N75,Q75,T75,U75,W75,X75,Y75)","v":11632738.4},"2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,6464442.9100000001,null,null,null,"New line on new route - single circuit"]
[null,"F3250, F451","C0065225","New line on new route - single circuit","Demand growth",null,"Other",null,6.6849999999999996,null,null,100,2,175038,6.4240192499999997,0.15123075,46676,0.66791999999999996,null,267910,6106518.7699999996,14464.42,2992121,2071262,3969700,15629225.77,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2016",null,null,6053106.9500000002,null,null,null,"New line on new route - dual circuit"]
[null,"F3009, F3011","C0065303","New line on new route - dual circuit","Demand growth",null,"Other",null,4.867,null,null,null,12,34851,1.98E-3,null,14,10.32372,null,1985454,4839922.54,17868,3670745,2974877,4783042,18288905.539999999,"2006, 2007, 2008, 2009, 2010, 2011, 2012, 2013, 2014, 2016",null,null,8080000.9100000001,null,null,null,"New line on new route - other"]
[null,"F323","C0065333","New line on new route - single circuit","Other",null,"Other",null,0.1,null,null,null,24,58260,null,1.21638,8657,0.13200000000000001,null,26665,2055051.49,8171.37,2042567,1497518,2460461,8149179.4900000002,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,4441816.5599999996,null,null,null,"Line rebuild over existing route - single circuit"]
[null,"F3005, F3004 (Ex-F341)","C0074512","New line on new route - single circuit","Demand growth",null,"Other",null,21,null,null,193,null,340957,20.37255,null,141094,null,null,null,1033704.58,14064.17,1584187,595511,2251924,5947377.5800000001,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,1780501.27,null,null,null,"Line rebuild over existing route - dual circuit"]
[null,"F3429, F3430","C0077211","New line on new route - dual circuit","Demand growth",null,"Other",null,3.4,null,null,null,null,null,null,null,null,8.4618599999999997,null,2841601,1288061.1499999999,6579.58,1578946,1161415,2861682,9731705.1500000004,"2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,3283626.22,null,null,null,"Reconductor - Single circuit"]
[null,"F7344, F3359","C0082077","New line on new route - dual circuit","Demand growth",null,"Other",null,10.079000000000001,null,null,3,null,7016,27.28341,null,786679,0.71411999999999998,null,588400,1702489.64,15881.97,9107105,8113232,11348230,31653151.640000001,"2007,2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,23871499.539999999,null,null,null,"Reconductor - Dual circuit"]
[null,"F378","C0117380","New line on new route - single circuit","Demand growth",null,"Other",null,15,null,null,155,85,429709,15.38111256,8.4439343999999998,170542,null,null,null,1088414.58,7201.25,1746050,1246886,2434527,7116128.5800000001,"2008,2009,2010,2011,2012,2013,2014,2015,2016",null,null,3720968.04,null,null,null,"Reconductor - Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - raising/retensoring"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - voltage upgrade"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - capacity"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"String spare circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N107,Q107,T107,U107,W107,X107,Y107)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,58024177.969999999,"2003,2004,2005,2006,2007,2008,2009,2010,2011,2012,2013,2014,2015,2016"]

{"sheet":"2.3(b) Augex","index":7,"n_rows":46,"n_cols":5,"rows_kept":46,"cut":false,"hidden":false,"merged":[[10,1,11,1],[21,1,22,1],[35,1,36,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.3 AUGEX  DATA"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS."]
[null,"DESCRIPTOR METRICS"]
[null,"PROJECT TYPE",null,"UNITS ADDED\n(0's)","UNITS UPGRADED\n(0's)"]
[null,null,"UNITS",{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"HV Feeder Augmentations - Overhead Lines","Circuit line length in km",70.62,107.47799999999999]
[null,"HV Feeder Augmentations - Underground Cables","Circuit line length in km",43.398000000000003,20.887599999999999]
[null,"LV Feeder Augmentations - Overhead Lines","Circuit line length in km",3.3155999999999999,21.94866]
[null,"LV Feeder Augmentations - Underground Cables","Circuit line length in km",1.179,6.54]
[null,"Distribution Substation Augmentations - Pole Mounted","Number",85,168]
[null,"Distribution Substation Augmentations - Ground Mounted","Number",1,4]
[null,"Distribution Substation Augmentations - Indoor","Number",1,9]
[]
[null,"COST METRICS"]
[null,"TOTAL DIRECT EXPENDITURE - Project Type",null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"HV Feeder Augmentations - Overhead Lines",null,6958582.9100000001]
[null,"HV Feeder Augmentations - Underground Cables",null,2838723.78]
[null,"HV Feeder Non-Material Projects",null,6863167.9500000002]
[null,"LV Feeder Augmentations - Overhead Lines",null,2414057.11]
[null,"LV Feeder Augmentations - Underground Cables",null,614634.31000000006]
[null,"LV Feeder Non-Material Projects",null,754224.77]
[null,"Distribution Substation Augmentations - Pole Mounted",null,3454335.78]
[null,"Distribution Substation Augmentations - Ground Mounted",null,429278.51]
[null,"Distribution Substation Augmentations - Indoor",null,525172.74]
[]
[]
[null,"2.3.4 - AUGEX DATA - TOTAL EXPENDITURE"]
[null,"AUGMENTATION CAPEX (As incurred)",null,"EXPENDITURE\n ($0's)"]
[null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Subtransmission Substations, Switching Stations, Zone Substations",null,17486560.52]
[null,"Subtransmission Lines",null,21349556.510000002]
[null,"HV Feeders",null,16660474.66]
[null,"HV Feeders - Land Purchases and Easements",null,0]
[null,"Distribution Substations",null,4408787.04]
[null,"Distribution Substations - Land Purchases And Easements",null,0]
[null,"LV Feeders",null,3782916.17]
[null,"LV Feeders - Land Purchases And Easements",null,0]
[null,"Other Assets",null,37079975.380000003]

{"sheet":"2.5 Connections","index":8,"n_rows":73,"n_cols":5,"rows_kept":73,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.5 CONNECTIONS"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.5.1 - DESCRIPTOR METRICS"]
[null,"<<<GROUP-ROW>>>"]
[]
[null,null,null,null,"VOLUMES AND EXPENDITURE"]
[null,"CONNECTION SUBCATEGORY","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2015-16"}]
[null,"RESIDENTIAL","Underground connections","0's",24746]
[null,null,"Overhead connections","0's",15242]
[null,null,"Distribution substation installed","MVA added",15.22]
[null,null,"Distribution substations installed","0's",109]
[null,null,"Distribution substation installed","total spend $0s",2736360.1700000004]
[null,null,"Augmentation HV","net circuit km added",13]
[null,null,"Augmentation HV","total spend $0s",630133.79]
[null,null,"Augmentation LV","net circuit km added",82.39]
[null,null,"Augmentation LV","total spend $0s",8800802.7398377843]
[null,null,"Mean days to connect residential customer with LV single phase connection","0's",8.1]
[null,null,"Volume of GSL breaches for residential customers","0's",36]
[null,null,"Volume of customer complaints relating to connection services","0's",461]
[null,null,"GSL payments","$0s",4322]
[null,"COMMERCIAL/INDUSTRIAL","Underground connections","0's",2437]
[null,null,"Overhead connections","0's",2512]
[null,null,"Distribution substation installed","MVA added",223.86]
[null,null,"Distribution substations installed","0's",372]
[null,null,"Distribution substation installed","total spend $0s",32791189.610000003]
[null,null,"Augmentation HV","net circuit km added",57.529999999999994]
[null,null,"Augmentation HV","total spend $0s",24464407.530000001]
[null,null,"Augmentation LV","net circuit km added",50.419999999999995]
[null,null,"Augmentation LV","total spend $0s",3138721.910162217]
[null,"SUBDIVISION","Underground connections","0's",26015.128822252911]
[null,null,"Overhead connections","0's",496.87117774709014]
[null,null,"Distribution substation installed","MVA added",1.5]
[null,null,"Distribution substations installed","0's",2]
[null,null,"Distribution substation installed","total spend $0s",124742.25]
[null,null,"Augmentation HV","net circuit km added",7.12]
[null,null,"Augmentation HV","total spend $0s",5615277.25]
[null,null,"Augmentation LV","net circuit km added",1.1299999999999999]
[null,null,"Augmentation LV","total spend $0s",23973.74]
[null,null,"Cost per lot ($)","$0s",217.41072872661437]
[null,"EMBEDDED GENERATION","Underground connections","0's",10676]
[null,null,"Overhead connections","0's",9258]
[null,null,"Distribution substation installed","MVA added",0]
[null,null,"Distribution substations installed","0's",0]
[null,null,"Distribution substation installed","total spend $0s",0]
[null,null,"Augmentation HV","net circuit km added",0]
[null,null,"Augmentation HV","total spend $0s",0]
[null,null,"Augmentation LV","net circuit km added",0]
[null,null,"Augmentation LV","total spend $0s",0]
[]
[]
[]
[null,"2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION"]
[null,null,null,"EXPENDITURE\n($0's)","VOLUMES\n(0's)"]
[null,"CONNECTION SUBCATEGORY","CONNECTION CLASSIFICATION",{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"RESIDENTIAL","Simple connection LV",8228527.1898377836,39699]
[null,null,"Complex connection LV",572275.55000000005,57]
[null,null,"Complex connection HV",3366493.9600000004,232]
[null,"COMMERCIAL/INDUSTRIAL","Simple connection LV",1356125.200162217,3139]
[null,null,"Complex connection HV (customer connected at LV, minor HV works)",53762900.469999999,1655]
[null,null,"Complex connection HV (customer connected at LV, upstream asset works)",3645701.34,140]
[null,null,"Complex connection HV (customer connected at HV)",10173.64,5]
[null,null,"Complex connection sub-transmission",1619418.4,10]
[null,"SUBDIVISION","Complex connection LV",23838.74,40]
[null,null,"Complex connection HV (no upstream asset works)",5740154.5,19894]
[null,null,"Complex connection HV (with upstream asset works)","-",0]
[null,"EMBEDDED GENERATION","Simple connection LV",0,19883]
[null,null,"Complex connection HV (small capacity)",0,4]
[null,null,"Complex connection HV (large capacity)",0,0]

{"sheet":"2.6 Non-network","index":9,"n_rows":94,"n_cols":6,"rows_kept":94,"cut":false,"hidden":false,"merged":[[89,2,93,2],[69,2,73,2],[74,2,78,2],[79,2,83,2],[84,2,88,2],[58,5,59,5],[61,2,61,4],[62,2,62,4],[63,2,63,4],[5,1,5,2],[60,2,60,4],[9,2,9,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.6 NON NETWORK EXPENDITURE"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.6.1 - NON-NETWORK EXPENDITURE"]
[null,null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","ASSET CATEGORY",null,null,{"$f":"CRY","v":"2015-16"}]
[null,"OPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,1649562]
[null,null,"Recurrent expenditure",null,null,95717078.919999987]
[null,null,"Non-recurrent expenditure",null,null,2699059.19]
[null,"MOTOR VEHICLES","Car",null,null,4959934.5469800578]
[null,null,"Light commercial vehicle",null,null,1662534.4354671475]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,8230838.1598437633]
[null,null,"Heavy commercial vehicle",null,null,5583599.5072945459]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,40931881]
[null,"OTHER","Other expenditure",null,null,8041437.3715269817]
[null,"OTHER - DNSP nominated","Other Non Network Expenditure - Mobile Generators",null,null,1232509.6506225085]
[null,null,"Other Non Network Expenditure - Fleet",null,null,910782]
[null,null,"Other Non Network Expenditure - Tools & Equipment",null,null,5898145.7209044732]
[null,null,"Other Non Network Expenditure - Office Furniture",null,null,0]
[]
[]
[]
[]
[]
[]
[]
[null,"CAPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,2480529.9999999902]
[null,null,"Recurrent expenditure",null,null,125930.82999999993]
[null,null,"Non-recurrent expenditure",null,null,0]
[null,"MOTOR VEHICLES","Car",null,null,2911298.290000001]
[null,null,"Light commercial vehicle",null,null,1107668.3000000003]
[null,null,"Elevated work platform (LCV)  "]
[null,null,"Elevated work platform (HCV)",null,null,10175577.369999997]
[null,null,"Heavy commercial vehicle",null,null,3843685.1400000006]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,15169154.880000001]
[null,"OTHER","Other expenditure",null,null,9110377.6199999992]
[null,"OTHER - DNSP nominated",{"$f":"IF(ISBLANK(C22),\"\",C22)","v":"Other Non Network Expenditure - Mobile Generators"},null,null,307891.19000000012]
[null,null,{"$f":"IF(ISBLANK(C23),\"\",C23)","v":"Other Non Network Expenditure - Fleet"},null,null,713961.48]
[null,null,"Other Non Network Expenditure - Tools & Equipment",null,null,5265498.42]
[null,null,"Other Non Network Expenditure - Office Furniture",null,null,2823026.53]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[]
[]
[]
[null,"2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE"]
[null,null,null,null,null,"VOLUMES\n(0's)"]
[]
[null,"NON-NETWORK CATEGORY","DESCRIPTOR METRIC",null,null,{"$f":"CRY","v":"2015-16"}]
[null,"IT & COMMUNICATIONS","Employee numbers",null,null,2440.2649999999999]
[null,null,"User numbers",null,null,3899.7999999999997]
[null,null,"Number of devices",null,null,4357.0999999999995]
[]
[]
[null,"2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES"]
[null,null,null,null,null,"VOLUMES / %"]
[null,"NON-NETWORK CATEGORY","ASSET CATEGORY","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2015-16"}]
[null,"MOTOR VEHICLES","CAR","Average kilometres travelled","0's",25600.892781832928]
[null,null,null,"Number purchased","0's",67]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",617]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.86]
[null,null,"LIGHT COMMERCIAL VEHICLE","Average kilometres travelled","0's",25448.609573459711]
[null,null,null,"Number purchased","0's",18]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",176]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.86]
[null,null,"ELEVATED WORK PLATFORM (LCV) ","Average kilometres travelled","0's",0]
[null,null,null,"Number purchased","0's",0]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",0]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0]
[null,null,"ELEVATED WORK PLATFORM (HCV)","Average kilometres travelled","0's",21902.625236593056]
[null,null,null,"Number purchased","0's",34]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",238]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.86]
[null,null,"HEAVY COMMERCIAL VEHICLE ","Average kilometres travelled","0's",23350.483806552256]
[null,null,null,"Number purchased","0's",6]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",267.08333333333337]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.86]

{"sheet":"2.7 Vegetation management","index":10,"n_rows":410,"n_cols":5,"rows_kept":410,"cut":false,"hidden":false,"merged":[[405,1,405,3],[5,1,5,2],[7,1,7,2],[12,4,13,4],[124,4,125,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.7 VEGETATION MANAGEMENT"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"Please enter a description for each Zone in table 2.7.1 - Urban and CBD.  The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2."]
[]
[]
["`","2.7.1 - DESCRIPTOR METRICS BY ZONE"]
[null,"URBAN AND CBD"]
[null,null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"ZONES","ASSET","UNITS"]
[null,"ZONE 1","Route line length within zone","km",9731.65]
[null,null,"Number of maintenance spans","0's",123383]
[null,null,"Total length of maintenance spans","km",5552.2899377593358]
[null,null,"Length of vegetation corridors","km",2048.9654941064473]
[null,null,"Average number of trees per maintenance span","0's",2.84]
[null,null,"Average frequency of cutting cycle","years",1.38]
[null,"ZONE 2","Route line length within zone","km"]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 3","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 4","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 5","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 6","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 7","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 8","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 9","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 10","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 11","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 12","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 13","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 14","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 15","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 16","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 17","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 18","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[]
[null,"RURAL"]
[null,null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"ZONES","ASSET","UNITS"]
[null,{"$f":"B15","v":"ZONE 1"},"Route line length within zone","km",15994.45]
[null,null,"Number of maintenance spans","0's",80651]
[null,null,"Total length of maintenance spans","km",6479.964920948617]
[null,null,"Length of vegetation corridors","km",3269.2853058935534]
[null,null,"Average number of trees per maintenance span","0's",4.8499999999999996]
[null,null,"Average frequency of cutting cycle","years",1.93]
[null,{"$f":"B21","v":"ZONE 2"},"Route line length within zone","km"]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B27","v":"ZONE 3"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B33","v":"ZONE 4"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B39","v":"ZONE 5"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B45","v":"ZONE 6"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B51","v":"ZONE 7"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B57","v":"ZONE 8"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B63","v":"ZONE 9"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B69","v":"ZONE 10"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B75","v":"ZONE 11"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B81","v":"ZONE 12"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B87","v":"ZONE 13"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B93","v":"ZONE 14"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B99","v":"ZONE 15"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B105","v":"ZONE 16"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B111","v":"ZONE 17"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B117","v":"ZONE 18"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[]
[]
[]
[null,"2.7.2 - EXPENDITURE METRICS BY ZONE"]
[null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"ZONES","SERVICE SUBCATEGORY",null,{"$f":"CRY","v":"2015-16"}]
[null,{"$f":"B15","v":"ZONE 1"},"Tree trimming (excluding hazard trees) ",null,42283800.759999998]
[null,null,"Hazard tree cutting ",null,186717.62]
[null,null,"Ground clearance ",null,5776776.75]
[null,null,"Vegetation corridor clearance ",null,19792871.739999998]
[null,null,"Inspection ",null,3200887.52]
[null,null,"Audit ",null,1280999.1200000001]
[null,null,"Contractor liaison expenditure "]
[null,null,"Tree replacement program costs ",null,242591.47]
[null,null,"Other vegetation management costs not specified in sheet "]
[null,{"$f":"B21","v":"ZONE 2"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B27","v":"ZONE 3"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B33","v":"ZONE 4"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B39","v":"ZONE 5"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B45","v":"ZONE 6"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B51","v":"ZONE 7"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B57","v":"ZONE 8"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B63","v":"ZONE 9"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B69","v":"ZONE 10"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B75","v":"ZONE 11"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B81","v":"ZONE 12"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B87","v":"ZONE 13"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B93","v":"ZONE 14"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B99","v":"ZONE 15"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B105","v":"ZONE 16"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B111","v":"ZONE 17"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B117","v":"ZONE 18"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[]
[null,"2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS"]
[null,null,null,null,"VOLUMES\n(0's)"]
[null,"DESCRIPTOR METRIC",null,null,{"$f":"CRY","v":"2015-16"}]
[null,"Number of fire starts caused by vegetation grow-ins (NSP responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility)",null,null,40]
[null,"Number of fire starts caused by vegetation grow-ins (other party responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility)",null,null,0]

{"sheet":"2.8 Maintenance","index":11,"n_rows":85,"n_cols":10,"rows_kept":85,"cut":false,"hidden":false,"merged":[[8,7,9,7],[8,8,10,8],[8,9,10,9],[68,1,69,1],[5,1,5,2],[28,1,29,1],[48,5,48,6],[8,5,8,6]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.8 MAINTENANCE"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"ASSET QUANTITY\n(0's)",null,"AVERAGE AGE OF ASSET GROUP ","INSPECTION \nCYCLE \n(YEARS)","MAINTENANCE \nCYCLE \n(YEARS)"]
[null,null,null,null,null," AT YEAR END","INSPECTED / MAINTAINED"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units",{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",447856,19800,28,10]
[null,null,"Service lines","Number of customers","Number",591751,24827,16.82]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",447856,96353,28,5]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",35129,33296,37,1]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",17041,5814,17]
[null,null,"33 KV and above","Length (KM)","KM",1003,120,19,null,1]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",206,68,23]
[null,null,"Non-CBD","Length (KM)","KM",17838,5866,17]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",48505,585,16]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",22100,491,12,null,6]
[null,null,"Distribution substation - other equipment","Earth mat","Number",24,null,17]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",47753,209,24]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",588,1869,20,1.5,1]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",18,null,35]
[null,null,"Transformers - HV","Number of HV transformers","Number",495,null,20]
[null,null,"Zone substation - other equipment","All other plant items",{"$f":"D27","v":"All other plant items"},21402,4162,13,6,1]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",305,624,36,1.5]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",225584,56314,13,0.25]
[null,null,"Major roads","Number of public lights maintained","Number",88591,18358,13,0.11]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",11110,648,4.2273627362736272,1]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",19204,1017,14.342012080816497,null,6]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets","<DNSP to nominate>",{"$f":"D33","v":"<DNSP to nominate>"}]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number"]
[null,"Ground clearance - access tracks","Access tracks","Number","Number"]
[null,"Other","Zone Substation Inspection","All Zone Substation Assets",null,22430.999999992,1765,13,6]
[null,null,"Distribution Asset Inspection","Distribution Substations",null,48505,4740,16,3]
[null,null,"Distribution Pole Mounted Plant Maintenance","All Distribution PMP (Transformers, Reclosers, Regulators, Sectionalisers)",null,50063,8524,15,2.5,5]
[null,null,"Underground Feeder Asset Inspection","All Underground Feeder Assets",null,18044,2450,17,0.08]
[null,null,"Pilot Cable Inspection and Maintenance","All Pilot Cables (Copper & Fibre)",null,3616124,70,17.774161932739396,1]
[null,null,"Other","Adjustments to labour, fleet and materials oncosts"]
[]
[]
[]
[]
[]
[]
[null,"2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"EXPENDITURE ($0'S)"]
[null,null,null,null,null," ROUTINE MAINTENANCE ","NON-ROUTINE MAINTENANCE"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units",{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",174789.72,13761436.210000001]
[null,null,"Service lines","Number of customers","Number",null,7042081.8399999999]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",4655962.04,4286.3100000000004]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",3390092.44,487537.6]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",312178.23,1881887.57]
[null,null,"33 KV and above","Length (KM)","KM",null,2196066.9]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",3563.99,46556.12]
[null,null,"Non-CBD","Length (KM)","KM",308614.24,4031398.35]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",null,817019.32]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",1922140.7]
[null,null,"Distribution substation - other equipment","Earth mat","Number"]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",null,580549.65]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",871687.08,3401529]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number"]
[null,null,"Transformers - HV","Number of HV transformers","Number"]
[null,null,"Zone substation - other equipment",{"$f":"IF(ISBLANK(D27),\"\",D27)","v":"All other plant items"},{"$f":"IF(ISBLANK(E27),\"\",E27)","v":"All other plant items"},1548472.84,5205076.6399999997]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",170811.49,3588316.84]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number"]
[null,null,"Major roads","Number of public lights maintained","Number"]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",990040.32,87783.05]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",2297383.73,562485.98]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets",{"$f":"IF(ISBLANK(D33),\"\",D33)","v":"<DNSP to nominate>"},{"$f":"IF(ISBLANK(E33),\"\",E33)","v":"<DNSP to nominate>"}]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number"]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",null,811499.23]
[null,"Other",{"$f":"IF(ISBLANK(C36),\"\",C36)","v":"Zone Substation Inspection"},"All Zone Substation Assets",null,674335.85,637791.69999999995]
[null,null,"Distribution Asset Inspection","Distribution Substations",null,543093.13,1165399.97]
[null,null,"Distribution Pole Mounted Plant Maintenance","All Distribution PMP (Transformers, Reclosers, Regulators, Sectionalisers)",null,573356.51,1234779.93]
[null,null,"Underground Feeder Asset Inspection","All Underground Feeder Assets",null,257200.85,261222.12]
[null,null,"Pilot Cable Inspection and Maintenance","All Pilot Cables (Copper & Fibre)",null,7872.67,288457.99]
[null,null,"Other","Adjustments to labour, fleet and materials oncosts",null,null,969518.27]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]

{"sheet":"2.9 Emergency Response","index":12,"n_rows":421,"n_cols":4,"rows_kept":421,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.9 EMERGENCY RESPONSE"]
[]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"(A) TOTAL EMERGENCY RESPONSE EXPENDITURE","Total Expenditure",38441155.950000003]
[null,"(B) MAJOR EVENTS O&M EXPENDITURE","Storm struck Energex 29 November 2015",640588]
[null,null,"Storm struck Energex 10 December 2015",731996.96]
[null,null,"Storm struck Energex 04 June 2016",159169.35999999999]
[null,null,"Storm struck Energex 24 June 2016",404815.59]
[]
[]
[]
[null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"(C) MAJOR EVENT DAYS O&M EXPENDITURE","2015-07-01",0]
[null,null,"2015-07-02",0]
[null,null,"2015-07-03",0]
[null,null,"2015-07-04",0]
[null,null,"2015-07-05",0]
[null,null,"2015-07-06",0]
[null,null,"2015-07-07",0]
[null,null,"2015-07-08",0]
[null,null,"2015-07-09",0]
[null,null,"2015-07-10",0]
[null,null,"2015-07-11",0]
[null,null,"2015-07-12",0]
[null,null,"2015-07-13",0]
[null,null,"2015-07-14",0]
[null,null,"2015-07-15",0]
[null,null,"2015-07-16",0]
[null,null,"2015-07-17",0]
[null,null,"2015-07-18",0]
[null,null,"2015-07-19",0]
[null,null,"2015-07-20",0]
[null,null,"2015-07-21",0]
[null,null,"2015-07-22",0]
[null,null,"2015-07-23",0]
[null,null,"2015-07-24",0]
[null,null,"2015-07-25",0]
[null,null,"2015-07-26",0]
[null,null,"2015-07-27",0]
[null,null,"2015-07-28",0]
[null,null,"2015-07-29",0]
[null,null,"2015-07-30",0]
[null,null,"2015-07-31",0]
[null,null,"2015-08-01",0]
[null,null,"2015-08-02",0]
[null,null,"2015-08-03",0]
[null,null,"2015-08-04",0]
[null,null,"2015-08-05",0]
[null,null,"2015-08-06",0]
[null,null,"2015-08-07",0]
[null,null,"2015-08-08",0]
[null,null,"2015-08-09",0]
[null,null,"2015-08-10",0]
[null,null,"2015-08-11",0]
[null,null,"2015-08-12",0]
[null,null,"2015-08-13",0]
[null,null,"2015-08-14",0]
[null,null,"2015-08-15",0]
[null,null,"2015-08-16",0]
[null,null,"2015-08-17",0]
[null,null,"2015-08-18",0]
[null,null,"2015-08-19",0]
[null,null,"2015-08-20",0]
[null,null,"2015-08-21",0]
[null,null,"2015-08-22",0]
[null,null,"2015-08-23",0]
[null,null,"2015-08-24",0]
[null,null,"2015-08-25",0]
[null,null,"2015-08-26",0]
[null,null,"2015-08-27",0]
[null,null,"2015-08-28",0]
[null,null,"2015-08-29",0]
[null,null,"2015-08-30",0]
[null,null,"2015-08-31",0]
[null,null,"2015-09-01",0]
[null,null,"2015-09-02",0]
[null,null,"2015-09-03",0]
[null,null,"2015-09-04",0]
[null,null,"2015-09-05",0]
[null,null,"2015-09-06",0]
[null,null,"2015-09-07",0]
[null,null,"2015-09-08",0]
[null,null,"2015-09-09",0]
[null,null,"2015-09-10",0]
[null,null,"2015-09-11",0]
[null,null,"2015-09-12",0]
[null,null,"2015-09-13",0]
[null,null,"2015-09-14",0]
[null,null,"2015-09-15",0]
[null,null,"2015-09-16",0]
[null,null,"2015-09-17",0]
[null,null,"2015-09-18",0]
[null,null,"2015-09-19",0]
[null,null,"2015-09-20",0]
[null,null,"2015-09-21",0]
[null,null,"2015-09-22",0]
[null,null,"2015-09-23",0]
[null,null,"2015-09-24",0]
[null,null,"2015-09-25",0]
[null,null,"2015-09-26",0]
[null,null,"2015-09-27",0]
[null,null,"2015-09-28",0]
[null,null,"2015-09-29",0]
[null,null,"2015-09-30",0]
[null,null,"2015-10-01",0]
[null,null,"2015-10-02",0]
[null,null,"2015-10-03",0]
[null,null,"2015-10-04",0]
[null,null,"2015-10-05",0]
[null,null,"2015-10-06",0]
[null,null,"2015-10-07",0]
[null,null,"2015-10-08",0]
[null,null,"2015-10-09",0]
[null,null,"2015-10-10",0]
[null,null,"2015-10-11",0]
[null,null,"2015-10-12",0]
[null,null,"2015-10-13",0]
[null,null,"2015-10-14",0]
[null,null,"2015-10-15",0]
[null,null,"2015-10-16",0]
[null,null,"2015-10-17",0]
[null,null,"2015-10-18",0]
[null,null,"2015-10-19",0]
[null,null,"2015-10-20",0]
[null,null,"2015-10-21",0]
[null,null,"2015-10-22",0]
[null,null,"2015-10-23",0]
[null,null,"2015-10-24",0]
[null,null,"2015-10-25",0]
[null,null,"2015-10-26",0]
[null,null,"2015-10-27",0]
[null,null,"2015-10-28",0]
[null,null,"2015-10-29",0]
[null,null,"2015-10-30",0]
[null,null,"2015-10-31",0]
[null,null,"2015-11-01",0]
[null,null,"2015-11-02",0]
[null,null,"2015-11-03",0]
[null,null,"2015-11-04",0]
[null,null,"2015-11-05",0]
[null,null,"2015-11-06",0]
[null,null,"2015-11-07",0]
[null,null,"2015-11-08",0]
[null,null,"2015-11-09",0]
[null,null,"2015-11-10",0]
[null,null,"2015-11-11",0]
[null,null,"2015-11-12",0]
[null,null,"2015-11-13",0]
[null,null,"2015-11-14",0]
[null,null,"2015-11-15",0]
[null,null,"2015-11-16",0]
[null,null,"2015-11-17",0]
[null,null,"2015-11-18",0]
[null,null,"2015-11-19",0]
[null,null,"2015-11-20",0]
[null,null,"2015-11-21",0]
[null,null,"2015-11-22",0]
[null,null,"2015-11-23",0]
[null,null,"2015-11-24",0]
[null,null,"2015-11-25",0]
[null,null,"2015-11-26",0]
[null,null,"2015-11-27",0]
[null,null,"2015-11-28",483.89]
[null,null,"2015-11-29",206491.68]
[null,null,"2015-11-30",280059.96999999997]
[null,null,"2015-12-01",60788.12]
[null,null,"2015-12-02",26489.22]
[null,null,"2015-12-03",2518.56]
[null,null,"2015-12-04",-4096.87]
[null,null,"2015-12-05",26930.58]
[null,null,"2015-12-06",10054.879999999999]
[null,null,"2015-12-07",-30596.11]
[null,null,"2015-12-08",5815.49]
[null,null,"2015-12-09",78.150000000000006]
[null,null,"2015-12-10",195446.28]
[null,null,"2015-12-11",365462.72]
[null,null,"2015-12-12",27082.65]
[null,null,"2015-12-13",6045.62]
[null,null,"2015-12-14",56138.44]
[null,null,"2015-12-15",6612.44]
[null,null,"2015-12-16",2478.12]
[null,null,"2015-12-17",3671.28]
[null,null,"2015-12-18",562.30999999999995]
[null,null,"2015-12-19",7958.23]
[null,null,"2015-12-20",0]
[null,null,"2015-12-21",7732.15]
[null,null,"2015-12-22",-4673.62]
[null,null,"2015-12-23",1684.95]
[null,null,"2015-12-24",11716.79]
[null,null,"2015-12-25",0]
[null,null,"2015-12-26",0]
[null,null,"2015-12-27",0]
[null,null,"2015-12-28",0]
[null,null,"2015-12-29",0]
[null,null,"2015-12-30",-4.38]
[null,null,"2015-12-31",99.09]
[null,null,"2016-01-01",0]
[null,null,"2016-01-02",0]
[null,null,"2016-01-03",0]
[null,null,"2016-01-04",840]
[null,null,"2016-01-05",60.84]
[null,null,"2016-01-06",1850.55]
[null,null,"2016-01-07",0]
[null,null,"2016-01-08",5871.87]
[null,null,"2016-01-09",209.42]
[null,null,"2016-01-10",0]
[null,null,"2016-01-11",2613.5]
[null,null,"2016-01-12",160.57]
[null,null,"2016-01-13",0]
[null,null,"2016-01-14",0]
[null,null,"2016-01-15",0]
[null,null,"2016-01-16",0]
[null,null,"2016-01-17",0]
[null,null,"2016-01-18",-91.52]
[null,null,"2016-01-19",1454.55]
[null,null,"2016-01-20",-456.85]
[null,null,"2016-01-21",0]
[null,null,"2016-01-22",0]
[null,null,"2016-01-23",0]
[null,null,"2016-01-24",0]
[null,null,"2016-01-25",22.82]
[null,null,"2016-01-26",0]
[null,null,"2016-01-27",0]
[null,null,"2016-01-28",1065.5]
[null,null,"2016-01-29",15586.2]
[null,null,"2016-01-30",0]
[null,null,"2016-01-31",0]
[null,null,"2016-02-01",0]
[null,null,"2016-02-02",0]
[null,null,"2016-02-03",0]
[null,null,"2016-02-04",-142.85]
[null,null,"2016-02-05",-217.94]
[null,null,"2016-02-06",0]
[null,null,"2016-02-07",0]
[null,null,"2016-02-08",41099.78]
[null,null,"2016-02-09",0]
[null,null,"2016-02-10",0]
[null,null,"2016-02-11",0]
[null,null,"2016-02-12",67.61]
[null,null,"2016-02-13",0]
[null,null,"2016-02-14",0]
[null,null,"2016-02-15",0]
[null,null,"2016-02-16",38.14]
[null,null,"2016-02-17",0]
[null,null,"2016-02-18",0]
[null,null,"2016-02-19",0]
[null,null,"2016-02-20",0]
[null,null,"2016-02-21",0]
[null,null,"2016-02-22",1841.4]
[null,null,"2016-02-23",0]
[null,null,"2016-02-24",0]
[null,null,"2016-02-25",30.41]
[null,null,"2016-02-26",0]
[null,null,"2016-02-27",0]
[null,null,"2016-02-28",0]
[null,null,"2016-02-29",0]
[null,null,"2016-03-01",0]
[null,null,"2016-03-02",0]
[null,null,"2016-03-03",0]
[null,null,"2016-03-04",0]
[null,null,"2016-03-05",0]
[null,null,"2016-03-06",0]
[null,null,"2016-03-07",0]
[null,null,"2016-03-08",0]
[null,null,"2016-03-09",0]
[null,null,"2016-03-10",0]
[null,null,"2016-03-11",0]
[null,null,"2016-03-12",0]
[null,null,"2016-03-13",0]
[null,null,"2016-03-14",18228.05]
[null,null,"2016-03-15",0]
[null,null,"2016-03-16",0]
[null,null,"2016-03-17",0]
[null,null,"2016-03-18",0]
[null,null,"2016-03-19",0]
[null,null,"2016-03-20",0]
[null,null,"2016-03-21",0]
[null,null,"2016-03-22",0]
[null,null,"2016-03-23",0]
[null,null,"2016-03-24",0]
[null,null,"2016-03-25",0]
[null,null,"2016-03-26",0]
[null,null,"2016-03-27",0]
[null,null,"2016-03-28",0]
[null,null,"2016-03-29",0]
[null,null,"2016-03-30",0]
[null,null,"2016-03-31",0]
[null,null,"2016-04-01",180.59]
[null,null,"2016-04-02",0]
[null,null,"2016-04-03",0]
[null,null,"2016-04-04",0]
[null,null,"2016-04-05",0]
[null,null,"2016-04-06",0]
[null,null,"2016-04-07",0]
[null,null,"2016-04-08",0]
[null,null,"2016-04-09",0]
[null,null,"2016-04-10",0]
[null,null,"2016-04-11",0]
[null,null,"2016-04-12",0]
[null,null,"2016-04-13",0]
[null,null,"2016-04-14",0]
[null,null,"2016-04-15",0]
[null,null,"2016-04-16",0]
[null,null,"2016-04-17",0]
[null,null,"2016-04-18",0]
[null,null,"2016-04-19",0]
[null,null,"2016-04-20",0]
[null,null,"2016-04-21",0]
[null,null,"2016-04-22",0]
[null,null,"2016-04-23",0]
[null,null,"2016-04-24",0]
[null,null,"2016-04-25",0]
[null,null,"2016-04-26",0]
[null,null,"2016-04-27",0]
[null,null,"2016-04-28",0]
[null,null,"2016-04-29",0]
[null,null,"2016-04-30",0]
[null,null,"2016-05-01",0]
[null,null,"2016-05-02",0]
[null,null,"2016-05-03",0]
[null,null,"2016-05-04",0]
[null,null,"2016-05-05",0]
[null,null,"2016-05-06",0]
[null,null,"2016-05-07",0]
[null,null,"2016-05-08",0]
[null,null,"2016-05-09",0]
[null,null,"2016-05-10",0]
[null,null,"2016-05-11",0]
[null,null,"2016-05-12",0]
[null,null,"2016-05-13",0]
[null,null,"2016-05-14",0]
[null,null,"2016-05-15",0]
[null,null,"2016-05-16",0]
[null,null,"2016-05-17",0]
[null,null,"2016-05-18",0]
[null,null,"2016-05-19",0]
[null,null,"2016-05-20",17615.509999999998]
[null,null,"2016-05-21",0]
[null,null,"2016-05-22",0]
[null,null,"2016-05-23",0]
[null,null,"2016-05-24",0]
[null,null,"2016-05-25",0]
[null,null,"2016-05-26",0]
[null,null,"2016-05-27",0]
[null,null,"2016-05-28",0]
[null,null,"2016-05-29",0]
[null,null,"2016-05-30",0]
[null,null,"2016-05-31",0]
[null,null,"2016-06-01",0]
[null,null,"2016-06-02",0]
[null,null,"2016-06-03",2547.5700000000002]
[null,null,"2016-06-04",82261.53]
[null,null,"2016-06-05",37272.07]
[null,null,"2016-06-06",14019.28]
[null,null,"2016-06-07",3773.67]
[null,null,"2016-06-08",620.87]
[null,null,"2016-06-09",2946.57]
[null,null,"2016-06-10",-6158.01]
[null,null,"2016-06-11",8016.15]
[null,null,"2016-06-12",131.71]
[null,null,"2016-06-13",1388.14]
[null,null,"2016-06-14",1464.76]
[null,null,"2016-06-15",385.13]
[null,null,"2016-06-16",0]
[null,null,"2016-06-17",0]
[null,null,"2016-06-18",0]
[null,null,"2016-06-19",0]
[null,null,"2016-06-20",393.6]
[null,null,"2016-06-21",45.45]
[null,null,"2016-06-22",0]
[null,null,"2016-06-23",-11]
[null,null,"2016-06-24",47827.77]
[null,null,"2016-06-25",191089.45]
[null,null,"2016-06-26",20302.45]
[null,null,"2016-06-27",49144.4]
[null,null,"2016-06-28",3171.72]
[null,null,"2016-06-29",15909.2]
[null,null,"2016-06-30",79068.649999999994]

{"sheet":"2.10 Overheads","index":13,"n_rows":174,"n_cols":4,"rows_kept":174,"cut":false,"hidden":false,"merged":[[5,1,5,2],[106,1,106,3],[152,1,152,3],[10,1,10,3],[70,1,70,3]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.10 OVERHEADS"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"NETWORK OVERHEADS"]
[null,"Standard Control Services","Network management",29037622.296194233]
[null,null,"Network planning",7596746.8975109123]
[null,null,"Network control and operational switching",25399959.154884145]
[null,null,"Quality and standard functions",12204309.237355717]
[null,null,"Project governance and related functions",29105717.199826114]
[null,null,"Other",0]
[null,null,"Training and Development",15152678.242811576]
[null,null,"OHS",5014161.0311900238]
[null,null,"Customer Service",14349000.833483404]
[null,null,"Network Billing and Other Energy Market Services (including meter reading)",6059229.47958754]
[null,null,"DSM Initiatives",8196524.5700000003]
[null,null,"Levies",8833576]
[null,null,"Network Property",6895419.1668284778]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","Network management",4129919.6917485762]
[null,null,"Network planning",1079026.9126975832]
[null,null,"Network control and operational switching",777917.21432718274]
[null,null,"Quality and standard functions",1623681.7323132711]
[null,null,"Project governance and related functions",4278959.849279061]
[null,null,"Other",0]
[null,null,"Training and Development",2331141.5424520508]
[null,null,"OHS",712201.52128883393]
[null,null,"Customer Service",1281878.7516536114]
[null,null,"Network Billing and Other Energy Market Services (including meter reading)",8398087.8052848261]
[null,null,"DSM Initiatives",0]
[null,null,"Levies",0]
[null,null,"Network Property",979411.70815846382]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total  ",""]
[null,"Unregulated Services","Total  ",2607309.9488971825]
[]
[null,"CAPITALISED NETWORK OVERHEADS"]
[null,"Standard Control Services","Network management",19310070.448456228]
[null,null,"Network planning",5072120.2899928773]
[null,null,"Network control and operational switching",3656711.0980201215]
[null,null,"Quality and standard functions",7632348.1481736461]
[null,null,"Project governance and related functions",20844540.737685837]
[null,null,"Other",""]
[null,null,"Training and Development",7584658.3608005438]
[null,null,"OHS",3347805.0864013261]
[null,null,"Customer Service",1846231.8837018353]
[null,null,"Network Billing and Other Energy Market Services (including meter reading)",2346189.1818763628]
[null,null,"DSM Initiatives",0]
[null,null,"Levies",0]
[null,null,"Network Property",4603864.7773741046]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"CORPORATE OVERHEADS"]
[null,"Standard Control Services","  Office of CEO",621638.40512278921]
[null,null,"Legal and Secretariat",1372404.638863744]
[null,null,"Audit",1237974.5097565234]
[null,null,"Strategy and Regulation",5071891.6811646894]
[null,null,"Human Resources",8843027.4529935867]
[null,null,"Finance",7614283.518834726]
[null,null,"Business Support Services",16086674.569463409]
[null,null,"Business Operations and Performance",1950925.9503173158]
[null,null,"Field Support Services",8763417.4208760429]
[null,null,"Stakeholder Engagement and Management",6264816.0658633877]
[null,null,"Other Operating",7738860.4438993521]
[null,null,"Corporate Restructuring",15568913.2002181]
[null,null,"IT and Communications",85007880.033160359]
[null,null,"Property",34775250.668293968]
[null,null,"Fleet",18318747.111499995]
[null,null,"Debt Raising Costs",4718784.6929867947]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","  Office of CEO",117615.575882031]
[null,null,"Legal and Secretariat",259662.46713995459]
[null,null,"Audit",234227.94295266847]
[null,null,"Strategy and Regulation",959614.87574699777]
[null,null,"Human Resources",1571517.579932055]
[null,null,"Finance",1440641.9127529745]
[null,null,"Business Support Services",2389910.8415962132]
[null,null,"Business Operations and Performance",296246.40915826545]
[null,null,"Field Support Services",1244796.6229109054]
[null,null,"Stakeholder Engagement and Management",1185319.2198380628]
[null,null,"Other Operating",1231744.776118869]
[null,null,"Corporate Restructuring",2945678.189781901]
[null,null,"IT and Communications",12074351.24331991]
[null,null,"Property",4939536.3509657411]
[null,null,"Fleet",2262260.3346999995]
[null,null,"Debt Raising Costs",192895.44701320463]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total",""]
[null,"Unregulated Services","Total",6817456.7591028186]
[]
[null,"CAPITALISED CORPORATE OVERHEADS"]
[null,"Standard Control Services","  Office of CEO",0]
[null,null,"Legal and Secretariat",0]
[null,null,"Audit",0]
[null,null,"Strategy and Regulation",0]
[null,null,"Human Resources",1438351.2560951235]
[null,null,"Finance",8.5065994833626767E-10]
[null,null,"Business Support Services",9254312.7778060269]
[null,null,"Business Operations and Performance",1031614.8265667224]
[null,null,"Field Support Services",5850248.2690944793]
[null,null,"Stakeholder Engagement and Management",0]
[null,null,"Other Operating",2.6540590388091549E-9]
[null,null,"Corporate Restructuring",0]
[null,null,"IT and Communications",56757214.494897373]
[null,null,"Property",23216574.051557496]
[null,null,"Fleet",10310731.011499997]
[null,null,"Debt Raising Costs",0]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]

{"sheet":"2.11 Labour","index":14,"n_rows":55,"n_cols":7,"rows_kept":55,"cut":false,"hidden":false,"merged":[[36,1,36,2],[5,1,5,2],[11,1,11,2],[33,5,33,6],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,6,9,6],[33,3,33,4],[10,1,10,2],[35,1,35,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.11 LABOUR"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.11.1 - COST METRICS PER ANNUM"]
[null,null,null,"ASL \n(0's)","TOTAL LABOUR EXPENDITURE\n($0's)","AVERAGE PRODUCTIVE WORK HOURS \nPER ASL \n(0's)","STAND-DOWN OCCURENCES \nPER ASL \n(0's)"]
[]
[null,null,null,{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"INTERNAL LABOUR EXPENDITURE"]
[null,"CORPORATE OVERHEADS","Executive manager",3.7874186488666886,1162509.8292345495,1569.9692221592045,0]
[null,null,"Senior manager",19.410520575441783,5957862.8748270664,1569.9692221592045,0]
[null,null,"Manager",23.513704387417402,5571638.4180351803,1655.8515801391436,0]
[null,null,"Professional",136.3148704338395,23450081.45617222,1662.2488456432914,0]
[null,null,"Semi professional",25.337908038577666,4215160.4702834943,1680.243889707876,0]
[null,null,"Support staff",168.0439313394547,18634208.148795433,1669.7570168928553,0]
[null,null,"Intern, junior staff, apprentice",31.793693043052574,4236624.3724864209,1730.2174838622143,0]
[null,"NETWORK OVERHEADS ","Executive manager",2.7993272750990355,861800.26614934276,1570.2992110981763,0]
[null,null,"Senior manager",32.192263663638904,9910703.0607174411,1570.2992110981763,0]
[null,null,"Manager",35.753534183071352,8497290.6933758445,1655.5041559104056,0]
[null,null,"Professional",185.27232541435356,32023566.30134552,1659.070851905215,8.0848990058277809E-2]
[null,null,"Semi professional",368.37405107175766,58785376.27766075,1604.8377882457012,0.93455569220873702]
[null,null,"Support staff",233.71701570544488,26848826.712440249,1682.0392039122917,0.15929870852491682]
[null,null,"Intern, junior staff, apprentice",195.75199331260183,24785412.455314703,1651.1269099384244,4.7930575635145631]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker",595.83291083734969,91724690.600935981,1894.9303788185805,0]
[null,null,"Skilled non electical worker",326.41633887202033,55897046.747349441,1713.3687273695689,0]
[null,null,"Apprentice",93.203860831859629,8460207.7957198452,1491.7768713575924,0]
[null,null,"Unskilled worker",66.346854068637072,7365996.9245565059,1794.4505375200831,0]
[]
[]
[null,"2.11.2 - DESCRIPTOR METRICS"]
[null,null,null,"ORDINARY TIME (0's)",null,"OVERTIME (0's)"]
[null,null,null,"PER ASL","HOURLY RATE\nPER ASL","PER ASL","HOURLY RATE\nPER ASL"]
[null,null,null,{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"AVERAGE PRODUCTIVE WORK HOURS PER ASL"]
[null,"CORPORATE OVERHEADS","Executive manager",1569.8830701467712,189.13795733199544,8.6152012433381747E-2,0]
[null,null,"Senior manager",1569.8830701467712,189.13795733199541,8.6152012433381747E-2,0]
[null,null,"Manager",1654.3641662666982,138.55539338336766,1.4874138724454253,0]
[null,null,"Professional",1655.1563836080109,100.11833439397688,7.0924620352805219,111.733917143092]
[null,null,"Semi professional",1551.3277496400287,94.9490575793277,128.91614006784724,97.515322422491835]
[null,null,"Support staff",1656.5503787267146,64.214345578451457,13.206638166140685,75.526232636147341]
[null,null,"Intern, junior staff, apprentice",1551.3277496400287,72.860016887404726,178.88973422218555,81.837772091589429]
[null,"NETWORK OVERHEADS ","Executive manager",1569.8830701467712,189.13795733199544,0.41614095140516538,0]
[null,null,"Senior manager",1569.8830701467712,189.13795733199544,0.41614095140516544,0]
[null,null,"Manager",1654.3641662666982,138.55539338336766,1.1399896437073771,0]
[null,null,"Professional",1654.6176326950686,100.45219727429119,4.4532192101465213,129.41588808779588]
[null,null,"Semi professional",1551.3277496400287,94.9490575793277,53.510038605672356,129.42250954304916]
[null,null,"Support staff",1655.4205568475277,65.635542593416972,26.618647064763998,88.100326510720308]
[null,null,"Intern, junior staff, apprentice",1551.5838639101316,72.577446873852196,99.543046028292821,100.29927898374285]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker",1551.3277496400287,72.860016887404726,343.60262917855169,103.71582767242977]
[null,null,"Skilled non electical worker",1551.3277496400287,94.949057579327715,162.04097772954017,112.09528289034806]
[null,null,"Apprentice",1260.3277496400287,57.634502260740106,231.4491217175638,65.004407753556393]
[null,null,"Unskilled worker",1551.3277496400287,56.582022870608938,243.12278788005432,80.061453123547764]

{"sheet":"2.12 Input tables","index":15,"n_rows":82,"n_cols":9,"rows_kept":82,"cut":false,"hidden":false,"merged":[[9,3,9,8],[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"2.12 INPUT TABLES"]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.12.1 - INPUT TABLES"]
[null,null,null,"DIRECT MATERIAL EXPENDITURE","DIRECT LABOUR EXPENDITURE","CONTRACT EXPENDITURE","OTHER EXPENDITURE","RELATED PARTY CONTRACT EXPENDITURE","RELATED PARTY CONTRACT MARGIN\nEXPENDITURE"]
[null,null,null,"EXPENDITURE ($0's)"]
[null,null,null,{"$f":"CRY","v":"2015-16"},"2015-16","2015-16","2015-16","2015-16","2015-16"]
[null,"VEGETATION MANAGEMENT",{"$f":"'2.7 Vegetation management'!B15","v":"ZONE 1"},3404.4900000000002,99341.559999999939,45246324.079999983,10949.650000000009," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B21","v":"ZONE 2"},null,null,null,null," "]
[null,null,{"$f":"'2.7 Vegetation management'!B27","v":"ZONE 3"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B33","v":"ZONE 4"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B39","v":"ZONE 5"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B45","v":"ZONE 6"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B51","v":"ZONE 7"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B57","v":"ZONE 8"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B63","v":"ZONE 9"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B69","v":"ZONE 10"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B75","v":"ZONE 11"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B81","v":"ZONE 12"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B87","v":"ZONE 13"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B93","v":"ZONE 14"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B99","v":"ZONE 15"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B105","v":"ZONE 16"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B111","v":"ZONE 17"},"","","",""," ",""]
[null,null,{"$f":"'2.7 Vegetation management'!B117","v":"ZONE 18"},"","","",""," ",""]
[null,"ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",4197.28,152118.23000000001,124.95,18349.259999999998," ",""]
[null,null,"Pole inspection and treatment",363806.57,77239.56,4186281.34,28634.57,116672.67,""]
[null,null,"Overhead asset inspection",16553.02,1326683.81,1903790.19,143065.42000000001," ",""]
[null,null,"Network underground cable maintenance",8041.61,200516.72,80993.39,22626.51," ",""]
[null,null,"Distribution substation equipment & property maintenance",456069.47,1073239.29,249473.18,143358.76," ",""]
[null,null,"Zone substation equipment maintenance",369609.21,1602873.1,248332.87,199344.74," ",""]
[null,null,"Zone substation property maintenance",186.49,119412.48,38341.760000000002,12870.76," ",""]
[null,null,"Public lighting maintenance","","","",""," ",""]
[null,null,"Scada & network control maintenance",4649.24,782246.84,117253.97,85890.27," ",""]
[null,null,"Protection systems maintenance",1785.75,2057052.55,9715.5400000000009,228829.89," ",""]
[null,null,"Subtransmission asset maintenance - for dnsps with dual function assets","","","",""," ",""]
[null,null,"Other",125059.46,1590766.98,164210.85,175821.72," ",""]
[null,"NON-ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",1801866.71,7809571.3399999999,10233455.460000001,958624.54," ",""]
[null,null,"Pole inspection and treatment",2410.9299999999998,1371.24,164.8,339.34," ",""]
[null,null,"Overhead asset inspection",14580.75,242313.75,204702.45,25940.65," ",""]
[null,null,"Network underground cable maintenance",738494.37,1824045.17,1285475.4099999999,229939.52," ",""]
[null,null,"Distribution substation equipment & property maintenance",-168426.42,423510.46,257277.91,885207.02," ",""]
[null,null,"Zone substation equipment maintenance",1217489.82,4619902.67,2214978.2200000002,554234.93000000005," ",""]
[null,null,"Zone substation property maintenance",192707.02,176325.32,1212766.18,2006518.32," ",""]
[null,null,"Public lighting maintenance","","","",""," ",""]
[null,null,"SCADA & network control maintenance",729.56,78678.28,0,8375.2099999999991," ",""]
[null,null,"Protection systems maintenance",4411.3500000000004,501053.36,2349.2399999999998,54672.03," ",""]
[null,null,"Subtransmission asset maintenance - for DNSP with dual function assets","","","",""," ",""]
[null,null,"Other",596423.81000000006,2539695.5699999998,1762060.17,470489.66," ",""]
[null,"OVERHEADS","Network overheads",14256409.497661324,150855218.74195141,16474898.947971307,14457953.600188708,1294447.5899999999,""]
[null,null,"Corporate overheads",988552.52310114494,73276373.927404881,121461761.113337,68392279.348384336,100238536.29000001,""]
[null,"AUGMENTATION","Subtransmission substations, switching stations, zone substations",2682263.11,4178795.6,8578912.4000000004,2046589.41,271194.57999999996,""]
[null,null,"Subtransmission lines",4857423.78,3154682.99,10366718.859999999,2970730.88," ",""]
[null,null,"HV feeders",4031025.59,5400133.1299999999,6060051.5999999996,1169264.3400000001," ",""]
[null,null,"Distribution substations",820784.28,1565612.21,1724637.27,297753.28999999998," ",""]
[null,null,"LV feeders",773074.09,1301718.8400000001,1478335.3,229787.94," ",""]
[null,null,"Other assets",12744836.709999999,11693115.32,9668168.6099999994,2973854.7399999998," ",""]
[null,"CONNECTIONS","Simple and complex customer connections",23147975.699999999,27813217.02,25312046.780000001,2052369.49," ",""]
[null,"EMERGENCY RESPONSE","Major storms",184361.41,3782933.21,245347.32,407711.38," ",""]
[null,null,"Major event days",96413.22,1503819.04,170006.71,166330.94," ",""]
[null,"PUBLIC LIGHTING","All public lighting services",3833274.57,1558807.5899999999,12693973.960000001,299130.81," ",""]
[null,"METERING","All metering services",16495300.279999986,10743255.709999897,12328417.999999998,19553.509999999995," ",""]
[null,"FEE-BASED SERVICES","All fee-based services",455876.8,6322948.7199999988,10839929.119999999,676951.30000000016," ",""]
[null,"QUOTED SERVICES","All quoted services",4589529.959999999,8814191.0899999999,4789432.1500000004,-2466000.6200000006," ",""]
[null,"REPLACEMENT","Poles",5947795.4611380799,9954635.39568533,12709500.609764701,1422606.62738126," ",""]
[null,null,"Pole top structures",3487635.1764672599,5585521.7740171403,6757184.2738243202,792400.49228029104," ",""]
[null,null,"Overhead conductors",2921762.99729248,4620741.3323683599,8083772.2529327497,672443.87139290501," ",""]
[null,null,"Underground cables",3219205.6695364001,2825700.8378043901,8334731.4975387696,927491.59914106003," ",""]
[null,null,"Service lines",3414363.7127236598,839269.01211388898,8930231.3764979895,278442.994308102," ",""]
[null,null,"Transformers",10361961.690825701,6196289.0316787697,4806984.2004357995,1560954.4813457399," ",""]
[null,null,"Switchgear",9990520.8672904391,10235578.8444051,7665838.8648478799,2216199.6237429101," ",""]
[null,null,"Public lighting",879203.00584499002,1185515.85028029,2384815.1785649601,170881.29529583," ",""]
[null,null,"SCADA network control and protection systems",6714599.9067711905,10499284.276357001,7555163.4142548302,2265165.7656626198,232646.41000000003,""]
[null,null,"Other",1469354.01159716,5903986.8535859995,1264588.7565846993,757139.08878326602," ",""]
[null,"NON-NETWORK EXPENDITURE","IT and communications",2630919.7099999948,1.7763568394002501E-11,100319733.13000001,-278491.90000000002,102833727.59999999,""]
[null,null,"Motor vehicles",18585950.720865816,4136017.7895539743,691218.54992843175,15061948.689237289," ",""]
[null,null,"Buildings and property",3889378.1429557689,3435128.3043397111,14352861,34423668.16936855,98630.62999999999,""]
[null,null,"Other",9320277.9928220697,5003149.4894910306,1566250.2919944683,1262137.1561069104," ",""]

{"sheet":"4.1 Public lighting","index":16,"n_rows":291,"n_cols":5,"rows_kept":291,"cut":false,"hidden":false,"merged":[[9,2,10,2],[6,1,6,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"4.1 PUBLIC LIGHTING"]
[]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.1.1 - DESCRIPTOR METRICS OVER YEAR"]
[null,null,"LIGHT TYPE",null,"VOLUME \n(0's)"]
[null,null,null,null,{"$f":"CRY","v":"2015-16"}]
[null,"POPULATION OF LIGHTS","High Pressure Sodium - Major",null,37253]
[null,null,"Mercury Vapour - Major",null,2162]
[null,null,"Metal Hallide - Major",null,296]
[null,null,"High Pressure Sodium - Minor",null,15581]
[null,null,"Mercury Vapour - Minor",null,60462]
[null,null,"Metal Hallide - Minor",null,26]
[null,null,"Fluorescent - Minor",null,31257]
[null,null,"LED - Minor",null,1538]
[null,null,"Low Pressure Sodium - Minor",null,30]
[]
[]
[null,null,"TOTAL",null,148605]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"4.1.2 - DESCRIPTOR METRICS ANNUALLY"]
[]
[]
[null,null,null,null,"VOLUMES \n& EXPENDITURE"]
[null,"SERVICE/SERVICE QUALITY ","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2015-16"}]
[null,"LIGHT INSTALLATION","Major road light installation","0's",361]
[null,null,"Minor road light installation","0's",539]
[null,null,"Number of poles installed","0's",335]
[null,null,"Total cost","$0s",4676039.8899999997]
[null,"LIGHT REPLACEMENT","Major road light replacement","0's",924]
[null,null,"Minor road light replacement","0's",5649]
[null,null,"Number of poles replaced","0's",325]
[null,null,"Total cost","$0s",1863618.64]
[null,"LIGHT MAINTENANCE","Major road light maintenance","0's",18358]
[null,null,"Minor road light maintenance","0's",56314]
[null,null,"Number of poles installed","0's",273]
[null,null,"Total cost","$0s",11845528.4]
[null,"QUALITY OF SUPPLY","Mean days to rectify/replace public lighting assets","days",3.98]
[null,null,"GSO breaches","0's",0]
[null,null,"GSL payments","$0s",0]
[null,null,"Customer complaints","0's",16]
[]
[]
[null,"4.1.3 - COST METRICS"]
[null,null,null,null,"AVERAGE UNIT COST \n($)"]
[null,"ACTIVITY TYPE","LIGHT TYPE",null,{"$f":"CRY","v":"2015-16"}]
[null,"LIGHT INSTALLATION","Wood Pole Major",null,1625]
[null,null,"Steel Overhead Major",null,6634]
[null,null,"Underground Major",null,10858]
[null,null,"Wood Pole Minor",null,894]
[null,null,"Steel Underground Decorative Minor",null,4595]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,"LIGHT REPLACEMENT","High Pressure Sodium Major 150W",null,331]
[null,null,"Compact Flourescent Minor 32W",null,224]
[null,null,"High Pressure Sodium Minor 70W",null,229]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,"LIGHT MAINTENANCE","Public Lighting Maintenance (average cost per unit)",null,22.096912507551721]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]

{"sheet":"4.2 Metering","index":17,"n_rows":61,"n_cols":5,"rows_kept":61,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"4.2 METERING"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.2.1 - METERING DESCRIPTOR METRIC"]
[null,null,null,"VOLUMES\n(0's)"]
[null,"ASSET CATEGORY","ASSET SUBCATEGORY",{"$f":"CRY","v":"2015-16"}]
[null,"Meter Type 4","Single phase meter population "]
[null,null,"Multi phase meter population "]
[null,null,"Current transformer connected meter population "]
[null,null,"Direct connect meter population "]
[null,"Meter Type 5","Single phase meter population "]
[null,null,"Multi phase meter population "]
[null,null,"Current transformer connected meter population "]
[null,null,"Direct connect meter population "]
[null,"Meter Type 6","Single phase meter population ",2042076.5]
[null,null,"Multi phase meter population ",137137.5]
[null,null,"Current transformer connected meter population ",9603]
[null,null,"Direct connect meter population ",2169611]
[]
[]
[null,"4.2.2 - COST METRICS"]
[null,null,null,"VOLUMES\n(0's)","EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","METER TYPE",{"$f":"CRY","v":"2015-16"},{"$f":"CRY","v":"2015-16"}]
[null,"Meter purchase ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",88421,7769563]
[null,"Meter testing ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",6336,982751.62]
[null,"Meter investigation ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",4794,225196.77000000002]
[null,"Scheduled meter reading ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6"]
[null,"Special meter reading ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6"]
[null,"New meter installation ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",52122,11740928.9699999]
[null,"Meter replacement ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",20385,4359057.2199999969]
[null,"Meter maintenance ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",4089,1419935.24]
[null,"Remote meter reading ","Meter Type 4"]
[null,"Remote meter re-configuration ","Meter Type 4"]
[null,"Other metering ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6",null,3522589.6499999901]
[null,null,"Meter Type 7"]
[null,"IT infrastructure capex ","Meter Type 4"]
[null,"IT infrastructure opex ","Meter Type 4"]
[null,"Communications infrastructure capex ","Meter Type 4"]
[null,"Communications infrastructure opex ","Meter Type 4"]

{"sheet":"4.3 Fee-based services","index":18,"n_rows":479,"n_cols":6,"rows_kept":479,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"4.3 ANCILLARY SERVICES - FEE BASED SERVICES"]
[]
[null,"4.3.1 - COST METRICS FOR FEE-BASED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY",{"$f":"CRY","v":"2015-16"},null,{"$f":"CRY","v":"2015-16"}]
[null,"Common Fee-Based Services","Energisation",null,"ED_FEE431_00001"]
[null,null,"De-energisation",null,"ED_FEE431_00002"]
[null,null,"Re-energisation",null,"ED_FEE431_00003"]
[null,"Miscellaneous Fee-Based Services","A&A to current metering equipment",191048.12000000002,"ED_FEE431_00004",2354]
[null,null,"Attending LOS - LV cust at fault",224059.90999999997,"ED_FEE431_00005",720]
[null,null,"OH service replacement - single phase - part of Customer initiated supply enhancement",0,"ED_FEE431_00006",0]
[null,null,"OH service replacement - multi phase - part of Customer initiated supply enhancement",0,"ED_FEE431_00007",0]
[null,null,"De-en",4983643.18,"ED_FEE431_00008",119410]
[null,null,"Meter test",0,"ED_FEE431_00009",1059]
[null,null,"Meter inspect",-6557.71000000001,"ED_FEE431_00010",119]
[null,null,"Reconfigure meter",411495.9,"ED_FEE431_00011",8819]
[null,null,"Off-cycle read",309868.82,"ED_FEE431_00012",57079]
[null,null,"Site visit",744453.79,"ED_FEE431_00013",24915]
[null,null,"Locating Energex UG cables",0,"ED_FEE431_00014",""]
[null,null,"Temp connection",232504.72,"ED_FEE431_00015",2702]
[null,null,"Re-en - BH",5516501.517367796,"ED_FEE431_00016",228707]
[null,null,"Re-en - AH",18379.735452934368,"ED_FEE431_00017",762]
[null,null,"Re-en Visual - BH",1682445.2851877664,"ED_FEE431_00018",69752]
[null,null,"Re-en Visual - AH",76678.712604827248,"ED_FEE431_00019",3179]
[null,null,"Re-en NoPay Visual - BH",1133.6582234749546,"ED_FEE431_00020",47]
[null,null,"Re-en NoPay Visual - AH",72.361163200529006,"ED_FEE431_00021",3]
[null,null,"Supply Abolishment",356798.87,"ED_FEE431_00022",2893]
[null,null,"UMS (unmetered supply)",0,"ED_FEE431_00023",0]
[null,null,"SL glare screening - standard",16530.419999999998,"ED_FEE431_00024",1]
[null,null,"Replacement of standard luminaires with aero screen units/SL",0,"ED_FEE431_00025",""]
[null,null,"Rearrange connection assets",8532.24,"ED_FEE431_00026",48]
[null,null,"OH service line replacement",107562.03,"ED_FEE431_00027",1042]
[null,null,"Temporary disconnections and reconnection","","ED_FEE431_00028",53]
[null,null,"Customer initiated supply enhancement",482533.54000000004,"ED_FEE431_00029",1387]
[null,null,"Customer consultation or appointment",523444.63000000006,"ED_FEE431_00030",1]
[null,null,"Accreditation of alternative service providers",0,"ED_FEE431_00031",7]
[null,null,"Small customer connections",1527886.34,"ED_FEE431_00032",264]
[null,null,"CT Metering",886689.86999999988,"ED_FEE431_00033",573]
[null,null,null,"","ED_FEE431_00034",""]
[null,null,null,"","ED_FEE431_00035",""]
[null,null,null,"","ED_FEE431_00036",""]
[null,null,null,"","ED_FEE431_00037",""]
[null,null,null,"","ED_FEE431_00038",""]
[null,null,null,"","ED_FEE431_00039",""]
[null,null,null,"","ED_FEE431_00040",""]
[null,null,null,"","ED_FEE431_00041",""]
[null,null,null,"","ED_FEE431_00042",""]
[null,null,null,"","ED_FEE431_00043",""]
[null,null,null,"","ED_FEE431_00044",""]
[null,null,null,"","ED_FEE431_00045",""]
[null,null,null,"","ED_FEE431_00046",""]
[null,null,null,"","ED_FEE431_00047",""]
[null,null,null,"","ED_FEE431_00048",""]
[null,null,null,"","ED_FEE431_00049",""]
[null,null,null,"","ED_FEE431_00050",""]
[null,null,null,"","ED_FEE431_00051",""]
[null,null,null,"","ED_FEE431_00052",""]
[null,null,null,"","ED_FEE431_00053",""]
[null,null,null,"","ED_FEE431_00054",""]
[null,null,null,"","ED_FEE431_00055",""]
[null,null,null,"","ED_FEE431_00056",""]
[null,null,null,"","ED_FEE431_00057",""]
[null,null,null,"","ED_FEE431_00058",""]
[null,null,null,"","ED_FEE431_00059",""]
[null,null,null,"","ED_FEE431_00060",""]
[null,null,null,"","ED_FEE431_00061",""]
[null,null,null,"","ED_FEE431_00062",""]
[null,null,null,"","ED_FEE431_00063",""]
[null,null,null,"","ED_FEE431_00064",""]
[null,null,null,"","ED_FEE431_00065",""]
[null,null,null,"","ED_FEE431_00066",""]
[null,null,null,"","ED_FEE431_00067",""]
[null,null,null,"","ED_FEE431_00068",""]
[null,null,null,"","ED_FEE431_00069",""]
[null,null,null,"","ED_FEE431_00070",""]
[null,null,null,"","ED_FEE431_00071",""]
[null,null,null,"","ED_FEE431_00072",""]
[null,null,null,"","ED_FEE431_00073",""]
[null,null,null,"","ED_FEE431_00074",""]
[null,null,null,"","ED_FEE431_00075",""]
[null,null,null,"","ED_FEE431_00076",""]
[null,null,null,"","ED_FEE431_00077",""]
[null,null,null,"","ED_FEE431_00078",""]
[null,null,null,"","ED_FEE431_00079",""]
[null,null,null,"","ED_FEE431_00080",""]
[null,null,null,"","ED_FEE431_00081",""]
[null,null,null,"","ED_FEE431_00082",""]
[null,null,null,"","ED_FEE431_00083",""]
[null,null,null,"","ED_FEE431_00084",""]
[null,null,null,"","ED_FEE431_00085",""]
[null,null,null,"","ED_FEE431_00086",""]
[null,null,null,"","ED_FEE431_00087",""]
[null,null,null,"","ED_FEE431_00088",""]
[null,null,null,"","ED_FEE431_00089",""]
[null,null,null,"","ED_FEE431_00090",""]
[null,null,null,"","ED_FEE431_00091",""]
[null,null,null,"","ED_FEE431_00092",""]
[null,null,null,"","ED_FEE431_00093",""]
[null,null,null,"","ED_FEE431_00094",""]
[null,null,null,"","ED_FEE431_00095",""]
[null,null,null,"","ED_FEE431_00096",""]
[null,null,null,"","ED_FEE431_00097",""]
[null,null,null,"","ED_FEE431_00098",""]
[null,null,null,"","ED_FEE431_00099",""]
[null,null,null,"","ED_FEE431_00100",""]
[null,null,null,"","ED_FEE431_00101",""]
[null,null,null,"","ED_FEE431_00102",""]
[null,null,null,"","ED_FEE431_00103",""]
[null,null,null,"","ED_FEE431_00104",""]
[null,null,null,"","ED_FEE431_00105",""]
[null,null,null,"","ED_FEE431_00106",""]
[null,null,null,"","ED_FEE431_00107",""]
[null,null,null,"","ED_FEE431_00108",""]
[null,null,null,"","ED_FEE431_00109",""]
[null,null,null,"","ED_FEE431_00110",""]
[null,null,null,"","ED_FEE431_00111",""]
[null,null,null,"","ED_FEE431_00112",""]
[null,null,null,"","ED_FEE431_00113",""]
[null,null,null,"","ED_FEE431_00114",""]
[null,null,null,"","ED_FEE431_00115",""]
[null,null,null,"","ED_FEE431_00116",""]
[null,null,null,"","ED_FEE431_00117",""]
[null,null,null,"","ED_FEE431_00118",""]
[null,null,null,"","ED_FEE431_00119",""]
[null,null,null,"","ED_FEE431_00120",""]
[null,null,null,"","ED_FEE431_00121",""]
[null,null,null,"","ED_FEE431_00122",""]
[null,null,null,"","ED_FEE431_00123",""]
[null,null,null,"","ED_FEE431_00124",""]
[null,null,null,"","ED_FEE431_00125",""]
[null,null,null,"","ED_FEE431_00126",""]
[null,null,null,"","ED_FEE431_00127",""]
[null,null,null,"","ED_FEE431_00128",""]
[null,null,null,"","ED_FEE431_00129",""]
[null,null,null,"","ED_FEE431_00130",""]
[null,null,null,"","ED_FEE431_00131",""]
[null,null,null,"","ED_FEE431_00132",""]
[null,null,null,"","ED_FEE431_00133",""]
[null,null,null,"","ED_FEE431_00134",""]
[null,null,null,"","ED_FEE431_00135",""]
[null,null,null,"","ED_FEE431_00136",""]
[null,null,null,"","ED_FEE431_00137",""]
[null,null,null,"","ED_FEE431_00138",""]
[null,null,null,"","ED_FEE431_00139",""]
[null,null,null,"","ED_FEE431_00140",""]
[null,null,null,"","ED_FEE431_00141",""]
[null,null,null,"","ED_FEE431_00142",""]
[null,null,null,"","ED_FEE431_00143",""]
[null,null,null,"","ED_FEE431_00144",""]
[null,null,null,"","ED_FEE431_00145",""]
[null,null,null,"","ED_FEE431_00146",""]
[null,null,null,"","ED_FEE431_00147",""]
[null,null,null,"","ED_FEE431_00148",""]
[null,null,null,"","ED_FEE431_00149",""]
[null,null,null,"","ED_FEE431_00150",""]
[null,null,null,"","ED_FEE431_00151",""]
[null,null,null,"","ED_FEE431_00152",""]
[null,null,null,"","ED_FEE431_00153",""]
[null,null,null,"","ED_FEE431_00154",""]
[null,null,null,"","ED_FEE431_00155",""]
[null,null,null,"","ED_FEE431_00156",""]
[null,null,null,"","ED_FEE431_00157",""]
[null,null,null,"","ED_FEE431_00158",""]
[null,null,null,"","ED_FEE431_00159",""]
[null,null,null,"","ED_FEE431_00160",""]
[null,null,null,"","ED_FEE431_00161",""]
[null,null,null,"","ED_FEE431_00162",""]
[null,null,null,"","ED_FEE431_00163",""]
[null,null,null,"","ED_FEE431_00164",""]
[null,null,null,"","ED_FEE431_00165",""]
[null,null,null,"","ED_FEE431_00166",""]
[null,null,null,"","ED_FEE431_00167",""]
[null,null,null,"","ED_FEE431_00168",""]
[null,null,null,"","ED_FEE431_00169",""]
[null,null,null,"","ED_FEE431_00170",""]
[null,null,null,"","ED_FEE431_00171",""]
[null,null,null,"","ED_FEE431_00172",""]
[null,null,null,"","ED_FEE431_00173",""]
[null,null,null,"","ED_FEE431_00174",""]
[null,null,null,"","ED_FEE431_00175",""]
[null,null,null,"","ED_FEE431_00176",""]
[null,null,null,"","ED_FEE431_00177",""]
[null,null,null,"","ED_FEE431_00178",""]
[null,null,null,"","ED_FEE431_00179",""]
[null,null,null,"","ED_FEE431_00180",""]
[null,null,null,"","ED_FEE431_00181",""]
[null,null,null,"","ED_FEE431_00182",""]
[null,null,null,"","ED_FEE431_00183",""]
[null,null,null,"","ED_FEE431_00184",""]
[null,null,null,"","ED_FEE431_00185",""]
[null,null,null,"","ED_FEE431_00186",""]
[null,null,null,"","ED_FEE431_00187",""]
[null,null,null,"","ED_FEE431_00188",""]
[null,null,null,"","ED_FEE431_00189",""]
[null,null,null,"","ED_FEE431_00190",""]
[null,null,null,"","ED_FEE431_00191",""]
[null,null,null,"","ED_FEE431_00192",""]
[null,null,null,"","ED_FEE431_00193",""]
[null,null,null,"","ED_FEE431_00194",""]
[null,null,null,"","ED_FEE431_00195",""]
[null,null,null,"","ED_FEE431_00196",""]
[null,null,null,"","ED_FEE431_00197",""]
[null,null,null,"","ED_FEE431_00198",""]
[null,null,null,"","ED_FEE431_00199",""]
[null,null,null,"","ED_FEE431_00200",""]
[null,null,null,"","ED_FEE431_00201",""]
[null,null,null,"","ED_FEE431_00202",""]
[null,null,null,"","ED_FEE431_00203",""]
[null,null,null,"","ED_FEE431_00204",""]
[null,null,null,"","ED_FEE431_00205",""]
[null,null,null,"","ED_FEE431_00206",""]
[null,null,null,"","ED_FEE431_00207",""]
[null,null,null,"","ED_FEE431_00208",""]
[null,null,null,"","ED_FEE431_00209",""]
[null,null,null,"","ED_FEE431_00210",""]
[null,null,null,"","ED_FEE431_00211",""]
[null,null,null,"","ED_FEE431_00212",""]
[null,null,null,"","ED_FEE431_00213",""]
[null,null,null,"","ED_FEE431_00214",""]
[null,null,null,"","ED_FEE431_00215",""]
[null,null,null,"","ED_FEE431_00216",""]
[null,null,null,"","ED_FEE431_00217",""]
[null,null,null,"","ED_FEE431_00218",""]
[null,null,null,"","ED_FEE431_00219",""]
[null,null,null,"","ED_FEE431_00220",""]
[null,null,null,"","ED_FEE431_00221",""]
[null,null,null,"","ED_FEE431_00222",""]
[null,null,null,"","ED_FEE431_00223",""]
[null,null,null,"","ED_FEE431_00224",""]
[null,null,null,"","ED_FEE431_00225",""]
[null,null,null,"","ED_FEE431_00226",""]
[null,null,null,"","ED_FEE431_00227",""]
[null,null,null,"","ED_FEE431_00228",""]
[null,null,null,"","ED_FEE431_00229",""]
[null,null,null,"","ED_FEE431_00230",""]
[null,null,null,"","ED_FEE431_00231",""]
[null,null,null,"","ED_FEE431_00232",""]
[null,null,null,null,"ED_FEE431_00233"]
[null,null,null,"","ED_FEE431_00234",""]
[null,null,null,"","ED_FEE431_00235",""]
[null,null,null,"","ED_FEE431_00236",""]
[null,null,null,"","ED_FEE431_00237",""]
[null,null,null,"","ED_FEE431_00238",""]
[null,null,null,"","ED_FEE431_00239",""]
[null,null,null,"","ED_FEE431_00240",""]
[null,null,null,"","ED_FEE431_00241",""]
[null,null,null,"","ED_FEE431_00242",""]
[null,null,null,"","ED_FEE431_00243",""]
[null,null,null,"","ED_FEE431_00244",""]
[null,null,null,"","ED_FEE431_00245",""]
[null,null,null,"","ED_FEE431_00246",""]
[null,null,null,"","ED_FEE431_00247",""]
[null,null,null,"","ED_FEE431_00248",""]
[null,null,null,"","ED_FEE431_00249",""]
[null,null,null,"","ED_FEE431_00250",""]
[null,null,null,"","ED_FEE431_00251",""]
[null,null,null,"","ED_FEE431_00252",""]
[null,null,null,"","ED_FEE431_00253",""]
[null,null,null,"","ED_FEE431_00254",""]
[null,null,null,"","ED_FEE431_00255",""]
[null,null,null,"","ED_FEE431_00256",""]
[null,null,null,"","ED_FEE431_00257",""]
[null,null,null,"","ED_FEE431_00258",""]
[null,null,null,"","ED_FEE431_00259",""]
[null,null,null,"","ED_FEE431_00260",""]
[null,null,null,"","ED_FEE431_00261",""]
[null,null,null,"","ED_FEE431_00262",""]
[null,null,null,"","ED_FEE431_00263",""]
[null,null,null,"","ED_FEE431_00264",""]
[null,null,null,"","ED_FEE431_00265",""]
[null,null,null,"","ED_FEE431_00266",""]
[null,null,null,"","ED_FEE431_00267",""]
[null,null,null,"","ED_FEE431_00268",""]
[null,null,null,"","ED_FEE431_00269",""]
[null,null,null,"","ED_FEE431_00270",""]
[null,null,null,"","ED_FEE431_00271",""]
[null,null,null,"","ED_FEE431_00272",""]
[null,null,null,"","ED_FEE431_00273",""]
[null,null,null,"","ED_FEE431_00274",""]
[null,null,null,"","ED_FEE431_00275",""]
[null,null,null,"","ED_FEE431_00276",""]
[null,null,null,"","ED_FEE431_00277",""]
[null,null,null,"","ED_FEE431_00278",""]
[null,null,null,"","ED_FEE431_00279",""]
[null,null,null,"","ED_FEE431_00280",""]
[null,null,null,"","ED_FEE431_00281",""]
[null,null,null,"","ED_FEE431_00282",""]
[null,null,null,"","ED_FEE431_00283",""]
[null,null,null,"","ED_FEE431_00284",""]
[null,null,null,"","ED_FEE431_00285",""]
[null,null,null,"","ED_FEE431_00286",""]
[null,null,null,"","ED_FEE431_00287",""]
[null,null,null,"","ED_FEE431_00288",""]
[null,null,null,"","ED_FEE431_00289",""]
[null,null,null,"","ED_FEE431_00290",""]
[null,null,null,"","ED_FEE431_00291",""]
[null,null,null,"","ED_FEE431_00292",""]
[null,null,null,"","ED_FEE431_00293",""]
[null,null,null,"","ED_FEE431_00294",""]
[null,null,null,"","ED_FEE431_00295",""]
[null,null,null,"","ED_FEE431_00296",""]
[null,null,null,"","ED_FEE431_00297",""]
[null,null,null,"","ED_FEE431_00298",""]
[null,null,null,"","ED_FEE431_00299",""]
[null,null,null,"","ED_FEE431_00300",""]
[null,null,null,"","ED_FEE431_00301",""]
[null,null,null,"","ED_FEE431_00302",""]
[null,null,null,"","ED_FEE431_00303",""]
[null,null,null,"","ED_FEE431_00304",""]
[null,null,null,"","ED_FEE431_00305",""]
[null,null,null,"","ED_FEE431_00306",""]
[null,null,null,"","ED_FEE431_00307",""]
[null,null,null,"","ED_FEE431_00308",""]
[null,null,null,"","ED_FEE431_00309",""]
[null,null,null,"","ED_FEE431_00310",""]
[null,null,null,"","ED_FEE431_00311",""]
[null,null,null,"","ED_FEE431_00312",""]
[null,null,null,"","ED_FEE431_00313",""]
[null,null,null,"","ED_FEE431_00314",""]
[null,null,null,"","ED_FEE431_00315",""]
[null,null,null,"","ED_FEE431_00316",""]
[null,null,null,"","ED_FEE431_00317",""]
[null,null,null,"","ED_FEE431_00318",""]
[null,null,null,"","ED_FEE431_00319",""]
[null,null,null,"","ED_FEE431_00320",""]
[null,null,null,"","ED_FEE431_00321",""]
[null,null,null,"","ED_FEE431_00322",""]
[null,null,null,"","ED_FEE431_00323",""]
[null,null,null,"","ED_FEE431_00324",""]
[null,null,null,"","ED_FEE431_00325",""]
[null,null,null,"","ED_FEE431_00326",""]
[null,null,null,"","ED_FEE431_00327",""]
[null,null,null,"","ED_FEE431_00328",""]
[null,null,null,"","ED_FEE431_00329",""]
[null,null,null,"","ED_FEE431_00330",""]
[null,null,null,"","ED_FEE431_00331",""]
[null,null,null,"","ED_FEE431_00332",""]
[null,null,null,"","ED_FEE431_00333",""]
[null,null,null,"","ED_FEE431_00334",""]
[null,null,null,"","ED_FEE431_00335",""]
[null,null,null,"","ED_FEE431_00336",""]
[null,null,null,"","ED_FEE431_00337",""]
[null,null,null,"","ED_FEE431_00338",""]
[null,null,null,"","ED_FEE431_00339",""]
[null,null,null,"","ED_FEE431_00340",""]
[null,null,null,"","ED_FEE431_00341",""]
[null,null,null,"","ED_FEE431_00342",""]
[null,null,null,"","ED_FEE431_00343",""]
[null,null,null,"","ED_FEE431_00344",""]
[null,null,null,"","ED_FEE431_00345",""]
[null,null,null,"","ED_FEE431_00346",""]
[null,null,null,"","ED_FEE431_00347",""]
[null,null,null,"","ED_FEE431_00348",""]
[null,null,null,"","ED_FEE431_00349",""]
[null,null,null,"","ED_FEE431_00350",""]
[null,null,null,"","ED_FEE431_00351",""]
[null,null,null,"","ED_FEE431_00352",""]
[null,null,null,"","ED_FEE431_00353",""]
[null,null,null,"","ED_FEE431_00354",""]
[null,null,null,"","ED_FEE431_00355",""]
[null,null,null,"","ED_FEE431_00356",""]
[null,null,null,"","ED_FEE431_00357",""]
[null,null,null,"","ED_FEE431_00358",""]
[null,null,null,"","ED_FEE431_00359",""]
[null,null,null,"","ED_FEE431_00360",""]
[null,null,null,"","ED_FEE431_00361",""]
[null,null,null,"","ED_FEE431_00362",""]
[null,null,null,"","ED_FEE431_00363",""]
[null,null,null,"","ED_FEE431_00364",""]
[null,null,null,"","ED_FEE431_00365",""]
[null,null,null,"","ED_FEE431_00366",""]
[null,null,null,"","ED_FEE431_00367",""]
[null,null,null,"","ED_FEE431_00368",""]
[null,null,null,"","ED_FEE431_00369",""]
[null,null,null,"","ED_FEE431_00370",""]
[null,null,null,"","ED_FEE431_00371",""]
[null,null,null,"","ED_FEE431_00372",""]
[null,null,null,"","ED_FEE431_00373",""]
[null,null,null,"","ED_FEE431_00374",""]
[null,null,null,"","ED_FEE431_00375",""]
[null,null,null,"","ED_FEE431_00376",""]
[null,null,null,"","ED_FEE431_00377",""]
[null,null,null,"","ED_FEE431_00378",""]
[null,null,null,"","ED_FEE431_00379",""]
[null,null,null,"","ED_FEE431_00380",""]
[null,null,null,"","ED_FEE431_00381",""]
[null,null,null,"","ED_FEE431_00382",""]
[null,null,null,"","ED_FEE431_00383",""]
[null,null,null,"","ED_FEE431_00384",""]
[null,null,null,"","ED_FEE431_00385",""]
[null,null,null,"","ED_FEE431_00386",""]
[null,null,null,"","ED_FEE431_00387",""]
[null,null,null,"","ED_FEE431_00388",""]
[null,null,null,"","ED_FEE431_00389",""]
[null,null,null,"","ED_FEE431_00390",""]
[null,null,null,"","ED_FEE431_00391",""]
[null,null,null,"","ED_FEE431_00392",""]
[null,null,null,"","ED_FEE431_00393",""]
[null,null,null,"","ED_FEE431_00394",""]
[null,null,null,"","ED_FEE431_00395",""]
[null,null,null,"","ED_FEE431_00396",""]
[null,null,null,"","ED_FEE431_00397",""]
[null,null,null,"","ED_FEE431_00398",""]
[null,null,null,"","ED_FEE431_00399",""]
[null,null,null,"","ED_FEE431_00400",""]
[null,null,null,"","ED_FEE431_00401",""]
[null,null,null,"","ED_FEE431_00402",""]
[null,null,null,"","ED_FEE431_00403",""]
[null,null,null,"","ED_FEE431_00404",""]
[null,null,null,"","ED_FEE431_00405",""]
[null,null,null,"","ED_FEE431_00406",""]
[null,null,null,"","ED_FEE431_00407",""]
[null,null,null,"","ED_FEE431_00408",""]
[null,null,null,"","ED_FEE431_00409",""]
[null,null,null,"","ED_FEE431_00410",""]
[null,null,null,"","ED_FEE431_00411",""]
[null,null,null,"","ED_FEE431_00412",""]
[null,null,null,"","ED_FEE431_00413",""]
[null,null,null,"","ED_FEE431_00414",""]
[null,null,null,"","ED_FEE431_00415",""]
[null,null,null,"","ED_FEE431_00416",""]
[null,null,null,"","ED_FEE431_00417",""]
[null,null,null,"","ED_FEE431_00418",""]
[null,null,null,"","ED_FEE431_00419",""]
[null,null,null,"","ED_FEE431_00420",""]
[null,null,null,"","ED_FEE431_00421",""]
[null,null,null,"","ED_FEE431_00422",""]
[null,null,null,"","ED_FEE431_00423",""]
[null,null,null,"","ED_FEE431_00424",""]
[null,null,null,"","ED_FEE431_00425",""]
[null,null,null,"","ED_FEE431_00426",""]
[null,null,null,"","ED_FEE431_00427",""]
[null,null,null,"","ED_FEE431_00428",""]
[null,null,null,"","ED_FEE431_00429",""]
[null,null,null,"","ED_FEE431_00430",""]
[null,null,null,"","ED_FEE431_00431",""]
[null,null,null,"","ED_FEE431_00432",""]
[null,null,null,"","ED_FEE431_00433",""]
[null,null,null,"","ED_FEE431_00434",""]
[null,null,null,"","ED_FEE431_00435",""]
[null,null,null,"","ED_FEE431_00436",""]
[null,null,null,"","ED_FEE431_00437",""]
[null,null,null,"","ED_FEE431_00438",""]
[null,null,null,"","ED_FEE431_00439",""]
[null,null,null,"","ED_FEE431_00440",""]
[null,null,null,"","ED_FEE431_00441",""]
[null,null,null,"","ED_FEE431_00442",""]
[null,null,null,"","ED_FEE431_00443",""]
[null,null,null,"","ED_FEE431_00444",""]
[null,null,null,"","ED_FEE431_00445",""]
[null,null,null,"","ED_FEE431_00446",""]
[null,null,null,"","ED_FEE431_00447",""]
[null,null,null,"","ED_FEE431_00448",""]
[null,null,null,"","ED_FEE431_00449",""]
[null,null,null,"","ED_FEE431_00450",""]
[null,null,null,"","ED_FEE431_00451",""]
[null,null,null,"","ED_FEE431_00452",""]
[null,null,null,"","ED_FEE431_00453",""]
[null,null,null,"","ED_FEE431_00454",""]
[null,null,null,"","ED_FEE431_00455",""]
[null,null,null,"","ED_FEE431_00456",""]
[null,null,null,"","ED_FEE431_00457",""]
[null,null,null,"","ED_FEE431_00458",""]
[null,null,null,"","ED_FEE431_00459",""]
[null,null,null,"","ED_FEE431_00460",""]
[null,null,null,"","ED_FEE431_00461",""]
[null,null,null,"","ED_FEE431_00462",""]
[null,null,null,"","ED_FEE431_00463",""]
[null,null,null,"","ED_FEE431_00464",""]
[null,null,null,"","ED_FEE431_00465",""]
[null,null,null,"","ED_FEE431_00466",""]
[null,null,null,"","ED_FEE431_00467",""]
[null,null,null,"","ED_FEE431_00468",""]
[null,null,null,"","ED_FEE431_00469",""]
[null,null,null,"","ED_FEE431_00470",""]
[null,null,null,"","ED_FEE431_00471",""]

{"sheet":"4.4 Quoted services","index":19,"n_rows":481,"n_cols":6,"rows_kept":481,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"4.4 ANCILLARY SERVICES - QUOTED SERVICES"]
[]
[null,"4.4.1 - COST METRICS FOR QUOTED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY",{"$f":"CRY","v":"2015-16"},null,{"$f":"CRY","v":"2015-16"}]
[null,"Quoted Services ","Rearrangement of network assets",6755659.1499999994,"ED_QUO441_00001",174]
[null,null,"Customer requested works (work close)",335578.68000000011,"ED_QUO441_00002",267]
[null,null,"Non-standard data and meter services",0,"ED_QUO441_00003",0]
[null,null,"Emergency recoverable works and rectification of illegal connections",0,"ED_QUO441_00004",0]
[null,null,"Large customer connections",4772842.1399999987,"ED_QUO441_00005",178]
[null,null,"Design specification & other sub-division activities",0,"ED_QUO441_00006",0]
[null,null,"Unmetered services, inc Streetlighting",42028.17,"ED_QUO441_00007",53]
[null,null,"After Hours provision of any fee-based service (excluding re-ens)",0,"ED_QUO441_00008",0]
[null,null,"Supply abolishment - complex",0,"ED_QUO441_00009",0]
[null,null,"Additional crew",0,"ED_QUO441_00010",0]
[null,null,"Temp connections - complex",168950.21999999997,"ED_QUO441_00011",11]
[null,null,"Loss of asset",327976.24000000005,"ED_QUO441_00012",145]
[null,null,"Energy Efficient Streetlights",0,"ED_QUO441_00013",0]
[null,null,"Other recoverable works",-7074.0300000000097,"ED_QUO441_00014",2]
[null,null,"Recoverable Streetlighting Construction",1078318.77,"ED_QUO441_00015",26]
[null,null,"Unique glare shields / luminaires",4027.3599999999997,"ED_QUO441_00016",2]
[null,null,"Real Estate development inc design spec & audit",2029193.9399999997,"ED_QUO441_00017",399]
[null,null,"Parallel generator assessment",219651.93999999997,"ED_QUO441_00018",26]
[null,null,null,null,"ED_QUO441_00019"]
[null,null,null,null,"ED_QUO441_00020"]
[null,null,null,null,"ED_QUO441_00021"]
[null,null,null,null,"ED_QUO441_00022"]
[null,null,null,null,"ED_QUO441_00023"]
[null,null,null,null,"ED_QUO441_00024"]
[null,null,null,null,"ED_QUO441_00025"]
[null,null,null,null,"ED_QUO441_00026"]
[null,null,null,null,"ED_QUO441_00027"]
[null,null,null,null,"ED_QUO441_00028"]
[null,null,null,null,"ED_QUO441_00029"]
[null,null,null,null,"ED_QUO441_00030"]
[null,null,null,null,"ED_QUO441_00031"]
[null,null,null,null,"ED_QUO441_00032"]
[null,null,null,null,"ED_QUO441_00033"]
[null,null,null,"","ED_QUO441_00034",""]
[null,null,null,"","ED_QUO441_00035",""]
[null,null,null,"","ED_QUO441_00036",""]
[null,null,null,"","ED_QUO441_00037",""]
[null,null,null,"","ED_QUO441_00038",""]
[null,null,null,"","ED_QUO441_00039",""]
[null,null,null,"","ED_QUO441_00040",""]
[null,null,null,"","ED_QUO441_00041",""]
[null,null,null,"","ED_QUO441_00042",""]
[null,null,null,"","ED_QUO441_00043",""]
[null,null,null,"","ED_QUO441_00044",""]
[null,null,null,"","ED_QUO441_00045",""]
[null,null,null,"","ED_QUO441_00046",""]
[null,null,null,"","ED_QUO441_00047",""]
[null,null,null,"","ED_QUO441_00048",""]
[null,null,null,"","ED_QUO441_00049",""]
[null,null,null,"","ED_QUO441_00050",""]
[null,null,null,"","ED_QUO441_00051",""]
[null,null,null,"","ED_QUO441_00052",""]
[null,null,null,"","ED_QUO441_00053",""]
[null,null,null,"","ED_QUO441_00054",""]
[null,null,null,"","ED_QUO441_00055",""]
[null,null,null,"","ED_QUO441_00056",""]
[null,null,null,"","ED_QUO441_00057",""]
[null,null,null,"","ED_QUO441_00058",""]
[null,null,null,"","ED_QUO441_00059",""]
[null,null,null,"","ED_QUO441_00060",""]
[null,null,null,"","ED_QUO441_00061",""]
[null,null,null,"","ED_QUO441_00062",""]
[null,null,null,"","ED_QUO441_00063",""]
[null,null,null,"","ED_QUO441_00064",""]
[null,null,null,"","ED_QUO441_00065",""]
[null,null,null,"","ED_QUO441_00066",""]
[null,null,null,"","ED_QUO441_00067",""]
[null,null,null,"","ED_QUO441_00068",""]
[null,null,null,"","ED_QUO441_00069",""]
[null,null,null,"","ED_QUO441_00070",""]
[null,null,null,"","ED_QUO441_00071",""]
[null,null,null,"","ED_QUO441_00072",""]
[null,null,null,"","ED_QUO441_00073",""]
[null,null,null,"","ED_QUO441_00074",""]
[null,null,null,"","ED_QUO441_00075",""]
[null,null,null,"","ED_QUO441_00076",""]
[null,null,null,"","ED_QUO441_00077",""]
[null,null,null,"","ED_QUO441_00078",""]
[null,null,null,"","ED_QUO441_00079",""]
[null,null,null,"","ED_QUO441_00080",""]
[null,null,null,"","ED_QUO441_00081",""]
[null,null,null,"","ED_QUO441_00082",""]
[null,null,null,"","ED_QUO441_00083",""]
[null,null,null,"","ED_QUO441_00084",""]
[null,null,null,"","ED_QUO441_00085",""]
[null,null,null,"","ED_QUO441_00086",""]
[null,null,null,"","ED_QUO441_00087",""]
[null,null,null,"","ED_QUO441_00088",""]
[null,null,null,"","ED_QUO441_00089",""]
[null,null,null,"","ED_QUO441_00090",""]
[null,null,null,"","ED_QUO441_00091",""]
[null,null,null,"","ED_QUO441_00092",""]
[null,null,null,"","ED_QUO441_00093",""]
[null,null,null,"","ED_QUO441_00094",""]
[null,null,null,"","ED_QUO441_00095",""]
[null,null,null,"","ED_QUO441_00096",""]
[null,null,null,"","ED_QUO441_00097",""]
[null,null,null,"","ED_QUO441_00098",""]
[null,null,null,"","ED_QUO441_00099",""]
[null,null,null,"","ED_QUO441_00100",""]
[null,null,null,"","ED_QUO441_00101",""]
[null,null,null,"","ED_QUO441_00102",""]
[null,null,null,"","ED_QUO441_00103",""]
[null,null,null,"","ED_QUO441_00104",""]
[null,null,null,"","ED_QUO441_00105",""]
[null,null,null,"","ED_QUO441_00106",""]
[null,null,null,"","ED_QUO441_00107",""]
[null,null,null,"","ED_QUO441_00108",""]
[null,null,null,"","ED_QUO441_00109",""]
[null,null,null,"","ED_QUO441_00110",""]
[null,null,null,"","ED_QUO441_00111",""]
[null,null,null,"","ED_QUO441_00112",""]
[null,null,null,"","ED_QUO441_00113",""]
[null,null,null,"","ED_QUO441_00114",""]
[null,null,null,"","ED_QUO441_00115",""]
[null,null,null,"","ED_QUO441_00116",""]
[null,null,null,"","ED_QUO441_00117",""]
[null,null,null,"","ED_QUO441_00118",""]
[null,null,null,"","ED_QUO441_00119",""]
[null,null,null,"","ED_QUO441_00120",""]
[null,null,null,"","ED_QUO441_00121",""]
[null,null,null,"","ED_QUO441_00122",""]
[null,null,null,"","ED_QUO441_00123",""]
[null,null,null,"","ED_QUO441_00124",""]
[null,null,null,"","ED_QUO441_00125",""]
[null,null,null,"","ED_QUO441_00126",""]
[null,null,null,"","ED_QUO441_00127",""]
[null,null,null,"","ED_QUO441_00128",""]
[null,null,null,"","ED_QUO441_00129",""]
[null,null,null,"","ED_QUO441_00130",""]
[null,null,null,"","ED_QUO441_00131",""]
[null,null,null,"","ED_QUO441_00132",""]
[null,null,null,"","ED_QUO441_00133",""]
[null,null,null,"","ED_QUO441_00134",""]
[null,null,null,"","ED_QUO441_00135",""]
[null,null,null,"","ED_QUO441_00136",""]
[null,null,null,"","ED_QUO441_00137",""]
[null,null,null,"","ED_QUO441_00138",""]
[null,null,null,"","ED_QUO441_00139",""]
[null,null,null,"","ED_QUO441_00140",""]
[null,null,null,"","ED_QUO441_00141",""]
[null,null,null,"","ED_QUO441_00142",""]
[null,null,null,"","ED_QUO441_00143",""]
[null,null,null,"","ED_QUO441_00144",""]
[null,null,null,"","ED_QUO441_00145",""]
[null,null,null,"","ED_QUO441_00146",""]
[null,null,null,"","ED_QUO441_00147",""]
[null,null,null,"","ED_QUO441_00148",""]
[null,null,null,"","ED_QUO441_00149",""]
[null,null,null,"","ED_QUO441_00150",""]
[null,null,null,"","ED_QUO441_00151",""]
[null,null,null,"","ED_QUO441_00152",""]
[null,null,null,"","ED_QUO441_00153",""]
[null,null,null,"","ED_QUO441_00154",""]
[null,null,null,"","ED_QUO441_00155",""]
[null,null,null,"","ED_QUO441_00156",""]
[null,null,null,"","ED_QUO441_00157",""]
[null,null,null,"","ED_QUO441_00158",""]
[null,null,null,"","ED_QUO441_00159",""]
[null,null,null,"","ED_QUO441_00160",""]
[null,null,null,"","ED_QUO441_00161",""]
[null,null,null,"","ED_QUO441_00162",""]
[null,null,null,"","ED_QUO441_00163",""]
[null,null,null,"","ED_QUO441_00164",""]
[null,null,null,"","ED_QUO441_00165",""]
[null,null,null,"","ED_QUO441_00166",""]
[null,null,null,"","ED_QUO441_00167",""]
[null,null,null,"","ED_QUO441_00168",""]
[null,null,null,"","ED_QUO441_00169",""]
[null,null,null,"","ED_QUO441_00170",""]
[null,null,null,"","ED_QUO441_00171",""]
[null,null,null,"","ED_QUO441_00172",""]
[null,null,null,"","ED_QUO441_00173",""]
[null,null,null,"","ED_QUO441_00174",""]
[null,null,null,"","ED_QUO441_00175",""]
[null,null,null,"","ED_QUO441_00176",""]
[null,null,null,"","ED_QUO441_00177",""]
[null,null,null,"","ED_QUO441_00178",""]
[null,null,null,"","ED_QUO441_00179",""]
[null,null,null,"","ED_QUO441_00180",""]
[null,null,null,"","ED_QUO441_00181",""]
[null,null,null,"","ED_QUO441_00182",""]
[null,null,null,"","ED_QUO441_00183",""]
[null,null,null,"","ED_QUO441_00184",""]
[null,null,null,"","ED_QUO441_00185",""]
[null,null,null,"","ED_QUO441_00186",""]
[null,null,null,"","ED_QUO441_00187",""]
[null,null,null,"","ED_QUO441_00188",""]
[null,null,null,"","ED_QUO441_00189",""]
[null,null,null,"","ED_QUO441_00190",""]
[null,null,null,"","ED_QUO441_00191",""]
[null,null,null,"","ED_QUO441_00192",""]
[null,null,null,"","ED_QUO441_00193",""]
[null,null,null,"","ED_QUO441_00194",""]
[null,null,null,"","ED_QUO441_00195",""]
[null,null,null,"","ED_QUO441_00196",""]
[null,null,null,"","ED_QUO441_00197",""]
[null,null,null,"","ED_QUO441_00198",""]
[null,null,null,"","ED_QUO441_00199",""]
[null,null,null,"","ED_QUO441_00200",""]
[null,null,null,"","ED_QUO441_00201",""]
[null,null,null,"","ED_QUO441_00202",""]
[null,null,null,"","ED_QUO441_00203",""]
[null,null,null,"","ED_QUO441_00204",""]
[null,null,null,"","ED_QUO441_00205",""]
[null,null,null,"","ED_QUO441_00206",""]
[null,null,null,"","ED_QUO441_00207",""]
[null,null,null,"","ED_QUO441_00208",""]
[null,null,null,"","ED_QUO441_00209",""]
[null,null,null,"","ED_QUO441_00210",""]
[null,null,null,"","ED_QUO441_00211",""]
[null,null,null,"","ED_QUO441_00212",""]
[null,null,null,"","ED_QUO441_00213",""]
[null,null,null,"","ED_QUO441_00214",""]
[null,null,null,"","ED_QUO441_00215",""]
[null,null,null,"","ED_QUO441_00216",""]
[null,null,null,"","ED_QUO441_00217",""]
[null,null,null,"","ED_QUO441_00218",""]
[null,null,null,"","ED_QUO441_00219",""]
[null,null,null,"","ED_QUO441_00220",""]
[null,null,null,"","ED_QUO441_00221",""]
[null,null,null,"","ED_QUO441_00222",""]
[null,null,null,"","ED_QUO441_00223",""]
[null,null,null,"","ED_QUO441_00224",""]
[null,null,null,"","ED_QUO441_00225",""]
[null,null,null,"","ED_QUO441_00226",""]
[null,null,null,"","ED_QUO441_00227",""]
[null,null,null,"","ED_QUO441_00228",""]
[null,null,null,"","ED_QUO441_00229",""]
[null,null,null,"","ED_QUO441_00230",""]
[null,null,null,"","ED_QUO441_00231",""]
[null,null,null,"","ED_QUO441_00232",""]
[null,null,null,"","ED_QUO441_00233",""]
[null,null,null,"","ED_QUO441_00234",""]
[null,null,null,"","ED_QUO441_00235",""]
[null,null,null,"","ED_QUO441_00236",""]
[null,null,null,"","ED_QUO441_00237",""]
[null,null,null,"","ED_QUO441_00238",""]
[null,null,null,"","ED_QUO441_00239",""]
[null,null,null,"","ED_QUO441_00240",""]
[null,null,null,"","ED_QUO441_00241",""]
[null,null,null,"","ED_QUO441_00242",""]
[null,null,null,"","ED_QUO441_00243",""]
[null,null,null,"","ED_QUO441_00244",""]
[null,null,null,"","ED_QUO441_00245",""]
[null,null,null,"","ED_QUO441_00246",""]
[null,null,null,"","ED_QUO441_00247",""]
[null,null,null,"","ED_QUO441_00248",""]
[null,null,null,"","ED_QUO441_00249",""]
[null,null,null,"","ED_QUO441_00250",""]
[null,null,null,"","ED_QUO441_00251",""]
[null,null,null,"","ED_QUO441_00252",""]
[null,null,null,"","ED_QUO441_00253",""]
[null,null,null,"","ED_QUO441_00254",""]
[null,null,null,"","ED_QUO441_00255",""]
[null,null,null,"","ED_QUO441_00256",""]
[null,null,null,"","ED_QUO441_00257",""]
[null,null,null,"","ED_QUO441_00258",""]
[null,null,null,"","ED_QUO441_00259",""]
[null,null,null,"","ED_QUO441_00260",""]
[null,null,null,"","ED_QUO441_00261",""]
[null,null,null,"","ED_QUO441_00262",""]
[null,null,null,"","ED_QUO441_00263",""]
[null,null,null,"","ED_QUO441_00264",""]
[null,null,null,"","ED_QUO441_00265",""]
[null,null,null,"","ED_QUO441_00266",""]
[null,null,null,"","ED_QUO441_00267",""]
[null,null,null,"","ED_QUO441_00268",""]
[null,null,null,"","ED_QUO441_00269",""]
[null,null,null,"","ED_QUO441_00270",""]
[null,null,null,"","ED_QUO441_00271",""]
[null,null,null,"","ED_QUO441_00272",""]
[null,null,null,"","ED_QUO441_00273",""]
[null,null,null,"","ED_QUO441_00274",""]
[null,null,null,"","ED_QUO441_00275",""]
[null,null,null,"","ED_QUO441_00276",""]
[null,null,null,"","ED_QUO441_00277",""]
[null,null,null,"","ED_QUO441_00278",""]
[null,null,null,"","ED_QUO441_00279",""]
[null,null,null,"","ED_QUO441_00280",""]
[null,null,null,"","ED_QUO441_00281",""]
[null,null,null,"","ED_QUO441_00282",""]
[null,null,null,"","ED_QUO441_00283",""]
[null,null,null,"","ED_QUO441_00284",""]
[null,null,null,"","ED_QUO441_00285",""]
[null,null,null,"","ED_QUO441_00286",""]
[null,null,null,"","ED_QUO441_00287",""]
[null,null,null,"","ED_QUO441_00288",""]
[null,null,null,"","ED_QUO441_00289",""]
[null,null,null,"","ED_QUO441_00290",""]
[null,null,null,"","ED_QUO441_00291",""]
[null,null,null,"","ED_QUO441_00292",""]
[null,null,null,"","ED_QUO441_00293",""]
[null,null,null,"","ED_QUO441_00294",""]
[null,null,null,"","ED_QUO441_00295",""]
[null,null,null,"","ED_QUO441_00296",""]
[null,null,null,"","ED_QUO441_00297",""]
[null,null,null,"","ED_QUO441_00298",""]
[null,null,null,"","ED_QUO441_00299",""]
[null,null,null,"","ED_QUO441_00300",""]
[null,null,null,"","ED_QUO441_00301",""]
[null,null,null,"","ED_QUO441_00302",""]
[null,null,null,"","ED_QUO441_00303",""]
[null,null,null,"","ED_QUO441_00304",""]
[null,null,null,"","ED_QUO441_00305",""]
[null,null,null,"","ED_QUO441_00306",""]
[null,null,null,"","ED_QUO441_00307",""]
[null,null,null,"","ED_QUO441_00308",""]
[null,null,null,"","ED_QUO441_00309",""]
[null,null,null,"","ED_QUO441_00310",""]
[null,null,null,"","ED_QUO441_00311",""]
[null,null,null,"","ED_QUO441_00312",""]
[null,null,null,"","ED_QUO441_00313",""]
[null,null,null,"","ED_QUO441_00314",""]
[null,null,null,"","ED_QUO441_00315",""]
[null,null,null,"","ED_QUO441_00316",""]
[null,null,null,"","ED_QUO441_00317",""]
[null,null,null,"","ED_QUO441_00318",""]
[null,null,null,"","ED_QUO441_00319",""]
[null,null,null,"","ED_QUO441_00320",""]
[null,null,null,"","ED_QUO441_00321",""]
[null,null,null,"","ED_QUO441_00322",""]
[null,null,null,"","ED_QUO441_00323",""]
[null,null,null,"","ED_QUO441_00324",""]
[null,null,null,"","ED_QUO441_00325",""]
[null,null,null,"","ED_QUO441_00326",""]
[null,null,null,"","ED_QUO441_00327",""]
[null,null,null,"","ED_QUO441_00328",""]
[null,null,null,"","ED_QUO441_00329",""]
[null,null,null,"","ED_QUO441_00330",""]
[null,null,null,"","ED_QUO441_00331",""]
[null,null,null,"","ED_QUO441_00332",""]
[null,null,null,"","ED_QUO441_00333",""]
[null,null,null,"","ED_QUO441_00334",""]
[null,null,null,"","ED_QUO441_00335",""]
[null,null,null,"","ED_QUO441_00336",""]
[null,null,null,"","ED_QUO441_00337",""]
[null,null,null,"","ED_QUO441_00338",""]
[null,null,null,"","ED_QUO441_00339",""]
[null,null,null,"","ED_QUO441_00340",""]
[null,null,null,"","ED_QUO441_00341",""]
[null,null,null,"","ED_QUO441_00342",""]
[null,null,null,"","ED_QUO441_00343",""]
[null,null,null,"","ED_QUO441_00344",""]
[null,null,null,"","ED_QUO441_00345",""]
[null,null,null,"","ED_QUO441_00346",""]
[null,null,null,"","ED_QUO441_00347",""]
[null,null,null,"","ED_QUO441_00348",""]
[null,null,null,"","ED_QUO441_00349",""]
[null,null,null,"","ED_QUO441_00350",""]
[null,null,null,"","ED_QUO441_00351",""]
[null,null,null,"","ED_QUO441_00352",""]
[null,null,null,"","ED_QUO441_00353",""]
[null,null,null,"","ED_QUO441_00354",""]
[null,null,null,"","ED_QUO441_00355",""]
[null,null,null,"","ED_QUO441_00356",""]
[null,null,null,"","ED_QUO441_00357",""]
[null,null,null,"","ED_QUO441_00358",""]
[null,null,null,"","ED_QUO441_00359",""]
[null,null,null,"","ED_QUO441_00360",""]
[null,null,null,"","ED_QUO441_00361",""]
[null,null,null,"","ED_QUO441_00362",""]
[null,null,null,"","ED_QUO441_00363",""]
[null,null,null,"","ED_QUO441_00364",""]
[null,null,null,"","ED_QUO441_00365",""]
[null,null,null,"","ED_QUO441_00366",""]
[null,null,null,"","ED_QUO441_00367",""]
[null,null,null,"","ED_QUO441_00368",""]
[null,null,null,"","ED_QUO441_00369",""]
[null,null,null,"","ED_QUO441_00370",""]
[null,null,null,"","ED_QUO441_00371",""]
[null,null,null,"","ED_QUO441_00372",""]
[null,null,null,"","ED_QUO441_00373",""]
[null,null,null,"","ED_QUO441_00374",""]
[null,null,null,"","ED_QUO441_00375",""]
[null,null,null,"","ED_QUO441_00376",""]
[null,null,null,"","ED_QUO441_00377",""]
[null,null,null,"","ED_QUO441_00378",""]
[null,null,null,"","ED_QUO441_00379",""]
[null,null,null,"","ED_QUO441_00380",""]
[null,null,null,"","ED_QUO441_00381",""]
[null,null,null,"","ED_QUO441_00382",""]
[null,null,null,"","ED_QUO441_00383",""]
[null,null,null,"","ED_QUO441_00384",""]
[null,null,null,"","ED_QUO441_00385",""]
[null,null,null,"","ED_QUO441_00386",""]
[null,null,null,"","ED_QUO441_00387",""]
[null,null,null,"","ED_QUO441_00388",""]
[null,null,null,"","ED_QUO441_00389",""]
[null,null,null,"","ED_QUO441_00390",""]
[null,null,null,"","ED_QUO441_00391",""]
[null,null,null,"","ED_QUO441_00392",""]
[null,null,null,"","ED_QUO441_00393",""]
[null,null,null,"","ED_QUO441_00394",""]
[null,null,null,"","ED_QUO441_00395",""]
[null,null,null,"","ED_QUO441_00396",""]
[null,null,null,"","ED_QUO441_00397",""]
[null,null,null,"","ED_QUO441_00398",""]
[null,null,null,"","ED_QUO441_00399",""]
[null,null,null,"","ED_QUO441_00400",""]
[null,null,null,"","ED_QUO441_00401",""]
[null,null,null,"","ED_QUO441_00402",""]
[null,null,null,"","ED_QUO441_00403",""]
[null,null,null,"","ED_QUO441_00404",""]
[null,null,null,"","ED_QUO441_00405",""]
[null,null,null,"","ED_QUO441_00406",""]
[null,null,null,"","ED_QUO441_00407",""]
[null,null,null,"","ED_QUO441_00408",""]
[null,null,null,"","ED_QUO441_00409",""]
[null,null,null,"","ED_QUO441_00410",""]
[null,null,null,"","ED_QUO441_00411",""]
[null,null,null,"","ED_QUO441_00412",""]
[null,null,null,"","ED_QUO441_00413",""]
[null,null,null,"","ED_QUO441_00414",""]
[null,null,null,"","ED_QUO441_00415",""]
[null,null,null,"","ED_QUO441_00416",""]
[null,null,null,"","ED_QUO441_00417",""]
[null,null,null,"","ED_QUO441_00418",""]
[null,null,null,"","ED_QUO441_00419",""]
[null,null,null,"","ED_QUO441_00420",""]
[null,null,null,"","ED_QUO441_00421",""]
[null,null,null,"","ED_QUO441_00422",""]
[null,null,null,"","ED_QUO441_00423",""]
[null,null,null,"","ED_QUO441_00424",""]
[null,null,null,"","ED_QUO441_00425",""]
[null,null,null,"","ED_QUO441_00426",""]
[null,null,null,"","ED_QUO441_00427",""]
[null,null,null,"","ED_QUO441_00428",""]
[null,null,null,"","ED_QUO441_00429",""]
[null,null,null,"","ED_QUO441_00430",""]
[null,null,null,"","ED_QUO441_00431",""]
[null,null,null,"","ED_QUO441_00432",""]
[null,null,null,"","ED_QUO441_00433",""]
[null,null,null,"","ED_QUO441_00434",""]
[null,null,null,"","ED_QUO441_00435",""]
[null,null,null,"","ED_QUO441_00436",""]
[null,null,null,"","ED_QUO441_00437",""]
[null,null,null,"","ED_QUO441_00438",""]
[null,null,null,"","ED_QUO441_00439",""]
[null,null,null,"","ED_QUO441_00440",""]
[null,null,null,"","ED_QUO441_00441",""]
[null,null,null,"","ED_QUO441_00442",""]
[null,null,null,"","ED_QUO441_00443",""]
[null,null,null,"","ED_QUO441_00444",""]
[null,null,null,"","ED_QUO441_00445",""]
[null,null,null,"","ED_QUO441_00446",""]
[null,null,null,"","ED_QUO441_00447",""]
[null,null,null,"","ED_QUO441_00448",""]
[null,null,null,"","ED_QUO441_00449",""]
[null,null,null,"","ED_QUO441_00450",""]
[null,null,null,"","ED_QUO441_00451",""]
[null,null,null,"","ED_QUO441_00452",""]
[null,null,null,"","ED_QUO441_00453",""]
[null,null,null,"","ED_QUO441_00454",""]
[null,null,null,"","ED_QUO441_00455",""]
[null,null,null,"","ED_QUO441_00456",""]
[null,null,null,"","ED_QUO441_00457",""]
[null,null,null,"","ED_QUO441_00458",""]
[null,null,null,"","ED_QUO441_00459",""]
[null,null,null,"","ED_QUO441_00460",""]
[null,null,null,"","ED_QUO441_00461",""]
[null,null,null,"","ED_QUO441_00462",""]
[null,null,null,"","ED_QUO441_00463",""]
[null,null,null,"","ED_QUO441_00464",""]
[null,null,null,"","ED_QUO441_00465",""]
[null,null,null,"","ED_QUO441_00466",""]
[null,null,null,"","ED_QUO441_00467",""]
[null,null,null,"","ED_QUO441_00468",""]
[null,null,null,"","ED_QUO441_00469",""]
[null,null,null,"","ED_QUO441_00470",""]
[null,null,null,"","ED_QUO441_00471",""]
[null,null,null,"","ED_QUO441_00472",""]
[null,null,null,"","ED_QUO441_00473",""]

{"sheet":"5.2 Asset Age Profile","index":20,"n_rows":129,"n_cols":112,"rows_kept":129,"cut":false,"hidden":false,"merged":[[8,3,8,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"5.2 ASSET AGE PROFILE"]
[]
[null,"There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.2.1 - ASSET AGE PROFILE"]
[null,null,null,"ECONOMIC LIFE (YEARS)",null,"INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR"]
[null,"ASSET GROUP","ASSET CATEGORY","MEAN ","STANDARD DEVIATION ",{"$f":"CRY","v":"2015-16"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(F10,4)-1)&\"-\"&MID(F10,3,2)),VALUE(LEFT(F10,4)-1))","v":"2014-15"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(G10,4)-1)&\"-\"&MID(G10,3,2)),VALUE(LEFT(G10,4)-1))","v":"2013-14"},"2012-13","2011-12","2010-11","2009-10","2008-09","2007-08","2006-07","2005-06","2004-05","2003-04","2002-03","2001-02","2000-01","1999-00","1998-99","1997-98","1996-97","1995-96","1994-95","1993-94","1992-93","1991-92","1990-91","1989-90","1988-89","1987-88","1986-87","1985-86","1984-85","1983-84",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(AL10,4)-1)&\"-\"&MID(AL10,3,2)),VALUE(LEFT(AL10,4)-1))","v":"1982-83"},"1981-82","1980-81","1979-80","1978-79","1977-78","1976-77","1975-76","1974-75","1973-74","1972-73","1971-72","1970-71","1969-70","1968-69","1967-68","1966-67","1965-66","1964-65","1963-64","1962-63","1961-62","1960-61","1959-60","1958-59","1957-58","1956-57","1955-56","1954-55","1953-54","1952-53","1951-52",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(BR10,4)-1)&\"-\"&MID(BR10,3,2)),VALUE(LEFT(BR10,4)-1))","v":"1950-51"},"1949-50","1948-49","1947-48","1946-47","1945-46","1944-45","1943-44","1942-43","1941-42","1940-41","1939-40","1938-39","1937-38","1936-37","1935-36","1934-35","1933-34","1932-33","1931-32","1930-31","1929-30","1928-29","1927-28","1926-27","1925-26","1924-25","1923-24","1922-23","1921-22","1920-21","1919-20",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(CX10,4)-1)&\"-\"&MID(CX10,3,2)),VALUE(LEFT(CX10,4)-1))","v":"1918-19"},"1917-18","1916-17",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DA10,4)-1)&\"-\"&MID(DA10,3,2)),VALUE(LEFT(DA10,4)-1))","v":"1915-16"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DB10,4)-1)&\"-\"&MID(DB10,3,2)),VALUE(LEFT(DB10,4)-1))","v":"1914-15"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DC10,4)-1)&\"-\"&MID(DC10,3,2)),VALUE(LEFT(DC10,4)-1))","v":"1913-14"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DD10,4)-1)&\"-\"&MID(DD10,3,2)),VALUE(LEFT(DD10,4)-1))","v":"1912-13"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DE10,4)-1)&\"-\"&MID(DE10,3,2)),VALUE(LEFT(DE10,4)-1))","v":"1911-12"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DF10,4)-1)&\"-\"&MID(DF10,3,2)),VALUE(LEFT(DF10,4)-1))","v":"1910-11"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DG10,4)-1)&\"-\"&MID(DG10,3,2)),VALUE(LEFT(DG10,4)-1))","v":"1909-10"}]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole",13,3.6055512754639891,1647,1371,2158,2134,1966,1095,1793,4437,4804,3869,4198,4722,2238,258,1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"˂ = 1 kV; Wood",48.6,6.9713700231733506,2471,3137,3294,3276,3445,2730,3010,3233,2666,2303,2560,1714,1645,1715,1969,1816,2377,2206,2485,2952,3042,3801,3949,4598,4197,4571,4979,4938,3834,3988,5090,4744,5242,4818,3770,3579,3372,3346,3736,3719,3605,2994,3132,3361,2934,2754,2726,2164,2058,1898,1780,1462,1156,826,665,637,500,498,370,311,310,318,339,300,284,199,199,233,181,165,125,55,17,34,76,84,116,133,82,106,114,137,52,28,37,11,15,7,7,6,9,3,2]
[null,null,"> 1 kV & < = 11 kV; Wood",47.1,6.8629439747093963,3030,5274,5434,5284,5785,4764,4973,4552,3688,3692,2888,2559,1878,1525,2470,2388,2633,2411,2700,3012,3189,3810,3636,4052,4332,4862,5269,4933,4340,4475,5850,4720,5755,5591,4584,4323,3969,3760,3907,3372,3276,3194,2953,2842,2694,2618,2550,2074,1927,1770,1644,1654,1234,846,631,737,605,611,493,578,429,426,613,455,302,249,166,199,206,180,194,35,38,37,68,72,204,164,80,151,64,66,161,43,98,10,7,3,5,"              -  ",4,2,"              -  "]
[null,null,"˃ 11 kV & < = 22 kV; Wood",47.1,6.8629439747093963,"              -  ","              -  ",2,"              -  ",3,"              -  ","              -  ",4,"              -  ",8,9,"              -  ",7,"              -  ","              -  ",8,2,"              -  ","              -  ",1,2,"              -  ","              -  ",95,18,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 22 kV & < = 66 kV; Wood",48.02,6.9296464556281663,238,564,640,1427,1351,948,862,574,655,480,564,260,364,364,365,579,329,313,310,343,344,287,271,194,255,281,307,241,463,324,406,299,345,286,260,227,451,457,738,716,575,606,482,270,367,332,418,342,145,377,235,315,109,57,50,66,107,71,134,109,32,17,51,23,33,49,31,41,16,25,67,"              -  ","              -  ",15,29,56,55,20,24,41,23,5,1,"              -  ",10,1,"              -  ",15,1,"              -  ","              -  ","              -  ","              -  "]
[null,null,"> 66 kV & < = 132 kV; Wood",55,7.416198487095663,27,22,76,21,17,67,52,11,19,244,207,29,8,9,107,328,315,40,48,7,15,"              -  ","              -  ",12,8,31,1,3,5,17,15,"              -  ",15,5,2,"              -  ",51,44,"              -  ",2,1,"              -  ","              -  ","              -  ",2,"              -  ","              -  ",1,"              -  ",1,33,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 132 kV; Wood"]
[null,null,"˂ = 1 kV; Concrete",55,7.416198487095663,26,4,2,7,2,2,"              -  ",7,80,19,21,11,9,19,53,24,36,36,60,80,112,377,180,57,6,18,62,30,21,72,71,46,43,49,26,41,82,87,85,30,34,43,76,159,53,38,38,22,11,26,10,7,8,3,33,2,21,2,5,"              -  ","              -  ","              -  ","              -  ",2,1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ",1,"              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 1 kV & < = 11 kV; Concrete",55,7.416198487095663,97,133,161,210,215,186,217,240,325,329,342,402,101,61,42,43,87,52,44,42,56,80,95,106,70,58,53,54,61,292,351,191,44,27,27,34,21,13,20,24,17,23,39,52,53,94,104,64,60,67,38,44,24,1,1,1,1,"              -  ","              -  ",1,"              -  ",2,"              -  ",1,"              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",2,"              -  ",1,"              -  ","              -  ",1,"              -  ",1,"              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"˃ 11 kV & < = 22 kV; Concrete"]
[null,null,"> 22 kV & < = 66 kV; Concrete",55,7.416198487095663,8,23,38,7,13,10,27,2,4,6,22,"              -  ",1,10,"              -  ",67,22,53,"              -  ",6,4,34,23,4,3,2,18,94,22,20,37,"              -  ","              -  ",2,"              -  ",149,"              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 66 kV & < = 132 kV; Concrete",55,7.416198487095663,1,22,114,7,43,27,33,5,77,105,32,31,2,1,98,213,37,85,5,"              -  ","              -  ",1,"              -  ",8,80,2,1,2,"              -  ",104,1,24,2,182,39,"              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 132 kV; Concrete"]
[null,null,"˂ = 1 kV; Steel",78.38,8.853247991556545,"              -  ","              -  ",205,12,54,7,"              -  ",5,1,8,1,"              -  ",1,5,6,16,"              -  ",550,"              -  ","              -  ","              -  ","              -  ","              -  ",9,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 1 kV & < = 11 kV; Steel",78.322000000000003,8.8499717513673453,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",2,1,"              -  ","              -  ","              -  ",1,1,2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"˃ 11 kV & < = 22 kV; Steel"]
[null,null,"> 22 kV & < = 66 kV; Steel",77.575999999999993,8.8077238830471973,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 66 kV & < = 132 kV; Steel",80,8.9442719099991592,"              -  ","              -  ","              -  ","              -  ","              -  ",1,1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"> 132 kV; Steel"]
[null,null,"Other"]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",60,7.7460000000000004,19,39,38,59,84,55,64,63,54,59,62,52,46,32,41,50,66,60,75,94,109,166,186,219,240,256,299,284,243,288,379,363,423,480,369,367,400,496,554,552,582,533,504,533,485,501,487,180,203,190,198,197,161,118,110,110,91,94,78,80,66,74,68,84,70,63,55,62,52,42,36,13,6,8,17,22,26,26,19,34,44,33,34,18,19,8,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",60,7.7460000000000004,43,56,62,102,141,114,116,112,107,131,114,121,81,73,87,133,110,139,160,199,210,251,263,260,321,407,421,402,404,432,514,466,532,611,579,563,538,585,638,585,589,557,549,505,468,489,498,120,137,164,150,171,134,103,89,108,84,97,96,143,89,86,127,110,75,72,45,44,67,54,49,11,7,12,17,32,65,47,22,28,23,14,35,9,29,3,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",60,7.7460000000000004,0,0,0,0,0,0,0,0,0,2,0,0,1,0,0,1,0,0,0,0,0,0,0,13,23,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase"]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase"]
[null,null,"> 22 kV & < = 66 kV",60,7.7460000000000004,0,0,0,1,3,41,42,3,23,16,1,7,6,18,20,10,4,22,3,32,24,4,4,0,2,25,73,9,5,3,13,61,59,56,7,12,68,21,46,79,102,80,76,69,46,112,180,13,15,20,24,33,4,6,2,2,16,11,12,34,10,9,15,9,55,40,11,7,32,0,3,0,0,5,16,61,43,27,8,13,47,17,0,0,27,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",60,7.7460000000000004,0,0,0,0,0,20,0,0,9,0,0,0,0,0,8,10,26,217,2,0,0,0,42,40,0,6,5,0,15,8,19,14,0,45,8,0,8,252,0,0,0,0,0,0,186,0,0,0,0,0,5,177,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV"]
[null,null,"Other"]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",55,7.4160000000000004,239,298,196,176,241,280,271,387,466,487,446,553,473,314,235,247,258,270,282,294,305,317,329,341,352,364,375,384,398,406,418,430,0,0,0,0,0,10,218,0,50,0,30,139,1,12,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",55,7.4160000000000004,25,83,85,95,117,151,201,225,287,332,401,304,203,140,500,239,89,94,131,114,114,118,131,133,133,143,145,153,168,162,162,8,7,5,2,4,3,11,82,141,34,17,6,14,11,9,3,3,0,7,0,2,1,1,1,0,1,0,0,3,0,3,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV"]
[null,null,"> 22 kV & < = 33 kV",65.519000000000005,8.0943807669271415,0,1,16,3,13,32,8,31,21,40,66,39,11,38,64,49,58,1,12,0,16,0,15,0,2,8,3,1,17,21,13,17,0,0,0,0,0,0,223,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV"]
[null,null,"> 66 kV & < = 132 kV",57.512,7.5836666593409809,0,0,0,0,6,1,8,0,9,34,18,2,0,3,25,5,31,7,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,">  132 kV"]
[null,null,"Other"]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",35,5.9160000000000004,20896.433999999786,21379.864000000001,16959.280000000002,13281.859382352941,20132.179382352944,19227.819382352944,21318.059382352945,27044.139382352943,34786.116120040686,31044.693025384731,4013.8083823529405,3634.2153823529407,22370.435617421052,23279.475281759158,18161.490859824131,17914.415749799678,21091.095735828319,19467.459298524791,15655.443315290422,2435.9883196564692,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,6682.1427619047618,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,7695.0070043290025,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,856.43587878787878,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",35,5.9160000000000004,1866.5659999999807,1909.136,1474.72,1154.9442941176469,1750.6242941176472,1671.9842941176473,1853.7442941176473,2351.6642941176474,3024.8796626122339,2699.5385239464981,344.49529411764695,310.58829411764697,1944.3563580366133,2024.3021984138397,1579.2600747673155,1557.7752825912764,1834.0083248546364,1692.822547697808,1361.3428969817758,211.82507127447559,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,577.52628571428568,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,665.60143722943712,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,74.23533333333333,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Residential ; Complex Type"]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type"]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type"]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  "]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  "]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  "]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  "]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  "]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  "]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  "]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  "]
[null,null,"> 132 kV ; Commercial & Industrial  "]
[null,null,"> 132 kV ; Subdivision  "]
[null,null,"Other"]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",37.299999999999997,6.1073725938409877,6,127,161,161,163,150,191,241,203,151,61,30,71,78,61,15,63,15,3,10,64,138,222,145,158,173,159,304,4,3,402,156,120,191,247,146,264,116,244,165,67,20,39,27,34,29,14,18,18,"              -  ",20,39,20,9,6,5,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",6,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",40,6.324555320336759,"              -  ","              -  ","              -  ","              -  ",3,1,3,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase"]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",37.299999999999997,6.1073725938409877,4,130,239,235,154,191,223,222,227,147,50,40,88,65,55,11,8,5,7,7,27,153,193,133,157,178,80,327,1,4,361,229,144,159,222,200,123,102,92,47,58,"              -  ",55,48,73,115,78,62,27,28,69,85,55,47,47,"              -  ",47,44,4,20,2,5,"              -  ","              -  ",15,"              -  ",7,5,19,6,2,2,8,1,"              -  ",4,4,5,"              -  ",8,1,3,2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",40,6.324555320336759,79,900,1061,893,990,1191,1266,1567,1646,1324,783,478,1136,606,395,291,181,182,146,115,246,594,597,232,294,385,185,582,33,22,433,306,445,316,294,348,175,144,98,35,102,19,151,64,58,103,61,26,15,47,41,24,22,19,9,10,12,4,5,"              -  ","              -  ",4,1,"              -  ",2,"              -  ",17,11,9,1,2,1,2,4,2,"              -  ",1,1,"              -  ","              -  ",2,"              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase"]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",40.5,6.3639610306789276,29,374,355,215,200,439,598,722,806,660,569,184,452,305,50,151,128,96,203,104,160,134,145,78,99,116,177,18,388,7,202,1,7,208,117,71,133,57,2,11,36,25,10,2,13,15,12,7,1,1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",39.5,6.2849025449882676,19,182,119,115,91,182,211,285,284,287,274,59,102,77,30,26,32,7,44,27,22,31,12,10,4,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",45,6.7082039324993694,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",43.7,6.6105975524153644,"              -  ",6,4,16,9,10,10,10,8,4,24,8,8,3,2,"              -  ",6,2,1,"              -  ",2,"              -  ",12,7,"              -  ","              -  ",5,3,"              -  ",34,27,3,9,58,4,40,19,14,9,1,1,"              -  ",7,2,1,21,7,24,"              -  ",20,34,15,12,14,9,2,7,3,2,2,"              -  ",5,1,1,13,8,1,12,10,7,1,2,1,"              -  ",1,"              -  ",3,"              -  ",3,"              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",41.7,6.4575537163851759,1,42,76,64,64,129,108,151,280,237,169,32,116,78,62,16,23,11,18,12,55,67,66,43,14,29,10,77,31,195,122,115,46,121,36,96,58,60,24,8,11,28,10,"              -  ",14,16,6,10,2,5,14,10,7,1,1,6,"              -  ",2,1,"              -  ",4,1,"              -  ","              -  ","              -  ",4,2,"              -  ",1,"              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",51.8,7.197221686178632,"              -  ","              -  ","              -  ",1,"              -  ",5,14,10,2,2,1,8,12,6,15,10,7,5,1,1,2,5,"              -  ",1,"              -  ","              -  ",5,1,3,"              -  ",2,"              -  ",1,3,2,6,"              -  ",1,"              -  ",2,15,"              -  ",1,9,1,7,6,1,2,12,7,7,7,2,7,"              -  ",3,"              -  ",1,3,"              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ",6,"              -  ",5,"              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",53.6,7.3212020870892509,"              -  ","              -  ",1,5,10,20,21,23,17,11,20,38,26,2,5,1,1,7,"              -  ",2,"              -  ",5,2,"              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ",1,5,2,"              -  ","              -  ","              -  ","              -  ",1,8,"              -  ","              -  ",5,"              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",53.6,7.3212020870892509,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",53.7,7.3280283842245044,"              -  ","              -  ","              -  ","              -  ",1,15,9,7,6,7,18,15,7,1,9,4,1,6,2,"              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ",3,"              -  ",1,"              -  ",3,"              -  ",7,3,"              -  ",8,"              -  ","              -  ",2,2,2,2,"              -  ","              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",53.8,7.334848328356899,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,1,2,"              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ",1,1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA"]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA"]
[null,null,"Other"]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  Fuse"]
[null,null,"˂ = 11 kV  ; Switch",40,6.3250000000000002,8132,17429,13605,13867,11231,11169,9565,9899,10102,9622,8720,9105,5145,2939,4137,3999,3907,3817,2865,2326,1993,2795,3042,3334,3281,4223,4717,6085,3383,3718,4230,2906,2091,1260,877,611,723,418,205,303,174,205,126,133,246,185,499,125,158,109,202,18,5,10,4,1,0,0,0,2,0,1,0,0,1,0,1,0,0,1]
[null,null,"˂ = 11 kV ;  Circuit Breaker",50.3,7.0922492905988577,43,76,187,255,395,233,188,419,269,399,352,379,211,68,132,93,155,74,27,45,47,43,34,33,35,30,48,68,73,34,86,96,175,90,63,43,26,17,61,25,40,59,22,33,18,52,35,47,18,25,17,12,10,0,6,3,0,0,0,0,1,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Switch",40,6.3250000000000002,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker",50.3,7.0922492905988577,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Switch",40,6.3250000000000002,40,164,138,119,177,300,117,173,173,98,95,98,27,31,57,61,412,18,1,2,10,9,22,0,14,1,27,16,17,1,4,0,2,0,0,1,3,0,315,0,0,0,0,0,0,0,0,0,0,0,3,0,0,0,0,0,0,0,1,5,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",54.18,7.3607064878311785,3,44,22,25,48,27,91,115,176,53,129,176,52,27,46,54,69,38,4,11,5,18,9,16,9,2,1,35,3,10,6,12,1,11,1,0,3,3,8,27,7,15,9,26,3,29,2,20,7,18,21,6,12,15,9,2,4,14,14,1,0,0,16,0,8,1,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Switch",40,6.3250000000000002,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",54.18,7.3607064878311785,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Switch",40,6.3250000000000002,19,109,121,162,64,172,122,67,54,89,25,45,6,80,103,86,287,8,22,4,0,2,0,0,0,0,4,7,14,0,6,3,13,0,0,0,2,0,52,0,0,0,0,0,0,0,0,2,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",49.93,7.0661163307718056,2,1,22,22,12,23,47,25,39,30,27,24,2,26,4,14,16,8,2,0,0,0,0,0,0,0,6,1,1,6,0,3,1,0,5,1,0,0,1,0,0,4,0,0,0,0,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Switch"]
[null,null,"> 132 kV ; Circuit Breaker"]
[null,null,"Other"]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",20,4.4721000000000002,6173,6533,6085,7173,6250,6265,5216,4875,4385,3810,4024,3758,3407,3499,2122,2801,3454,2562,2495,3705]
[null,null,"Luminaires ;  Minor Road",20,4.4721000000000002,20472,24480,26914,17716,11692,13106,11824,12604,10825,11103,9963,8440,7117,5665,5331,5550,5940,4938,4899,7007]
[null,null,"Brackets ; Major Road",44.927,6.7027606252946255,2191,2744,2648,4264,4454,4101,3659,3943,3681,3331,3697,3607,3322,3417,2067,2760,3384,2484,2426,3671,3879,3717,3408,2880,1773,2149,1530,919,695,478,323,147,75,73,51,40,62,78,68,28,96,71,14,7,19,11,15,1,3,1,3,0,1,7,1,0,0,0,0,0,1,0,0,0,1,0,0,0,0,0,0,0,0,0,0,1]
[null,null,"Brackets ; Minor Road",44.966000000000001,6.7056692432597655,10428,14913,19328,9995,5866,6557,6728,8492,7412,7284,6910,7398,6482,5269,4927,4974,5701,4729,4777,6807,9966,9515,7430,7669,5772,6494,5009,4044,3392,3769,3037,1019,621,379,397,572,237,203,120,193,55,35,80,49,54,38,48,51,17,22,16,19,6,5,3,4,0,6,2,1,2,1,2,0,0,2,4,0,0,0,0,0,0,0,0,0]
[null,null,"Lamps ; Major Road",7.8170358049549158,2.7958962435961237,23730,22455,19699,22260,479]
[null,null,"Lamps ; Minor Road",7.3258307230277389,2.7066271858214495,50353,52728,53511,41836,27216]
[null,null,"Poles / Columns ; Major Road",44.927,6.7027606252946255,1270,1577,1270,2006,2193,2063,2024,2035,2261,2021,1668,1972,1501,1523,1029,1283,1591,1214,939,1085,829,871,1050,914,738,1028,818,507,703,468,275,87,94,138,75,107,112,32,20,64,39,8,25,17,40,31,2]
[null,null,"Poles / Columns ; Minor Road",44.966000000000001,6.7056692432597655,4435,4198,2879,2622,3205,4025,3807,5132,6155,5970,4971,6008,5446,3926,4239,3684,3963,3525,3216,3001,3120,5046,4144,4318,2993,2467,2369,1892,1265,1610,1355,482,489,271,355,356,155,145,119,113,22,27,1,0,2,2,2]
[null,null,"Other"]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",26.543133776792313,5.152002889827636,1485,3228,2598,2054,1975,1431,1420,1569,1044,1152,1065,816,466,387,510,350,446,96,140,140,125,83,119,165,125,248,162,224,278,293,483,280,196,98,62,90,48,169,106,120,142,85,112,134,154,53,82,123,120,15,123,27,18,15,0,3,0,0,4,0,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Local Network Wiring Assets",47.466666666666669,6.8896056974740336,2253,4885,3875,3974,3283,3309,2814,2980,3042,2884,2619,2715,1534,892,1267,1170,3921,1488,651,532,472,655,708,760,739,944,1064,1393,781,892,997,700,529,355,223,187,189,118,185,103,68,86,49,56,77,86,153,63,51,52,81,19,14,11,10,4,4,5,5,4,1,2,5,0,6,4,1,5,3,4,0,1,1,0,0,0,1,0,1,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Network Assets",11.777402517654282,3.4318220404989361,403,417,524,728,365,197,286,56,37,38,29,19,16,29,10,13,28,7,5,6,11,24,6,0,0,0,0,0,0,0,0]
[null,null,"Master Station Assets",5,2.2360679774997898,13,0,6,8,60,12,0,0,0,0,0]
[null,null,"Communications Site Infrastructure",21.451530612244898,4.6315797102333125,6,16,17,21,22,22,21,25,15,14,13,12,11,11,15,13,11,10,11,10,11,11,11,11,11,13,11,2,0,0,0,0,4,5,5,3,1,3,0,0,0,0]
[null,null,"Communications Linear Assets",34.731686468716227,5.8933595231172031,85922.4959684028,91402.792548638172,108377.70364631244,188070.46680158796,103294.3784514135,133282.26301770902,386223.41411320335,217681.44814010544,127364.54419099232,183512.25261551264,123091.89799698369,87718.376696245279,78948.045714663196,144718.02557477166,48377.402171138732,64658.995217509684,143778.46998481979,28237.260136136676,24747.496773028797,35447.712719622177,55130.56053946037,116636.74491550146,36409.195584360874,17194.303617569887,5110.7015566062119,13396.452319128308,27540.887882270035,253314.55848166812,22398.115121563664,25058.203157203949,14804.481634622449,15228.737634577916,16056.293149499679,34402.056449762422,5749.0219736965018,9621.3612300481327,31936.711953933962,75957.0259688316,18684.06277577089,28601.306727517276,27684.691023235271,7159.1203991325883,13664.402056610294,11015.941330919624,37626.764294285007,21842.559102151205,1934.6177957193556,53845.482574227433,32829.532893883588,63966.533855255482,23968.569567500552,34736.217705386676,14605.847080195648,12134.295254541348,1138.0104680702091,6677.0177826592089,3687.1539165474778,398.30366382457322,3879.5811411484406,3672.6701469538571,0,2414.6513022507893,3258.84815856469,0,0,3414.0314042106274,2482.9319303350017,0,0,0]
[null,null,"AFLC",24.1,4.9091750834534311,16,15,15,11,11,9,10,15,12,18,22,17,3,2,3,6,1,3,10,2,1,4,1,3,7,7,2,1,0,2,3,5,0,10,4,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other"]
[null,"OTHER BY: \nDNSP DEFINED","Transformer Pole Mounted ; > 22kV ;  < = 60 kVA  ; Multiple Phase",45,6.7082039324993694,"              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ",10,"              -  ",15,"              -  ","              -  ",6,1,9,"              -  ","              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Transformer Pole Mounted ; > 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",39.9,6.3166446789415023,"              -  ","              -  ","              -  ","              -  ",1,1,"              -  ","              -  ",4,1,"              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ",6,1,"              -  ",9,"              -  ","              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ",2,"              -  ",2,"              -  ","              -  ",1,1,"              -  ",1,"              -  ","              -  ",2,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ",1,"              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  ","              -  "]
[null,null,"Regulator Distribution; < = 11 kV",34.82,5.9008473967727717,8,1,9,11,31,16,15,26,19,26,16,11,5,1,3,5,8,5,2,2,1,1,1,0,1,0,0,2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Regulator Substation; < = 11 kV",35,5.9160797830996161,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Regulator Substation; > = 33 kV",34.58,5.8804761711956628,0,0,0,0,0,0,1,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,2,1]
[null,null,"Towers",80,8.9440000000000008,0,0,134,48,0,0,0,0,0,0,4,0,0,0,0,0,3,0,0,0,0,0,0,0,1,0,30,23,0,0,12,1,31,9,4,2,0,0,60,70,589,0,0,15,0,15,29,0,31,42]

{"sheet":"5.3 MD - Network level","index":21,"n_rows":15,"n_cols":4,"rows_kept":15,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"5.3 MAXIMUM DEMAND AT NETWORK LEVEL"]
[]
[]
[null,"5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL  (Summed at transmission connection point)"]
[null,null,"UNIT",{"$f":"CRY","v":"2015-16"}]
[null,"Raw network coincident MD","MW",4613.3562127191999]
[null,"Date MD occurred",null,"2016-02-01T16:30:00"]
[null,"Half hour time period MD occurred",null,"16:30:00"]
[null,"Winter/summer peaking",null,"Summer"]
[null,"Embedded generation","MW",20]
[null,"Weather corrected (10% POE) network coincident MD","MW",4889]
[null,"Weather corrected (50% POE) network coincident MD","MW",4595]

{"sheet":"5.4 MD & utilisation-Spatial","index":22,"n_rows":11431,"n_cols":7,"rows_kept":11431,"cut":false,"hidden":false,"merged":[[5,1,5,2],[25,3,26,3],[25,4,26,4],[27,3,28,3],[27,4,28,4],[29,3,30,3],[29,4,30,4],[17,4,18,4],[19,3,20,3],[19,4,20,4],[21,3,22,3],[21,4,22,4],[23,3,24,3],[23,4,24,4],[9,2,30,2],[9,3,10,3],[9,4,10,4],[11,3,12,3],[11,4,12,4],[13,3,14,3],[13,4,14,4],[15,3,16,3],[15,4,16,4],[17,3,18,3],[69,3,70,3],[69,4,70,4],[71,3,72,3],[71,4,72,4],[73,3,74,3],[73,4,74,4],[61,4,62,4],[63,3,64,3],[63,4,64,4],[65,3,66,3],[65,4,66,4],[67,3,68,3],[67,4,68,4],[53,2,74,2],[53,3,54,3],[53,4,54,4],[55,3,56,3],[55,4,56,4],[57,3,58,3],[57,4,58,4],[59,3,60,3],[59,4,60,4],[61,3,62,3],[47,3,48,3],[47,4,48,4],[49,3,50,3],[49,4,50,4],[51,3,52,3],[51,4,52,4],[39,4,40,4],[41,3,42,3],[41,4,42,4],[43,3,44,3],[43,4,44,4],[45,3,46,3],[45,4,46,4],[31,2,52,2],[31,3,32,3],[31,4,32,4],[33,3,34,3],[33,4,34,4],[35,3,36,3],[35,4,36,4],[37,3,38,3],[37,4,38,4],[39,3,40,3],[113,3,114,3],[113,4,114,4],[115,3,116,3],[115,4,116,4],[117,3,118,3],[117,4,118,4],[105,4,106,4],[107,3,108,3],[107,4,108,4],[109,3,110,3],[109,4,110,4],[111,3,112,3],[111,4,112,4],[97,2,118,2],[97,3,98,3],[97,4,98,4],[99,3,100,3],[99,4,100,4],[101,3,102,3],[101,4,102,4],[103,3,104,3],[103,4,104,4],[105,3,106,3],[91,3,92,3],[91,4,92,4],[93,3,94,3],[93,4,94,4],[95,3,96,3],[95,4,96,4],[83,4,84,4],[85,3,86,3],[85,4,86,4],[87,3,88,3],[87,4,88,4],[89,3,90,3],[89,4,90,4],[75,2,96,2],[75,3,76,3],[75,4,76,4],[77,3,78,3],[77,4,78,4],[79,3,80,3],[79,4,80,4],[81,3,82,3],[81,4,82,4],[83,3,84,3],[157,3,158,3],[157,4,158,4],[159,3,160,3],[159,4,160,4],[161,3,162,3],[161,4,162,4],[149,4,150,4],[151,3,152,3],[151,4,152,4],[153,3,154,3],[153,4,154,4],[155,3,156,3],[155,4,156,4],[141,2,162,2],[141,3,142,3],[141,4,142,4],[143,3,144,3],[143,4,144,4],[145,3,146,3],[145,4,146,4],[147,3,148,3],[147,4,148,4],[149,3,150,3],[135,3,136,3],[135,4,136,4],[137,3,138,3],[137,4,138,4],[139,3,140,3],[139,4,140,4],[127,4,128,4],[129,3,130,3],[129,4,130,4],[131,3,132,3],[131,4,132,4],[133,3,134,3],[133,4,134,4],[119,2,140,2],[119,3,120,3],[119,4,120,4],[121,3,122,3],[121,4,122,4],[123,3,124,3],[123,4,124,4],[125,3,126,3],[125,4,126,4],[127,3,128,3],[201,3,202,3],[201,4,202,4],[203,3,204,3],[203,4,204,4],[205,3,206,3],[205,4,206,4],[193,4,194,4],[195,3,196,3],[195,4,196,4],[197,3,198,3],[197,4,198,4],[199,3,200,3],[199,4,200,4],[185,2,206,2],[185,3,186,3],[185,4,186,4],[187,3,188,3],[187,4,188,4],[189,3,190,3],[189,4,190,4],[191,3,192,3],[191,4,192,4],[193,3,194,3],[179,3,180,3],[179,4,180,4],[181,3,182,3],[181,4,182,4],[183,3,184,3],[183,4,184,4],[171,4,172,4],[173,3,174,3],[173,4,174,4],[175,3,176,3],[175,4,176,4],[177,3,178,3],[177,4,178,4],[163,2,184,2],[163,3,164,3],[163,4,164,4],[165,3,166,3],[165,4,166,4],[167,3,168,3],[167,4,168,4],[169,3,170,3],[169,4,170,4],[171,3,172,3],[245,3,246,3],[245,4,246,4],[247,3,248,3],[247,4,248,4],[249,3,250,3],[249,4,250,4],[237,4,238,4],[239,3,240,3],[239,4,240,4],[241,3,242,3],[241,4,242,4],[243,3,244,3],[243,4,244,4],[229,2,250,2],[229,3,230,3],[229,4,230,4],[231,3,232,3],[231,4,232,4],[233,3,234,3],[233,4,234,4],[235,3,236,3],[235,4,236,4],[237,3,238,3],[223,3,224,3],[223,4,224,4],[225,3,226,3],[225,4,226,4],[227,3,228,3],[227,4,228,4],[215,4,216,4],[217,3,218,3],[217,4,218,4],[219,3,220,3],[219,4,220,4],[221,3,222,3],[221,4,222,4],[207,2,228,2],[207,3,208,3],[207,4,208,4],[209,3,210,3],[209,4,210,4],[211,3,212,3],[211,4,212,4],[213,3,214,3],[213,4,214,4],[215,3,216,3],[289,3,290,3],[289,4,290,4],[291,3,292,3],[291,4,292,4],[293,3,294,3],[293,4,294,4],[281,4,282,4],[283,3,284,3],[283,4,284,4],[285,3,286,3],[285,4,286,4],[287,3,288,3],[287,4,288,4],[273,2,294,2],[273,3,274,3],[273,4,274,4],[275,3,276,3],[275,4,276,4],[277,3,278,3],[277,4,278,4],[279,3,280,3],[279,4,280,4],[281,3,282,3],[267,3,268,3],[267,4,268,4],[269,3,270,3],[269,4,270,4],[271,3,272,3],[271,4,272,4],[259,4,260,4],[261,3,262,3],[261,4,262,4],[263,3,264,3],[263,4,264,4],[265,3,266,3],[265,4,266,4],[251,2,272,2],[251,3,252,3],[251,4,252,4],[253,3,254,3],[253,4,254,4],[255,3,256,3],[255,4,256,4],[257,3,258,3],[257,4,258,4],[259,3,260,3],[333,3,334,3],[333,4,334,4],[335,3,336,3],[335,4,336,4],[337,3,338,3],[337,4,338,4],[325,4,326,4],[327,3,328,3],[327,4,328,4],[329,3,330,3],[329,4,330,4],[331,3,332,3],[331,4,332,4],[317,2,338,2],[317,3,318,3],[317,4,318,4],[319,3,320,3],[319,4,320,4],[321,3,322,3],[321,4,322,4],[323,3,324,3],[323,4,324,4],[325,3,326,3],[311,3,312,3],[311,4,312,4],[313,3,314,3],[313,4,314,4],[315,3,316,3],[315,4,316,4],[303,4,304,4],[305,3,306,3],[305,4,306,4],[307,3,308,3],[307,4,308,4],[309,3,310,3],[309,4,310,4],[295,2,316,2],[295,3,296,3],[295,4,296,4],[297,3,298,3],[297,4,298,4],[299,3,300,3],[299,4,300,4],[301,3,302,3],[301,4,302,4],[303,3,304,3],[377,3,378,3],[377,4,378,4],[379,3,380,3],[379,4,380,4],[381,3,382,3],[381,4,382,4],[369,4,370,4],[371,3,372,3],[371,4,372,4],[373,3,374,3],[373,4,374,4],[375,3,376,3],[375,4,376,4],[361,2,382,2],[361,3,362,3],[361,4,362,4],[363,3,364,3],[363,4,364,4],[365,3,366,3],[365,4,366,4],[367,3,368,3],[367,4,368,4],[369,3,370,3],[355,3,356,3],[355,4,356,4],[357,3,358,3],[357,4,358,4],[359,3,360,3],[359,4,360,4],[347,4,348,4],[349,3,350,3],[349,4,350,4],[351,3,352,3],[351,4,352,4],[353,3,354,3],[353,4,354,4],[339,2,360,2],[339,3,340,3],[339,4,340,4],[341,3,342,3],[341,4,342,4],[343,3,344,3],[343,4,344,4],[345,3,346,3],[345,4,346,4],[347,3,348,3],[421,3,422,3],[421,4,422,4],[423,3,424,3],[423,4,424,4],[425,3,426,3],[425,4,426,4],[413,4,414,4],[415,3,416,3],[415,4,416,4],[417,3,418,3],[417,4,418,4],[419,3,420,3],[419,4,420,4],[405,2,426,2],[405,3,406,3],[405,4,406,4],[407,3,408,3],[407,4,408,4],[409,3,410,3],[409,4,410,4],[411,3,412,3],[411,4,412,4],[413,3,414,3],[399,3,400,3],[399,4,400,4],[401,3,402,3],[401,4,402,4],[403,3,404,3],[403,4,404,4],[391,4,392,4],[393,3,394,3],[393,4,394,4],[395,3,396,3],[395,4,396,4],[397,3,398,3],[397,4,398,4],[383,2,404,2],[383,3,384,3],[383,4,384,4],[385,3,386,3],[385,4,386,4],[387,3,388,3],[387,4,388,4],[389,3,390,3],[389,4,390,4],[391,3,392,3],[465,3,466,3],[465,4,466,4],[467,3,468,3],[467,4,468,4],[469,3,470,3],[469,4,470,4],[457,4,458,4],[459,3,460,3],[459,4,460,4],[461,3,462,3],[461,4,462,4],[463,3,464,3],[463,4,464,4],[449,2,470,2],[449,3,450,3],[449,4,450,4],[451,3,452,3],[451,4,452,4],[453,3,454,3],[453,4,454,4],[455,3,456,3],[455,4,456,4],[457,3,458,3],[443,3,444,3],[443,4,444,4],[445,3,446,3],[445,4,446,4],[447,3,448,3],[447,4,448,4],[435,4,436,4],[437,3,438,3],[437,4,438,4],[439,3,440,3],[439,4,440,4],[441,3,442,3],[441,4,442,4],[427,2,448,2],[427,3,428,3],[427,4,428,4],[429,3,430,3],[429,4,430,4],[431,3,432,3],[431,4,432,4],[433,3,434,3],[433,4,434,4],[435,3,436,3],[509,3,510,3],[509,4,510,4],[511,3,512,3],[511,4,512,4],[513,3,514,3],[513,4,514,4],[501,4,502,4],[503,3,504,3],[503,4,504,4],[505,3,506,3],[505,4,506,4],[507,3,508,3],[507,4,508,4],[493,2,514,2],[493,3,494,3],[493,4,494,4],[495,3,496,3],[495,4,496,4],[497,3,498,3],[497,4,498,4],[499,3,500,3],[499,4,500,4],[501,3,502,3],[487,3,488,3],[487,4,488,4],[489,3,490,3],[489,4,490,4],[491,3,492,3],[491,4,492,4],[479,4,480,4],[481,3,482,3],[481,4,482,4],[483,3,484,3],[483,4,484,4],[485,3,486,3],[485,4,486,4],[471,2,492,2],[471,3,472,3],[471,4,472,4],[473,3,474,3],[473,4,474,4],[475,3,476,3],[475,4,476,4],[477,3,478,3],[477,4,478,4],[479,3,480,3],[553,3,554,3],[553,4,554,4],[555,3,556,3],[555,4,556,4],[557,3,558,3],[557,4,558,4],[545,4,546,4],[547,3,548,3],[547,4,548,4],[549,3,550,3],[549,4,550,4],[551,3,552,3],[551,4,552,4],[537,2,558,2],[537,3,538,3],[537,4,538,4],[539,3,540,3],[539,4,540,4],[541,3,542,3],[541,4,542,4],[543,3,544,3],[543,4,544,4],[545,3,546,3],[531,3,532,3],[531,4,532,4],[533,3,534,3],[533,4,534,4],[535,3,536,3],[535,4,536,4],[523,4,524,4],[525,3,526,3],[525,4,526,4],[527,3,528,3],[527,4,528,4],[529,3,530,3],[529,4,530,4],[515,2,536,2],[515,3,516,3],[515,4,516,4],[517,3,518,3],[517,4,518,4],[519,3,520,3],[519,4,520,4],[521,3,522,3],[521,4,522,4],[523,3,524,3],[597,3,598,3],[597,4,598,4],[599,3,600,3],[599,4,600,4],[601,3,602,3],[601,4,602,4],[589,4,590,4],[591,3,592,3],[591,4,592,4],[593,3,594,3],[593,4,594,4],[595,3,596,3],[595,4,596,4],[581,2,602,2],[581,3,582,3],[581,4,582,4],[583,3,584,3],[583,4,584,4],[585,3,586,3],[585,4,586,4],[587,3,588,3],[587,4,588,4],[589,3,590,3],[575,3,576,3],[575,4,576,4],[577,3,578,3],[577,4,578,4],[579,3,580,3],[579,4,580,4],[567,4,568,4],[569,3,570,3],[569,4,570,4],[571,3,572,3],[571,4,572,4],[573,3,574,3],[573,4,574,4],[559,2,580,2],[559,3,560,3],[559,4,560,4],[561,3,562,3],[561,4,562,4],[563,3,564,3],[563,4,564,4],[565,3,566,3],[565,4,566,4],[567,3,568,3],[641,3,642,3],[641,4,642,4],[643,3,644,3],[643,4,644,4],[645,3,646,3],[645,4,646,4],[633,4,634,4],[635,3,636,3],[635,4,636,4],[637,3,638,3],[637,4,638,4],[639,3,640,3],[639,4,640,4],[625,2,646,2],[625,3,626,3],[625,4,626,4],[627,3,628,3],[627,4,628,4],[629,3,630,3],[629,4,630,4],[631,3,632,3],[631,4,632,4],[633,3,634,3],[619,3,620,3],[619,4,620,4],[621,3,622,3],[621,4,622,4],[623,3,624,3],[623,4,624,4],[611,4,612,4],[613,3,614,3],[613,4,614,4],[615,3,616,3],[615,4,616,4],[617,3,618,3],[617,4,618,4],[603,2,624,2],[603,3,604,3],[603,4,604,4],[605,3,606,3],[605,4,606,4],[607,3,608,3],[607,4,608,4],[609,3,610,3],[609,4,610,4],[611,3,612,3],[685,3,686,3],[685,4,686,4],[687,3,688,3],[687,4,688,4],[689,3,690,3],[689,4,690,4],[677,4,678,4],[679,3,680,3],[679,4,680,4],[681,3,682,3],[681,4,682,4],[683,3,684,3],[683,4,684,4],[669,2,690,2],[669,3,670,3],[669,4,670,4],[671,3,672,3],[671,4,672,4],[673,3,674,3],[673,4,674,4],[675,3,676,3],[675,4,676,4],[677,3,678,3],[663,3,664,3],[663,4,664,4],[665,3,666,3],[665,4,666,4],[667,3,668,3],[667,4,668,4],[655,4,656,4],[657,3,658,3],[657,4,658,4],[659,3,660,3],[659,4,660,4],[661,3,662,3],[661,4,662,4],[647,2,668,2],[647,3,648,3],[647,4,648,4],[649,3,650,3],[649,4,650,4],[651,3,652,3],[651,4,652,4],[653,3,654,3],[653,4,654,4],[655,3,656,3],[729,3,730,3],[729,4,730,4],[731,3,732,3],[731,4,732,4],[733,3,734,3],[733,4,734,4],[721,4,722,4],[723,3,724,3],[723,4,724,4],[725,3,726,3],[725,4,726,4],[727,3,728,3],[727,4,728,4],[713,2,734,2],[713,3,714,3],[713,4,714,4],[715,3,716,3],[715,4,716,4],[717,3,718,3],[717,4,718,4],[719,3,720,3],[719,4,720,4],[721,3,722,3],[707,3,708,3],[707,4,708,4],[709,3,710,3],[709,4,710,4],[711,3,712,3],[711,4,712,4],[699,4,700,4],[701,3,702,3],[701,4,702,4],[703,3,704,3],[703,4,704,4],[705,3,706,3],[705,4,706,4],[691,2,712,2],[691,3,692,3],[691,4,692,4],[693,3,694,3],[693,4,694,4],[695,3,696,3],[695,4,696,4],[697,3,698,3],[697,4,698,4],[699,3,700,3],[773,3,774,3],[773,4,774,4],[775,3,776,3],[775,4,776,4],[777,3,778,3],[777,4,778,4],[765,4,766,4],[767,3,768,3],[767,4,768,4],[769,3,770,3],[769,4,770,4],[771,3,772,3],[771,4,772,4],[757,2,778,2],[757,3,758,3],[757,4,758,4],[759,3,760,3],[759,4,760,4],[761,3,762,3],[761,4,762,4],[763,3,764,3],[763,4,764,4],[765,3,766,3],[751,3,752,3],[751,4,752,4],[753,3,754,3],[753,4,754,4],[755,3,756,3],[755,4,756,4],[743,4,744,4],[745,3,746,3],[745,4,746,4],[747,3,748,3],[747,4,748,4],[749,3,750,3],[749,4,750,4],[735,2,756,2],[735,3,736,3],[735,4,736,4],[737,3,738,3],[737,4,738,4],[739,3,740,3],[739,4,740,4],[741,3,742,3],[741,4,742,4],[743,3,744,3],[817,3,818,3],[817,4,818,4],[819,3,820,3],[819,4,820,4],[821,3,822,3],[821,4,822,4],[809,4,810,4],[811,3,812,3],[811,4,812,4],[813,3,814,3],[813,4,814,4],[815,3,816,3],[815,4,816,4],[801,2,822,2],[801,3,802,3],[801,4,802,4],[803,3,804,3],[803,4,804,4],[805,3,806,3],[805,4,806,4],[807,3,808,3],[807,4,808,4],[809,3,810,3],[795,3,796,3],[795,4,796,4],[797,3,798,3],[797,4,798,4],[799,3,800,3],[799,4,800,4],[787,4,788,4],[789,3,790,3],[789,4,790,4],[791,3,792,3],[791,4,792,4],[793,3,794,3],[793,4,794,4],[779,2,800,2],[779,3,780,3],[779,4,780,4],[781,3,782,3],[781,4,782,4],[783,3,784,3],[783,4,784,4],[785,3,786,3],[785,4,786,4],[787,3,788,3],[861,3,862,3],[861,4,862,4],[863,3,864,3],[863,4,864,4],[865,3,866,3],[865,4,866,4],[853,4,854,4],[855,3,856,3],[855,4,856,4],[857,3,858,3],[857,4,858,4],[859,3,860,3],[859,4,860,4],[845,2,866,2],[845,3,846,3],[845,4,846,4],[847,3,848,3],[847,4,848,4],[849,3,850,3],[849,4,850,4],[851,3,852,3],[851,4,852,4],[853,3,854,3],[839,3,840,3],[839,4,840,4],[841,3,842,3],[841,4,842,4],[843,3,844,3],[843,4,844,4],[831,4,832,4],[833,3,834,3],[833,4,834,4],[835,3,836,3],[835,4,836,4],[837,3,838,3],[837,4,838,4],[823,2,844,2],[823,3,824,3],[823,4,824,4],[825,3,826,3],[825,4,826,4],[827,3,828,3],[827,4,828,4],[829,3,830,3],[829,4,830,4],[831,3,832,3],[905,3,906,3],[905,4,906,4],[907,3,908,3],[907,4,908,4],[909,3,910,3],[909,4,910,4],[897,4,898,4],[899,3,900,3],[899,4,900,4],[901,3,902,3],[901,4,902,4],[903,3,904,3],[903,4,904,4],[889,2,910,2],[889,3,890,3],[889,4,890,4],[891,3,892,3],[891,4,892,4],[893,3,894,3],[893,4,894,4],[895,3,896,3],[895,4,896,4],[897,3,898,3],[883,3,884,3],[883,4,884,4],[885,3,886,3],[885,4,886,4],[887,3,888,3],[887,4,888,4],[875,4,876,4],[877,3,878,3],[877,4,878,4],[879,3,880,3],[879,4,880,4],[881,3,882,3],[881,4,882,4],[867,2,888,2],[867,3,868,3],[867,4,868,4],[869,3,870,3],[869,4,870,4],[871,3,872,3],[871,4,872,4],[873,3,874,3],[873,4,874,4],[875,3,876,3],[949,3,950,3],[949,4,950,4],[951,3,952,3],[951,4,952,4],[953,3,954,3],[953,4,954,4],[941,4,942,4],[943,3,944,3],[943,4,944,4],[945,3,946,3],[945,4,946,4],[947,3,948,3],[947,4,948,4],[933,2,954,2],[933,3,934,3],[933,4,934,4],[935,3,936,3],[935,4,936,4],[937,3,938,3],[937,4,938,4],[939,3,940,3],[939,4,940,4],[941,3,942,3],[927,3,928,3],[927,4,928,4],[929,3,930,3],[929,4,930,4],[931,3,932,3],[931,4,932,4],[919,4,920,4],[921,3,922,3],[921,4,922,4],[923,3,924,3],[923,4,924,4],[925,3,926,3],[925,4,926,4],[911,2,932,2],[911,3,912,3],[911,4,912,4],[913,3,914,3],[913,4,914,4],[915,3,916,3],[915,4,916,4],[917,3,918,3],[917,4,918,4],[919,3,920,3],[993,3,994,3],[993,4,994,4],[995,3,996,3],[995,4,996,4],[997,3,998,3],[997,4,998,4],[985,4,986,4],[987,3,988,3],[987,4,988,4],[989,3,990,3]],"merged_total":11938,"flags":["merged_cut"]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL"]
[]
[null,"There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND"]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND",{"$f":"CRY","v":"2015-16"}]
[null,"SUBTRANSMISSION SUBSTATION","Abermain BS","Substation Rating","MVA","Non-Coincident",263.5]
[null,null,null,null,null,"Coincident",263.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",85.382537841796875]
[null,null,null,null,null,"Coincident",82.101402282714844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",85.426177978515625]
[null,null,null,null,null,"Coincident",82.228904724121094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4063999652862549]
[null,null,null,null,null,"Coincident",2.2576000690460205]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",96.933944702148438]
[null,null,null,null,null,"Coincident",93.208900451660156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",96.983489990234375]
[null,null,null,null,null,"Coincident",93.353652954101563]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",84.761810302734375]
[null,null,null,null,null,"Coincident",81.504524230957031]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",84.805130004882813]
[null,null,null,null,null,"Coincident",81.631103515625]
[null,null,"Algester BS","Substation Rating","MVA","Non-Coincident",201.69999694824219]
[null,null,null,null,null,"Coincident",201.69999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",66.840339660644531]
[null,null,null,null,null,"Coincident",63.623199462890625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",67.108024597167969]
[null,null,null,null,null,"Coincident",64.323127746582031]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",72.618019104003906]
[null,null,null,null,null,"Coincident",69.122787475585938]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",72.908836364746094]
[null,null,null,null,null,"Coincident",69.883216857910156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",65.607803344726563]
[null,null,null,null,null,"Coincident",62.449985504150391]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",65.870552062988281]
[null,null,null,null,null,"Coincident",63.137008666992188]
[null,null,"Archerfield BS","Substation Rating","MVA","Non-Coincident",175.5]
[null,null,null,null,null,"Coincident",175.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",92.819900512695312]
[null,null,null,null,null,"Coincident",74.098861694335938]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",94.292694091796875]
[null,null,null,null,null,"Coincident",74.275650024414063]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.405656099319458]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",90.021377563476563]
[null,null,null,null,null,"Coincident",71.864784240722656]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",91.44976806640625]
[null,null,null,null,null,"Coincident",72.036239624023438]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",85.345115661621094]
[null,null,null,null,null,"Coincident",68.131683349609375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",86.699302673339844]
[null,null,null,null,null,"Coincident",68.294235229492188]
[null,null,"Ashgrove West BS","Substation Rating","MVA","Non-Coincident",168.19999694824219]
[null,null,null,null,null,"Coincident",168.19999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",68.5997314453125]
[null,null,null,null,null,"Coincident",66.810409545898438]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",68.936050415039063]
[null,null,null,null,null,"Coincident",67.109527587890625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",71.671630859375]
[null,null,null,null,null,"Coincident",69.802177429199219]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",72.02301025390625]
[null,null,null,null,null,"Coincident",70.114692687988281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",61.654010772705078]
[null,null,null,null,null,"Coincident",60.045856475830078]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",61.956275939941406]
[null,null,null,null,null,"Coincident",60.314689636230469]
[null,null,"Beaudesert BS","Substation Rating","MVA","Non-Coincident",145.10000610351562]
[null,null,null,null,null,"Coincident",145.10000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.458822250366211]
[null,null,null,null,null,"Coincident",31.383945465087891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.461795806884766]
[null,null,null,null,null,"Coincident",31.387369155883789]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.11906623840332]
[null,null,null,null,null,"Coincident",31.044998168945313]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.122007369995117]
[null,null,null,null,null,"Coincident",31.048385620117188]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.759101867675781]
[null,null,null,null,null,"Coincident",29.688270568847656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.76191520690918]
[null,null,null,null,null,"Coincident",29.691509246826172]
[null,null,"Beenleigh BS","Substation Rating","MVA","Non-Coincident",259.60000610351562]
[null,null,null,null,null,"Coincident",259.60000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",109.81461334228516]
[null,null,null,null,null,"Coincident",109.71613311767578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",110.78303527832031]
[null,null,null,null,null,"Coincident",110.3914794921875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.8142280578613281]
[null,null,null,null,null,"Coincident",1.8129639625549316]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",122.24671936035156]
[null,null,null,null,null,"Coincident",122.13709259033203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",123.32477569580078]
[null,null,null,null,null,"Coincident",122.88889312744141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",108.43094635009766]
[null,null,null,null,null,"Coincident",108.33370971679687]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",109.38716888427734]
[null,null,null,null,null,"Coincident",109.00054931640625]
[null,null,"Beerwah BS","Substation Rating","MVA","Non-Coincident",143.5]
[null,null,null,null,null,"Coincident",143.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",46.026798248291016]
[null,null,null,null,null,"Coincident",42.800888061523438]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",47.880455017089844]
[null,null,null,null,null,"Coincident",43.997489929199219]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.633132934570313]
[null,null,null,null,null,"Coincident",44.294635772705078]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.551479339599609]
[null,null,null,null,null,"Coincident",45.533000946044922]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.016483306884766]
[null,null,null,null,null,"Coincident",39.071647644042969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",43.708629608154297]
[null,null,null,null,null,"Coincident",40.163990020751953]
[null,null,"Belmont BS","Substation Rating","MVA","Non-Coincident",298.89999389648437]
[null,null,null,null,null,"Coincident",298.89999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",128.73075866699219]
[null,null,null,null,null,"Coincident",126.73635864257812]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",129.5826416015625]
[null,null,null,null,null,"Coincident",127.65715026855469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.8167040348052979]
[null,null,null,null,null,"Coincident",3.7718119621276855]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",130.36306762695312]
[null,null,null,null,null,"Coincident",128.3433837890625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",131.22575378417969]
[null,null,null,null,null,"Coincident",129.27584838867187]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",115.64656829833984]
[null,null,null,null,null,"Coincident",113.85487365722656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",116.411865234375]
[null,null,null,null,null,"Coincident",114.68207550048828]
[null,null,"Brendale BS","Substation Rating","MVA","Non-Coincident",273.20001220703125]
[null,null,null,null,null,"Coincident",273.20001220703125]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",168.47554016113281]
[null,null,null,null,null,"Coincident",160.70462036132812]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",168.68367004394531]
[null,null,null,null,null,"Coincident",160.87165832519531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",170.83924865722656]
[null,null,null,null,null,"Coincident",162.95930480957031]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",171.05029296875]
[null,null,null,null,null,"Coincident",163.12867736816406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",151.31294250488281]
[null,null,null,null,null,"Coincident",144.33363342285156]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",151.49986267089844]
[null,null,null,null,null,"Coincident",144.48365783691406]
[null,null,"Browns Plains BS","Substation Rating","MVA","Non-Coincident",196.39999389648437]
[null,null,null,null,null,"Coincident",196.39999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",92.515022277832031]
[null,null,null,null,null,"Coincident",89.618972778320312]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",94.394088745117188]
[null,null,null,null,null,"Coincident",91.682891845703125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.3408360481262207]
[null,null,null,null,null,"Coincident",3.3390998840332031]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",96.889129638671875]
[null,null,null,null,null,"Coincident",93.856155395507812]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",98.857040405273437]
[null,null,null,null,null,"Coincident",96.017654418945313]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",88.059494018554688]
[null,null,null,null,null,"Coincident",85.302925109863281]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",89.848068237304688]
[null,null,null,null,null,"Coincident",87.267440795898437]
[null,null,"Burleigh Heads BS","Substation Rating","MVA","Non-Coincident",164.89999389648437]
[null,null,null,null,null,"Coincident",164.89999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",80.7742919921875]
[null,null,null,null,null,"Coincident",80.7742919921875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",81.855949401855469]
[null,null,null,null,null,"Coincident",81.855949401855469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",83.511734008789063]
[null,null,null,null,null,"Coincident",83.511734008789063]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",84.630050659179688]
[null,null,null,null,null,"Coincident",84.630050659179688]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",78.388221740722656]
[null,null,null,null,null,"Coincident",78.388221740722656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",79.43792724609375]
[null,null,null,null,null,"Coincident",79.43792724609375]
[null,null,"Caboolture BS","Substation Rating","MVA","Non-Coincident",269.524]
[null,null,null,null,null,"Coincident",269.524]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",124.39958190917969]
[null,null,null,null,null,"Coincident",107.96089172363281]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",124.67660522460937]
[null,null,null,null,null,"Coincident",108.39515686035156]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",126.07648468017578]
[null,null,null,null,null,"Coincident",109.41619873046875]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",126.35723876953125]
[null,null,null,null,null,"Coincident",109.85631561279297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",111.27169036865234]
[null,null,null,null,null,"Coincident",96.567779541015625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",111.51947784423828]
[null,null,null,null,null,"Coincident",96.956214904785156]
[null,null,"Cleveland BS","Substation Rating","MVA","Non-Coincident",286.5]
[null,null,null,null,null,"Coincident",286.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",150.99000549316406]
[null,null,null,null,null,"Coincident",136.24000549316406]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",152.41458129882813]
[null,null,null,null,null,"Coincident",137.28541564941406]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.7424359917640686]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",160.72282409667969]
[null,null,null,null,null,"Coincident",145.02204895019531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",162.23922729492187]
[null,null,null,null,null,"Coincident",146.13484191894531]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",139.93905639648437]
[null,null,null,null,null,"Coincident",126.26860046386719]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",141.25936889648437]
[null,null,null,null,null,"Coincident",127.23750305175781]
[null,null,"Coomera BS","Substation Rating","MVA","Non-Coincident",189.60000610351562]
[null,null,null,null,null,"Coincident",189.60000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",72.185516357421875]
[null,null,null,null,null,"Coincident",68.942947387695312]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",73.847267150878906]
[null,null,null,null,null,"Coincident",70.572029113769531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",80.608123779296875]
[null,null,null,null,null,"Coincident",76.987213134765625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",82.463768005371094]
[null,null,null,null,null,"Coincident",78.806373596191406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",68.923454284667969]
[null,null,null,null,null,"Coincident",65.827415466308594]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",70.510108947753906]
[null,null,null,null,null,"Coincident",67.382881164550781]
[null,null,"Coorparoo BS","Substation Rating","MVA","Non-Coincident",178.553]
[null,null,null,null,null,"Coincident",178.553]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",69.47467041015625]
[null,null,null,null,null,"Coincident",64.383941650390625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",72.233169555664063]
[null,null,null,null,null,"Coincident",67.707572937011719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",71.080924987792969]
[null,null,null,null,null,"Coincident",65.87249755859375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",73.903205871582031]
[null,null,null,null,null,"Coincident",69.272972106933594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",63.060768127441406]
[null,null,null,null,null,"Coincident",58.440013885498047]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",65.564598083496094]
[null,null,null,null,null,"Coincident",61.456809997558594]
[null,null,"Doboy BS","Substation Rating","MVA","Non-Coincident",262.89999389648437]
[null,null,null,null,null,"Coincident",262.89999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",123.91932678222656]
[null,null,null,null,null,"Coincident",118.76438903808594]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",125.1158447265625]
[null,null,null,null,null,"Coincident",119.24189758300781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",126.14615631103516]
[null,null,null,null,null,"Coincident",120.89858245849609]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",127.36417388916016]
[null,null,null,null,null,"Coincident",121.38467407226562]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",118.42969512939453]
[null,null,null,null,null,"Coincident",113.50312805175781]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",119.57321166992187]
[null,null,null,null,null,"Coincident",113.95948028564453]
[null,null,"Gatton BS","Substation Rating","MVA","Non-Coincident",143.19999694824219]
[null,null,null,null,null,"Coincident",143.19999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.494960784912109]
[null,null,null,null,null,"Coincident",18.279331207275391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.867305755615234]
[null,null,null,null,null,"Coincident",18.363031387329102]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.60533332824707]
[null,null,null,null,null,"Coincident",20.600440979003906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.024957656860352]
[null,null,null,null,null,"Coincident",20.694770812988281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.956562042236328]
[null,null,null,null,null,"Coincident",17.877552032470703]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.320722579956055]
[null,null,null,null,null,"Coincident",17.95941162109375]
[null,null,"Goodna BS","Substation Rating","MVA","Non-Coincident",217.80000305175781]
[null,null,null,null,null,"Coincident",217.80000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",97.477981567382813]
[null,null,null,null,null,"Coincident",92.70654296875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",97.6385498046875]
[null,null,null,null,null,"Coincident",92.864768981933594]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",105.63883209228516]
[null,null,null,null,null,"Coincident",100.46793365478516]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",105.81284332275391]
[null,null,null,null,null,"Coincident",100.639404296875]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",96.367713928222656]
[null,null,null,null,null,"Coincident",91.650619506835938]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",96.526451110839844]
[null,null,null,null,null,"Coincident",91.807044982910156]
[null,null,"Griffin BS","Substation Rating","MVA","Non-Coincident",189.059]
[null,null,null,null,null,"Coincident",189.059]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",55.827796936035156]
[null,null,null,null,null,"Coincident",51.860973358154297]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",55.97772216796875]
[null,null,null,null,null,"Coincident",53.077068328857422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",55.454307556152344]
[null,null,null,null,null,"Coincident",51.514022827148438]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",55.603229522705078]
[null,null,null,null,null,"Coincident",52.721981048583984]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",48.085597991943359]
[null,null,null,null,null,"Coincident",44.668895721435547]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",48.214733123779297]
[null,null,null,null,null,"Coincident",45.716342926025391]
[null,null,"Gympie BS","Substation Rating","MVA","Non-Coincident",135.19999694824219]
[null,null,null,null,null,"Coincident",135.19999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",45.582706451416016]
[null,null,null,null,null,"Coincident",39.952880859375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",47.158493041992188]
[null,null,null,null,null,"Coincident",40.729900360107422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.66583251953125]
[null,null,null,null,null,"Coincident",41.778724670410156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.313632965087891]
[null,null,null,null,null,"Coincident",42.591255187988281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",44.349239349365234]
[null,null,null,null,null,"Coincident",38.871757507324219]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",45.88238525390625]
[null,null,null,null,null,"Coincident",39.627750396728516]
[null,null,"Hays Inlet BS","Substation Rating","MVA","Non-Coincident",267.89999389648438]
[null,null,null,null,null,"Coincident",267.89999389648438]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",143.82749938964844]
[null,null,null,null,null,"Coincident",115.89173126220703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",143.94413757324219]
[null,null,null,null,null,"Coincident",115.96562194824219]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",140.34255981445312]
[null,null,null,null,null,"Coincident",110.28720855712891]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",140.45637512207031]
[null,null,null,null,null,"Coincident",110.35752868652344]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",124.60208129882812]
[null,null,null,null,null,"Coincident",105.00485992431641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",124.703125]
[null,null,null,null,null,"Coincident",105.07180786132812]
[null,null,"Ibis BS","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.995347023010254]
[null,null,null,null,null,"Coincident",8.3940668106079102]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.132973670959473]
[null,null,null,null,null,"Coincident",11.443393707275391]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-03"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.135300636291504]
[null,null,null,null,null,"Coincident",8.4780073165893555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.284303665161133]
[null,null,null,null,null,"Coincident",11.557827949523926]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.995347023010254]
[null,null,null,null,null,"Coincident",8.3940668106079102]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.132973670959473]
[null,null,null,null,null,"Coincident",11.443393707275391]
[null,null,"Jimboomba BS","Substation Rating","MVA","Non-Coincident",88]
[null,null,null,null,null,"Coincident",88]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",54.595226287841797]
[null,null,null,null,null,"Coincident",45.3463134765625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",57.421703338623047]
[null,null,null,null,null,"Coincident",47.604274749755859]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",59.449287414550781]
[null,null,null,null,null,"Coincident",49.3780517578125]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",62.527065277099609]
[null,null,null,null,null,"Coincident",51.836769104003906]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",51.867649078369141]
[null,null,null,null,null,"Coincident",43.080810546875]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",54.552913665771484]
[null,null,null,null,null,"Coincident",45.225963592529297]
[null,null,"Lockrose BS","Substation Rating","MVA","Non-Coincident",206.39999389648437]
[null,null,null,null,null,"Coincident",206.39999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",49.689998626708984]
[null,null,null,null,null,"Coincident",40.805625915527344]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",51.861530303955078]
[null,null,null,null,null,"Coincident",40.893318176269531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.0687999725341797]
[null,null,null,null,null,"Coincident",3.6692380905151367]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",54.412532806396484]
[null,null,null,null,null,"Coincident",44.683792114257812]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",56.790447235107422]
[null,null,null,null,null,"Coincident",44.779819488525391]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",48.128242492675781]
[null,null,null,null,null,"Coincident",39.523105621337891]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",50.231521606445313]
[null,null,null,null,null,"Coincident",39.608039855957031]
[null,null,"Loganlea BS","Substation Rating","MVA","Non-Coincident",247.69999694824219]
[null,null,null,null,null,"Coincident",247.69999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",90.686309814453125]
[null,null,null,null,null,"Coincident",88.895713806152344]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",90.926803588867188]
[null,null,null,null,null,"Coincident",88.975822448730469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",99.221710205078125]
[null,null,null,null,null,"Coincident",97.262580871582031]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",99.484840393066406]
[null,null,null,null,null,"Coincident",97.350227355957031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",88.49169921875]
[null,null,null,null,null,"Coincident",86.744438171386719]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",88.726371765136719]
[null,null,null,null,null,"Coincident",86.822608947753906]
[null,null,"Lytton BS","Substation Rating","MVA","Non-Coincident",238.30000305175781]
[null,null,null,null,null,"Coincident",238.69999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",105.33326721191406]
[null,null,null,null,null,"Coincident",104.32225036621094]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",105.34451293945312]
[null,null,null,null,null,"Coincident",104.37214660644531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",108.46272277832031]
[null,null,null,null,null,"Coincident",102.37872314453125]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",108.47430419921875]
[null,null,null,null,null,"Coincident",102.42768859863281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",102.63778686523437]
[null,null,null,null,null,"Coincident",99.063369750976563]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",102.64875030517578]
[null,null,null,null,null,"Coincident",99.110748291015625]
[null,null,"Meeandah BS","Substation Rating","MVA","Non-Coincident",167.80000305175781]
[null,null,null,null,null,"Coincident",167.80000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",46.745742797851562]
[null,null,null,null,null,"Coincident",37.590160369873047]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",46.757350921630859]
[null,null,null,null,null,"Coincident",38.256195068359375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",49.929595947265625]
[null,null,null,null,null,"Coincident",40.150424957275391]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.941993713378906]
[null,null,null,null,null,"Coincident",40.861824035644531]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",47.308094024658203]
[null,null,null,null,null,"Coincident",38.042369842529297]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",47.319843292236328]
[null,null,null,null,null,"Coincident",38.716415405273437]
[null,null,"Molendinar BS","Substation Rating","MVA","Non-Coincident",316.20001220703125]
[null,null,null,null,null,"Coincident",316.20001220703125]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",129.05781555175781]
[null,null,null,null,null,"Coincident",125.17523193359375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",129.12278747558594]
[null,null,null,null,null,"Coincident",125.24173736572266]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",139.14497375488281]
[null,null,null,null,null,"Coincident",134.95893859863281]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",139.21502685546875]
[null,null,null,null,null,"Coincident",135.0306396484375]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",122.55201721191406]
[null,null,null,null,null,"Coincident",118.86515045166016]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",122.61370849609375]
[null,null,null,null,null,"Coincident",118.92830657958984]
[null,null,"Mudgeeraba BS","Substation Rating","MVA","Non-Coincident",98]
[null,null,null,null,null,"Coincident",98]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.087299346923828]
[null,null,null,null,null,"Coincident",19.548618316650391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.884822845458984]
[null,null,null,null,null,"Coincident",20.03203010559082]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.963653564453125]
[null,null,null,null,null,"Coincident",19.323026657104492]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.835674285888672]
[null,null,null,null,null,"Coincident",19.800861358642578]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.275571823120117]
[null,null,null,null,null,"Coincident",17.992353439331055]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.040866851806641]
[null,null,null,null,null,"Coincident",18.437280654907227]
[null,null,"Myrtletown BS","Substation Rating","MVA","Non-Coincident",239.60000610351562]
[null,null,null,null,null,"Coincident",239.60000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",40.750755310058594]
[null,null,null,null,null,"Coincident",35.190521240234375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.055522918701172]
[null,null,null,null,null,"Coincident",36.083515167236328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-12-10"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",41.15826416015625]
[null,null,null,null,null,"Coincident",35.542427062988281]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",42.476078033447266]
[null,null,null,null,null,"Coincident",36.444351196289063]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",40.750755310058594]
[null,null,null,null,null,"Coincident",35.190521240234375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",42.055522918701172]
[null,null,null,null,null,"Coincident",36.083515167236328]
[null,null,"Nambour BS","Substation Rating","MVA","Non-Coincident",143.80000305175781]
[null,null,null,null,null,"Coincident",143.80000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",66.677566528320313]
[null,null,null,null,null,"Coincident",63.818458557128906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",68.705032348632812]
[null,null,null,null,null,"Coincident",67.021697998046875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",63.665740966796875]
[null,null,null,null,null,"Coincident",60.935779571533203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",65.60162353515625]
[null,null,null,null,null,"Coincident",63.994327545166016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",57.742103576660156]
[null,null,null,null,null,"Coincident",55.266147613525391]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",59.497871398925781]
[null,null,null,null,null,"Coincident",58.040119171142578]
[null,null,"Nudgee BS","Substation Rating","MVA","Non-Coincident",249.5]
[null,null,null,null,null,"Coincident",249.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",136.21049499511719]
[null,null,null,null,null,"Coincident",127.53192138671875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",136.91073608398437]
[null,null,null,null,null,"Coincident",129.21368408203125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",143.33975219726562]
[null,null,null,null,null,"Coincident",134.20693969726562]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",144.07664489746094]
[null,null,null,null,null,"Coincident",135.97673034667969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",131.39137268066406]
[null,null,null,null,null,"Coincident",123.01984405517578]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",132.06683349609375]
[null,null,null,null,null,"Coincident",124.64210510253906]
[null,null,"Postmans Ridge BS","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.769599914550781]
[null,null,null,null,null,"Coincident",32.831714630126953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",36.505329132080078]
[null,null,null,null,null,"Coincident",33.293018341064453]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-16"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",37.521953582763672]
[null,null,null,null,null,"Coincident",34.440139770507812]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",38.293724060058594]
[null,null,null,null,null,"Coincident",34.924045562744141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",35.960609436035156]
[null,null,null,null,null,"Coincident",33.007034301757813]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",36.700267791748047]
[null,null,null,null,null,"Coincident",33.470802307128906]
[null,null,"Raceview BS","Substation Rating","MVA","Non-Coincident",132]
[null,null,null,null,null,"Coincident",132]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",88.88812255859375]
[null,null,null,null,null,"Coincident",85.073371887207031]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",88.892936706542969]
[null,null,null,null,null,"Coincident",85.076522827148438]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.82606798410415649]
[null,null,null,null,null,"Coincident",0.8397979736328125]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",104.67287445068359]
[null,null,null,null,null,"Coincident",100.18070220947266]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",104.67854309082031]
[null,null,null,null,null,"Coincident",100.18441009521484]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",89.86944580078125]
[null,null,null,null,null,"Coincident",86.012580871582031]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",89.874313354492188]
[null,null,null,null,null,"Coincident",86.015762329101563]
[null,null,"Richlands BS","Substation Rating","MVA","Non-Coincident",188.126]
[null,null,null,null,null,"Coincident",188.126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",110.44059753417969]
[null,null,null,null,null,"Coincident",95.238685607910156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",113.22576904296875]
[null,null,null,null,null,"Coincident",97.14398193359375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-29"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",107.05007171630859]
[null,null,null,null,null,"Coincident",92.314857482910156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",109.74973297119141]
[null,null,null,null,null,"Coincident",94.161659240722656]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",99.116020202636719]
[null,null,null,null,null,"Coincident",85.472908020019531]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",101.6156005859375]
[null,null,null,null,null,"Coincident",87.182838439941406]
[null,null,"Runcorn BS","Substation Rating","MVA","Non-Coincident",187.10000610351562]
[null,null,null,null,null,"Coincident",187.10000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",49.641166687011719]
[null,null,null,null,null,"Coincident",46.974559783935547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",49.857749938964844]
[null,null,null,null,null,"Coincident",47.280021667480469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",52.335193634033203]
[null,null,null,null,null,"Coincident",49.523872375488281]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",52.563529968261719]
[null,null,null,null,null,"Coincident",49.845909118652344]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",47.338809967041016]
[null,null,null,null,null,"Coincident",44.795879364013672]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",47.54534912109375]
[null,null,null,null,null,"Coincident",45.087173461914063]
[null,null,"Sandgate BS","Substation Rating","MVA","Non-Coincident",191.39999389648437]
[null,null,null,null,null,"Coincident",191.39999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",78.877822875976563]
[null,null,null,null,null,"Coincident",73.097190856933594]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",79.490989685058594]
[null,null,null,null,null,"Coincident",73.670448303222656]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.455485999584198]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",77.776687622070313]
[null,null,null,null,null,"Coincident",72.076751708984375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",78.381294250488281]
[null,null,null,null,null,"Coincident",72.642005920410156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",69.679878234863281]
[null,null,null,null,null,"Coincident",64.573326110839844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",70.221542358398437]
[null,null,null,null,null,"Coincident",65.079734802246094]
[null,null,"Stafford BS","Substation Rating","MVA","Non-Coincident",262.29998779296875]
[null,null,null,null,null,"Coincident",262.29998779296875]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",150.58505249023437]
[null,null,null,null,null,"Coincident",150.58505249023437]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",150.69036865234375]
[null,null,null,null,null,"Coincident",150.69036865234375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",155.88414001464844]
[null,null,null,null,null,"Coincident",155.88414001464844]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",155.9931640625]
[null,null,null,null,null,"Coincident",155.9931640625]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",137.17243957519531]
[null,null,null,null,null,"Coincident",137.17243957519531]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",137.26837158203125]
[null,null,null,null,null,"Coincident",137.26837158203125]
[null,null,"Stradbroke Is BS","Substation Rating","MVA","Non-Coincident",31.5]
[null,null,null,null,null,"Coincident",31.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.9264516830444336]
[null,null,null,null,null,"Coincident",8.7939844131469727]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.557492256164551]
[null,null,null,null,null,"Coincident",8.9572114944458008]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-08-03"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.174612998962402]
[null,null,null,null,null,"Coincident",9.0138339996337891]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.821429252624512]
[null,null,null,null,null,"Coincident",9.1811418533325195]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9264516830444336]
[null,null,null,null,null,"Coincident",8.7939844131469727]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.557492256164551]
[null,null,null,null,null,"Coincident",8.9572114944458008]
[null,null,"Sunrise Hills BS","Substation Rating","MVA","Non-Coincident",143]
[null,null,null,null,null,"Coincident",143]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",69.498794555664063]
[null,null,null,null,null,"Coincident",62.723957061767578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",72.040992736816406]
[null,null,null,null,null,"Coincident",65.136756896972656]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",68.944198608398438]
[null,null,null,null,null,"Coincident",62.223419189453125]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",71.466102600097656]
[null,null,null,null,null,"Coincident",64.616966247558594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",60.249198913574219]
[null,null,null,null,null,"Coincident",54.376026153564453]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",62.453056335449219]
[null,null,null,null,null,"Coincident",56.467704772949219]
[null,null,"Tennyson BS","Substation Rating","MVA","Non-Coincident",257.79998779296875]
[null,null,null,null,null,"Coincident",257.79998779296875]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",166.86079406738281]
[null,null,null,null,null,"Coincident",166.86079406738281]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",167.14482116699219]
[null,null,null,null,null,"Coincident",167.14482116699219]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",182.72257995605469]
[null,null,null,null,null,"Coincident",182.72257995605469]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",183.03359985351562]
[null,null,null,null,null,"Coincident",183.03359985351562]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",160.36990356445312]
[null,null,null,null,null,"Coincident",160.36990356445312]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",160.64288330078125]
[null,null,null,null,null,"Coincident",160.64288330078125]
[null,null,"Victoria Park BS","Substation Rating","MVA","Non-Coincident",251.39999389648438]
[null,null,null,null,null,"Coincident",251.39999389648438]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",48.76953125]
[null,null,null,null,null,"Coincident",48.413852691650391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",49.026397705078125]
[null,null,null,null,null,"Coincident",48.601291656494141]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.6175060000000001]
[null,null,null,null,null,"Coincident",3.4389958381652832]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",51.182155609130859]
[null,null,null,null,null,"Coincident",50.808883666992188]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",51.451732635498047]
[null,null,null,null,null,"Coincident",51.005596160888672]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",46.617328643798828]
[null,null,null,null,null,"Coincident",46.277347564697266]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.862861633300781]
[null,null,null,null,null,"Coincident",46.456516265869141]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[]
[]
[]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND",{"$f":"CRY","v":"2015-16"}]
[null,"ZONE SUBSTATION","Acacia Ridge","Substation Rating","MVA","Non-Coincident",41.900001525878906]
[null,null,null,null,null,"Coincident",41.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.527214050292969]
[null,null,null,null,null,"Coincident",16.395816802978516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.556097193452661]
[null,null,null,null,null,"Coincident",16.51750120626798]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01T13:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42401.5625]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.805097579956055]
[null,null,null,null,null,"Coincident",15.78950023651123]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.832912731104937]
[null,null,null,null,null,"Coincident",15.906684021682601]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.684625625610352]
[null,null,null,null,null,"Coincident",14.84870719909668]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.71078383518913]
[null,null,null,null,null,"Coincident",14.958909769564293]
[null,null,"Albany Creek","Substation Rating","MVA","Non-Coincident",59.299999237060547]
[null,null,null,null,null,"Coincident",59.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.345199584960938]
[null,null,null,null,null,"Coincident",23.610439300537109]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.017778396606445]
[null,null,null,null,null,"Coincident",24.404190063476563]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",29.00474739074707]
[null,null,null,null,null,"Coincident",25.993913650512695]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.745223999023438]
[null,null,null,null,null,"Coincident",26.867794036865234]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.540491104125977]
[null,null,null,null,null,"Coincident",21.096872329711914]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.14146614074707]
[null,null,null,null,null,"Coincident",21.806119918823242]
[null,null,"Alexandra Headland","Substation Rating","MVA","Non-Coincident",130.24299999999999]
[null,null,null,null,null,"Coincident",130.24299999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",71.393585205078125]
[null,null,null,null,null,"Coincident",65.362937927246094]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",72.84722900390625]
[null,null,null,null,null,"Coincident",66.504463195800781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",77.9853515625]
[null,null,null,null,null,"Coincident",71.397895812988281]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",79.573211669921875]
[null,null,null,null,null,"Coincident",72.644821166992187]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",67.97454833984375]
[null,null,null,null,null,"Coincident",62.232707977294922]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",69.358573913574219]
[null,null,null,null,null,"Coincident",63.319564819335938]
[null,null,"Algester","Substation Rating","MVA","Non-Coincident",54.799999237060547]
[null,null,null,null,null,"Coincident",54.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.248275756835937]
[null,null,null,null,null,"Coincident",16.323158264160156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.342123031616211]
[null,null,null,null,null,"Coincident",16.339174270629883]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.85211181640625]
[null,null,null,null,null,"Coincident",16.863290786743164]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.949064254760742]
[null,null,null,null,null,"Coincident",16.879837036132813]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.375461578369141]
[null,null,null,null,null,"Coincident",15.542422294616699]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.464818954467773]
[null,null,null,null,null,"Coincident",15.557671546936035]
[null,null,"Amamoor","Substation Rating","MVA","Non-Coincident",7.1999998092651367]
[null,null,null,null,null,"Coincident",7.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4]
[null,null,null,null,null,"Coincident",2.7479331493377686]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0811886787414551]
[null,null,null,null,null,"Coincident",3.0532326698303223]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-06-04"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0341200828552246]
[null,null,null,null,null,"Coincident",2.7713730335235596]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.1160011291503906]
[null,null,null,null,null,"Coincident",3.0792768001556396]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7975599765777588]
[null,null,null,null,null,"Coincident",2.6088602542877197]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.8746397495269775]
[null,null,null,null,null,"Coincident",2.8987085819244385]
[null,null,"Amberley","Substation Rating","MVA","Non-Coincident",26.299999237060547]
[null,null,null,null,null,"Coincident",26.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.4490399360656738]
[null,null,null,null,null,"Coincident",1.6675039529800415]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.7338368892669678]
[null,null,null,null,null,"Coincident",1.689470648765564]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5352659225463867]
[null,null,null,null,null,"Coincident",1.7091915607452393]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.8271827697753906]
[null,null,null,null,null,"Coincident",1.7317073345184326]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.4490399360656738]
[null,null,null,null,null,"Coincident",1.6675039529800415]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.7338368892669678]
[null,null,null,null,null,"Coincident",1.689470648765564]
[null,null,"Ann St","Substation Rating","MVA","Non-Coincident",188.10000610351562]
[null,null,null,null,null,"Coincident",188.10000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.826740264892578]
[null,null,null,null,null,"Coincident",40.388839721679688]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.973094940185547]
[null,null,null,null,null,"Coincident",40.525104522705078]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.109416961669922]
[null,null,null,null,null,"Coincident",44.427722930908203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",47.270404815673828]
[null,null,null,null,null,"Coincident",44.577617645263672]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",41.370632171630859]
[null,null,null,null,null,"Coincident",39.015621185302734]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",41.512012481689453]
[null,null,null,null,null,"Coincident",39.147251129150391]
[null,null,"Annerley","Substation Rating","MVA","Non-Coincident",59.200000762939453]
[null,null,null,null,null,"Coincident",59.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.055530548095703]
[null,null,null,null,null,"Coincident",13.587813377380371]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.477761268615723]
[null,null,null,null,null,"Coincident",13.741413116455078]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.699606895446777]
[null,null,null,null,null,"Coincident",13.420547485351563]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.139900207519531]
[null,null,null,null,null,"Coincident",13.572256088256836]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.052831649780273]
[null,null,null,null,null,"Coincident",12.640199661254883]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.446942329406738]
[null,null,null,null,null,"Coincident",12.783086776733398]
[null,null,"Arana Hills","Substation Rating","MVA","Non-Coincident",59.799999237060547]
[null,null,null,null,null,"Coincident",59.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.676918029785156]
[null,null,null,null,null,"Coincident",31.181243896484375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.099021911621094]
[null,null,null,null,null,"Coincident",31.301513671875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",34.737197875976563]
[null,null,null,null,null,"Coincident",29.141365051269531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.185916900634766]
[null,null,null,null,null,"Coincident",29.253767013549805]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.896764755249023]
[null,null,null,null,null,"Coincident",26.920639038085938]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.282957077026367]
[null,null,null,null,null,"Coincident",27.02447509765625]
[null,null,"Archerfield","Substation Rating","MVA","Non-Coincident",54.799999237060547]
[null,null,null,null,null,"Coincident",54.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.871990203857422]
[null,null,null,null,null,"Coincident",11.920374870300293]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.025510787963867]
[null,null,null,null,null,"Coincident",11.927369117736816]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.91558837890625]
[null,null,null,null,null,"Coincident",12.516392707824707]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.076786041259766]
[null,null,null,null,null,"Coincident",12.523736953735352]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.871990203857422]
[null,null,null,null,null,"Coincident",11.920374870300293]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.025510787963867]
[null,null,null,null,null,"Coincident",11.927369117736816]
[null,null,"Arundel","Substation Rating","MVA","Non-Coincident",53.200000762939453]
[null,null,null,null,null,"Coincident",53.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.208381652832031]
[null,null,null,null,null,"Coincident",20.868003845214844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.312969207763672]
[null,null,null,null,null,"Coincident",20.910343170166016]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.33624267578125]
[null,null,null,null,null,"Coincident",21.977764129638672]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.446392059326172]
[null,null,null,null,null,"Coincident",22.022354125976563]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.727798461914063]
[null,null,null,null,null,"Coincident",20.395133972167969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.83001708984375]
[null,null,null,null,null,"Coincident",20.436513900756836]
[null,null,"Ashgrove","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.475238800048828]
[null,null,null,null,null,"Coincident",22.236150741577148]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.511266708374023]
[null,null,null,null,null,"Coincident",22.27418327331543]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.154937744140625]
[null,null,null,null,null,"Coincident",24.774408340454102]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.195079803466797]
[null,null,null,null,null,"Coincident",24.816781997680664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.932916641235352]
[null,null,null,null,null,"Coincident",20.775236129760742]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.966577529907227]
[null,null,null,null,null,"Coincident",20.810770034790039]
[null,null,"Astor Terrace","Substation Rating","MVA","Non-Coincident",47.160899999999998]
[null,null,null,null,null,"Coincident",47.160899999999998]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.371471405029297]
[null,null,null,null,null,"Coincident",24.604114532470703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.956144332885742]
[null,null,null,null,null,"Coincident",25.129051208496094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.57427978515625]
[null,null,null,null,null,"Coincident",26.659294128417969]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.207790374755859]
[null,null,null,null,null,"Coincident",27.228078842163086]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.710870742797852]
[null,null,null,null,null,"Coincident",24.920768737792969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.303068161010742]
[null,null,null,null,null,"Coincident",25.452461242675781]
[null,null,"Bald Hills Bus 1","Substation Rating","MVA","Non-Coincident",22.100000381469727]
[null,null,null,null,null,"Coincident",22.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.7388391494750977]
[null,null,null,null,null,"Coincident",8.3289833068847656]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.9050712585449219]
[null,null,null,null,null,"Coincident",8.4555683135986328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.29588508605957]
[null,null,null,null,null,"Coincident",9.6606216430664062]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.488694190979004]
[null,null,null,null,null,"Coincident",9.8074445724487305]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.1567487716674805]
[null,null,null,null,null,"Coincident",7.8311600685119629]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.3130455017089844]
[null,null,null,null,null,"Coincident",7.9501791000366211]
[null,null,"Bald Hills Bus 2","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.170110702514648]
[null,null,null,null,null,"Coincident",11.857143402099609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.58714771270752]
[null,null,null,null,null,"Coincident",12.328987121582031]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.921006202697754]
[null,null,null,null,null,"Coincident",12.588728904724121]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.363774299621582]
[null,null,null,null,null,"Coincident",13.089685440063477]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.108024597167969]
[null,null,null,null,null,"Coincident",10.822370529174805]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.488667488098145]
[null,null,null,null,null,"Coincident",11.253036499023437]
[null,null,"Beaudesert","Substation Rating","MVA","Non-Coincident",21]
[null,null,null,null,null,"Coincident",21]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.474688529968262]
[null,null,null,null,null,"Coincident",14.429400444030762]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.851724624633789]
[null,null,null,null,null,"Coincident",14.526595115661621]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.472341537475586]
[null,null,null,null,null,"Coincident",16.420803070068359]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.901411056518555]
[null,null,null,null,null,"Coincident",16.531410217285156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.51710033416748]
[null,null,null,null,null,"Coincident",14.4716796875]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.895240783691406]
[null,null,null,null,null,"Coincident",14.569158554077148]
[null,null,"Beenleigh","Substation Rating","MVA","Non-Coincident",54.900001525878906]
[null,null,null,null,null,"Coincident",54.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.451976776123047]
[null,null,null,null,null,"Coincident",28.796539306640625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.838008880615234]
[null,null,null,null,null,"Coincident",29.09431266784668]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.8096100091934204]
[null,null,null,null,null,"Coincident",1.8129639625549316]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",30.789096832275391]
[null,null,null,null,null,"Coincident",30.103902816772461]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.192655563354492]
[null,null,null,null,null,"Coincident",30.415195465087891]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",27.80413818359375]
[null,null,null,null,null,"Coincident",27.185373306274414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.168573379516602]
[null,null,null,null,null,"Coincident",27.466485977172852]
[null,null,"Beenleigh North","Substation Rating","MVA","Non-Coincident",54.5]
[null,null,null,null,null,"Coincident",54.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.86666202545166]
[null,null,null,null,null,"Coincident",13.007681846618652]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.250422477722168]
[null,null,null,null,null,"Coincident",13.323971748352051]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.278715133666992]
[null,null,null,null,null,"Coincident",12.456155776977539]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.646204948425293]
[null,null,null,null,null,"Coincident",12.759035110473633]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.582609176635742]
[null,null,null,null,null,"Coincident",11.803170204162598]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.93083381652832]
[null,null,null,null,null,"Coincident",12.090171813964844]
[null,null,"Beerwah","Substation Rating","MVA","Non-Coincident",57.157600000000002]
[null,null,null,null,null,"Coincident",57.157600000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.509780883789063]
[null,null,null,null,null,"Coincident",14.86750316619873]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.169713973999023]
[null,null,null,null,null,"Coincident",15.550939559936523]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.368402481079102]
[null,null,null,null,null,"Coincident",15.690567970275879]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.064868927001953]
[null,null,null,null,null,"Coincident",16.411838531494141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.845582008361816]
[null,null,null,null,null,"Coincident",13.272220611572266]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.434703826904297]
[null,null,null,null,null,"Coincident",13.88232421875]
[null,null,"Belmont","Substation Rating","MVA","Non-Coincident",37.898800000000001]
[null,null,null,null,null,"Coincident",37.898800000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.39317798614502]
[null,null,null,null,null,"Coincident",11.130551338195801]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.199142456054687]
[null,null,null,null,null,"Coincident",11.863327026367188]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.7970681190490723]
[null,null,null,null,null,"Coincident",3.7718119621276855]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.713326454162598]
[null,null,null,null,null,"Coincident",11.443320274353027]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.541938781738281]
[null,null,null,null,null,"Coincident",12.196686744689941]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.492774963378906]
[null,null,null,null,null,"Coincident",10.250904083251953]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.235044479370117]
[null,null,null,null,null,"Coincident",10.925768852233887]
[null,null,"Bethania","Substation Rating","MVA","Non-Coincident",47.799999237060547]
[null,null,null,null,null,"Coincident",47.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.881099700927734]
[null,null,null,null,null,"Coincident",17.273948669433594]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.207395553588867]
[null,null,null,null,null,"Coincident",17.599430084228516]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.039436340332031]
[null,null,null,null,null,"Coincident",18.392955780029297]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.386871337890625]
[null,null,null,null,null,"Coincident",18.739521026611328]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.743682861328125]
[null,null,null,null,null,"Coincident",16.175151824951172]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.049222946166992]
[null,null,null,null,null,"Coincident",16.479930877685547]
[null,null,"Birkdale","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.966453552246094]
[null,null,null,null,null,"Coincident",25.341423034667969]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.300703048706055]
[null,null,null,null,null,"Coincident",25.363584518432617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.74513000249862671]
[null,null,null,null,null,"Coincident",0.75517600774765015]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.23192024230957]
[null,null,null,null,null,"Coincident",25.368030548095703]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.592311859130859]
[null,null,null,null,null,"Coincident",25.390216827392578]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.674047470092773]
[null,null,null,null,null,"Coincident",23.941055297851563]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.981845855712891]
[null,null,null,null,null,"Coincident",23.961992263793945]
[null,null,"Birtinya","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.749787330627441]
[null,null,null,null,null,"Coincident",9.7596492767333984]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.757169723510742]
[null,null,null,null,null,"Coincident",9.7605810165405273]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.51225471496582]
[null,null,null,null,null,"Coincident",11.223596572875977]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.520745277404785]
[null,null,null,null,null,"Coincident",11.224667549133301]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.749787330627441]
[null,null,null,null,null,"Coincident",9.7596492767333984]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.757169723510742]
[null,null,null,null,null,"Coincident",9.7605810165405273]
[null,null,"Black Mountain","Substation Rating","MVA","Non-Coincident",17.899999618530273]
[null,null,null,null,null,"Coincident",17.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.6423168182373047]
[null,null,null,null,null,"Coincident",4.2679238319396973]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.767998218536377]
[null,null,null,null,null,"Coincident",4.2921967506408691]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.7146902084350586]
[null,null,null,null,null,"Coincident",4.6588230133056641]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.8423309326171875]
[null,null,null,null,null,"Coincident",4.6853194236755371]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.1749749183654785]
[null,null,null,null,null,"Coincident",4.3320279121398926]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.2880039215087891]
[null,null,null,null,null,"Coincident",4.3566656112670898]
[null,null,"Boonah","Substation Rating","MVA","Non-Coincident",18]
[null,null,null,null,null,"Coincident",18]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.3557891845703125]
[null,null,null,null,null,"Coincident",5.9075260162353516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.5041756629943848]
[null,null,null,null,null,"Coincident",6.1471414566040039]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.1244583129882812]
[null,null,null,null,null,"Coincident",6.6219820976257324]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.2907905578613281]
[null,null,null,null,null,"Coincident",6.8905763626098633]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.2427830696105957]
[null,null,null,null,null,"Coincident",5.802490234375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.3885312080383301]
[null,null,null,null,null,"Coincident",6.0378451347351074]
[null,null,"Booval","Substation Rating","MVA","Non-Coincident",37.200000762939453]
[null,null,null,null,null,"Coincident",37.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.683284759521484]
[null,null,null,null,null,"Coincident",20.302331924438477]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.695047378540039]
[null,null,null,null,null,"Coincident",20.322229385375977]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.83998000621795654]
[null,null,null,null,null,"Coincident",0.8397979736328125]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.563259124755859]
[null,null,null,null,null,"Coincident",22.99888801574707]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.576583862304688]
[null,null,null,null,null,"Coincident",23.021427154541016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.301008224487305]
[null,null,null,null,null,"Coincident",19.944402694702148]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.312564849853516]
[null,null,null,null,null,"Coincident",19.963949203491211]
[null,null,"Brendale","Substation Rating","MVA","Non-Coincident",58.799999237060547]
[null,null,null,null,null,"Coincident",58.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.047866821289063]
[null,null,null,null,null,"Coincident",30.063747406005859]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.055629730224609]
[null,null,null,null,null,"Coincident",30.074542999267578]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.488201141357422]
[null,null,null,null,null,"Coincident",30.476821899414062]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.496070861816406]
[null,null,null,null,null,"Coincident",30.487766265869141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.378387451171875]
[null,null,null,null,null,"Coincident",26.621448516845703]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.385259628295898]
[null,null,null,null,null,"Coincident",26.631008148193359]
[null,null,"Bribie Island","Substation Rating","MVA","Non-Coincident",41.599998474121094]
[null,null,null,null,null,"Coincident",41.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.113433837890625]
[null,null,null,null,null,"Coincident",19.415214538574219]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.599061965942383]
[null,null,null,null,null,"Coincident",19.583572387695313]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.948049545288086]
[null,null,null,null,null,"Coincident",20.846115112304688]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.452873229980469]
[null,null,null,null,null,"Coincident",21.026880264282227]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.645696640014648]
[null,null,null,null,null,"Coincident",19.062828063964844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.074563980102539]
[null,null,null,null,null,"Coincident",19.228130340576172]
[null,null,"Brighton","Substation Rating","MVA","Non-Coincident",35.900001525878906]
[null,null,null,null,null,"Coincident",35.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.6198148727416992]
[null,null,null,null,null,"Coincident",8.9402866363525391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.864875629534966]
[null,null,null,null,null,"Coincident",9.0057153701782227]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02T19:00:00"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42402.791666666664]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.15236759185791]
[null,null,null,null,null,"Coincident",8.5105266571044922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.410995150113068]
[null,null,null,null,null,"Coincident",8.572810173034668]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.4648599624633789]
[null,null,null,null,null,"Coincident",7.9657955169677734]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.6804986925930763]
[null,null,null,null,null,"Coincident",8.0240926742553711]
[null,null,"Brisbane Airport","Substation Rating","MVA","Non-Coincident",52.3]
[null,null,null,null,null,"Coincident",52.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.911504745483398]
[null,null,null,null,null,"Coincident",13.853111267089844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.744989074978944]
[null,null,null,null,null,"Coincident",14.480895470783796]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02T11:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42402.479166666664]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.048244476318359]
[null,null,null,null,null,"Coincident",13.980145454406738]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.889370631745905]
[null,null,null,null,null,"Coincident",14.613685288642351]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.223936080932617]
[null,null,null,null,null,"Coincident",13.21434497833252]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.018987621467872]
[null,null,null,null,null,"Coincident",13.813181373945341]
[null,null,"Broadbeach","Substation Rating","MVA","Non-Coincident",118.202]
[null,null,null,null,null,"Coincident",118.202]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",44.980430603027344]
[null,null,null,null,null,"Coincident",43.213008880615234]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.456027984619141]
[null,null,null,null,null,"Coincident",43.524982452392578]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",52.203388214111328]
[null,null,null,null,null,"Coincident",50.152156829833984]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",52.755359649658203]
[null,null,null,null,null,"Coincident",50.514225006103516]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",46.730171203613281]
[null,null,null,null,null,"Coincident",44.893997192382813]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",47.224269866943359]
[null,null,null,null,null,"Coincident",45.218105316162109]
[null,null,"Bromelton","Substation Rating","MVA","Non-Coincident",31.418099999999999]
[null,null,null,null,null,"Coincident",30.404699999999998]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.4492330551147461]
[null,null,null,null,null,"Coincident",6.4493680000305176]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.5430774688720703]
[null,null,null,null,null,"Coincident",6.4507489204406738]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.6354637145996094]
[null,null,null,null,null,"Coincident",7.0943050384521484]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.731654167175293]
[null,null,null,null,null,"Coincident",7.0958237648010254]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4492330551147461]
[null,null,null,null,null,"Coincident",6.4493680000305176]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.5430774688720703]
[null,null,null,null,null,"Coincident",6.4507489204406738]
[null,null,"Browns Plains","Substation Rating","MVA","Non-Coincident",80.400001525878906]
[null,null,null,null,null,"Coincident",80.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",45.410804748535156]
[null,null,null,null,null,"Coincident",45.058132171630859]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.446590423583984]
[null,null,null,null,null,"Coincident",45.102264404296875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",49.6839599609375]
[null,null,null,null,null,"Coincident",49.298103332519531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.723114013671875]
[null,null,null,null,null,"Coincident",49.346385955810547]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",44.69921875]
[null,null,null,null,null,"Coincident",44.352069854736328]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",44.734443664550781]
[null,null,null,null,null,"Coincident",44.395511627197266]
[null,null,"Bulimba","Substation Rating","MVA","Non-Coincident",58.342100000000002]
[null,null,null,null,null,"Coincident",58.342100000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.173492431640625]
[null,null,null,null,null,"Coincident",21.808403015136719]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.676164627075195]
[null,null,null,null,null,"Coincident",22.395292282104492]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.742536544799805]
[null,null,null,null,null,"Coincident",22.321773529052734]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.257041931152344]
[null,null,null,null,null,"Coincident",22.922477722167969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.52093505859375]
[null,null,null,null,null,"Coincident",19.415367126464844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.968448638916016]
[null,null,null,null,null,"Coincident",19.937856674194336]
[null,null,"Bundall","Substation Rating","MVA","Non-Coincident",45.599998474121094]
[null,null,null,null,null,"Coincident",45.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.147689819335938]
[null,null,null,null,null,"Coincident",18.973590850830078]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.115524291992188]
[null,null,null,null,null,"Coincident",20.892555236816406]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.092485427856445]
[null,null,null,null,null,"Coincident",18.921602249145508]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.054927825927734]
[null,null,null,null,null,"Coincident",20.835309982299805]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.446821212768555]
[null,null,null,null,null,"Coincident",17.37183952331543]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.248531341552734]
[null,null,null,null,null,"Coincident",19.128805160522461]
[null,null,"Bundamba","Substation Rating","MVA","Non-Coincident",114.407]
[null,null,null,null,null,"Coincident",114.407]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.834197998046875]
[null,null,null,null,null,"Coincident",32.910285949707031]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",36.315116882324219]
[null,null,null,null,null,"Coincident",34.991283416748047]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",37.184432983398437]
[null,null,null,null,null,"Coincident",34.150344848632813]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.6834716796875]
[null,null,null,null,null,"Coincident",36.309757232666016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.816505432128906]
[null,null,null,null,null,"Coincident",31.97563362121582]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",35.283767700195312]
[null,null,null,null,null,"Coincident",33.997531890869141]
[null,null,"Buranda","Substation Rating","MVA","Non-Coincident",54.799999237060547]
[null,null,null,null,null,"Coincident",54.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.044975280761719]
[null,null,null,null,null,"Coincident",15.75883674621582]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.525978088378906]
[null,null,null,null,null,"Coincident",16.133848190307617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.580007553100586]
[null,null,null,null,null,"Coincident",16.226085662841797]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.075273513793945]
[null,null,null,null,null,"Coincident",16.612216949462891]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.045284271240234]
[null,null,null,null,null,"Coincident",14.885796546936035]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.499639511108398]
[null,null,null,null,null,"Coincident",15.240033149719238]
[null,null,"Burleigh Heads","Substation Rating","MVA","Non-Coincident",120.41200000000001]
[null,null,null,null,null,"Coincident",129.86199999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",48.360233306884766]
[null,null,null,null,null,"Coincident",47.506935119628906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",48.602184295654297]
[null,null,null,null,null,"Coincident",48.131969451904297]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",50.474544525146484]
[null,null,null,null,null,"Coincident",48.607192993164063]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",50.727073669433594]
[null,null,null,null,null,"Coincident",49.2467041015625]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",46.451938629150391]
[null,null,null,null,null,"Coincident",46.164390563964844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.684341430664063]
[null,null,null,null,null,"Coincident",46.771759033203125]
[null,null,"Burpengary","Substation Rating","MVA","Non-Coincident",59.599998474121094]
[null,null,null,null,null,"Coincident",59.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.369489669799805]
[null,null,null,null,null,"Coincident",16.284910202026367]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.66148567199707]
[null,null,null,null,null,"Coincident",16.618917465209961]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.060829162597656]
[null,null,null,null,null,"Coincident",16.837619781494141]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.362735748291016]
[null,null,null,null,null,"Coincident",17.182962417602539]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.999092102050781]
[null,null,null,null,null,"Coincident",14.389834403991699]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.257108688354492]
[null,null,null,null,null,"Coincident",14.68497371673584]
[null,null,"Caboolture","Substation Rating","MVA","Non-Coincident",59.200000762939453]
[null,null,null,null,null,"Coincident",59.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.422189712524414]
[null,null,null,null,null,"Coincident",18.502140045166016]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.071516036987305]
[null,null,null,null,null,"Coincident",19.004499435424805]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.450159072875977]
[null,null,null,null,null,"Coincident",18.528783798217773]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.100419998168945]
[null,null,null,null,null,"Coincident",19.031866073608398]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.347705841064453]
[null,null,null,null,null,"Coincident",16.52592658996582]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.927677154541016]
[null,null,null,null,null,"Coincident",16.974628448486328]
[null,null,"Caboolture West","Substation Rating","MVA","Non-Coincident",39.999899999999997]
[null,null,null,null,null,"Coincident",39.999899999999997]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.947509765625]
[null,null,null,null,null,"Coincident",19.318161010742188]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.130332946777344]
[null,null,null,null,null,"Coincident",19.383768081665039]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.788619995117188]
[null,null,null,null,null,"Coincident",21.938283920288086]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.996240615844727]
[null,null,null,null,null,"Coincident",22.012788772583008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.599990844726562]
[null,null,null,null,null,"Coincident",18.997673034667969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.779781341552734]
[null,null,null,null,null,"Coincident",19.062191009521484]
[null,null,"Cades County","Substation Rating","MVA","Non-Coincident",126.774]
[null,null,null,null,null,"Coincident",126.774]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",59.987957000732422]
[null,null,null,null,null,"Coincident",59.987957000732422]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",60.1868896484375]
[null,null,null,null,null,"Coincident",60.1868896484375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",68.956756591796875]
[null,null,null,null,null,"Coincident",68.956756591796875]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",69.185432434082031]
[null,null,null,null,null,"Coincident",69.185432434082031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",58.998756408691406]
[null,null,null,null,null,"Coincident",58.998756408691406]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",59.194408416748047]
[null,null,null,null,null,"Coincident",59.194408416748047]
[null,null,"Calamvale","Substation Rating","MVA","Non-Coincident",59.099998474121094]
[null,null,null,null,null,"Coincident",59.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.205089569091797]
[null,null,null,null,null,"Coincident",32.057914733886719]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.246479034423828]
[null,null,null,null,null,"Coincident",32.096263885498047]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",37.212398529052734]
[null,null,null,null,null,"Coincident",34.876445770263672]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.257427215576172]
[null,null,null,null,null,"Coincident",34.918167114257812]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.958656311035156]
[null,null,null,null,null,"Coincident",30.889724731445313]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",32.99853515625]
[null,null,null,null,null,"Coincident",30.926675796508789]
[null,null,"Caloundra","Substation Rating","MVA","Non-Coincident",115.077]
[null,null,null,null,null,"Coincident",121.93600000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",45.952873229980469]
[null,null,null,null,null,"Coincident",40.958217620849609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.955135345458984]
[null,null,null,null,null,"Coincident",41.284255981445313]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",45.485992431640625]
[null,null,null,null,null,"Coincident",45.461166381835938]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",45.488231658935547]
[null,null,null,null,null,"Coincident",45.823047637939453]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",41.039131164550781]
[null,null,null,null,null,"Coincident",41.666385650634766]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",41.041152954101563]
[null,null,null,null,null,"Coincident",41.998062133789063]
[null,null,"Camp Hill","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.548671722412109]
[null,null,null,null,null,"Coincident",28.308149337768555]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.078819274902344]
[null,null,null,null,null,"Coincident",28.444984436035156]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.194568634033203]
[null,null,null,null,null,"Coincident",29.619098663330078]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.752372741699219]
[null,null,null,null,null,"Coincident",29.762269973754883]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.213661193847656]
[null,null,null,null,null,"Coincident",26.790266036987305]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.687767028808594]
[null,null,null,null,null,"Coincident",26.919765472412109]
[null,null,"Capalaba","Substation Rating","MVA","Non-Coincident",29.299999237060547]
[null,null,null,null,null,"Coincident",29.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.516571044921875]
[null,null,null,null,null,"Coincident",16.419601440429688]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.554439544677734]
[null,null,null,null,null,"Coincident",16.427509307861328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.797536849975586]
[null,null,null,null,null,"Coincident",16.682971954345703]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.83601188659668]
[null,null,null,null,null,"Coincident",16.691005706787109]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.478713989257813]
[null,null,null,null,null,"Coincident",15.44674015045166]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.514339447021484]
[null,null,null,null,null,"Coincident",15.454179763793945]
[null,null,"Capalaba South","Substation Rating","MVA","Non-Coincident",59.799999237060547]
[null,null,null,null,null,"Coincident",59.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.304111480712891]
[null,null,null,null,null,"Coincident",14.10936164855957]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.967931747436523]
[null,null,null,null,null,"Coincident",14.676005363464355]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.251123428344727]
[null,null,null,null,null,"Coincident",14.063506126403809]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.912786483764648]
[null,null,null,null,null,"Coincident",14.628308296203613]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.580114364624023]
[null,null,null,null,null,"Coincident",12.617437362670898]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.173742294311523]
[null,null,null,null,null,"Coincident",13.124164581298828]
[null,null,"Carole Park","Substation Rating","MVA","Non-Coincident",42.138399999999997]
[null,null,null,null,null,"Coincident",42.138399999999997]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.658382415771484]
[null,null,null,null,null,"Coincident",17.518543243408203]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.80122184753418]
[null,null,null,null,null,"Coincident",17.534660339355469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-12"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.871923446655273]
[null,null,null,null,null,"Coincident",18.657949447631836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.024053573608398]
[null,null,null,null,null,"Coincident",18.675113677978516]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.784139633178711]
[null,null,null,null,null,"Coincident",17.636617660522461]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.927942276000977]
[null,null,null,null,null,"Coincident",17.652843475341797]
[null,null,"Carole Park Central","Substation Rating","MVA","Non-Coincident",52.400001525878906]
[null,null,null,null,null,"Coincident",52.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.432336807250977]
[null,null,null,null,null,"Coincident",16.985429763793945]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.584079920316004]
[null,null,null,null,null,"Coincident",17.224792125200153]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-17T13:30:00"]
[null,null,null,null,null,"Coincident","2015-07-17T18:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42417.5625]
[null,null,null,null,null,"Coincident",42202.770833333328]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.730014801025391]
[null,null,null,null,null,"Coincident",17.553762435913086]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.88377066076437]
[null,null,null,null,null,"Coincident",17.801133646752838]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.460342407226563]
[null,null,null,null,null,"Coincident",16.903049468994141]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.605511763321829]
[null,null,null,null,null,"Coincident",17.141251880928905]
[null,null,"Carpendale","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5561219453811646]
[null,null,null,null,null,"Coincident",1.1412299871444702]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5865508317947388]
[null,null,null,null,null,"Coincident",1.1412502527236938]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-18"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.7119207382202148]
[null,null,null,null,null,"Coincident",1.2007451057434082]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.7453962564468384]
[null,null,null,null,null,"Coincident",1.2007664442062378]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5402339696884155]
[null,null,null,null,null,"Coincident",1.1400202512741089]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5703521966934204]
[null,null,null,null,null,"Coincident",1.1400405168533325]
[null,null,"Charlotte St","Substation Rating","MVA","Non-Coincident",186.89999389648437]
[null,null,null,null,null,"Coincident",186.89999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",90.2269287109375]
[null,null,null,null,null,"Coincident",84.77740478515625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",90.897315979003906]
[null,null,null,null,null,"Coincident",84.781455993652344]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",95.640541076660156]
[null,null,null,null,null,"Coincident",89.864044189453125]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",96.351150512695312]
[null,null,null,null,null,"Coincident",89.868339538574219]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",90.2269287109375]
[null,null,null,null,null,"Coincident",84.77740478515625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",90.897315979003906]
[null,null,null,null,null,"Coincident",84.781455993652344]
[null,null,"Chermside","Substation Rating","MVA","Non-Coincident",65.400001525878906]
[null,null,null,null,null,"Coincident",65.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38.33837890625]
[null,null,null,null,null,"Coincident",37.959182739257813]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.710872650146484]
[null,null,null,null,null,"Coincident",38.297687530517578]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",39.993446350097656]
[null,null,null,null,null,"Coincident",39.597881317138672]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",40.38201904296875]
[null,null,null,null,null,"Coincident",39.950996398925781]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",36.384269714355469]
[null,null,null,null,null,"Coincident",36.024402618408203]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",36.737777709960937]
[null,null,null,null,null,"Coincident",36.345653533935547]
[null,null,"Clayfield","Substation Rating","MVA","Non-Coincident",36.009399999999999]
[null,null,null,null,null,"Coincident",36.009399999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.801097869873047]
[null,null,null,null,null,"Coincident",16.867809295654297]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.646266937255859]
[null,null,null,null,null,"Coincident",17.536338806152344]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.800273895263672]
[null,null,null,null,null,"Coincident",17.814599990844727]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.692882537841797]
[null,null,null,null,null,"Coincident",18.520654678344727]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.837347030639648]
[null,null,null,null,null,"Coincident",15.954586982727051]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.636758804321289]
[null,null,null,null,null,"Coincident",16.586921691894531]
[null,null,"Cleveland","Substation Rating","MVA","Non-Coincident",65]
[null,null,null,null,null,"Coincident",65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.51121711730957]
[null,null,null,null,null,"Coincident",19.541309356689453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.871196746826172]
[null,null,null,null,null,"Coincident",19.666313171386719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.747037887573242]
[null,null,null,null,null,"Coincident",20.297754287719727]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.12769889831543]
[null,null,null,null,null,"Coincident",20.427597045898438]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.272602081298828]
[null,null,null,null,null,"Coincident",19.133090972900391]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.611852645874023]
[null,null,null,null,null,"Coincident",19.255483627319336]
[null,null,"Coolum","Substation Rating","MVA","Non-Coincident",59.5]
[null,null,null,null,null,"Coincident",59.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.380796432495117]
[null,null,null,null,null,"Coincident",19.062900543212891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.71788215637207]
[null,null,null,null,null,"Coincident",19.142431259155273]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.933937072753906]
[null,null,null,null,null,"Coincident",21.769830703735352]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.263978958129883]
[null,null,null,null,null,"Coincident",21.860654830932617]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.839260101318359]
[null,null,null,null,null,"Coincident",19.738489151000977]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.136276245117188]
[null,null,null,null,null,"Coincident",19.820838928222656]
[null,null,"Coomera","Substation Rating","MVA","Non-Coincident",59]
[null,null,null,null,null,"Coincident",59]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.438503265380859]
[null,null,null,null,null,"Coincident",28.8646240234375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.827911376953125]
[null,null,null,null,null,"Coincident",29.312728881835938]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.082401275634766]
[null,null,null,null,null,"Coincident",32.437488555908203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.520011901855469]
[null,null,null,null,null,"Coincident",32.941059112548828]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.524436950683594]
[null,null,null,null,null,"Coincident",27.968376159667969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.901754379272461]
[null,null,null,null,null,"Coincident",28.402568817138672]
[null,null,"Coominya","Substation Rating","MVA","Non-Coincident",12.65]
[null,null,null,null,null,"Coincident",12.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.1399998664855957]
[null,null,null,null,null,"Coincident",6.072361946105957]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.2659473419189453]
[null,null,null,null,null,"Coincident",6.1974903247167097]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.6176304817199707]
[null,null,null,null,null,"Coincident",6.5447311401367188]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.7533755302429199]
[null,null,null,null,null,"Coincident",6.679593094254213]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.1288862228393555]
[null,null,null,null,null,"Coincident",6.061370849609375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.254605770111084]
[null,null,null,null,null,"Coincident",6.1862728669486904]
[null,null,"Cooneana","Substation Rating","MVA","Non-Coincident",26.299999237060547]
[null,null,null,null,null,"Coincident",26.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2796599864959717]
[null,null,null,null,null,"Coincident",3.1123080253601074]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.3970460891723633]
[null,null,null,null,null,"Coincident",3.26279616355896]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.9355921745300293]
[null,null,null,null,null,"Coincident",3.7347698211669922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.0764555931091309]
[null,null,null,null,null,"Coincident",3.9153554439544678]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2796599864959717]
[null,null,null,null,null,"Coincident",3.1123080253601074]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3970460891723633]
[null,null,null,null,null,"Coincident",3.26279616355896]
[null,null,"Coopers Plains","Substation Rating","MVA","Non-Coincident",52.099998474121094]
[null,null,null,null,null,"Coincident",52.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.99591064453125]
[null,null,null,null,null,"Coincident",15.95042610168457]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.531562805175781]
[null,null,null,null,null,"Coincident",16.085657119750977]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.995704650878906]
[null,null,null,null,null,"Coincident",16.747945785522461]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.558139801025391]
[null,null,null,null,null,"Coincident",16.889938354492187]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.99591064453125]
[null,null,null,null,null,"Coincident",15.95042610168457]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.531562805175781]
[null,null,null,null,null,"Coincident",16.085657119750977]
[null,null,"Cooran","Substation Rating","MVA","Non-Coincident",36]
[null,null,null,null,null,"Coincident",36]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1892280578613281]
[null,null,null,null,null,"Coincident",5.0135002136230469]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.2370381355285645]
[null,null,null,null,null,"Coincident",5.0739312171936035]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.0232405662536621]
[null,null,null,null,null,"Coincident",5.819270133972168]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0787348747253418]
[null,null,null,null,null,"Coincident",5.8894133567810059]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.462803840637207]
[null,null,null,null,null,"Coincident",5.2778115272521973]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.5131344795227051]
[null,null,null,null,null,"Coincident",5.3414287567138672]
[null,null,"Cooroy","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.3278069496154785]
[null,null,null,null,null,"Coincident",5.3278069496154785]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3554062843322754]
[null,null,null,null,null,"Coincident",5.3554062843322754]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.6176395416259766]
[null,null,null,null,null,"Coincident",5.6176395416259766]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.6467404365539551]
[null,null,null,null,null,"Coincident",5.6467404365539551]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.2287096977233887]
[null,null,null,null,null,"Coincident",5.2287096977233887]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.255795955657959]
[null,null,null,null,null,"Coincident",5.255795955657959]
[null,null,"Coorparoo","Substation Rating","MVA","Non-Coincident",54.599998474121094]
[null,null,null,null,null,"Coincident",54.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.030235290527344]
[null,null,null,null,null,"Coincident",16.657501220703125]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.737432479858398]
[null,null,null,null,null,"Coincident",17.263820648193359]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.435911178588867]
[null,null,null,null,null,"Coincident",18.032411575317383]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.201480865478516]
[null,null,null,null,null,"Coincident",18.688777923583984]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.287376403808594]
[null,null,null,null,null,"Coincident",15.930901527404785]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.963726043701172]
[null,null,null,null,null,"Coincident",16.510772705078125]
[null,null,"Cornubia","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.255217552185059]
[null,null,null,null,null,"Coincident",9.8770971298217773]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.371711730957031]
[null,null,null,null,null,"Coincident",10.035347938537598]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.568193435668945]
[null,null,null,null,null,"Coincident",11.14166259765625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.699603080749512]
[null,null,null,null,null,"Coincident",11.320174217224121]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.094723701477051]
[null,null,null,null,null,"Coincident",9.7225208282470703]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.209394454956055]
[null,null,null,null,null,"Coincident",9.8782949447631836]
[null,null,"Crestmead","Substation Rating","MVA","Non-Coincident",51.5]
[null,null,null,null,null,"Coincident",51.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.095905303955078]
[null,null,null,null,null,"Coincident",20.098976135253906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.177209854125977]
[null,null,null,null,null,"Coincident",20.104597091674805]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.3340239524841309]
[null,null,null,null,null,"Coincident",3.3390998840332031]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.547765731811523]
[null,null,null,null,null,"Coincident",20.510000228881836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.630733489990234]
[null,null,null,null,null,"Coincident",20.515735626220703]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.046791076660156]
[null,null,null,null,null,"Coincident",19.144676208496094]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.124237060546875]
[null,null,null,null,null,"Coincident",19.150030136108398]
[null,null,"Currimundi","Substation Rating","MVA","Non-Coincident",72]
[null,null,null,null,null,"Coincident",72]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.026103973388672]
[null,null,null,null,null,"Coincident",13.910948753356934]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.056817054748535]
[null,null,null,null,null,"Coincident",13.966837882995605]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.675382614135742]
[null,null,null,null,null,"Coincident",14.512041091918945]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.707422256469727]
[null,null,null,null,null,"Coincident",14.570344924926758]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.218601226806641]
[null,null,null,null,null,"Coincident",13.163373947143555]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.247663497924805]
[null,null,null,null,null,"Coincident",13.216259956359863]
[null,null,"Currumbin","Substation Rating","MVA","Non-Coincident",37.5]
[null,null,null,null,null,"Coincident",37.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.379222869873047]
[null,null,null,null,null,"Coincident",19.598991394042969]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.727565765380859]
[null,null,null,null,null,"Coincident",19.845075607299805]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.508781433105469]
[null,null,null,null,null,"Coincident",19.717761993408203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.859235763549805]
[null,null,null,null,null,"Coincident",19.965337753295898]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.41651725769043]
[null,null,null,null,null,"Coincident",18.716449737548828]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.749174118041992]
[null,null,null,null,null,"Coincident",18.951452255249023]
[null,null,"Darra","Substation Rating","MVA","Non-Coincident",52.200000762939453]
[null,null,null,null,null,"Coincident",52.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.411296844482422]
[null,null,null,null,null,"Coincident",15.615945816040039]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.504959106445313]
[null,null,null,null,null,"Coincident",15.626218795776367]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.983335494995117]
[null,null,null,null,null,"Coincident",16.101133346557617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.07990837097168]
[null,null,null,null,null,"Coincident",16.111724853515625]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.063138961791992]
[null,null,null,null,null,"Coincident",15.320648193359375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.155031204223633]
[null,null,null,null,null,"Coincident",15.330727577209473]
[null,null,"Deception Bay","Substation Rating","MVA","Non-Coincident",42.799999237060547]
[null,null,null,null,null,"Coincident",42.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.24737548828125]
[null,null,null,null,null,"Coincident",22.388799667358398]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.276309967041016]
[null,null,null,null,null,"Coincident",22.657384872436523]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.210201263427734]
[null,null,null,null,null,"Coincident",22.464027404785156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.243194580078125]
[null,null,null,null,null,"Coincident",22.733514785766602]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.988716125488281]
[null,null,null,null,null,"Coincident",21.394737243652344]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.015336990356445]
[null,null,null,null,null,"Coincident",21.651397705078125]
[null,null,"Doboy","Substation Rating","MVA","Non-Coincident",52.299999237060547]
[null,null,null,null,null,"Coincident",52.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.243780136108398]
[null,null,null,null,null,"Coincident",11.773059844970703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.248476982116699]
[null,null,null,null,null,"Coincident",12.482491493225098]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-04"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.243780136108398]
[null,null,null,null,null,"Coincident",11.773059844970703]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.248476982116699]
[null,null,null,null,null,"Coincident",12.482491493225098]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.389153480529785]
[null,null,null,null,null,"Coincident",11.066676139831543]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.333568572998047]
[null,null,null,null,null,"Coincident",11.733542442321777]
[null,null,"Duffield Road","Substation Rating","MVA","Non-Coincident",54.962699999999998]
[null,null,null,null,null,"Coincident",59.933399999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.438266754150391]
[null,null,null,null,null,"Coincident",20.935447692871094]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.909725189208984]
[null,null,null,null,null,"Coincident",21.060430526733398]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.137195587158203]
[null,null,null,null,null,"Coincident",20.95366096496582]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.622713088989258]
[null,null,null,null,null,"Coincident",21.078752517700195]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.986623764038086]
[null,null,null,null,null,"Coincident",19.705070495605469]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.408767700195313]
[null,null,null,null,null,"Coincident",19.822708129882813]
[null,null,"Eight Mile Plains Bus 1","Substation Rating","MVA","Non-Coincident",26.200000762939453]
[null,null,null,null,null,"Coincident",26.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.892890930175781]
[null,null,null,null,null,"Coincident",13.544323921203613]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.502185821533203]
[null,null,null,null,null,"Coincident",14.228655815124512]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.933608055114746]
[null,null,null,null,null,"Coincident",14.558929443359375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.588544845581055]
[null,null,null,null,null,"Coincident",15.294525146484375]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.407612800598145]
[null,null,null,null,null,"Coincident",13.071220397949219]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.995624542236328]
[null,null,null,null,null,"Coincident",13.731649398803711]
[null,null,"Eight Mile Plains Bus 2","Substation Rating","MVA","Non-Coincident",27.5]
[null,null,null,null,null,"Coincident",27.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.161579132080078]
[null,null,null,null,null,"Coincident",14.280588150024414]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.701379776000977]
[null,null,null,null,null,"Coincident",14.826641082763672]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.729379653930664]
[null,null,null,null,null,"Coincident",14.815395355224609]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.289396286010742]
[null,null,null,null,null,"Coincident",15.381897926330566]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.655124664306641]
[null,null,null,null,null,"Coincident",12.861669540405273]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.141290664672852]
[null,null,null,null,null,"Coincident",13.353466033935547]
[null,null,"Enoggera","Substation Rating","MVA","Non-Coincident",55.0092]
[null,null,null,null,null,"Coincident",55.0092]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.353763580322266]
[null,null,null,null,null,"Coincident",16.353763580322266]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.843992233276367]
[null,null,null,null,null,"Coincident",16.843992233276367]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.178810119628906]
[null,null,null,null,null,"Coincident",17.178810119628906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.693771362304688]
[null,null,null,null,null,"Coincident",17.693771362304688]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.039411544799805]
[null,null,null,null,null,"Coincident",15.039411544799805]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.490240097045898]
[null,null,null,null,null,"Coincident",15.490240097045898]
[null,null,"Esk","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5186009407043457]
[null,null,null,null,null,"Coincident",2.3577160835266113]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6596698760986328]
[null,null,null,null,null,"Coincident",2.4695801734924316]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.0687642097473145]
[null,null,null,null,null,"Coincident",2.8727357387542725]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.2406482696533203]
[null,null,null,null,null,"Coincident",3.0090353488922119]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5841350555419922]
[null,null,null,null,null,"Coincident",2.4190640449523926]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.728874683380127]
[null,null,null,null,null,"Coincident",2.5338387489318848]
[null,null,"Eumundi","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8173530101776123]
[null,null,null,null,null,"Coincident",2.4297549724578857]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8285483877250845]
[null,null,null,null,null,"Coincident",2.4438387807002697]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02T18:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42402.770833333328]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.2855970859527588]
[null,null,null,null,null,"Coincident",2.8335802555084229]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.2986531214701382]
[null,null,null,null,null,"Coincident",2.8500047788859786]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.926131010055542]
[null,null,null,null,null,"Coincident",2.5235676765441895]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9377586414370995]
[null,null,null,null,null,"Coincident",2.538195396422227]
[null,null,"Fisherman Is A","Substation Rating","MVA","Non-Coincident",37.799999237060547]
[null,null,null,null,null,"Coincident",37.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.306955337524414]
[null,null,null,null,null,"Coincident",8.9510469436645508]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.096549987792969]
[null,null,null,null,null,"Coincident",9.5104856491088867]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-03"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.564628601074219]
[null,null,null,null,null,"Coincident",9.1748228073120117]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.373963356018066]
[null,null,null,null,null,"Coincident",9.7482471466064453]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.306955337524414]
[null,null,null,null,null,"Coincident",8.9510469436645508]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.096549987792969]
[null,null,null,null,null,"Coincident",9.5104856491088867]
[null,null,"Fisherman Is B","Substation Rating","MVA","Non-Coincident",26.299999237060547]
[null,null,null,null,null,"Coincident",26.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.8916680812835693]
[null,null,null,null,null,"Coincident",2.1069190502166748]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.2268304824829102]
[null,null,null,null,null,"Coincident",2.3281373977661133]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-22"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0473346710205078]
[null,null,null,null,null,"Coincident",2.1911957263946533]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3959035873413086]
[null,null,null,null,null,"Coincident",2.4212627410888672]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.969501256942749]
[null,null,null,null,null,"Coincident",2.1490573883056641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.3113670349121094]
[null,null,null,null,null,"Coincident",2.3747000694274902]
[null,null,"Flinders","Substation Rating","MVA","Non-Coincident",11.899999618530273]
[null,null,null,null,null,"Coincident",11.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.1177229881286621]
[null,null,null,null,null,"Coincident",3.0979318618774414]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.3973641395568848]
[null,null,null,null,null,"Coincident",3.2866733074188232]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2320308685302734]
[null,null,null,null,null,"Coincident",3.1839306354522705]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.519434928894043]
[null,null,null,null,null,"Coincident",3.3779115676879883]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7274041175842285]
[null,null,null,null,null,"Coincident",2.8042788505554199]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9805381298065186]
[null,null,null,null,null,"Coincident",2.9751296043395996]
[null,null,"Gatton A","Substation Rating","MVA","Non-Coincident",59.799999237060547]
[null,null,null,null,null,"Coincident",59.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.228116989135742]
[null,null,null,null,null,"Coincident",13.995426177978516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.246425628662109]
[null,null,null,null,null,"Coincident",14.228370666503906]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.323057174682617]
[null,null,null,null,null,"Coincident",14.203258514404297]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.343591690063477]
[null,null,null,null,null,"Coincident",14.439661979675293]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.031543731689453]
[null,null,null,null,null,"Coincident",13.660796165466309]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.049644470214844]
[null,null,null,null,null,"Coincident",13.88817024230957]
[null,null,"Gaven","Substation Rating","MVA","Non-Coincident",59.799999237060547]
[null,null,null,null,null,"Coincident",59.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.648584365844727]
[null,null,null,null,null,"Coincident",21.163734436035156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.239606857299805]
[null,null,null,null,null,"Coincident",21.830039978027344]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.864151000976563]
[null,null,null,null,null,"Coincident",22.352077484130859]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.488359451293945]
[null,null,null,null,null,"Coincident",23.055795669555664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.005023956298828]
[null,null,null,null,null,"Coincident",19.556983947753906]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.551176071166992]
[null,null,null,null,null,"Coincident",20.172702789306641]
[null,null,"Geebung","Substation Rating","MVA","Non-Coincident",78.699996948242188]
[null,null,null,null,null,"Coincident",78.699996948242188]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.432060241699219]
[null,null,null,null,null,"Coincident",30.314502716064453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",35.870601654052734]
[null,null,null,null,null,"Coincident",30.511899948120117]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",36.578639984130859]
[null,null,null,null,null,"Coincident",31.295478820800781]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.0313720703125]
[null,null,null,null,null,"Coincident",31.499263763427734]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.132411956787109]
[null,null,null,null,null,"Coincident",29.202568054199219]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.554866790771484]
[null,null,null,null,null,"Coincident",29.392723083496094]
[null,null,"Gibson Island","Substation Rating","MVA","Non-Coincident",39.661799999999999]
[null,null,null,null,null,"Coincident",39.661799999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.103713989257813]
[null,null,null,null,null,"Coincident",17.284904479980469]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.27509880065918]
[null,null,null,null,null,"Coincident",17.286052703857422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-08-04"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.314750671386719]
[null,null,null,null,null,"Coincident",17.457754135131836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.487850189208984]
[null,null,null,null,null,"Coincident",17.458913803100586]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.103713989257813]
[null,null,null,null,null,"Coincident",17.284904479980469]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.27509880065918]
[null,null,null,null,null,"Coincident",17.286052703857422]
[null,null,"Glenore Grove","Substation Rating","MVA","Non-Coincident",17.100000381469727]
[null,null,null,null,null,"Coincident",17.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.663416862487793]
[null,null,null,null,null,"Coincident",5.6204538345336914]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.1343498229980469]
[null,null,null,null,null,"Coincident",6.0138740539550781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.7237272262573242]
[null,null,null,null,null,"Coincident",6.3980998992919922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.2598190307617187]
[null,null,null,null,null,"Coincident",6.8459539413452148]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.546013355255127]
[null,null,null,null,null,"Coincident",5.5343484878540039]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.0097312927246094]
[null,null,null,null,null,"Coincident",5.9217414855957031]
[null,null,"Goodna","Substation Rating","MVA","Non-Coincident",27.5]
[null,null,null,null,null,"Coincident",27.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.384957313537598]
[null,null,null,null,null,"Coincident",10.922150611877441]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.547518730163574]
[null,null,null,null,null,"Coincident",11.117935180664063]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.824746131896973]
[null,null,null,null,null,"Coincident",11.309995651245117]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.993080139160156]
[null,null,null,null,null,"Coincident",11.51273250579834]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.401467323303223]
[null,null,null,null,null,"Coincident",10.05482292175293]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.551119804382324]
[null,null,null,null,null,"Coincident",10.23505973815918]
[null,null,"Goomboorian","Substation Rating","MVA","Non-Coincident",8.8000001907348633]
[null,null,null,null,null,"Coincident",8.8000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0924220085144043]
[null,null,null,null,null,"Coincident",1.5541759729385376]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.108198881149292]
[null,null,null,null,null,"Coincident",1.5673897266387939]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5112202167510986]
[null,null,null,null,null,"Coincident",1.8652442693710327]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5301549434661865]
[null,null,null,null,null,"Coincident",1.8811028003692627]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2151217460632324]
[null,null,null,null,null,"Coincident",1.6453129053115845]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2318236827850342]
[null,null,null,null,null,"Coincident",1.6593015193939209]
[null,null,"Grantham","Substation Rating","MVA","Non-Coincident",5.25]
[null,null,null,null,null,"Coincident",5.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.3041999340057373]
[null,null,null,null,null,"Coincident",2.5950000286102295]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.3605082947107761]
[null,null,null,null,null,"Coincident",2.617023232097905]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-12-10T12:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42348.520833333328]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5685360431671143]
[null,null,null,null,null,"Coincident",2.8026001453399658]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.6293489522785811]
[null,null,null,null,null,"Coincident",2.8263850859861352]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3041999340057373]
[null,null,null,null,null,"Coincident",2.5950000286102295]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3605082947107761]
[null,null,null,null,null,"Coincident",2.617023232097905]
[null,null,"Grovely","Substation Rating","MVA","Non-Coincident",59.799999237060547]
[null,null,null,null,null,"Coincident",59.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.433017730712891]
[null,null,null,null,null,"Coincident",21.748458862304688]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.447238922119141]
[null,null,null,null,null,"Coincident",21.758955001831055]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.702342987060547]
[null,null,null,null,null,"Coincident",23.94853401184082]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.718002319335937]
[null,null,null,null,null,"Coincident",23.960092544555664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.483364105224609]
[null,null,null,null,null,"Coincident",19.858299255371094]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.496349334716797]
[null,null,null,null,null,"Coincident",19.867883682250977]
[null,null,"Gympie","Substation Rating","MVA","Non-Coincident",55]
[null,null,null,null,null,"Coincident",55]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.110774993896484]
[null,null,null,null,null,"Coincident",20.084739685058594]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.824806213378906]
[null,null,null,null,null,"Coincident",21.714427947998047]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.521442413330078]
[null,null,null,null,null,"Coincident",21.366146087646484]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.344827651977539]
[null,null,null,null,null,"Coincident",23.099807739257812]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.603925704956055]
[null,null,null,null,null,"Coincident",18.715965270996094]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.201145172119141]
[null,null,null,null,null,"Coincident",20.234590530395508]
[null,null,"Gympie North","Substation Rating","MVA","Non-Coincident",55.306100000000001]
[null,null,null,null,null,"Coincident",55.306100000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.292098045349121]
[null,null,null,null,null,"Coincident",13.328668594360352]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.676513671875]
[null,null,null,null,null,"Coincident",13.736078262329102]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.766023635864258]
[null,null,null,null,null,"Coincident",13.770647048950195]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.163186073303223]
[null,null,null,null,null,"Coincident",14.191566467285156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.230910301208496]
[null,null,null,null,null,"Coincident",12.339015007019043]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.586782455444336]
[null,null,null,null,null,"Coincident",12.716175079345703]
[null,null,"Gympie South","Substation Rating","MVA","Non-Coincident",15.800000190734863]
[null,null,null,null,null,"Coincident",15.800000190734863]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.3182997703552246]
[null,null,null,null,null,"Coincident",5.9081740379333496]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.5140490531921387]
[null,null,null,null,null,"Coincident",6.0386919975280762]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-06-10"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.5012569427490234]
[null,null,null,null,null,"Coincident",6.2035822868347168]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.7019000053405762]
[null,null,null,null,null,"Coincident",6.3406262397766113]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3182997703552246]
[null,null,null,null,null,"Coincident",5.9081740379333496]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.5140490531921387]
[null,null,null,null,null,"Coincident",6.0386919975280762]
[null,null,"Hamilton","Substation Rating","MVA","Non-Coincident",54.900001525878906]
[null,null,null,null,null,"Coincident",54.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.665130615234375]
[null,null,null,null,null,"Coincident",19.278036117553711]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.094375610351563]
[null,null,null,null,null,"Coincident",19.284460067749023]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.399595260620117]
[null,null,null,null,null,"Coincident",20.978359222412109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.86669921875]
[null,null,null,null,null,"Coincident",20.985349655151367]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.821693420410156]
[null,null,null,null,null,"Coincident",18.451200485229492]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.232526779174805]
[null,null,null,null,null,"Coincident",18.45734977722168]
[null,null,"Hamilton Lands","Substation Rating","MVA","Non-Coincident",52.400001525878906]
[null,null,null,null,null,"Coincident",52.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.617154121398926]
[null,null,null,null,null,"Coincident",9.2519817352294922]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.705963134765625]
[null,null,null,null,null,"Coincident",9.2693061828613281]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-18"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.248011589050293]
[null,null,null,null,null,"Coincident",9.7145805358886719]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.34126091003418]
[null,null,null,null,null,"Coincident",9.7327709197998047]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.617154121398926]
[null,null,null,null,null,"Coincident",9.2519817352294922]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.705963134765625]
[null,null,null,null,null,"Coincident",9.2693061828613281]
[null,null,"Heathwood","Substation Rating","MVA","Non-Coincident",52.099998474121094]
[null,null,null,null,null,"Coincident",52.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.363239288330078]
[null,null,null,null,null,"Coincident",24.616710662841797]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.816871643066406]
[null,null,null,null,null,"Coincident",25.097341537475586]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.760248184204102]
[null,null,null,null,null,"Coincident",25.972600936889648]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.238866806030273]
[null,null,null,null,null,"Coincident",26.479703903198242]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.613248825073242]
[null,null,null,null,null,"Coincident",23.888795852661133]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.053466796875]
[null,null,null,null,null,"Coincident",24.355213165283203]
[null,null,"Helidon","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0872039794921875]
[null,null,null,null,null,"Coincident",2.5217149257659912]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.1961276531219482]
[null,null,null,null,null,"Coincident",2.6100280284881592]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-17"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5727283954620361]
[null,null,null,null,null,"Coincident",2.9183049201965332]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.6987824440002441]
[null,null,null,null,null,"Coincident",3.0205070972442627]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2017390727996826]
[null,null,null,null,null,"Coincident",2.6152703762054443]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3147039413452148]
[null,null,null,null,null,"Coincident",2.7068600654602051]
[null,null,"Hemmant","Substation Rating","MVA","Non-Coincident",26.799999237060547]
[null,null,null,null,null,"Coincident",26.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.743730545043945]
[null,null,null,null,null,"Coincident",9.5433502197265625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.638227462768555]
[null,null,null,null,null,"Coincident",10.180417060852051]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-12-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.280916213989258]
[null,null,null,null,null,"Coincident",10.020517349243164]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.220138549804688]
[null,null,null,null,null,"Coincident",10.689437866210937]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.743730545043945]
[null,null,null,null,null,"Coincident",9.5433502197265625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.638227462768555]
[null,null,null,null,null,"Coincident",10.180417060852051]
[null,null,"Hendra","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.071475982666016]
[null,null,null,null,null,"Coincident",16.627571105957031]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.735872268676758]
[null,null,null,null,null,"Coincident",17.310243606567383]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.819253921508789]
[null,null,null,null,null,"Coincident",18.329902648925781]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.551671981811523]
[null,null,null,null,null,"Coincident",19.082466125488281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.160030364990234]
[null,null,null,null,null,"Coincident",15.739824295043945]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.78895378112793]
[null,null,null,null,null,"Coincident",16.386049270629883]
[null,null,"Holland Park","Substation Rating","MVA","Non-Coincident",42.371699999999997]
[null,null,null,null,null,"Coincident",42.371699999999997]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.326665878295898]
[null,null,null,null,null,"Coincident",20.755256652832031]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.870815277099609]
[null,null,null,null,null,"Coincident",21.532726287841797]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.285726547241211]
[null,null,null,null,null,"Coincident",21.688621520996094]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.854347229003906]
[null,null,null,null,null,"Coincident",22.501052856445313]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.808206558227539]
[null,null,null,null,null,"Coincident",19.277482986450195]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.313613891601563]
[null,null,null,null,null,"Coincident",19.999595642089844]
[null,null,"Holland Park East","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.895156860351563]
[null,null,null,null,null,"Coincident",16.580177307128906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.527481079101563]
[null,null,null,null,null,"Coincident",16.931894302368164]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.34343147277832]
[null,null,null,null,null,"Coincident",16.600570678710937]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.991596221923828]
[null,null,null,null,null,"Coincident",16.952720642089844]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.243791580200195]
[null,null,null,null,null,"Coincident",15.458527565002441]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.817764282226562]
[null,null,null,null,null,"Coincident",15.78645133972168]
[null,null,"Hollywell","Substation Rating","MVA","Non-Coincident",59.599998474121094]
[null,null,null,null,null,"Coincident",59.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.119297027587891]
[null,null,null,null,null,"Coincident",34.119297027587891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.449619293212891]
[null,null,null,null,null,"Coincident",34.449619293212891]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.672981262207031]
[null,null,null,null,null,"Coincident",32.672981262207031]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.989299774169922]
[null,null,null,null,null,"Coincident",32.989299774169922]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.609104156494141]
[null,null,null,null,null,"Coincident",30.609104156494141]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.90544319152832]
[null,null,null,null,null,"Coincident",30.90544319152832]
[null,null,"Hope Island","Substation Rating","MVA","Non-Coincident",58.099998474121094]
[null,null,null,null,null,"Coincident",58.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.623834609985352]
[null,null,null,null,null,"Coincident",27.758338928222656]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.760644912719727]
[null,null,null,null,null,"Coincident",27.89996337890625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.825973510742187]
[null,null,null,null,null,"Coincident",31.695859909057617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.982192993164062]
[null,null,null,null,null,"Coincident",31.857572555541992]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.444509506225586]
[null,null,null,null,null,"Coincident",26.653280258178711]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.575874328613281]
[null,null,null,null,null,"Coincident",26.789266586303711]
[null,null,"Herring Lagoon","Substation Rating","MVA","Non-Coincident",5.3]
[null,null,null,null,null,"Coincident",5.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9500000476837158]
[null,null,null,null,null,"Coincident",0.72000002861022949]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9906029716482556]
[null,null,null,null,null,"Coincident",0.73545906955239237]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-08-16T11:30:00"]
[null,null,null,null,null,"Coincident","2015-07-17T18:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42232.479166666664]
[null,null,null,null,null,"Coincident",42202.770833333328]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9987499713897705]
[null,null,null,null,null,"Coincident",0.73800003528594971]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0403680466810195]
[null,null,null,null,null,"Coincident",0.75384554656518199]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9500000476837158]
[null,null,null,null,null,"Coincident",0.72000002861022949]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9906029716482556]
[null,null,null,null,null,"Coincident",0.73545906955239237]
[null,null,"Ibis","Substation Rating","MVA","Non-Coincident",6]
[null,null,null,null,null,"Coincident",6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.25]
[null,null,null,null,null,"Coincident",0.11999999731779099]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.27312999963760376]
[null,null,null,null,null,"Coincident",0.12999999523162842]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-03"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.27056750655174255]
[null,null,null,null,null,"Coincident",0.1298723965883255]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.29560041427612305]
[null,null,null,null,null,"Coincident",0.14069509506225586]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.24519999325275421]
[null,null,null,null,null,"Coincident",0.11769599467515945]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.26788589358329773]
[null,null,null,null,null,"Coincident",0.12750399112701416]
[null,null,"Imbil","Substation Rating","MVA","Non-Coincident",8.3999996185302734]
[null,null,null,null,null,"Coincident",8.3999996185302734]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1181368827819824]
[null,null,null,null,null,"Coincident",1.3266210556030273]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1976633071899414]
[null,null,null,null,null,"Coincident",1.4152379035949707]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","06:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2319018840789795]
[null,null,null,null,null,"Coincident",1.3597865104675293]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3156998157501221]
[null,null,null,null,null,"Coincident",1.4506188631057739]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1560726165771484]
[null,null,null,null,null,"Coincident",1.3266210556030273]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2370233535766602]
[null,null,null,null,null,"Coincident",1.4152379035949707]
[null,null,"Inala","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.5364990234375]
[null,null,null,null,null,"Coincident",28.442462921142578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.649505615234375]
[null,null,null,null,null,"Coincident",29.615585327148438]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",30.754356384277344]
[null,null,null,null,null,"Coincident",30.653013229370117]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.953866958618164]
[null,null,null,null,null,"Coincident",31.91731071472168]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.164669036865234]
[null,null,null,null,null,"Coincident",28.071857452392578]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.263172149658203]
[null,null,null,null,null,"Coincident",29.229694366455078]
[null,null,"Indooroopilly","Substation Rating","MVA","Non-Coincident",54.099998474121094]
[null,null,null,null,null,"Coincident",54.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.153404235839844]
[null,null,null,null,null,"Coincident",21.56182861328125]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.165477752685547]
[null,null,null,null,null,"Coincident",21.56724739074707]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.968873977661133]
[null,null,null,null,null,"Coincident",23.328819274902344]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.981937408447266]
[null,null,null,null,null,"Coincident",23.334682464599609]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.008077621459961]
[null,null,null,null,null,"Coincident",21.420381546020508]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.020071029663086]
[null,null,null,null,null,"Coincident",21.425765991210938]
[null,null,"Innisplain","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9771060943603516]
[null,null,null,null,null,"Coincident",3.8902759552001953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9888226985931396]
[null,null,null,null,null,"Coincident",4.0127830505371094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-18"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.1629166603088379]
[null,null,null,null,null,"Coincident",4.0720295906066895]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.1751804351806641]
[null,null,null,null,null,"Coincident",4.2002601623535156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.0416145324707031]
[null,null,null,null,null,"Coincident",3.9533760547637939]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.0535211563110352]
[null,null,null,null,null,"Coincident",4.0778703689575195]
[null,null,"Ipswich South","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.255575180053711]
[null,null,null,null,null,"Coincident",17.481378555297852]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.676788330078125]
[null,null,null,null,null,"Coincident",17.94287109375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.033248901367188]
[null,null,null,null,null,"Coincident",19.095258712768555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.493349075317383]
[null,null,null,null,null,"Coincident",19.599355697631836]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.380023956298828]
[null,null,null,null,null,"Coincident",16.686500549316406]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.782085418701172]
[null,null,null,null,null,"Coincident",17.127008438110352]
[null,null,"Jimboomba","Substation Rating","MVA","Non-Coincident",48]
[null,null,null,null,null,"Coincident",48]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.960525512695313]
[null,null,null,null,null,"Coincident",18.631813049316406]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.361988067626953]
[null,null,null,null,null,"Coincident",19.076984405517578]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.706523895263672]
[null,null,null,null,null,"Coincident",19.264736175537109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.121623992919922]
[null,null,null,null,null,"Coincident",19.725028991699219]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.987371444702148]
[null,null,null,null,null,"Coincident",16.957744598388672]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.352764129638672]
[null,null,null,null,null,"Coincident",17.362916946411133]
[null,null,"Jindalee","Substation Rating","MVA","Non-Coincident",35.599998474121094]
[null,null,null,null,null,"Coincident",35.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.090059280395508]
[null,null,null,null,null,"Coincident",13.804782867431641]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.548860549926758]
[null,null,null,null,null,"Coincident",14.267752647399902]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.809045791625977]
[null,null,null,null,null,"Coincident",15.48896598815918]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.323822021484375]
[null,null,null,null,null,"Coincident",16.008419036865234]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.360757827758789]
[null,null,null,null,null,"Coincident",13.09024715423584]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.795811653137207]
[null,null,null,null,null,"Coincident",13.529253959655762]
[null,null,"Kalbar","Substation Rating","MVA","Non-Coincident",17.776]
[null,null,null,null,null,"Coincident",18]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.0876932144165039]
[null,null,null,null,null,"Coincident",4.9201421737670898]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.1504144668579102]
[null,null,null,null,null,"Coincident",4.921410083770752]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.8031187057495117]
[null,null,null,null,null,"Coincident",5.0881156921386719]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.8732109069824219]
[null,null,null,null,null,"Coincident",5.0894269943237305]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.0445318222045898]
[null,null,null,null,null,"Coincident",4.7884302139282227]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.1068081855773926]
[null,null,null,null,null,"Coincident",4.7896637916564941]
[null,null,"Kallangur","Substation Rating","MVA","Non-Coincident",44.599998474121094]
[null,null,null,null,null,"Coincident",44.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.717643737792969]
[null,null,null,null,null,"Coincident",29.437503814697266]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.973907470703125]
[null,null,null,null,null,"Coincident",29.445896148681641]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.277420043945312]
[null,null,null,null,null,"Coincident",30.799282073974609]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.545539855957031]
[null,null,null,null,null,"Coincident",30.808063507080078]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.923397064208984]
[null,null,null,null,null,"Coincident",26.124900817871094]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.150823593139648]
[null,null,null,null,null,"Coincident",26.132349014282227]
[null,null,"Karrabin","Substation Rating","MVA","Non-Coincident",34.5]
[null,null,null,null,null,"Coincident",34.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.183425903320312]
[null,null,null,null,null,"Coincident",14.938314437866211]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.706714630126953]
[null,null,null,null,null,"Coincident",15.571310043334961]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.908910751342773]
[null,null,null,null,null,"Coincident",15.569009780883789]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.454292297363281]
[null,null,null,null,null,"Coincident",16.228731155395508]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.025777816772461]
[null,null,null,null,null,"Coincident",13.931920051574707]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.513813018798828]
[null,null,null,null,null,"Coincident",14.522271156311035]
[null,null,"Kawana","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.949470520019531]
[null,null,null,null,null,"Coincident",24.627456665039063]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.388637542724609]
[null,null,null,null,null,"Coincident",25.641965866088867]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.495628356933594]
[null,null,null,null,null,"Coincident",23.390665054321289]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.862520217895508]
[null,null,null,null,null,"Coincident",24.354225158691406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.913045883178711]
[null,null,null,null,null,"Coincident",21.19365119934082]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.15155029296875]
[null,null,null,null,null,"Coincident",22.066707611083984]
[null,null,"Kedron","Substation Rating","MVA","Non-Coincident",56.058500000000002]
[null,null,null,null,null,"Coincident",56.058500000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.467647552490234]
[null,null,null,null,null,"Coincident",25.449062347412109]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.468584060668945]
[null,null,null,null,null,"Coincident",25.510187149047852]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.583641052246094]
[null,null,null,null,null,"Coincident",26.564241409301758]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.584617614746094]
[null,null,null,null,null,"Coincident",26.628044128417969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.551206588745117]
[null,null,null,null,null,"Coincident",23.534019470214844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.552072525024414]
[null,null,null,null,null,"Coincident",23.590545654296875]
[null,null,"Kelvin Grove","Substation Rating","MVA","Non-Coincident",131.60000610351562]
[null,null,null,null,null,"Coincident",131.60000610351562]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.952390670776367]
[null,null,null,null,null,"Coincident",16.659360885620117]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.267766952514648]
[null,null,null,null,null,"Coincident",16.96080207824707]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.042430877685547]
[null,null,null,null,null,"Coincident",17.730558395385742]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.378086090087891]
[null,null,null,null,null,"Coincident",18.051382064819336]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.087310791015625]
[null,null,null,null,null,"Coincident",15.809233665466309]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.386592864990234]
[null,null,null,null,null,"Coincident",16.095293045043945]
[null,null,"Kenilworth","Substation Rating","MVA","Non-Coincident",6]
[null,null,null,null,null,"Coincident",6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.0273327827453613]
[null,null,null,null,null,"Coincident",3.5462770462036133]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0295901298522949]
[null,null,null,null,null,"Coincident",3.5990118980407715]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-13"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3308329582214355]
[null,null,null,null,null,"Coincident",3.4228310585021973]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3332600593566895]
[null,null,null,null,null,"Coincident",3.4737303256988525]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.1193575859069824]
[null,null,null,null,null,"Coincident",3.2271475791931152]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.121666431427002]
[null,null,null,null,null,"Coincident",3.2751367092132568]
[null,null,"Kenmore","Substation Rating","MVA","Non-Coincident",59.700000762939453]
[null,null,null,null,null,"Coincident",59.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.087337493896484]
[null,null,null,null,null,"Coincident",29.466739654541016]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.101474761962891]
[null,null,null,null,null,"Coincident",29.475519180297852]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.480247497558594]
[null,null,null,null,null,"Coincident",30.745889663696289]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.494998931884766]
[null,null,null,null,null,"Coincident",30.755050659179687]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.938928604125977]
[null,null,null,null,null,"Coincident",26.575464248657227]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.951679229736328]
[null,null,null,null,null,"Coincident",26.583381652832031]
[null,null,"Kilcoy","Substation Rating","MVA","Non-Coincident",10.699999809265137]
[null,null,null,null,null,"Coincident",10.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.0721397399902344]
[null,null,null,null,null,"Coincident",8.5683937072753906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.0729560852050781]
[null,null,null,null,null,"Coincident",8.568638801574707]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.7246990203857422]
[null,null,null,null,null,"Coincident",9.1847190856933594]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.7255744934082031]
[null,null,null,null,null,"Coincident",9.1849813461303711]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.8731880187988281]
[null,null,null,null,null,"Coincident",8.3804893493652344]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.8739862442016602]
[null,null,null,null,null,"Coincident",8.3807287216186523]
[null,null,"Kingston","Substation Rating","MVA","Non-Coincident",59.400001525878906]
[null,null,null,null,null,"Coincident",59.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",30.578130722045898]
[null,null,null,null,null,"Coincident",30.345539093017578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.637138366699219]
[null,null,null,null,null,"Coincident",30.432369232177734]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.737346649169922]
[null,null,null,null,null,"Coincident",31.495937347412109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.798591613769531]
[null,null,null,null,null,"Coincident",31.5860595703125]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.054117202758789]
[null,null,null,null,null,"Coincident",28.833118438720703]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.110183715820313]
[null,null,null,null,null,"Coincident",28.915620803833008]
[null,null,"Kirra","Substation Rating","MVA","Non-Coincident",24.100000381469727]
[null,null,null,null,null,"Coincident",24.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.085056304931641]
[null,null,null,null,null,"Coincident",13.890421867370605]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.086590766906738]
[null,null,null,null,null,"Coincident",14.004936218261719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-29"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.055164337158203]
[null,null,null,null,null,"Coincident",14.52132511138916]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.056900024414062]
[null,null,null,null,null,"Coincident",14.641040802001953]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.644411087036133]
[null,null,null,null,null,"Coincident",13.887782096862793]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.646002769470215]
[null,null,null,null,null,"Coincident",14.002275466918945]
[null,null,"Labrador","Substation Rating","MVA","Non-Coincident",44.700000762939453]
[null,null,null,null,null,"Coincident",44.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.797389984130859]
[null,null,null,null,null,"Coincident",19.131309509277344]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.208749771118164]
[null,null,null,null,null,"Coincident",19.502346038818359]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.627658843994141]
[null,null,null,null,null,"Coincident",20.899999618530273]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.077049255371094]
[null,null,null,null,null,"Coincident",21.305337905883789]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.807882308959961]
[null,null,null,null,null,"Coincident",19.141448974609375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.219461441040039]
[null,null,null,null,null,"Coincident",19.51268196105957]
[null,null,"Laidley","Substation Rating","MVA","Non-Coincident",19.100000381469727]
[null,null,null,null,null,"Coincident",19.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.035757064819336]
[null,null,null,null,null,"Coincident",8.3206653594970703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.081056594848633]
[null,null,null,null,null,"Coincident",8.486053466796875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.779607772827148]
[null,null,null,null,null,"Coincident",8.7147312164306641]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.828265190124512]
[null,null,null,null,null,"Coincident",8.8879528045654297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.447962760925293]
[null,null,null,null,null,"Coincident",8.1886997222900391]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.4906091690063477]
[null,null,null,null,null,"Coincident",8.3514642715454102]
[null,null,"Landsborough","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.335737228393555]
[null,null,null,null,null,"Coincident",9.1967678070068359]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.397965431213379]
[null,null,null,null,null,"Coincident",9.2105560302734375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.252223968505859]
[null,null,null,null,null,"Coincident",9.6561460494995117]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.313949584960937]
[null,null,null,null,null,"Coincident",9.670623779296875]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.1754474639892578]
[null,null,null,null,null,"Coincident",9.0810728073120117]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.2306900024414062]
[null,null,null,null,null,"Coincident",9.0946874618530273]
[null,null,"Lawnton","Substation Rating","MVA","Non-Coincident",43.492800000000003]
[null,null,null,null,null,"Coincident",43.492800000000003]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.336776733398437]
[null,null,null,null,null,"Coincident",32.197940826416016]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.545330047607422]
[null,null,null,null,null,"Coincident",32.470607757568359]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",34.703147888183594]
[null,null,null,null,null,"Coincident",32.541492462158203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",34.913925170898437]
[null,null,null,null,null,"Coincident",32.817066192626953]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.227352142333984]
[null,null,null,null,null,"Coincident",28.344491958618164]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.410945892333984]
[null,null,null,null,null,"Coincident",28.584526062011719]
[null,null,"Lockrose","Substation Rating","MVA","Non-Coincident",18]
[null,null,null,null,null,"Coincident",18]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.5027899742126465]
[null,null,null,null,null,"Coincident",5.3616809844970703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7096409797668457]
[null,null,null,null,null,"Coincident",5.4875097274780273]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.7035369873046875]
[null,null,null,null,null,"Coincident",6.2197647094726563]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.9434919357299805]
[null,null,null,null,null,"Coincident",6.3657307624816895]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4418673515319824]
[null,null,null,null,null,"Coincident",5.3181443214416504]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.647038459777832]
[null,null,null,null,null,"Coincident",5.4429512023925781]
[null,null,"Logan Village","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.143561840057373]
[null,null,null,null,null,"Coincident",6.173065185546875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.2158064842224121]
[null,null,null,null,null,"Coincident",6.2924079895019531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.0108613967895508]
[null,null,null,null,null,"Coincident",6.9225373268127441]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.0918779373168945]
[null,null,null,null,null,"Coincident",7.0563693046569824]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.0373373031616211]
[null,null,null,null,null,"Coincident",6.0812716484069824]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.1085076332092285]
[null,null,null,null,null,"Coincident",6.1988401412963867]
[null,null,"Loganholme","Substation Rating","MVA","Non-Coincident",39.769599999999997]
[null,null,null,null,null,"Coincident",39.769599999999997]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.249420166015625]
[null,null,null,null,null,"Coincident",24.249420166015625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.449285507202148]
[null,null,null,null,null,"Coincident",24.449285507202148]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.610101699829102]
[null,null,null,null,null,"Coincident",26.610101699829102]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.829423904418945]
[null,null,null,null,null,"Coincident",26.829423904418945]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.784072875976562]
[null,null,null,null,null,"Coincident",23.784072875976562]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.9801025390625]
[null,null,null,null,null,"Coincident",23.9801025390625]
[null,null,"Loganlea","Substation Rating","MVA","Non-Coincident",54.900001525878906]
[null,null,null,null,null,"Coincident",54.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.458690643310547]
[null,null,null,null,null,"Coincident",14.687944412231445]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.260971069335938]
[null,null,null,null,null,"Coincident",15.26515007019043]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.365205764770508]
[null,null,null,null,null,"Coincident",14.604516983032227]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.162927627563477]
[null,null,null,null,null,"Coincident",15.178443908691406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.292922019958496]
[null,null,null,null,null,"Coincident",13.647597312927246]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.038375854492187]
[null,null,null,null,null,"Coincident",14.183919906616211]
[null,null,"Lota","Substation Rating","MVA","Non-Coincident",40.849400000000003]
[null,null,null,null,null,"Coincident",41.340600000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.118610382080078]
[null,null,null,null,null,"Coincident",22.95262336730957]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.557968139648438]
[null,null,null,null,null,"Coincident",23.267328262329102]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.139122009277344]
[null,null,null,null,null,"Coincident",23.489255905151367]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.631313323974609]
[null,null,null,null,null,"Coincident",23.811319351196289]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.321876525878906]
[null,null,null,null,null,"Coincident",21.651668548583984]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.729806900024414]
[null,null,null,null,null,"Coincident",21.948535919189453]
[null,null,"Lowood","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6518650054931641]
[null,null,null,null,null,"Coincident",2.6518650054931641]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8469634056091309]
[null,null,null,null,null,"Coincident",2.8469634056091309]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.9572272300720215]
[null,null,null,null,null,"Coincident",2.9572272300720215]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.1747910976409912]
[null,null,null,null,null,"Coincident",3.1747910976409912]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5873451232910156]
[null,null,null,null,null,"Coincident",2.5873451232910156]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7776968479156494]
[null,null,null,null,null,"Coincident",2.7776968479156494]
[null,null,"Lytton A","Substation Rating","MVA","Non-Coincident",65]
[null,null,null,null,null,"Coincident",65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.975175857543945]
[null,null,null,null,null,"Coincident",25.71827507019043]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.905620574951172]
[null,null,null,null,null,"Coincident",26.534055709838867]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-10"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.244926452636719]
[null,null,null,null,null,"Coincident",25.975458145141602]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.184677124023438]
[null,null,null,null,null,"Coincident",26.799396514892578]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.975175857543945]
[null,null,null,null,null,"Coincident",25.71827507019043]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.905620574951172]
[null,null,null,null,null,"Coincident",26.534055709838867]
[null,null,"Lytton B","Substation Rating","MVA","Non-Coincident",52.5]
[null,null,null,null,null,"Coincident",52.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.43011474609375]
[null,null,null,null,null,"Coincident",10.519618034362793]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.649982452392578]
[null,null,null,null,null,"Coincident",10.585597991943359]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.251619338989258]
[null,null,null,null,null,"Coincident",11.045598030090332]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.482481002807617]
[null,null,null,null,null,"Coincident",11.114877700805664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.43011474609375]
[null,null,null,null,null,"Coincident",10.519618034362793]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.649982452392578]
[null,null,null,null,null,"Coincident",10.585597991943359]
[null,null,"Makerston St","Substation Rating","MVA","Non-Coincident",157.30000305175781]
[null,null,null,null,null,"Coincident",157.30000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",64.536331176757813]
[null,null,null,null,null,"Coincident",61.249099731445313]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",65.129356384277344]
[null,null,null,null,null,"Coincident",61.781932830810547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",66.004531860351563]
[null,null,null,null,null,"Coincident",62.64251708984375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",66.611053466796875]
[null,null,null,null,null,"Coincident",63.187473297119141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",62.635089874267578]
[null,null,null,null,null,"Coincident",59.4447021484375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",63.210643768310547]
[null,null,null,null,null,"Coincident",59.961837768554688]
[null,null,"Maleny","Substation Rating","MVA","Non-Coincident",12]
[null,null,null,null,null,"Coincident",12]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.4327936172485352]
[null,null,null,null,null,"Coincident",8.4327936172485352]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.4372825622558594]
[null,null,null,null,null,"Coincident",8.4372825622558594]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.2146825790405273]
[null,null,null,null,null,"Coincident",9.2146825790405273]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.2195873260498047]
[null,null,null,null,null,"Coincident",9.2195873260498047]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.4853296279907227]
[null,null,null,null,null,"Coincident",8.4853296279907227]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.4898471832275391]
[null,null,null,null,null,"Coincident",8.4898471832275391]
[null,null,"Mango Hill Bus 1","Substation Rating","MVA","Non-Coincident",28.578800000000001]
[null,null,null,null,null,"Coincident",28.578800000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.211238861083984]
[null,null,null,null,null,"Coincident",11.641895294189453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.336053848266602]
[null,null,null,null,null,"Coincident",11.769360542297363]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.452007293701172]
[null,null,null,null,null,"Coincident",13.356863021850586]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.595209121704102]
[null,null,null,null,null,"Coincident",13.503105163574219]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.584853172302246]
[null,null,null,null,null,"Coincident",10.397143363952637]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.696322441101074]
[null,null,null,null,null,"Coincident",10.510980606079102]
[null,null,"Mango Hill Bus 2","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.04327392578125]
[null,null,null,null,null,"Coincident",22.693447113037109]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.550712585449219]
[null,null,null,null,null,"Coincident",23.240203857421875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.489772796630859]
[null,null,null,null,null,"Coincident",24.004220962524414]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.026521682739258]
[null,null,null,null,null,"Coincident",24.582557678222656]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.653896331787109]
[null,null,null,null,null,"Coincident",20.528264999389648]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.112918853759766]
[null,null,null,null,null,"Coincident",21.022855758666992]
[null,null,"Marburg","Substation Rating","MVA","Non-Coincident",7.1999998092651367]
[null,null,null,null,null,"Coincident",7.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2168769836425781]
[null,null,null,null,null,"Coincident",3.2054040431976318]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.3023436069488525]
[null,null,null,null,null,"Coincident",3.3009319305419922]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0359582901000977]
[null,null,null,null,null,"Coincident",4.0215640068054199]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.143186092376709]
[null,null,null,null,null,"Coincident",4.1414151191711426]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3577439785003662]
[null,null,null,null,null,"Coincident",3.3457686901092529]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.4469530582427979]
[null,null,null,null,null,"Coincident",3.4454796314239502]
[null,null,"McLachlan St","Substation Rating","MVA","Non-Coincident",125.90000152587891]
[null,null,null,null,null,"Coincident",125.90000152587891]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",47.485191345214844]
[null,null,null,null,null,"Coincident",43.764442443847656]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",48.541927337646484]
[null,null,null,null,null,"Coincident",44.681015014648438]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",48.568328857421875]
[null,null,null,null,null,"Coincident",44.762706756591797]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.649166107177734]
[null,null,null,null,null,"Coincident",45.700187683105469]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",45.20257568359375]
[null,null,null,null,null,"Coincident",41.660686492919922]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.208515167236328]
[null,null,null,null,null,"Coincident",42.533199310302734]
[null,null,"Meeandah","Substation Rating","MVA","Non-Coincident",52.400001525878906]
[null,null,null,null,null,"Coincident",52.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.609468460083008]
[null,null,null,null,null,"Coincident",21.035503387451172]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.825010299682617]
[null,null,null,null,null,"Coincident",23.435052871704102]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.88994026184082]
[null,null,null,null,null,"Coincident",22.087278366088867]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",30.266260147094727]
[null,null,null,null,null,"Coincident",24.606803894042969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.609468460083008]
[null,null,null,null,null,"Coincident",21.035503387451172]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.825010299682617]
[null,null,null,null,null,"Coincident",23.435052871704102]
[null,null,"Merrimac","Substation Rating","MVA","Non-Coincident",63.406999999999996]
[null,null,null,null,null,"Coincident",67.217399999999998]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.851961135864258]
[null,null,null,null,null,"Coincident",23.324251174926758]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.409395217895508]
[null,null,null,null,null,"Coincident",23.497383117675781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.296005249023438]
[null,null,null,null,null,"Coincident",22.708492279052734]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.906139373779297]
[null,null,null,null,null,"Coincident",22.877052307128906]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.087778091430664]
[null,null,null,null,null,"Coincident",21.401165008544922]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.628734588623047]
[null,null,null,null,null,"Coincident",21.560022354125977]
[null,null,"Miami","Substation Rating","MVA","Non-Coincident",44.700000762939453]
[null,null,null,null,null,"Coincident",44.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.207973480224609]
[null,null,null,null,null,"Coincident",24.207973480224609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.661880493164063]
[null,null,null,null,null,"Coincident",24.661880493164063]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.425361633300781]
[null,null,null,null,null,"Coincident",24.425361633300781]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.883344650268555]
[null,null,null,null,null,"Coincident",24.883344650268555]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.131929397583008]
[null,null,null,null,null,"Coincident",23.131929397583008]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.56566047668457]
[null,null,null,null,null,"Coincident",23.56566047668457]
[null,null,"Milton","Substation Rating","MVA","Non-Coincident",125.80000305175781]
[null,null,null,null,null,"Coincident",125.80000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.364658355712891]
[null,null,null,null,null,"Coincident",38.354068756103516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.776386260986328]
[null,null,null,null,null,"Coincident",38.537429809570313]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",45.662746429443359]
[null,null,null,null,null,"Coincident",41.339931488037109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",46.106525421142578]
[null,null,null,null,null,"Coincident",41.537567138671875]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.504459381103516]
[null,null,null,null,null,"Coincident",38.480636596679688]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",42.917545318603516]
[null,null,null,null,null,"Coincident",38.664600372314453]
[null,null,"Moggill","Substation Rating","MVA","Non-Coincident",33.700000762939453]
[null,null,null,null,null,"Coincident",33.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.635177612304688]
[null,null,null,null,null,"Coincident",15.965641975402832]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.942131042480469]
[null,null,null,null,null,"Coincident",16.257345199584961]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.788518905639648]
[null,null,null,null,null,"Coincident",17.009794235229492]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.115547180175781]
[null,null,null,null,null,"Coincident",17.320575714111328]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.069879531860352]
[null,null,null,null,null,"Coincident",14.548531532287598]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.349586486816406]
[null,null,null,null,null,"Coincident",14.814342498779297]
[null,null,"Molendinar","Substation Rating","MVA","Non-Coincident",59.825000000000003]
[null,null,null,null,null,"Coincident",59.825000000000003]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",36.0509033203125]
[null,null,null,null,null,"Coincident",33.207412719726563]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",37.001079559326172]
[null,null,null,null,null,"Coincident",33.793487548828125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7158039808273315]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.495357513427734]
[null,null,null,null,null,"Coincident",32.695686340332031]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",36.430892944335937]
[null,null,null,null,null,"Coincident",33.272727966308594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.749721527099609]
[null,null,null,null,null,"Coincident",30.166608810424805]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",33.612888336181641]
[null,null,null,null,null,"Coincident",30.699016571044922]
[null,null,"Mooloolaba","Substation Rating","MVA","Non-Coincident",67.750900000000001]
[null,null,null,null,null,"Coincident",67.750900000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.045135498046875]
[null,null,null,null,null,"Coincident",32.252330780029297]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.488525390625]
[null,null,null,null,null,"Coincident",32.689491271972656]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.046401977539062]
[null,null,null,null,null,"Coincident",33.200870513916016]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.502834320068359]
[null,null,null,null,null,"Coincident",33.650890350341797]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.323074340820313]
[null,null,null,null,null,"Coincident",27.778932571411133]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.704967498779297]
[null,null,null,null,null,"Coincident",28.155458450317383]
[null,null,"Moorooka","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.60307788848877]
[null,null,null,null,null,"Coincident",14.961334228515625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.496294021606445]
[null,null,null,null,null,"Coincident",15.571187019348145]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.621021270751953]
[null,null,null,null,null,"Coincident",14.97853946685791]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.515264511108398]
[null,null,null,null,null,"Coincident",15.589094161987305]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.113295555114746]
[null,null,null,null,null,"Coincident",13.532825469970703]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.92122745513916]
[null,null,null,null,null,"Coincident",14.084449768066406]
[null,null,"Morayfield","Substation Rating","MVA","Non-Coincident",47.799999237060547]
[null,null,null,null,null,"Coincident",47.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.180656433105469]
[null,null,null,null,null,"Coincident",19.189369201660156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.669536590576172]
[null,null,null,null,null,"Coincident",19.730175018310547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.262849807739258]
[null,null,null,null,null,"Coincident",20.125617980957031]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.775583267211914]
[null,null,null,null,null,"Coincident",20.69281005859375]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.052200317382812]
[null,null,null,null,null,"Coincident",17.347957611083984]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.494167327880859]
[null,null,null,null,null,"Coincident",17.83686637878418]
[null,null,"Morayfield North","Substation Rating","MVA","Non-Coincident",53.5]
[null,null,null,null,null,"Coincident",53.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.694595336914063]
[null,null,null,null,null,"Coincident",23.719905853271484]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.58599853515625]
[null,null,null,null,null,"Coincident",24.513328552246094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.822845458984375]
[null,null,null,null,null,"Coincident",24.761447906494141]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.753391265869141]
[null,null,null,null,null,"Coincident",25.589710235595703]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.54578971862793]
[null,null,null,null,null,"Coincident",22.659389495849609]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.3973388671875]
[null,null,null,null,null,"Coincident",23.417337417602539]
[null,null,"Mt Cotton","Substation Rating","MVA","Non-Coincident",15.699999809265137]
[null,null,null,null,null,"Coincident",15.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.19976806640625]
[null,null,null,null,null,"Coincident",7.0081357955932617]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.2937498092651367]
[null,null,null,null,null,"Coincident",7.1288957595825195]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.31561279296875]
[null,null,null,null,null,"Coincident",7.1208968162536621]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.4111065864562988]
[null,null,null,null,null,"Coincident",7.2435998916625977]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.8755626678466797]
[null,null,null,null,null,"Coincident",6.6925592422485352]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.9653124809265137]
[null,null,null,null,null,"Coincident",6.8078818321228027]
[null,null,"Mt Crosby West","Substation Rating","MVA","Non-Coincident",28.302600000000002]
[null,null,null,null,null,"Coincident",28.302600000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.426691055297852]
[null,null,null,null,null,"Coincident",8.2855396270751953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.190373420715332]
[null,null,null,null,null,"Coincident",8.5307807922363281]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.467576026916504]
[null,null,null,null,null,"Coincident",8.3127994537353516]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.233770370483398]
[null,null,null,null,null,"Coincident",8.5588474273681641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.191726684570312]
[null,null,null,null,null,"Coincident",7.4621224403381348]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.879513740539551]
[null,null,null,null,null,"Coincident",7.6829915046691895]
[null,null,"Mt Gravatt","Substation Rating","MVA","Non-Coincident",59.299999237060547]
[null,null,null,null,null,"Coincident",59.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.506217956542969]
[null,null,null,null,null,"Coincident",25.495765686035156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.130329132080078]
[null,null,null,null,null,"Coincident",26.043891906738281]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.339229583740234]
[null,null,null,null,null,"Coincident",25.335142135620117]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.959409713745117]
[null,null,null,null,null,"Coincident",25.879816055297852]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.667745590209961]
[null,null,null,null,null,"Coincident",23.727378845214844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.248569488525391]
[null,null,null,null,null,"Coincident",24.23748779296875]
[null,null,"Mt Sylvia","Substation Rating","MVA","Non-Coincident",3.5999999046325684]
[null,null,null,null,null,"Coincident",3.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.3600000143051147]
[null,null,null,null,null,"Coincident",0.69999998807907104]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4864723682403564]
[null,null,null,null,null,"Coincident",0.71386271715164185]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4279999732971191]
[null,null,null,null,null,"Coincident",0.71749997138977051]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5607959032058716]
[null,null,null,null,null,"Coincident",0.73170924186706543]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3600000143051147]
[null,null,null,null,null,"Coincident",0.69999998807907104]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4864723682403564]
[null,null,null,null,null,"Coincident",0.71386271715164185]
[null,null,"Mt Tamborine Bus 1","Substation Rating","MVA","Non-Coincident",21.600000381469727]
[null,null,null,null,null,"Coincident",21.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.2694492340087891]
[null,null,null,null,null,"Coincident",8.2694492340087891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.381230354309082]
[null,null,null,null,null,"Coincident",8.381230354309082]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.2706890106201172]
[null,null,null,null,null,"Coincident",8.2706890106201172]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.3824872970581055]
[null,null,null,null,null,"Coincident",8.3824872970581055]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.6943917274475098]
[null,null,null,null,null,"Coincident",7.6943917274475098]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.7983994483947754]
[null,null,null,null,null,"Coincident",7.7983994483947754]
[null,null,"Mt Tamborine Bus 2","Substation Rating","MVA","Non-Coincident",18]
[null,null,null,null,null,"Coincident",18]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.758061408996582]
[null,null,null,null,null,"Coincident",8.758061408996582]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.8091297149658203]
[null,null,null,null,null,"Coincident",8.8091297149658203]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.9714069366455078]
[null,null,null,null,null,"Coincident",8.9714069366455078]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.0237197875976563]
[null,null,null,null,null,"Coincident",9.0237197875976563]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.3544902801513672]
[null,null,null,null,null,"Coincident",8.3544902801513672]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.4032049179077148]
[null,null,null,null,null,"Coincident",8.4032049179077148]
[null,null,"Mudgeeraba West Pkg","Substation Rating","MVA","Non-Coincident",33.0809]
[null,null,null,null,null,"Coincident",33.976300000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.52787971496582]
[null,null,null,null,null,"Coincident",19.093381881713867]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.839916229248047]
[null,null,null,null,null,"Coincident",19.192554473876953]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.476415634155273]
[null,null,null,null,null,"Coincident",20.221992492675781]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.851545333862305]
[null,null,null,null,null,"Coincident",20.3270263671875]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.472570419311523]
[null,null,null,null,null,"Coincident",18.645641326904297]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.751764297485352]
[null,null,null,null,null,"Coincident",18.742488861083984]
[null,null,"Murarrie","Substation Rating","MVA","Non-Coincident",50.900001525878906]
[null,null,null,null,null,"Coincident",50.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.247058868408203]
[null,null,null,null,null,"Coincident",16.480627059936523]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.030689239501953]
[null,null,null,null,null,"Coincident",16.905033111572266]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-17"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.521881103515625]
[null,null,null,null,null,"Coincident",17.469463348388672]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.352529525756836]
[null,null,null,null,null,"Coincident",17.919334411621094]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.247058868408203]
[null,null,null,null,null,"Coincident",16.480627059936523]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.030689239501953]
[null,null,null,null,null,"Coincident",16.905033111572266]
[null,null,"Murrumba","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6697549819946289]
[null,null,null,null,null,"Coincident",0.13673299551010132]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9759401567233861]
[null,null,null,null,null,"Coincident",0.1445470005273819]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-22T13:00:00"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42391.541666666664]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5980890989303589]
[null,null,null,null,null,"Coincident",0.13086441159248352]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8911328035149884]
[null,null,null,null,null,"Coincident",0.13834305107593536]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4056665897369385]
[null,null,null,null,null,"Coincident",0.11510730534791946]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6634254594820157]
[null,null,null,null,null,"Coincident",0.1216854527592659]
[null,null,"Myrtletown","Substation Rating","MVA","Non-Coincident",49.799999237060547]
[null,null,null,null,null,"Coincident",49.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.635709762573242]
[null,null,null,null,null,"Coincident",13.190034866333008]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.706165313720703]
[null,null,null,null,null,"Coincident",13.877605438232422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-12-09"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.467494964599609]
[null,null,null,null,null,"Coincident",13.321934700012207]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.591472625732422]
[null,null,null,null,null,"Coincident",14.01638126373291]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.635709762573242]
[null,null,null,null,null,"Coincident",13.190034866333008]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.706165313720703]
[null,null,null,null,null,"Coincident",13.877605438232422]
[null,null,"Nambour","Substation Rating","MVA","Non-Coincident",76.8108]
[null,null,null,null,null,"Coincident",76.8108]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.457984924316406]
[null,null,null,null,null,"Coincident",32.252128601074219]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.463272094726563]
[null,null,null,null,null,"Coincident",32.511512756347656]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.169574737548828]
[null,null,null,null,null,"Coincident",31.974115371704102]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.174816131591797]
[null,null,null,null,null,"Coincident",32.23126220703125]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.556114196777344]
[null,null,null,null,null,"Coincident",28.490884780883789]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.560785293579102]
[null,null,null,null,null,"Coincident",28.720020294189453]
[null,null,"Narangba","Substation Rating","MVA","Non-Coincident",47.400001525878906]
[null,null,null,null,null,"Coincident",47.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.146028518676758]
[null,null,null,null,null,"Coincident",15.279886245727539]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.150302886962891]
[null,null,null,null,null,"Coincident",15.335304260253906]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.796037673950195]
[null,null,null,null,null,"Coincident",14.323823928833008]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.800233840942383]
[null,null,null,null,null,"Coincident",14.375774383544922]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.859609603881836]
[null,null,null,null,null,"Coincident",13.775428771972656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.863374710083008]
[null,null,null,null,null,"Coincident",13.825389862060547]
[null,null,"Nerang","Substation Rating","MVA","Non-Coincident",132]
[null,null,null,null,null,"Coincident",132]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",47.653007507324219]
[null,null,null,null,null,"Coincident",44.774429321289063]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",47.969558715820313]
[null,null,null,null,null,"Coincident",45.243911743164063]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",49.450477600097656]
[null,null,null,null,null,"Coincident",46.46331787109375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.778968811035156]
[null,null,null,null,null,"Coincident",46.950511932373047]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",44.536022186279297]
[null,null,null,null,null,"Coincident",41.845733642578125]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",44.831867218017578]
[null,null,null,null,null,"Coincident",42.284507751464844]
[null,null,"Newmarket","Substation Rating","MVA","Non-Coincident",57.546199999999999]
[null,null,null,null,null,"Coincident",57.546199999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.165567398071289]
[null,null,null,null,null,"Coincident",21.888996124267578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.180900573730469]
[null,null,null,null,null,"Coincident",21.910924911499023]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.203248977661133]
[null,null,null,null,null,"Coincident",21.92620849609375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.218608856201172]
[null,null,null,null,null,"Coincident",21.948173522949219]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.052080154418945]
[null,null,null,null,null,"Coincident",19.8018798828125]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.065950393676758]
[null,null,null,null,null,"Coincident",19.821718215942383]
[null,null,"Newstead","Substation Rating","MVA","Non-Coincident",131.19999694824219]
[null,null,null,null,null,"Coincident",131.19999694824219]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",37.703044891357422]
[null,null,null,null,null,"Coincident",34.799644470214844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",39.495296478271484]
[null,null,null,null,null,"Coincident",36.356605529785156]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",40.132251739501953]
[null,null,null,null,null,"Coincident",37.041786193847656]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",42.03997802734375]
[null,null,null,null,null,"Coincident",38.699062347412109]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",36.725784301757813]
[null,null,null,null,null,"Coincident",33.897640228271484]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",38.471580505371094]
[null,null,null,null,null,"Coincident",35.414241790771484]
[null,null,"Ningi","Substation Rating","MVA","Non-Coincident",18]
[null,null,null,null,null,"Coincident",18]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.7610578536987305]
[null,null,null,null,null,"Coincident",6.9243988990783691]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.9410338401794434]
[null,null,null,null,null,"Coincident",6.9910645484924316]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.9800753593444824]
[null,null,null,null,null,"Coincident",7.4555001258850098]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.165130615234375]
[null,null,null,null,null,"Coincident",7.5272789001464844]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.1139411926269531]
[null,null,null,null,null,"Coincident",6.927584171295166]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2789106369018555]
[null,null,null,null,null,"Coincident",6.9942808151245117]
[null,null,"Noosaville","Substation Rating","MVA","Non-Coincident",134.66399999999999]
[null,null,null,null,null,"Coincident",138.34200000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.3800048828125]
[null,null,null,null,null,"Coincident",32.6224365234375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.722740173339844]
[null,null,null,null,null,"Coincident",32.736312866210937]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",36.525661468505859]
[null,null,null,null,null,"Coincident",37.932716369628906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",36.889785766601563]
[null,null,null,null,null,"Coincident",38.065132141113281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.757610321044922]
[null,null,null,null,null,"Coincident",34.265300750732422]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",33.084175109863281]
[null,null,null,null,null,"Coincident",34.384910583496094]
[null,null,"North Maclean","Substation Rating","MVA","Non-Coincident",59.700000762939453]
[null,null,null,null,null,"Coincident",59.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.117237091064453]
[null,null,null,null,null,"Coincident",19.209877014160156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.482370376586914]
[null,null,null,null,null,"Coincident",19.281040191650391]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.666044235229492]
[null,null,null,null,null,"Coincident",18.952655792236328]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.05462646484375]
[null,null,null,null,null,"Coincident",19.022867202758789]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.423242568969727]
[null,null,null,null,null,"Coincident",17.896881103515625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.762727737426758]
[null,null,null,null,null,"Coincident",17.963180541992188]
[null,null,"North Springwood","Substation Rating","MVA","Non-Coincident",124.45099999999999]
[null,null,null,null,null,"Coincident",124.45099999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",44.474822998046875]
[null,null,null,null,null,"Coincident",42.757350921630859]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",46.98321533203125]
[null,null,null,null,null,"Coincident",44.251564025878906]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",47.535579681396484]
[null,null,null,null,null,"Coincident",45.699913024902344]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",50.216598510742187]
[null,null,null,null,null,"Coincident",47.296955108642578]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",41.975337982177734]
[null,null,null,null,null,"Coincident",40.354385375976563]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",44.342758178710937]
[null,null,null,null,null,"Coincident",41.764625549316406]
[null,null,"Nth Ipswich","Substation Rating","MVA","Non-Coincident",59.099998474121094]
[null,null,null,null,null,"Coincident",59.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.535343170166016]
[null,null,null,null,null,"Coincident",19.724147796630859]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.217937469482422]
[null,null,null,null,null,"Coincident",19.724405288696289]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.189813613891602]
[null,null,null,null,null,"Coincident",23.234258651733398]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.99388313293457]
[null,null,null,null,null,"Coincident",23.234561920166016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.926746368408203]
[null,null,null,null,null,"Coincident",20.100090026855469]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.622352600097656]
[null,null,null,null,null,"Coincident",20.100353240966797]
[null,null,"Nth Pine Dam","Substation Rating","MVA","Non-Coincident",6.5999999046325684]
[null,null,null,null,null,"Coincident",6.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.83917701244354248]
[null,null,null,null,null,"Coincident",0.2573620080947876]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.89162051677703857]
[null,null,null,null,null,"Coincident",0.26384168863296509]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-11"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.96505355834960938]
[null,null,null,null,null,"Coincident",0.26379606127738953]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.025363564491272]
[null,null,null,null,null,"Coincident",0.27043771743774414]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.83917701244354248]
[null,null,null,null,null,"Coincident",0.2573620080947876]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.89162051677703857]
[null,null,null,null,null,"Coincident",0.26384168863296509]
[null,null,"Nudgee","Substation Rating","MVA","Non-Coincident",47.299999237060547]
[null,null,null,null,null,"Coincident",47.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.594390869140625]
[null,null,null,null,null,"Coincident",25.974924087524414]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.371156692504883]
[null,null,null,null,null,"Coincident",26.327217102050781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.370052337646484]
[null,null,null,null,null,"Coincident",27.533418655395508]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.193424224853516]
[null,null,null,null,null,"Coincident",27.906848907470703]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.594390869140625]
[null,null,null,null,null,"Coincident",25.974924087524414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.371156692504883]
[null,null,null,null,null,"Coincident",26.327217102050781]
[null,null,"Nundah","Substation Rating","MVA","Non-Coincident",44]
[null,null,null,null,null,"Coincident",44]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.046009063720703]
[null,null,null,null,null,"Coincident",20.037322998046875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.108867645263672]
[null,null,null,null,null,"Coincident",20.110712051391602]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.093782424926758]
[null,null,null,null,null,"Coincident",20.082807540893555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.156784057617188]
[null,null,null,null,null,"Coincident",20.156362533569336]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.006019592285156]
[null,null,null,null,null,"Coincident",18.095104217529297]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.062784194946289]
[null,null,null,null,null,"Coincident",18.161380767822266]
[null,null,"Oxley","Substation Rating","MVA","Non-Coincident",30.700000762939453]
[null,null,null,null,null,"Coincident",30.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.646438598632812]
[null,null,null,null,null,"Coincident",17.656902313232422]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.669300079345703]
[null,null,null,null,null,"Coincident",17.657695770263672]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.093029022216797]
[null,null,null,null,null,"Coincident",19.026723861694336]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.117664337158203]
[null,null,null,null,null,"Coincident",19.027580261230469]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.08387565612793]
[null,null,null,null,null,"Coincident",17.12419319152832]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.106046676635742]
[null,null,null,null,null,"Coincident",17.124961853027344]
[null,null,"Palm Beach","Substation Rating","MVA","Non-Coincident",44.799999237060547]
[null,null,null,null,null,"Coincident",44.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.243946075439453]
[null,null,null,null,null,"Coincident",19.163816452026367]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.4688720703125]
[null,null,null,null,null,"Coincident",19.381650924682617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-15"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.384920120239258]
[null,null,null,null,null,"Coincident",20.300039291381836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.62318229675293]
[null,null,null,null,null,"Coincident",20.530790328979492]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.943548202514648]
[null,null,null,null,null,"Coincident",18.864669799804688]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.164962768554688]
[null,null,null,null,null,"Coincident",19.079103469848633]
[null,null,"Palmwoods Central","Substation Rating","MVA","Non-Coincident",30.259799999999998]
[null,null,null,null,null,"Coincident",30.259799999999998]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.843498229980469]
[null,null,null,null,null,"Coincident",17.729022979736328]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.450305938720703]
[null,null,null,null,null,"Coincident",18.402713775634766]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.954675674438477]
[null,null,null,null,null,"Coincident",17.833623886108398]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.5650634765625]
[null,null,null,null,null,"Coincident",18.511289596557617]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.810850143432617]
[null,null,null,null,null,"Coincident",15.816593170166016]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.352201461791992]
[null,null,null,null,null,"Coincident",16.417613983154297]
[null,null,"Pandanus Avenue","Substation Rating","MVA","Non-Coincident",52.368699999999997]
[null,null,null,null,null,"Coincident",52.368699999999997]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.6223058700561523]
[null,null,null,null,null,"Coincident",8.9935855865478516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.163070790537702]
[null,null,null,null,null,"Coincident",9.4050848315587121]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01T13:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42401.5625]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.020477294921875]
[null,null,null,null,null,"Coincident",9.3657407760620117]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.583618653441146]
[null,null,null,null,null,"Coincident",9.7942672359576033]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.5415744781494141]
[null,null,null,null,null,"Coincident",8.9181289672851562]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.077802625690383]
[null,null,null,null,null,"Coincident",9.326176168975449]
[null,null,"Parkwood","Substation Rating","MVA","Non-Coincident",54.799999237060547]
[null,null,null,null,null,"Coincident",54.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.08092212677002]
[null,null,null,null,null,"Coincident",13.972470283508301]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.425631523132324]
[null,null,null,null,null,"Coincident",14.305393218994141]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.925776481628418]
[null,null,null,null,null,"Coincident",14.810817718505859]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.291168212890625]
[null,null,null,null,null,"Coincident",15.163716316223145]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.827465057373047]
[null,null,null,null,null,"Coincident",13.720965385437012]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.165969848632813]
[null,null,null,null,null,"Coincident",14.047896385192871]
[null,null,"Peregian","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.5875301361083984]
[null,null,null,null,null,"Coincident",7.7647161483764648]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.6606588363647461]
[null,null,null,null,null,"Coincident",7.8552889823913574]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3999786376953125]
[null,null,null,null,null,"Coincident",7.5951347351074219]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.4715099334716797]
[null,null,null,null,null,"Coincident",7.6837296485900879]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.0507917404174805]
[null,null,null,null,null,"Coincident",6.3752202987670898]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.1108336448669434]
[null,null,null,null,null,"Coincident",6.4495849609375]
[null,null,"Pimpama East","Substation Rating","MVA","Non-Coincident",59.5]
[null,null,null,null,null,"Coincident",59.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.613369941711426]
[null,null,null,null,null,"Coincident",12.34492301940918]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.745990753173828]
[null,null,null,null,null,"Coincident",12.465201377868652]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.675348281860352]
[null,null,null,null,null,"Coincident",13.307950019836426]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.818314552307129]
[null,null,null,null,null,"Coincident",13.43761157989502]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.648862838745117]
[null,null,null,null,null,"Coincident",11.470285415649414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.772087097167969]
[null,null,null,null,null,"Coincident",11.58204174041748]
[null,null,"Postmans Ridge","Substation Rating","MVA","Non-Coincident",7.1999998092651367]
[null,null,null,null,null,"Coincident",7.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.4273319244384766]
[null,null,null,null,null,"Coincident",3.599402904510498]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.5043396949768066]
[null,null,null,null,null,"Coincident",3.6186277866363525]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.8083925247192383]
[null,null,null,null,null,"Coincident",3.5216197967529297]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.8920283317565918]
[null,null,null,null,null,"Coincident",3.5404291152954102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2983636856079102]
[null,null,null,null,null,"Coincident",3.3536357879638672]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.3731284141540527]
[null,null,null,null,null,"Coincident",3.3715479373931885]
[null,null,"Queensport","Substation Rating","MVA","Non-Coincident",52.400001525878906]
[null,null,null,null,null,"Coincident",52.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.875381469726562]
[null,null,null,null,null,"Coincident",26.801406860351562]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.895416259765625]
[null,null,null,null,null,"Coincident",26.801603317260742]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.693744659423828]
[null,null,null,null,null,"Coincident",25.665294647216797]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.712930679321289]
[null,null,null,null,null,"Coincident",25.665483474731445]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.613124847412109]
[null,null,null,null,null,"Coincident",23.664836883544922]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.630815505981445]
[null,null,null,null,null,"Coincident",23.665010452270508]
[null,null,"Raby Bay","Substation Rating","MVA","Non-Coincident",42.735199999999999]
[null,null,null,null,null,"Coincident",42.735199999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.352025985717773]
[null,null,null,null,null,"Coincident",23.640575408935547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.433231353759766]
[null,null,null,null,null,"Coincident",23.676164627075195]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.999231338500977]
[null,null,null,null,null,"Coincident",24.221187591552734]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.082431793212891]
[null,null,null,null,null,"Coincident",24.257650375366211]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.007749557495117]
[null,null,null,null,null,"Coincident",21.537509918212891]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.081731796264648]
[null,null,null,null,null,"Coincident",21.56993293762207]
[null,null,"Redbank","Substation Rating","MVA","Non-Coincident",43.099998474121094]
[null,null,null,null,null,"Coincident",43.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.654224395751953]
[null,null,null,null,null,"Coincident",10.099331855773926]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.16240119934082]
[null,null,null,null,null,"Coincident",10.473997116088867]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.799341201782227]
[null,null,null,null,null,"Coincident",11.184808731079102]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.362136840820313]
[null,null,null,null,null,"Coincident",11.599742889404297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.912483215332031]
[null,null,null,null,null,"Coincident",10.34414005279541]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.432977676391602]
[null,null,null,null,null,"Coincident",10.727887153625488]
[null,null,"Redbank Plains","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.706241607666016]
[null,null,null,null,null,"Coincident",17.391826629638672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.097848892211914]
[null,null,null,null,null,"Coincident",17.749015808105469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.409824013710022]
[null,null,null,null,null,"Coincident",1.3670519590377808]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.709972381591797]
[null,null,null,null,null,"Coincident",19.160228729248047]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.141399383544922]
[null,null,null,null,null,"Coincident",19.553735733032227]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.610179901123047]
[null,null,null,null,null,"Coincident",16.424493789672852]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.980007171630859]
[null,null,null,null,null,"Coincident",16.761816024780273]
[null,null,"Redcliffe","Substation Rating","MVA","Non-Coincident",28.303999999999998]
[null,null,null,null,null,"Coincident",28.303999999999998]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.403911590576172]
[null,null,null,null,null,"Coincident",18.15089225769043]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.44767951965332]
[null,null,null,null,null,"Coincident",18.153751373291016]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.673854827880859]
[null,null,null,null,null,"Coincident",18.391027450561523]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.71820068359375]
[null,null,null,null,null,"Coincident",18.393924713134766]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.895654678344727]
[null,null,null,null,null,"Coincident",16.809177398681641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.936187744140625]
[null,null,null,null,null,"Coincident",16.811826705932617]
[null,null,"Redland Bay","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.051102638244629]
[null,null,null,null,null,"Coincident",13.108650207519531]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.302027702331543]
[null,null,null,null,null,"Coincident",13.167947769165039]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.766331672668457]
[null,null,null,null,null,"Coincident",12.871514320373535]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.029180526733398]
[null,null,null,null,null,"Coincident",12.929738998413086]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.664896011352539]
[null,null,null,null,null,"Coincident",12.036100387573242]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.89271068572998]
[null,null,null,null,null,"Coincident",12.090546607971191]
[null,null,"Robina","Substation Rating","MVA","Non-Coincident",131.39999389648437]
[null,null,null,null,null,"Coincident",131.39999389648437]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",44.228813171386719]
[null,null,null,null,null,"Coincident",43.74920654296875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.779544830322266]
[null,null,null,null,null,"Coincident",45.384494781494141]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",48.827724456787109]
[null,null,null,null,null,"Coincident",48.298248291015625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",50.539699554443359]
[null,null,null,null,null,"Coincident",50.103572845458984]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.925830841064453]
[null,null,null,null,null,"Coincident",42.460353851318359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",44.430877685546875]
[null,null,null,null,null,"Coincident",44.047466278076172]
[null,null,"Rocklea","Substation Rating","MVA","Non-Coincident",31.600000381469727]
[null,null,null,null,null,"Coincident",31.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.387468338012695]
[null,null,null,null,null,"Coincident",10.598136901855469]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.393476212099717]
[null,null,null,null,null,"Coincident",10.686894529537945]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01T13:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42401.5625]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.458466529846191]
[null,null,null,null,null,"Coincident",11.445988655090332]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.464954285118292]
[null,null,null,null,null,"Coincident",11.541846072791325]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.387468338012695]
[null,null,null,null,null,"Coincident",10.598136901855469]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.393476212099717]
[null,null,null,null,null,"Coincident",10.686894529537945]
[null,null,"Roderick St","Substation Rating","MVA","Non-Coincident",49.299999237060547]
[null,null,null,null,null,"Coincident",49.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.638484954833984]
[null,null,null,null,null,"Coincident",23.778003692626953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.14640998840332]
[null,null,null,null,null,"Coincident",24.111291885375977]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.538040161132813]
[null,null,null,null,null,"Coincident",25.539716720581055]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.083597183227539]
[null,null,null,null,null,"Coincident",25.897697448730469]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.569774627685547]
[null,null,null,null,null,"Coincident",23.714279174804688]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.076337814331055]
[null,null,null,null,null,"Coincident",24.046672821044922]
[null,null,"Rosewood","Substation Rating","MVA","Non-Coincident",12]
[null,null,null,null,null,"Coincident",12]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.7368040084838867]
[null,null,null,null,null,"Coincident",4.6779308319091797]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.801826000213623]
[null,null,null,null,null,"Coincident",4.6865811347961426]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.283177375793457]
[null,null,null,null,null,"Coincident",5.1234569549560547]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.3543920516967773]
[null,null,null,null,null,"Coincident",5.1329312324523926]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.4238615036010742]
[null,null,null,null,null,"Coincident",4.4227495193481445]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.4853363037109375]
[null,null,null,null,null,"Coincident",4.4309282302856445]
[null,null,"Runcorn","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.701181411743164]
[null,null,null,null,null,"Coincident",18.429056167602539]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.130685908583267]
[null,null,null,null,null,"Coincident",18.809231646142692]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-13T20:00:00"]
[null,null,null,null,null,"Coincident","2015-07-17T18:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42198.833333333328]
[null,null,null,null,null,"Coincident",42202.770833333328]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.507076263427734]
[null,null,null,null,null,"Coincident",19.14649772644043]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.953303487225298]
[null,null,null,null,null,"Coincident",19.541475012960326]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.346157073974609]
[null,null,null,null,null,"Coincident",18.112998962402344]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.768294650792807]
[null,null,null,null,null,"Coincident",18.486653328344261]
[null,null,"Russell Island","Substation Rating","MVA","Non-Coincident",22.100000381469727]
[null,null,null,null,null,"Coincident",22.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.4092779159545898]
[null,null,null,null,null,"Coincident",5.4092779159545898]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.436917781829834]
[null,null,null,null,null,"Coincident",5.436917781829834]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.811403751373291]
[null,null,null,null,null,"Coincident",5.811403751373291]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.8410983085632324]
[null,null,null,null,null,"Coincident",5.8410983085632324]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.2754526138305664]
[null,null,null,null,null,"Coincident",5.2754526138305664]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.3024086952209473]
[null,null,null,null,null,"Coincident",5.3024086952209473]
[null,null,"Salisbury","Substation Rating","MVA","Non-Coincident",28.399999618530273]
[null,null,null,null,null,"Coincident",28.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.767004013061523]
[null,null,null,null,null,"Coincident",14.734947204589844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.885463714599609]
[null,null,null,null,null,"Coincident",14.742853164672852]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.405656099319458]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.105836868286133]
[null,null,null,null,null,"Coincident",15.051600456237793]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.226842880249023]
[null,null,null,null,null,"Coincident",15.059677124023438]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.793864250183105]
[null,null,null,null,null,"Coincident",13.825506210327148]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.905013084411621]
[null,null,null,null,null,"Coincident",13.832923889160156]
[null,null,"Samford","Substation Rating","MVA","Non-Coincident",59.099998474121094]
[null,null,null,null,null,"Coincident",59.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.40394115447998]
[null,null,null,null,null,"Coincident",12.211416244506836]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.723361015319824]
[null,null,null,null,null,"Coincident",12.446689605712891]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.144303321838379]
[null,null,null,null,null,"Coincident",12.839082717895508]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.480140686035156]
[null,null,null,null,null,"Coincident",13.086448669433594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.675756454467773]
[null,null,null,null,null,"Coincident",10.746291160583496]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.956852912902832]
[null,null,null,null,null,"Coincident",10.953335762023926]
[null,null,"Sandgate","Substation Rating","MVA","Non-Coincident",77.699996948242188]
[null,null,null,null,null,"Coincident",77.699996948242188]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.288919448852539]
[null,null,null,null,null,"Coincident",27.522953033447266]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.313415071951596]
[null,null,null,null,null,"Coincident",27.526711348362465]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02T18:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42402.770833333328]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.455485999584198]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.782970428466797]
[null,null,null,null,null,"Coincident",28.876336768718428]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.807853913407449]
[null,null,null,null,null,"Coincident",28.880279890920551]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.430990219116211]
[null,null,null,null,null,"Coincident",25.830902266343948]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.453247803559215]
[null,null,null,null,null,"Coincident",25.834429528303911]
[null,null,"Scarborough","Substation Rating","MVA","Non-Coincident",45.503900000000002]
[null,null,null,null,null,"Coincident",50.054600000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.92851448059082]
[null,null,null,null,null,"Coincident",14.978592872619629]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.232872009277344]
[null,null,null,null,null,"Coincident",15.006814002990723]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.909383773803711]
[null,null,null,null,null,"Coincident",14.79780101776123]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.230392456054687]
[null,null,null,null,null,"Coincident",14.825681686401367]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.9285888671875]
[null,null,null,null,null,"Coincident",13.961545944213867]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.198995590209961]
[null,null,null,null,null,"Coincident",13.987851142883301]
[null,null,"Scrub Road","Substation Rating","MVA","Non-Coincident",46.700000762939453]
[null,null,null,null,null,"Coincident",46.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",30.154468536376953]
[null,null,null,null,null,"Coincident",29.791530609130859]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.836820602416992]
[null,null,null,null,null,"Coincident",30.494647979736328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",31.97821044921875]
[null,null,null,null,null,"Coincident",31.59332275390625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.701831817626953]
[null,null,null,null,null,"Coincident",32.338962554931641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.658805847167969]
[null,null,null,null,null,"Coincident",28.313871383666992]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.307313919067383]
[null,null,null,null,null,"Coincident",28.982112884521484]
[null,null,"Sherwood","Substation Rating","MVA","Non-Coincident",59.700000762939453]
[null,null,null,null,null,"Coincident",59.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.870960235595703]
[null,null,null,null,null,"Coincident",24.032199859619141]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.957160949707031]
[null,null,null,null,null,"Coincident",24.178239822387695]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.829822540283203]
[null,null,null,null,null,"Coincident",26.78076171875]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.925880432128906]
[null,null,null,null,null,"Coincident",26.943504333496094]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.85328483581543]
[null,null,null,null,null,"Coincident",22.157928466796875]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.932762145996094]
[null,null,null,null,null,"Coincident",22.292579650878906]
[null,null,"Somerset Dam","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.3402169942855835]
[null,null,null,null,null,"Coincident",0.31590399146080017]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.37149941921234131]
[null,null,null,null,null,"Coincident",0.33891898393630981]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-13"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.39224639534950256]
[null,null,null,null,null,"Coincident",0.32334670424461365]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.42831283807754517]
[null,null,null,null,null,"Coincident",0.34690392017364502]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.35186603665351868]
[null,null,null,null,null,"Coincident",0.29761946201324463]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.38421955704689026]
[null,null,null,null,null,"Coincident",0.31930235028266907]
[null,null,"Southport","Substation Rating","MVA","Non-Coincident",172.69200000000001]
[null,null,null,null,null,"Coincident",172.69200000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",74.415756225585938]
[null,null,null,null,null,"Coincident",66.903373718261719]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",75.100479125976563]
[null,null,null,null,null,"Coincident",67.220497131347656]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",76.698089599609375]
[null,null,null,null,null,"Coincident",68.955307006835938]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",77.403816223144531]
[null,null,null,null,null,"Coincident",69.282150268554688]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",70.766403198242188]
[null,null,null,null,null,"Coincident",63.622432708740234]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",71.417549133300781]
[null,null,null,null,null,"Coincident",63.924003601074219]
[null,null,"Spring Creek","Substation Rating","MVA","Non-Coincident",16.5]
[null,null,null,null,null,"Coincident",16.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.7746150493621826]
[null,null,null,null,null,"Coincident",2.7790629863739014]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.2149567604064941]
[null,null,null,null,null,"Coincident",3.0600156784057617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-17"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.9657237529754639]
[null,null,null,null,null,"Coincident",2.919766902923584]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.4283599853515625]
[null,null,null,null,null,"Coincident",3.2149441242218018]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6097397804260254]
[null,null,null,null,null,"Coincident",2.6576735973358154]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.0308475494384766]
[null,null,null,null,null,"Coincident",2.9263541698455811]
[null,null,"Springfield","Substation Rating","MVA","Non-Coincident",59.900001525878906]
[null,null,null,null,null,"Coincident",59.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",30.975584030151367]
[null,null,null,null,null,"Coincident",29.129377365112305]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.017847061157227]
[null,null,null,null,null,"Coincident",29.177938461303711]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.356151580810547]
[null,null,null,null,null,"Coincident",33.248855590820312]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.404392242431641]
[null,null,null,null,null,"Coincident",33.304283142089844]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.265005111694336]
[null,null,null,null,null,"Coincident",28.461149215698242]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.306299209594727]
[null,null,null,null,null,"Coincident",28.508596420288086]
[null,null,"Springfield Central","Substation Rating","MVA","Non-Coincident",54.900001525878906]
[null,null,null,null,null,"Coincident",54.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2724170684814453]
[null,null,null,null,null,"Coincident",3.1569449901580811]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2727758884429932]
[null,null,null,null,null,"Coincident",3.1574103832244873]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.7560474872589111]
[null,null,null,null,null,"Coincident",3.6235096454620361]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.7564592361450195]
[null,null,null,null,null,"Coincident",3.6240439414978027]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2345225811004639]
[null,null,null,null,null,"Coincident",3.1203875541687012]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.2348771095275879]
[null,null,null,null,null,"Coincident",3.1208477020263672]
[null,null,"St Lucia","Substation Rating","MVA","Non-Coincident",49.299999237060547]
[null,null,null,null,null,"Coincident",49.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.301809310913086]
[null,null,null,null,null,"Coincident",25.390453338623047]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.62080192565918]
[null,null,null,null,null,"Coincident",25.560506820678711]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.20222282409668]
[null,null,null,null,null,"Coincident",26.227828979492188]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.531734466552734]
[null,null,null,null,null,"Coincident",26.403491973876953]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.700895309448242]
[null,null,null,null,null,"Coincident",24.831607818603516]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.012866973876953]
[null,null,null,null,null,"Coincident",24.997919082641602]
[null,null,"Stafford","Substation Rating","MVA","Non-Coincident",59.400001525878906]
[null,null,null,null,null,"Coincident",59.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.257556915283203]
[null,null,null,null,null,"Coincident",26.401529312133789]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.299848556518555]
[null,null,null,null,null,"Coincident",26.521091461181641]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.180496215820313]
[null,null,null,null,null,"Coincident",27.29548454284668]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.224220275878906]
[null,null,null,null,null,"Coincident",27.419094085693359]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.623659133911133]
[null,null,null,null,null,"Coincident",23.850349426269531]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.661865234375]
[null,null,null,null,null,"Coincident",23.958358764648438]
[null,null,"Stapylton","Substation Rating","MVA","Non-Coincident",54.400001525878906]
[null,null,null,null,null,"Coincident",54.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.11293888092041]
[null,null,null,null,null,"Coincident",7.9841251373291016]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.628561019897461]
[null,null,null,null,null,"Coincident",8.2572040557861328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-04"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.921974182128906]
[null,null,null,null,null,"Coincident",8.6228551864624023]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.478846549987793]
[null,null,null,null,null,"Coincident",8.917780876159668]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.11293888092041]
[null,null,null,null,null,"Coincident",7.9841251373291016]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.628561019897461]
[null,null,null,null,null,"Coincident",8.2572040557861328]
[null,null,"Stradbroke Is","Substation Rating","MVA","Non-Coincident",7.5]
[null,null,null,null,null,"Coincident",7.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.3554830551147461]
[null,null,null,null,null,"Coincident",3.7269699573516846]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.383275032043457]
[null,null,null,null,null,"Coincident",3.7293612957000732]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-12-27"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.5501294136047363]
[null,null,null,null,null,"Coincident",3.8196225166320801]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.5791635513305664]
[null,null,null,null,null,"Coincident",3.822073221206665]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.1078739166259766]
[null,null,null,null,null,"Coincident",3.6127383708953857]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.1340856552124023]
[null,null,null,null,null,"Coincident",3.6150562763214111]
[null,null,"Strathpine","Substation Rating","MVA","Non-Coincident",52.5]
[null,null,null,null,null,"Coincident",52.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.084583282470703]
[null,null,null,null,null,"Coincident",18.72747802734375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.052597045898437]
[null,null,null,null,null,"Coincident",19.00721549987793]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.686697006225586]
[null,null,null,null,null,"Coincident",19.19566535949707]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.678911209106445]
[null,null,null,null,null,"Coincident",19.482395172119141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.384925842285156]
[null,null,null,null,null,"Coincident",18.183444976806641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.324819564819336]
[null,null,null,null,null,"Coincident",18.455055236816406]
[null,null,"Sumner","Substation Rating","MVA","Non-Coincident",129.57400000000001]
[null,null,null,null,null,"Coincident",129.57400000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.072898864746094]
[null,null,null,null,null,"Coincident",34.048515319824219]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.990478515625]
[null,null,null,null,null,"Coincident",35.103317260742188]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",37.820236206054688]
[null,null,null,null,null,"Coincident",37.793170928955078]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",38.838729858398437]
[null,null,null,null,null,"Coincident",38.963977813720703]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",33.312732696533203]
[null,null,null,null,null,"Coincident",33.288890838623047]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.2098388671875]
[null,null,null,null,null,"Coincident",34.320159912109375]
[null,null,"Sunnybank","Substation Rating","MVA","Non-Coincident",27.277100000000001]
[null,null,null,null,null,"Coincident",27.277100000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.610780715942383]
[null,null,null,null,null,"Coincident",18.470891952514648]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.995533920110411]
[null,null,null,null,null,"Coincident",19.704296482908024]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-29T14:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42398.604166666664]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.233243942260742]
[null,null,null,null,null,"Coincident",18.175542831420898]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.595855327274993]
[null,null,null,null,null,"Coincident",19.389224777847772]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.505643844604492]
[null,null,null,null,null,"Coincident",16.824026107788086]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.766932046604737]
[null,null,null,null,null,"Coincident",17.94746135394967]
[null,null,"Surfers Paradise","Substation Rating","MVA","Non-Coincident",170.96799999999999]
[null,null,null,null,null,"Coincident",170.96799999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",53.420688629150391]
[null,null,null,null,null,"Coincident",51.746734619140625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",54.540683746337891]
[null,null,null,null,null,"Coincident",52.924140930175781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",62.018745422363281]
[null,null,null,null,null,"Coincident",60.075366973876953]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",63.319004058837891]
[null,null,null,null,null,"Coincident",61.442279815673828]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",55.954967498779297]
[null,null,null,null,null,"Coincident",54.201602935791016]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",57.128097534179688]
[null,null,null,null,null,"Coincident",55.434864044189453]
[null,null,"Tamborine Village","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.7377233505249023]
[null,null,null,null,null,"Coincident",3.2172622680664062]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.7857227325439453]
[null,null,null,null,null,"Coincident",3.2233011722564697]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-18"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3916382789611816]
[null,null,null,null,null,"Coincident",3.0641205310821533]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.4480347633361816]
[null,null,null,null,null,"Coincident",3.0698719024658203]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.5784215927124023]
[null,null,null,null,null,"Coincident",2.9011340141296387]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.6243751049041748]
[null,null,null,null,null,"Coincident",2.9065797328948975]
[null,null,"Tanah Merah","Substation Rating","MVA","Non-Coincident",35.5]
[null,null,null,null,null,"Coincident",35.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.620460510253906]
[null,null,null,null,null,"Coincident",14.986734390258789]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.902673721313477]
[null,null,null,null,null,"Coincident",15.41849422454834]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.88792610168457]
[null,null,null,null,null,"Coincident",17.162208557128906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.211105346679687]
[null,null,null,null,null,"Coincident",17.656642913818359]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.594999313354492]
[null,null,null,null,null,"Coincident",14.962306022644043]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.876751899719238]
[null,null,null,null,null,"Coincident",15.393362045288086]
[null,null,"Tarampa","Substation Rating","MVA","Non-Coincident",12.399999618530273]
[null,null,null,null,null,"Coincident",12.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.6097278594970703]
[null,null,null,null,null,"Coincident",5.5348920822143555]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.9396114349365234]
[null,null,null,null,null,"Coincident",5.8286151885986328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.318819522857666]
[null,null,null,null,null,"Coincident",6.1286754608154297]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.6840929985046387]
[null,null,null,null,null,"Coincident",6.4539089202880859]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.3819565773010254]
[null,null,null,null,null,"Coincident",5.3441596031188965]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.700472354888916]
[null,null,null,null,null,"Coincident",5.6277608871459961]
[null,null,"Taringa","Substation Rating","MVA","Non-Coincident",34.900001525878906]
[null,null,null,null,null,"Coincident",34.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.290048599243164]
[null,null,null,null,null,"Coincident",12.627559661865234]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.576399803161621]
[null,null,null,null,null,"Coincident",13.021557807922363]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.144730567932129]
[null,null,null,null,null,"Coincident",13.439637184143066]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.449497222900391]
[null,null,null,null,null,"Coincident",13.858973503112793]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.887284278869629]
[null,null,null,null,null,"Coincident",11.294720649719238]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.143410682678223]
[null,null,null,null,null,"Coincident",11.647132873535156]
[null,null,"Tennyson","Substation Rating","MVA","Non-Coincident",54.5]
[null,null,null,null,null,"Coincident",54.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.144704818725586]
[null,null,null,null,null,"Coincident",10.046224594116211]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.586380004882812]
[null,null,null,null,null,"Coincident",11.091421127319336]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.75193977355957]
[null,null,null,null,null,"Coincident",10.548535346984863]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.265698432922363]
[null,null,null,null,null,"Coincident",11.645991325378418]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.144704818725586]
[null,null,null,null,null,"Coincident",10.046224594116211]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.586380004882812]
[null,null,null,null,null,"Coincident",11.091421127319336]
[null,null,"Tenthill","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0575189590454102]
[null,null,null,null,null,"Coincident",1.8125900030136108]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.0705952644348145]
[null,null,null,null,null,"Coincident",1.8622351884841919]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-18"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4520306587219238]
[null,null,null,null,null,"Coincident",1.6820472478866577]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.4667942523956299]
[null,null,null,null,null,"Coincident",1.7281169891357422]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.9829461574554443]
[null,null,null,null,null,"Coincident",1.6196578741073608]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9957034587860107]
[null,null,null,null,null,"Coincident",1.6640188694000244]
[null,null,"Tewantin","Substation Rating","MVA","Non-Coincident",58.700000762939453]
[null,null,null,null,null,"Coincident",58.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.66596794128418]
[null,null,null,null,null,"Coincident",24.039665222167969]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.736927032470703]
[null,null,null,null,null,"Coincident",24.063831329345703]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.646974563598633]
[null,null,null,null,null,"Coincident",24.021875381469727]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.71788215637207]
[null,null,null,null,null,"Coincident",24.046024322509766]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.371740341186523]
[null,null,null,null,null,"Coincident",20.954174041748047]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.433591842651367]
[null,null,null,null,null,"Coincident",20.975238800048828]
[null,null,"The Gap","Substation Rating","MVA","Non-Coincident",34.700000762939453]
[null,null,null,null,null,"Coincident",34.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.995571136474609]
[null,null,null,null,null,"Coincident",16.435894012451172]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.22309684753418]
[null,null,null,null,null,"Coincident",16.692975997924805]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.909746170043945]
[null,null,null,null,null,"Coincident",17.270837783813477]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.148830413818359]
[null,null,null,null,null,"Coincident",17.540979385375977]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.313705444335938]
[null,null,null,null,null,"Coincident",14.899794578552246]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.519966125488281]
[null,null,null,null,null,"Coincident",15.13284969329834]
[null,null,"Tin Can Bay","Substation Rating","MVA","Non-Coincident",15]
[null,null,null,null,null,"Coincident",15]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.6942758560180664]
[null,null,null,null,null,"Coincident",6.6571779251098633]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.7608819007873535]
[null,null,null,null,null,"Coincident",6.7154288291931152]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-18"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.4898905754089355]
[null,null,null,null,null,"Coincident",7.4483833312988281]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.5644125938415527]
[null,null,null,null,null,"Coincident",7.5135574340820313]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.9117059707641602]
[null,null,null,null,null,"Coincident",6.8734030723571777]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.9804754257202148]
[null,null,null,null,null,"Coincident",6.9335460662841797]
[null,null,"Tingalpa","Substation Rating","MVA","Non-Coincident",55.400001525878906]
[null,null,null,null,null,"Coincident",55.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.166393280029297]
[null,null,null,null,null,"Coincident",19.944339752197266]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.754783630371094]
[null,null,null,null,null,"Coincident",20.641857147216797]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.698387145996094]
[null,null,null,null,null,"Coincident",20.423004150390625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.300899505615234]
[null,null,null,null,null,"Coincident",21.137262344360352]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.276266098022461]
[null,null,null,null,null,"Coincident",18.243686676025391]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.814483642578125]
[null,null,null,null,null,"Coincident",18.881725311279297]
[null,null,"Toogoolawah","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.450343132019043]
[null,null,null,null,null,"Coincident",3.4493730068206787]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.5283360481262207]
[null,null,null,null,null,"Coincident",3.7199921607971191]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-16"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.00445556640625]
[null,null,null,null,null,"Coincident",3.878854513168335]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.0921592712402344]
[null,null,null,null,null,"Coincident",4.1831684112548828]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2853245735168457]
[null,null,null,null,null,"Coincident",3.3214702606201172]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.3604254722595215]
[null,null,null,null,null,"Coincident",3.5820548534393311]
[null,null,"Toorbul Point","Substation Rating","MVA","Non-Coincident",17.600000381469727]
[null,null,null,null,null,"Coincident",17.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.5013008117675781]
[null,null,null,null,null,"Coincident",5.8182768821716309]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.6281580924987793]
[null,null,null,null,null,"Coincident",5.8664798736572266]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.7611579895019531]
[null,null,null,null,null,"Coincident",6.1581225395202637]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.8930859565734863]
[null,null,null,null,null,"Coincident",6.2091412544250488]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.7936344146728516]
[null,null,null,null,null,"Coincident",5.5812983512878418]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.9066829681396484]
[null,null,null,null,null,"Coincident",5.6275382041931152]
[null,null,"Toowong","Substation Rating","MVA","Non-Coincident",43.900001525878906]
[null,null,null,null,null,"Coincident",43.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.067821502685547]
[null,null,null,null,null,"Coincident",27.759780883789063]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.624608993530273]
[null,null,null,null,null,"Coincident",28.335493087768555]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",30.609922409057617]
[null,null,null,null,null,"Coincident",30.273983001708984]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.217138290405273]
[null,null,null,null,null,"Coincident",30.901838302612305]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.837610244750977]
[null,null,null,null,null,"Coincident",26.543069839477539]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.369993209838867]
[null,null,null,null,null,"Coincident",27.093549728393555]
[null,null,"Upper Mt Gravatt","Substation Rating","MVA","Non-Coincident",81.199996948242188]
[null,null,null,null,null,"Coincident",81.199996948242188]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.844463348388672]
[null,null,null,null,null,"Coincident",34.844463348388672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",35.434873119081388]
[null,null,null,null,null,"Coincident",35.434873119081388]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01T16:30:00"]
[null,null,null,null,null,"Coincident","2016-02-01T16:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42401.6875]
[null,null,null,null,null,"Coincident",42401.6875]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",36.934085845947266]
[null,null,null,null,null,"Coincident",36.934085845947266]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.55990242091692]
[null,null,null,null,null,"Coincident",37.55990242091692]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",33.372982025146484]
[null,null,null,null,null,"Coincident",33.372982025146484]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",33.938458467772335]
[null,null,null,null,null,"Coincident",33.938458467772335]
[null,null,"Varsity Lakes","Substation Rating","MVA","Non-Coincident",71.900001525878906]
[null,null,null,null,null,"Coincident",71.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.195793151855469]
[null,null,null,null,null,"Coincident",31.195793151855469]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.316402435302734]
[null,null,null,null,null,"Coincident",31.316402435302734]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.942131042480469]
[null,null,null,null,null,"Coincident",32.942131042480469]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.069492340087891]
[null,null,null,null,null,"Coincident",33.069492340087891]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.782936096191406]
[null,null,null,null,null,"Coincident",29.782936096191406]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.898082733154297]
[null,null,null,null,null,"Coincident",29.898082733154297]
[null,null,"Victoria Park","Substation Rating","MVA","Non-Coincident",126]
[null,null,null,null,null,"Coincident",126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.824638366699219]
[null,null,null,null,null,"Coincident",29.873172760009766]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",36.384525299072266]
[null,null,null,null,null,"Coincident",30.007007598876953]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.9035820960998535]
[null,null,null,null,null,"Coincident",3.4389958381652832]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",36.532535552978516]
[null,null,null,null,null,"Coincident",30.463466644287109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.103485107421875]
[null,null,null,null,null,"Coincident",30.599946975708008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",33.866462707519531]
[null,null,null,null,null,"Coincident",28.240304946899414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.395748138427734]
[null,null,null,null,null,"Coincident",28.366823196411133]
[null,null,"Victoria Point","Substation Rating","MVA","Non-Coincident",59.400001525878906]
[null,null,null,null,null,"Coincident",59.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.724861145019531]
[null,null,null,null,null,"Coincident",20.235752105712891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.164918899536133]
[null,null,null,null,null,"Coincident",20.308197021484375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.069141387939453]
[null,null,null,null,null,"Coincident",19.846416473388672]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.515867233276367]
[null,null,null,null,null,"Coincident",19.91746711730957]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.1484375]
[null,null,null,null,null,"Coincident",18.805084228515625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.557968139648438]
[null,null,null,null,null,"Coincident",18.872407913208008]
[null,null,"Visypaper","Substation Rating","MVA","Non-Coincident",25]
[null,null,null,null,null,"Coincident",25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.496933937072754]
[null,null,null,null,null,"Coincident",12.6025390625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.528605003552784]
[null,null,null,null,null,"Coincident",13.369797798675759]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-01-15T19:00:00"]
[null,null,null,null,null,"Coincident","2015-07-17T18:30:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident",42384.791666666664]
[null,null,null,null,null,"Coincident",42202.770833333328]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.631902694702148]
[null,null,null,null,null,"Coincident",12.728564262390137]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.673891050340915]
[null,null,null,null,null,"Coincident",13.503495773674134]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.496933937072754]
[null,null,null,null,null,"Coincident",12.6025390625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.528605003552784]
[null,null,null,null,null,"Coincident",13.369797798675759]
[null,null,"Wacol","Substation Rating","MVA","Non-Coincident",74.145899999999997]
[null,null,null,null,null,"Coincident",74.145899999999997]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.792154312133789]
[null,null,null,null,null,"Coincident",19.078224182128906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.636173248291016]
[null,null,null,null,null,"Coincident",19.367744445800781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.981760025024414]
[null,null,null,null,null,"Coincident",20.032135009765625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.86798095703125]
[null,null,null,null,null,"Coincident",20.336130142211914]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.792154312133789]
[null,null,null,null,null,"Coincident",19.078224182128906]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.636173248291016]
[null,null,null,null,null,"Coincident",19.367744445800781]
[null,null,"Wacol South","Substation Rating","MVA","Non-Coincident",52.5]
[null,null,null,null,null,"Coincident",52.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.743793487548828]
[null,null,null,null,null,"Coincident",18.705963134765625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.560964584350586]
[null,null,null,null,null,"Coincident",18.705963134765625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-31"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.334177017211914]
[null,null,null,null,null,"Coincident",19.601791381835938]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.136631011962891]
[null,null,null,null,null,"Coincident",19.601791381835938]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.338455200195313]
[null,null,null,null,null,"Coincident",18.663312911987305]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.105133056640625]
[null,null,null,null,null,"Coincident",18.663312911987305]
[null,null,"Wamuran","Substation Rating","MVA","Non-Coincident",9.6000003814697266]
[null,null,null,null,null,"Coincident",9.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2731139659881592]
[null,null,null,null,null,"Coincident",3.2295591831207275]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2833623886108398]
[null,null,null,null,null,"Coincident",3.2328979969024658]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2015-07-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4337255954742432]
[null,null,null,null,null,"Coincident",3.3880336284637451]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.4444770812988281]
[null,null,null,null,null,"Coincident",3.3915362358093262]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2775001525878906]
[null,null,null,null,null,"Coincident",3.2338869571685791]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.2877621650695801]
[null,null,null,null,null,"Coincident",3.2372303009033203]
[null,null,"Wellington Rd","Substation Rating","MVA","Non-Coincident",125.80000305175781]
[null,null,null,null,null,"Coincident",125.80000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",51.193111419677734]
[null,null,null,null,null,"Coincident",47.398605346679688]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",54.07171630859375]
[null,null,null,null,null,"Coincident",49.896488189697266]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",54.717758178710937]
[null,null,null,null,null,"Coincident",50.662002563476563]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",57.7945556640625]
[null,null,null,null,null,"Coincident",53.331863403320312]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",50.386821746826172]
[null,null,null,null,null,"Coincident",46.652076721191406]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",53.220088958740234]
[null,null,null,null,null,"Coincident",49.110618591308594]
[null,null,"West End","Substation Rating","MVA","Non-Coincident",126]
[null,null,null,null,null,"Coincident",126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",59.791072845458984]
[null,null,null,null,null,"Coincident",55.895053863525391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",60.287799835205078]
[null,null,null,null,null,"Coincident",56.305824279785156]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",64.143867492675781]
[null,null,null,null,null,"Coincident",59.964214324951172]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",64.6767578125]
[null,null,null,null,null,"Coincident",60.404891967773437]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",59.633224487304688]
[null,null,null,null,null,"Coincident",55.747489929199219]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",60.128639221191406]
[null,null,null,null,null,"Coincident",56.157176971435547]
[null,null,"West Maroochydore","Substation Rating","MVA","Non-Coincident",85.468000000000004]
[null,null,null,null,null,"Coincident",85.468000000000004]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.9678955078125]
[null,null,null,null,null,"Coincident",29.718534469604492]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.182231903076172]
[null,null,null,null,null,"Coincident",30.601896286010742]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.063117980957031]
[null,null,null,null,null,"Coincident",30.736692428588867]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",34.319057464599609]
[null,null,null,null,null,"Coincident",31.650318145751953]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.855501174926758]
[null,null,null,null,null,"Coincident",26.825138092041016]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.951608657836914]
[null,null,null,null,null,"Coincident",27.622495651245117]
[null,null,"Whinstanes","Substation Rating","MVA","Non-Coincident",52.400001525878906]
[null,null,null,null,null,"Coincident",52.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.0046358108520508]
[null,null,null,null,null,"Coincident",7.2621488571166992]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.6780824661254883]
[null,null,null,null,null,"Coincident",7.7861666679382324]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.9050998687744141]
[null,null,null,null,null,"Coincident",7.9883637428283691]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.645891189575195]
[null,null,null,null,null,"Coincident",8.5647830963134766]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.0046358108520508]
[null,null,null,null,null,"Coincident",7.2621488571166992]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.6780824661254883]
[null,null,null,null,null,"Coincident",7.7861666679382324]
[null,null,"Whiteside","Substation Rating","MVA","Non-Coincident",16.5]
[null,null,null,null,null,"Coincident",16.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.0974249839782715]
[null,null,null,null,null,"Coincident",5.0374341011047363]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.5459170341491699]
[null,null,null,null,null,"Coincident",5.0558652877807617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-17"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.5165276527404785]
[null,null,null,null,null,"Coincident",5.1123409271240234]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.9915032386779785]
[null,null,null,null,null,"Coincident",5.1310462951660156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.8069982528686523]
[null,null,null,null,null,"Coincident",4.9200115203857422]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2371377944946289]
[null,null,null,null,null,"Coincident",4.9380130767822266]
[null,null,"Wivenhoe","Substation Rating","MVA","Non-Coincident",10.300000190734863]
[null,null,null,null,null,"Coincident",10.300000190734863]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1852860450744629]
[null,null,null,null,null,"Coincident",5.0290260314941406]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3690338134765625]
[null,null,null,null,null,"Coincident",5.1867704391479492]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.0411176681518555]
[null,null,null,null,null,"Coincident",5.8590669631958008]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.2551932334899902]
[null,null,null,null,null,"Coincident",6.0428471565246582]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1823306083679199]
[null,null,null,null,null,"Coincident",5.0261592864990234]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.3659734725952148]
[null,null,null,null,null,"Coincident",5.1838140487670898]
[null,null,"Woodford","Substation Rating","MVA","Non-Coincident",18]
[null,null,null,null,null,"Coincident",18]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.2197656631469727]
[null,null,null,null,null,"Coincident",8.7458047866821289]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.3969354629516602]
[null,null,null,null,null,"Coincident",8.9355535507202148]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.531277656555176]
[null,null,null,null,null,"Coincident",9.9898958206176758]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.733650207519531]
[null,null,null,null,null,"Coincident",10.206636428833008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.0690231323242187]
[null,null,null,null,null,"Coincident",8.6028108596801758]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.2432956695556641]
[null,null,null,null,null,"Coincident",8.7894573211669922]
[null,null,"Woodridge","Substation Rating","MVA","Non-Coincident",85.3613]
[null,null,null,null,null,"Coincident",85.3613]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.916526794433594]
[null,null,null,null,null,"Coincident",30.58643913269043]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.629535675048828]
[null,null,null,null,null,"Coincident",31.083292007446289]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.543502807617187]
[null,null,null,null,null,"Coincident",32.053672790527344]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",36.290718078613281]
[null,null,null,null,null,"Coincident",32.574359893798828]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.130142211914063]
[null,null,null,null,null,"Coincident",28.97545051574707]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",32.805599212646484]
[null,null,null,null,null,"Coincident",29.446134567260742]
[null,null,"Wynnum","Substation Rating","MVA","Non-Coincident",58.700000762939453]
[null,null,null,null,null,"Coincident",58.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.051738739013672]
[null,null,null,null,null,"Coincident",18.715991973876953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.10113525390625]
[null,null,null,null,null,"Coincident",19.267454147338867]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2015-07-17"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","18:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","WINTER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.636066436767578]
[null,null,null,null,null,"Coincident",18.352340698242188]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.684438705444336]
[null,null,null,null,null,"Coincident",18.893087387084961]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.935678482055664]
[null,null,null,null,null,"Coincident",17.226760864257813]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.979862213134766]
[null,null,null,null,null,"Coincident",17.734342575073242]
[null,null,"Yamanto","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.1888265609741211]
[null,null,null,null,null,"Coincident",8.2772426605224609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.421605110168457]
[null,null,null,null,null,"Coincident",8.5557718276977539]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.352407455444336]
[null,null,null,null,null,"Coincident",9.3253898620605469]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.614662170410156]
[null,null,null,null,null,"Coincident",9.6391887664794922]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.7707347869873047]
[null,null,null,null,null,"Coincident",7.9006280899047852]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.9929218292236328]
[null,null,null,null,null,"Coincident",8.1664848327636719]
[null,null,"Yandina","Substation Rating","MVA","Non-Coincident",16.5]
[null,null,null,null,null,"Coincident",16.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.7817950248718262]
[null,null,null,null,null,"Coincident",5.7817950248718262]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8245320320129395]
[null,null,null,null,null,"Coincident",5.8245320320129395]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.7318921089172363]
[null,null,null,null,null,"Coincident",5.8336577415466309]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.7510733604431152]
[null,null,null,null,null,"Coincident",5.8767781257629395]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.2104392051696777]
[null,null,null,null,null,"Coincident",5.3029465675354004]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.2278752326965332]
[null,null,null,null,null,"Coincident",5.3421444892883301]
[null,null,"Yatala","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",47.985450744628906]
[null,null,null,null,null,"Coincident",45.313732147216797]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",48.273593902587891]
[null,null,null,null,null,"Coincident",45.488437652587891]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-02"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",48.819438934326172]
[null,null,null,null,null,"Coincident",46.101284027099609]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.112590789794922]
[null,null,null,null,null,"Coincident",46.279026031494141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",45.444141387939453]
[null,null,null,null,null,"Coincident",42.913917541503906]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",45.717025756835938]
[null,null,null,null,null,"Coincident",43.079372406005859]
[null,null,"Zillmere","Substation Rating","MVA","Non-Coincident",54.799999237060547]
[null,null,null,null,null,"Coincident",54.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.932706832885742]
[null,null,null,null,null,"Coincident",29.932706832885742]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.342464447021484]
[null,null,null,null,null,"Coincident",30.342464447021484]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-02-01"]
[null,null,null,null,null,"Coincident","2016-02-01"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","16:30"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.5985107421875]
[null,null,null,null,null,"Coincident",32.5985107421875]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.044761657714844]
[null,null,null,null,null,"Coincident",33.044761657714844]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.030782699584961]
[null,null,null,null,null,"Coincident",28.030782699584961]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",28.414505004882812]
[null,null,null,null,null,"Coincident",28.414505004882812]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]

{"sheet":"6.3 Sustained interruptionss","index":23,"n_rows":60015,"n_cols":12,"rows_kept":4500,"cut":true,"hidden":false,"merged":[[7,1,7,4],[11,1,11,4],[11,10,11,11],[10,1,10,4],[10,10,10,11],[10,8,10,9],[11,8,11,9],[10,6,10,7]],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Energex"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2015-16"}]
[null,"6.3 SUSTAINED INTERRUPTIONS TO SUPPLY"]
[]
[null,"6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2015-16)"]
[]
[null,"There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data."]
[]
[null,"Definitions:"]
[null,"Feeder classification definitions\n(column E)",null,null,null,null,"Average duration of sustained customer interruption \n(column I)",null,"Effect on unplanned SAIDI \n(column J)",null,"Effect on unplanned SAIFI \n(column K)"]
[null,"CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.\nUrban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km.\nShort rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km.\nLong rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km.\n",null,null,null,null,"The average duration of an  interruption experienced by an affected customer.",null,"The sum of the duration of each unplanned sustained customer\ninterruption (in minutes) divided by the total number of distribution\ncustomers. Unplanned SAIDI excludes momentary interruptions (one minute or less).",null,"The total number of unplanned sustained customer interruptions\ndivided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions."]
[]
[null,"Date of event\n(DD/MM/YYYY)","Time of interruption\n(HH:MM)","Asset ID\n(eg. feeder ID)","Feeder classification\n(CBD, Urban, Short rural, Long rural)","Reason for interruption\n(select from options in drop-down box)","Detailed reason for interruption\n(select from options in column 'O' that correspond with reason in column 'F')","Number of customers affected by the interruption","Average duration of sustained customer interruption\n(minutes)","Effect on unplanned SAIDI\n(by feeder classification)","Effect on unplanned SAIFI\n(by feeder classification)","MED"]
[null,"2015-07-01","11:52","THL1","RURAL","Planned","",1,94,2.4095273737689623E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","08:54","NRG17A","URBAN","Planned","",3,422,1.2566467780311145E-3,2.9778359668983753E-6,"NO"]
[null,"2015-07-01","08:54","NRG8B","URBAN","Planned","",8,422,3.3510580747496384E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-01","09:01","CSE7","URBAN","Planned","",40,174,6.9085794432042309E-3,3.9704479558645003E-5,"NO"]
[null,"2015-07-01","09:01","CSE9","URBAN","Planned","",3,174,5.1814345824031732E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-01","09:02","EMP21A","RURAL","Planned","",6,23,3.5373912508523063E-4,1.5379961960227417E-5,"NO"]
[null,"2015-07-01","09:08","CCY3B","URBAN","Planned","",21,109,2.2720888427434603E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-01","09:08","CCY8A","RURAL","Planned","",39,109,1.0896703048821127E-2,9.9969752741478217E-5,"NO"]
[null,"2015-07-01","09:14","LLY1","RURAL","Planned","",1,317,8.1257465689868198E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","09:26","NRG8B","URBAN","Planned","",2,407,8.0798615901842583E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-01","08:53","GGR4","RURAL","Planned","",1,196,5.0241209070076237E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","10:00","TBV4","RURAL","Planned","",21,165,8.8819280320313349E-3,5.3829866860795964E-5,"NO"]
[null,"2015-07-01","09:56","KSN6","URBAN","Planned","",23,320,7.305624238790681E-3,2.2830075746220877E-5,"NO"]
[null,"2015-07-01","12:12","BDB35A","URBAN","Planned","",10,151,1.498844103338849E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-01","12:12","NRA16A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",271,20.167901234555558,2.0591077571388401E-2,6.9466161520360514E-4,"NO"]
[null,"2015-07-01","12:18","ALY3A","URBAN","Planned","",9,115,1.0273534085799396E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-01","12:20","TRG13A","URBAN","Unknown","Unknown",185,112,2.0566920411378111E-2,1.8363321795873314E-4,"NO"]
[null,"2015-07-01","12:39","CNB26A","RURAL","Unknown","Unknown",2,161,8.2539129186553811E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-01","13:08","NSW3A","URBAN","Planned","",4,48,1.9058150188149602E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-01","14:51","CHL4","URBAN","Asset failure","LV",1,91.666666666699996,9.0989432321927883E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-01","15:22","IPS5B","URBAN","Asset failure","LV",1,112.8333333333,1.119997194216447E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-01","21:36","BLH12A","RURAL","Asset failure","LV",1,154.80000000000001,3.9680301857386742E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","05:36","WSE3A","RURAL","Overloads","",1,105.1166666667,2.6944838911995857E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","09:27","THL1","RURAL","Planned","",8,175,3.5886577907197309E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-01","07:15","KMR17B","URBAN","Planned","",29,365,1.0506797903206435E-2,2.878574768001763E-5,"NO"]
[null,"2015-07-01","10:37","SMF5A","RURAL","Planned","",17,170,7.408015010842873E-3,4.3576558887311015E-5,"NO"]
[null,"2015-07-01","07:08","ABY5A","RURAL","Planned","",1,3357,8.60508871674724E-3,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","08:48","INA2A","URBAN","Planned","",8,257,2.0408102493143531E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-01","07:51","COR22A","RURAL","Asset failure","LV",1,56.633333333300001,1.4516975205783892E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","08:00","MTG13A","URBAN","Planned","",8,358,2.8428407363989823E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-01","08:00","UMG1B","URBAN","Planned","",86,358,3.0560537916289061E-2,8.536463105108677E-5,"NO"]
[null,"2015-07-01","08:03","MTB3A","RURAL","Planned","",62,490,7.7873874058618162E-2,1.5892627358901667E-4,"NO"]
[null,"2015-07-01","08:05","HPK8A","RURAL","Planned","",3,197,1.5149262530824007E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-01","08:07","GBN4","RURAL","Planned","",45,304.93333333330008,3.517397300303627E-2,1.1534971470170564E-4,"NO"]
[null,"2015-07-01","08:08","CPS15A","URBAN","Planned","",5,74,3.6726643591746628E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-01","08:15","NBR4A","RURAL","Planned","",7,290,5.2035537965436102E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-01","08:19","GYN13A","RURAL","Planned","",145,302.91666666666669,0.11259413818383157,3.7168241403882929E-4,"NO"]
[null,"2015-07-01","08:48","BMT2","RURAL","Planned","",1,235,6.0238184344224056E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-01","08:48","COR25A","RURAL","Planned","",6,235,3.6142910606534432E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-01","08:46","KBR6A","RURAL","Planned","",3,369,2.8376029816619586E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-01","08:45","AGE7B","URBAN","Planned","",2,265,5.2608435415204635E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-01","08:45","ACR4","URBAN","Planned","",1,212,2.1043374166081853E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-01","08:42","IPL3","RURAL","Planned","",2,256,1.312423420606073E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-01","08:36","RCF9A","URBAN","Planned","",20,229,4.5461629094648535E-3,1.9852239779322502E-5,"NO"]
[null,"2015-07-01","08:32","NGE12","URBAN","Planned","",35,293,1.0179235946847612E-2,3.4741419613814383E-5,"NO"]
[null,"2015-07-01","08:21","BDB35A","URBAN","Planned","",29,161,4.6345053764828385E-3,2.878574768001763E-5,"NO"]
[null,"2015-07-01","08:40","CLM3","RURAL","Planned","",5,70,8.9716444767993272E-4,1.2816634966856181E-5,"NO"]
[null,"2015-07-01","08:48","CSE9","URBAN","Planned","",6,342,2.0368398013584886E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-01","09:10","WRD21A","URBAN","Asset failure","LV",16,142,2.2552144389310362E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-01","10:46","AHD18B","RURAL","Asset failure","HV",2264,89.433333333300055,0.51901493052510073,5.8033723129924794E-3,"NO"]
[null,"2015-07-01","10:46","AHD18A","URBAN","Asset failure","HV",777,89.798039215676454,6.9218969873905217E-2,7.7125951542667936E-4,"NO"]
[null,"2015-07-02","09:18","BVL13A","URBAN","Planned","",4,186,7.3850331979079709E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-02","10:30","CBT12A","RURAL","Planned","",13,223,7.431084953783214E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-02","10:27","CBW13","RURAL","Planned","",33,254,2.1485806858437703E-2,8.4589790781250797E-5,"NO"]
[null,"2015-07-02","10:25","CRB22A","URBAN","Planned","",8,45,3.5734031602780504E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-02","10:15","MMC24A","URBAN","Overloads","",1,74.466666666699993,7.3916506111710526E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","10:11","CPK13","RURAL","Planned","",50,276,3.5373912508523064E-2,1.2816634966856182E-4,"NO"]
[null,"2015-07-02","09:42","CHL7","URBAN","Overloads","",1,95.033333333300007,9.4331226018047677E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","09:21","YTA2B","RURAL","Animal","Animal nesting/burrowing, etc and other",1574,47.479914529923079,0.12472482684733618,4.0346766875663251E-3,"NO"]
[null,"2015-07-02","10:39","NBR4A","RURAL","Planned","",3,201,1.5456861770028556E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-02","15:57","BDA12B","URBAN","Asset failure","LV",1,115.5666666667,1.1471285885821828E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","09:18","BKD5B","URBAN","Planned","",20,262,5.201286822182496E-3,1.9852239779322502E-5,"NO"]
[null,"2015-07-02","09:30","WMD4A","RURAL","Planned","",6,194,2.9837126202841191E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-02","10:52","CBT8A","RURAL","Planned","",6,134,2.060914902670474E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-02","11:41","GYS5A","RURAL","Planned","",10,163,4.1782229991951152E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-02","12:16","GTN12A","RURAL","Planned","",2,86,4.4089224285985264E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-02","12:48","ACR5","RURAL","Planned","",10,112,2.8709262325757848E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-02","21:57","LGL11A","URBAN","Overloads","",1,149.19999999999999,1.4809770875374585E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","14:23","BBH3A","URBAN","Asset failure","LV",1,80.599999999999994,8.0004526310669676E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","09:18","BDB35A","URBAN","Planned","",19,170,3.2061367243605842E-3,1.8859627790356379E-5,"NO"]
[null,"2015-07-02","16:03","CMA15A","RURAL","Asset failure","LV",1,126.0166666667,3.2302192328141741E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-02","16:12","CPB4","URBAN","Asset failure","LV",1,74.566666666700002,7.4015767310607158E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","17:22","ALY3A","URBAN","Asset failure","LV",1,143.4166666667,1.4235710275092487E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","18:48","RIS2","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",683,102.81666666670002,0.18000651939504481,1.7507523364725546E-3,"NO"]
[null,"2015-07-02","09:10","THL1","RURAL","Planned","",2,183,9.3817767957387254E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-02","13:53","RCF10A","URBAN","Asset failure","LV",1,86.816666666700002,8.617526417544219E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","08:00","GAP4A","RURAL","Planned","",3,338,2.5992135712784338E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-02","09:15","TBV4","RURAL","Planned","",7,340,6.1007182442235431E-3,1.7943288953598652E-5,"NO"]
[null,"2015-07-02","07:40","DRA15A","URBAN","Planned","",14,327,4.5441776854869206E-3,1.3896567845525752E-5,"NO"]
[null,"2015-07-02","08:02","KWA12A","URBAN","Planned","",244,364,8.8159826412015363E-2,2.4219732530773454E-4,"NO"]
[null,"2015-07-02","08:03","AMR2","RURAL","Planned","",51,410,5.3599167431392557E-2,1.3072967666193306E-4,"NO"]
[null,"2015-07-02","08:10","KRN18","URBAN","Planned","",28,40,1.11172542764206E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-02","08:10","KWA12A","URBAN","Asset failure","LV",1,61.2,6.0747853724726858E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","08:20","HPK2","URBAN","Planned","",31,371,1.1416030485099406E-2,3.0770971657949879E-5,"NO"]
[null,"2015-07-02","08:23","SIS1","RURAL","Planned","",15,304,1.1688771089772837E-2,3.8449904900568543E-5,"NO"]
[null,"2015-07-02","08:32","JBB16A","RURAL","Planned","",3,441,3.3912816122301458E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-02","08:32","MTB13A","RURAL","Planned","",20,288,1.4764763481818322E-2,5.1266539867424725E-5,"NO"]
[null,"2015-07-02","08:33","WHO2","RURAL","Planned","",14,243,8.7204384314489465E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-02","08:35","NDH8","URBAN","Planned","",7,348,2.418002805121481E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-02","08:58","CLD2","URBAN","Planned","",53,334,1.7571217428678346E-2,5.2608435415204633E-5,"NO"]
[null,"2015-07-02","09:15","BTA5A","RURAL","Planned","",3,133,1.0227674703551233E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-02","08:40","BVL2A","URBAN","Planned","",1,195,1.9355933784839441E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-02","09:03","SMF5A","RURAL","Planned","",8,390,7.9975802193182569E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-02","07:00","CDRT1","URBAN","Planned","",28,62,1.7231744128451932E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-02","08:57","JBB16A","RURAL","Planned","",6,353,5.4291265719602789E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-02","08:45","NGE4B","URBAN","Planned","",121,445.5,5.3350909182951295E-2,1.2010605066490114E-4,"NO"]
[null,"2015-07-02","08:42","RLA4A","URBAN","Planned","",16,187,2.9698950709866464E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-02","08:42","GAP6A","URBAN","Planned","",10,381,3.7818516779609367E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-02","08:42","GAP1A","URBAN","Planned","",17,381,6.429147852533592E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-02","08:40","RLB15A","URBAN","Planned","",27,253,6.7805324966276007E-3,2.6800523702085381E-5,"NO"]
[null,"2015-07-02","09:05","NSD8A","URBAN","Planned","",2,75,1.4889179834491877E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-02","11:30","BHL4A","RURAL","Asset failure","LV",2,69,3.5373912508523063E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-02","18:25","TWT5B","URBAN","Asset failure","LV",73,40,1.7519601605252109E-3,7.2460675194527141E-5,"NO"]
[null,"2015-07-02","18:45","LDR8","URBAN","Asset failure","LV",134,135,1.7956350880397202E-2,1.3301000652146076E-4,"NO"]
[null,"2015-07-02","22:23","WMD6A","URBAN","Asset failure","LV",12,96.683333333299998,1.1516284295981015E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-03","11:07","EZRRWD4","RURAL","Planned","",5,143,1.8327788002604341E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-03","10:30","BTY7A","URBAN","Planned","",1,75,7.4445899172459386E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","09:50","GNA13A","URBAN","Planned","",50,365,1.8115168798631783E-2,4.9630599448306258E-5,"NO"]
[null,"2015-07-03","09:41","KWA12A","URBAN","Planned","",155,212,3.2617229957426871E-2,1.5385485828974939E-4,"NO"]
[null,"2015-07-03","09:13","TWG13A","URBAN","Planned","",1,94,9.3305526962815765E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","09:05","MSV2","RURAL","Planned","",1,260,6.6646501827652145E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","08:59","BIS16A","URBAN","Planned","",81,83,6.6733304018192592E-3,8.0401571106256136E-5,"NO"]
[null,"2015-07-03","11:10","MFD8A","RURAL","Planned","",3,125,9.6124762251421361E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-03","08:45","CSE9","URBAN","Planned","",8,280,2.2234508552841201E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-03","13:18","MDH5A","URBAN","Planned","",1,12,1.1911343867593501E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","08:49","GBN4","RURAL","Planned","",12,345.25,1.0727523467258623E-2,3.0759923920454833E-5,"NO"]
[null,"2015-07-03","11:23","KWA12A","URBAN","Asset failure","LV",1,97.216666666699993,9.6498428860689877E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","11:30","HPK3A","URBAN","Overloads","",1,53.816666666700002,5.3419068539560059E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","11:47","BKD5B","URBAN","Planned","",1,120,1.1911343867593501E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","11:56","INA10A","RURAL","Asset failure","LV",1,108.21666666669999,2.7739470279940942E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","16:05","TMH5A","URBAN","Third party","Vehicle impact",8,290,2.3028598144014104E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-03","13:09","CLM6","RURAL","Asset failure","LV",1,81.150000000000006,2.0801398551207584E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","13:21","BRD13A","RURAL","Asset failure","LV",1,72.3,1.8532854162074038E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","13:54","ALY6","URBAN","Asset failure","LV",1,71.216666666699993,7.0690517147570619E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","15:56","HTN22A","URBAN","Overloads","",1,88.583333333300004,8.7928878689216172E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","08:45","BVLNCM7","URBAN","Planned","",40,284,1.1276072194655182E-2,3.9704479558645003E-5,"NO"]
[null,"2015-07-03","08:15","QEN10","URBAN","Planned","",15,214,3.1862844845812616E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-03","12:44","TSN13A","URBAN","Planned","",1,1509,1.4978514913498828E-3,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","16:39","BBH13B","URBAN","Asset failure","LV",1,111.2666666667,1.1044462730566394E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","17:46","KSN3","URBAN","Overloads","",1,140.51666666669999,1.394785279829231E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","03:14","LTN3","URBAN","Animal","Animal impact",144,75.783333333300007,1.0832176113184766E-2,1.4293612641112202E-4,"NO"]
[null,"2015-07-03","05:25","LDR10A","URBAN","Third party","Vehicle impact",99,364.1666666667,3.5786143732204505E-2,9.8268586907646386E-5,"NO"]
[null,"2015-07-03","05:37","LDR10A","URBAN","Third party","Vehicle impact",1,428.0833333333,4.2492064894321564E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","06:00","BHD20A","URBAN","Overloads","",1,141.44999999999999,1.4040496583925838E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","06:43","AMR2","RURAL","Planned","",1,132,3.3835916312500319E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","08:00","GLY4A","RURAL","Planned","",35,120,1.0765973372159192E-2,8.9716444767993275E-5,"NO"]
[null,"2015-07-03","08:01","CBW6","RURAL","Planned","",35,136,1.2201436488447084E-2,8.9716444767993275E-5,"NO"]
[null,"2015-07-03","08:04","BKD13A","URBAN","Planned","",3,71,2.1142635364978466E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-03","08:24","DBY9","URBAN","Planned","",12,449,5.3481933965494818E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-03","08:12","ALY9","URBAN","Planned","",9,46,4.1094136343197582E-4,8.9335079006951264E-6,"NO"]
[null,"2015-07-03","08:41","JBB2A","RURAL","Overloads","",1,130.65,3.3489867168395203E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","08:21","KBR2A","RURAL","Planned","",27,314,2.1731886249801345E-2,6.920982882102339E-5,"NO"]
[null,"2015-07-03","08:24","TGW1","RURAL","Planned","",13,165,5.4983364007813017E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-03","08:25","MAI11","URBAN","Planned","",34,234,7.8972209842144911E-3,3.3748807624848254E-5,"NO"]
[null,"2015-07-03","08:30","BKD5B","URBAN","Planned","",1,137,1.3598784248835914E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","08:32","MFD12A","RURAL","Planned","",2,143,7.3311152010417365E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-03","08:32","RLB11B","URBAN","Planned","",3,328,9.7673019714266708E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-03","08:38","CRY6A","RURAL","Planned","",75,270,5.1907371615767535E-2,1.9224952450284276E-4,"NO"]
[null,"2015-07-03","08:40","AHL14A","URBAN","Planned","",3,332,9.8864154101026063E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-03","08:40","AHL6A","URBAN","Planned","",24,332,7.9091323280820851E-3,2.3822687735187003E-5,"NO"]
[null,"2015-07-03","08:41","HDA3A","URBAN","Planned","",3,124,3.6925165989539854E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-03","08:04","NVL24A","URBAN","Planned","",9,176,1.5722973905223422E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-03","22:07","CPK6","URBAN","Animal","Animal impact",17,126.83333333330003,2.1402368835418979E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-03","16:23","WSE3A","RURAL","Asset failure","LV",1,133.28333333329999,3.4164876609974414E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","22:53","CMA20A","URBAN","Asset failure","LV",1,61.416666666700003,6.0962919655702608E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","22:07","CPK9","RURAL","Animal","Animal impact",687,60,0.10566033866676236,1.7610056444460392E-3,"NO"]
[null,"2015-07-03","22:07","CPK7","URBAN","Animal","Animal impact",808,60,4.8121829225077746E-2,8.0203048708462905E-4,"NO"]
[null,"2015-07-03","22:07","CPK13","RURAL","Animal","Animal impact",407,2.7166666667000001,2.8342279344887962E-3,1.0432740863020931E-3,"NO"]
[null,"2015-07-03","22:07","CPK12","URBAN","Animal","Animal impact",2,192.8333333333,3.8281735707786942E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-03","22:07","CPK11","URBAN","Animal","Animal impact",40,110.83333333330003,4.4005798177484973E-3,3.9704479558644997E-5,"NO"]
[null,"2015-07-03","22:07","CPK10","URBAN","Animal","Animal impact",922,6.4666666667000019,5.918217374776936E-3,9.1518825382676727E-4,"NO"]
[null,"2015-07-03","20:24","BRD2A","URBAN","Asset failure","LV",1,172.63333333329999,1.7135791636181896E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","18:14","UPC1","RURAL","Asset failure","LV",1,5.8166666666999998,1.4910018678194802E-5,2.5633269933712364E-6,"NO"]
[null,"2015-07-03","18:12","MMC33A","URBAN","Asset failure","LV",1,194.4166666667,1.9298031418819725E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","18:06","KWA12A","URBAN","Asset failure","LV",1,142.05000000000001,1.4100053303263809E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-03","22:07","CPK8","URBAN","Animal","Animal impact",17,105.83333333330003,1.785874403480991E-3,1.687440381242413E-5,"NO"]
[null,"2015-07-03","21:51","WMD6A","URBAN","Asset failure","LV",12,113.9833333333,1.357694678507469E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-03","07:15","TGW5","RURAL","Asset failure","HV",12,13,3.9987901096591287E-4,3.0759923920454833E-5,"NO"]
[null,"2015-07-03","13:52","MTB1B","RURAL","Asset failure","LV",19,101.1833333333,4.9279534226380223E-3,4.8703212874053492E-5,"NO"]
[null,"2015-07-03","15:04","AMR3","RURAL","Asset failure","HV",15,82,3.1528922018466206E-3,3.844990490056855E-5,"NO"]
[null,"2015-07-04","08:28","RWD2","RURAL","Planned","",17,154,6.7107900686458975E-3,4.3576558887311015E-5,"NO"]
[null,"2015-07-04","11:07","BPN35A","URBAN","Overloads","",1,256.14999999999998,2.5425756097367292E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-04","20:03","NIP4A","RURAL","Overloads","",1,104.3833333333,2.6756861599131545E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-04","17:33","BLN2B","URBAN","Asset failure","LV",1,53.45,5.3055110810239388E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-04","17:06","MFN13A","RURAL","Overloads","",1,47.166666666700003,1.2090358985409544E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-04","14:02","NVL9","RURAL","Overloads","",1,155.9166666667,3.9966540038321736E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-04","08:30","MFD12A","RURAL","Asset failure","LV",1,39.299999999999997,1.0073875083948958E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-04","08:17","BWH7A","RURAL","Planned","",3,117,8.9972777467330393E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-04","03:09","WRG8A","URBAN","Asset failure","LV",1,113.3333333333,1.1249602541612777E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-04","02:06","AHD10A","URBAN","Animal","Animal impact",65,97.083333333300004,6.2637952387028344E-3,6.4519779282798132E-5,"NO"]
[null,"2015-07-04","09:04","NDH1","URBAN","Asset failure","LV",1,209.6666666667,2.0811764701993065E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-04","08:36","GTN12A","RURAL","Overloads","",1,75.766666666700004,1.9421474186451281E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-04","21:37","CPB3","RURAL","Asset failure","LV",161,47.9666666667,1.9795634483255581E-2,4.1269564593276906E-4,"NO"]
[null,"2015-07-05","17:29","HPK6","URBAN","Asset failure","LV",1,87.75,8.7101702031777483E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","09:09","CPD2A","RURAL","Planned","",1,167,4.280756078929965E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-05","09:11","LTN4","URBAN","Overloads","",1,54.4666666667,5.4064266332388038E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","09:42","PGN1B","RURAL","Overloads","",1,144.78333333329999,3.7112702652351338E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-05","10:10","PBH8A","URBAN","Asset failure","LV",1,100.8333333333,1.000883755540512E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","12:29","CPD2A","RURAL","Planned","",3,108,8.3051794585228063E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-05","16:24","RLB11B","URBAN","Asset failure","LV",1,58.116666666699999,5.7687300092114392E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","08:00","CRB18A","URBAN","Planned","",1,320,3.1763583646916003E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","08:44","CMD13A","URBAN","Asset failure","LV",1,123.1833333333,1.2227325350744409E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","12:50","DBY9","URBAN","Overloads","",1,111.9333333333,1.1110636863157518E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","02:31","WFD2B","RURAL","Third party","Vehicle impact",29,163,1.2116846697665834E-2,7.4336482807765855E-5,"NO"]
[null,"2015-07-05","08:01","KSN6","URBAN","Planned","",1,278,2.7594613293258281E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","08:23","MAI14","URBAN","Asset failure","LV",1,51.166666666700003,5.0788646768799828E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-05","00:22","CLM3","RURAL","Overloads","",1,66.349999999999994,1.7007674601018152E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-05","03:12","NSW16A","URBAN","Planned","",2,223.66666666666666,6.6604264459626996E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-05","05:55","CPK9","RURAL","Asset failure","LV",1,104.3333333333,2.6744044964164691E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-05","06:33","CPB3","RURAL","Planned","",17,100,4.3576558887311019E-3,4.3576558887311021E-5,"NO"]
[null,"2015-07-05","07:30","FIS7A","URBAN","Planned","",7,501,3.4810902453042006E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-05","08:00","GYN2B","URBAN","Planned","",35,301,1.045716730375813E-2,3.4741419613814383E-5,"NO"]
[null,"2015-07-05","05:24","SMR1A","URBAN","Asset failure","HV",912,74.06666666665383,6.844357447516812E-2,9.0526213393710608E-4,"NO"]
[null,"2015-07-06","19:47","MLT21B","URBAN","Overloads","",1,97.233333333299996,9.6514972393773146E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","09:13","HWL1A","URBAN","Planned","",18,427,7.6292157471936376E-3,1.7867015801390253E-5,"NO"]
[null,"2015-07-06","13:51","GTN13A","RURAL","Planned","",1,73,1.8712287051610025E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","09:34","RLA8A","URBAN","Planned","",8,98,7.7820779934944205E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-06","09:47","CRM5B","URBAN","Animal","Animal nesting/burrowing, etc and other",10,63,6.2534555304865887E-4,9.9261198896612508E-6,"NO"]
[null,"2015-07-06","10:05","ACR4","URBAN","Planned","",13,284,3.664723463262934E-3,1.2903955856559627E-5,"NO"]
[null,"2015-07-06","10:15","OXL8B","URBAN","Planned","",18,285,5.0920995033962215E-3,1.7867015801390253E-5,"NO"]
[null,"2015-07-06","09:12","CMV8","URBAN","Asset failure","LV",1,108.5,1.0769840080282458E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","11:26","GTN15A","RURAL","Planned","",3,75,5.7674857350852819E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-06","09:17","NVL6","URBAN","Planned","",43,234,9.9876618329771509E-3,4.2682315525543378E-5,"NO"]
[null,"2015-07-06","15:36","BBH3A","URBAN","Asset failure","LV",1,54.983333333300003,5.4577115859954364E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","15:41","NIP1A","URBAN","Unknown","Unknown",49,34.266666666699997,1.6666617036083431E-3,4.8637987459340128E-5,"NO"]
[null,"2015-07-06","17:47","HWD2B","RURAL","Asset failure","LV",1,128.53333333329999,3.2947296288123078E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","18:19","KVG32A","URBAN","Asset failure","LV",1,128.5,1.2755064058214707E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","19:55","KLG7A","URBAN","Overloads","",1,21.566666666700002,2.1407331895402522E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","20:03","INA1A","URBAN","Overloads","",1,108.4166666667,1.0761568313711048E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","20:41","MTB1B","RURAL","Asset failure","LV",1,78.7,2.017338343783163E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","20:50","MFN5A","RURAL","Overloads","",1,64.45,1.652064247227762E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","23:00","BIS13A","URBAN","Planned","",1,329,3.2656934436985519E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","09:15","WMD8B","RURAL","Planned","",2,374,1.9173685910416848E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-06","09:12","BMT1","RURAL","Planned","",13,104,3.4656180950379117E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-06","18:13","SMF5A","RURAL","Unknown","Unknown",308,1.2333333597052842,9.7372248054862053E-4,7.8950471395834081E-4,"NO"]
[null,"2015-07-06","08:09","DRA11A","URBAN","Planned","",31,288,8.8620398374895659E-3,3.0770971657949879E-5,"NO"]
[null,"2015-07-06","09:09","ACR6","RURAL","Planned","",4,317,3.2502986275947279E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-06","09:30","AHL14A","URBAN","Planned","",11,300,3.275619563588213E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-06","07:18","SBK10A","RURAL","Asset failure","LV",1,78.7,2.017338343783163E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","08:02","MGP16A","URBAN","Planned","",6,223,1.3281148412366754E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-06","08:02","RBA35A","URBAN","Planned","",1,223,2.213524735394459E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","08:04","JBB16A","RURAL","Planned","",4,284,2.9119394644697245E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-06","08:07","KRN2","URBAN","Planned","",35,248,8.6158720642259667E-3,3.4741419613814376E-5,"NO"]
[null,"2015-07-06","08:09","OXL8B","URBAN","Planned","",1,288,2.8587225282224405E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","08:11","NDH8","URBAN","Planned","",14,297,4.1272806501211484E-3,1.3896567845525752E-5,"NO"]
[null,"2015-07-06","08:20","BIS3","RURAL","Planned","",4,178,1.8250888192803203E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-06","08:30","NBR7A","RURAL","Planned","",79,236,4.7790668464413329E-2,2.0250283247632767E-4,"NO"]
[null,"2015-07-06","08:45","BDB4A","RURAL","Planned","",22,258,1.4549444014375138E-2,5.6393193854167202E-5,"NO"]
[null,"2015-07-06","08:04","SHW6A","URBAN","Planned","",14,214,2.9738655189425109E-3,1.3896567845525752E-5,"NO"]
[null,"2015-07-06","08:33","WRG1A","URBAN","Planned","",12,54,6.4321256885004909E-4,1.1911343867593501E-5,"NO"]
[null,"2015-07-06","09:03","GYM2A","RURAL","Planned","",2,227,1.1637504549905414E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-06","08:55","CGTMLS4","URBAN","Planned","",1,182,1.8065538199183478E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-06","08:57","BDT4","RURAL","Asset failure","LV",1,74.183333333299998,1.9015614079150411E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","08:41","HDN1","RURAL","Planned","",2,226,1.1586238010037988E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-06","09:06","ACR4","URBAN","Planned","",4,219,8.6952810233432564E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-06","08:40","UMG5A","URBAN","Planned","",19,280,5.2806957812997855E-3,1.8859627790356379E-5,"NO"]
[null,"2015-07-06","08:40","TWT11A","RURAL","Planned","",1,230,5.8956520847538432E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-06","08:40","SMF5A","RURAL","Planned","",14,410,1.4713496941950897E-2,3.5886577907197311E-5,"NO"]
[null,"2015-07-06","08:37","NRG16A","RURAL","Planned","",2,248,1.2714101887121333E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-06","08:53","KSN5","RURAL","Asset failure","HV",11,54,1.5226162340625145E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-06","14:47","AMR3","RURAL","Asset failure","HV",2,146,7.4849148206440098E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-06","09:12","CMV8","URBAN","Asset failure","LV",17,203.36666666670001,3.4316912553205492E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-06","17:47","YTA37A","URBAN","Asset failure","LV",8,40,3.1763583646916003E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-07","09:36","BBS11A","URBAN","Planned","",8,264,2.0963965206964564E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-07","10:42","GVN3A","URBAN","Asset failure","LV",1,81.05,8.0451201705704445E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","09:40","BSEENG15OLD","URBAN","Planned","",3,147,4.3774188713406121E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-07","10:47","MTG5A","URBAN","Planned","",27,151,4.0468790790148925E-3,2.6800523702085378E-5,"NO"]
[null,"2015-07-07","09:30","PWC3","RURAL","Planned","",76,135,2.6299734951988882E-2,1.9481285149621397E-4,"NO"]
[null,"2015-07-07","09:23","MLY6","RURAL","Planned","",13,193,6.4313874263684321E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-07","09:20","BBS11A","URBAN","Planned","",8,187,1.4849475354933232E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-07","09:08","LLY4","RURAL","Planned","",20,63,3.2297920116477578E-3,5.1266539867424725E-5,"NO"]
[null,"2015-07-07","09:07","MRK3","URBAN","Planned","",67,231,1.5362655753228718E-2,6.6505003260730378E-5,"NO"]
[null,"2015-07-07","10:49","GLY4A","RURAL","Asset failure","LV",1,123.5166666667,3.1661360579798934E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","21:52","NVL5","RURAL","Asset failure","LV",1,117.46666666669999,3.0110547748809331E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","09:08","NSW3A","URBAN","Planned","",19,51,9.6184101730817525E-4,1.8859627790356376E-5,"NO"]
[null,"2015-07-07","11:23","LLY3","RURAL","Planned","",24,131,8.0591000671591667E-3,6.1519847840909667E-5,"NO"]
[null,"2015-07-07","11:39","KBN1B","RURAL","Asset failure","LV",1,8.4,2.1531946744318387E-5,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","11:42","SMR12A","URBAN","Third party","Vehicle impact",22,107.15,2.3398842415898471E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-07","11:51","NRG14A","RURAL","Asset failure","LV",1,19.7833333333,5.071115235210885E-5,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","13:34","LHM1A","URBAN","Planned","",11,55,6.0053025332450574E-4,1.0918731878627377E-5,"NO"]
[null,"2015-07-07","14:28","BIS12B","RURAL","Asset failure","LV",1,96.366666666699999,2.4701927792796023E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","14:39","NMK12A","URBAN","Asset failure","LV",1,40.433333333299998,4.0134611420497239E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","15:40","KWA2A","URBAN","Asset failure","LV",1,193.1833333333,1.9175609273507286E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","16:16","HPE16A","URBAN","Asset failure","LV",1,51.35,5.0970625633410524E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","16:49","DRA9A","URBAN","Third party","Other",1,37.133333333300001,3.6858991856909029E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","09:07","MGL10A","RURAL","Planned","",11,261,7.3593117979688198E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-07","21:49","KBN5A","RURAL","Animal","Animal impact",23,101,5.9546086056013825E-3,5.8956520847538435E-5,"NO"]
[null,"2015-07-07","08:30","TGW4","RURAL","Planned","",18,306,1.4118805079488771E-2,4.6139885880682247E-5,"NO"]
[null,"2015-07-07","22:12","AGE6A","URBAN","Asset failure","LV",1,109.3333333333,1.0852557746026326E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","20:07","INA1A","URBAN","Asset failure","LV",1,130.9166666667,1.299494528888483E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","08:21","NDH6","URBAN","Planned","",2,298,5.9159674542381057E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-07","06:21","NBR5A","RURAL","Asset failure","LV",1,181.0666666667,4.6413307426650401E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","06:00","BBH11A","URBAN","Planned","",1,96,9.5290750940748011E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","07:42","KMR24A","URBAN","Asset failure","LV",1,43.2833333333,4.2963555589050693E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-07","08:00","CPD1","RURAL","Planned","",4,396,4.0603099575000383E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-07","08:01","CPR5","URBAN","Planned","",3,419,1.2477132701304192E-3,2.9778359668983749E-6,"NO"]
[null,"2015-07-07","08:01","CPR7","URBAN","Planned","",44,419,1.8299794628579481E-2,4.3674927514509508E-5,"NO"]
[null,"2015-07-07","08:03","BTA5A","RURAL","Planned","",53,425,5.7738940525687107E-2,1.3585633064867552E-4,"NO"]
[null,"2015-07-07","08:05","WMR1","RURAL","Planned","",36,433,3.9957141172670831E-2,9.2279771761364507E-5,"NO"]
[null,"2015-07-07","08:06","GAP1A","URBAN","Planned","",38,319,1.2032442530247369E-2,3.7719255580712758E-5,"NO"]
[null,"2015-07-07","08:14","GYGGYS6","RURAL","Planned","",9,408,9.4125367196591803E-3,2.3069942940341127E-5,"NO"]
[null,"2015-07-07","08:14","HDA3A","URBAN","Planned","",18,468,8.3617633950506375E-3,1.7867015801390249E-5,"NO"]
[null,"2015-07-07","08:35","CSE9","URBAN","Planned","",9,394,3.5198021128738798E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-07","08:21","GYGGYS6","RURAL","Planned","",59,397,6.0040808165734469E-2,1.5123629260890297E-4,"NO"]
[null,"2015-07-07","09:02","ACR12A","URBAN","Planned","",12,353,4.2047043852605059E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-07","08:24","BHD35A","RURAL","Unknown","Unknown",1,360,9.227977176136451E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","08:34","CNA7A","RURAL","Planned","",11,321,9.0511076135938364E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-07","08:35","HTN27A","URBAN","Planned","",11,385,4.2037117732715403E-3,1.0918731878627375E-5,"NO"]
[null,"2015-07-07","08:35","NRA15A","RURAL","Planned","",1,229,5.8700188148201311E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","08:35","NRA5A","RURAL","Planned","",18,229,1.0566033866676237E-2,4.6139885880682253E-5,"NO"]
[null,"2015-07-07","08:36","DRA8A","URBAN","Planned","",3,310,9.2312914973849641E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-07","08:36","OXL4A","URBAN","Planned","",11,310,3.3848068823744866E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-07","08:40","BMT5","RURAL","Planned","",58,298.72727272727275,4.4632649608579975E-2,1.4867296561553174E-4,"NO"]
[null,"2015-07-07","08:48","KSN6","URBAN","Planned","",55,252,1.3757602167070494E-2,5.4593659393136878E-5,"NO"]
[null,"2015-07-07","09:00","CRB25A","RURAL","Planned","",73,419,7.8404482746246007E-2,1.8712287051610025E-4,"NO"]
[null,"2015-07-07","09:00","KMR29A","URBAN","Planned","",4,50,1.9852239779322503E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-07","08:21","CSE7","URBAN","Planned","",37,298,1.0944539790340496E-2,3.6726643591746628E-5,"NO"]
[null,"2015-07-07","07:59","LGV5B","RURAL","Overloads","",1,91.633333333300001,2.3488619682583218E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","16:05","KBN2A","RURAL","Asset failure","Distribution substation",1,96,2.4607939136363867E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-07","17:20","AHD15B","URBAN","Asset failure","LV",66,73,4.7824045628387908E-3,6.5512391271764262E-5,"NO"]
[null,"2015-07-08","12:25","SMF5A","RURAL","Planned","",13,80,2.6658600731060858E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-08","09:09","ABY2A","RURAL","Planned","",2,293,1.5021096181155446E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-08","02:40","AHL14A","URBAN","Animal","Animal impact",632,80.966666666699993,5.0792881913273899E-2,6.2733077702659113E-4,"NO"]
[null,"2015-07-08","09:14","BTA15A","URBAN","Asset failure","LV",1,69.883333333300001,6.9367034495549621E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","09:14","KSN2A","URBAN","Planned","",25,274,6.7993921244179564E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-08","09:19","BHL3A","URBAN","Planned","",17,276,4.6573354522290592E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-08","09:22","BRD5A","RURAL","Overloads","",1,143.86666666670001,3.6877731011309404E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-08","09:24","NVL24A","URBAN","Planned","",93,259,2.3909044978227056E-2,9.2312914973849636E-5,"NO"]
[null,"2015-07-08","09:57","AHL12A","URBAN","Planned","",6,306,1.8224356117418057E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-08","09:57","AHL6A","URBAN","Planned","",2,306,6.0747853724726854E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-08","10:00","SMF5A","RURAL","Planned","",8,142,2.9119394644697245E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-08","10:49","KMR24A","URBAN","Asset failure","LV",1,108.5,1.0769840080282458E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","08:59","GYM7A","RURAL","Planned","",5,271,3.4733080760180252E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-08","12:02","NSW33A","URBAN","Asset failure","LV",1,148.35,1.4725398856312466E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","09:08","ABY2A","RURAL","Planned","",60,322,4.9523477511932285E-2,1.5379961960227417E-4,"NO"]
[null,"2015-07-08","12:32","AHL9A","URBAN","Asset failure","LV",1,70.366666666699999,6.984679695694943E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","12:42","CHL5","URBAN","Overloads","",1,61.433333333299998,6.0979463188785863E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","13:09","BDT4","RURAL","Planned","",1,76,1.9481285149621397E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-08","13:35","BPN36A","URBAN","Overloads","",1,119.2666666667,1.1838552321739295E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","14:25","BLH12A","RURAL","Asset failure","LV",1,122.6,3.1426388938731359E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-08","16:58","NIP4A","RURAL","Overloads","",1,124.1,3.181088798773704E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-08","16:59","LDR8","URBAN","Asset failure","LV",1,103.4166666667,1.0265262319227985E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","17:34","SHW6B","URBAN","Asset failure","LV",1,95.583333333300004,9.4877162611979037E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","19:01","SGT24A","URBAN","Asset failure","LV",1,26.833333333300001,2.6635088370557936E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","19:27","WRG4A","URBAN","Overloads","",1,121.4166666667,1.2051963899367011E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","20:10","BPN36A","URBAN","Asset failure","LV",1,234.8166666667,2.3308183854242872E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","20:40","PWC5","RURAL","Asset failure","LV",1,112.6833333333,2.8884423003629672E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-08","22:45","PWC5","RURAL","Other","Water Ingress",129,214.45,7.0912006110971551E-2,3.3066918214488952E-4,"NO"]
[null,"2015-07-08","11:00","GYM2A","RURAL","Planned","",3,110,8.4589790781250808E-4,7.68998098011371E-6,"NO"]
[null,"2015-07-08","08:15","NGE4B","URBAN","Planned","",1,172,1.7072926210217351E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","06:52","NRG5A","URBAN","Planned","",1,40,3.9704479558645003E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","07:31","CHL7","URBAN","Overloads","",1,40.016666666699997,3.9721023091827524E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","07:54","LGL11A","URBAN","Asset failure","LV",1,80.383333333300001,7.978946037969394E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","08:00","MGL10A","RURAL","Planned","",30,448.66666666666669,3.5066313269318514E-2,7.6899809801137087E-5,"NO"]
[null,"2015-07-08","08:03","CLD11","RURAL","Planned","",55,462,6.513413890156311E-2,1.4098298463541801E-4,"NO"]
[null,"2015-07-08","08:03","SRD18A","URBAN","Planned","",1,263,2.6105695309809092E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","08:07","CMY4","RURAL","Planned","",8,348,7.1363023495455225E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-08","08:09","CMY4","RURAL","Planned","",30,361,2.7760831338210487E-2,7.6899809801137087E-5,"NO"]
[null,"2015-07-08","08:10","BKD5B","URBAN","Planned","",2,358,7.1071018409974557E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-08","08:10","KLG14A","URBAN","Planned","",1,195,1.9355933784839441E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-08","08:10","SHW6A","URBAN","Planned","",2,314,6.2336032907072661E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-08","09:13","UMG5A","URBAN","Planned","",25,231,5.7323342362793723E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-08","08:14","NBR7A","RURAL","Planned","",53,361,4.9044135364171869E-2,1.3585633064867552E-4,"NO"]
[null,"2015-07-08","08:52","BDT3","RURAL","Planned","",30,287.73066666664005,4.3092218251910182E-2,7.68998098011371E-5,"NO"]
[null,"2015-07-08","08:38","ZMR4A","URBAN","Planned","",9,248,2.2155099593723915E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-08","08:47","CSE9","URBAN","Planned","",14,328,4.5580742533324458E-3,1.389656784552575E-5,"NO"]
[null,"2015-07-08","08:45","BBSRDL12","RURAL","Planned","",7,81,1.4534064052414909E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-08","08:45","ARG3","URBAN","Planned","",28,201,5.586420273901352E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-08","08:10","ZMR3","URBAN","Planned","",10,365,3.6230337597263568E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-08","08:40","LBH1B","RURAL","Planned","",20,433,2.2198411762594909E-2,5.1266539867424725E-5,"NO"]
[null,"2015-07-08","08:22","NSW17","URBAN","Planned","",35,291,1.0109753107619985E-2,3.4741419613814376E-5,"NO"]
[null,"2015-07-08","08:36","MHL2A","RURAL","Planned","",6,334,5.1369072947159578E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-08","08:35","TRP1","RURAL","Planned","",6,203,3.1221322779261661E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-08","08:35","AGT31A","RURAL","Planned","",15,240,9.227977176136451E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-08","08:34","AHL11A","RURAL","Planned","",7,176,3.1580188558333632E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-08","08:30","AHL6A","URBAN","Planned","",12,382,4.5501333574207176E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-08","08:24","ABY2A","RURAL","Planned","",1,149,3.8193572201231422E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-08","08:23","HTN24A","URBAN","Planned","",2,56,1.1117254276420601E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-08","08:43","KSN7","RURAL","Planned","",2,339,1.7379357015056983E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-09","08:01","CPS12B","RURAL","Planned","",3,260,1.9096786100615711E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-09","05:01","LHM8B","URBAN","Planned","",1,408,4.0498569149817904E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","06:37","MCW7","RURAL","Overloads","",1,72.383333333300001,1.8554215220343588E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","07:42","NBR2B","URBAN","Asset failure","LV",1,173.88333333329999,1.7259868134802663E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:22","BHL3A","URBAN","Planned","",1,292,2.8984270077810856E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:02","LGV6A","RURAL","Planned","",36,410.16666666666669,3.8631901117097897E-2,9.227977176136452E-5,"NO"]
[null,"2015-07-09","11:00","CHL2","URBAN","Planned","",7,141,9.7970803310956558E-4,6.9482839227628759E-6,"NO"]
[null,"2015-07-09","10:57","TRG7A","URBAN","Asset failure","LV",1,68.483333333299996,6.7977377710997045E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","10:18","MAI5","URBAN","Asset failure","LV",1,58.9,5.8464846150104771E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:37","CPK7","URBAN","Planned","",24,261,6.2177214988838082E-3,2.3822687735187003E-5,"NO"]
[null,"2015-07-09","12:47","RCF2A","URBAN","Asset failure","LV",1,17.333333333300001,1.720527447537975E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:22","ZMR4A","URBAN","Planned","",3,292,8.6952810233432564E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-09","13:01","NRA3B","URBAN","Planned","",1,112,1.1117254276420601E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:20","IPS2B","RURAL","Planned","",12,282,8.6742985455682646E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-09","09:15","CRY2A","RURAL","Planned","",2,51,2.6145935332386611E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-09","09:14","LWD1","RURAL","Planned","",1,319,8.1770131088542439E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","09:12","NRG9","RURAL","Planned","",31,123,9.7739658257245243E-3,7.9463136794508333E-5,"NO"]
[null,"2015-07-09","09:04","PPE6A","RURAL","Planned","",10,771,1.9650464731183898E-2,2.5633269933712362E-5,"NO"]
[null,"2015-07-09","07:44","TWG11","URBAN","Asset failure","LV",1,299.86666666669998,2.976512484246751E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:25","UMG5A","URBAN","Planned","",12,284,3.3828216583965546E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-09","17:36","BKD13A","URBAN","Asset failure","LV",1,127.2,1.2626024499649111E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","22:07","YTA43A","URBAN","Overloads","",1,86.833333333300004,8.6191807708525445E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","20:46","TSN15A","URBAN","Asset failure","LV",1,98.216666666699993,9.7491040849656007E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","18:54","GGR5","RURAL","Overloads","",1,61.6,1.5790094279166816E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","18:51","CHL11A","URBAN","Overloads","",70,68.583333333300004,4.7653647236925566E-3,6.9482839227628753E-5,"NO"]
[null,"2015-07-09","18:29","FGBSGT23","URBAN","Asset failure","LV",1,158.3166666667,1.5714702138652014E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","12:47","IPL3","RURAL","Planned","",1,109,2.7940264227746477E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","17:36","BKD13A","URBAN","Overloads","",1,80.383333333300001,7.978946037969394E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:00","NRA5A","RURAL","Planned","",21,249,1.3403636848338195E-2,5.3829866860795964E-5,"NO"]
[null,"2015-07-09","17:26","MDRMLD11","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",28,173.45,4.8207193856128839E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-09","17:12","RIS4","RURAL","Vegetation","Grow-in - NSP responsibility",94,58,1.3975258767859978E-2,2.4095273737689623E-4,"NO"]
[null,"2015-07-09","17:05","NVL27A","URBAN","Overloads","",1,63.5333333333,6.3063948365614734E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","15:16","CBT7A","URBAN","Overloads","",1,77.433333333299998,7.6861255012243874E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","14:32","NRG5A","URBAN","Asset failure","LV",1,115.3,1.1444816232779423E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","13:19","MSV1","RURAL","Other","Water Ingress",1,190.2,4.8754479413920911E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","17:56","CNB21B","URBAN","Asset failure","LV",1,152.6833333333,1.5155530718194478E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","08:04","RLB15A","URBAN","Planned","",44,300,1.3102478254352852E-2,4.3674927514509501E-5,"NO"]
[null,"2015-07-09","09:02","RST15A","URBAN","Planned","",1,13,1.2903955856559627E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","08:10","WMD11A","RURAL","Planned","",46,252,2.9714086507159371E-2,1.1791304169507687E-4,"NO"]
[null,"2015-07-09","08:10","LGV6A","RURAL","Planned","",11,477,1.3449776734218877E-2,2.8196596927083601E-5,"NO"]
[null,"2015-07-09","08:09","RCF11A","URBAN","Planned","",1,431,4.2781576724439991E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","08:06","ZMR5","URBAN","Planned","",16,264,4.1927930413929127E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-09","08:14","HTN3A","URBAN","Planned","",4,287,1.1395185633331117E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-09","08:05","JBB16A","RURAL","Planned","",59,352.66666666666669,6.7782055685715603E-2,1.5123629260890294E-4,"NO"]
[null,"2015-07-09","08:15","BHL3A","URBAN","Planned","",2,403,8.000452631066969E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-09","08:02","CLM10B","RURAL","Planned","",16,393,1.6118200134318333E-2,4.1013231893939782E-5,"NO"]
[null,"2015-07-09","08:01","NMC5A","RURAL","Planned","",40,525,5.4309209008556389E-2,1.0253307973484945E-4,"NO"]
[null,"2015-07-09","08:01","GAP8A","URBAN","Planned","",4,449,1.7827311321831608E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-09","08:01","GAP6A","URBAN","Planned","",11,449,4.902510613503692E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-09","08:01","GAP1A","URBAN","Planned","",40,449,1.7827311321831608E-2,3.9704479558645003E-5,"NO"]
[null,"2015-07-09","08:43","RBA1A","RURAL","Planned","",7,307,5.508589708754787E-3,1.7943288953598652E-5,"NO"]
[null,"2015-07-09","08:05","SPC2B","RURAL","Planned","",1,96,2.4607939136363867E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","08:30","NIP4A","RURAL","Planned","",13,395,1.3162684110961298E-2,3.3323250913826072E-5,"NO"]
[null,"2015-07-09","09:00","CPS15A","URBAN","Asset failure","LV",1,88.55,8.7895791622950376E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","09:00","BHD5A","URBAN","Planned","",36,335,1.1970900586931468E-2,3.5734031602780506E-5,"NO"]
[null,"2015-07-09","08:49","WNM1A","URBAN","Planned","",45,246,1.0988214717855004E-2,4.4667539503475631E-5,"NO"]
[null,"2015-07-09","08:42","CSE2","URBAN","Planned","",6,217,1.292380809633895E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-09","08:40","FDS4","RURAL","Planned","",2,380.5,1.950691841955511E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-09","08:14","HDA3B","RURAL","Planned","",46,287,3.3841042966487059E-2,1.1791304169507687E-4,"NO"]
[null,"2015-07-09","08:30","YTA39A","RURAL","Planned","",18,210,9.6893760349432735E-3,4.6139885880682253E-5,"NO"]
[null,"2015-07-09","07:46","PWC4","RURAL","Asset failure","LV",1,286.14999999999998,7.3349601915317919E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-09","08:30","CSE7","URBAN","Planned","",12,249,2.9659246230307819E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-09","08:30","CPR4","URBAN","Planned","",49,390,1.896881510914265E-2,4.8637987459340128E-5,"NO"]
[null,"2015-07-09","08:30","AMR2","RURAL","Planned","",143,368.44444444444446,0.13393896205763386,3.6655576005208677E-4,"NO"]
[null,"2015-07-09","08:20","CRY2A","RURAL","Planned","",215,358.12000000000006,0.19756073803310795,5.5111530357481581E-4,"NO"]
[null,"2015-07-09","08:16","SBH9","URBAN","Planned","",25,133,3.3004348633123661E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-09","08:16","LLY3","RURAL","Planned","",2,179,9.1767106362690258E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-09","08:33","BHD7A","URBAN","Planned","",1,212,2.1043374166081853E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-09","08:52","CPD1","RURAL","Planned","",13,213,7.0978524446449536E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-09","13:55","THL3","RURAL","Asset failure","LV",7,59,1.0586540482623206E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-09","09:01","CSE7","URBAN","Asset failure","HV",97,50.5,4.8623098279505636E-3,9.628336292971414E-5,"NO"]
[null,"2015-07-09","19:55","CMA18A","URBAN","Asset failure","LV",22,118,2.5768207233560609E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-10","08:22","CLD25A","URBAN","Planned","",1,377,3.7421471984022919E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","06:00","NRA3B","URBAN","Planned","",1,173,1.7172187409113964E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","08:45","KSN8","RURAL","Planned","",4,35,3.588657790719731E-4,1.0253307973484946E-5,"NO"]
[null,"2015-07-10","08:44","SPC2B","RURAL","Planned","",1,121,3.1016256619791961E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","08:38","383","URBAN","Planned","",1,181.98333333330001,1.8063883845865225E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","08:36","NRA1A","RURAL","Planned","",2,210,1.0765973372159194E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-10","08:36","KRA7","URBAN","Planned","",85,436,3.6786200311084601E-2,8.4372019062120641E-5,"NO"]
[null,"2015-07-10","08:36","GYN13A","RURAL","Planned","",21,321.87777777779996,1.7367437544538573E-2,5.3829866860795957E-5,"NO"]
[null,"2015-07-10","08:35","PPE6A","RURAL","Planned","",1,287,7.3567484709754485E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","08:35","HTN2A","URBAN","Planned","",15,374,5.5685532580999619E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-10","08:34","NRG10","URBAN","Planned","",67,79,5.2538952575977007E-3,6.6505003260730391E-5,"NO"]
[null,"2015-07-10","08:32","WMD14A","RURAL","Planned","",77,276,5.4475825263125513E-2,1.973761784895852E-4,"NO"]
[null,"2015-07-10","08:31","EMP21A","RURAL","Planned","",2,39,1.9993950548295643E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-10","08:53","KRA7","URBAN","Planned","",17,419,7.0703751974057092E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-10","08:14","UMG5A","URBAN","Planned","",3,168,5.0027644243892709E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-10","06:19","NRA3B","URBAN","Planned","",5,139,6.8986533233145696E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-10","08:05","LHM3","RURAL","Planned","",3,235,1.8071455303267216E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-10","08:06","AGT31A","RURAL","Planned","",37,236.93333333334999,2.2463288885244976E-2,9.4843098754735753E-5,"NO"]
[null,"2015-07-10","08:08","KMR22A","URBAN","Planned","",30,305,9.0823996990400443E-3,2.9778359668983753E-5,"NO"]
[null,"2015-07-10","08:11","MGL10A","RURAL","Planned","",8,329,6.7466766465530941E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-10","08:30","GAP1A","URBAN","Planned","",12,246,2.9301905914280012E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-10","08:14","LBH5A","RURAL","Planned","",42,336,3.6173670530454886E-2,1.0765973372159193E-4,"NO"]
[null,"2015-07-10","08:30","ARG3","URBAN","Planned","",78,219,1.6955797995519349E-2,7.7423735139357761E-5,"NO"]
[null,"2015-07-10","08:17","SMR9A","URBAN","Planned","",8,319,2.5331457958415512E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-10","08:18","NRA1A","RURAL","Planned","",97,279,6.9371318421605765E-2,2.4864271835700993E-4,"NO"]
[null,"2015-07-10","08:20","CHL7","URBAN","Planned","",10,298,2.9579837271190529E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-10","08:20","FDS3","RURAL","Planned","",5,198,2.537693723437524E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-10","08:22","CLD17A","URBAN","Planned","",119,377,4.4531551660987267E-2,1.1812082668696889E-4,"NO"]
[null,"2015-07-10","08:55","SMF5A","RURAL","Planned","",12,195,5.9981851644886931E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-10","08:11","MGL2A","RURAL","Planned","",3,329,2.5300037424574105E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-10","11:41","CMY1","RURAL","Planned","",3,79,6.0750849742898308E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-10","23:50","CLM9","URBAN","Asset failure","LV",1,64.016666666700004,6.354371082701453E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","22:08","GBN4","RURAL","Overloads","",1,105.7,2.7094366319933968E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","21:15","BTA13A","URBAN","Third party","Vehicle impact",11,65,7.0971757211077944E-4,1.0918731878627377E-5,"NO"]
[null,"2015-07-10","21:10","NMK3A","URBAN","Asset failure","LV",1,155.0833333333,1.5393757595546348E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","20:30","LLY4","RURAL","Overloads","",1,211.9166666667,5.4321171201200658E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","19:17","BKD12A","URBAN","Overloads","",1,94.616666666699999,9.3917637689377962E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","19:16","AHD15A","URBAN","Asset failure","LV",1,129.5833333333,1.2862597023682729E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","17:39","TMH15A","URBAN","Asset failure","LV",1,102.53333333330001,1.0177581593529362E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","15:53","TWT15A","RURAL","Overloads","",1,143.05000000000001,3.6668392640175541E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","15:22","RBA34A","URBAN","Asset failure","LV",1,26.816666666700002,2.6618544837474678E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","13:55","CCYUPC2","RURAL","Asset failure","LV",1,66.266666666700004,1.6986313542748606E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","13:41","BDL4","URBAN","Overloads","",1,200.28333333329999,1.9880363785673233E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-10","13:10","LRE6A","RURAL","Planned","",4,60,6.1519847840909669E-4,1.0253307973484946E-5,"NO"]
[null,"2015-07-10","08:53","BTN2","RURAL","Planned","",1,227,5.818752274952707E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","09:12","BBS11A","URBAN","Planned","",29,256,7.3691514060845132E-3,2.878574768001763E-5,"NO"]
[null,"2015-07-10","08:59","BDA12B","URBAN","Planned","",6,295,1.7569232204700414E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-10","09:00","BDL2","URBAN","Planned","",21,266,5.5447305703647748E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-10","09:00","MDR33A","URBAN","Planned","",31,266,8.1850784610146676E-3,3.0770971657949879E-5,"NO"]
[null,"2015-07-10","09:02","GYM7A","RURAL","Planned","",6,269,4.1372097673011759E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-10","09:05","TRP4","RURAL","Planned","",2,169,8.6640452375947793E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-10","11:53","CLM10B","RURAL","Asset failure","LV",1,45.75,1.1727220994673407E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","09:10","MGL10A","RURAL","Planned","",20,393,2.0147750167897917E-2,5.1266539867424725E-5,"NO"]
[null,"2015-07-10","11:46","BTA5A","RURAL","Planned","",5,21,2.6914933430397984E-4,1.2816634966856181E-5,"NO"]
[null,"2015-07-10","09:26","KCY2","RURAL","Overloads","",1,211.4166666667,5.4193004851532103E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","09:32","MLT5A","URBAN","Planned","",7,328,2.2790371266662233E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-10","09:45","IPL1","RURAL","Asset failure","LV",1,101.15,2.5928052537950056E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-10","10:12","NMC5A","RURAL","Planned","",33,274,2.3177602674062721E-2,8.4589790781250797E-5,"NO"]
[null,"2015-07-10","10:30","SMF5A","RURAL","Planned","",13,195,6.4980339281960845E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-10","08:45","CRM13A","URBAN","Planned","",2,35,6.9482839227628753E-5,1.9852239779322501E-6,"NO"]
[null,"2015-07-10","09:06","BIS16A","URBAN","Planned","",30,369,1.0988214717855006E-2,2.9778359668983753E-5,"NO"]
[null,"2015-07-10","08:50","NIP4A","RURAL","Planned","",5,188,2.4095273737689622E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-10","10:08","GBN4","RURAL","Asset failure","HV",11,67,1.8891719941146012E-3,2.8196596927083598E-5,"NO"]
[null,"2015-07-11","16:29","TCB3","RURAL","Asset failure","LV",1,179.51666666669999,4.6015991742677856E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-11","08:28","SPO41A","URBAN","Asset failure","LV",1,175.95,1.7465007945858971E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","09:28","JBB1B","RURAL","Overloads","",1,79.45,2.0365632962334474E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-11","12:38","CMD15A","URBAN","Asset failure","LV",1,128.55000000000001,1.2760027118159539E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","13:20","WFD1B","RURAL","Third party","Unauthorised access",310,191.72572463764979,0.17477314556106219,7.9463136794508289E-4,"NO"]
[null,"2015-07-11","13:43","NRA13A","RURAL","Asset failure","LV",1,93.216666666699993,2.3894479789884085E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-11","14:44","CCY26A","RURAL","Overloads","",1,89.533333333300007,2.2950321013975262E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-11","00:31","GTN3A","URBAN","Third party","Vehicle impact",25,37,9.1816608979366577E-4,2.4815299724153129E-5,"NO"]
[null,"2015-07-11","17:18","CVL17A","URBAN","Asset failure","LV",1,14.983333333299999,1.4872636301309354E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","17:20","HDA10A","URBAN","Asset failure","LV",1,87.9,8.7250593830122411E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","17:24","HDA10A","URBAN","Asset failure","LV",1,136.8333333333,1.358224071568317E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","18:12","CVL17A","URBAN","Asset failure","LV",1,115.6,1.1474594592448406E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","18:34","BBH13B","URBAN","Asset failure","LV",1,201.78333333329999,2.0029255584018153E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","18:53","RBA12A","URBAN","Planned","",1,813,8.069935470294597E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","14:32","MDR33A","URBAN","Asset failure","LV",1,68.383333333300001,6.787811651210044E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","09:11","CMV8","URBAN","Asset failure","LV",1,8.7833333332999999,8.7184419697193778E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-11","20:41","CBW7","RURAL","Asset failure","LV",65,176.21666666670001,2.9360560992662477E-2,1.6661625456913036E-4,"NO"]
[null,"2015-07-12","10:17","PWC5","RURAL","Weather","",13,162.9,5.4283575738622667E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-12","04:26","CMY1","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",52,122.33333333329999,1.6306177447161119E-2,1.3329300365530426E-4,"NO"]
[null,"2015-07-12","01:27","CPK9","RURAL","Asset failure","LV",1,131.38333333329999,3.367784448123388E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","00:15","CBT12A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",212,13.100000000000009,7.1188717259906007E-3,5.4342532259470209E-4,"NO"]
[null,"2015-07-12","00:15","BWH8A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",525,50.304964539034032,6.9057994418819935E-2,1.3457466715198992E-3,"NO"]
[null,"2015-07-12","09:23","MFD3A","RURAL","Overloads","",1,103.6166666667,2.6560339862990171E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","05:30","YTA43A","URBAN","Weather","",1526,106.90000000000006,0.16192419819285059,1.5147258951623069E-3,"NO"]
[null,"2015-07-12","10:15","CBW6","RURAL","Overloads","",1,50.55,1.2957617951491599E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","05:53","DRD3A","URBAN","Animal","Animal nesting/burrowing, etc and other",97,76.366666666699999,7.3528394824023792E-3,9.628336292971414E-5,"NO"]
[null,"2015-07-12","10:20","ACR5","RURAL","Overloads","",1,132.75,3.4028165837003162E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","00:13","BLN15A","URBAN","Animal","Animal impact",2127,55.25,0.11664853495433487,2.111285700530948E-3,"NO"]
[null,"2015-07-12","10:30","WRG19A","URBAN","Planned","",5,169,8.3875713067637573E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-12","10:45","LTN3","URBAN","Overloads","",1,131.63333333329999,1.3066082481420785E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","11:29","CRY2A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",3,356,2.7376332289204804E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-12","11:51","CCY8A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,69.833333333300004,1.7900566837033923E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","12:17","CPS12B","RURAL","Weather","",43,192.8,2.1839545983522932E-2,1.1022306071496317E-4,"NO"]
[null,"2015-07-12","09:26","TWT15A","RURAL","Asset failure","LV",1,164.9166666667,4.2273534332355848E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","19:32","BKD15A","URBAN","Unknown","Unknown",121,57.266666666699997,6.8780731680806754E-3,1.2010605066490114E-4,"NO"]
[null,"2015-07-12","08:01","NRA1A","RURAL","Planned","",16,204,8.3666993063637157E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-12","08:07","NSW7A","URBAN","Planned","",12,426,5.0742324875948314E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-12","08:10","KWH3","RURAL","Planned","",2,281,1.4405897702746348E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-12","08:11","FDS1","RURAL","Asset failure","LV",1,229.71666666670001,5.8883893249401468E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","08:14","WED22B","URBAN","Planned","",2,193,3.831482277409243E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-12","08:39","RBK11A","RURAL","Third party","Vehicle impact",983,77.373717948692303,0.16137630152920451,2.5197504344839257E-3,"NO"]
[null,"2015-07-12","05:18","JBB16A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",228,122.89824561402101,7.1597482471106685E-2,5.8443855448864191E-4,"NO"]
[null,"2015-07-12","07:48","SPE5","URBAN","Planned","",1,392,3.8910389967472103E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","07:58","HMT9A","RURAL","Planned","",11,167,4.7088316868229615E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-12","07:31","HTL6A","URBAN","Planned","",1,318,3.1565061249122777E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","13:20","MBG2","RURAL","Asset failure","LV",1,111.46666666669999,2.8572551552786591E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","07:06","PWC4","RURAL","Weather","",10,143.9,3.6886275434612091E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-12","07:04","HMT9A","RURAL","Planned","",5,200,2.5633269933712363E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-12","06:55","BRD10B","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,80.25,2.0570699121804173E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","06:36","CMA18A","URBAN","Asset failure","LV",1,10.35,1.0273534085799395E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","06:35","TWT15A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",251,98.083333333300033,6.3106333639202233E-2,6.4339507533618028E-4,"NO"]
[null,"2015-07-12","09:05","CPD1","RURAL","Overloads","",1,79.083333333300004,2.0271644305902317E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","18:00","COR25A","RURAL","Asset failure","LV",1,78.933333333299998,2.0233194401001747E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","17:56","TMH12A","URBAN","Asset failure","LV",1,215.85,2.1425529781833811E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","22:10","NSW26","URBAN","Asset failure","LV",1,139.69999999999999,1.3866789485856768E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","14:00","CVL7A","RURAL","Asset failure","LV",1,99.85,2.5594820028811794E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","19:34","BLB8B","URBAN","Overloads","",1,124.05,1.2313351723124781E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","22:41","ACR6","RURAL","Asset failure","LV",1,145.4166666667,3.7275046695281938E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","17:40","NIP2A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",60,70,4.1689703536577256E-3,5.9556719337967505E-5,"NO"]
[null,"2015-07-12","17:25","BLH12A","RURAL","Overloads","",10,115,2.947826042376922E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-12","17:21","YTA39A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,128.1666666667,3.2853307631716558E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-12","16:06","GTN3A","URBAN","Asset failure","LV",1,59.7833333333,5.9341653406991762E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","16:01","MTG11A","URBAN","Asset failure","LV",1,126.03333333330001,1.2510219767599757E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","14:52","KSN1","URBAN","Asset failure","LV",1,129.69999999999999,1.2874177496890641E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-12","07:42","GGR2","RURAL","Asset failure","HV",123,61.983333333299981,1.9542676831102133E-2,3.1528922018466207E-4,"NO"]
[null,"2015-07-12","11:24","CBW7","RURAL","Asset failure","LV",8,75.166666666699996,1.5414139653479202E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-12","08:10","WMD6A","URBAN","Asset failure","HV",12,60,7.1468063205561009E-4,1.1911343867593501E-5,"NO"]
[null,"2015-07-12","18:06","LTN9","URBAN","Asset failure","Distribution substation",53,188.4,9.9114292322245532E-3,5.2608435415204633E-5,"NO"]
[null,"2015-07-13","20:01","GYM3","URBAN","Overloads","",1,65.349999999999994,6.4867193478936269E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","20:20","NSW28","URBAN","Asset failure","LV",1,103.55,1.0278497145744225E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","20:27","BPN35A","URBAN","Overloads","",1,153.8333333333,1.5269681096925582E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","19:59","BLH12A","RURAL","Overloads","",10,145.46666666670001,3.7287863330248798E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-13","20:28","SBH11","URBAN","Overloads","",121,31.416666666699999,3.7733317583929812E-3,1.2010605066490114E-4,"NO"]
[null,"2015-07-13","20:34","SHW5A","URBAN","Overloads","",64,75.2,4.777242980496167E-3,6.3527167293832003E-5,"NO"]
[null,"2015-07-13","20:51","SGT7","URBAN","Asset failure","LV",1,40.416666666700003,4.0118067887413984E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","19:26","NBR12A","RURAL","Overloads","",74,108.1,2.0505077950773866E-2,1.8968619750947151E-4,"NO"]
[null,"2015-07-13","20:59","AHL11A","RURAL","Overloads","",13,150.6833333333,5.0212585251972483E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-13","16:55","MBG1","RURAL","Asset failure","LV",1,87.983333333299996,2.2553005330002717E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","23:02","CLM10B","RURAL","Animal","Animal impact",165,97.266666666700019,4.1138834916629077E-2,4.2294895390625393E-4,"NO"]
[null,"2015-07-13","20:54","KBN2A","RURAL","Asset failure","LV",1,123.1666666667,3.1571644135030939E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","19:17","NSW16A","URBAN","Network business","Network error",138,92.433333333299998,1.2661560008849534E-2,1.3698045447732527E-4,"NO"]
[null,"2015-07-13","18:06","TWT11A","RURAL","Overloads","",1,271.89999999999998,6.9696860949763917E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","18:00","MGL2A","RURAL","Asset failure","LV",1,215.45,5.5226880072183288E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","17:52","AHD16","URBAN","Asset failure","LV",1,127.4,1.2645876739428435E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","17:14","AMR1","RURAL","Overloads","",1,128.86666666670001,3.3032740521252548E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","16:51","BKD15A","URBAN","Asset failure","LV",1,94.7,9.4000355355092053E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","15:10","RBA43A","RURAL","Asset failure","LV",1,137.75,3.5309829333688781E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","14:54","BSEENG15OLD","URBAN","Asset failure","LV",1,54.566666666700002,5.416352753128465E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","14:38","SMF6A","RURAL","Planned","",15,217,8.3436293634233747E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-13","14:27","BPN26A","RURAL","Asset failure","LV",1,122.3833333333,3.1370850187199768E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","21:29","NSW16A","URBAN","Overloads","",138,144.73333333330001,1.9825637778013643E-2,1.3698045447732527E-4,"NO"]
[null,"2015-07-13","17:47","CNB25A","URBAN","Asset failure","LV",1,128.11666666670001,1.2717013931974318E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","10:49","JBB1B","RURAL","Asset failure","LV",1,223.25,5.722627512701285E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","08:46","FDS1","RURAL","Planned","",2,186,9.5355764153409999E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-13","08:49","WRG15A","URBAN","Overloads","",1,34.4,3.41458524204347E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","09:18","GNA7A","URBAN","Planned","",18,219,3.9128764605044653E-3,1.7867015801390249E-5,"NO"]
[null,"2015-07-13","09:26","SRD18A","URBAN","Planned","",53,54,2.8408555124210502E-3,5.2608435415204633E-5,"NO"]
[null,"2015-07-13","09:44","TGP9A","URBAN","Overloads","",1,56.2166666667,5.5801337313078758E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","09:45","IPL3","RURAL","Planned","",3,293,2.2531644271733169E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-13","09:50","NDH6","URBAN","Planned","",18,185,3.3053979232571967E-3,1.7867015801390253E-5,"NO"]
[null,"2015-07-13","08:35","SRD19A","URBAN","Planned","",2,294,5.8365584951208154E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-13","10:28","LTN3","URBAN","Overloads","",1,142.3166666667,1.4126522956306212E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","10:18","SMF6A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",77,238.97777777776673,4.4575060195460349E-2,1.9737617848958517E-4,"NO"]
[null,"2015-07-13","12:05","SHW10A","URBAN","Planned","",10,97,9.6283362929714138E-4,9.9261198896612508E-6,"NO"]
[null,"2015-07-13","12:37","MFD2A","URBAN","Planned","",6,80,4.7645375470374004E-4,5.9556719337967498E-6,"NO"]
[null,"2015-07-13","12:39","KSN7","RURAL","Overloads","",1,67.833333333300004,1.7387901438359676E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","13:00","NRA3B","URBAN","Planned","",1,80,7.9408959117290007E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","13:58","BPN28A","RURAL","Vegetation","Grow-in - NSP responsibility",1730,1.649999999999999,7.3170169025781936E-3,4.4345556985322387E-3,"NO"]
[null,"2015-07-13","00:47","CLD2","URBAN","Planned","",16,226,3.5892849521015086E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-13","08:26","BRT3","URBAN","Asset failure","LV",1,63.416666666700003,6.294814363363486E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","10:16","TRG3B","URBAN","Vegetation","Grow-in - NSP responsibility",43,81.099999999999994,3.4615357891215684E-3,4.2682315525543378E-5,"NO"]
[null,"2015-07-13","07:04","HWD16A","URBAN","Planned","",1,122,1.2109866265386727E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","05:55","MLB12A","RURAL","Overloads","",1,119.9166666667,3.0738562862185284E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","10:47","BLBNFM6","URBAN","Overloads","",1,60.55,6.0102655931898872E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","08:35","GYGGYS6","RURAL","Planned","",3,103,7.9206804095171201E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-13","06:05","NRA3B","URBAN","Planned","",2,145,2.8785747680017631E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-13","06:06","CMPCQE8","CBD","Asset failure","LV",1,218,5.5768738807879255E-2,2.5581990278843696E-4,"NO"]
[null,"2015-07-13","06:43","CBW9","URBAN","Unknown","Unknown",20,84,1.6675881414630902E-3,1.9852239779322502E-5,"NO"]
[null,"2015-07-13","06:01","CPD1","RURAL","Animal","Animal impact",1,125.9333333333,3.2280831269846559E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-13","07:20","TMH15A","URBAN","Asset failure","LV",1,68.016666666700004,6.7514158782879034E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","08:00","LGV2B","RURAL","Planned","",33,586.79999999999995,4.9210751618741E-2,8.458979078125081E-5,"NO"]
[null,"2015-07-13","08:22","CPB8","RURAL","Planned","",15,302,1.1611871279971701E-2,3.844990490056855E-5,"NO"]
[null,"2015-07-13","08:01","CSE6","URBAN","Planned","",22,181,3.9525809400631105E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-13","08:05","SGT6","URBAN","Planned","",9,190,1.6973665011320738E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-13","08:15","CBT12A","RURAL","Planned","",11,68,1.9173685910416848E-3,2.8196596927083598E-5,"NO"]
[null,"2015-07-13","08:20","BRT3","URBAN","Planned","",9,295,2.6353848307050622E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-13","08:22","CLR8","RURAL","Planned","",3,302,2.3223742559943402E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-13","08:27","SHW6B","URBAN","Planned","",43,158,6.743805853035854E-3,4.2682315525543378E-5,"NO"]
[null,"2015-07-13","06:33","SFD2A","URBAN","Asset failure","LV",1,117.03333333330001,1.1616868977530243E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-13","08:30","CBW6","RURAL","Planned","",4,241,2.471047221609872E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-13","08:35","CHL5","URBAN","Planned","",14,294,4.0855909465845712E-3,1.3896567845525752E-5,"NO"]
[null,"2015-07-13","11:55","NIP4A","RURAL","Asset failure","LV",7,215.1833333333,3.8610967279979393E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-13","13:35","LRE8A","RURAL","Asset failure","LV",9,130,2.9990925822443466E-3,2.3069942940341127E-5,"NO"]
[null,"2015-07-13","14:33","PRG1","RURAL","Asset failure","LV",49,77,9.6714327459896752E-3,1.2560302267519059E-4,"NO"]
[null,"2015-07-13","15:58","BPN26A","RURAL","Asset failure","Distribution substation",12,183,5.6290660774432353E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-13","23:29","KCY5","RURAL","Asset failure","HV",115,309.91666666669994,9.1358042096674585E-2,2.9478260423769232E-4,"NO"]
[null,"2015-07-13","09:50","SPD11A","URBAN","Asset failure","LV",9,275,2.4567146726911598E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-14","08:06","NVL3","URBAN","Planned","",54,410,2.1976429435710008E-2,5.3601047404170755E-5,"NO"]
[null,"2015-07-14","08:08","CSE6","URBAN","Planned","",4,332,1.3181887213470141E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-14","08:08","LRE4A","RURAL","Planned","",19,569.16249999997501,2.7553543628678501E-2,4.8703212874053492E-5,"NO"]
[null,"2015-07-14","08:10","BDL2","URBAN","Planned","",61,473,2.8639833717639607E-2,6.0549331326933635E-5,"NO"]
[null,"2015-07-14","08:14","GTN13A","RURAL","Planned","",2,108,5.5367863056818701E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-14","08:18","MFN13A","RURAL","Planned","",4,272,2.7888997687879054E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-14","08:25","FDS1","RURAL","Planned","",11,217,6.1186615331771414E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-14","08:06","ACR3","URBAN","Planned","",3,217,6.4619040481694748E-4,2.9778359668983749E-6,"NO"]
[null,"2015-07-14","08:20","MFN13A","RURAL","Planned","",7,238,4.2705027709564799E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-14","08:18","GAP8A","URBAN","Planned","",19,295,5.5635901981551314E-3,1.8859627790356379E-5,"NO"]
[null,"2015-07-14","08:04","NGI3A","RURAL","Planned","",10,143,3.6655576005208681E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-14","08:03","MGL10A","RURAL","Planned","",2,391,2.0045217088163069E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-14","08:00","MGL10A","RURAL","Planned","",56,477,6.8471590646932465E-2,1.4354631162878922E-4,"NO"]
[null,"2015-07-14","07:58","SFD8","URBAN","Asset failure","LV",1,342.85,3.4031702041703604E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","07:43","MFN12A","RURAL","Asset failure","LV",1,50.833333333299997,1.3030245549628574E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","07:18","TGW5","RURAL","Overloads","",1,196.45,5.0356558784777933E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","07:18","ALY8","URBAN","Asset failure","LV",1,86.4,8.5761675846673217E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","05:30","BHD7A","URBAN","Planned","",24,40,9.5290750940748008E-4,2.3822687735187003E-5,"NO"]
[null,"2015-07-14","01:59","PWC4","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",343,97.234615384615395,8.6289276577855956E-2,8.7922115872633407E-4,"NO"]
[null,"2015-07-14","08:25","TMH16A","URBAN","Planned","",2,304,6.0350808929140413E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-14","09:05","SHW12","URBAN","Planned","",9,157,1.4025607404091348E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-14","07:14","COR22A","RURAL","Overloads","",10,85.983333333299996,2.204033993132847E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-14","19:18","CPB8","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",35,32,2.8709262325757844E-3,8.9716444767993261E-5,"NO"]
[null,"2015-07-14","12:31","LLY4","RURAL","Planned","",2,76,3.8962570299242794E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-14","12:55","BGY6A","URBAN","Planned","",5,62,3.0770971657949879E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-14","14:48","GNA4A","URBAN","Overloads","",1,181.9166666667,1.8057266432612069E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","15:50","BBH3A","URBAN","Asset failure","LV",1,63.516666666699997,6.3047404832531465E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","17:03","RBA43A","RURAL","Asset failure","LV",1,414.98333333329998,1.0637379801324213E-3,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","17:08","CLM8","URBAN","Overloads","",1,150.53333333329999,1.4942119140566761E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","18:29","YTA2B","RURAL","Overloads","",1,102.4833333333,2.626982947039101E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","18:40","BRD8A","URBAN","Asset failure","LV",1,172,1.7072926210217351E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","08:56","MRB2","RURAL","Planned","",7,327,5.8674554878267605E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-14","19:10","AHD18B","RURAL","Asset failure","LV",1,88.166666666699996,2.259999965823161E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","10:47","CVL1A","URBAN","Other","Other System Failures",1,28,2.7793135691051504E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","19:33","BRD3B","RURAL","Other","Other System Failures",30,99.033333333300007,7.6156444973033803E-3,7.6899809801137087E-5,"NO"]
[null,"2015-07-14","20:04","SBH11","URBAN","Overloads","",121,219.05,2.6309230398146595E-2,1.2010605066490114E-4,"NO"]
[null,"2015-07-14","20:13","ZMR7A","URBAN","Overloads","",1,72.400000000000006,7.1865108001147471E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","20:22","COR22A","RURAL","Overloads","",10,97.95,2.5107787900071261E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-14","20:46","SFD10","URBAN","Overloads","",1,135.3333333333,1.3433348917338251E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","20:51","MLT24A","URBAN","Asset failure","LV",1,70.25,6.9730992224870285E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","21:04","NSW16A","URBAN","Planned","",1,306,3.0373926862363427E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","21:04","NSW26","URBAN","Planned","",7,306,2.12617488036544E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-14","21:53","CLD11","RURAL","Animal","Animal impact",2072,206.56178861790983,1.0748054434813443,5.3112135302652002E-3,"NO"]
[null,"2015-07-14","19:05","CVL7A","RURAL","Asset failure","LV",1,123.35,3.1618638463234202E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","09:34","SPO51A","URBAN","Planned","",13,160,2.0646329370495402E-3,1.2903955856559627E-5,"NO"]
[null,"2015-07-14","08:30","CSE7","URBAN","Planned","",21,192,4.0022115395114168E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-14","08:33","CLD17A","URBAN","Planned","",18,289,5.1635675666017828E-3,1.7867015801390253E-5,"NO"]
[null,"2015-07-14","08:34","NSW5A","URBAN","Planned","",10,204,2.0249284574908951E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-14","08:36","RPN5A","RURAL","Planned","",85,405,8.8242531746804811E-2,2.1788279443655509E-4,"NO"]
[null,"2015-07-14","08:55","KMR29A","URBAN","Planned","",3,226,6.7299092851903287E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-14","08:55","RPN5A","RURAL","Planned","",4,413,4.2346161930492824E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-14","09:00","CSE9","URBAN","Planned","",6,273,1.6258984379265129E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-14","10:20","IDY10A","URBAN","Planned","",32,290,9.2114392576056418E-3,3.1763583646916001E-5,"NO"]
[null,"2015-07-14","09:07","GYS3A","RURAL","Planned","",3,202,1.5533761579829693E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-14","11:59","WRG9A","URBAN","Asset failure","LV",1,99.116666666699999,9.8384391639725518E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","09:17","WNM1A","URBAN","Planned","",11,316,3.4503192736462509E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-14","11:52","THL3","RURAL","Planned","",2,106,5.4342532259470209E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-14","09:35","SMF3A","RURAL","Asset failure","LV",1,148.8166666667,3.8146577873028159E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","09:40","GNA7A","URBAN","Planned","",34,243,8.2009602528381256E-3,3.3748807624848254E-5,"NO"]
[null,"2015-07-14","09:42","LLY4","RURAL","Planned","",1,113,2.896559502509497E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","09:43","BLH9B","URBAN","Planned","",29,243.5,7.6738832866971134E-3,2.8785747680017626E-5,"NO"]
[null,"2015-07-14","09:52","CRB24B","URBAN","Asset failure","LV",1,66.316666666700002,6.5826718401636617E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-14","10:03","JBB1B","RURAL","Planned","",32,37,3.0349791601515441E-3,8.2026463787879565E-5,"NO"]
[null,"2015-07-14","10:25","CPR5","URBAN","Planned","",19,255,4.8092050865408765E-3,1.8859627790356379E-5,"NO"]
[null,"2015-07-14","00:44","YTA39A","RURAL","Third party","Vehicle impact",27,286.8333333333,1.9851685900161235E-2,6.920982882102339E-5,"NO"]
[null,"2015-07-14","08:29","GGR3","RURAL","Planned","",5,186,2.38389410383525E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-14","09:08","CBT12A","RURAL","Overloads","",1,279.43333333330003,7.162790061809504E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","10:30","BDT1","RURAL","Planned","",1,350,8.9716444767993272E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-14","19:59","RBA43A","RURAL","Asset failure","LV",28,175.73333333330001,1.2612935915113888E-2,7.1773155814394623E-5,"NO"]
[null,"2015-07-14","09:26","KSN3","URBAN","Asset failure","LV",12,51.883333333300001,6.1800022432991245E-4,1.1911343867593501E-5,"NO"]
[null,"2015-07-14","12:55","CPS1B","URBAN","Asset failure","LV",1,179,1.7767754602493639E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:50","NRA13A","RURAL","Planned","",4,376,3.8552437980303397E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-15","08:31","CSE9","URBAN","Planned","",15,339,5.0474319638927467E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-15","08:33","KSN7","RURAL","Planned","",12,257,7.9053004475568931E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-15","08:34","JBB1B","RURAL","Planned","",17,75,3.2682419165483262E-3,4.3576558887311021E-5,"NO"]
[null,"2015-07-15","08:35","CPR6","URBAN","Planned","",24,273,6.5035937517060518E-3,2.3822687735187003E-5,"NO"]
[null,"2015-07-15","08:35","NBR11A","RURAL","Planned","",18,92,4.2448695010227668E-3,4.6139885880682253E-5,"NO"]
[null,"2015-07-15","08:35","NMK16A","URBAN","Planned","",45,276,1.2328240902959274E-2,4.4667539503475631E-5,"NO"]
[null,"2015-07-15","08:45","BKD3A","URBAN","Planned","",7,230,1.5981053022354615E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-15","09:58","SPD11A","URBAN","Asset failure","LV",1,60.5,6.005302533245057E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:46","JBB3A","RURAL","Planned","",44,229,2.5828082785208577E-2,1.1278638770833439E-4,"NO"]
[null,"2015-07-15","08:30","GYN3A","RURAL","Planned","",104,139.1219512195122,3.6737602468996572E-2,2.6658600731060852E-4,"NO"]
[null,"2015-07-15","08:55","BTA15A","URBAN","Planned","",12,305,3.6329598796160179E-3,1.19113438675935E-5,"NO"]
[null,"2015-07-15","09:00","LRE6A","RURAL","Planned","",12,435,1.3380566905397854E-2,3.0759923920454833E-5,"NO"]
[null,"2015-07-15","09:18","BGY5A","RURAL","Asset failure","LV",1,79.016666666700004,2.0254555459296931E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","09:22","LRE6A","RURAL","Planned","",1,98,2.5120604535038119E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","09:25","CNB21B","URBAN","Planned","",47,264,1.231632955909168E-2,4.6652763481407883E-5,"NO"]
[null,"2015-07-15","09:40","UMG1B","URBAN","Planned","",8,36,2.8587225282224405E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-15","09:48","BGY5A","RURAL","Unknown","Unknown",16,71.883333333300001,2.9481678193080045E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-15","09:48","BHD21A","URBAN","Asset failure","LV",1,77.566666666700002,7.6993603277505533E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","06:10","NRA3B","URBAN","Planned","",10,145,1.4392873840008815E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-15","08:45","NBR7A","RURAL","Planned","",6,215,3.3066918214488951E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-15","08:16","SPO51A","URBAN","Planned","",5,201,9.9757504891095569E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-15","06:25","COR26A","RURAL","Asset failure","LV",1,141.9166666667,3.6377882247602006E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","06:31","SBH11","URBAN","Asset failure","LV",1,266.96666666670001,2.6499431398768964E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","07:08","BVLNCM7","URBAN","Asset failure","LV",1,279.75,2.776832039132735E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:02","BGY17A","URBAN","Planned","",1,388,3.8513345171885656E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:03","SPF12B","URBAN","Planned","",39,442,1.7110645465798064E-2,3.8711867569678874E-5,"NO"]
[null,"2015-07-15","08:03","TGW5","RURAL","Planned","",14,321,1.1519591508210338E-2,3.5886577907197304E-5,"NO"]
[null,"2015-07-15","08:04","CSE6","URBAN","Planned","",16,191,3.0334222382804783E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-15","08:07","FDS3","RURAL","Planned","",51,371,4.8500710041577161E-2,1.3072967666193306E-4,"NO"]
[null,"2015-07-15","08:08","KRN18","URBAN","Planned","",16,112,1.7787606842272962E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-15","08:30","SBK9","URBAN","Planned","",6,365,2.1738202558358138E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-15","08:15","GAP1A","URBAN","Planned","",30,251,7.4743682769149219E-3,2.9778359668983753E-5,"NO"]
[null,"2015-07-15","08:30","NGE4A","URBAN","Planned","",1,280,2.7793135691051501E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:17","LRE6A","RURAL","Planned","",8,61,1.2509035727651635E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-15","08:17","NRG10","URBAN","Planned","",23,175,3.9952632555886533E-3,2.2830075746220877E-5,"NO"]
[null,"2015-07-15","08:18","GYN3A","RURAL","Planned","",2,264,1.3534366525000128E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-15","08:20","SHW12","URBAN","Planned","",8,86,6.8291704840869405E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-15","08:25","LRE6A","RURAL","Planned","",58,424.33333333333331,6.2980944227131269E-2,1.4867296561553171E-4,"NO"]
[null,"2015-07-15","08:26","TRP5","RURAL","Planned","",1,159,4.0756899194602659E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","08:28","BWH7A","RURAL","Planned","",1,141,3.6142910606534436E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","08:30","CNA7A","RURAL","Planned","",10,371,9.5099431454072868E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-15","10:00","NVL24A","URBAN","Planned","",50,299,1.483954923504357E-2,4.9630599448306258E-5,"NO"]
[null,"2015-07-15","08:10","KSN1","URBAN","Planned","",1,240,2.3822687735187002E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","19:46","AHD7","URBAN","Overloads","",139,122.7,1.6929295255413954E-2,1.379730664662914E-4,"NO"]
[null,"2015-07-15","18:00","NSW24","URBAN","Planned","",6,1440,8.5761675846673206E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-15","18:19","KLG11A","URBAN","Asset failure","LV",1,221.6833333333,2.2004553442060742E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","18:23","NIP3A","RURAL","Asset failure","LV",1,200.45,5.1381889582126426E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","18:38","BKD15A","URBAN","Overloads","",121,76.400000000000006,9.1761022707984464E-3,1.2010605066490114E-4,"NO"]
[null,"2015-07-15","18:55","KWA2A","URBAN","Asset failure","LV",1,122.05,1.2114829325331556E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","19:01","BDB37A","RURAL","Overloads","",1,196.8,5.0446275229545934E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","19:07","NMK16A","URBAN","Overloads","",228,81.866666666699999,1.8527698341253649E-2,2.2631553348427652E-4,"NO"]
[null,"2015-07-15","19:22","BIS3","RURAL","Overloads","",1,59.9666666667,1.5371417536924725E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","09:48","BTA1A","RURAL","Asset failure","LV",1,65.483333333299996,1.6785519594917435E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","19:34","RPN5A","RURAL","Animal","Animal impact",119,205.1833333333,6.2588285253853196E-2,3.0503591221117714E-4,"NO"]
[null,"2015-07-15","16:08","YTA22B","RURAL","Asset failure","LV",1,61.416666666700003,1.5743099950963555E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","20:40","EMP21A","RURAL","Overloads","",21,84.866666666699999,4.5683613675880112E-3,5.3829866860795964E-5,"NO"]
[null,"2015-07-15","21:05","UMG2A","URBAN","Asset failure","LV",1,123.7666666667,1.2285227716774051E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","21:15","BBH12B","URBAN","Overloads","",1,70.833333333300004,7.0310015885067441E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","21:55","CBW7","RURAL","Overloads","",5,94.983333333299996,1.2173667112681291E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-15","22:10","GYM4","RURAL","Overloads","",1,74.216666666699993,1.9024158502478736E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","22:19","LBH5A","RURAL","Asset failure","LV",1,84.85,2.1749829538754941E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","22:38","KSN6","URBAN","Asset failure","LV",1,123.4166666667,1.2250486297160236E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","22:59","KSN3","URBAN","Asset failure","LV",1,151.78333333329999,1.5066195639187527E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","23:01","NVL9","RURAL","Other","Other System Failures",29,4,2.9734593123106342E-4,7.4336482807765855E-5,"NO"]
[null,"2015-07-15","19:27","SHW5A","URBAN","Unknown","Unknown",64,77.366666666699999,4.914885176301587E-3,6.3527167293832003E-5,"NO"]
[null,"2015-07-15","12:13","DBY6","URBAN","Overloads","",1,44.983333333300003,4.465099597029311E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","10:01","SMF6A","RURAL","Planned","",16,118,4.8395613634848941E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-15","10:25","ENG17A","URBAN","Planned","",9,193,1.7241670248341594E-3,8.9335079006951247E-6,"NO"]
[null,"2015-07-15","10:30","PPE16A","RURAL","Network business","Network error",7,32,5.7418524651515698E-4,1.7943288953598656E-5,"NO"]
[null,"2015-07-15","10:37","BHL3A","URBAN","Planned","",3,173,5.1516562227341893E-4,2.9778359668983749E-6,"NO"]
[null,"2015-07-15","10:38","CNA7A","RURAL","Asset failure","LV",1,133.1,3.4117882281771157E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","10:50","CRY6A","RURAL","Overloads","",1,125.3666666667,3.213557607357261E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","11:09","SMF6A","RURAL","Asset failure","LV",1,4.4000000000000004,1.1278638770833441E-5,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","11:15","CSE6","URBAN","Planned","",11,225,2.4567146726911598E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-15","11:15","NDH6","URBAN","Planned","",1,225,2.2333769751737816E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","17:06","KMR25A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",27,56,3.8757504139773098E-3,6.9209828821023377E-5,"NO"]
[null,"2015-07-15","12:04","LRE6A","RURAL","Planned","",1,86,2.2044612142992632E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","16:45","PWC6","RURAL","Overloads","",1,115.21666666669999,2.9533799175300807E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","12:16","AFD6OLD","URBAN","Asset failure","LV",1,152.69999999999999,1.5157185071512731E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","13:41","WRG6A","URBAN","Asset failure","LV",1,30.7833333333,3.0555905726974128E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","13:44","YTA35A","URBAN","Overloads","",1,61.933333333299998,6.1475769183268935E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","13:50","TWT15A","RURAL","Overloads","",1,163.9333333333,4.2021473844657258E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-15","13:59","KBN2A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",28,84,6.028945088409148E-3,7.1773155814394623E-5,"NO"]
[null,"2015-07-15","14:20","BRT6","URBAN","Asset failure","LV",1,114.2333333333,1.1338937620619727E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","14:30","EMP21A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",190,82.55151515148178,4.6478714987073136E-2,4.8703212874053498E-4,"NO"]
[null,"2015-07-15","14:34","IPS1B","URBAN","Asset failure","LV",1,53.7833333333,5.3385981473195012E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:35","CHL3","URBAN","Planned","",2,273,5.4196614597550432E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-15","11:49","NRG5A","URBAN","Asset failure","LV",1,193.21666666670001,1.9178917980143792E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-15","08:35","GGR5","RURAL","Planned","",3,293,2.2531644271733169E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-15","14:11","CLM9","URBAN","Asset failure","LV",5,10,4.9630599448306258E-5,4.9630599448306254E-6,"NO"]
[null,"2015-07-15","18:47","BVL10A","URBAN","Asset failure","LV",154,102.6333333333,1.5688761878665292E-2,1.5286224630078326E-4,"NO"]
[null,"2015-07-15","19:05","DBY7A","URBAN","Asset failure","HV",1874,46.465333333324004,8.1618496861177336E-2,1.8601548673225184E-3,"NO"]
[null,"2015-07-15","19:05","DBY9","URBAN","Asset failure","HV",1499,20.316666666700019,3.0229683796883098E-2,1.4879253714602215E-3,"NO"]
[null,"2015-07-15","20:00","BLB9A","URBAN","Asset failure","LV",26,142.5833333333,3.6797780784280604E-3,2.5807911713119255E-5,"NO"]
[null,"2015-07-16","09:10","AHL6A","URBAN","Planned","",1,363,3.6031815199470343E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","22:59","GYN2B","URBAN","Overloads","",1,59.583333333299997,5.9143131009198532E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","10:51","ENG17A","URBAN","Planned","",65,190,1.2258758063731645E-2,6.4519779282798132E-5,"NO"]
[null,"2015-07-16","10:49","COR26A","RURAL","Planned","",5,238,3.0503591221117711E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-16","10:20","SPD6B","URBAN","Planned","",1,13,1.2903955856559627E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","10:17","WED4B","URBAN","Overloads","",1,40.083333333299997,3.9787197224359095E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","10:07","BVL2A","URBAN","Planned","",67,184,1.223692059997439E-2,6.6505003260730391E-5,"NO"]
[null,"2015-07-16","09:50","ACR6","RURAL","Planned","",12,187,5.7521057731250548E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-16","09:29","CLD11","RURAL","Planned","",1,259,6.6390169128315024E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","11:42","CSE9","URBAN","Asset failure","LV",1,90.116666666699999,8.9450883739030393E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","09:25","EMD2","RURAL","Planned","",116,125,3.7168241403882925E-2,2.9734593123106342E-4,"NO"]
[null,"2015-07-16","11:44","CSE7","URBAN","Asset failure","LV",1,17.483333333299999,1.7354166273724668E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","09:10","AHL14A","URBAN","Planned","",4,363,1.4412726079788137E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-16","09:07","JBB16A","RURAL","Planned","",1,231,5.9212853546875563E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","09:05","CMV7","URBAN","Planned","",4,135,5.3601047404170754E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-16","09:01","NVL6","URBAN","Planned","",1,134,1.3301000652146076E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","09:00","LGV2B","RURAL","Planned","",15,195,7.4977314556108664E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-16","09:00","JBB3A","RURAL","Planned","",1,218,5.5880528455492953E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","09:00","HPK2","URBAN","Planned","",31,310,9.5390012139644625E-3,3.0770971657949879E-5,"NO"]
[null,"2015-07-16","09:28","YDA2B","RURAL","Overloads","",19,131.46666666670001,6.4028490525105224E-3,4.8703212874053492E-5,"NO"]
[null,"2015-07-16","19:00","NMC3A","RURAL","Asset failure","LV",1,92.666666666699996,2.3753496805248666E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","08:32","JBB16A","RURAL","Asset failure","LV",1,142,3.6399243305871556E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","22:29","WRG19A","URBAN","Planned","",32,235,7.4644421570252617E-3,3.1763583646916001E-5,"NO"]
[null,"2015-07-16","22:16","HDA10A","URBAN","Planned","",11,1004,1.0962406806141885E-2,1.0918731878627377E-5,"NO"]
[null,"2015-07-16","21:35","BVL13A","URBAN","Asset failure","LV",1,56.083333333299997,5.5668989047817092E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","21:28","SPO55A","URBAN","Asset failure","LV",1,215.46666666670001,2.1387479655593419E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","20:53","RCN8A","URBAN","Other","Other System Failures",54,112,6.0033173092671251E-3,5.3601047404170755E-5,"NO"]
[null,"2015-07-16","20:48","NMK16A","URBAN","Overloads","",228,71.883333333300001,1.6268314931953871E-2,2.2631553348427652E-4,"NO"]
[null,"2015-07-16","20:34","IPS15B","URBAN","Overloads","",1,54.866666666699999,5.4461311127974484E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","11:36","BDT1","RURAL","Planned","",7,29,5.2035537965436102E-4,1.7943288953598656E-5,"NO"]
[null,"2015-07-16","19:03","HTN28A","URBAN","Asset failure","LV",1,127.85,1.2690544278931909E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:46","MGL13A","URBAN","Planned","",1,107,1.0620948281937539E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","18:45","AGT25A","URBAN","Asset failure","LV",1,110.15,1.0933621058461868E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","18:35","BVL2A","URBAN","Overloads","",1,92.133333333300001,9.1452651250045907E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","17:52","TMH15A","URBAN","Overloads","",1,115.3,1.1444816232779423E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","16:44","NRG22A","URBAN","Overloads","",1,111.6166666667,1.1079204150180208E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","16:22","BBH3A","URBAN","Asset failure","LV",1,94.466666666699993,9.3768745891033035E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","16:20","BHD5A","URBAN","Asset failure","LV",1,64.366666666699999,6.3891125023152667E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","13:20","BRD3B","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",743,68.595641025619997,0.16890910784256122,1.9045519560748289E-3,"NO"]
[null,"2015-07-16","13:10","NGI3A","RURAL","Animal","Animal nesting/burrowing, etc and other",1317,38.75,0.13081618894795935,3.3759016502699184E-3,"NO"]
[null,"2015-07-16","19:50","HIS12A","URBAN","Unknown","Unknown",37,9.5666666666999998,3.5135155702893363E-4,3.6726643591746628E-5,"NO"]
[null,"2015-07-16","08:20","GAP1A","URBAN","Planned","",27,332,8.8977738690923461E-3,2.6800523702085378E-5,"NO"]
[null,"2015-07-16","08:10","BRD13A","RURAL","Planned","",13,248,8.2641662266288666E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-16","08:10","NBR7A","RURAL","Planned","",7,250,4.4858222383996633E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-16","08:10","SHW81","URBAN","Planned","",8,250,1.9852239779322503E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-16","08:11","CRB25A","RURAL","Planned","",73,426.4,8.0370554550161746E-2,1.8712287051610027E-4,"NO"]
[null,"2015-07-16","08:12","BTA15A","URBAN","Planned","",5,316,1.5683269425664777E-3,4.9630599448306254E-6,"NO"]
[null,"2015-07-16","08:14","RLB11B","URBAN","Planned","",31,345,1.0615985221992709E-2,3.0770971657949879E-5,"NO"]
[null,"2015-07-16","08:14","RLB15A","URBAN","Planned","",21,345,7.1914738600595768E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-16","08:15","INA1A","URBAN","Planned","",42,305,1.2715359578656063E-2,4.1689703536577256E-5,"NO"]
[null,"2015-07-16","08:59","KWH3","RURAL","Planned","",6,352,5.413746610000051E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-16","08:15","TMH2A","RURAL","Planned","",67,292,5.0148929298314868E-2,1.7174290855587283E-4,"NO"]
[null,"2015-07-16","08:03","RWD1","RURAL","Planned","",6,447,6.8748429962216554E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-16","08:20","GAP6A","URBAN","Planned","",1,332,3.2954718033675353E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:20","GAP8A","URBAN","Planned","",4,332,1.3181887213470141E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-16","08:22","UMG5A","URBAN","Planned","",10,248,2.4616777326359903E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-16","08:25","RCF12A","URBAN","Planned","",4,183,7.2659197592320364E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-16","08:30","LTN8","RURAL","Planned","",3,344,2.6453534571591157E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-16","08:30","RBY12","URBAN","Planned","",6,230,1.3698045447732526E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-16","08:30","RBY15","URBAN","Planned","",1,230,2.2830075746220878E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:30","ZMR5","URBAN","Planned","",11,380,4.1491181138784026E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-16","08:15","INA9A","URBAN","Planned","",11,305,3.3302132229813498E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-16","08:32","WSE3A","RURAL","Planned","",56,500,7.2080755053599177E-2,1.4354631162878925E-4,"NO"]
[null,"2015-07-16","23:25","JNST2","CBD","Planned","",1,51,1.3046815042210284E-2,2.5581990278843696E-4,"NO"]
[null,"2015-07-16","08:46","BKD13A","URBAN","Planned","",50,157,7.7920041133840816E-3,4.9630599448306251E-5,"NO"]
[null,"2015-07-16","08:43","BTA5A","RURAL","Asset failure","LV",1,144.98333333330001,3.7163969192218767E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","08:39","CRB24B","URBAN","Asset failure","LV",1,189.7,1.8829849430687393E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:38","EZRRWD4","RURAL","Planned","",34,334,2.9109141336723762E-2,8.7153117774622029E-5,"NO"]
[null,"2015-07-16","08:37","HIS13A","URBAN","Planned","",1,363,3.6031815199470343E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:36","RCF12A","URBAN","Planned","",18,299,5.3422377246156857E-3,1.7867015801390253E-5,"NO"]
[null,"2015-07-16","08:35","JBB16A","RURAL","Planned","",3,349,2.6838033620596845E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-16","08:07","GYGGYS6","RURAL","Planned","",68,405.5,7.0681178515218462E-2,1.7430623554924406E-4,"NO"]
[null,"2015-07-16","08:33","TBV4","RURAL","Planned","",3,440,3.5297012698721924E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-16","08:05","KRN11","URBAN","Planned","",5,275,1.3648414848284221E-3,4.9630599448306254E-6,"NO"]
[null,"2015-07-16","04:19","SFD6B","URBAN","Animal","Animal impact",740,74.433333333299984,5.4673730093555667E-2,7.3453287183493246E-4,"NO"]
[null,"2015-07-16","04:46","EMP4A","URBAN","Asset failure","LV",1,83.716666666699993,8.3098167009647183E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","06:17","TMH15A","URBAN","Asset failure","LV",1,51.016666666699997,5.0639754970454901E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","06:21","GAP9A","URBAN","Overloads","",1,156.76666666669999,1.5560847280362262E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","06:38","JBB12B","RURAL","Asset failure","LV",1,204.61666666670001,5.2449942496039662E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-16","06:46","NRA12A","URBAN","Planned","",1,111,1.1017993077523989E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:00","BGY17A","URBAN","Planned","",1,230,2.2830075746220878E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","08:01","NGE4B","URBAN","Planned","",121,467,5.6214594771118565E-2,1.2010605066490114E-4,"NO"]
[null,"2015-07-16","08:47","CHL3","URBAN","Planned","",3,268,7.9806003912876464E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-16","08:34","SBY3A","URBAN","Planned","",37,198,7.2718754311658328E-3,3.6726643591746628E-5,"NO"]
[null,"2015-07-16","22:29","WRG8A","URBAN","Planned","",1,235,2.332638174070394E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-16","20:12","TRG8A","URBAN","Asset failure","LV",401,68,2.7066543715128302E-2,3.9803740757541619E-4,"NO"]
[null,"2015-07-16","10:08","CRB24B","URBAN","Asset failure","LV",73,42,3.0433483581701398E-3,7.2460675194527141E-5,"NO"]
[null,"2015-07-17","08:45","BNH2B","RURAL","Planned","",18,383,1.7671576292301303E-2,4.6139885880682253E-5,"NO"]
[null,"2015-07-17","09:31","EMP4A","URBAN","Planned","",32,144,4.5739560451559047E-3,3.1763583646916001E-5,"NO"]
[null,"2015-07-17","09:25","NRA15A","RURAL","Planned","",11,243,6.8517730532813145E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-17","09:22","LGL15A","URBAN","Planned","",4,216,8.5761675846673208E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-17","09:18","RPN4A","RURAL","Planned","",1,71,1.8199621652935778E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","09:01","BHL1A","URBAN","Unknown","Unknown",656,67.566666666700016,4.3996269102425843E-2,6.5115346476177813E-4,"NO"]
[null,"2015-07-17","08:58","TRG3B","URBAN","Overloads","",1,69.966666666699993,6.9449752161362971E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","08:54","BVLNCM7","URBAN","Planned","",71,352,2.4807358828241401E-2,7.0475451216594882E-5,"NO"]
[null,"2015-07-17","08:53","GYM9B","RURAL","Planned","",29,387,2.8768218846605381E-2,7.4336482807765841E-5,"NO"]
[null,"2015-07-17","08:23","CLD17A","URBAN","Planned","",7,262,1.8204503877638735E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-17","08:47","GYM2A","RURAL","Planned","",24,247,1.519540241670469E-2,6.1519847840909667E-5,"NO"]
[null,"2015-07-17","09:55","CFD6A","URBAN","Network business","Switching and protection error",161,65,1.03876844645305E-2,1.5981053022354614E-4,"NO"]
[null,"2015-07-17","08:42","BHL2A","URBAN","Weather","",26,162.86666666670001,4.2032485543442152E-3,2.5807911713119255E-5,"NO"]
[null,"2015-07-17","08:40","CSE4","URBAN","Planned","",33,162,5.3065036930129046E-3,3.2756195635882124E-5,"NO"]
[null,"2015-07-17","08:40","BPN3","URBAN","Planned","",2,305,6.0549331326933628E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-17","08:39","MTB13A","RURAL","Planned","",13,217,7.2311454483002576E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-17","08:35","GNA5A","RURAL","Planned","",2,275,1.4098298463541799E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-17","08:35","GAP1A","URBAN","Planned","",26,198,5.1099665191976125E-3,2.5807911713119252E-5,"NO"]
[null,"2015-07-17","08:30","KSN7","RURAL","Planned","",10,220,5.6393193854167196E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-17","08:50","ACR4","URBAN","Planned","",28,292,8.11559562178704E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-17","11:37","HWD5A","RURAL","Unknown","Unknown",2000,68.308333333349992,0.35023937201914784,5.1266539867424717E-3,"NO"]
[null,"2015-07-17","13:32","TRG15A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",535,256.80999999998005,0.1344615195764472,5.3104741409687689E-4,"NO"]
[null,"2015-07-17","13:14","SMF5A","RURAL","Asset failure","LV",1,91.3,2.3403175449479387E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","08:34","KMR21B","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",39,81.416666666699996,3.1517912179659792E-3,3.8711867569678881E-5,"NO"]
[null,"2015-07-17","13:12","INA11A","URBAN","Weather","",132,34.333333333333336,3.2954718033675352E-3,1.3102478254352855E-4,"NO"]
[null,"2015-07-17","13:12","INA10A","RURAL","Weather","",105,47.333333333333336,1.25654289215058E-2,2.6914933430397984E-4,"NO"]
[null,"2015-07-17","13:12","CVL17A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",2154,115.80000000000005,0.24759038476618525,2.1380862242330336E-3,"NO"]
[null,"2015-07-17","13:01","NRA2A","URBAN","Planned","",8,81,6.4321256885004909E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-17","12:08","CCY26A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1696,140.59215686273231,0.61122292913078813,4.3474025807576167E-3,"NO"]
[null,"2015-07-17","09:38","KMR28A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",585,51.29999999999999,2.9788782094867901E-2,5.8067801354518326E-4,"NO"]
[null,"2015-07-17","11:37","HWD5B","URBAN","Unknown","Unknown",1602,67.916666666699967,0.10799866592953984,1.5901644063237323E-3,"NO"]
[null,"2015-07-17","09:53","MTB13A","RURAL","Network business","Switching and protection error",17,76.816666666700002,3.347405998528394E-3,4.3576558887311021E-5,"NO"]
[null,"2015-07-17","11:29","RPN5A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,228.25,5.8507938623698474E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","11:19","RBY13","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",935,146.12647058823526,0.15921461561597033,9.2809220968332695E-4,"NO"]
[null,"2015-07-17","11:19","CVL17A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",63,642,4.0147184505723896E-2,6.2534555304865887E-5,"NO"]
[null,"2015-07-17","11:00","NRA3B","URBAN","Planned","",3,120,3.5734031602780504E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-17","10:56","TBV3","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",363,98.96666666669995,9.2087265904193361E-2,9.304876985937586E-4,"NO"]
[null,"2015-07-17","10:39","ENG4A","URBAN","Planned","",31,136,4.1848521454811837E-3,3.0770971657949879E-5,"NO"]
[null,"2015-07-17","10:35","NVL9","RURAL","Planned","",139,203,7.2329397771956183E-2,3.5630245207860184E-4,"NO"]
[null,"2015-07-17","10:23","NIP4A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",7,126.28333333330001,2.2659383400230187E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-17","08:19","BBH1B","URBAN","Planned","",1,8771,8.7061997552218828E-3,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","11:53","CPS12B","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",76,153,2.9806366278920738E-2,1.9481285149621397E-4,"NO"]
[null,"2015-07-17","08:06","RBY3","URBAN","Planned","",3,158,4.7049808276994332E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-17","20:01","GNA4A","URBAN","Overloads","",42,103.85,4.3294757122735476E-3,4.1689703536577256E-5,"NO"]
[null,"2015-07-17","20:09","KMR17B","URBAN","Asset failure","LV",1,4.5666666666999998,4.5329280829783919E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","08:34","KMR21A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",1049,139.47962962963331,0.13114692344877535,1.0412499764254654E-3,"NO"]
[null,"2015-07-17","20:15","WNM4","URBAN","Overloads","",106,174.05,1.8312996368032731E-2,1.0521687083040927E-4,"NO"]
[null,"2015-07-17","08:09","CLD17A","URBAN","Planned","",51,381,1.9287443557600779E-2,5.0623211437272387E-5,"NO"]
[null,"2015-07-17","20:28","WMD14A","RURAL","Overloads","",48,71.599999999999994,8.8096422108182651E-3,1.2303969568181933E-4,"NO"]
[null,"2015-07-17","21:26","MLY3","RURAL","Overloads","",10,118.3,3.0324158331581728E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-17","21:35","HTN3A","URBAN","Overloads","",1,147.44999999999999,1.4636063777305513E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","08:26","CHL2","URBAN","Planned","",11,238,2.5986581871133155E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-17","08:07","IPS1B","URBAN","Planned","",23,58,1.3241443932808109E-3,2.283007574622088E-5,"NO"]
[null,"2015-07-17","17:45","BLN16A","URBAN","Overloads","",1,105,1.0422425884144314E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","07:44","KWH2","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",379,66.095542696449073,6.9673876451055328E-2,9.7150093048769821E-4,"NO"]
[null,"2015-07-17","07:35","SHW81","URBAN","Planned","",10,124,1.2308388663179951E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-17","07:27","RCN11","URBAN","Planned","",1,14,1.3896567845525752E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","06:51","WMD10A","URBAN","Asset failure","LV",1,153.1,1.5196889551071375E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","06:01","NRA3B","URBAN","Planned","",1,115,1.1415037873110439E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","05:56","LTN9","URBAN","Overloads","",1,161.78333333329999,1.6058807628153651E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","05:27","GYN2B","URBAN","Overloads","",1,49.566666666700002,4.9200467586454022E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","01:44","CRM15A","URBAN","Animal","Animal impact",66,65.483333333299996,4.2899697551105117E-3,6.5512391271764262E-5,"NO"]
[null,"2015-07-17","21:41","WMD6A","URBAN","Asset failure","LV",1,71.516666666700004,7.0988300744260474E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","14:51","LTN5","URBAN","Weather","",1938,48.166666666700003,9.2657351334084995E-2,1.9236820346163507E-3,"NO"]
[null,"2015-07-17","08:15","AHD7","URBAN","Planned","",60,305,1.8164799398080089E-2,5.9556719337967505E-5,"NO"]
[null,"2015-07-17","08:15","AHD19","URBAN","Planned","",4,305,1.2109866265386726E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-17","08:15","AHD15B","URBAN","Planned","",2,305,6.0549331326933628E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-17","08:12","CCY3B","URBAN","Planned","",1,206,2.0447806972702178E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","13:41","LTA12A","URBAN","Asset failure","LV",1,20.2833333333,2.0133479842829816E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","08:12","CCY13A","URBAN","Planned","",20,206,4.0895613945404353E-3,1.9852239779322502E-5,"NO"]
[null,"2015-07-17","08:11","CMD11A","RURAL","Asset failure","LV",1,179.6,4.6037352800947407E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","13:44","BWH7A","RURAL","Weather","",86,235.61666666670001,5.1940780310921822E-2,2.2044612142992635E-4,"NO"]
[null,"2015-07-17","19:08","MLY1","RURAL","Overloads","",1,191.4333333333,4.9070623076428153E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","14:28","MCN2","RURAL","Weather","",14,122.6,4.3996944514223908E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-17","18:33","UPC1","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",586,1.3999999710358679,2.1029534653617633E-3,1.5021096181155448E-3,"NO"]
[null,"2015-07-17","15:02","MTB15A","RURAL","Overloads","",1,303.81666666669997,7.787814627028232E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","15:30","MGL1A","RURAL","Weather","",20,102.03333333330001,5.2308959511378613E-3,5.1266539867424725E-5,"NO"]
[null,"2015-07-17","16:08","BVLNCM7","URBAN","Overloads","",1,115.1666666667,1.1431581406263183E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","16:26","BBS11A","URBAN","Third party","Vehicle impact",21,183.88333333329999,3.8330208259914457E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-17","16:35","NRG4","URBAN","Overloads","",1,89.833333333300004,8.916964367542382E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-17","17:04","OXL8B","URBAN","Weather","",81,50,4.0200785553128069E-3,8.0401571106256136E-5,"NO"]
[null,"2015-07-17","17:30","SHW10A","URBAN","Overloads","",87,179.2,1.5475217952777476E-2,8.6357243040052886E-5,"NO"]
[null,"2015-07-17","17:35","BIS3","RURAL","Asset failure","LV",1,123.05,3.154173865343306E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-17","14:16","SMF6A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",18,133.38333333329999,6.1542917783834628E-3,4.6139885880682253E-5,"NO"]
[null,"2015-07-17","15:24","BDT1","RURAL","Asset failure","HV",21,176.8333333333,9.5189147898822931E-3,5.382986686079597E-5,"NO"]
[null,"2015-07-17","14:59","CRB22A","URBAN","Asset failure","LV",46,62,2.8309293925313887E-3,4.5660151492441753E-5,"NO"]
[null,"2015-07-17","07:27","HPE5A","URBAN","Asset failure","LV",122,52.75,6.387954454991498E-3,1.2109866265386727E-4,"NO"]
[null,"2015-07-17","16:13","CLD21A","RURAL","Asset failure","LV",28,16,1.148370493030314E-3,7.1773155814394623E-5,"NO"]
[null,"2015-07-17","15:19","KMR25A","RURAL","Asset failure","LV",14,191,6.8543363802746858E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-17","11:00","RWD1","RURAL","Asset failure","HV",14,159,5.7059658872443729E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-17","14:48","LLY3","RURAL","Asset failure","Distribution substation",3,81.099999999999994,6.2365745748722183E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-18","20:23","NSW24","URBAN","Asset failure","LV",1,87.666666666699996,8.7018984366063392E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","05:55","RBY13","URBAN","Weather","",1,213.38333333329999,2.1180685491218858E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","11:10","BWH7A","RURAL","Asset failure","LV",1,227.2,5.8238789289394484E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","08:43","STL1A","URBAN","Asset failure","LV",1,96.416666666699996,9.5704339269516984E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","08:41","IPS5B","URBAN","Asset failure","LV",1,112.5166666667,1.1168539229187161E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","08:32","BGY6A","URBAN","Planned","",1,353,3.5039203210504219E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","07:20","RBY13","URBAN","Weather","",1,112.46666666669999,1.1163576169242328E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","09:17","RBY13","URBAN","Weather","",1,19.366666666699999,1.9223585519677043E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","07:18","KBN1B","RURAL","Overloads","",1,230.1,5.8982154117472149E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","07:17","RBY13","URBAN","Weather","",1,242.1833333333,2.4039408019441299E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","03:30","NMK9A","URBAN","Third party","Vehicle impact",2,140,2.7793135691051501E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-18","09:19","KVG2A","URBAN","Asset failure","LV",1,73.183333333299998,7.2642654059137837E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","06:15","HPE12A","URBAN","Asset failure","LV",1,176.46666666670001,1.751629289862553E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","11:20","MLB3A","RURAL","Asset failure","LV",1,321.1666666667,8.2325518603781423E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","07:05","1084","URBAN","Planned","",1,593,5.8861890945691219E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","07:05","MLY1","RURAL","Overloads","",1,126.3,3.2374819926278716E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","07:06","JBB1B","RURAL","Asset failure","LV",1,127.05,3.2567069450781559E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","07:11","GCN1","URBAN","Planned","",1,15,1.4889179834491876E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","12:28","BDA13A","URBAN","Asset failure","LV",1,69.183333333299998,6.8672206103273333E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","19:14","LHM5","RURAL","Asset failure","LV",1,116.0166666667,2.9738865334770509E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","18:55","TGW4","RURAL","Overloads","",1,105.15,2.6953383335298555E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","12:38","CBW7","RURAL","Weather","",8,92.783333333300007,1.9026721829456729E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-18","12:55","KMR24A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",85,33,2.784276629049981E-3,8.4372019062120641E-5,"NO"]
[null,"2015-07-18","13:59","MCW7","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",68,66.283333333300007,1.1553598312983249E-2,1.7430623554924406E-4,"NO"]
[null,"2015-07-18","14:30","NMK17A","URBAN","Asset failure","LV",1,71.583333333300004,7.1054474876792038E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","14:42","STL1A","URBAN","Overloads","",1,178.38333333329999,1.7706543529837418E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","14:50","KSN4","URBAN","Third party","Vehicle impact",9,60,5.3601047404170754E-4,8.9335079006951264E-6,"NO"]
[null,"2015-07-18","16:12","GYM9B","RURAL","Asset failure","LV",1,53.7166666667,1.3769338166067703E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","10:52","KRN5A","URBAN","Asset failure","LV",1,181.8333333333,1.8048994666030734E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","18:21","BBH12B","URBAN","Overloads","",1,106.2333333333,1.0544848029446827E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","10:24","COR26A","RURAL","Asset failure","LV",1,229.71666666670001,5.8883893249401468E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","19:01","AHL9A","URBAN","Overloads","",1,47.25,4.6900916478649415E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","19:06","RBY7A","URBAN","Animal","Animal impact",61,61,3.6935092109429517E-3,6.0549331326933635E-5,"NO"]
[null,"2015-07-18","19:06","SMF6A","RURAL","Overloads","",1,112.6,2.8863061945360121E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","19:08","PWC4","RURAL","Unknown","Unknown",15,55,2.1147447695312699E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-18","20:01","BMT1","RURAL","Overloads","",1,72.2,1.8507220892140328E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","21:10","BKD16A","URBAN","Asset failure","LV",1,110.21666666669999,1.0940238471724951E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-18","22:30","BPN31A","URBAN","Planned","",30,310,9.2312914973849639E-3,2.9778359668983753E-5,"NO"]
[null,"2015-07-18","17:41","NBR5A","RURAL","Asset failure","LV",1,67.983333333299996,1.7426351343260245E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-18","10:34","CBW7","RURAL","Asset failure","LV",8,55.333333333299997,1.1346994157316504E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-18","17:31","WMD8B","RURAL","Asset failure","LV",16,102.75,4.2141095771023127E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-18","16:59","MAI17","URBAN","Asset failure","LV",118,211,2.4714053301278585E-2,1.1712821469800276E-4,"NO"]
[null,"2015-07-19","19:46","BIS2B","RURAL","Asset failure","LV",1,133.96666666670001,3.4340037287871879E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","19:32","BDB37A","RURAL","Asset failure","LV",1,89.983333333299996,2.3065670728676963E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","18:37","TRG13A","URBAN","Overloads","",1,141.30000000000001,1.4025607404091349E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","19:44","TMH15A","URBAN","Asset failure","LV",1,112.3666666667,1.1153650049352668E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","11:37","CRB24B","URBAN","Overloads","",1,90.816666666700002,9.0145712131306681E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","21:01","LTN5","URBAN","Overloads","",1,122.46666666669999,1.2156188158208454E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","21:08","KBN13A","RURAL","Overloads","",1,172.6833333333,4.4264384963857087E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","21:13","SGT5","URBAN","Asset failure","LV",1,63.166666666700003,6.2699990636393328E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","22:06","ZMR10","URBAN","Asset failure","LV",1,133.61666666670001,1.3262950525905686E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","22:41","KWA6A","URBAN","Asset failure","LV",1,141.5833333333,1.4053731410442079E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","18:00","SHW10A","URBAN","Overloads","",1,48.616666666699999,4.8257486196936202E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","19:28","MGP2A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",48,10,1.2303969568181934E-3,1.2303969568181933E-4,"NO"]
[null,"2015-07-19","08:49","CSE7","URBAN","Planned","",1,264,2.6204956508705705E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","05:20","LBS10A","URBAN","Planned","",9,320,2.8587225282224404E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-19","06:34","LBS10A","URBAN","Planned","",16,357,5.6697996809745065E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-19","06:41","KWA12A","URBAN","Asset failure","LV",1,208.71666666670001,2.0717466563041284E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","07:21","NRA1A","RURAL","Planned","",35,451,4.0462116590364965E-2,8.9716444767993261E-5,"NO"]
[null,"2015-07-19","07:44","NGI2B","RURAL","Unknown","Unknown",13,45.633333333300001,1.5206510166998189E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-19","08:00","GYN2B","URBAN","Planned","",30,349,1.0392647524475329E-2,2.9778359668983756E-5,"NO"]
[null,"2015-07-19","08:07","KRN1","URBAN","Planned","",147,445,6.4931713258219073E-2,1.4591396237802038E-4,"NO"]
[null,"2015-07-19","08:20","CSE6","URBAN","Asset failure","LV",1,71.383333333300001,7.0855952478998815E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","08:20","SIS1","RURAL","Asset failure","LV",1,166.0666666667,4.2568316936593544E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","08:39","CSE6","URBAN","Planned","",3,370,1.1017993077523987E-3,2.9778359668983749E-6,"NO"]
[null,"2015-07-19","14:49","LBH6A","RURAL","Asset failure","LV",1,150.25,3.8513988075402825E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","08:49","BGY6A","URBAN","Overloads","",1,88.25,8.7598008026260548E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","17:58","LTA12A","URBAN","Asset failure","LV",1,214.36666666670001,2.1278292336807147E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","08:49","CSE9","URBAN","Planned","",17,264,4.4548426064799701E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-19","09:08","BIS15A","RURAL","Overloads","",1,197.38333333329999,5.0595802637484039E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","10:00","QPT6","URBAN","Planned","",6,120,7.1468063205561009E-4,5.9556719337967507E-6,"NO"]
[null,"2015-07-19","10:31","BPN31A","URBAN","Asset failure","LV",1,359.03333333329999,3.5638079110510471E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","10:38","WMD4A","RURAL","Asset failure","LV",1,177.0666666667,4.5387976629301902E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","11:25","GGR1","RURAL","Third party","Vehicle impact",98,168.16153846153082,4.2206802386283125E-2,2.5120604535038113E-4,"NO"]
[null,"2015-07-19","14:06","NRG22A","URBAN","Overloads","",1,63.6,6.3130122498245556E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","14:52","RPN8","RURAL","Overloads","",1,98.95,2.5364120599408386E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","15:12","BIS12B","RURAL","Overloads","",1,162.69999999999999,4.1705330182150016E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-19","17:22","ZMR9","URBAN","Unknown","Unknown",50,138,6.8490227238662636E-3,4.9630599448306258E-5,"NO"]
[null,"2015-07-19","17:30","KMR17B","URBAN","Asset failure","LV",1,198.9333333333,1.9746361167162808E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","08:39","CSE7","URBAN","Planned","",4,370,1.4690657436698651E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-19","18:54","KCY1","URBAN","Overloads","",1,95.883333333300001,9.5174946208668879E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-19","21:01","GNA12A","RURAL","Asset failure","LV",60,104.0666666667,1.6005413746615127E-2,1.5379961960227417E-4,"NO"]
[null,"2015-07-19","23:25","LDR3","URBAN","Asset failure","LV",31,50,1.538548582897494E-3,3.0770971657949879E-5,"NO"]
[null,"2015-07-20","21:36","AJV1","URBAN","Asset failure","LV",1,66.533333333300007,6.6041784332513108E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","11:30","NMK12A","URBAN","Planned","",13,135,1.7420340406355496E-3,1.2903955856559627E-5,"NO"]
[null,"2015-07-20","09:21","SPO32A","URBAN","Planned","",51,138,6.9860031783435883E-3,5.062321143727238E-5,"NO"]
[null,"2015-07-20","09:21","LDR10A","URBAN","Planned","",8,138,1.0958436358186022E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-20","10:30","GNA5A","RURAL","Planned","",37,329,3.1203379490308061E-2,9.4843098754735753E-5,"NO"]
[null,"2015-07-20","10:10","THL1","RURAL","Planned","",2,72,3.6911908704545803E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-20","10:44","AHD9","URBAN","Overloads","",1,75.900000000000006,7.5339249962528898E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","10:53","NDC3","CBD","Third party","Other",1,70.25,1.7971348170887694E-2,2.5581990278843696E-4,"NO"]
[null,"2015-07-20","11:03","ENG4A","URBAN","Planned","",49,207,1.0068063404083408E-2,4.8637987459340128E-5,"NO"]
[null,"2015-07-20","11:15","SRD18A","URBAN","Planned","",7,45,3.1267277652432943E-4,6.9482839227628759E-6,"NO"]
[null,"2015-07-20","05:03","AHD22A","URBAN","Planned","",10,59,5.856410734900138E-4,9.9261198896612508E-6,"NO"]
[null,"2015-07-20","22:39","TWG13A","URBAN","Overloads","",1,52.633333333300001,5.2244477685883968E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","06:31","BSEENG35","URBAN","Planned","",1,12,1.1911343867593501E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","20:12","GTN15A","RURAL","Overloads","",120,57.233333333300003,1.7604929790463398E-2,3.0759923920454835E-4,"NO"]
[null,"2015-07-20","19:52","CLM4A","URBAN","Asset failure","LV",1,200.65,1.9916759558605301E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","18:35","NVL3","URBAN","Asset failure","LV",1,45.95,4.5610520892993451E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","18:04","INA3A","URBAN","Asset failure","LV",1,70.216666666699993,6.9697905158604503E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","16:32","INA10A","RURAL","Asset failure","LV",1,154.01666666669999,3.9479507909581202E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-20","16:27","EMP21A","RURAL","Third party","Vehicle impact",7,59.416666666700003,1.0661304186602516E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-20","15:56","SMR10B","URBAN","Asset failure","LV",1,138.9,1.3787380526739478E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","15:53","SMR15A","URBAN","Other","Other System Failures",1,101.2666666667,1.0051850741600269E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","13:33","MRE8","URBAN","Asset failure","LV",1,69.516666666700004,6.9003076766328229E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","12:50","NBR5A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",185,56.187745086292402,2.261828472409886E-2,4.7421549377367884E-4,"NO"]
[null,"2015-07-20","11:58","THL1","RURAL","Planned","",5,86,1.1022306071496316E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-20","23:22","NSW17","URBAN","Asset failure","LV",1,194.95,1.9350970724894609E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","08:23","NRA12A","URBAN","Planned","",10,216,2.1440418961668302E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-20","09:42","DRD15B","URBAN","Planned","",35,123,4.2731946124991687E-3,3.4741419613814376E-5,"NO"]
[null,"2015-07-20","09:15","CHL7","URBAN","Planned","",1,112,1.1117254276420601E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","09:14","UMG5A","URBAN","Planned","",9,246,2.1976429435710009E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-20","09:25","CLD17A","URBAN","Planned","",33,399,1.3069722058716971E-2,3.2756195635882131E-5,"NO"]
[null,"2015-07-20","09:14","BLN15A","URBAN","Planned","",5,262,1.300321705545624E-3,4.9630599448306254E-6,"NO"]
[null,"2015-07-20","09:14","BLH9A","URBAN","Planned","",10,262,2.600643411091248E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-20","09:05","SPO11A","URBAN","Asset failure","LV",1,248.28333333329999,2.4644901332710633E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","08:59","FDS4","RURAL","Planned","",1,179,4.5883553181345129E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-20","08:55","TRP3","RURAL","Planned","",1,131,3.3579583613163198E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-20","08:51","NRA13A","RURAL","Asset failure","LV",1,113.4833333333,2.9089489163099368E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-20","04:59","LBH3A","RURAL","Animal","Animal impact",179,75.716666666699993,3.4741497017157119E-2,4.5883553181345134E-4,"NO"]
[null,"2015-07-20","08:28","BDT4","RURAL","Planned","",30,123,9.4586766055398622E-3,7.6899809801137087E-5,"NO"]
[null,"2015-07-20","08:20","RCN4A","URBAN","Planned","",3,300,8.9335079006951264E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-20","08:18","GYM5B","RURAL","Planned","",29,286,2.1260234083021034E-2,7.4336482807765855E-5,"NO"]
[null,"2015-07-20","08:14","GAP1A","URBAN","Planned","",56,590,3.2795900115440771E-2,5.5586271382103001E-5,"NO"]
[null,"2015-07-20","08:10","NRA13A","RURAL","Third party","Vehicle impact",70,108.25,1.9423610292270545E-2,1.7943288953598655E-4,"NO"]
[null,"2015-07-20","08:06","NGE7","URBAN","Planned","",1,211,2.094411296718524E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","08:04","LGV5B","RURAL","Planned","",8,423,8.6742985455682646E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-20","08:01","SBH11","URBAN","Planned","",3,205,6.1045637321416693E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-20","08:00","BHD23A","RURAL","Planned","",2,205,1.0509640672822069E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-20","07:22","WMD11A","RURAL","Asset failure","LV",1,87.616666666699999,2.2459016673596194E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-20","07:13","CBW8","URBAN","Asset failure","LV",1,52.116666666699999,5.1731628158317642E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","07:10","MFN1B","URBAN","Asset failure","LV",1,38.733333333300003,3.8447171039254828E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-20","08:35","JBB13A","RURAL","Planned","",4,35,3.588657790719731E-4,1.0253307973484946E-5,"NO"]
[null,"2015-07-20","19:54","KRN10","URBAN","Asset failure","LV",100,113.35,1.1251256894931028E-2,9.9261198896612515E-5,"NO"]
[null,"2015-07-21","09:40","DRD15B","URBAN","Planned","",25,120,2.9778359668983755E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-21","08:59","JBB1B","RURAL","Planned","",12,206,6.3365443276136961E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-21","09:00","BHD20A","URBAN","Planned","",4,260,1.0323164685247701E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-21","09:00","LTN9","URBAN","Planned","",8,80,6.3527167293832005E-4,7.9408959117290003E-6,"NO"]
[null,"2015-07-21","09:04","MTB13A","RURAL","Planned","",14,323,1.1591364664024731E-2,3.5886577907197311E-5,"NO"]
[null,"2015-07-21","09:11","HDA10A","URBAN","Planned","",14,334,4.6414536604056011E-3,1.3896567845525752E-5,"NO"]
[null,"2015-07-21","08:05","BHL2A","URBAN","Planned","",3,375,1.1166884875868908E-3,2.9778359668983753E-6,"NO"]
[null,"2015-07-21","09:42","TWG14A","URBAN","Planned","",154,356,5.4418959683078846E-2,1.5286224630078326E-4,"NO"]
[null,"2015-07-21","09:45","KSN6","URBAN","Planned","",12,270,3.2160628442502452E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-21","10:20","MLY6","RURAL","Planned","",8,200,4.1013231893939784E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-21","10:21","WRD20A","URBAN","Overloads","",1,98.116666666699999,9.7391779650759402E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","09:11","CPK9","RURAL","Planned","",39,226,2.2593164119574079E-2,9.9969752741478217E-5,"NO"]
[null,"2015-07-21","08:31","CRM15A","URBAN","Planned","",11,245,2.6750893102637074E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-21","08:03","RBY12","URBAN","Planned","",10,66,6.5512391271764264E-4,9.9261198896612508E-6,"NO"]
[null,"2015-07-21","08:20","CPS15A","URBAN","Planned","",10,216,2.1440418961668302E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-21","08:21","GYN12B","URBAN","Planned","",7,203,1.4105016363208638E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-21","08:25","CPD1","RURAL","Planned","",3,281,2.1608846554119522E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-21","08:25","EMP3","URBAN","Planned","",6,180,1.0720209480834151E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-21","08:18","AHD7","URBAN","Planned","",59,400,2.3425642939600554E-2,5.8564107349001382E-5,"NO"]
[null,"2015-07-21","08:30","DBY4","URBAN","Planned","",2,171,3.3947330022641482E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-21","08:18","AHD15B","URBAN","Planned","",1,400,3.9704479558645006E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","08:31","INA1A","URBAN","Planned","",26,301,7.7681814256488953E-3,2.5807911713119252E-5,"NO"]
[null,"2015-07-21","08:36","LLY3","RURAL","Planned","",6,240,3.6911908704545804E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-21","08:37","JBB13A","RURAL","Planned","",1,333,8.5358788879262169E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-21","08:41","UMG5A","URBAN","Planned","",8,299,2.3743278776069713E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-21","08:50","WMR3","RURAL","Planned","",24,163,1.0027735198068276E-2,6.1519847840909667E-5,"NO"]
[null,"2015-07-21","08:54","NVL12","URBAN","Planned","",40,281,1.1156958755979246E-2,3.9704479558645003E-5,"NO"]
[null,"2015-07-21","08:28","BKD5B","URBAN","Planned","",7,52,3.6131076398366956E-4,6.9482839227628759E-6,"NO"]
[null,"2015-07-21","10:29","TWG18","URBAN","Planned","",8,208,1.6517063496396323E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-21","06:41","NRA3B","URBAN","Planned","",4,126,5.0027644243892709E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-21","06:47","MLS26B","URBAN","Asset failure","LV",1,73.099999999999994,7.2559936393423746E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","07:20","HPK3A","URBAN","Asset failure","LV",1,39.2166666667,3.8926933500654631E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","07:41","BRT5","URBAN","Third party","Other",1,188.6833333333,1.8728933878472528E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","08:00","MCN1","RURAL","Planned","",14,352,1.2632075423333455E-2,3.5886577907197304E-5,"NO"]
[null,"2015-07-21","08:19","CRB24B","URBAN","Planned","",29,265,7.6282231352046721E-3,2.878574768001763E-5,"NO"]
[null,"2015-07-21","08:02","BKD5B","URBAN","Planned","",15,200,2.9778359668983755E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-21","06:40","LYT4A","URBAN","Planned","",1,655,6.50160852772812E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","08:03","SHW4","URBAN","Planned","",1,112,1.1117254276420601E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","15:20","JBB1B","RURAL","Asset failure","LV",1,372.15,9.5394214058310554E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-21","08:05","BLB8B","URBAN","Planned","",28,300,8.3379407073154513E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-21","08:05","LTA16A","URBAN","Planned","",25,252,6.2534555304865885E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-21","08:09","FDS3","RURAL","Planned","",18,271,1.2503909073664891E-2,4.6139885880682253E-5,"NO"]
[null,"2015-07-21","08:15","GAP1A","URBAN","Planned","",22,188,4.1054431863638934E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-21","08:01","HIS1B","URBAN","Planned","",109,134.33333333333334,2.4700156733433058E-2,1.0819470679730764E-4,"NO"]
[null,"2015-07-21","21:09","SHW5A","URBAN","Asset failure","LV",1,60.166666666700003,5.9722154669494953E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","14:58","RLA4A","URBAN","Overloads","",1,45.3,4.4965323100165465E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","06:12","ALY3A","URBAN","Planned","",13,84,1.0839322919510086E-3,1.2903955856559627E-5,"NO"]
[null,"2015-07-21","10:32","RBY12","URBAN","Planned","",4,59,2.3425642939600553E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-21","21:35","DRD3A","URBAN","Asset failure","LV",1,82.083333333300004,8.1476900760936357E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","21:05","WRG19A","URBAN","Asset failure","LV",1,91.3,9.0625474592607219E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","20:08","SDST1","URBAN","Asset failure","LV",1,87.466666666699993,8.6820461968270155E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","19:45","LTN8","RURAL","Asset failure","LV",1,144.65,3.7078524959114934E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-21","18:27","MTB3A","RURAL","Asset failure","LV",1,123.9833333333,3.1780982506139166E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-21","17:57","BPN36A","URBAN","Asset failure","LV",1,174.4166666667,1.7312807440887475E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","17:53","RLB16A","RURAL","Third party","Vehicle impact",2,41,2.1019281345644139E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-21","16:20","MHL3A","URBAN","Asset failure","LV",1,195.0833333333,1.936420555141085E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","16:01","NBR12A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",153,21,8.235969629701783E-3,3.921890299857992E-4,"NO"]
[null,"2015-07-21","11:56","HWL10A","URBAN","Asset failure","LV",1,156.05000000000001,1.5489710087816385E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","22:10","TRG7A","URBAN","Asset failure","LV",1,127.0666666667,1.2612789673132873E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","11:07","MLY3","RURAL","Asset failure","LV",1,223.05,5.7175008587145425E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-21","10:56","MLY4","RURAL","Asset failure","LV",1,122.45,3.1387939033830788E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-21","11:08","SMF5A","RURAL","Planned","",20,125,6.4083174834280911E-3,5.1266539867424725E-5,"NO"]
[null,"2015-07-21","06:12","ALY8","URBAN","Planned","",2,84,1.6675881414630902E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-21","11:54","WRG1A","URBAN","Asset failure","LV",1,21.7833333333,2.1622397826279004E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","12:15","AFD6OLD","URBAN","Planned","",1,40,3.9704479558645003E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","12:34","RBY12","URBAN","Planned","",11,63,6.8788010835352481E-4,1.0918731878627375E-5,"NO"]
[null,"2015-07-21","12:55","EMP3","URBAN","Planned","",4,113,4.4866061901268858E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-21","14:42","FGBSGT23","URBAN","Third party","Vehicle impact",2,148,2.9381314873397303E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-21","08:58","DRD15B","URBAN","Planned","",15,257,3.8265192174644124E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-21","15:12","KVG32A","URBAN","Overloads","",1,115.45,1.1459705412613915E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-21","10:39","BRD3B","RURAL","Unknown","Unknown",745,33.383076923078463,9.1385341529147596E-2,1.9096786100615711E-3,"NO"]
[null,"2015-07-21","14:40","WSE3A","RURAL","Asset failure","HV",2,422,2.1634479824053235E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-21","17:37","ZMR10","URBAN","Asset failure","LV",69,82.9,5.677839838085133E-3,6.8490227238662637E-5,"NO"]
[null,"2015-07-22","08:35","IDY9B","URBAN","Planned","",36,295,1.0541539322820249E-2,3.5734031602780506E-5,"NO"]
[null,"2015-07-22","08:56","IPL4A","RURAL","Animal","Animal nesting/burrowing, etc and other",124,22.208333333300036,1.4117950637136467E-2,3.1785254717803328E-4,"NO"]
[null,"2015-07-22","08:56","IPL2A","RURAL","Animal","Animal nesting/burrowing, etc and other",274,5.3833333333000066,3.7809927594322731E-3,7.0235159618371886E-4,"NO"]
[null,"2015-07-22","08:56","IPL1","RURAL","Animal","Animal nesting/burrowing, etc and other",489,25.216666666699922,3.160825698895281E-2,1.2534668997585363E-3,"NO"]
[null,"2015-07-22","08:50","KMR17A","URBAN","Planned","",14,188,2.6125547549588415E-3,1.3896567845525752E-5,"NO"]
[null,"2015-07-22","09:00","WNM2A","URBAN","Planned","",4,222,8.8143944620191908E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-22","08:39","YDA3A","RURAL","Planned","",11,380,1.0714706832291768E-2,2.8196596927083601E-5,"NO"]
[null,"2015-07-22","09:20","MTB1B","RURAL","Planned","",15,248,9.5355764153409999E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-22","08:35","AGT25A","URBAN","Planned","",32,189,6.0033173092671251E-3,3.1763583646916008E-5,"NO"]
[null,"2015-07-22","08:40","FDS4","RURAL","Planned","",1,97,2.4864271835700993E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","09:03","LRE6A","RURAL","Planned","",3,246,1.8917353211079725E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-22","09:05","BRD10B","RURAL","Planned","",31,288,2.28853833968184E-2,7.9463136794508333E-5,"NO"]
[null,"2015-07-22","09:07","KSN1","URBAN","Planned","",35,284,9.8665631703232833E-3,3.4741419613814376E-5,"NO"]
[null,"2015-07-22","09:30","WFD5A","RURAL","Planned","",14,338.5,1.2134789986619432E-2,3.5886577907197304E-5,"NO"]
[null,"2015-07-22","09:50","BHD41A","RURAL","Planned","",20,162,8.3051794585228059E-3,5.1266539867424725E-5,"NO"]
[null,"2015-07-22","10:00","PPE6A","RURAL","Planned","",1,184,4.7165216678030748E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","10:24","RBK9A","URBAN","Planned","",2,146,2.8984270077810856E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-22","08:31","GAP1A","URBAN","Planned","",4,116,4.6057196288028208E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-22","08:05","YDA3A","RURAL","Planned","",17,416,1.8127848497121384E-2,4.3576558887311015E-5,"NO"]
[null,"2015-07-22","09:05","GNA13A","URBAN","Planned","",59,216,1.2649847187384298E-2,5.8564107349001382E-5,"NO"]
[null,"2015-07-22","08:12","KRN18","URBAN","Planned","",2,215,4.2682315525543378E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-22","08:12","KRNQNP7","URBAN","Planned","",9,215,1.9207041986494522E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-22","01:25","TGW4","RURAL","Asset failure","LV",1,153.53333333329999,3.9355613771551172E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","02:46","BMT1","RURAL","Unknown","Unknown",158,17.083333333300001,6.9188467762610313E-3,4.0500566495265539E-4,"NO"]
[null,"2015-07-22","05:42","CDRSPD9","URBAN","Third party","Other",552,49.038888888899997,2.7337179373926563E-2,5.4792181790930109E-4,"NO"]
[null,"2015-07-22","07:35","NPD1","URBAN","Planned","",1,1622,1.6100166461030549E-3,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","08:00","WMR3","RURAL","Planned","",17,390.75,1.7363977053096755E-2,4.3576558887311015E-5,"NO"]
[null,"2015-07-22","08:05","MTG16A","URBAN","Planned","",26,270,6.9681361625421982E-3,2.5807911713119252E-5,"NO"]
[null,"2015-07-22","08:05","NIP4A","RURAL","Planned","",1,268,6.869716342234913E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","08:12","BDT4","RURAL","Planned","",1,122,3.1272589319129087E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","08:10","MLY4","RURAL","Planned","",25,365,2.3390358814512534E-2,6.4083174834280912E-5,"NO"]
[null,"2015-07-22","08:30","CRY2A","RURAL","Planned","",100,324,8.2692928806156085E-2,2.5633269933712365E-4,"NO"]
[null,"2015-07-22","08:12","NMK4A","URBAN","Planned","",25,215,5.3352894406929223E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-22","08:13","FDS4","RURAL","Planned","",10,417,1.0689073562358056E-2,2.5633269933712362E-5,"NO"]
[null,"2015-07-22","08:15","CPR5","URBAN","Planned","",1,224,2.2234508552841203E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","08:15","CPR7","URBAN","Planned","",15,224,3.3351762829261803E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-22","08:18","FDS4","RURAL","Planned","",3,428,3.2913118594886676E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-22","08:18","TBV4","RURAL","Planned","",3,394,3.0298525061648015E-3,7.68998098011371E-6,"NO"]
[null,"2015-07-22","08:20","BDT6","URBAN","Planned","",1,280,2.7793135691051501E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","08:25","NIP4A","RURAL","Planned","",14,220,7.8950471395834079E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-22","08:27","CMY4","RURAL","Planned","",9,157,3.6219810416335571E-3,2.3069942940341127E-5,"NO"]
[null,"2015-07-22","08:05","NMC5A","RURAL","Planned","",32,691,5.6680286477424777E-2,8.2026463787879565E-5,"NO"]
[null,"2015-07-22","21:55","PWC3","RURAL","Animal","Animal impact",41,84.616666666699999,8.8929076159897768E-3,1.0509640672822069E-4,"NO"]
[null,"2015-07-22","08:12","YTA35A","URBAN","Third party","Other",1,584,5.7968540155621713E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","10:30","CSE9","URBAN","Planned","",15,46,6.8490227238662631E-4,1.4889179834491876E-5,"NO"]
[null,"2015-07-22","22:36","GYGGYS6","RURAL","Animal","Animal impact",1,73.066666666700002,1.8729375898241045E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","21:40","KMR19A","URBAN","Asset failure","LV",1,50.8,5.0424689039479157E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","20:29","KWA2A","URBAN","Asset failure","LV",1,159.19999999999999,1.5802382864340712E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","20:24","LTA3A","RURAL","Asset failure","LV",1,98.816666666700002,2.5329942906171982E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","20:03","MLY4","RURAL","Asset failure","LV",1,95.966666666699993,2.4599394713061175E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","18:13","NRG22A","URBAN","Overloads","",1,11.6833333333,1.1597016737721141E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","11:47","FDS4","RURAL","Planned","",2,78,3.9987901096591287E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-22","22:45","ALY3A","URBAN","Asset failure","LV",1,109.8666666667,1.0905497052111137E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","18:12","BHD35A","RURAL","Overloads","",36,103.0666666667,9.510968476207712E-3,9.2279771761364507E-5,"NO"]
[null,"2015-07-22","11:29","BDT4","RURAL","Planned","",3,91,6.9978826919034755E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-22","10:56","RST20A","RURAL","Asset failure","LV",1,182.9333333333,4.6891795132062607E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","12:02","MCW7","RURAL","Overloads","",1,110.03333333330001,2.8205141350386295E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","12:03","KWH1","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",39,198.49761904760709,1.7982935077761084E-2,9.9969752741478217E-5,"NO"]
[null,"2015-07-22","12:25","MTG4B","URBAN","Asset failure","LV",1,54.383333333300001,5.3981548666574688E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-22","13:26","GYM7A","RURAL","Asset failure","LV",1,106.5,2.729943247940367E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","17:13","KBR3A","RURAL","Asset failure","LV",1,237.01666666669999,6.0755121954562464E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","08:47","GBN4","RURAL","Asset failure","LV",1,111.5666666667,2.8598184822720303E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-22","18:46","RBA43A","RURAL","Asset failure","LV",22,286.43333333330003,1.6152890492960079E-2,5.6393193854167202E-5,"NO"]
[null,"2015-07-22","13:00","KSN3","URBAN","Asset failure","HV",78,299.04999999999995,3.1675836747091402E-2,7.7423735139357761E-5,"NO"]
[null,"2015-07-22","20:00","CPB4","URBAN","Asset failure","Distribution substation",48,75,3.5734031602780505E-3,4.7645375470374005E-5,"NO"]
[null,"2015-07-22","20:07","WRD25B","URBAN","Asset failure","Distribution substation",113,203,2.2769526414893944E-2,1.1216515475317214E-4,"NO"]
[null,"2015-07-23","12:24","AHD4A","URBAN","Unknown","Unknown",1652,92.01031746032379,0.15593600167289634,1.6397950057720385E-3,"NO"]
[null,"2015-07-23","11:36","SMF6A","RURAL","Planned","",18,168,7.7515008279546186E-3,4.6139885880682253E-5,"NO"]
[null,"2015-07-23","12:02","TPT1","URBAN","Asset failure","LV",1,95.233333333299996,9.4529748415840887E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","11:53","NDH12","URBAN","Asset failure","LV",1,61.366666666699999,6.0913289056254299E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","11:39","KMR22A","URBAN","Asset failure","LV",1,12.0666666667,1.1977518000224331E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","12:07","MDR8A","RURAL","Asset failure","LV",1,147.21666666670001,3.7736445554088766E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","11:34","KSN8","RURAL","Planned","",1,236,6.0494517043561177E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","11:33","BRD10B","RURAL","Planned","",2,92,4.7165216678030748E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-23","11:15","CLD20A","URBAN","Planned","",33,127,4.1600368457570302E-3,3.2756195635882131E-5,"NO"]
[null,"2015-07-23","10:12","SMF5A","RURAL","Planned","",15,93,3.5758411557528747E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-23","12:24","AHD4B","RURAL","Unknown","Unknown",532,61.70000000000001,8.413967056121481E-2,1.3636899604734978E-3,"NO"]
[null,"2015-07-23","19:28","SPD4A","RURAL","Overloads","",1,95.816666666700002,2.4560944808160609E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","10:46","SMF5A","RURAL","Asset failure","LV",1,32.483333333300003,8.3265405167923554E-5,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","12:40","KSN7","RURAL","Planned","",1,46,1.1791304169507687E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","13:03","NRA2A","URBAN","Planned","",1,134,1.3301000652146076E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","15:12","AHD4A","URBAN","Asset failure","LV",1,59.016666666699997,5.8580650882183903E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","16:10","JBB16A","RURAL","Overloads","",1,258.5,6.6262002778646458E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","16:23","LBS4A","URBAN","Third party","Vehicle impact",6,96.583333333300004,5.7521864760567097E-4,5.9556719337967507E-6,"NO"]
[null,"2015-07-23","16:35","KSN6","URBAN","Asset failure","LV",1,138.4,1.3737749927291172E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","16:58","BKD3A","URBAN","Overloads","",1,88.366666666699999,8.771381275833968E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","17:58","CNB26A","RURAL","Third party","Vehicle impact",29,57,4.2371795200426537E-3,7.4336482807765855E-5,"NO"]
[null,"2015-07-23","10:02","INA2A","URBAN","Planned","",2,118,2.3425642939600553E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-23","18:56","CNB26A","RURAL","Asset failure","LV",1,140.44999999999999,3.6001927621899011E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","10:52","BPN4","URBAN","Asset failure","LV",1,70.666666666699996,7.0144580553639258E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","20:05","CPS12B","RURAL","Asset failure","LV",1,91.116666666699999,2.3356181121276127E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","18:37","WRG11A","URBAN","Overloads","",1,139.0833333333,1.3805578413200549E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","08:00","THL1","RURAL","Planned","",58,423.625,6.523667198129797E-2,1.4867296561553168E-4,"NO"]
[null,"2015-07-23","02:45","KSN1","URBAN","Asset failure","LV",1,113.95,1.1310813614268996E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","06:02","BHD20A","URBAN","Overloads","",1,103.5833333333,1.0281805852370805E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","08:00","KBR1A","RURAL","Planned","",4,447,4.5678487021875436E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-23","09:44","ECWMTS47","URBAN","Asset failure","LV",1,115.15,1.1429927052944932E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","08:04","CPR5","URBAN","Planned","",2,256,5.0821733835065602E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-23","08:04","CPR7","URBAN","Planned","",27,256,6.8609340677338567E-3,2.6800523702085378E-5,"NO"]
[null,"2015-07-23","08:05","ACR12A","URBAN","Planned","",26,333,8.5940346004687099E-3,2.5807911713119252E-5,"NO"]
[null,"2015-07-23","08:05","ACR3","URBAN","Planned","",1,333,3.3053979232571966E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","08:14","KMR24A","URBAN","Planned","",9,295,2.6353848307050622E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-23","08:15","ZMR5","URBAN","Planned","",21,254,5.2945923491453115E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-23","08:17","NGI3A","RURAL","Planned","",5,215,2.7555765178740792E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-23","08:21","GAP1A","URBAN","Planned","",22,514,1.1224456371228942E-2,2.1837463757254754E-5,"NO"]
[null,"2015-07-23","08:21","GAP6A","URBAN","Planned","",1,514,5.1020256232858828E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","08:21","GAP8A","URBAN","Planned","",4,514,2.0408102493143531E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-23","09:06","SMF1B","RURAL","Planned","",20,289,1.4816030021685746E-2,5.1266539867424725E-5,"NO"]
[null,"2015-07-23","07:08","MDH4A","URBAN","Planned","",1,316,3.1366538851329556E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","08:23","BDT2","RURAL","Planned","",1,164,4.2038562691288278E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","09:22","VSL1B","URBAN","Planned","",1,3,2.9778359668983753E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-23","09:17","SMF6A","RURAL","Asset failure","LV",1,69.3,1.7763856064062668E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-23","08:49","KBN2A","RURAL","Planned","",7,203,3.6424876575805267E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-23","08:41","ALY8","URBAN","Planned","",44,298,1.3015128399323833E-2,4.3674927514509508E-5,"NO"]
[null,"2015-07-23","08:30","CMY4","RURAL","Planned","",25,201,1.2880718141690463E-2,6.4083174834280912E-5,"NO"]
[null,"2015-07-23","08:36","KSN8","RURAL","Planned","",36,341,3.1467402170625297E-2,9.2279771761364507E-5,"NO"]
[null,"2015-07-23","08:26","KRN2","URBAN","Planned","",21,265,5.5238857185964862E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-23","08:30","SMF6A","RURAL","Planned","",13,139,4.6319318770218238E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-23","08:38","NVL12","URBAN","Planned","",52,226,1.1665176094329903E-2,5.161582342623851E-5,"NO"]
[null,"2015-07-23","08:28","AMR2","RURAL","Planned","",4,231,2.3685141418750225E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-23","20:30","BKD13A","URBAN","Asset failure","Distribution substation",67,81.8,5.4401092667277461E-3,6.6505003260730378E-5,"NO"]
[null,"2015-07-23","15:29","KWH3","RURAL","Asset failure","HV",4,16,1.6405292757575913E-4,1.0253307973484946E-5,"NO"]
[null,"2015-07-23","17:51","PGN2B","RURAL","Asset failure","HV",1556,94.265476201108825,0.37058368664523728,3.9885368016856441E-3,"NO"]
[null,"2015-07-23","17:51","PGN6A","URBAN","Asset failure","HV",2146,94.420952391281219,0.19266391911668126,2.1301453283213041E-3,"NO"]
[null,"2015-07-24","10:48","BHD45B","URBAN","Planned","",43,97,4.140184605977708E-3,4.2682315525543378E-5,"NO"]
[null,"2015-07-24","10:44","GYS3A","RURAL","Overloads","",1,64.816666666700002,1.6614631128709776E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-24","10:29","HWL3A","URBAN","Planned","",34,115,3.8811128768575492E-3,3.3748807624848254E-5,"NO"]
[null,"2015-07-24","10:29","HWL10A","URBAN","Planned","",21,115,2.397157953353192E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-24","10:21","JBB2A","RURAL","Planned","",26,226,1.5062109413049385E-2,6.6646501827652145E-5,"NO"]
[null,"2015-07-24","09:48","KBN13A","RURAL","Planned","",5,168,2.1531946744318387E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-24","10:03","LDR10A","URBAN","Asset failure","LV",1,50.066666666700002,4.9696773580937087E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","10:49","KBR5A","RURAL","Asset failure","LV",1,142.6833333333,3.6574403983743379E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-24","14:05","LGL5A","URBAN","Planned","",1,189,1.8760366591459766E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","09:31","RBY6","URBAN","Planned","",15,263,3.9158542964713638E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-24","09:31","BKD15A","URBAN","Planned","",23,263,6.0043099212560907E-3,2.2830075746220877E-5,"NO"]
[null,"2015-07-24","09:30","GNA5A","RURAL","Planned","",3,290,2.2300944842329755E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-24","10:18","RBARHP14","URBAN","Planned","",73,83,6.0142360411457527E-3,7.2460675194527127E-5,"NO"]
[null,"2015-07-24","11:07","VSL10B","URBAN","Asset failure","LV",1,169.6666666667,1.6841316746128566E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","11:10","CRB25A","RURAL","Planned","",3,105,8.0744800291193946E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-24","12:02","AGT31A","RURAL","Planned","",1,258,6.6133836428977904E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-24","12:15","SMF5A","RURAL","Planned","",15,47,1.8071455303267216E-3,3.8449904900568543E-5,"NO"]
[null,"2015-07-24","12:54","SFD7A","URBAN","Asset failure","LV",1,77.283333333300007,7.671236321389896E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","13:45","CBW6","RURAL","Asset failure","LV",1,140.6666666667,3.6057466373430602E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-24","15:40","ZMR3","URBAN","Asset failure","LV",1,71.216666666699993,7.0690517147570619E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","16:02","CHL2","URBAN","Asset failure","LV",1,112.03333333330001,1.1120562983047181E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","20:06","SPO8A","URBAN","Asset failure","LV",1,110,1.0918731878627377E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","10:06","NSW17","URBAN","Asset failure","LV",1,52.45,5.2062498821273265E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","08:20","RCF10A","URBAN","Planned","",29,351,1.0103797435686188E-2,2.8785747680017626E-5,"NO"]
[null,"2015-07-24","09:30","GNA13A","URBAN","Planned","",15,290,4.3178621520026444E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-24","10:07","SMF6A","RURAL","Planned","",6,293,4.5063288543466338E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-24","13:38","TWT12A","RURAL","Planned","",29,15,1.1150472421164878E-3,7.4336482807765855E-5,"NO"]
[null,"2015-07-24","10:13","TWT12A","RURAL","Planned","",4,46,4.7165216678030748E-4,1.0253307973484946E-5,"NO"]
[null,"2015-07-24","08:25","COR26A","RURAL","Planned","",47,305,3.6745292449976666E-2,1.204763686884481E-4,"NO"]
[null,"2015-07-24","02:10","KRN10","URBAN","Animal","Animal impact",1567,150.02878787875451,0.23204914157255652,1.5554229867099181E-3,"NO"]
[null,"2015-07-24","03:13","BVL3A","URBAN","Animal","Animal impact",92,100.25,9.1548603742345729E-3,9.1320302984883506E-5,"NO"]
[null,"2015-07-24","04:04","VPT16A","URBAN","Asset failure","LV",1,83.7,8.308162347646467E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","08:07","MLY4","RURAL","Planned","",25,471,3.0183175346946308E-2,6.4083174834280912E-5,"NO"]
[null,"2015-07-24","08:08","MDHQBI2","URBAN","Planned","",1,107,1.0620948281937539E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","08:14","SRD4A","URBAN","Planned","",2,82,1.6278836619044453E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-24","08:15","ESK3A","RURAL","Planned","",1,219,5.6136861154830074E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-24","09:30","CRB25A","RURAL","Planned","",9,257,5.9289753356676694E-3,2.3069942940341127E-5,"NO"]
[null,"2015-07-24","08:19","ZMR3","URBAN","Planned","",4,254,1.0084937807895832E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-24","00:16","CSE7","URBAN","Animal","Animal impact",41,209.65,8.5321452429566735E-3,4.0697091547611133E-5,"NO"]
[null,"2015-07-24","08:22","NMK4A","URBAN","Planned","",22,298,6.5075641996619167E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-24","10:10","BLN16A","URBAN","Asset failure","LV",1,71.733333333299996,7.1203366675136952E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","09:05","SMF6A","RURAL","Planned","",16,103,4.224362885075798E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-24","09:23","IDY9B","URBAN","Planned","",83,209,1.7218840172595371E-2,8.2386795084188382E-5,"NO"]
[null,"2015-07-24","09:19","ALY3A","URBAN","Asset failure","LV",1,74.783333333300007,7.423083324148365E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","08:16","GYN13A","RURAL","Planned","",12,268,8.2436596106818961E-3,3.0759923920454833E-5,"NO"]
[null,"2015-07-24","09:13","SMF6A","RURAL","Planned","",6,467,7.1824422354262044E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-24","08:31","NMK12A","URBAN","Asset failure","LV",1,192.13333333329999,1.9071385014665841E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-24","09:02","KBN13A","RURAL","Planned","",40,197,2.0199016707765343E-2,1.0253307973484945E-4,"NO"]
[null,"2015-07-24","09:00","CMA10A","RURAL","Planned","",1,265,6.7928165324337769E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-24","08:56","WMR2","RURAL","Planned","",2,117,5.9981851644886936E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-24","08:50","MLB3A","RURAL","Planned","",70,300,5.3829866860795966E-2,1.7943288953598655E-4,"NO"]
[null,"2015-07-24","08:48","LGL15A","URBAN","Planned","",21,206,4.2940394642674573E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-24","08:39","CPB4","URBAN","Planned","",3,259,7.7125951542667925E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-24","08:35","COR23A","RURAL","Planned","",24,316,1.9440271917727459E-2,6.151984784090968E-5,"NO"]
[null,"2015-07-24","08:34","GYN13A","RURAL","Planned","",65,305.85714285714283,5.2063734562363177E-2,1.6661625456913036E-4,"NO"]
[null,"2015-07-24","20:42","KVG9A","URBAN","Asset failure","LV",69,99,6.7805324966276007E-3,6.8490227238662637E-5,"NO"]
[null,"2015-07-24","16:51","PGN1B","RURAL","Asset failure","LV",169,484,0.20966989474979364,4.3320226187973897E-4,"NO"]
[null,"2015-07-24","07:07","MLY1","RURAL","Asset failure","LV",10,413,1.0586540482623205E-2,2.5633269933712362E-5,"NO"]
[null,"2015-07-25","20:57","UMG5A","URBAN","Planned","",4,293,1.1633412510682986E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-25","20:09","CPC2B","URBAN","Third party","Vehicle impact",43,220.7,9.4199870364874237E-3,4.2682315525543378E-5,"NO"]
[null,"2015-07-25","19:49","CPK10","URBAN","Third party","Vehicle impact",45,245.05,1.0945780555326703E-2,4.4667539503475631E-5,"NO"]
[null,"2015-07-25","19:27","MLS12B","URBAN","Overloads","",1,69.783333333300007,6.9267773296653016E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-25","19:02","MCN4","RURAL","Third party","Other",1,87.15,2.2339394747230326E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-25","18:11","CMA10A","RURAL","Asset failure","LV",1,59.483333333300003,1.5247523398894693E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-25","21:20","SBY3A","URBAN","Planned","",7,322,2.3485199658938522E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-25","17:46","BWH8A","RURAL","Third party","Unauthorised access",87,157.51666666669999,3.5127704950817192E-2,2.2300944842329758E-4,"NO"]
[null,"2015-07-25","15:28","CLD28A","RURAL","Asset failure","LV",1,127.2666666667,3.262260820231315E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-25","13:50","MGL9A","URBAN","Unknown","Unknown",27,187.8166666667,5.0335850266475619E-3,2.6800523702085378E-5,"NO"]
[null,"2015-07-25","09:39","WHO1","RURAL","Overloads","",1,39.4,1.0099508353882671E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-25","09:35","GYS3A","RURAL","Asset failure","LV",1,116.28333333330001,2.9807220721243317E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-25","09:11","NMK3A","URBAN","Asset failure","LV",1,39.9,3.9605218359748392E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-25","09:01","MAI5","URBAN","Asset failure","LV",1,66.616666666699999,6.6124501998326458E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-25","06:51","MCN3","URBAN","Planned","",2,489,9.7077452520887041E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-25","17:53","SPO11A","URBAN","Asset failure","LV",1,110.4333333333,1.09617450648126E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-25","17:46","CBT12A","RURAL","Third party","Unauthorised access",212,201.93578431373234,9.4189194038739821E-2,5.4342532259470209E-4,"NO"]
[null,"2015-07-25","12:07","CMD11A","RURAL","Asset failure","HV",2259,63.182051282038486,0.36785476872801687,5.7905556780256228E-3,"NO"]
[null,"2015-07-25","15:43","ARG5A","URBAN","Asset failure","HV",197,11,2.1509901800895932E-3,1.9554456182632664E-4,"NO"]
[null,"2015-07-26","10:51","COR26A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,51.483333333300003,1.3196861804197705E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-26","09:30","GTN15A","RURAL","Planned","",10,195,4.9984876370739104E-3,2.5633269933712362E-5,"NO"]
[null,"2015-07-26","22:09","DRD5A","URBAN","Asset failure","LV",1,44.65,4.4320125307337487E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","20:48","DRD5A","URBAN","Asset failure","LV",1,82.85,8.2237903285843468E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","19:13","JBB16A","RURAL","Overloads","",8,161.38333333329999,3.309426036907807E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-26","17:57","WRD20A","URBAN","Asset failure","LV",1,5.9833333333000001,5.9391284006142286E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","17:09","VPT12A","URBAN","Asset failure","LV",1,198.01666666669999,1.965537173484753E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","09:29","KWH3","RURAL","Planned","",25,559.94999999999993,3.5883373748455592E-2,6.4083174834280912E-5,"NO"]
[null,"2015-07-26","11:08","GLY3A","URBAN","Overloads","",1,60.433333333299998,5.998685119981974E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","08:12","BSEENG15OLD","URBAN","Planned","",3,415,1.2358019262628257E-3,2.9778359668983753E-6,"NO"]
[null,"2015-07-26","10:40","MLS14A","URBAN","Planned","",16,88,1.3975976804643042E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-26","11:21","RIS2","RURAL","Asset failure","LV",1,130.15,3.3361700818726643E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-26","09:29","KWH2","RURAL","Planned","",7,561.03333333329999,1.0066783212600034E-2,1.7943288953598652E-5,"NO"]
[null,"2015-07-26","09:29","KWH1","RURAL","Planned","",88,561.78333333329999,0.12672302568282007,2.2557277541666878E-4,"NO"]
[null,"2015-07-26","08:45","ACR4","URBAN","Planned","",3,310,9.2312914973849641E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-26","08:32","CSE6","URBAN","Planned","",48,308,1.4674775644875194E-2,4.7645375470374005E-5,"NO"]
[null,"2015-07-26","08:20","CBT15A","RURAL","Overloads","",1,175.01666666669999,4.4862494595660797E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-26","08:06","DBS4A","URBAN","Planned","",6,237,1.4114942483098298E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-26","07:36","CPS12B","RURAL","Asset failure","LV",1,157.11666666670001,4.0274139277526291E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-26","07:30","DRD16A","URBAN","Planned","",1,105,1.0422425884144314E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","10:30","ZMR4A","URBAN","Planned","",1,5,4.9630599448306254E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","07:18","KSN2A","URBAN","Asset failure","LV",1,88.3,8.7647638625708844E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","07:00","LYT1","URBAN","Planned","",7,374,2.5986581871133155E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-26","08:22","ZMR4A","URBAN","Planned","",1,44,4.3674927514509508E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-26","11:42","EMD2","RURAL","Asset failure","HV",459,155.03091397851287,0.18896692795515227,1.1765670899573978E-3,"NO"]
[null,"2015-07-26","18:50","AHD7","URBAN","Asset failure","LV",89,99.85,8.8209953317458147E-3,8.8342467017985132E-5,"NO"]
[null,"2015-07-27","12:05","TGP2A","URBAN","Planned","",12,100,1.1911343867593502E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-27","15:21","NMC2A","RURAL","Overloads","",1,143.96666666670001,3.6903364281243111E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","09:00","PGN1B","RURAL","Unknown","Unknown",361,50.883333333300001,4.7085454486389497E-2,9.253610446070163E-4,"NO"]
[null,"2015-07-27","09:00","SMF1B","RURAL","Planned","",13,295,9.8303590195786914E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-27","09:15","MTB3A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,158.96666666670001,4.0748354771299967E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","09:42","BLN2B","URBAN","Overloads","",1,93.383333333300001,9.2693416236253569E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","10:42","RBY12","URBAN","Asset failure","LV",1,75.3,7.4743682769149214E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","11:56","NMC3A","RURAL","Asset failure","LV",1,82.683333333299998,2.1194442023515962E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","08:56","TGW4","RURAL","Planned","",45,183,2.1108997790412132E-2,1.1534971470170564E-4,"NO"]
[null,"2015-07-27","15:13","SPD29A","URBAN","Asset failure","LV",1,26.333333333300001,2.6138782376074875E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","22:05","CPC2B","URBAN","Asset failure","LV",1,151.0833333333,1.4996712799959899E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","15:42","KSN1","URBAN","Overloads","",1,35,3.4741419613814376E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","19:59","NRG15A","URBAN","Asset failure","LV",1,104.0166666667,1.0324819038565955E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","20:11","KSN1","URBAN","Asset failure","LV",1,141.3333333333,1.4028916110717926E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","22:19","WMD2A","URBAN","Asset failure","LV",1,77.533333333300007,7.6960516211140492E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","00:35","LDR10B","URBAN","Planned","",2,28,5.5586271382103007E-5,1.9852239779322501E-6,"NO"]
[null,"2015-07-27","10:58","FDS3","RURAL","Unknown","Unknown",1,389.55,9.9854403026776515E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","12:08","BBH16A","URBAN","Asset failure","LV",1,69.349999999999994,6.8837641434800774E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","06:01","BRD3B","RURAL","Asset failure","LV",1,133.1,3.4117882281771157E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","22:32","HDN1","RURAL","Overloads","",1,89.666666666699996,2.2984498707237297E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","02:40","MMC31A","URBAN","Planned","",4,33,1.3102478254352852E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-27","03:09","GBP6","URBAN","Animal","Animal impact",49,80.566666666700002,3.9186005229757907E-3,4.8637987459340128E-5,"NO"]
[null,"2015-07-27","08:45","GNA4A","URBAN","Planned","",1,196,1.9455194983736051E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","06:00","WNM5","URBAN","Animal","Animal impact",34,63,2.12617488036544E-3,3.3748807624848254E-5,"NO"]
[null,"2015-07-27","04:30","NBR12A","RURAL","Asset failure","LV",1,115.75,2.9670509948272059E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","06:15","NSD30B","URBAN","Planned","",1,183,1.8164799398080091E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","06:27","BTA13A","URBAN","Overloads","",1,74.483333333299996,7.3933049644793795E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","07:46","NIP6A","URBAN","Asset failure","LV",1,72.016666666700004,7.1484606738743539E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-27","08:00","TWG21","URBAN","Planned","",13,248,3.2001810524267876E-3,1.2903955856559627E-5,"NO"]
[null,"2015-07-27","08:14","TRP5","RURAL","Planned","",1,168,4.3063893488636771E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-27","08:18","HDA4A","URBAN","Planned","",8,337,2.6760819222526734E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-27","08:18","WRD20A","URBAN","Planned","",6,207,1.2328240902959274E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-27","08:19","IPL3","RURAL","Planned","",4,363,3.7219507943750353E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-27","08:34","AMR1","RURAL","Planned","",4,256.66666666666669,2.647916784152487E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-27","08:35","CHL5","URBAN","Planned","",50,313,1.5534377627319858E-2,4.9630599448306258E-5,"NO"]
[null,"2015-07-27","05:46","GCL3","URBAN","Planned","",2,12,2.3822687735187003E-5,1.9852239779322501E-6,"NO"]
[null,"2015-07-27","15:31","IBL2","RURAL","Asset failure","HV",27,47,3.2528619545880992E-3,6.920982882102339E-5,"NO"]
[null,"2015-07-27","22:56","PWC5","RURAL","Asset failure","LV",37,164,1.5554268195776662E-2,9.4843098754735753E-5,"NO"]
[null,"2015-07-28","09:42","DBY7A","URBAN","Asset failure","LV",1,47.65,4.7297961274235861E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","09:44","BVL2A","URBAN","Planned","",4,261,1.0362869164806346E-3,3.9704479558645002E-6,"NO"]
[null,"2015-07-28","09:56","RBK4A","URBAN","Asset failure","LV",1,60.766666666699997,6.0317721862874623E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","10:00","KWH3","RURAL","Planned","",2,160,8.2026463787879559E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-28","10:05","SMF5A","RURAL","Planned","",19,146,7.1106690796118093E-3,4.8703212874053492E-5,"NO"]
[null,"2015-07-28","10:18","ESK5A","RURAL","Planned","",2,260,1.3329300365530429E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-28","10:18","RWD1","RURAL","Planned","",2,180,9.227977176136451E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-28","10:29","CMY4","RURAL","Planned","",4,206,2.112181442537899E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-28","10:30","GLY11A","URBAN","Planned","",1,256,2.5410866917532801E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","10:44","MDR6A","URBAN","Asset failure","LV",1,32,3.1763583646916001E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","12:26","ACR5","RURAL","Asset failure","LV",1,51.3,1.3149867475994442E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","14:10","SMF5A","RURAL","Planned","",17,88,3.8347371820833696E-3,4.3576558887311021E-5,"NO"]
[null,"2015-07-28","08:58","LDR8","URBAN","Third party","Dig-in",834,104.83333333330003,8.6785058807269694E-2,8.2783839879774842E-4,"NO"]
[null,"2015-07-28","14:18","GNA4A","URBAN","Planned","",4,41,1.6278836619044453E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-28","13:14","COR26A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",339,114.44999999999996,9.9453370518663611E-2,8.6896785075284881E-4,"NO"]
[null,"2015-07-28","09:31","NSW22B","URBAN","Planned","",24,309,7.3612105101727842E-3,2.3822687735187003E-5,"NO"]
[null,"2015-07-28","09:28","MTG16A","URBAN","Planned","",27,157,4.2076822212274044E-3,2.6800523702085378E-5,"NO"]
[null,"2015-07-28","09:10","BRD3B","RURAL","Planned","",16,132.5,4.66525512793565E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-28","09:05","SMF5B","RURAL","Planned","",1,205,5.2548203364110343E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","09:03","TWG17","URBAN","Planned","",29,192,5.5268635545633847E-3,2.878574768001763E-5,"NO"]
[null,"2015-07-28","09:00","GYM7A","RURAL","Planned","",11,390,1.0996672801562603E-2,2.8196596927083601E-5,"NO"]
[null,"2015-07-28","08:58","HWL6A","URBAN","Third party","Dig-in",703,104.83333333330003,7.315335292747073E-2,6.9780622824318589E-4,"NO"]
[null,"2015-07-28","08:58","HWL2A","URBAN","Third party","Dig-in",687,116.81428571425718,8.3309494102046966E-2,6.8192443641972792E-4,"NO"]
[null,"2015-07-28","08:58","BVL2A","URBAN","Planned","",6,295,1.7569232204700414E-3,5.9556719337967507E-6,"NO"]
[null,"2015-07-28","08:54","DRD13A","URBAN","Planned","",22,291,6.354701953361133E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-28","08:53","UMG3A","URBAN","Planned","",18,304,5.4315728036226371E-3,1.7867015801390253E-5,"NO"]
[null,"2015-07-28","08:53","UMG1A","URBAN","Planned","",1,304,3.0175404464570206E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","15:49","GTN5B","RURAL","Animal","Animal nesting/burrowing, etc and other",388,60.919892473151648,7.8913217710230243E-2,9.9457087342803992E-4,"NO"]
[null,"2015-07-28","08:36","JBB1B","RURAL","Planned","",21,73,3.9295802808381056E-3,5.3829866860795964E-5,"NO"]
[null,"2015-07-28","09:03","KWA12A","URBAN","Planned","",97,205,1.9738089400591397E-2,9.628336292971414E-5,"NO"]
[null,"2015-07-28","09:28","MTG8A","URBAN","Planned","",12,157,1.8700809872121797E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-28","05:35","BHD42A","URBAN","Planned","",1,13,1.2903955856559627E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","08:05","CRB24B","URBAN","Planned","",85,278,2.3455421299269537E-2,8.4372019062120641E-5,"NO"]
[null,"2015-07-28","08:12","OXL8B","URBAN","Planned","",25,327,8.1146030097980736E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-28","08:13","GYGGYS6","RURAL","Planned","",4,302,3.0964990079924534E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-28","08:15","BIS16A","URBAN","Planned","",24,202,4.8121829225077749E-3,2.3822687735187006E-5,"NO"]
[null,"2015-07-28","08:15","RLA8A","URBAN","Planned","",46,457,1.7197995320827084E-2,4.5660151492441753E-5,"NO"]
[null,"2015-07-28","08:20","DRD15B","URBAN","Planned","",10,97,9.6283362929714138E-4,9.9261198896612508E-6,"NO"]
[null,"2015-07-28","08:23","GYM5B","RURAL","Planned","",11,198,5.5829261915625525E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-28","08:23","YDA3A","RURAL","Planned","",5,230,2.9478260423769216E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-28","08:24","HWL6A","URBAN","Planned","",17,414,6.9860031783435883E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-28","08:28","CPR5","URBAN","Planned","",11,357,3.8979872806699733E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-28","08:30","KWA12A","URBAN","Planned","",177,318,5.5870158410947314E-2,1.7569232204700416E-4,"NO"]
[null,"2015-07-28","08:34","MTB13A","RURAL","Planned","",24,301,1.8517474200113813E-2,6.1519847840909667E-5,"NO"]
[null,"2015-07-28","08:40","GNA4A","URBAN","Planned","",17,282,4.7585818751036037E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-28","18:29","MTB16A","RURAL","Asset failure","LV",1,82.933333333299998,2.1258525198350242E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","16:23","TGW3","RURAL","Unknown","Unknown",1,165.4333333333,4.2405972893662944E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","16:53","KSN15","RURAL","Asset failure","LV",1,139.6666666667,3.5801133674093476E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","17:45","MAI17","URBAN","Asset failure","LV",1,68.516666666700004,6.8010464777362099E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","18:01","BBH12B","URBAN","Asset failure","LV",1,59.833333333299997,5.9391284006440064E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","18:08","KSN5","RURAL","Overloads","",1,108.5833333333,2.7833458936347467E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","08:40","BDT2","RURAL","Planned","",3,155,1.191947051917625E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-28","18:24","GYM4","RURAL","Asset failure","LV",1,86.3,2.2121511952793771E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","08:47","LLY1","RURAL","Planned","",4,303,3.1067523159659387E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-28","18:44","WNM2A","URBAN","Unknown","Unknown",2086,52.093209876548151,0.15563451232477679,2.0705886089833372E-3,"NO"]
[null,"2015-07-28","18:59","SPO32A","URBAN","Asset failure","LV",1,174.15,1.7286337787845069E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","20:17","HWL1A","URBAN","Asset failure","LV",1,221.76666666669999,2.2012825208642077E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","22:56","KBR2A","RURAL","Asset failure","LV",1,98.683333333299998,2.5295765212909942E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","08:44","CLD11","RURAL","Planned","",1,216,5.5367863056818701E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-28","16:11","NRG15A","URBAN","Weather","",1,118.1,1.1722747589689937E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","18:20","SBH11","URBAN","Asset failure","LV",1,186.13333333329999,1.8475817821286166E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-28","09:40","BVLNCM7","URBAN","Planned","",3,159,4.7347591873684171E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-28","08:46","COR23A","RURAL","Asset failure","HV",429,107.01934523809015,0.14410417702676728,1.0996672801562601E-3,"NO"]
[null,"2015-07-28","12:30","CLD25A","URBAN","Asset failure","LV",13,127,1.6388023937830725E-3,1.2903955856559627E-5,"NO"]
[null,"2015-07-28","02:48","RLA8A","URBAN","Asset failure","Distribution substation",79,77,6.0380587288809389E-3,7.8416347128323891E-5,"NO"]
[null,"2015-07-28","12:30","CLD22A","URBAN","Asset failure","LV",120,140,1.6675881414630903E-2,1.1911343867593502E-4,"NO"]
[null,"2015-07-29","03:46","BPN29A","URBAN","Overloads","",1,101.7,1.0094863927785493E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","08:06","BKD15A","URBAN","Planned","",7,170,1.1812082668696889E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-29","08:05","GBG26","URBAN","Planned","",1,43526,4.3204429431739563E-2,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","08:03","KBR1A","RURAL","Planned","",4,447,4.5832286641477706E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-29","08:03","CRY2A","RURAL","Planned","",2,71,3.6399243305871556E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-29","07:00","RLA8A","URBAN","Planned","",1,624,6.1938988111486209E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","19:39","HWL10A","URBAN","Asset failure","LV",1,2.2999999999999998,2.2830075746220878E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","04:03","AGE7B","URBAN","Animal","Animal impact",81,82,6.5929288307130032E-3,8.0401571106256136E-5,"NO"]
[null,"2015-07-29","08:15","RCF10A","URBAN","Planned","",60,370,2.2035986155047978E-2,5.9556719337967505E-5,"NO"]
[null,"2015-07-29","08:49","LWD1","RURAL","Planned","",1,179,4.5883553181345129E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","22:15","BPN35A","URBAN","Asset failure","LV",1,147.13333333329999,1.4604631064318277E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","22:02","WRG15A","URBAN","Overloads","",1,100.95,1.0020418028613034E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","20:54","CRB25A","RURAL","Third party","Vehicle impact",49,50.383333333300008,6.3282989591141653E-3,1.2560302267519057E-4,"NO"]
[null,"2015-07-29","19:39","PPE3A","RURAL","Asset failure","LV",1,3,7.6899809801137083E-6,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","05:00","BKD3A","URBAN","Asset failure","LV",1,85.316666666700002,8.4686346191992996E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","08:34","GNA4A","URBAN","Planned","",5,308,1.5286224630078327E-3,4.9630599448306254E-6,"NO"]
[null,"2015-07-29","08:45","RLA8A","URBAN","Planned","",21,203,4.2315049089625915E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-29","08:44","LRE6A","RURAL","Planned","",3,118,9.0741775565341765E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-29","08:40","PWC4","RURAL","Planned","",110,359.79404761907847,0.10148638787923139,2.8196596927083597E-4,"NO"]
[null,"2015-07-29","08:37","GTN5B","RURAL","Planned","",2,111,5.6905859252841446E-4,5.1266539867424728E-6,"NO"]
[null,"2015-07-29","08:36","IPL4A","RURAL","Planned","",1,335,8.5871454277936421E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","08:10","JBB16A","RURAL","Planned","",6,456,7.0132626538637029E-3,1.5379961960227417E-5,"NO"]
[null,"2015-07-29","08:34","RBK9A","URBAN","Planned","",7,308,2.1400714482109656E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-29","08:14","AMR2","RURAL","Planned","",92,321,7.5700172768239343E-2,2.3582608339015371E-4,"NO"]
[null,"2015-07-29","08:33","WMD4A","RURAL","Planned","",3,312,2.3992740657954774E-3,7.6899809801137083E-6,"NO"]
[null,"2015-07-29","08:29","WRD15B","URBAN","Asset failure","LV",1,109.0166666667,1.0821125033049017E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","08:20","RCF2A","URBAN","Planned","",39,342,1.3239458708830178E-2,3.8711867569678881E-5,"NO"]
[null,"2015-07-29","08:20","ALY5","URBAN","Planned","",31,255,7.8465977727772192E-3,3.0770971657949879E-5,"NO"]
[null,"2015-07-29","08:15","RCF2A","URBAN","Planned","",2,370,7.3453287183493257E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-29","08:22","CLD17A","URBAN","Planned","",16,212,3.3669398665730965E-3,1.5881791823458001E-5,"NO"]
[null,"2015-07-29","08:35","TGW1","RURAL","Planned","",13,346,1.1529844816183823E-2,3.3323250913826079E-5,"NO"]
[null,"2015-07-29","09:20","MLS11A","URBAN","Asset failure","LV",1,117.4166666667,1.1654919103780561E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","10:05","MAI17","URBAN","Planned","",17,407,6.8678823516566201E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-29","09:59","NDH5A","URBAN","Planned","",22,286,6.2455146345748594E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-29","09:59","NDH12","URBAN","Planned","",21,286,5.9616276057305479E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-29","08:52","LRE4A","RURAL","Planned","",9,82,1.8917353211079725E-3,2.3069942940341127E-5,"NO"]
[null,"2015-07-29","09:57","NBR15A","RURAL","Planned","",20,234,1.1996370328977386E-2,5.1266539867424725E-5,"NO"]
[null,"2015-07-29","10:26","GNA4A","URBAN","Planned","",11,244,2.6641705783850798E-3,1.0918731878627375E-5,"NO"]
[null,"2015-07-29","09:26","IBL2","RURAL","Planned","",13,226.96666666669998,7.5632671824091696E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-29","09:36","LBH1B","RURAL","Planned","",11,57,1.6072060248437652E-3,2.8196596927083601E-5,"NO"]
[null,"2015-07-29","09:14","RLB13B","RURAL","Planned","",6,351,5.3983666480398231E-3,1.537996196022742E-5,"NO"]
[null,"2015-07-29","09:11","AGT37A","URBAN","Planned","",22,311,6.7914512285062283E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-29","09:00","NIP5A","URBAN","Planned","",44,325,1.419435144221559E-2,4.3674927514509508E-5,"NO"]
[null,"2015-07-29","08:57","NSW17","URBAN","Planned","",21,280,5.8365584951208154E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-29","19:34","MLY3","RURAL","Third party","Other",38,129.46666666670001,1.261088525352483E-2,9.7406425748106985E-5,"NO"]
[null,"2015-07-29","08:30","HPE3A","URBAN","Planned","",9,309,2.7604539413147939E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-29","09:35","SBY14A","URBAN","Planned","",1,287,2.8487964083327792E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","17:01","BVL13A","URBAN","Asset failure","LV",1,30.7,3.047318806126004E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","09:29","SFD3","URBAN","Asset failure","LV",1,125.6333333333,1.247051528804111E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","17:22","KWA12A","URBAN","Asset failure","LV",1,292.86666666669998,2.9070296450191225E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","10:56","SMF1B","RURAL","Planned","",26,233,1.552863492584295E-2,6.6646501827652145E-5,"NO"]
[null,"2015-07-29","16:40","WRG12A","URBAN","Asset failure","LV",1,95.35,9.4645553147920032E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","16:31","RCF2A","URBAN","Asset failure","LV",1,86.633333333300001,8.5993285310732222E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","16:09","CVL3A","RURAL","Asset failure","LV",1,184.65,4.7331832932599884E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","14:23","BVL13A","URBAN","Planned","",58,86,4.9511486009630318E-3,5.757149536003526E-5,"NO"]
[null,"2015-07-29","13:56","MAI14","URBAN","Asset failure","LV",1,80.066666666700002,7.9475133249920843E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-29","12:32","BHD41A","RURAL","Third party","Unauthorised access",19,121.9,5.9369216493471207E-3,4.8703212874053492E-5,"NO"]
[null,"2015-07-29","12:29","LRE4A","RURAL","Planned","",20,74,3.7937239501894299E-3,5.1266539867424725E-5,"NO"]
[null,"2015-07-29","11:58","LRE8A","RURAL","Planned","",1,138,3.5373912508523063E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","11:48","TWT12A","RURAL","Asset failure","LV",1,250.26666666669999,6.4151530220779357E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","11:34","QPT21","URBAN","Planned","",7,77,5.3501786205274141E-4,6.9482839227628759E-6,"NO"]
[null,"2015-07-29","11:12","SMF1B","RURAL","Planned","",29,221,1.6428362700516255E-2,7.4336482807765855E-5,"NO"]
[null,"2015-07-29","17:48","SGT3","RURAL","Asset failure","LV",1,184.9166666667,4.7400188319098323E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-29","16:10","COR23A","RURAL","Asset failure","HV",14,36,1.291916804659103E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-29","20:51","GYM4","RURAL","Asset failure","LV",106,109,2.9616680081411266E-2,2.7171266129735104E-4,"NO"]
[null,"2015-07-29","20:03","PBH6","URBAN","Asset failure","LV",107,142,8.0143491989124946E-3,1.0620948281937538E-4,"NO"]
[null,"2015-07-30","17:54","AHD16","URBAN","Asset failure","LV",1,109.85,1.0903842698792884E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","11:47","ESMT1","CBD","Asset failure","LV",1,230.6833333333,5.9013387908237402E-2,2.5581990278843696E-4,"NO"]
[null,"2015-07-30","11:48","AQETR1H","CBD","Asset failure","LV",1,120.8333333333,3.0911571586927603E-2,2.5581990278843696E-4,"NO"]
[null,"2015-07-30","12:44","NIP4A","RURAL","Asset failure","LV",1,149.80000000000001,3.8398638360701123E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","14:45","CHL7","URBAN","Third party","Vehicle impact",143,23,3.2647008317095855E-3,1.4194351442215589E-4,"NO"]
[null,"2015-07-30","16:02","TBV3","RURAL","Overloads","",1,79.849999999999994,2.0468166042069322E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","16:41","MTG4B","URBAN","Asset failure","LV",1,77.55,7.6977059744323006E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","16:46","NIP6A","URBAN","Asset failure","LV",1,188.13333333329999,1.8674340219079392E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","16:51","CPS2B","URBAN","Asset failure","LV",1,99.483333333299996,9.8748349368946923E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","17:24","CMV13","URBAN","Asset failure","LV",1,82.033333333300007,8.1427270161488048E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","11:47","DBY6","URBAN","Asset failure","LV",1,76.233333333299996,7.5670120625484508E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","18:22","NVL24A","URBAN","Unknown","Unknown",4,112.3833333333,4.4621217610643979E-4,3.9704479558645002E-6,"NO"]
[null,"2015-07-30","18:46","CMA10A","RURAL","Asset failure","LV",1,167.48333333330001,4.2931454927304049E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","13:49","ACR4","URBAN","Planned","",15,86,1.2804694657663016E-3,1.4889179834491878E-5,"NO"]
[null,"2015-07-30","17:22","WNM5","URBAN","Overloads","",1,148.15,1.4705546616533146E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","08:06","KRN18","URBAN","Planned","",5,64,3.1763583646916003E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-30","08:39","RCF10A","URBAN","Planned","",10,241,2.3921948934083614E-3,9.9261198896612508E-6,"NO"]
[null,"2015-07-30","08:37","NDH5A","URBAN","Planned","",22,346,7.5557624600101443E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-30","08:37","NDH12","URBAN","Planned","",21,346,7.2123187118278654E-3,2.0844851768288628E-5,"NO"]
[null,"2015-07-30","11:23","LLY2B","URBAN","Asset failure","LV",1,115.8166666667,1.1496101185545981E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","08:30","KRN18","URBAN","Planned","",39,120,4.6454241083614661E-3,3.8711867569678881E-5,"NO"]
[null,"2015-07-30","15:59","GYS3A","RURAL","Asset failure","LV",1,212.95,5.4586048323840481E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","08:19","CMY4","RURAL","Planned","",1,61,1.5636294659564543E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","08:17","TWT6B","RURAL","Planned","",7,253,4.53965210526046E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-30","08:39","RCF2A","URBAN","Planned","",33,241,7.8942431482475935E-3,3.2756195635882131E-5,"NO"]
[null,"2015-07-30","08:06","LTA12A","URBAN","Planned","",3,295,8.784616102350207E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-30","08:35","RCF10A","URBAN","Planned","",28,350,9.7275974918680265E-3,2.7793135691051504E-5,"NO"]
[null,"2015-07-30","08:03","NMK4A","URBAN","Planned","",11,257,2.8061140928072356E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-30","08:00","THL1","RURAL","Planned","",24,417,2.5653776549659335E-2,6.1519847840909667E-5,"NO"]
[null,"2015-07-30","08:00","KWH3","RURAL","Planned","",38,77,7.5002947826042369E-3,9.7406425748106971E-5,"NO"]
[null,"2015-07-30","08:00","BWH7A","RURAL","Planned","",86,292.87444444447323,6.4489163107920938E-2,2.2044612142992632E-4,"NO"]
[null,"2015-07-30","07:54","KWA12A","URBAN","Overloads","",1,133.63333333329999,1.3264604879214008E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","07:48","BDT4","RURAL","Asset failure","LV",1,132.9333333333,3.4075160165206425E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","07:18","ZMR4A","URBAN","Overloads","",1,141.19999999999999,1.4015681284201684E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","05:30","ARL6B","URBAN","Planned","",2,103,2.0447806972702178E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-30","05:17","BIS3","RURAL","Overloads","",1,177.26666666669999,4.5439243169169327E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","08:14","CDRSPD9","URBAN","Planned","",34,460,1.5524451507430197E-2,3.3748807624848254E-5,"NO"]
[null,"2015-07-30","09:30","TRP1","RURAL","Planned","",2,313,1.6046426978503939E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-30","10:38","FGBSGT23","URBAN","Planned","",7,267,1.8551918073776879E-3,6.9482839227628759E-6,"NO"]
[null,"2015-07-30","10:23","MFN2A","URBAN","Animal","Animal nesting/burrowing, etc and other",569,76.544444444449994,4.5367115889766871E-2,5.6479622172172519E-4,"NO"]
[null,"2015-07-30","08:28","RCN8A","URBAN","Unknown","Unknown",153,84.133333333300001,1.2777298566762485E-2,1.5186963431181713E-4,"NO"]
[null,"2015-07-30","08:40","CPR5","URBAN","Planned","",15,245,3.6478490594505099E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-30","09:57","UMG5A","URBAN","Planned","",9,212,1.8939036749473668E-3,8.9335079006951264E-6,"NO"]
[null,"2015-07-30","09:49","BDT1","RURAL","Planned","",6,355,5.4598864958807338E-3,1.537996196022742E-5,"NO"]
[null,"2015-07-30","09:40","MTG16A","URBAN","Planned","",3,136,4.0498569149817904E-4,2.9778359668983753E-6,"NO"]
[null,"2015-07-30","10:20","SMF1B","RURAL","Planned","",13,171,5.6982759062642581E-3,3.3323250913826072E-5,"NO"]
[null,"2015-07-30","09:21","MLB3A","RURAL","Planned","",114,223,6.5164898825483569E-2,2.9221927724432095E-4,"NO"]
[null,"2015-07-30","08:50","NSD30B","URBAN","Planned","",35,318,1.1047771437192972E-2,3.4741419613814383E-5,"NO"]
[null,"2015-07-30","08:43","AMR2","RURAL","Planned","",10,399,1.0227674703551234E-2,2.5633269933712362E-5,"NO"]
[null,"2015-07-30","08:50","KVG2A","URBAN","Planned","",1,308,3.0572449260156653E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-30","09:40","MTG8A","URBAN","Planned","",15,136,2.0249284574908951E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-30","08:50","MLT8B","URBAN","Planned","",12,308,3.6686939112187985E-3,1.1911343867593501E-5,"NO"]
[null,"2015-07-30","09:10","IPL1","RURAL","Asset failure","LV",1,236.61666666670001,6.0652588874827616E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-30","11:22","JBB3A","RURAL","Planned","",22,48,2.7068733050000255E-3,5.6393193854167202E-5,"NO"]
[null,"2015-07-30","08:56","GNA4A","URBAN","Planned","",8,290,2.3028598144014104E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-30","08:58","TRP1","RURAL","Planned","",2,297,1.5226162340625145E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-30","08:59","GGR5","RURAL","Planned","",18,354,1.633351960176152E-2,4.6139885880682253E-5,"NO"]
[null,"2015-07-30","09:02","AGT37A","URBAN","Planned","",15,317,4.719870007533925E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-31","16:24","IDY6A","URBAN","Asset failure","LV",1,71.483333333299996,7.095521367789542E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","12:23","BDB35A","URBAN","Planned","",17,127,2.1430492841778641E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-31","13:54","RCF12A","URBAN","Asset failure","LV",1,108.6166666667,1.0781420553490371E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","14:21","LTN7","URBAN","Asset failure","LV",1,179.1,1.7777680722383301E-4,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","15:00","RLA7A","URBAN","Overloads","",1,68.433333333299998,6.7927747111548736E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","12:17","ALY8","URBAN","Asset failure","LV",1,99.733333333299996,9.8996502366188456E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","16:53","AHL14A","URBAN","Asset failure","LV",1,6.9833333333000001,6.9317403895803539E-6,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","17:39","HWD5A","RURAL","Asset failure","LV",1,156.71666666670001,4.0171606197791438E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","18:36","NBR11A","RURAL","Overloads","",1,56.75,1.4546880687381768E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","20:35","TRP1","RURAL","Animal","Animal impact",4,92.716666666699993,9.5065253760862089E-4,1.0253307973484946E-5,"NO"]
[null,"2015-07-31","21:20","BTN3","RURAL","Third party","Vehicle impact",59,137,1.3706109433556001E-2,1.5123629260890294E-4,"NO"]
[null,"2015-07-31","22:46","BTN2","RURAL","Asset failure","LV",1,152.9333333333,3.9201814151948894E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","11:59","HPE3A","URBAN","Asset failure","LV",1,47.333333333299997,4.69836341443635E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","09:35","KBR2A","RURAL","Planned","",4,245,2.5120604535038117E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-31","09:10","IPL3","RURAL","Planned","",14,367,1.3170374091941411E-2,3.5886577907197318E-5,"NO"]
[null,"2015-07-31","08:15","KSN5","RURAL","Planned","",8,265,5.4342532259470215E-3,2.0506615946969891E-5,"NO"]
[null,"2015-07-31","08:51","ACR12A","URBAN","Planned","",3,350,1.0422425884144314E-3,2.9778359668983753E-6,"NO"]
[null,"2015-07-31","11:09","GNA7A","URBAN","Planned","",2,96,1.9058150188149602E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-31","08:40","LTN9","URBAN","Planned","",14,55,7.6431123150391635E-4,1.3896567845525752E-5,"NO"]
[null,"2015-07-31","08:39","RBY15","URBAN","Planned","",15,83,1.2358019262628257E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-31","08:33","UMG3A","URBAN","Planned","",17,315,5.3154372009136001E-3,1.6874403812424127E-5,"NO"]
[null,"2015-07-31","08:33","BNH5A","RURAL","Planned","",7,344,6.1724914000379372E-3,1.7943288953598656E-5,"NO"]
[null,"2015-07-31","08:32","MRE1","URBAN","Asset failure","LV",1,67,6.6505003260730378E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","08:25","KWA6A","URBAN","Planned","",3,50,1.4889179834491877E-4,2.9778359668983749E-6,"NO"]
[null,"2015-07-31","08:25","KWA2A","URBAN","Planned","",5,50,2.4815299724153129E-4,4.9630599448306254E-6,"NO"]
[null,"2015-07-31","08:22","PPE6A","RURAL","Third party","Dig-in",15,423,1.6264309772940494E-2,3.8449904900568543E-5,"NO"]
[null,"2015-07-31","08:21","GGR2","RURAL","Planned","",3,90,6.9209828821023382E-4,7.6899809801137083E-6,"NO"]
[null,"2015-07-31","08:54","CMY4","RURAL","Planned","",17,37,1.6123326788305076E-3,4.3576558887311021E-5,"NO"]
[null,"2015-07-31","08:16","CDRSPD9","URBAN","Planned","",8,266,2.1122783125199144E-3,7.9408959117290003E-6,"NO"]
[null,"2015-07-31","08:40","RPN3A","URBAN","Planned","",32,143,4.5421924615089886E-3,3.1763583646916001E-5,"NO"]
[null,"2015-07-31","08:10","MLT21B","URBAN","Planned","",15,325,4.8389834462098606E-3,1.4889179834491876E-5,"NO"]
[null,"2015-07-31","08:10","KMR24A","URBAN","Planned","",11,175,1.9107780787597909E-3,1.0918731878627377E-5,"NO"]
[null,"2015-07-31","08:09","EMD3","RURAL","Planned","",5,120,1.5379961960227419E-3,1.2816634966856181E-5,"NO"]
[null,"2015-07-31","08:07","BWH7A","RURAL","Planned","",24,309,1.9009632982841088E-2,6.1519847840909667E-5,"NO"]
[null,"2015-07-31","08:06","CMY4","RURAL","Planned","",16,153,6.2750244797727863E-3,4.1013231893939782E-5,"NO"]
[null,"2015-07-31","08:03","RST9A","URBAN","Planned","",2,377,7.4842943968045838E-4,1.9852239779322501E-6,"NO"]
[null,"2015-07-31","08:01","LGV5B","RURAL","Planned","",25,257,1.6469375932410196E-2,6.4083174834280912E-5,"NO"]
[null,"2015-07-31","08:01","CPR5","URBAN","Planned","",19,174,3.2815752355220096E-3,1.8859627790356379E-5,"NO"]
[null,"2015-07-31","08:00","MLB3A","RURAL","Planned","",131,223,7.4882471457353925E-2,3.3579583613163198E-4,"NO"]
[null,"2015-07-31","07:46","JBB16A","RURAL","Planned","",1,354,9.0741775565341765E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","07:08","JBB13A","RURAL","Other","Other System Failures",469,2.9166666667000012,3.5064177163891437E-3,1.2022003598911098E-3,"NO"]
[null,"2015-07-31","06:08","BPN36A","URBAN","Asset failure","LV",1,87.966666666699993,8.731676796275322E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","08:21","CRB22A","URBAN","Overloads","",1,19.0333333333,1.8892714856622161E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","08:57","TRP5","RURAL","Planned","",1,140,3.588657790719731E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","11:03","CCY8A","RURAL","Overloads","",1,71.516666666700004,1.8332060214268505E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","11:02","BLH12A","RURAL","Planned","",4,118,1.2098903408712235E-3,1.0253307973484946E-5,"NO"]
[null,"2015-07-31","10:49","CMY4","RURAL","Planned","",42,203,2.1854925945483161E-2,1.0765973372159193E-4,"NO"]
[null,"2015-07-31","10:34","MSV2","RURAL","Planned","",1,155,3.9731568397254166E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","10:14","WMD2A","URBAN","Overloads","",1,46.433333333299998,4.6090283354293988E-5,9.9261198896612504E-7,"NO"]
[null,"2015-07-31","10:08","TWT12A","RURAL","Asset failure","LV",1,113.45,2.9080944739796676E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","10:08","SMF5B","RURAL","Planned","",9,250,5.7674857350852819E-3,2.3069942940341127E-5,"NO"]
[null,"2015-07-31","09:56","CHL5","URBAN","Planned","",48,80,1.2874177496890644E-2,4.7645375470374005E-5,"NO"]
[null,"2015-07-31","09:53","GNA4A","URBAN","Planned","",22,241,5.2628287654983954E-3,2.1837463757254754E-5,"NO"]
[null,"2015-07-31","09:41","NMC15A","RURAL","Planned","",14,93,3.33745174536935E-3,3.5886577907197311E-5,"NO"]
[null,"2015-07-31","09:00","SCV7","URBAN","Planned","",91,75,6.7745768246938037E-3,9.0327690995917391E-5,"NO"]
[null,"2015-07-31","09:35","VSL2A","URBAN","Planned","",25,111,2.7544982693809973E-3,2.4815299724153129E-5,"NO"]
[null,"2015-07-31","18:23","BPN35A","URBAN","Asset failure","LV",11,62,6.7696137647489738E-4,1.0918731878627377E-5,"NO"]
[null,"2015-07-31","12:59","GBN4","RURAL","Asset failure","LV",1,300.93333333330003,7.7139053653843201E-4,2.5633269933712364E-6,"NO"]
[null,"2015-07-31","21:00","AMR2","RURAL","Asset failure","HV",2,878,4.5012022003598912E-3,5.1266539867424728E-6,"NO"]
[null,"2015-07-31","06:02","CMV10B","URBAN","Asset failure","LV",77,317.21666666670001,2.4245226115359279E-2,7.6431123150391632E-5,"NO"]
[null,"2015-07-31","14:23","CVL9A","URBAN","Asset failure","HV",63,58,3.6270042076822213E-3,6.2534555304865887E-5,"NO"]
[null,"2015-08-01","11:38","NBR11A","RURAL","Third party","Unauthorised access",170,147,6.405754156434719E-2,4.3576558887311017E-4,"NO"]
[null,"2015-08-01","20:55","UMG5A","URBAN","Planned","",13,274,3.5356839046973378E-3,1.2903955856559627E-5,"NO"]
[null,"2015-08-01","20:10","BNH5A","RURAL","Animal","Animal nesting/burrowing, etc and other",34,200.99803921568827,1.4973418299078226E-2,8.7153117774622029E-5,"NO"]
[null,"2015-08-01","19:31","GBG33A","URBAN","Asset failure","LV",1,80.45,7.9855634512324776E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-01","18:53","LBH1B","RURAL","Asset failure","LV",1,97.95,2.510778790007126E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-01","14:38","SFD7A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",38,191.48333333330001,7.2226087894455568E-3,3.7719255580712758E-5,"NO"]
[null,"2015-08-01","08:42","HPK9","URBAN","Asset failure","LV",1,87.383333333300001,8.6737744302456819E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-01","23:40","BNH5A","RURAL","Asset failure","LV",1,162.23333333330001,4.1585708255784148E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-01","07:34","RST16A","URBAN","Asset failure","LV",1,133.0666666667,1.3208356866512548E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-01","08:23","WMR2","RURAL","Asset failure","LV",1,87.3,2.2377844652130894E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-01","10:49","DRD2A","RURAL","Overloads","",1,37.4666666667,9.6039318018394435E-5,2.5633269933712364E-6,"NO"]
[null,"2015-08-01","20:37","KMR25A","RURAL","Unknown","Unknown",18,127.71666666669999,5.8928324250626732E-3,4.6139885880682253E-5,"NO"]
[null,"2015-08-01","00:36","KRN10","URBAN","Animal","Animal impact",1570,67.033333333300035,0.10446480181338398,1.5584008226768164E-3,"NO"]
[null,"2015-08-01","04:35","NBR12A","RURAL","Overloads","",1,64.116666666699999,1.6435198239173789E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-01","11:21","LTA4A","URBAN","Asset failure","LV",1,116.95,1.1608597210958834E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-01","17:56","BKD3A","URBAN","Asset failure","LV",1,54.3,5.389883100086059E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-01","08:22","DRD5A","URBAN","Asset failure","LV",1,116.6333333333,1.1577164497971597E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-01","06:25","SPC2B","RURAL","Asset failure","HV",440,237.31201550384233,0.2101868323600859,1.127863877083345E-3,"NO"]
[null,"2015-08-01","12:53","AGT23A","URBAN","Asset failure","LV",59,28,1.6397950057720388E-3,5.8564107349001382E-5,"NO"]
[null,"2015-08-02","12:09","LHM3","RURAL","Third party","Vehicle impact",49,24,3.014472544204574E-3,1.2560302267519059E-4,"NO"]
[null,"2015-08-02","13:32","CMD15A","URBAN","Asset failure","LV",1,162.19999999999999,1.6100166461030548E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-02","13:37","MLT8B","URBAN","Asset failure","LV",1,244.5833333333,2.4277634896793169E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-02","15:40","WFD1B","RURAL","Third party","Unauthorised access",310,127.05507246373487,0.11341525726401507,7.9463136794508278E-4,"NO"]
[null,"2015-08-02","20:06","CBT12A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",675,148.19454545456722,0.23328433106566879,1.730245720525585E-3,"NO"]
[null,"2015-08-02","08:06","LGV5B","RURAL","Planned","",11,257,7.2465254102604855E-3,2.8196596927083601E-5,"NO"]
[null,"2015-08-02","11:16","NBR4A","RURAL","Asset failure","LV",1,178.1,4.565285375194172E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-02","18:29","WRG2A","URBAN","Overloads","",1,119.5833333333,1.1869985034716605E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-02","09:25","GTN1B","RURAL","Planned","",8,243,4.9831076751136833E-3,2.0506615946969891E-5,"NO"]
[null,"2015-08-02","09:20","BIS2B","RURAL","Asset failure","LV",1,126.2666666667,3.2366275502976024E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-02","08:35","ZMR5","URBAN","Planned","",6,295,1.7569232204700414E-3,5.9556719337967498E-6,"NO"]
[null,"2015-08-02","08:10","IDY9B","URBAN","Planned","",2,256,5.0821733835065602E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-02","08:00","NDH8","URBAN","Planned","",22,391,8.5384483290866092E-3,2.1837463757254754E-5,"NO"]
[null,"2015-08-02","08:00","NDH6","URBAN","Planned","",39,391,1.5136340219744441E-2,3.8711867569678881E-5,"NO"]
[null,"2015-08-02","07:06","MDR31A","URBAN","Planned","",6,401,2.3882244454524969E-3,5.9556719337967507E-6,"NO"]
[null,"2015-08-02","07:02","MDR31A","URBAN","Planned","",1,429,4.2583054326646771E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-02","08:30","SMR12A","URBAN","Planned","",20,87,1.7271448608010577E-3,1.9852239779322502E-5,"NO"]
[null,"2015-08-03","11:44","TGP9A","URBAN","Planned","",19,109,2.0556994291488452E-3,1.8859627790356379E-5,"NO"]
[null,"2015-08-03","11:42","BPN3","URBAN","Planned","",3,110,3.2756195635882127E-4,2.9778359668983753E-6,"NO"]
[null,"2015-08-03","11:33","GYGGYS6","RURAL","Animal","Animal nesting/burrowing, etc and other",18,79,3.6450509845738985E-3,4.613988588068226E-5,"NO"]
[null,"2015-08-03","11:29","SMF6A","RURAL","Planned","",6,79,1.2150169948579662E-3,1.5379961960227417E-5,"NO"]
[null,"2015-08-03","11:07","BDA12B","URBAN","Asset failure","LV",1,38.616666666699999,3.8331366307274948E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","10:58","KWA1A","URBAN","Overloads","",1,26.45,2.625458710815401E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","10:42","EMP2A","URBAN","Asset failure","LV",1,93.333333333300004,9.264378563680526E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","10:21","SMF1B","RURAL","Planned","",19,79,3.8475538170502257E-3,4.8703212874053492E-5,"NO"]
[null,"2015-08-03","11:55","GBN4","RURAL","Overloads","",1,145.69999999999999,3.7347674293418913E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","09:58","CLD30A","URBAN","Asset failure","LV",1,190.55,1.8914221449749515E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","16:53","PWC4","RURAL","Overloads","",1,177.55,4.5511870767306307E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","10:16","WNM1A","URBAN","Planned","",39,282,1.0916746654649444E-2,3.8711867569678881E-5,"NO"]
[null,"2015-08-03","14:11","TRP2","RURAL","Unknown","Unknown",60,94.599999999999966,1.4549444014375138E-2,1.5379961960227417E-4,"NO"]
[null,"2015-08-03","15:23","MFN13A","RURAL","Asset failure","LV",1,51.633333333300001,1.3235311709098273E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","15:24","WRG5A","URBAN","Asset failure","LV",1,72.733333333299996,7.2195978664103082E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","09:35","IPS2B","RURAL","Planned","",49,405,5.0869224183452189E-2,1.2560302267519059E-4,"NO"]
[null,"2015-08-03","16:26","NSW5A","URBAN","Asset failure","LV",1,196.73333333330001,1.9527986529590261E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","12:48","WFD3A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",31,67,5.3240301652320576E-3,7.9463136794508319E-5,"NO"]
[null,"2015-08-03","19:55","LDR8","URBAN","Asset failure","LV",1,73.5,7.2956981189010192E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","22:05","WMR1","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",31,33,2.6222835142187748E-3,7.9463136794508333E-5,"NO"]
[null,"2015-08-03","22:33","CPB4","URBAN","Asset failure","LV",1,132.36666666670001,1.313887402728492E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","23:22","WMD2A","URBAN","Asset failure","LV",1,139.8166666667,1.3878369959064682E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","23:35","CPS12B","RURAL","Animal","Animal impact",66,59,9.9815953121875946E-3,1.6917958156250159E-4,"NO"]
[null,"2015-08-03","15:56","MFD13A","RURAL","Asset failure","LV",1,12.916666666699999,3.3109640331130578E-5,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","08:25","MTB13A","RURAL","Planned","",5,201,2.5761436283380924E-3,1.2816634966856181E-5,"NO"]
[null,"2015-08-03","07:00","RBA37A","URBAN","Planned","",9,45.5,8.1294921896325647E-4,8.9335079006951264E-6,"NO"]
[null,"2015-08-03","03:05","ACR5","RURAL","Animal","Animal impact",26,74.816666666700002,4.9862691117410632E-3,6.6646501827652145E-5,"NO"]
[null,"2015-08-03","15:01","BVL2A","URBAN","Unknown","Unknown",875,67.76666666669999,5.8857755062432807E-2,8.685354903453594E-4,"NO"]
[null,"2015-08-03","09:19","WMD6A","URBAN","Planned","",2,340,6.7497615249696513E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-03","07:25","BDB27A","RURAL","Asset failure","LV",1,86.7,2.2224045032528622E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","07:43","NMC5A","RURAL","Asset failure","LV",1,89.066666666700002,2.2830699087635024E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","08:02","IPS2B","RURAL","Asset failure","LV",1,16.2833333333,4.1739507875309524E-5,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","08:20","KRN2","URBAN","Planned","",18,460,8.2188272686395166E-3,1.7867015801390253E-5,"NO"]
[null,"2015-08-03","08:27","MFD8A","RURAL","Planned","",14,348,1.2488529111704665E-2,3.5886577907197311E-5,"NO"]
[null,"2015-08-03","08:30","FDS3","RURAL","Planned","",1,71,1.8199621652935778E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-03","08:30","IPL1","RURAL","Planned","",20,348,1.7840755873863808E-2,5.1266539867424731E-5,"NO"]
[null,"2015-08-03","08:30","TCB3","RURAL","Planned","",2,145,7.4336482807765857E-4,5.1266539867424728E-6,"NO"]
[null,"2015-08-03","08:30","YDA5A","RURAL","Planned","",33,376,3.1805761333750307E-2,8.4589790781250797E-5,"NO"]
[null,"2015-08-03","08:43","LHM2","URBAN","Asset failure","LV",1,90.483333333299996,8.9814841468251799E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","09:12","GAP1A","URBAN","Asset failure","LV",1,84.233333333299996,8.3611016537213516E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","08:06","GBP5","URBAN","Planned","",1,139,1.379730664662914E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","09:12","WMD6A","URBAN","Planned","",34,338,1.1407096977198711E-2,3.3748807624848254E-5,"NO"]
[null,"2015-08-03","09:13","CBW6","RURAL","Planned","",8,285,5.8443855448864187E-3,2.0506615946969891E-5,"NO"]
[null,"2015-08-03","09:02","COR22A","RURAL","Planned","",129,210,6.9440528250426806E-2,3.3066918214488941E-4,"NO"]
[null,"2015-08-03","08:53","TRP5","RURAL","Planned","",2,407,2.0865481726041863E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-03","09:02","FDS4","RURAL","Planned","",2,362,1.8558487432007752E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-03","08:43","GBG32A","URBAN","Planned","",11,215,2.3475273539048857E-3,1.0918731878627377E-5,"NO"]
[null,"2015-08-03","08:40","TGP9A","URBAN","Planned","",10,110,1.0918731878627377E-3,9.9261198896612508E-6,"NO"]
[null,"2015-08-03","08:39","ZMR11A","URBAN","Planned","",1,71,7.0475451216594882E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-03","08:36","KRN18","URBAN","Planned","",18,199,3.55553614447666E-3,1.7867015801390253E-5,"NO"]
[null,"2015-08-03","08:31","ACR3","URBAN","Planned","",2,442,8.7746899824605457E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-03","16:50","CBW12","URBAN","Asset failure","HV",3,152,4.5263106696855304E-4,2.9778359668983753E-6,"NO"]
[null,"2015-08-04","12:12","BGY5A","RURAL","Asset failure","LV",1,56.75,1.4546880687381768E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","11:08","BIS1","RURAL","Asset failure","LV",1,195.01666666669999,4.9989148582403272E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","11:36","GYM2A","RURAL","Asset failure","LV",1,241.13333333329999,6.1810358233483199E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","11:28","CMD7A","URBAN","Asset failure","LV",1,105.3833333333,1.0460476010384707E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","12:12","EMD3","RURAL","Planned","",4,56,5.7418524651515698E-4,1.0253307973484946E-5,"NO"]
[null,"2015-08-04","11:56","GTN12A","RURAL","Planned","",1,114,2.9221927724432095E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","10:06","GYM4","RURAL","Planned","",3,335,2.5761436283380924E-3,7.6899809801137083E-6,"NO"]
[null,"2015-08-04","10:01","AGT31A","RURAL","Planned","",17,335,1.4598147227249191E-2,4.3576558887311021E-5,"NO"]
[null,"2015-08-04","09:52","BKD2B","URBAN","Asset failure","LV",1,129.8166666667,1.2885757970098555E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","09:34","IBL2","RURAL","Planned","",40,340,3.4861247109848816E-2,1.0253307973484945E-4,"NO"]
[null,"2015-08-04","09:17","CPR4","URBAN","Planned","",49,167,8.1225439057098017E-3,4.8637987459340128E-5,"NO"]
[null,"2015-08-04","09:19","GBG34A","URBAN","Planned","",1,166,1.6477359016837676E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","12:35","CPK7","URBAN","Planned","",1,145,1.4392873840008815E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","17:57","BDA12B","URBAN","Asset failure","LV",1,33.366666666699999,3.3120153365202795E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","09:17","GBP5","URBAN","Planned","",1,167,1.6576620215734289E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","09:45","HDA10A","URBAN","Planned","",9,239,2.1351083882661351E-3,8.9335079006951264E-6,"NO"]
[null,"2015-08-04","15:27","BRD13A","RURAL","Asset failure","LV",1,123.45,3.1644271733167914E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","08:43","EZRRWD4","RURAL","Planned","",4,407,4.1730963452083726E-3,1.0253307973484946E-5,"NO"]
[null,"2015-08-04","09:10","AGE10","URBAN","Planned","",14,207,2.8765895440238305E-3,1.3896567845525752E-5,"NO"]
[null,"2015-08-04","22:05","PWC4","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",9,392.45,9.0537991069368755E-3,2.3069942940341127E-5,"NO"]
[null,"2015-08-04","18:37","HPK11","RURAL","Asset failure","LV",1,31.516666666700001,8.0787522407835575E-5,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","18:14","MDR30A","URBAN","Overloads","",1,96.05,9.534038154019632E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","16:31","CPK10","URBAN","Asset failure","LV",1,39.166666666700003,3.8877302901206322E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","15:57","SHW3","URBAN","Network business","Network error",2,18,3.5734031602780506E-5,1.9852239779322501E-6,"NO"]
[null,"2015-08-04","15:53","LRE6A","RURAL","Third party","Vehicle impact",2,222,1.1381171850568289E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-04","12:35","GNA5A","RURAL","Planned","",26,145,9.6637427650095604E-3,6.6646501827652145E-5,"NO"]
[null,"2015-08-04","14:45","EMD1","RURAL","Overloads","",1,107.5,2.755576517874079E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","14:24","PBH8A","URBAN","Network business","Network error",0,1.0000000870786607,0,0,"NO"]
[null,"2015-08-04","14:24","MLT3B","URBAN","Asset failure","LV",1,127.2333333333,1.2629333206275691E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","14:20","VSL10A","URBAN","Asset failure","LV",1,99.033333333300007,9.8301673973912181E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","13:28","ZMR4A","URBAN","Asset failure","LV",1,77.016666666700004,7.6447666683574159E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","13:12","BRD3B","RURAL","Planned","",12,80,2.4607939136363868E-3,3.0759923920454833E-5,"NO"]
[null,"2015-08-04","12:39","MLT21B","URBAN","Planned","",16,101,1.6040609741692583E-3,1.5881791823458001E-5,"NO"]
[null,"2015-08-04","15:56","JBB2A","RURAL","Third party","Other",20,289.14999999999998,1.4823720002665861E-2,5.1266539867424725E-5,"NO"]
[null,"2015-08-04","08:08","UPC2","RURAL","Planned","",121,416.76923076923077,0.13077581654781373,3.1016256619791966E-4,"NO"]
[null,"2015-08-04","08:32","BPN34A","URBAN","Planned","",37,297,1.0907813146748749E-2,3.6726643591746628E-5,"NO"]
[null,"2015-08-04","08:32","BPN3","URBAN","Planned","",1,297,2.9480576072293916E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","08:30","RCF2A","URBAN","Planned","",5,213,1.0571317682489232E-3,4.9630599448306254E-6,"NO"]
[null,"2015-08-04","08:30","RCF10A","URBAN","Planned","",43,213,9.0913332069407406E-3,4.2682315525543378E-5,"NO"]
[null,"2015-08-04","08:28","MTG13A","URBAN","Asset failure","LV",1,87.933333333299998,8.7283680896388179E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","08:25","BMT5","RURAL","Planned","",6,194,2.9837126202841191E-3,1.537996196022742E-5,"NO"]
[null,"2015-08-04","08:32","NBR11A","RURAL","Planned","",40,398,4.0808165734470082E-2,1.0253307973484945E-4,"NO"]
[null,"2015-08-04","08:10","EMD1","RURAL","Planned","",12,318,9.7816558067046373E-3,3.0759923920454833E-5,"NO"]
[null,"2015-08-04","08:24","LHM5","RURAL","Planned","",1,66,1.6917958156250159E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","08:07","CMV9A","URBAN","Planned","",40,325,1.2903955856559627E-2,3.9704479558645003E-5,"NO"]
[null,"2015-08-04","08:05","UPC2","RURAL","Planned","",5,371,4.7549715727036434E-3,1.2816634966856181E-5,"NO"]
[null,"2015-08-04","08:05","MFN12A","RURAL","Planned","",14,77,2.7632664988541927E-3,3.5886577907197311E-5,"NO"]
[null,"2015-08-04","08:04","SHW12","URBAN","Planned","",24,182,4.3357291678040345E-3,2.3822687735187003E-5,"NO"]
[null,"2015-08-04","09:08","WSE3A","RURAL","Planned","",1,68,1.7430623554924409E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","08:50","RBY13","URBAN","Asset failure","LV",1,13.233333333299999,1.3135565320618634E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","08:15","NBR11A","RURAL","Planned","",21,375,2.0186200072798487E-2,5.3829866860795964E-5,"NO"]
[null,"2015-08-04","09:04","AHD12A","URBAN","Planned","",1,6,1.1911343867593501E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","08:15","BTN3","RURAL","Planned","",19,363,1.7679266273281421E-2,4.8703212874053499E-5,"NO"]
[null,"2015-08-04","09:05","BDT5","RURAL","Planned","",36,310,2.8606729246022998E-2,9.2279771761364507E-5,"NO"]
[null,"2015-08-04","08:33","SFD8","URBAN","Planned","",23,337,7.6937355264764355E-3,2.283007574622088E-5,"NO"]
[null,"2015-08-04","09:02","WSE5A","RURAL","Planned","",3,267,2.0532249216903605E-3,7.6899809801137083E-6,"NO"]
[null,"2015-08-04","09:02","EZRRWD4","RURAL","Planned","",34,388.52999999999992,3.4065846743805722E-2,8.7153117774622029E-5,"NO"]
[null,"2015-08-04","09:01","BLHSTN16","RURAL","Planned","",2,256,1.312423420606073E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-04","08:58","RPN3A","URBAN","Planned","",1,169,1.6775142613527515E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-04","08:58","FDS4","RURAL","Planned","",3,278,2.1378147124716113E-3,7.6899809801137083E-6,"NO"]
[null,"2015-08-04","08:56","IBL2","RURAL","Planned","",48,402,4.9461957664091373E-2,1.2303969568181936E-4,"NO"]
[null,"2015-08-04","08:54","WRG5A","URBAN","Planned","",22,203,4.433005142722715E-3,2.1837463757254754E-5,"NO"]
[null,"2015-08-04","08:52","LTA3A","RURAL","Planned","",18,298,1.3749685992443313E-2,4.6139885880682253E-5,"NO"]
[null,"2015-08-04","08:43","MRK5A","URBAN","Planned","",15,262,3.9009651166368718E-3,1.4889179834491876E-5,"NO"]
[null,"2015-08-04","08:41","CMD15A","URBAN","Planned","",55,422,2.3038524263903765E-2,5.4593659393136885E-5,"NO"]
[null,"2015-08-04","08:37","KWA2A","URBAN","Planned","",76,455,3.4324522578448605E-2,7.5438511161425516E-5,"NO"]
[null,"2015-08-04","08:34","WRG6A","URBAN","Planned","",25,236,5.8564107349001384E-3,2.4815299724153129E-5,"NO"]
[null,"2015-08-04","09:40","COR25A","RURAL","Asset failure","LV",1,172.98333333330001,4.4341284773658228E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-04","11:30","COR25A","RURAL","Asset failure","Distribution substation",6,50,7.6899809801137095E-4,1.5379961960227417E-5,"NO"]
[null,"2015-08-05","08:29","TRG7A","URBAN","Asset failure","LV",1,105.1166666667,1.0434006357352227E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","08:16","WFD6A","RURAL","Planned","",1,182,4.6652551279356501E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","08:17","HDA3A","URBAN","Planned","",14,276,3.8354527253651074E-3,1.3896567845525752E-5,"NO"]
[null,"2015-08-05","08:17","WFD1B","RURAL","Planned","",10,13,3.3323250913826072E-4,2.5633269933712362E-5,"NO"]
[null,"2015-08-05","08:18","KWA12A","URBAN","Planned","",161,275,4.3947895811475193E-2,1.5981053022354617E-4,"NO"]
[null,"2015-08-05","10:12","TGW4","RURAL","Planned","",2,245,1.2560302267519059E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-05","08:18","PPE5A","RURAL","Planned","",6,467,7.1824422354262035E-3,1.5379961960227417E-5,"NO"]
[null,"2015-08-05","08:18","ZMR5","URBAN","Planned","",22,392,8.5602857928438643E-3,2.1837463757254754E-5,"NO"]
[null,"2015-08-05","08:20","MLS26B","URBAN","Planned","",34,247,8.3359554833375184E-3,3.3748807624848254E-5,"NO"]
[null,"2015-08-05","08:20","TGP9A","URBAN","Planned","",24,313,7.4565012611135326E-3,2.3822687735187003E-5,"NO"]
[null,"2015-08-05","08:34","KRN18","URBAN","Planned","",8,352,2.7951953609286085E-3,7.9408959117290003E-6,"NO"]
[null,"2015-08-05","08:26","WSE3A","RURAL","Asset failure","LV",1,72.416666666699996,1.8562759643671914E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","08:14","LBH5A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",794,42.683333333300048,8.6872604357246294E-2,2.0352816327367622E-3,"NO"]
[null,"2015-08-05","08:30","COR25A","RURAL","Planned","",4,50,5.126653986742473E-4,1.0253307973484946E-5,"NO"]
[null,"2015-08-05","08:30","SMF6A","RURAL","Planned","",10,420,1.0765973372159192E-2,2.5633269933712362E-5,"NO"]
[null,"2015-08-05","08:35","MFN2A","URBAN","Planned","",32,343,1.0894909190892189E-2,3.1763583646916001E-5,"NO"]
[null,"2015-08-05","03:50","PWC4","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",3,615,4.7293383027699311E-3,7.6899809801137083E-6,"NO"]
[null,"2015-08-05","08:23","FDS1","RURAL","Planned","",36,331.34999999999997,3.0576902373128129E-2,9.2279771761364507E-5,"NO"]
[null,"2015-08-05","08:03","RLB13B","RURAL","Planned","",1,438,1.1227372230966015E-3,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","08:35","RLB13B","RURAL","Planned","",1,377,9.6637427650095612E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","07:01","MLY1","RURAL","Overloads","",1,184.1833333333,4.7212211006234011E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","07:33","LGV5B","RURAL","Planned","",8,417,8.551258849886445E-3,2.0506615946969891E-5,"NO"]
[null,"2015-08-05","08:00","GYM5B","RURAL","Planned","",19,200,9.740642574810698E-3,4.8703212874053492E-5,"NO"]
[null,"2015-08-05","08:01","VPT13A","RURAL","Planned","",36,357,3.2943878518807132E-2,9.2279771761364507E-5,"NO"]
[null,"2015-08-05","08:03","BBH16A","URBAN","Planned","",134,409,5.4401092667277461E-2,1.3301000652146078E-4,"NO"]
[null,"2015-08-05","07:20","CVL9A","URBAN","Asset failure","LV",1,127.8,1.268558121898708E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","08:03","MAI7","URBAN","Planned","",2,409,8.1195660697429034E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-05","08:11","YDA3A","RURAL","Planned","",11,380,1.0714706832291768E-2,2.8196596927083601E-5,"NO"]
[null,"2015-08-05","08:04","SHW10A","URBAN","Planned","",18,303,5.4137057878212462E-3,1.7867015801390253E-5,"NO"]
[null,"2015-08-05","08:04","SHW5A","URBAN","Planned","",2,303,6.0152286531347187E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-05","08:06","CDRSPD12","URBAN","Planned","",16,481,7.6391418670832987E-3,1.5881791823458001E-5,"NO"]
[null,"2015-08-05","08:06","CDRSPD9","URBAN","Planned","",65,481,3.1034013835025902E-2,6.4519779282798132E-5,"NO"]
[null,"2015-08-05","08:06","IPL3","RURAL","Planned","",4,383,3.9270169538447343E-3,1.0253307973484946E-5,"NO"]
[null,"2015-08-05","08:10","KRN2","URBAN","Planned","",34,220,7.4247376774666156E-3,3.3748807624848254E-5,"NO"]
[null,"2015-08-05","08:11","WFD6A","RURAL","Planned","",1,178,4.5627220482008008E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","08:03","LRE6A","RURAL","Planned","",6,92,1.4149565003409225E-3,1.5379961960227417E-5,"NO"]
[null,"2015-08-05","18:53","DRD3A","URBAN","Asset failure","LV",1,47.683333333299998,4.7331048340501644E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","11:11","MTB13A","RURAL","Overloads","",1,152.44999999999999,3.9077920013944495E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","12:28","CMY4","RURAL","Planned","",3,82,6.3057844036932414E-4,7.68998098011371E-6,"NO"]
[null,"2015-08-05","13:11","NBR12A","RURAL","Asset failure","LV",1,131.73333333330001,3.376756092600188E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","15:36","PGN2B","RURAL","Asset failure","LV",1,80.25,2.0570699121804173E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","15:48","GYM5B","RURAL","Asset failure","LV",1,114.9166666667,2.9456899365499671E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","10:39","BHD23A","RURAL","Asset failure","LV",1,32.35,8.29236282355595E-5,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","17:19","KSN7","RURAL","Asset failure","LV",1,46.35,1.188102061427568E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","20:14","CPD2A","RURAL","Overloads","",1,59.45,1.5238978975592001E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","18:54","CPC2B","URBAN","Overloads","",1,49.05,4.8687618058788437E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","19:26","MRK3","URBAN","Overloads","",1,74.616666666699999,7.4065397910055454E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","19:35","AGE8","URBAN","Overloads","",1,149.55000000000001,1.4844512294988403E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","20:24","CVL3A","RURAL","Asset failure","LV",1,87.666666666699996,2.247183330856305E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","21:42","AHL5A","RURAL","Asset failure","LV",1,130.11666666670001,3.3353156395423951E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","09:41","NSW33A","URBAN","Asset failure","LV",1,64.716666666699993,6.4238539219290818E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","17:13","MTB2A","RURAL","Asset failure","LV",1,255.95,6.5608354395336793E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","08:45","MRK9","URBAN","Planned","",51,421,2.1312372015091674E-2,5.062321143727238E-5,"NO"]
[null,"2015-08-05","21:34","AHD19","URBAN","Asset failure","LV",1,111.21666666669999,1.1039499670621564E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","10:21","SMF5A","RURAL","Planned","",12,216,6.644143566818245E-3,3.0759923920454833E-5,"NO"]
[null,"2015-08-05","08:40","ENG17A","URBAN","Planned","",18,263,4.6990251557656364E-3,1.7867015801390253E-5,"NO"]
[null,"2015-08-05","08:43","CPL26A","URBAN","Planned","",21,178,3.7103836147553758E-3,2.0844851768288628E-5,"NO"]
[null,"2015-08-05","08:49","ACR5","RURAL","Planned","",4,369,3.7834706422159451E-3,1.0253307973484946E-5,"NO"]
[null,"2015-08-05","08:49","BTY7A","URBAN","Planned","",49,261,1.2694514726887774E-2,4.8637987459340128E-5,"NO"]
[null,"2015-08-05","09:00","AHL6A","URBAN","Planned","",16,404,6.4162438966770333E-3,1.5881791823458001E-5,"NO"]
[null,"2015-08-05","09:05","BMT1","RURAL","Planned","",3,225.29999999999998,1.7325527148196185E-3,7.68998098011371E-6,"NO"]
[null,"2015-08-05","09:08","SMF5A","RURAL","Asset failure","LV",1,75.099999999999994,1.9250585720217983E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","09:09","JBB3A","RURAL","Overloads","",1,58.516666666699997,1.4999735122885895E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-05","09:30","WRG5A","URBAN","Planned","",1,300,2.9778359668983755E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-05","09:36","BPN3","URBAN","Planned","",34,164,5.5348044504751137E-3,3.3748807624848254E-5,"NO"]
[null,"2015-08-05","09:05","AHL6A","URBAN","Planned","",6,247,1.4710509676477974E-3,5.9556719337967507E-6,"NO"]
[null,"2015-08-05","09:42","GNA4A","URBAN","Planned","",5,268,1.3301000652146077E-3,4.9630599448306254E-6,"NO"]
[null,"2015-08-05","08:37","CRY2A","RURAL","Planned","",2,285,1.4610963862216047E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-05","11:35","LBH6A","RURAL","Asset failure","LV",16,88,3.609164406666701E-3,4.1013231893939782E-5,"NO"]
[null,"2015-08-06","08:40","NSW24","URBAN","Planned","",27,300,8.0401571106256137E-3,2.6800523702085378E-5,"NO"]
[null,"2015-08-06","09:09","NMC5A","RURAL","Planned","",9,297,6.8517730532813145E-3,2.3069942940341127E-5,"NO"]
[null,"2015-08-06","09:08","LRE4A","RURAL","Planned","",1,238,6.1007182442235428E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","08:57","NRG8B","URBAN","Planned","",2,179,3.5535509204987279E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-06","08:57","NRG22A","URBAN","Planned","",72,179,1.279278331379542E-2,7.1468063205561012E-5,"NO"]
[null,"2015-08-06","08:54","EMD1","RURAL","Planned","",6,248,3.8142305661364E-3,1.5379961960227417E-5,"NO"]
[null,"2015-08-06","08:53","KRN2","URBAN","Planned","",13,325,4.1937856533818783E-3,1.2903955856559627E-5,"NO"]
[null,"2015-08-06","08:40","F1173","URBAN","Planned","",1,300,2.9778359668983755E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-06","08:40","SPO41A","URBAN","Planned","",69,390,2.6961326844297889E-2,6.8490227238662637E-5,"NO"]
[null,"2015-08-06","09:10","GTN5B","RURAL","Planned","",1,172,4.4089224285985264E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","12:50","HWL3A","URBAN","Asset failure","LV",1,99.683333333299998,9.8946871766740147E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-06","08:40","CSE9","URBAN","Planned","",52,300,1.5484747027871552E-2,5.1615823426238503E-5,"NO"]
[null,"2015-08-06","08:49","NBR2B","URBAN","Planned","",40,271,1.0759913960392796E-2,3.9704479558645003E-5,"NO"]
[null,"2015-08-06","09:15","BLBNFM6","URBAN","Planned","",1,63,6.2534555304865887E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-06","09:20","SMF5A","RURAL","Planned","",48,256,3.1498162094545749E-2,1.2303969568181933E-4,"NO"]
[null,"2015-08-06","09:28","TWT11A","RURAL","Planned","",26,242,1.6128453442291819E-2,6.6646501827652145E-5,"NO"]
[null,"2015-08-06","09:29","RBY13","URBAN","Planned","",2,181,3.593255400057373E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-06","10:11","CMD11A","RURAL","Planned","",6,116,1.7840755873863806E-3,1.5379961960227417E-5,"NO"]
[null,"2015-08-06","10:20","NRA1A","RURAL","Planned","",6,178,2.7376332289204804E-3,1.5379961960227417E-5,"NO"]
[null,"2015-08-06","10:40","MFD5A","RURAL","Planned","",5,188,2.4095273737689622E-3,1.2816634966856181E-5,"NO"]
[null,"2015-08-06","18:59","CPK13","RURAL","Overloads","",1,109.1833333333,2.7987258555949739E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","22:53","BTA1A","RURAL","Asset failure","LV",1,114.4,2.9324460804166944E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","23:06","CLM3","RURAL","Overloads","",1,69.066666666700002,1.7704045100892552E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","08:40","BMT5","RURAL","Planned","",4,50,5.126653986742473E-4,1.0253307973484946E-5,"NO"]
[null,"2015-08-06","17:22","PGN2B","RURAL","Overloads","",1,46.083333333299997,1.1812665227777236E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","10:23","MFN15A","RURAL","Planned","",28,259,1.8589247355928207E-2,7.1773155814394609E-5,"NO"]
[null,"2015-08-06","08:03","CNA8A","RURAL","Planned","",4,438,4.4345556985322387E-3,1.0253307973484946E-5,"NO"]
[null,"2015-08-06","08:38","FDS3","RURAL","Planned","",26,361,2.4059387159782425E-2,6.6646501827652145E-5,"NO"]
[null,"2015-08-06","07:30","MFD5A","RURAL","Asset failure","LV",1,58.433333333299998,1.4978374064590714E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","20:56","BKD13A","URBAN","Overloads","",1,90.383333333300001,8.9715580269355194E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-06","07:53","KMR17B","URBAN","Planned","",32,246,7.8138415771413366E-3,3.1763583646916001E-5,"NO"]
[null,"2015-08-06","03:07","KSN15","RURAL","Asset failure","LV",1,96.866666666699999,2.4830094142464589E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","08:00","PPE16A","RURAL","Planned","",10,232,5.9469186246212686E-3,2.5633269933712362E-5,"NO"]
[null,"2015-08-06","08:02","MRK2","URBAN","Planned","",51,138,6.9860031783435883E-3,5.062321143727238E-5,"NO"]
[null,"2015-08-06","06:34","CPB4","URBAN","Asset failure","LV",1,66.283333333300007,6.5793631335271576E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-06","08:03","ENG13A","URBAN","Planned","",22,347,7.5775999237673985E-3,2.1837463757254754E-5,"NO"]
[null,"2015-08-06","08:03","NMC16A","RURAL","Overloads","",1,91.75,2.3518525164181094E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-06","08:03","NMK12A","URBAN","Planned","",34,347,1.1710836245822344E-2,3.3748807624848254E-5,"NO"]
[null,"2015-08-06","08:05","MRK9","URBAN","Planned","",16,323,5.1298187589769347E-3,1.5881791823458001E-5,"NO"]
[null,"2015-08-06","08:05","RLA8A","URBAN","Planned","",5,323,1.6030683621802921E-3,4.9630599448306254E-6,"NO"]
[null,"2015-08-06","08:34","THL3","RURAL","Planned","",3,523,4.0218600525994703E-3,7.6899809801137083E-6,"NO"]
[null,"2015-08-06","08:01","CRY2A","RURAL","Planned","",6,57,8.7665783173296286E-4,1.5379961960227417E-5,"NO"]
[null,"2015-08-06","08:35","ZMR10","URBAN","Planned","",9,115,1.0273534085799396E-3,8.9335079006951264E-6,"NO"]
[null,"2015-08-06","08:07","NMK5A","URBAN","Planned","",27,269,7.2093408758609669E-3,2.6800523702085378E-5,"NO"]
[null,"2015-08-06","08:30","THL3","RURAL","Planned","",38,514.98888888886665,5.0229930431303353E-2,9.7406425748106971E-5,"NO"]
[null,"2015-08-06","08:30","LTA12A","URBAN","Planned","",15,430,6.4023473288315072E-3,1.4889179834491876E-5,"NO"]
[null,"2015-08-06","08:28","AMR2","RURAL","Planned","",56,416,5.9715265637576322E-2,1.4354631162878922E-4,"NO"]
[null,"2015-08-06","08:26","CRB22A","URBAN","Planned","",15,254,3.7818516779609367E-3,1.4889179834491876E-5,"NO"]
[null,"2015-08-06","08:24","ESK5A","RURAL","Planned","",15,358,1.3765065954403539E-2,3.8449904900568543E-5,"NO"]
[null,"2015-08-06","08:22","MTG13A","URBAN","Planned","",14,270,3.752073318291953E-3,1.3896567845525752E-5,"NO"]
[null,"2015-08-06","08:22","KRN2","URBAN","Planned","",30,293,8.7250593830122403E-3,2.9778359668983753E-5,"NO"]
[null,"2015-08-06","08:22","CMD15A","URBAN","Planned","",44,348,1.5198874775049309E-2,4.3674927514509508E-5,"NO"]
[null,"2015-08-07","18:56","CVL9A","URBAN","Asset failure","LV",1,108.6,1.0779766200172118E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-07","06:47","BMT5","RURAL","Overloads","",1,101.2666666667,2.5957958019547935E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-08","13:05","CMV13","URBAN","Asset failure","LV",1,126.3833333333,1.2544961187213569E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-09","15:47","MDR3A","URBAN","Overloads","",1,86.716666666699993,8.6076002976545558E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-10","08:23","HDA10A","URBAN","Planned","",2,452,8.9732123802537716E-4,1.9852239779322501E-6,"NO"]
[null,"2015-08-11","09:45","NVL12","URBAN","Planned","",15,135,2.0100392776564034E-3,1.4889179834491876E-5,"NO"]
[null,"2015-08-11","08:35","TGP9A","URBAN","Planned","",8,321,2.5490275876650093E-3,7.9408959117290003E-6,"NO"]
[null,"2015-08-12","17:21","MLY3","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",49,261,3.2782388918224742E-2,1.2560302267519059E-4,"NO"]
[null,"2015-08-12","09:00","GYS3A","RURAL","Planned","",3,129,9.9200754643466839E-4,7.6899809801137083E-6,"NO"]
[null,"2015-08-13","08:40","MTG3A","URBAN","Planned","",23,208,4.7486557552139427E-3,2.2830075746220877E-5,"NO"]
[null,"2015-08-13","08:15","BMT1","RURAL","Planned","",38,330.84705882352932,3.2370846769438986E-2,9.7406425748106971E-5,"NO"]
[null,"2015-08-13","18:53","KWA12A","URBAN","Asset failure","LV",1,124.6166666667,1.2369599735836172E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-13","16:48","AMR3","RURAL","Asset failure","LV",2,166.71666666670001,8.5469866382325351E-4,5.1266539867424728E-6,"NO"]
[null,"2015-08-14","08:28","GGR5","RURAL","Planned","",52,293.2153846153538,3.9281704509913654E-2,1.3329300365530426E-4,"NO"]
[null,"2015-08-16","08:00","MRE2","URBAN","Planned","",19,130,2.4517516127463292E-3,1.8859627790356379E-5,"NO"]
[null,"2015-08-16","06:28","DBY7A","URBAN","Animal","Animal impact",75,101.35,7.5450918811287588E-3,7.4445899172459386E-5,"NO"]
[null,"2015-08-17","08:25","GYGGYS6","RURAL","Planned","",1,175,4.4858222383996636E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-18","20:37","CRM13A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",1793,57.616666666699992,0.10254345241705297,1.7797532962162623E-3,"NO"]
[null,"2015-08-18","08:16","GYGGYS6","RURAL","Planned","",5,206,2.6402268031723735E-3,1.2816634966856181E-5,"NO"]
[null,"2015-08-19","10:01","LLY1","RURAL","Planned","",2,48,2.4607939136363867E-4,5.1266539867424728E-6,"NO"]
[null,"2015-08-19","08:36","WFD2B","RURAL","Planned","",2,222,1.1381171850568289E-3,5.1266539867424728E-6,"NO"]
[null,"2015-08-19","13:04","WSE3A","RURAL","Asset failure","HV",6,8,1.2303969568181933E-4,1.5379961960227417E-5,"NO"]
[null,"2015-08-20","18:20","DRA11A","URBAN","Asset failure","LV",1,102.5,1.0174272886902783E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-20","08:53","SBH6","URBAN","Asset failure","LV",1,242.4166666667,2.4062568965857125E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-21","09:32","GBG27","URBAN","Overloads","",1,215.2,2.1361010002551013E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-23","21:33","SPO51A","URBAN","Asset failure","LV",1,102.6666666667,1.0190816420055527E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-23","11:10","BLB2A","URBAN","Asset failure","LV",1,86.766666666700004,8.6125633575993881E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-24","19:02","NDH6","URBAN","Asset failure","LV",85,58,4.8935771056029965E-3,8.4372019062120641E-5,"NO"]
[null,"2015-08-25","14:32","CBW11","RURAL","Overloads","",1,89.45,2.2928959955705711E-4,2.5633269933712364E-6,"NO"]
[null,"2015-08-25","08:50","MTG8A","URBAN","Planned","",31,231,7.1080944529864224E-3,3.0770971657949879E-5,"NO"]
[null,"2015-08-26","10:15","CBW7","RURAL","Planned","",4,91,9.3305102558713003E-4,1.0253307973484946E-5,"NO"]
[null,"2015-08-26","04:40","BLH10B","URBAN","Planned","",1,60,5.9556719337967505E-5,9.9261198896612504E-7,"NO"]
[null,"2015-08-27","08:03","CBW6","RURAL","Planned","",4,176,1.8045822033333505E-3,1.0253307973484946E-5,"NO"]
[null,"2015-08-27","09:10","HDN4","RURAL","Planned","",20,95,4.870321287405349E-3,5.1266539867424725E-5,"NO"]
[null,"2015-08-28","09:33","YDA3A","RURAL","Planned","",24,44,2.7068733050000255E-3,6.151984784090968E-5,"NO"]
[null,"2015-08-29","08:37","AMR1","RURAL","Unknown","Unknown",4,182.23333333330001,1.8684944897010649E-3,1.0253307973484946E-5,"NO"]
[null,"2015-08-30","18:47","NIP1A","URBAN","Asset failure","LV",89,139.94999999999999,1.236352825916702E-2,8.8342467017985132E-5,"NO"]
[null,"2015-08-31","16:20","CLD25A","URBAN","Asset failure","LV",1,361.51666666670002,3.5884577754443677E-4,9.9261198896612504E-7,"NO"]
[null,"2015-08-31","06:14","COR22A","RURAL","Asset failure","LV",2,174.05,8.9229412639252749E-4,5.1266539867424728E-6,"NO"]
[null,"2015-09-01","12:48","CLD28A","RURAL","Planned","",3,38,2.9221927724432095E-4,7.6899809801137083E-6,"NO"]
[null,"2015-09-01","01:52","MGP13A","RURAL","Asset failure","LV",1,63.883333333300001,1.6375387275978037E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-02","08:14","MRK9","URBAN","Planned","",3,319,9.499296734405818E-4,2.9778359668983753E-6,"NO"]
[null,"2015-09-02","09:00","CSE2","URBAN","Planned","",30,448,1.3340705131704721E-2,2.9778359668983753E-5,"NO"]
[null,"2015-09-02","08:22","MDR24A","URBAN","Asset failure","LV",1,314.71666666670001,3.1239153646082213E-4,9.9261198896612504E-7,"NO"]
[null,"2015-09-03","09:31","LRE6A","RURAL","Overloads","",1,85.75,2.1980528968158352E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-03","08:03","FDS3","RURAL","Network business","Switching and protection error",156,1.5166666667000004,6.0648316664496367E-4,3.9987901096591276E-4,"NO"]
[null,"2015-09-04","09:59","TBV4","RURAL","Planned","",2,150,7.6899809801137095E-4,5.1266539867424728E-6,"NO"]
[null,"2015-09-04","08:14","CRB24B","URBAN","Planned","",157,282,4.3946903199486222E-2,1.5584008226768168E-4,"NO"]
[null,"2015-09-04","08:54","LWD1","RURAL","Planned","",3,229,1.7610056444460395E-3,7.6899809801137083E-6,"NO"]
[null,"2015-09-06","15:47","CLM5","URBAN","Asset failure","LV",1,92.366666666699999,9.1684260714204171E-5,9.9261198896612504E-7,"NO"]
[null,"2015-09-07","09:05","BTY5A","URBAN","Planned","",7,40,2.7793135691051506E-4,6.9482839227628759E-6,"NO"]
[null,"2015-09-07","08:26","AHL9A","URBAN","Planned","",50,326,1.6179575420147838E-2,4.9630599448306258E-5,"NO"]
[null,"2015-09-08","17:40","KSN5","RURAL","Asset failure","LV",1,52.333333333299997,1.341474459863426E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-08","19:19","TGW4","RURAL","Asset failure","LV",65,35,5.831568909919563E-3,1.6661625456913036E-4,"NO"]
[null,"2015-09-09","09:10","BLBNFM6","URBAN","Planned","",3,210,6.2534555304865887E-4,2.9778359668983753E-6,"NO"]
[null,"2015-09-09","14:35","AHD22A","URBAN","Asset failure","LV",3,26,7.7423735139357761E-5,2.9778359668983753E-6,"NO"]
[null,"2015-09-10","01:18","SDM1","RURAL","Animal","Animal nesting/burrowing, etc and other",184,3.2166666667000046,1.5171478031590436E-3,4.7165216678030796E-4,"NO"]
[null,"2015-09-10","08:22","GYN6A","RURAL","Planned","",23,284,1.6743651920700917E-2,5.8956520847538435E-5,"NO"]
[null,"2015-09-11","19:15","GYN6A","RURAL","Asset failure","LV",1,104.0666666667,2.6675689577691878E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-12","21:29","SPD12B","URBAN","Asset failure","LV",1,289.38333333330002,2.8724536607361412E-4,9.9261198896612504E-7,"NO"]
[null,"2015-09-13","08:04","HDA4A","URBAN","Planned","",24,465,1.1077549796861957E-2,2.3822687735187006E-5,"NO"]
[null,"2015-09-14","12:15","KBN1B","RURAL","Planned","",6,47,7.2285821213068872E-4,1.537996196022742E-5,"NO"]
[null,"2015-09-14","08:26","CCY6A","URBAN","Planned","",1,213,2.1142635364978466E-4,9.9261198896612504E-7,"NO"]
[null,"2015-09-15","17:37","SHW6A","URBAN","Asset failure","LV",1,77.45,7.6877798545426387E-5,9.9261198896612504E-7,"NO"]
[null,"2015-09-15","10:39","GYN3A","RURAL","Asset failure","LV",2,140.35,7.1952588703930599E-4,5.1266539867424728E-6,"NO"]
[null,"2015-09-16","09:26","TBV4","RURAL","Planned","",1,184,4.7165216678030748E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-16","08:04","ZMR7A","URBAN","Planned","",52,304,1.5691210321576506E-2,5.161582342623851E-5,"NO"]
[null,"2015-09-16","17:17","SCV4","URBAN","Asset failure","HV",379,189.93484848488185,7.0271188212811336E-2,3.7619994381816145E-4,"NO"]
[null,"2015-09-17","08:25","FDS4","RURAL","Planned","",1,34,8.7153117774622043E-5,2.5633269933712364E-6,"NO"]
[null,"2015-09-17","21:10","MCW11","RURAL","Asset failure","LV",1,133.28333333329999,3.4164876609974414E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-17","06:26","BTN3","RURAL","Asset failure","LV",22,74,4.1730963452083726E-3,5.6393193854167202E-5,"NO"]
[null,"2015-09-18","15:26","GLY15A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",56,72.2,5.2856588412446169E-3,5.5586271382103007E-5,"NO"]
[null,"2015-09-18","08:36","NMK9A","URBAN","Planned","",2,217,4.307936032112983E-4,1.9852239779322501E-6,"NO"]
[null,"2015-09-19","08:00","BLBNFM6","URBAN","Planned","",47,267,1.2456287849535905E-2,4.6652763481407883E-5,"NO"]
[null,"2015-09-21","12:19","TBV3","RURAL","Planned","",1,125,3.2041587417140454E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-22","09:55","MFN12A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1582,73.103875969000001,0.29031105118624134,4.0551833035132956E-3,"NO"]
[null,"2015-09-22","08:03","BLB2A","URBAN","Planned","",20,382,7.5835555957011963E-3,1.9852239779322502E-5,"NO"]
[null,"2015-09-23","09:40","AHD10B","URBAN","Overloads","",1,132.4,1.3142182733911497E-4,9.9261198896612504E-7,"NO"]
[null,"2015-09-23","11:27","ABY2A","RURAL","Planned","",1,183,4.6908883978693627E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-23","08:27","CRY6A","RURAL","Planned","",27,327.46153846153845,2.2657247294408357E-2,6.9209828821023377E-5,"NO"]
[null,"2015-09-24","12:48","CNA9A","RURAL","Planned","",5,126,1.6148960058238789E-3,1.2816634966856181E-5,"NO"]
[null,"2015-09-24","08:35","KBN15A","URBAN","Planned","",6,350,2.0844851768288628E-3,5.9556719337967507E-6,"NO"]
[null,"2015-09-25","19:47","CMD5A","URBAN","Asset failure","LV",1,76.45,7.5885186556460272E-5,9.9261198896612504E-7,"NO"]
[null,"2015-09-25","08:06","GYGGYS6","RURAL","Planned","",2,244,1.2509035727651635E-3,5.1266539867424728E-6,"NO"]
[null,"2015-09-27","15:14","TMH15A","URBAN","Overloads","",1,94.366666666699999,9.366948469213643E-5,9.9261198896612504E-7,"NO"]
[null,"2015-09-27","07:16","CRMEDB2","URBAN","Planned","",2,247,4.903503225492658E-4,1.9852239779322501E-6,"NO"]
[null,"2015-09-28","10:21","NMC1B","RURAL","Asset failure","LV",1,4.4166666667000003,1.1321360887475073E-5,2.5633269933712364E-6,"NO"]
[null,"2015-09-28","07:47","FDS3","RURAL","Unknown","Unknown",1,57.183333333299998,1.4657958190419308E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-29","14:56","NMC5A","RURAL","Weather","",760,88.28333333330005,0.17198727906250924,1.9481285149621397E-3,"NO"]
[null,"2015-09-29","17:46","CBW11","RURAL","Weather","",18,23,1.0612173752556919E-3,4.6139885880682253E-5,"NO"]
[null,"2015-09-29","12:37","BHD23A","RURAL","Asset failure","LV",1,106.5,2.729943247940367E-4,2.5633269933712364E-6,"NO"]
[null,"2015-09-29","09:32","CSE4","URBAN","Planned","",21,388,8.087802486095988E-3,2.0844851768288628E-5,"NO"]
[null,"2015-09-30","09:20","CPK13","RURAL","Planned","",50,202,2.5889602633049489E-2,1.2816634966856182E-4,"NO"]
[null,"2015-10-01","10:55","CBT8A","RURAL","Planned","",1,178,4.5627220482008008E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-01","08:57","TGW1","RURAL","Planned","",28,315,2.2608544081534305E-2,7.1773155814394623E-5,"NO"]
[null,"2015-10-02","10:33","NSW8A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",1816,79.002666666668006,0.13218239973211726,1.8025833719624831E-3,"NO"]
[null,"2015-10-02","08:02","NBR13A","URBAN","Planned","",34,334,1.1272101746699317E-2,3.3748807624848254E-5,"NO"]
[null,"2015-10-02","08:35","RCF5A","URBAN","Planned","",56,325,1.8065538199183478E-2,5.5586271382103007E-5,"NO"]
[null,"2015-10-04","09:30","AJV1","URBAN","Asset failure","LV",16,141,2.2393326471075782E-3,1.5881791823458001E-5,"NO"]
[null,"2015-10-06","10:15","KSN8","RURAL","Planned","",30,207,1.5918260628835376E-2,7.68998098011371E-5,"NO"]
[null,"2015-10-06","08:20","ACR12A","URBAN","Planned","",13,455,5.87129991473463E-3,1.2903955856559627E-5,"NO"]
[null,"2015-10-07","10:17","CCY8A","RURAL","Planned","",39,166,1.6594978955085386E-2,9.9969752741478217E-5,"NO"]
[null,"2015-10-07","08:05","ZMR9","URBAN","Planned","",21,283,5.8990930504256821E-3,2.0844851768288628E-5,"NO"]
[null,"2015-10-08","09:55","KRN12","URBAN","Planned","",33,367,1.2021523798368742E-2,3.2756195635882131E-5,"NO"]
[null,"2015-10-08","09:12","NMC15A","RURAL","Weather","",11,177.48333333330001,5.0044260112742812E-3,2.8196596927083601E-5,"NO"]
[null,"2015-10-09","10:05","MLT42A","URBAN","Planned","",2,58,1.1514299072007052E-4,1.9852239779322501E-6,"NO"]
[null,"2015-10-09","08:19","GYM2A","RURAL","Planned","",10,258,6.7979431864205186E-3,2.5633269933712362E-5,"NO"]
[null,"2015-10-10","19:19","WMD8B","RURAL","Overloads","",1,66.183333333299998,1.6964952484453422E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-10","08:02","SFD2A","URBAN","Planned","",45,243,1.0854212099344578E-2,4.4667539503475631E-5,"NO"]
[null,"2015-10-11","08:41","WRG9A","URBAN","Planned","",1,297,2.9480576072293916E-4,9.9261198896612504E-7,"NO"]
[null,"2015-10-12","14:55","AFD3AOLD","URBAN","Network business","Network error",16,5.3,8.4173496664327418E-5,1.5881791823458001E-5,"NO"]
[null,"2015-10-12","09:07","BNH6A","RURAL","Planned","",4,289,2.9632060043371495E-3,1.0253307973484946E-5,"NO"]
[null,"2015-10-13","17:24","RPN4A","RURAL","Overloads","",1,48.25,1.2368052743016216E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-14","16:01","LLY1","RURAL","Unknown","Unknown",483,27.533333333300078,3.4088660354005408E-2,1.2380869377983075E-3,"NO"]
[null,"2015-10-14","17:16","GTN3A","URBAN","Weather","",1,53.4666666667,5.3071654343421908E-5,9.9261198896612504E-7,"NO"]
[null,"2015-10-14","16:01","TRP1","RURAL","Unknown","Unknown",684,32.75,5.7421087978509089E-2,1.7533156634659268E-3,"NO"]
[null,"2015-10-14","08:55","CVL7A","RURAL","Planned","",1,170,4.3576558887311017E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-14","12:00","RCF1A","URBAN","Asset failure","LV",5,90,4.4667539503475632E-4,4.9630599448306254E-6,"NO"]
[null,"2015-10-15","10:10","NSW8A","URBAN","Planned","",1,214,2.1241896563875079E-4,9.9261198896612504E-7,"NO"]
[null,"2015-10-16","09:00","HWL1A","URBAN","Planned","",10,221,2.1936724956151364E-3,9.9261198896612508E-6,"NO"]
[null,"2015-10-16","17:40","SMR7A","URBAN","Unknown","Unknown",1,59.3,5.8861890945691217E-5,9.9261198896612504E-7,"NO"]
[null,"2015-10-17","09:31","WTWT1","CBD","7 - STPIS Exclusion (3.3)(a)","",103,237.4333333333,6.2562377419621136,2.6349449987209006E-2,"NO"]
[null,"2015-10-17","11:50","SFD10","URBAN","Asset failure","LV",1,65.150000000000006,6.466867108114306E-5,9.9261198896612504E-7,"NO"]
[null,"2015-10-17","09:31","CMUT1","CBD","7 - STPIS Exclusion (3.3)(a)","",1,237.4333333333,6.0740172252059348E-2,2.5581990278843696E-4,"NO"]
[null,"2015-10-19","13:57","TWT11A","RURAL","Asset failure","LV",1,98.783333333300007,2.5321398482843654E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-19","08:30","CSE9","URBAN","Planned","",20,371,7.3651809581286483E-3,1.9852239779322502E-5,"NO"]
[null,"2015-10-20","10:00","GYS3A","RURAL","Planned","",4,45,4.6139885880682255E-4,1.0253307973484946E-5,"NO"]
[null,"2015-10-20","08:22","BKD15A","URBAN","Planned","",38,328,1.2371915830473784E-2,3.7719255580712758E-5,"NO"]
[null,"2015-10-21","13:01","NBR12A","RURAL","Overloads","",1,112.7666666667,2.8905784061924853E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-21","08:11","PWC4","RURAL","Planned","",43,335,3.692472533951266E-2,1.1022306071496315E-4,"NO"]
[null,"2015-10-22","14:47","KBR3A","RURAL","Weather","",28,128,9.1869639442425099E-3,7.1773155814394609E-5,"NO"]
[null,"2015-10-22","08:40","WHO1","RURAL","Planned","",15,272,1.0458374132954645E-2,3.844990490056855E-5,"NO"]
[null,"2015-10-22","21:58","NVL10","URBAN","Asset failure","HV",591,38.700000000033327,2.1227454059455177E-2,5.8663368547897993E-4,"NO"]
[null,"2015-10-22","21:58","TWT12A","RURAL","Asset failure","HV",1018,23.883333333333347,5.2654581434335254E-2,2.6094668792519199E-3,"NO"]
[null,"2015-10-23","06:46","KVG40A","URBAN","Vegetation","Blow-in/Fall-in - NSP responsibility",174,83.966666666699993,1.4502259681198637E-2,1.7271448608010577E-4,"NO"]
[null,"2015-10-24","07:10","WLDT1","URBAN","Planned","",1,400,3.9704479558645006E-4,9.9261198896612504E-7,"NO"]
[null,"2015-10-25","09:50","CPS12B","RURAL","Overloads","",1,71.383333333300001,1.8297882521006465E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-26","17:07","NRA15A","RURAL","Unknown","Unknown",17,127.05,5.5364018066328645E-3,4.3576558887311021E-5,"NO"]
[null,"2015-10-26","09:06","ZMR3","URBAN","Planned","",6,287,1.7092778449996674E-3,5.9556719337967507E-6,"NO"]
[null,"2015-10-27","16:30","BLN16A","URBAN","Asset failure","LV",1,170.71666666670001,1.6945541004970008E-4,9.9261198896612504E-7,"NO"]
[null,"2015-10-27","18:15","CBW11","RURAL","Weather","",2,94.066666666700002,4.8224725168641286E-4,5.1266539867424728E-6,"NO"]
[null,"2015-10-27","08:16","LGV5B","RURAL","Planned","",7,202,3.6245443686269284E-3,1.7943288953598656E-5,"NO"]
[null,"2015-10-27","09:18","KWA12A","URBAN","Planned","",69,332,2.2738755443235996E-2,6.8490227238662637E-5,"NO"]
[null,"2015-10-28","17:35","AHD10B","URBAN","Asset failure","LV",1,177.86666666670001,1.765525857708079E-4,9.9261198896612504E-7,"NO"]
[null,"2015-10-28","13:38","BWH13A","RURAL","Weather","",2,77,3.947523569791704E-4,5.1266539867424728E-6,"NO"]
[null,"2015-10-28","23:35","YDA5A","RURAL","Asset failure","HV",910,9,2.0993648075710421E-2,2.3326275639678254E-3,"NO"]
[null,"2015-10-29","07:04","BBSRDL12","RURAL","Network business","Switching and protection error",0,1.0000000766012818,0,0,"NO"]
[null,"2015-10-29","08:39","TWT11A","RURAL","Asset failure","LV",1,147.35,3.7770623247325165E-4,2.5633269933712364E-6,"NO"]
[null,"2015-10-30","09:50","BLN15A","URBAN","Planned","",6,170,1.0124642287454475E-3,5.9556719337967507E-6,"NO"]
[null,"2015-10-30","04:05","KMR24A","URBAN","Asset failure","LV",1,78.066666666700002,7.7489909271988584E-5,9.9261198896612504E-7,"NO"]
[null,"2015-10-30","05:18","KMR24A","URBAN","Asset failure","LV",8,707,5.6142134095924041E-3,7.9408959117290003E-6,"NO"]
[null,"2015-11-01","11:14","INA7A","RURAL","Planned","",1,76,1.9481285149621397E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-02","20:15","WRD20A","URBAN","Asset failure","LV",1,77.349999999999994,7.6778537346529769E-5,9.9261198896612504E-7,"NO"]
[null,"2015-11-02","09:05","WMD14A","RURAL","Planned","",83,255,5.4252815814702218E-2,2.1275614044981262E-4,"NO"]
[null,"2015-11-03","18:23","SPO51A","URBAN","Third party","Vehicle impact",53,96.416666666699996,5.0723299812844005E-3,5.2608435415204633E-5,"NO"]
[null,"2015-11-03","21:11","CLD22A","URBAN","Asset failure","LV",1,107,1.0620948281937539E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-03","09:00","CLD21A","RURAL","Planned","",30,124,9.5355764153409999E-3,7.6899809801137087E-5,"NO"]
[null,"2015-11-04","17:31","CBT15A","RURAL","Unknown","Unknown",203,1.4166666730307043,7.3717012117701145E-4,5.2035537965436102E-4,"NO"]
[null,"2015-11-04","08:06","DBY6","URBAN","Planned","",7,157,1.0908805758737714E-3,6.9482839227628759E-6,"NO"]
[null,"2015-11-05","17:59","CSE4","URBAN","Asset failure","LV",1,85.833333333300004,8.5199195719559329E-5,9.9261198896612504E-7,"NO"]
[null,"2015-11-05","22:12","KSN14","URBAN","Weather","",70,138.65,9.6337956589107269E-3,6.9482839227628753E-5,"NO"]
[null,"2015-11-05","04:32","GVN15A","URBAN","Planned","",2,143,2.8388702884431179E-4,1.9852239779322501E-6,"NO"]
[null,"2015-11-06","15:58","TGW5","RURAL","Weather","",408,45.383333333299866,4.7463587940024379E-2,1.0458374132954649E-3,"NO"]
[null,"2015-11-06","08:19","RCN11","URBAN","Planned","",1,33,3.2756195635882131E-5,9.9261198896612504E-7,"NO"]
[null,"2015-11-06","10:10","IPL4A","RURAL","Asset failure","LV",1,135.73333333330001,3.4792891723350373E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-07","17:22","GYM2A","RURAL","Weather","",1395,3.18333333330001,1.1383094345694128E-2,3.5758411557528756E-3,"NO"]
[null,"2015-11-07","20:22","WHO9","RURAL","Weather","",1,214.23333333330001,5.4915008621314577E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-07","17:22","GYM5A","RURAL","Weather","",1,3.1833333332999998,8.1599242621463247E-6,2.5633269933712364E-6,"NO"]
[null,"2015-11-07","14:48","NMC3A","RURAL","Weather","",12,71.25,2.1916445793324071E-3,3.0759923920454833E-5,"NO"]
[null,"2015-11-08","12:28","SMF5A","RURAL","Weather","",13,48.35,1.6111791816834904E-3,3.3323250913826072E-5,"NO"]
[null,"2015-11-09","11:36","LRE7A","RURAL","Planned","",29,162,1.2042510214858068E-2,7.4336482807765855E-5,"NO"]
[null,"2015-11-09","09:13","SGT9","URBAN","Planned","",1,239,2.3723426536290392E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-10","09:38","SPD5B","URBAN","Planned","",1,157,1.5584008226768165E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-10","06:57","GBN4","RURAL","Asset failure","LV",1,421.71666666670001,1.0809977152212921E-3,2.5633269933712364E-6,"NO"]
[null,"2015-11-11","10:36","IPL1","RURAL","Planned","",1,77,1.973761784895852E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-11","05:58","ARG3","URBAN","Asset failure","LV",1,172.7,1.7142409049444979E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-11","08:25","CLM9","URBAN","Planned","",11,235,2.5659019914774333E-3,1.0918731878627377E-5,"NO"]
[null,"2015-11-12","08:01","NMK4A","URBAN","Planned","",3,269,8.0103787509566303E-4,2.9778359668983753E-6,"NO"]
[null,"2015-11-12","08:26","NBR11A","RURAL","Planned","",22,340,1.9173685910416849E-2,5.6393193854167202E-5,"NO"]
[null,"2015-11-13","13:38","KSN6","URBAN","Asset failure","LV",1,143.61666666670001,1.425556251487181E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-13","08:15","CRY6A","RURAL","Planned","",1,140,3.588657790719731E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-14","18:32","ARG5A","URBAN","Asset failure","LV",1,115.0166666667,1.1416692226428692E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-15","10:00","BTN7","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",63,67.299999999999969,1.0868250119194702E-2,1.6148960058238784E-4,"NO"]
[null,"2015-11-15","07:55","COR23A","RURAL","Weather","",1,497.35,1.2748706801531844E-3,2.5633269933712364E-6,"NO"]
[null,"2015-11-16","09:45","NRA1A","RURAL","Other","Safety",18,255,1.1381171850568288E-2,4.6139885880682253E-5,"NO"]
[null,"2015-11-16","08:56","RCF2A","URBAN","Planned","",14,88,1.2228979704062661E-3,1.3896567845525752E-5,"NO"]
[null,"2015-11-17","09:15","RBA43A","RURAL","Planned","",2,261,1.3380566905397853E-3,5.1266539867424728E-6,"NO"]
[null,"2015-11-17","08:10","WRG19A","URBAN","Planned","",7,208,1.4452430559346782E-3,6.9482839227628759E-6,"NO"]
[null,"2015-11-18","10:24","CDRSPD12","URBAN","Asset failure","LV",1,61.95,6.1492312716451448E-5,9.9261198896612504E-7,"NO"]
[null,"2015-11-18","06:35","GGR2","RURAL","Weather","",1,109.03333333330001,2.7948808651049174E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-19","10:02","CMD5A","URBAN","Planned","",61,139,8.4163570544437752E-3,6.0549331326933635E-5,"NO"]
[null,"2015-11-19","08:01","MMC22A","URBAN","Planned","",33,417,1.3659333580162848E-2,3.2756195635882131E-5,"NO"]
[null,"2015-11-20","20:27","DBY7A","URBAN","Unknown","Unknown",108,63,6.7537319729255151E-3,1.0720209480834151E-4,"NO"]
[null,"2015-11-20","08:05","PWC4","RURAL","Planned","",8,349,7.1568089654924921E-3,2.0506615946969891E-5,"NO"]
[null,"2015-11-21","12:42","NRG9","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,148,3.7937239501894301E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-21","18:31","LHM1A","URBAN","Asset failure","LV",26,148.4166666667,3.8303242300896426E-3,2.5807911713119255E-5,"NO"]
[null,"2015-11-22","08:51","NSW17","URBAN","Planned","",30,248,7.3850331979079713E-3,2.9778359668983753E-5,"NO"]
[null,"2015-11-23","20:42","NIP1A","URBAN","Asset failure","LV",1,213.36666666670001,2.1179031137910534E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-23","20:31","TRP3","RURAL","Overloads","",1,74.983333333299996,1.922068023862011E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-23","16:00","KMR25A","RURAL","Asset failure","HV",30,11.8166666667,9.0869941915266658E-4,7.68998098011371E-5,"NO"]
[null,"2015-11-24","09:09","CMY1","RURAL","Weather","",2,541,2.7735198068276779E-3,5.1266539867424728E-6,"NO"]
[null,"2015-11-24","19:58","DRD13A","URBAN","Asset failure","LV",1,117,1.1613560270903664E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-24","02:16","GGR4","RURAL","Weather","",4,107,1.0971039531628892E-3,1.0253307973484946E-5,"NO"]
[null,"2015-11-25","10:36","AHL12A","URBAN","Asset failure","LV",1,7.9,7.8416347128323887E-6,9.9261198896612504E-7,"NO"]
[null,"2015-11-25","13:48","LBH1B","RURAL","Overloads","",1,103.8166666667,2.6611606402857595E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-25","08:55","CVL7A","RURAL","Planned","",19,280,1.3636899604734978E-2,4.8703212874053492E-5,"NO"]
[null,"2015-11-26","11:39","TRP3","RURAL","Unknown","Unknown",1,395.98333333329998,1.0150347672583679E-3,2.5633269933712364E-6,"NO"]
[null,"2015-11-26","09:57","BDT5","RURAL","Planned","",3,122,9.3817767957387254E-4,7.6899809801137083E-6,"NO"]
[null,"2015-11-26","09:52","RWD1","RURAL","Planned","",9,265,6.0597050123296029E-3,2.306994294034113E-5,"NO"]
[null,"2015-11-27","10:33","CVL17A","URBAN","Planned","",4,114,4.5263106696855304E-4,3.9704479558645002E-6,"NO"]
[null,"2015-11-27","08:04","RCF2A","URBAN","Planned","",39,349,1.351044178181793E-2,3.8711867569678881E-5,"NO"]
[null,"2015-11-28","08:04","CBW14","URBAN","Asset failure","LV",1,170.8166666667,1.695546712485967E-4,9.9261198896612504E-7,"NO"]
[null,"2015-11-28","06:48","ALY5","URBAN","Asset failure","LV",1,57.1,5.6678144569965749E-5,9.9261198896612504E-7,"NO"]
[null,"2015-11-29","19:36","RCF10A","URBAN","Overloads","",1,268.64999999999998,2.6666521083574949E-4,9.9261198896612504E-7,"YES"]
[null,"2015-11-29","16:30","BNH6A","RURAL","Weather","",22,380,2.1429413664583542E-2,5.6393193854167209E-5,"YES"]
[null,"2015-11-29","17:18","WCL19A","RURAL","Weather","",121,391.58571428571435,0.14342660425819881,3.1016256619791961E-4,"YES"]
[null,"2015-11-29","15:18","BHD35A","RURAL","Asset failure","HV",93,242,5.7690237312813052E-2,2.3838941038352492E-4,"YES"]
[null,"2015-11-30","15:16","AGT25A","RURAL","Overloads","",1,92.483333333299996,2.3706502477019773E-4,2.5633269933712364E-6,"NO"]
[null,"2015-11-30","03:05","YMT5A","RURAL","Weather","",2,64,3.2810585515151826E-4,5.1266539867424728E-6,"NO"]
[null,"2015-11-30","04:45","LLY5","RURAL","Weather","",6,479.21666666670001,7.3703341040408281E-3,1.5379961960227417E-5,"NO"]
[null,"2015-11-30","08:05","SMR12A","URBAN","Planned","",38,468,1.7652611611773571E-2,3.7719255580712751E-5,"NO"]
[null,"2015-12-01","21:21","MDH5A","URBAN","Animal","Animal impact",64,71.549999999999983,4.5453688198736804E-3,6.3527167293832003E-5,"NO"]
[null,"2015-12-01","00:50","BMT1","RURAL","Weather","",8,629.98333333330004,1.29188262696579E-2,2.0506615946969891E-5,"NO"]
[null,"2015-12-01","09:05","AGE10","URBAN","Planned","",21,295,6.1492312716451454E-3,2.0844851768288628E-5,"NO"]
[null,"2015-12-02","12:49","MRK2","URBAN","Planned","",36,148,5.2886366772115145E-3,3.5734031602780506E-5,"NO"]
[null,"2015-12-02","08:16","ZMR6A","URBAN","Planned","",1,225,2.2333769751737816E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-03","13:15","AHD22A","URBAN","Weather","",1196,53.204545454545453,6.3223229502810577E-2,1.1871639388034859E-3,"NO"]
[null,"2015-12-03","17:41","KLG11A","URBAN","Asset failure","LV",1,86.05,8.5414261650535066E-5,9.9261198896612504E-7,"NO"]
[null,"2015-12-03","08:49","GGR5","RURAL","Planned","",12,144,4.4294290445454961E-3,3.0759923920454833E-5,"NO"]
[null,"2015-12-03","08:52","AMR3","RURAL","Planned","",3,294,2.2608544081534304E-3,7.68998098011371E-6,"NO"]
[null,"2015-12-04","08:39","WRG15A","URBAN","Planned","",1,258,2.5609389315326027E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-05","07:52","NVL9","RURAL","Asset failure","LV",1,199.95,5.1253723232457871E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-06","07:48","WED20A","URBAN","Planned","",61,497,3.0093017669486015E-2,6.0549331326933635E-5,"NO"]
[null,"2015-12-07","09:08","LTA8A","URBAN","Planned","",35,359,1.2472169641359363E-2,3.4741419613814383E-5,"NO"]
[null,"2015-12-07","00:12","MTB3A","RURAL","Animal","Animal impact",1,175.76666666669999,4.505474412016364E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-08","11:20","WFD1B","RURAL","Planned","",41,105,1.1035122706463172E-2,1.0509640672822068E-4,"NO"]
[null,"2015-12-08","05:47","BBH8A","URBAN","Animal","Animal nesting/burrowing, etc and other",576,32.983333333300003,1.8858039611154974E-2,5.7174450564448809E-4,"NO"]
[null,"2015-12-09","10:47","SMF11A","RURAL","Planned","",9,253,5.8366955639063056E-3,2.3069942940341127E-5,"NO"]
[null,"2015-12-09","12:43","NMK12A","URBAN","Planned","",14,123,1.7092778449996674E-3,1.3896567845525752E-5,"NO"]
[null,"2015-12-09","08:37","RLA5A","URBAN","Planned","",9,155,1.3846937246077445E-3,8.9335079006951264E-6,"NO"]
[null,"2015-12-10","18:01","YTA39A","RURAL","Weather","",59,259,3.9170199785705864E-2,1.5123629260890294E-4,"YES"]
[null,"2015-12-10","21:37","BLN2B","URBAN","Weather","",6,76,4.5263106696855304E-4,5.9556719337967507E-6,"YES"]
[null,"2015-12-10","19:45","RLB13B","RURAL","Weather","",1,270.76666666670002,6.9406350557190397E-4,2.5633269933712364E-6,"YES"]
[null,"2015-12-10","08:20","RLA8A","URBAN","Planned","",24,111,2.6443183386057573E-3,2.3822687735187003E-5,"YES"]
[null,"2015-12-10","16:09","KBR1A","RURAL","Weather","",577,134.4333333333004,0.19883223366600367,1.4790396751752054E-3,"YES"]
[null,"2015-12-10","15:40","JBB1B","RURAL","Weather","",162,464.87948717946921,0.1850108172399072,4.1525897292614037E-4,"YES"]
[null,"2015-12-11","16:48","PRG2A","RURAL","Weather","",118,342.19444444444423,0.10897036281330259,3.0247258521780605E-4,"NO"]
[null,"2015-12-11","20:22","IBL2","RURAL","Weather","",1,261.75,6.7095084051492114E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-11","08:03","BKD3A","URBAN","Planned","",6,53,3.1565061249122782E-4,5.9556719337967507E-6,"NO"]
[null,"2015-12-11","09:05","LGV2B","RURAL","Asset failure","LV",1,160.1666666667,4.1055954010504512E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-12","01:34","GCLSBK30","URBAN","Unknown","Unknown",11,240,2.6204956508705701E-3,1.0918731878627377E-5,"NO"]
[null,"2015-12-12","07:40","TGW2","RURAL","Weather","",1,157.94999999999999,4.0487749860298674E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-13","06:59","MTB13A","RURAL","Animal","Animal impact",47,76,9.1562040203220559E-3,1.2047636868844811E-4,"NO"]
[null,"2015-12-14","22:52","CSE7","URBAN","Asset failure","LV",1,131.9333333333,1.3095860841089767E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-14","08:04","CHL2","URBAN","Planned","",24,259,6.1700761234134332E-3,2.3822687735187003E-5,"NO"]
[null,"2015-12-15","09:30","CHL10","URBAN","Planned","",3,379,1.1285998314544844E-3,2.9778359668983753E-6,"NO"]
[null,"2015-12-15","08:22","CRY6A","RURAL","Planned","",245,39.033333333300057,2.4513523258753746E-2,6.2801511337595283E-4,"NO"]
[null,"2015-12-16","08:55","LTN3","URBAN","Planned","",14,295,4.0994875144300964E-3,1.3896567845525752E-5,"NO"]
[null,"2015-12-16","08:01","SPO32A","URBAN","Planned","",28,331,9.1995279137380478E-3,2.7793135691051504E-5,"NO"]
[null,"2015-12-16","08:25","MTNWLP5","RURAL","Planned","",1,81,2.0762948646307016E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-17","17:46","WNM3","URBAN","Overloads","",1,54.416666666700003,5.4014635732939736E-5,9.9261198896612504E-7,"NO"]
[null,"2015-12-17","08:16","RBY3","URBAN","Planned","",15,195,2.9033900677259161E-3,1.4889179834491876E-5,"NO"]
[null,"2015-12-18","10:45","AGE10","URBAN","Asset failure","LV",1,105.96666666669999,1.0518378376414347E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-18","08:16","GYN6A","RURAL","Planned","",129,256.125,8.4620550705171257E-2,3.3066918214488946E-4,"NO"]
[null,"2015-12-20","17:14","LTN4","URBAN","Overloads","",1,81.633333333300001,8.1030225365901601E-5,9.9261198896612504E-7,"NO"]
[null,"2015-12-21","10:37","CFD8A","URBAN","Asset failure","LV",1,26.433333333299998,2.6238043574971487E-5,9.9261198896612504E-7,"NO"]
[null,"2015-12-21","08:08","CPL25B","URBAN","Planned","",9,582,5.1993015982045631E-3,8.9335079006951264E-6,"NO"]
[null,"2015-12-22","10:23","OXL5B","URBAN","Asset failure","LV",1,128.36666666670001,1.2741829231698468E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-22","08:28","CFD8A","URBAN","Planned","",1,312,3.0969494055743105E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-23","15:19","NBR3B","URBAN","Asset failure","LV",1,206.3,2.0477585332371164E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-24","23:04","NMC16A","RURAL","Asset failure","LV",1,92.866666666699999,2.3804763345116093E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-24","18:52","MTB1B","RURAL","Asset failure","Distribution substation",40,147.30000000000001,1.5103122644943325E-2,1.0253307973484945E-4,"NO"]
[null,"2015-12-25","19:02","SMR15A","URBAN","Asset failure","LV",7,32,2.2234508552841203E-4,6.9482839227628759E-6,"NO"]
[null,"2015-12-27","19:29","RLB13B","RURAL","Weather","",4,92,9.4330433356061495E-4,1.0253307973484946E-5,"NO"]
[null,"2015-12-28","01:30","NBR12A","RURAL","Unknown","Unknown",469,97.872549019617637,0.11398773362590936,1.2022003598911102E-3,"NO"]
[null,"2015-12-29","19:27","CMD13A","URBAN","Asset failure","LV",1,145.6833333333,1.446070232591819E-4,9.9261198896612504E-7,"NO"]
[null,"2015-12-30","08:00","CPB8","RURAL","Planned","",7,243,4.3602192157244733E-3,1.7943288953598656E-5,"NO"]
[null,"2015-12-30","08:10","TBV4","RURAL","Planned","",1,155,3.9731568397254166E-4,2.5633269933712364E-6,"NO"]
[null,"2015-12-31","11:49","BHD3A","URBAN","Asset failure","LV",1,79.7,7.9111175520600179E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-02","05:01","AHL6A","URBAN","Asset failure","LV",1,150.6833333333,1.4957008320401252E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-03","21:16","DRD2A","RURAL","Asset failure","LV",1,110.8166666667,2.840593529821746E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-04","02:30","MFD9A","URBAN","Asset failure","LV",1,964.21666666670001,9.5709302329432036E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-05","09:09","SBK22A","RURAL","Planned","",21,228,1.2273209644261481E-2,5.3829866860795964E-5,"NO"]
[null,"2016-01-05","07:42","NSW22B","URBAN","Overloads","",1,51.15,5.0772103235617301E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-06","08:42","AMR1","RURAL","Planned","",6,193,2.9683326583238917E-3,1.5379961960227417E-5,"NO"]
[null,"2016-01-06","07:04","TWG14A","URBAN","Planned","",125,468,5.806780135451832E-2,1.2407649862076564E-4,"NO"]
[null,"2016-01-06","08:12","NBR12A","RURAL","Planned","",23,300,1.7686956254261532E-2,5.8956520847538435E-5,"NO"]
[null,"2016-01-07","09:45","MTB1B","RURAL","Planned","",1,88,2.2557277541666881E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-07","12:07","BBS8A","URBAN","Planned","",7,57,3.9605218359748393E-4,6.9482839227628759E-6,"NO"]
[null,"2016-01-08","09:52","UMG1B","URBAN","Planned","",46,208,9.4973115104278853E-3,4.566015149244176E-5,"NO"]
[null,"2016-01-08","08:03","LTA5A","URBAN","Planned","",36,202,7.2182743837616616E-3,3.5734031602780506E-5,"NO"]
[null,"2016-01-08","08:52","NBR12A","RURAL","Planned","",71,383,6.9704550930744028E-2,1.8199621652935778E-4,"NO"]
[null,"2016-01-09","22:49","LBH1B","RURAL","Asset failure","Distribution substation",12,45,1.3841965764204676E-3,3.0759923920454833E-5,"NO"]
[null,"2016-01-11","10:18","WSE3A","RURAL","Asset failure","LV",1,131.19999999999999,3.3630850153030617E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-11","21:31","SFD4","URBAN","Asset failure","LV",1,91.05,9.0377321595365686E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-11","18:16","RWD1","RURAL","Asset failure","HV",63,79.606666666683992,6.8904792908855775E-3,1.6148960058238782E-4,"NO"]
[null,"2016-01-12","08:12","TGW2","RURAL","Planned","",5,410,5.3471001081723995E-3,1.2816634966856181E-5,"NO"]
[null,"2016-01-12","06:22","KBR6A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",1,317.78333333329999,8.1458259637673727E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-13","10:04","BMT5","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",15,71.033333333300007,2.7312249114357706E-3,3.8449904900568543E-5,"NO"]
[null,"2016-01-13","04:33","IPL1","RURAL","Unknown","Unknown",1,83.35,2.1365330489749254E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-14","08:40","LWD1","RURAL","Animal","Animal nesting/burrowing, etc and other",698,7.43333333330001,1.3299736660813908E-2,1.789202241373123E-3,"NO"]
[null,"2016-01-14","08:37","TWT6B","RURAL","Planned","",56,199,2.8565716014129057E-2,1.4354631162878925E-4,"NO"]
[null,"2016-01-14","08:26","MGP13A","RURAL","Planned","",12,271,8.3359393824432599E-3,3.0759923920454833E-5,"NO"]
[null,"2016-01-15","09:05","GBN4","RURAL","Planned","",4,149,1.5277428880492569E-3,1.0253307973484946E-5,"NO"]
[null,"2016-01-15","19:41","RLB15A","URBAN","Asset failure","LV",1,117.25,1.1638375570627817E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-15","08:35","UMG5A","URBAN","Planned","",2,255,5.0623211437272376E-4,1.9852239779322501E-6,"NO"]
[null,"2016-01-16","04:54","EMD3","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",486,85.907142857142858,0.14658898076992091,1.2457769187784208E-3,"NO"]
[null,"2016-01-17","08:16","KVG2A","URBAN","Planned","",1,507,5.0325427840582548E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-17","07:39","CPL6A","URBAN","Planned","",1,291,2.8885008878914243E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-19","10:49","GYN13A","RURAL","Planned","",17,57,2.4838638565767282E-3,4.3576558887311021E-5,"NO"]
[null,"2016-01-19","09:10","SPEWSP29","URBAN","Planned","",1,365,3.6230337597263569E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-19","08:28","AHD21","URBAN","Asset failure","LV",1,46.05,4.5709782091890062E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-20","11:46","KSN14","URBAN","Asset failure","LV",1,73.733333333299996,7.3188590653069197E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-20","22:27","AHD25A","URBAN","Overloads","",1,80.283333333300007,7.9690199180797335E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-20","08:26","GYM3","URBAN","Planned","",35,342,1.1881565507924519E-2,3.4741419613814376E-5,"NO"]
[null,"2016-01-21","09:13","NBR5A","RURAL","Planned","",8,322,6.6031303349243049E-3,2.0506615946969891E-5,"NO"]
[null,"2016-01-21","08:15","KBN1B","RURAL","Planned","",36,244.1,2.3428808719413097E-2,9.2279771761364493E-5,"NO"]
[null,"2016-01-22","12:21","RBY2A","URBAN","Overloads","",1,52.766666666699997,5.2376825951145621E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-22","01:26","WMR1","RURAL","Unknown","Unknown",451,8.1911347517457482,9.4796958868539789E-3,1.1560604740104275E-3,"NO"]
[null,"2016-01-22","08:40","WRG6A","URBAN","Planned","",12,201,2.3941801173862939E-3,1.1911343867593501E-5,"NO"]
[null,"2016-01-23","05:07","MDR35A","URBAN","Planned","",1,720,7.1468063205561009E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-24","19:36","KLG16A","URBAN","Asset failure","LV",1,89.066666666700002,8.8408641150615968E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-25","17:11","RWD1","RURAL","Weather","",238,8.9666666667000019,5.4703106923407871E-3,6.1007182442235418E-4,"NO"]
[null,"2016-01-25","08:02","ARL13A","URBAN","Planned","",1,208,2.0646329370495404E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-26","01:16","LDR6","URBAN","Asset failure","LV",1,108.3,1.0749987840503135E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-27","09:54","MHL2A","RURAL","Planned","",2,359,1.8404687812405478E-3,5.1266539867424728E-6,"NO"]
[null,"2016-01-27","08:02","MMC33A","URBAN","Planned","",38,411,1.5502614043672942E-2,3.7719255580712758E-5,"NO"]
[null,"2016-01-28","10:15","TRP5","RURAL","Planned","",6,33,5.0753874468750478E-4,1.5379961960227417E-5,"NO"]
[null,"2016-01-28","09:02","BIS12B","RURAL","Planned","",1,416,1.0663440292424343E-3,2.5633269933712364E-6,"NO"]
[null,"2016-01-29","17:50","KLG10A","URBAN","Asset failure","LV",1,54.733333333300003,5.4328962862712832E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-29","17:14","NRG17A","URBAN","Weather","",1392,307.04126984129044,0.39222971754566754,1.381715888640846E-3,"NO"]
[null,"2016-01-29","20:21","SHW10A","URBAN","Unknown","Unknown",88,54.516666666699997,4.7620229300015986E-3,8.7349855029019016E-5,"NO"]
[null,"2016-01-29","08:35","TWT11A","RURAL","Planned","",8,148,3.0349791601515441E-3,2.0506615946969891E-5,"NO"]
[null,"2016-01-29","08:20","GYS3A","RURAL","Planned","",1,60,1.5379961960227417E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-29","16:50","CMD15A","URBAN","Overloads","",1,80.966666666699993,8.0368484039990341E-5,9.9261198896612504E-7,"NO"]
[null,"2016-01-30","17:44","BDT1","RURAL","Weather","",1,141,3.6142910606534436E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-30","18:15","COR23A","RURAL","Weather","",802,11.96971009456148,2.5679153486925194E-2,2.0557882486837357E-3,"NO"]
[null,"2016-01-30","18:51","GBN2","RURAL","Weather","",3,618.76666666669996,4.7583038977952827E-3,7.6899809801137083E-6,"NO"]
[null,"2016-01-30","06:23","CRY2A","RURAL","Asset failure","LV",1,200.73333333330001,5.1454517180263412E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-30","09:13","MTB2A","RURAL","Weather","",1,150.0666666667,3.8466993747199568E-4,2.5633269933712364E-6,"NO"]
[null,"2016-01-31","21:30","AHL15B","URBAN","Asset failure","LV",1,156.38333333329999,1.5522797154111944E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-31","17:57","TWG17","URBAN","Network business","Switching and protection error",114,107.0666666667,1.2115424892528709E-2,1.1315776674213826E-4,"NO"]
[null,"2016-01-31","08:35","RBY6","URBAN","Planned","",1,240,2.3822687735187002E-4,9.9261198896612504E-7,"NO"]
[null,"2016-01-31","08:20","NMK11A","URBAN","Planned","",2,115,2.2830075746220878E-4,1.9852239779322501E-6,"NO"]
[null,"2016-02-01","22:47","KRA4","URBAN","Animal","Other",282,2.2833333332999999,6.391428596859575E-4,2.7991658088844727E-4,"NO"]
[null,"2016-02-01","19:04","TWG11","URBAN","Asset failure","LV",1,91.833333333300004,9.1154867653356079E-5,9.9261198896612504E-7,"NO"]
[null,"2016-02-01","03:23","HPK5A","URBAN","Animal","Animal impact",115,57,6.5065715876729503E-3,1.1415037873110439E-4,"NO"]
[null,"2016-02-01","12:51","EMD2","RURAL","Asset failure","LV",1,171.8166666667,4.4042229957782006E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-02","18:00","BMT3","RURAL","Weather","",266,277.68235294117648,0.17643148995944813,6.8184498023674889E-4,"NO"]
[null,"2016-02-02","20:08","CHL8","URBAN","Other","Other System Failures",121,46.266666666699997,5.556906610766763E-3,1.2010605066490114E-4,"NO"]
[null,"2016-02-02","08:29","MTB3A","RURAL","Planned","",16,230,9.4330433356061491E-3,4.1013231893939782E-5,"NO"]
[null,"2016-02-02","02:20","CRB25A","RURAL","Weather","",1,202,5.1779205266098971E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-03","11:55","BDT3","RURAL","Planned","",10,85,2.178827944365551E-3,2.5633269933712362E-5,"NO"]
[null,"2016-02-03","15:34","CPK7","URBAN","Asset failure","LV",1,98.533333333300007,9.7805367979429117E-5,9.9261198896612504E-7,"NO"]
[null,"2016-02-03","08:26","YTA41A","RURAL","Planned","",1,3229,8.2769828615957223E-3,2.5633269933712364E-6,"NO"]
[null,"2016-02-03","08:36","AMR2","RURAL","Asset failure","LV",1,74,1.8968619750947151E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-04","06:04","MLS12B","URBAN","Asset failure","LV",1,79.966666666699993,7.9375872051024225E-5,9.9261198896612504E-7,"NO"]
[null,"2016-02-05","10:13","MGP13A","RURAL","Planned","",5,87,1.1150472421164878E-3,1.2816634966856181E-5,"NO"]
[null,"2016-02-05","09:15","LLY4","RURAL","Overloads","",1,140,3.588657790719731E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-05","01:57","THL1","RURAL","Animal","Animal impact",2,92.383333333300001,4.7361738414172122E-4,5.1266539867424728E-6,"NO"]
[null,"2016-02-06","21:19","MLY3","RURAL","Asset failure","LV",1,137.11666666670001,3.5147485290783816E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-06","02:05","BPN26A","RURAL","Asset failure","LV",6,84.366666666699999,1.2975561240450325E-3,1.5379961960227417E-5,"NO"]
[null,"2016-02-07","21:11","BIS15A","RURAL","Asset failure","LV",1,115.8333333333,2.969187100654161E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-08","18:32","LBH1B","RURAL","Third party","Vehicle impact",1031,209.09635416667965,0.66785750294352741,2.6427901301657453E-3,"NO"]
[null,"2016-02-08","08:35","CMA10A","RURAL","Planned","",5,653,8.3692626333570861E-3,1.2816634966856181E-5,"NO"]
[null,"2016-02-09","08:31","RLB13B","RURAL","Planned","",14,374,1.3421580137291793E-2,3.5886577907197311E-5,"NO"]
[null,"2016-02-09","20:10","LTN7","URBAN","Planned","",18,270,4.8240942663753681E-3,1.7867015801390249E-5,"NO"]
[null,"2016-02-09","14:45","WRD17A","URBAN","Asset failure","LV",26,25,6.4519779282798135E-4,2.5807911713119255E-5,"NO"]
[null,"2016-02-10","14:31","BRT5","URBAN","Asset failure","LV",1,61.7833333333,6.1326877384924007E-5,9.9261198896612504E-7,"NO"]
[null,"2016-02-11","01:31","PRG2B","RURAL","Unknown","Unknown",199,50.599999999999952,2.5811164827052341E-2,5.101020716808762E-4,"NO"]
[null,"2016-02-11","05:47","NIP2A","URBAN","Planned","",2,81,1.6080314221251227E-4,1.9852239779322501E-6,"NO"]
[null,"2016-02-11","15:42","JBB1B","RURAL","Overloads","",1,122.85,3.1490472113565636E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-12","11:00","MLB12A","RURAL","Planned","",53,10,1.3585633064867554E-3,1.3585633064867552E-4,"NO"]
[null,"2016-02-12","09:37","CNB26A","RURAL","Planned","",8,192,3.9372702618182187E-3,2.0506615946969891E-5,"NO"]
[null,"2016-02-13","23:34","ENG17A","URBAN","Asset failure","LV",106,131,1.3783410078783613E-2,1.0521687083040927E-4,"NO"]
[null,"2016-02-15","09:30","SBY3A","URBAN","Planned","",2,347,6.8887272034249083E-4,1.9852239779322501E-6,"NO"]
[null,"2016-02-15","08:14","KRN11","URBAN","Planned","",28,33,9.1717347780469964E-4,2.7793135691051504E-5,"NO"]
[null,"2016-02-16","13:33","BLN15A","URBAN","Unknown","Unknown",50,83,4.1193397542094194E-3,4.9630599448306258E-5,"NO"]
[null,"2016-02-16","08:06","MAI5","URBAN","Planned","",4,314,1.2467206581414532E-3,3.9704479558645002E-6,"NO"]
[null,"2016-02-16","09:07","IDY10A","URBAN","Planned","",15,31,4.6156457486924821E-4,1.4889179834491876E-5,"NO"]
[null,"2016-02-17","08:30","GYM2A","RURAL","Planned","",4,130,1.3329300365530429E-3,1.0253307973484946E-5,"NO"]
[null,"2016-02-17","12:15","BDT2","RURAL","Planned","",8,118,2.4197806817424471E-3,2.0506615946969891E-5,"NO"]
[null,"2016-02-18","08:01","KMR25A","RURAL","Planned","",19,383,1.8653330530762485E-2,4.8703212874053492E-5,"NO"]
[null,"2016-02-18","20:00","GBN4","RURAL","Weather","",10,279.63333333330002,7.1679167157962468E-3,2.5633269933712362E-5,"NO"]
[null,"2016-02-18","09:19","TWG10","URBAN","Planned","",22,126,2.7515204334140988E-3,2.1837463757254754E-5,"NO"]
[null,"2016-02-19","08:55","KRN18","URBAN","Planned","",7,274,1.9038297948370279E-3,6.9482839227628759E-6,"NO"]
[null,"2016-02-19","09:09","SMF11A","RURAL","Planned","",8,361,7.4028883568561304E-3,2.0506615946969891E-5,"NO"]
[null,"2016-02-20","20:18","MDR12B","URBAN","Planned","",23,558,1.2739182266391249E-2,2.2830075746220877E-5,"NO"]
[null,"2016-02-20","07:25","SGT4","URBAN","Asset failure","LV",1,16.899999999999999,1.6775142613527512E-5,9.9261198896612504E-7,"NO"]
[null,"2016-02-21","05:52","YTA34A","URBAN","Planned","",1,238,2.3624165337393779E-4,9.9261198896612504E-7,"NO"]
[null,"2016-02-22","20:15","MRE2","URBAN","Planned","",1,270,2.6800523702085377E-4,9.9261198896612504E-7,"NO"]
[null,"2016-02-22","08:03","NIP5A","URBAN","Planned","",40,51,2.0249284574908951E-3,3.9704479558645003E-5,"NO"]
[null,"2016-02-23","10:15","DRD2A","RURAL","Planned","",37,30,2.8452929626420721E-3,9.4843098754735753E-5,"NO"]
[null,"2016-02-23","16:17","ORE3","URBAN","Network business","Switching and protection error",1,5.2333333333000001,5.1946694088896349E-6,9.9261198896612504E-7,"NO"]
[null,"2016-02-23","21:59","BPN26A","RURAL","Asset failure","HV",45,75,8.6512286026279219E-3,1.1534971470170564E-4,"NO"]
[null,"2016-02-24","11:23","SBY11A","URBAN","Planned","",1,242,2.4021210132980228E-4,9.9261198896612504E-7,"NO"]
[null,"2016-02-24","12:18","BTN2","RURAL","Weather","",1,96.333333333300004,2.46933833694677E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-24","08:11","KVG32A","URBAN","Planned","",17,282,4.7585818751036037E-3,1.6874403812424127E-5,"NO"]
[null,"2016-02-25","08:39","AMR3","RURAL","Planned","",4,160,1.6405292757575912E-3,1.0253307973484946E-5,"NO"]
[null,"2016-02-25","08:48","KBN15A","URBAN","Planned","",5,204,1.0124642287454475E-3,4.9630599448306254E-6,"NO"]
[null,"2016-02-25","10:53","GBG33A","URBAN","Planned","",4,87,3.4542897216021154E-4,3.9704479558645002E-6,"NO"]
[null,"2016-02-26","08:46","TGW4","RURAL","Planned","",3,177,1.3611266334801265E-3,7.6899809801137083E-6,"NO"]
[null,"2016-02-26","15:48","TCB2","RURAL","Overloads","",1,108.5,2.7812097878077916E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-27","23:55","TWG21","URBAN","Animal","Animal impact",118,220,2.576820723356061E-2,1.1712821469800276E-4,"NO"]
[null,"2016-02-28","15:55","NRG9","RURAL","Asset failure","LV",1,53.833333333299997,1.3799243647639943E-4,2.5633269933712364E-6,"NO"]
[null,"2016-02-29","09:17","DRD5A","URBAN","Third party","Vehicle impact",164,186,3.0278636111422681E-2,1.6278836619044453E-4,"NO"]
[null,"2016-02-29","11:49","MAI17","URBAN","Asset failure","LV",1,66.45,6.5959066666799017E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-01","09:28","BMT1","RURAL","Planned","",7,261,4.6831984168892492E-3,1.7943288953598656E-5,"NO"]
[null,"2016-03-01","08:00","CMY1","RURAL","Planned","",52,285,3.7988506041761731E-2,1.3329300365530426E-4,"NO"]
[null,"2016-03-01","08:00","SFD4","URBAN","Planned","",21,100,2.0844851768288628E-3,2.0844851768288628E-5,"NO"]
[null,"2016-03-02","16:27","KWA1A","URBAN","Overloads","",1,74.366666666699999,7.3817244912813921E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-02","13:05","ESK5A","RURAL","Planned","",1,60,1.5379961960227417E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-02","08:03","GBG33A","URBAN","Planned","",16,342,5.4315728036226363E-3,1.5881791823458001E-5,"NO"]
[null,"2016-03-03","08:07","AGE6A","URBAN","Planned","",4,326,1.2943660336118272E-3,3.9704479558645002E-6,"NO"]
[null,"2016-03-03","08:20","CCY8A","RURAL","Planned","",58,11.00000004353933,3.1221322779261661E-3,1.4867296561553171E-4,"NO"]
[null,"2016-03-03","08:23","WNM5","URBAN","Planned","",38,193,7.2798163270775618E-3,3.7719255580712758E-5,"NO"]
[null,"2016-03-04","09:47","CPR21A","URBAN","Planned","",34,197,6.6485151020951056E-3,3.3748807624848254E-5,"NO"]
[null,"2016-03-04","08:07","SMF12A","RURAL","Planned","",19,106,5.1625405646496701E-3,4.8703212874053492E-5,"NO"]
[null,"2016-03-05","08:16","WCL17A","URBAN","Planned","",41,149,6.0638666405940589E-3,4.0697091547611133E-5,"NO"]
[null,"2016-03-06","15:42","LTN2","RURAL","Asset failure","LV",1,116.21666666669999,2.9790131874637927E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-07","07:51","BDT4","RURAL","Asset failure","LV",1,116.3833333333,2.9832853991177029E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-07","08:18","INA1A","URBAN","Asset failure","LV",1,94.466666666699993,9.3768745891033035E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-08","08:30","GYM8A","RURAL","Planned","",40,369,3.7834706422159449E-2,1.0253307973484945E-4,"NO"]
[null,"2016-03-08","18:59","MTB17A","RURAL","Asset failure","LV",1,90.533333333300007,2.3206653713312385E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-09","12:54","HPK3A","URBAN","Overloads","",1,81.3,8.0699354702945964E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-09","08:10","AGE16B","URBAN","Planned","",1,275,2.7296829696568442E-4,9.9261198896612504E-7,"NO"]
[null,"2016-03-09","08:05","PWC5","RURAL","Planned","",97,250.33333333333334,4.6557708180601766E-2,2.4864271835700993E-4,"NO"]
[null,"2016-03-10","19:15","WRG8A","URBAN","Overloads","",1,98.616666666699999,9.7888085645242453E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-11","10:20","MAI11","URBAN","Planned","",23,213,4.8628061339450468E-3,2.2830075746220877E-5,"NO"]
[null,"2016-03-11","08:01","WMD10A","URBAN","Overloads","",1,82.866666666699999,8.2254446819025995E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-11","08:50","CHL3","URBAN","Planned","",1,170,1.6874403812424128E-4,9.9261198896612504E-7,"NO"]
[null,"2016-03-12","12:38","LHM3","RURAL","Asset failure","LV",1,191.1666666667,4.9002267689955345E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-13","11:03","KRN12","URBAN","Animal","Animal nesting/burrowing, etc and other",1878,65.574561403542063,0.1221982782153061,1.8641253152783834E-3,"NO"]
[null,"2016-03-14","10:17","RBK11A","RURAL","Planned","",25,199,1.27525517920219E-2,6.4083174834280912E-5,"NO"]
[null,"2016-03-14","08:07","MGL2A","RURAL","Planned","",6,123,1.8917353211079725E-3,1.5379961960227417E-5,"NO"]
[null,"2016-03-15","09:29","SBY14A","URBAN","Planned","",16,183,2.9063679036928146E-3,1.5881791823458001E-5,"NO"]
[null,"2016-03-16","09:44","RPN5A","RURAL","Overloads","",1,82.25,2.1083364520478419E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-16","08:14","STT13A","RURAL","Planned","",1,556,1.4252098083144074E-3,2.5633269933712364E-6,"NO"]
[null,"2016-03-16","09:30","BSEENG15","URBAN","Planned","",8,195,1.5484747027871553E-3,7.9408959117290003E-6,"NO"]
[null,"2016-03-17","10:38","CLD11","RURAL","Asset failure","LV",1,40.916666666700003,1.0488279614552521E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-17","18:02","AGT25A","RURAL","Planned","",1,147,3.7680906802557175E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-18","08:38","TWT6B","RURAL","Planned","",16,113,4.6344952040151951E-3,4.1013231893939782E-5,"NO"]
[null,"2016-03-18","13:42","PWC3","RURAL","Asset failure","LV",1,176.8333333333,4.5328165666106156E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-18","08:22","LBH3A","RURAL","Planned","",121,410.45999999999992,0.12774352888100526,3.1016256619791961E-4,"NO"]
[null,"2016-03-19","16:53","FDS4","RURAL","Weather","",3,283,2.1762646173721797E-3,7.6899809801137083E-6,"NO"]
[null,"2016-03-19","10:08","ARG9A","URBAN","Planned","",23,69,1.5752752264892407E-3,2.2830075746220877E-5,"NO"]
[null,"2016-03-20","08:02","WMD8B","RURAL","Planned","",189,201,9.7378229151179899E-2,4.8446880174716361E-4,"NO"]
[null,"2016-03-21","08:20","OXL8B","URBAN","Planned","",12,250,2.9778359668983755E-3,1.1911343867593501E-5,"NO"]
[null,"2016-03-22","08:09","CLM9","URBAN","Planned","",58,216,1.2435442997767616E-2,5.7571495360035253E-5,"NO"]
[null,"2016-03-22","09:29","SMR10B","URBAN","Planned","",65,207,1.3355594311539213E-2,6.4519779282798132E-5,"NO"]
[null,"2016-03-22","09:20","BPN3","URBAN","Planned","",74,215,1.5792456744451049E-2,7.3453287183493257E-5,"NO"]
[null,"2016-03-23","08:35","PBH2B","URBAN","Planned","",22,325,7.0971757211077948E-3,2.1837463757254754E-5,"NO"]
[null,"2016-03-23","19:53","KCY4","RURAL","Asset failure","LV",1,115.75,2.9670509948272059E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-24","08:01","BNH2B","RURAL","Planned","",15,150,5.7674857350852819E-3,3.8449904900568543E-5,"NO"]
[null,"2016-03-24","07:48","JBB16A","RURAL","Overloads","",1,101.28333333330001,2.5962230231186466E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-24","11:00","ZMR3","URBAN","Planned","",9,185,1.6526989616285983E-3,8.9335079006951264E-6,"NO"]
[null,"2016-03-27","22:17","SMR9A","URBAN","Animal","Animal impact",123,71,8.6684804996411714E-3,1.2209127464283339E-4,"NO"]
[null,"2016-03-27","02:15","BLH12B","URBAN","Third party","Vehicle impact",57,95,5.3749939202515674E-3,5.657888337106913E-5,"NO"]
[null,"2016-03-29","16:26","RLB13B","RURAL","Asset failure","LV",1,51.2,1.312423420606073E-4,2.5633269933712364E-6,"NO"]
[null,"2016-03-29","08:15","SPO41A","URBAN","Planned","",17,347,5.8554181229111719E-3,1.6874403812424127E-5,"NO"]
[null,"2016-03-30","08:56","CMY4","RURAL","Planned","",12,215,6.6133836428977901E-3,3.0759923920454833E-5,"NO"]
[null,"2016-03-30","15:51","BPN34A","URBAN","Overloads","",1,98.683333333299998,9.7954259777774031E-5,9.9261198896612504E-7,"NO"]
[null,"2016-03-30","20:22","GCLSBK30","URBAN","Unknown","Unknown",11,52.25,5.7050374065828046E-4,1.0918731878627377E-5,"NO"]
[null,"2016-03-31","08:26","MTG8A","URBAN","Planned","",35,317,1.1013030017579159E-2,3.4741419613814376E-5,"NO"]
[null,"2016-04-01","09:24","KBR6A","RURAL","Planned","",2,228,1.1688771089772838E-3,5.1266539867424728E-6,"NO"]
[null,"2016-04-01","08:05","CSE2","URBAN","Planned","",24,91.2,2.5440645277201783E-3,2.3822687735187006E-5,"NO"]
[null,"2016-04-01","08:27","LWD1","RURAL","Planned","",23,345,2.0339999692400759E-2,5.8956520847538435E-5,"NO"]
[null,"2016-04-02","10:44","BBS8A","URBAN","Asset failure","LV",1,9.0833333333000006,9.016225566409216E-6,9.9261198896612504E-7,"NO"]
[null,"2016-04-04","09:16","RCN4A","URBAN","Planned","",13,218,2.8130623767299986E-3,1.2903955856559627E-5,"NO"]
[null,"2016-04-04","17:56","AGT37A","URBAN","Asset failure","LV",1,103.3,1.0253681846020072E-4,9.9261198896612504E-7,"NO"]
[null,"2016-04-05","09:53","MGP4","RURAL","Planned","",8,54,1.107357261136374E-3,2.0506615946969891E-5,"NO"]
[null,"2016-04-05","14:52","CMY4","RURAL","Asset failure","HV",1,73,1.8712287051610025E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-05","08:25","INA10A","RURAL","Planned","",7,230,4.1269564593276907E-3,1.7943288953598656E-5,"NO"]
[null,"2016-04-06","12:36","BHD23A","RURAL","Third party","Unauthorised access",1236,70.112121212149006,0.2224717478644179,3.168272163806848E-3,"NO"]
[null,"2016-04-07","09:20","JDL5A","URBAN","Planned","",5,290,1.4392873840008815E-3,4.9630599448306254E-6,"NO"]
[null,"2016-04-07","08:05","BHD5A","URBAN","Planned","",20,292,5.7968540155621711E-3,1.9852239779322505E-5,"NO"]
[null,"2016-04-08","09:39","VSL1A","URBAN","Planned","",65,131,8.4520910860465554E-3,6.4519779282798132E-5,"NO"]
[null,"2016-04-08","20:03","NMC2A","RURAL","Overloads","",1,109.1,2.7965897497680189E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-08","08:04","SGT6","URBAN","Planned","",8,51,4.0498569149817904E-4,7.9408959117290003E-6,"NO"]
[null,"2016-04-10","08:01","GVN5A","RURAL","Planned","",11,380.33333333333331,1.0430177536027561E-2,2.8196596927083598E-5,"NO"]
[null,"2016-04-11","13:18","PBH2B","URBAN","Planned","",24,103,2.4537368367242613E-3,2.3822687735187003E-5,"NO"]
[null,"2016-04-11","08:37","PBH2B","URBAN","Planned","",37,220,8.079861590184258E-3,3.6726643591746628E-5,"NO"]
[null,"2016-04-12","17:02","NVL5","RURAL","Overloads","",1,136.44999999999999,3.4976596824550519E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-12","08:21","SMF12A","RURAL","Planned","",192,414.08333333333331,0.20388959237974147,4.9215878272727744E-4,"NO"]
[null,"2016-04-12","08:25","MAI11","URBAN","Planned","",76,349,2.6328040395337503E-2,7.5438511161425516E-5,"NO"]
[null,"2016-04-13","08:02","MRE3","URBAN","Planned","",2,323,6.4122734487211683E-4,1.9852239779322501E-6,"NO"]
[null,"2016-04-14","10:01","HPE3A","URBAN","Asset failure","LV",1,449.7,4.4637761143806644E-4,9.9261198896612504E-7,"NO"]
[null,"2016-04-14","12:42","CMA8A","RURAL","Asset failure","LV",1,79.5,2.037844959730133E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-14","08:40","VPT16A","URBAN","Planned","",1,50,4.9630599448306258E-5,9.9261198896612504E-7,"NO"]
[null,"2016-04-15","18:42","MLT24A","URBAN","Network business","Network error",144,92.166666666699996,1.3173946317563178E-2,1.4293612641112202E-4,"NO"]
[null,"2016-04-15","08:01","LHM1A","URBAN","Planned","",248,373,9.1820579427322455E-2,2.4616777326359903E-4,"NO"]
[null,"2016-04-16","08:16","TGW2","RURAL","Asset failure","LV",1,141,3.6142910606534436E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-17","21:43","NVL24A","URBAN","Unknown","Unknown",116,81.05,9.3323393978617143E-3,1.1514299072007052E-4,"NO"]
[null,"2016-04-18","17:46","BKD3A","URBAN","Asset failure","LV",1,237.61666666670001,2.3586115211153387E-4,9.9261198896612504E-7,"NO"]
[null,"2016-04-18","08:18","BGY6A","URBAN","Planned","",28,184,5.1139369671534766E-3,2.7793135691051504E-5,"NO"]
[null,"2016-04-19","08:52","SBH6","URBAN","Planned","",7,138,9.5886318134127686E-4,6.9482839227628759E-6,"NO"]
[null,"2016-04-19","08:32","KSN8","RURAL","Planned","",11,200,5.6393193854167196E-3,2.8196596927083601E-5,"NO"]
[null,"2016-04-20","17:20","CMV11A","URBAN","Asset failure","LV",1,104.2333333333,1.0346325631653601E-4,9.9261198896612504E-7,"NO"]
[null,"2016-04-20","08:28","BHD1A","URBAN","Planned","",22,101,2.20558383948273E-3,2.1837463757254754E-5,"NO"]
[null,"2016-04-21","08:58","PGN2B","RURAL","Planned","",13,52,1.7328090475189559E-3,3.3323250913826072E-5,"NO"]
[null,"2016-04-21","08:01","NBR5A","RURAL","Planned","",150,301.57575757575756,0.11845134036368485,3.8449904900568547E-4,"NO"]
[null,"2016-04-21","08:37","CRM13A","URBAN","Planned","",19,226,4.2622758806205412E-3,1.8859627790356379E-5,"NO"]
[null,"2016-04-22","22:01","RBA35A","URBAN","Planned","",1,279,2.7693874492154893E-4,9.9261198896612504E-7,"NO"]
[null,"2016-04-23","14:12","HIS5B","URBAN","Planned","",5,93,4.6156457486924821E-4,4.9630599448306254E-6,"NO"]
[null,"2016-04-25","15:47","BWH13A","RURAL","Weather","",5,117.95,1.5117220943406866E-3,1.2816634966856181E-5,"NO"]
[null,"2016-04-25","13:08","LHM1A","URBAN","Overloads","",1,336,3.3351762829261804E-4,9.9261198896612504E-7,"NO"]
[null,"2016-04-26","08:22","GYM4","RURAL","Planned","",12,163,5.0138675990341382E-3,3.0759923920454833E-5,"NO"]
[null,"2016-04-27","10:10","CRY2A","RURAL","Planned","",9,95,2.1916445793324071E-3,2.3069942940341127E-5,"NO"]
[null,"2016-04-27","20:08","MLB3A","RURAL","Asset failure","LV",1,188.5666666667,4.8335802671678826E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-27","08:36","BNH1B","RURAL","Planned","",1,285,7.3054819311080233E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-28","18:42","ALY3A","URBAN","Asset failure","LV",1,53.85,5.3452155605825841E-5,9.9261198896612504E-7,"NO"]
[null,"2016-04-28","08:58","KWA12A","URBAN","Planned","",42,306,1.275704928219264E-2,4.1689703536577256E-5,"NO"]
[null,"2016-04-29","15:23","WMD2A","URBAN","Third party","Vehicle impact",120,323,3.8473640692327005E-2,1.1911343867593501E-4,"NO"]
[null,"2016-04-29","07:23","NIP4A","RURAL","Asset failure","LV",1,144.11666666670001,3.6941814186143682E-4,2.5633269933712364E-6,"NO"]
[null,"2016-04-30","08:04","DBY9","URBAN","Third party","Vehicle impact",1556,178.21666666667193,0.24359042314718951,1.5445042548312903E-3,"NO"]
[null,"2016-05-01","12:18","PRG1","RURAL","Overloads","",1,435.68333333330003,1.1167988488952061E-3,2.5633269933712364E-6,"NO"]
[null,"2016-05-02","11:27","MCW11","RURAL","Asset failure","LV",30,93,7.1516823115057495E-3,7.68998098011371E-5,"NO"]
[null,"2016-05-03","11:06","AGE8","URBAN","Planned","",6,31,1.8462582994769927E-4,5.9556719337967507E-6,"NO"]
[null,"2016-05-03","09:25","SBH11","URBAN","Planned","",22,280,6.1144898520313308E-3,2.1837463757254754E-5,"NO"]
[null,"2016-05-04","08:15","KBR6A","RURAL","Planned","",4,219,2.245474446193203E-3,1.0253307973484946E-5,"NO"]
[null,"2016-05-04","07:49","CBT8A","RURAL","Planned","",4,86,8.8178448571970527E-4,1.0253307973484946E-5,"NO"]
[null,"2016-05-05","08:55","MRK9","URBAN","Planned","",29,140,4.0300046752024679E-3,2.878574768001763E-5,"NO"]
[null,"2016-05-05","08:05","BLH12A","RURAL","Planned","",24,220,1.3534366525000128E-2,6.1519847840909667E-5,"NO"]
[null,"2016-05-06","09:32","NBR11A","RURAL","Planned","",23,214,1.2616695461373225E-2,5.8956520847538441E-5,"NO"]
[null,"2016-05-06","08:54","LRE6A","RURAL","Planned","",1,151,3.8706237599905668E-4,2.5633269933712364E-6,"NO"]
[null,"2016-05-08","07:20","AHD15B","URBAN","Planned","",1,255,2.5311605718636188E-4,9.9261198896612504E-7,"NO"]
[null,"2016-05-09","17:12","HPE3A","URBAN","Asset failure","LV",1,71.033333333300007,7.0508538282860678E-5,9.9261198896612504E-7,"NO"]
[null,"2016-05-09","09:02","AGE3","URBAN","Planned","",16,273,4.3357291678040345E-3,1.5881791823458001E-5,"NO"]
[null,"2016-05-10","14:11","GGR1","RURAL","Asset failure","LV",1,25.2833333333,6.4809450815650648E-5,2.5633269933712364E-6,"NO"]
[null,"2016-05-10","06:26","439","URBAN","Unknown","Unknown",1,4.8333333332999997,4.7976246133031843E-6,9.9261198896612504E-7,"NO"]
[null,"2016-05-11","10:19","NBR12A","RURAL","Unknown","Unknown",2,175.98333333330001,9.0220565743339201E-4,5.1266539867424728E-6,"NO"]
[null,"2016-05-12","09:23","BHD23A","RURAL","Planned","",27,57,3.9449602427983326E-3,6.9209828821023377E-5,"NO"]
[null,"2016-05-12","08:00","CRB22A","URBAN","Planned","",85,427,3.6026852139525514E-2,8.4372019062120641E-5,"NO"]
[null,"2016-05-12","08:03","DBY8A","URBAN","Planned","",23,241,5.502048254839232E-3,2.2830075746220877E-5,"NO"]
[null,"2016-05-13","09:54","KLG13A","URBAN","Asset failure","LV",1,33.683333333299998,3.3434480494975892E-5,9.9261198896612504E-7,"NO"]
[null,"2016-05-13","08:37","AHD15B","URBAN","Planned","",3,128,3.8116300376299204E-4,2.9778359668983753E-6,"NO"]
[null,"2016-05-14","18:00","HTN28A","URBAN","Asset failure","LV",1,23.833333333300001,2.3657252403659562E-5,9.9261198896612504E-7,"NO"]
[null,"2016-05-15","23:40","BDL7","URBAN","Third party","Vehicle impact",9,346,3.0909937336405136E-3,8.9335079006951264E-6,"NO"]
[null,"2016-05-16","11:52","MGP17A","RURAL","Overloads","",1,116.6833333333,2.9909753800978165E-4,2.5633269933712364E-6,"NO"]
[null,"2016-05-16","08:10","CPR21A","URBAN","Planned","",3,345,1.0273534085799396E-3,2.9778359668983753E-6,"NO"]
[null,"2016-05-17","09:10","MTB17A","RURAL","Planned","",20,260,1.3329300365530429E-2,5.1266539867424725E-5,"NO"]
[null,"2016-05-17","22:11","HMRHTN7","URBAN","Planned","",75,152,1.1315776674213827E-2,7.4445899172459386E-5,"NO"]
[null,"2016-05-18","18:00","ALY3A","URBAN","Overloads","",1,60.483333333300003,6.0036481799268049E-5,9.9261198896612504E-7,"NO"]
[null,"2016-05-18","08:30","IBL2","RURAL","Planned","",61,233.0344827586207,3.6737602468996565E-2,1.5636294659564541E-4,"NO"]
[null,"2016-05-18","08:30","STL1A","URBAN","Animal","Animal impact",43,95,4.0548199749266215E-3,4.2682315525543378E-5,"NO"]
[null,"2016-05-19","08:05","SGT26A","RURAL","Planned","",7,336,6.028945088409148E-3,1.7943288953598656E-5,"NO"]
[null,"2016-05-20","08:00","BRT3","URBAN","Asset failure","LV",6,104,6.1938988111486209E-4,5.9556719337967507E-6,"NO"]
[null,"2016-05-20","06:01","GYM7A","RURAL","Asset failure","LV",1,83.116666666699999,2.1305519526579138E-4,2.5633269933712364E-6,"NO"]
[null,"2016-05-20","08:26","CBW6","RURAL","Planned","",4,102,1.0458374132954645E-3,1.0253307973484946E-5,"NO"]
[null,"2016-05-22","10:57","YTA33A","RURAL","Planned","",2,60,3.0759923920454835E-4,5.1266539867424728E-6,"NO"]
[null,"2016-05-22","08:01","GYM8B","URBAN","Planned","",42,260,8.1473592054339562E-3,4.1689703536577256E-5,"NO"]
[null,"2016-05-23","15:29","BIS16A","URBAN","Asset failure","LV",1,172.3333333333,1.7106013276512914E-4,9.9261198896612504E-7,"NO"]
[null,"2016-05-24","08:02","AGT31A","RURAL","Planned","",150,358.88333333333327,0.1364576871613204,3.8449904900568547E-4,"NO"]
[null,"2016-05-24","09:38","BLH12A","RURAL","Planned","",44,398,4.4888982307917089E-2,1.127863877083344E-4,"NO"]
[null,"2016-05-25","09:14","SPO67B","URBAN","Planned","",2,295,5.856410734900138E-4,1.9852239779322501E-6,"NO"]
[null,"2016-05-25","08:14","CCY13A","URBAN","Planned","",30,85,2.5311605718636191E-3,2.9778359668983753E-5,"NO"]
[null,"2016-05-25","08:05","BDT4","RURAL","Planned","",3,386,2.9683326583238917E-3,7.6899809801137083E-6,"NO"]
[null,"2016-05-26","13:23","EMP21A","RURAL","Planned","",6,77,1.1842570709375113E-3,1.5379961960227417E-5,"NO"]
[null,"2016-05-26","08:00","MTG11A","URBAN","Planned","",1,440,4.3674927514509508E-4,9.9261198896612504E-7,"NO"]
[null,"2016-05-27","11:13","CPB8","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",346,64.961111111138123,6.6874936984899686E-2,8.8691113970644801E-4,"NO"]
[null,"2016-05-27","08:22","WRD15A","URBAN","Planned","",74,264,1.9391667816442221E-2,7.3453287183493257E-5,"NO"]
[null,"2016-05-27","13:56","RBY12","URBAN","Asset failure","LV",1,16.116666666699999,1.5997596555537136E-5,9.9261198896612504E-7,"NO"]
[null,"2016-05-28","13:12","LHM8A","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",471,66.683333333299984,8.0508589708714537E-2,1.2073270138778522E-3,"NO"]
[null,"2016-05-29","08:10","JHDMDH11","URBAN","Planned","",1,377,3.7421471984022919E-4,9.9261198896612504E-7,"NO"]
[null,"2016-05-30","08:03","SFD9","URBAN","Planned","",8,217,1.7231744128451932E-3,7.9408959117290003E-6,"NO"]
[null,"2016-05-31","09:30","KLG7A","URBAN","Planned","",43,286,1.2207142240305406E-2,4.2682315525543378E-5,"NO"]
[null,"2016-05-31","12:09","WMD6A","URBAN","Asset failure","LV",1,89.766666666700004,8.9103469542892256E-5,9.9261198896612504E-7,"NO"]
[null,"2016-05-31","08:23","PWC6","RURAL","Planned","",13,155,5.1651038916430414E-3,3.3323250913826072E-5,"NO"]
[null,"2016-06-01","17:30","CPS5A","URBAN","Asset failure","LV",1,143.15,1.4209240622050081E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-01","09:02","BIS1A","URBAN","Planned","",67,163,1.0840315531499053E-2,6.6505003260730378E-5,"NO"]
[null,"2016-06-02","10:00","RIS4","RURAL","Planned","",30,180,1.3841965764204676E-2,7.6899809801137087E-5,"NO"]
[null,"2016-06-02","08:31","SMF5A","RURAL","Planned","",9,87,2.0070850358096782E-3,2.3069942940341127E-5,"NO"]
[null,"2016-06-03","23:47","NMC15A","RURAL","Weather","",401,122.83377192981844,0.12539791379359708,1.0278941243418657E-3,"NO"]
[null,"2016-06-03","08:19","WFD2B","RURAL","Planned","",14,219,7.8591605616762112E-3,3.5886577907197311E-5,"NO"]
[null,"2016-06-04","14:09","VPT16A","URBAN","Asset failure","LV",1,54.65,5.4246245196998734E-5,9.9261198896612504E-7,"NO"]
[null,"2016-06-04","23:29","PBH4","URBAN","Asset failure","LV",1,112.6833333333,1.1185082762329978E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-04","17:03","BSEENG15","URBAN","Asset failure","LV",1,123.25,1.2233942764007492E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-04","01:46","NRG16A","RURAL","Weather","",666,81.155072463773877,0.11993392597454049,1.7071757775852432E-3,"NO"]
[null,"2016-06-04","08:58","SHW5A","URBAN","Overloads","",1,204.95,2.0343582713860733E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-05","17:03","LTN9","URBAN","Third party","Vehicle impact",1612,97.000537634425797,0.16942948633325561,1.6000905262133936E-3,"NO"]
[null,"2016-06-05","20:33","CPK13","RURAL","Asset failure","LV",1,11.166666666699999,2.8623818092730915E-5,2.5633269933712364E-6,"NO"]
[null,"2016-06-05","05:10","NSW31A","URBAN","Planned","",2,74,1.4690657436698651E-4,1.9852239779322501E-6,"NO"]
[null,"2016-06-06","17:53","RBY9A","URBAN","Asset failure","LV",16,637,1.0116701391542747E-2,1.5881791823458001E-5,"NO"]
[null,"2016-06-06","14:57","PWC5","RURAL","Overloads","",1,484.6666666667,1.2423591494540114E-3,2.5633269933712364E-6,"NO"]
[null,"2016-06-06","01:23","NBR7A","RURAL","Weather","",526,132.79702380955717,0.15291980033396099,1.3483099985132701E-3,"NO"]
[null,"2016-06-07","09:35","BHD35A","RURAL","Planned","",1,146,3.7424574103220049E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-07","08:48","BDT6","URBAN","Asset failure","LV",1,119.9333333333,1.1904726454330419E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-08","09:51","MLS9B","URBAN","Asset failure","Zone substation",1823,37.933333333299991,6.8641567479853366E-2,1.8095316558852466E-3,"NO"]
[null,"2016-06-08","15:34","DRD16A","URBAN","Overloads","",1,115.71666666669999,1.1486175065656319E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-08","06:52","COR26A","RURAL","Weather","",2,117.6833333333,6.0332173000630582E-4,5.1266539867424728E-6,"NO"]
[null,"2016-06-09","19:23","MDR12B","URBAN","Asset failure","LV",1,457,4.5362367895751917E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-09","17:08","SBK22A","RURAL","Asset failure","LV",1,19.0333333333,4.8788657107080419E-5,2.5633269933712364E-6,"NO"]
[null,"2016-06-10","09:35","CLD28A","RURAL","Planned","",2,210,1.0765973372159194E-3,5.1266539867424728E-6,"NO"]
[null,"2016-06-10","05:13","CCY14B","URBAN","Asset failure","LV",1,110.6833333333,1.0986560364536753E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-10","08:25","AHL9A","URBAN","Planned","",20,306,6.0747853724726856E-3,1.9852239779322502E-5,"NO"]
[null,"2016-06-11","12:00","PWC5","RURAL","Vegetation","Blow-in/Fall-in - NSP responsibility",12,29.583333333300001,9.0998108264576352E-4,3.0759923920454833E-5,"NO"]
[null,"2016-06-12","08:45","INA7A","RURAL","Planned","",1,317,8.1257465689868198E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-13","08:38","BWH16A","RURAL","Planned","",17,305,1.3290850460629861E-2,4.3576558887311021E-5,"NO"]
[null,"2016-06-13","07:36","MFN1B","URBAN","Network business","Network error",585,1.8833333333000004,1.0936102588240725E-3,5.8067801354518326E-4,"NO"]
[null,"2016-06-14","15:15","GYM4","RURAL","Asset failure","LV",1,289.8333333333,7.4293760691201125E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-14","08:28","MHL2A","RURAL","Planned","",21,307,1.6525769126264363E-2,5.3829866860795957E-5,"NO"]
[null,"2016-06-14","10:08","WRD19A","URBAN","Planned","",4,279,1.1077549796861957E-3,3.9704479558645002E-6,"NO"]
[null,"2016-06-15","08:02","KBR5A","RURAL","Planned","",20,400,2.050661594696989E-2,5.1266539867424731E-5,"NO"]
[null,"2016-06-15","08:47","AHL9A","URBAN","Planned","",45,272,1.2149570744945371E-2,4.4667539503475631E-5,"NO"]
[null,"2016-06-16","08:06","MRK3","URBAN","Planned","",20,279,5.5387748984309778E-3,1.9852239779322502E-5,"NO"]
[null,"2016-06-16","10:02","BHD44A","URBAN","Planned","",8,214,1.6993517251100063E-3,7.9408959117290003E-6,"NO"]
[null,"2016-06-17","08:28","SFD5","URBAN","Planned","",59,294,1.7217847560606406E-2,5.8564107349001382E-5,"NO"]
[null,"2016-06-17","09:38","KVG32A","URBAN","Planned","",11,224,2.4457959408125322E-3,1.0918731878627377E-5,"NO"]
[null,"2016-06-18","22:36","MDH3A","URBAN","Unknown","Unknown",79,70.683333333299984,5.5427288028510819E-3,7.8416347128323864E-5,"NO"]
[null,"2016-06-19","11:36","BHD35A","RURAL","Asset failure","LV",1,111.4833333333,2.8576823764425122E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-20","16:48","BLN15A","URBAN","Overloads","",1,185.1833333333,1.8381519682334385E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-20","09:30","TWG11","URBAN","Asset failure","LV",1,158.01666666669999,1.5684923778983028E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-20","09:22","SMF12A","RURAL","Planned","",7,77,1.3816332494270963E-3,1.7943288953598656E-5,"NO"]
[null,"2016-06-20","12:42","KBN5A","RURAL","Third party","Vehicle impact",35,130.69880952377861,1.1689625532101827E-2,8.9716444767993261E-5,"NO"]
[null,"2016-06-21","11:53","CPC2B","URBAN","Asset failure","HV",1781,93.196874999999963,0.1362074578909179,1.7678419523486685E-3,"NO"]
[null,"2016-06-21","16:22","HPE12A","URBAN","Asset failure","LV",1,102.9166666667,1.021563171977968E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-21","08:38","CRB24B","URBAN","Planned","",5,421,2.0894482367736934E-3,4.9630599448306254E-6,"NO"]
[null,"2016-06-22","08:20","IPL1","RURAL","Planned","",70,417.20959595957277,7.4723246128944834E-2,1.794328895359865E-4,"NO"]
[null,"2016-06-22","09:50","COR22A","RURAL","Planned","",9,228,5.2599469903977774E-3,2.3069942940341127E-5,"NO"]
[null,"2016-06-22","08:52","SFD7A","URBAN","Planned","",36,230,8.2188272686395166E-3,3.5734031602780506E-5,"NO"]
[null,"2016-06-23","02:50","NGE2A","URBAN","Asset failure","LV",1,77.583333333300004,7.7010146810588788E-5,9.9261198896612504E-7,"NO"]
[null,"2016-06-24","23:04","SMF3A","RURAL","Weather","",714,278.87906504064017,0.61879674867600165,1.830215473267063E-3,"YES"]
[null,"2016-06-24","23:45","MTB3A","RURAL","Weather","",320,484.24777777780662,0.37627863022643615,8.202646378787957E-4,"YES"]
[null,"2016-06-24","08:42","ARG5A","URBAN","Planned","",2,206,4.0895613945404356E-4,1.9852239779322501E-6,"YES"]
[null,"2016-06-24","22:28","SMF12A","RURAL","Weather","",462,1178.063333333334,1.7783327095904338,1.1842570709375113E-3,"YES"]
[null,"2016-06-24","20:07","NIP6A","URBAN","Overloads","",1,72.650000000000006,7.211326099838899E-5,9.9261198896612504E-7,"YES"]
[null,"2016-06-25","10:08","CBW6","RURAL","Asset failure","LV",1,263.25,6.74795831004978E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-25","18:04","NRA1A","RURAL","Overloads","",1,325.88333333330002,8.3534554502304431E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-25","14:36","NRA1A","RURAL","Overloads","",1,494.1666666667,1.266710755891038E-3,2.5633269933712364E-6,"NO"]
[null,"2016-06-26","06:18","CPS1B","URBAN","Planned","",1,351,3.4840680812710993E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-26","11:24","SPO51A","URBAN","Asset failure","LV",1,113.6666666667,1.1282689607918264E-4,9.9261198896612504E-7,"NO"]
[null,"2016-06-27","09:33","AFD18A","URBAN","Asset failure","LV",1,39.5,3.9208173564161945E-5,9.9261198896612504E-7,"NO"]
[null,"2016-06-27","18:02","RBY9A","URBAN","Asset failure","LV",1,68.3,6.7795398846386349E-5,9.9261198896612504E-7,"NO"]
[null,"2016-06-28","09:35","BNH1B","RURAL","Asset failure","HV",13,85,2.8324763276752164E-3,3.3323250913826079E-5,"NO"]
[null,"2016-06-28","08:59","GBG2A","URBAN","Planned","",4,482,1.9137559147266892E-3,3.9704479558645002E-6,"NO"]
[null,"2016-06-28","08:03","BBSRDL12","RURAL","Planned","",2,219,1.1227372230966015E-3,5.1266539867424728E-6,"NO"]
[null,"2016-06-28","17:36","WMR1","RURAL","Asset failure","LV",1,123.6833333333,3.170408269633803E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-29","19:48","CRY2A","RURAL","Asset failure","LV",9,252.88333333329999,5.8340040705624971E-3,2.3069942940341127E-5,"NO"]
[null,"2016-06-29","09:10","CPS2B","URBAN","Planned","",24,206,4.9074736734485225E-3,2.3822687735187003E-5,"NO"]
[null,"2016-06-30","09:49","RLB13B","RURAL","Planned","",5,176,2.2557277541666882E-3,1.2816634966856181E-5,"NO"]
[null,"2016-06-30","15:15","KSN8","RURAL","Asset failure","LV",1,186.51666666669999,4.7810320638037721E-4,2.5633269933712364E-6,"NO"]
[null,"2016-06-30","08:07","WMD10A","URBAN","Planned","",1,137,1.3598784248835914E-4,9.9261198896612504E-7,"NO"]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]

{"sheet":"Amendments","index":24,"n_rows":3,"n_cols":4,"rows_kept":3,"cut":false,"hidden":false,"merged":[[1,1,1,3]]}
[null,"This sheet may be used to identify amendments made to data resubmitted to the AER."]
[null,"NSP data amendments"]
[null,"Worksheet","Table","Comments"]