{"text_format":"1","workbook":"xlsx","n_sheets":26,"sheets":["AER only","Instructions","Contents","Business & other details","2.1 Expenditure summary","2.2 Repex","2.3(a) Augex","2.3(b) Augex","2.5 Connections","2.6 Non-network","2.7 Vegetation management","2.8 Maintenance","2.9 Emergency Response","2.10 Overheads","2.10(A) Overheads","2.11 Labour","2.12 Input tables","4.1 Public lighting","4.2 Metering","4.3 Fee-based services","4.4 Quoted services","5.2 Asset Age Profile","5.3 MD - Network level","5.4 MD & utilisation-Spatial","6.3 Sustained interruptionss","Amendments"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":0,"defined_names":851,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"AER only","index":0,"n_rows":150,"n_cols":39,"rows_kept":150,"cut":false,"hidden":true,"merged":[[58,35,62,35],[66,35,67,35],[72,14,72,15],[72,24,72,27],[110,1,110,8],[55,35,57,35],[0,1,0,11],[4,27,4,37],[6,27,6,30],[6,33,6,37],[53,24,53,28],[53,29,53,32],[54,1,54,5],[54,14,54,21],[54,24,54,28],[54,29,54,32],[55,2,55,3]]}
[null,"Data in these columns used for data validation and database purposes."]
[null,"Date last modified:","2017-01-16","added (Albury and Victora) for AGN"]
[null,null,"2016-10-17","updated TransGrid's correct legal name, corrected TasNetworks (T) to June financial year"]
[null,null,"2017-02-01","inserted Power and Water, added NRs (dms_FeederCat_1 and dms_FeederCat_2)"]
[null,null,"2017-03-03","inserted AEMO as a business",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"FOR ELECTRICITY BUSINESSES ONLY"]
[null,null,"2018-03-28","major changes to accommodate STPIS"]
[null,null,"Template Version",5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Feeder Types",null,null,null,"TasNetworks (D)","MAIFI flag","Feeder Names"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","long rural","EXTRA"]
[null,"dms_TradingName_List","dms_TradingNameFull_List","dms_ABN_List","dms_JurisdictionList","dms_Sector_List","dms_Segment_List","dms_FormControl_List","dms_RPT_List","dms_RPTMonth_List","dms_CRCPlength_List","dms_FRCPlength_List","dms_663_List","dms_DeterminationRef_List","dms_Addr1_List","dms_Addr2_List","dms_Suburb_List","dms_State_List","dms_PostCode_List","dms_PAddr1_List","dms_PAddr2_List","dms_PSuburb_List","dms_PState_List","dms_PPostCode_List","dms_ContactName1_List","dms_ContactPh1_List","dms_ContactEmail_List","dms_CBD_flag","dms_Urban_flag","dms_ShortRural_flag","dms_LongRural_flag","dms_FeederType_5_flag","dms_MAIFI_flag_List","dms_FeederName_1","dms_FeederName_2","dms_FeederName_3","dms_FeederName_4","dms_FeederName_5","Column1"]
[null,"ActewAGL Distribution","ActewAGL Distribution",76670568688,"ACT","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","40 Bunda Street",null,"CANBERRA","ACT",2600,"GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au","NO","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural"," ","ActewAGL Distribution"]
[null,"ActewAGL Distribution (Tx Assets)","ActewAGL Distribution (Tx Assets)",76670568688,"ACT","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","40 Bunda Street",null,"CANBERRA","ACT",2600,"GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au","NO","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural"," ","ActewAGL Distribution (Tx Assets)"]
[null,"ActewAGL Gas","ActewAGL Gas",76670568688,"ACT","Gas","Distribution","Weighted average price cap","Financial","June",5,5,"x",null,"40 Bunda Street",null,"CANBERRA","ACT",2600,"GPO BOX 366",null,"CANBERRA","ACT",2601,"Philip Deamer","02 6248 3438","GasAAReview@actewagl.com.au",null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural"," ","ActewAGL Gas"]
[null,"AEMO","Australian Energy Market Operator Ltd",94072010327,"Vic","Electricity","Transmission","-","Financial","March",5,5,"x","-","Level 22","530 Collins Street","MELBOURNE","VIC",3000,"GPO Box 2008",null,"MELBOURNE","VIC",3001,null,null,null,"n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","AEMO"]
[null,"AGN (Albury and Victoria)","Australian Gas Networks Limited (reporting data for Albury and Victoria)",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 6","400 King William Street","ADELAIDE","SA",5000,"PO Box 6468","Halifax Street","ADELAIDE","SA",5000,"Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","AGN (Albury)"]
[null,"AGN (Albury)","Australian Gas Networks Limited (reporting data for Albury)",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 6","400 King William Street","ADELAIDE","SA",5000,"PO Box 6468","Halifax Street","ADELAIDE","SA",5000,"Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," "]
[null,"AGN (SA)","Australian Gas Networks Limited (reporting data for SA)",19078551685,"SA","Gas","Distribution","Weighted average price cap","Financial","June",5,5,5,"distribution determination","Level 6","400 King William Street","ADELAIDE","SA",5000,"PO Box 6468","Halifax Street","ADELAIDE","SA",5000,"Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","AGN (SA)"]
[null,"AGN (Victoria)","Australian Gas Networks Limited (reporting data for Victoria)",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 6","400 King William Street","ADELAIDE","SA",5000,"PO Box 6468","Halifax Street","ADELAIDE","SA",5000,"Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","AGN (Victoria)"]
[null,"Amadeus","APT Pipelines (NT) Pty Ltd",39009737393,"NT","Gas","Transmission","Weighted average price cap","Financial","June",5,5,"x","n/a","Level 19, HSBC Building","580 George Street","SYDNEY","NSW",2000,"Level 19, HSBC Building","580 George Street","SYDNEY","NSW",2000,"Alexandra Curran","02 9275 0020","alexandra.curran@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Amadeus"]
[null,"APA GasNet","APA GasNet Australia (Operations) Pty Ltd","065083009","Vic","Gas","Transmission","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 19, HSBC Building","580 George Street","SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Alexandra Curran","02 9275 0020","alexandra.curran@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","APA GasNet"]
[null,"Ausgrid","Ausgrid",78508211731,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","570 George St",null,"SYDNEY","NSW",2000,"GPO Box 4009",null,"SYDNEY","NSW",2001,"John Thomson","02 9269 2312","john.thomson@ausgrid.com.au","YES","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","Ausgrid"]
[null,"Ausgrid (Tx Assets)","Ausgrid (Tx Assets)",67505337385,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","570 George St",null,"SYDNEY","NSW",2000,"GPO Box 4009",null,"SYDNEY","NSW",2001,"John Thomson","02 9269 2312","john.thomson@ausgrid.com.au","YES","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","Ausgrid (Tx Assets)"]
[null,"AusNet (D)","AusNet Electricity Services Pty Ltd",91064651118,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 32","2 Southbank Boulevard","SOUTHBANK","Vic",3006,"Locked Bag 14051",null,"MELBOURNE CITY MAIL CENTRE","VIC",8001,"please provide contact details",null,null,null,"YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","AusNet (D)"]
[null,"AusNet (Gas)","AusNet Gas Services","086015036","Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"X",null,"Level 19, HSBC Building","580 George Street","SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Alexandra Curran","02 9275 0020","alexandra.curran@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","AusNet (Gas)"]
[null,"AusNet (T)","Ausnet Services (Transmission) Ltd",48116124362,"Vic","Electricity","Transmission","Revenue cap","Financial","March",5,5,2,"transmission determination","Level 32","2 Southbank Boulevard","SOUTHBANK","Vic",3006,"Locked Bag 14051",null,"MELBOURNE CITY MAIL CENTRE","Vic",8001,"Clare Thompson","03 9695 6670","clare.e.thompson@ausnetservices.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","AusNet (T)"]
[null,"Australian Distribution Co.","Australian Distribution Co.",11222333444,"-","Electricity","Distribution","Revenue cap","Financial","June",5,5,2,"distribution determination","123 Straight Street",null,"SYDNEY","NSW",2000,"PO Box 123",null,"SYDNEY","NSW",2000,"Bob Smith","02 1234 5678","bob@auselec.net.au","n/a","n/a","n/a","n/a","NO",null,"CBD","Urban","Short rural","Long rural"," ","Australian Distribution Co."]
[null,"Australian Distribution Co. (Vic)","Australian Distribution Co. (Victoria)",11222333444,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"distribution determination","123 Straight Street",null,"MELBOURNE","Vic",3000,"PO Box 123",null,"MELBOURNE","VIC",3000,"Bob Smith","02 1234 5678","bob@auselec.net.au","n/a","n/a","n/a","n/a","NO",null,"CBD","Urban","Short rural","Long rural"," ","Australian Distribution Co. (Vic)"]
[null,"Australian Transmission Co.","Australian Transmission Co.",11222333444,"-","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","123 Straight Street",null,"SYDNEY","NSW",2000,"PO Box 123",null,"SYDNEY","NSW",2000,"Bob Smith","02 1234 5678","bob@auselec.net.au","n/a","n/a","n/a","n/a","NO",null,"CBD","Urban","Short rural","Long rural"," ","Australian Transmission Co."]
[null,"Central Ranges Pipeline (D)","Central Ranges Pipeline Pty Ltd",108218355,"NSW","Gas","Distribution","Weighted average price cap","Financial","June",15,5,5,"distribution determination","Level 19","580 George Street","SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Scott Young","02 9275 0031","scott.young@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," "]
[null,"Central Ranges Pipeline (T)","Central Ranges Pipeline Pty Ltd",108218355,"NSW","Gas","Distribution","Weighted average price cap","Financial","June",14,5,5,"transmission determination","Level 19","580 George Street","SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Scott Young","02 9275 0031","scott.young@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," "]
[null,"CitiPower","CitiPower",76064651056,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","40 Market Street",null,"MELBOURNE","Vic",3000,"Locked Bag 14090",null,"MELBOURNE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au","YES","YES","NO","NO","NO",null,"CBD","Urban","Short rural","Long rural"," ","CitiPower"]
[null,"Directlink","Directlink",16779340889,"Qld","Electricity","Transmission","Revenue cap","Financial","June",9,5,5,"transmission determination","Level 19, HSBC Building","580 George Street","SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Scott Young","02 9275 0031","scott.young@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Directlink"]
[null,"ElectraNet","ElectraNet",41094482416,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","52-55 East Terrace","Rymill Park","ADELAIDE","SA",5000,"PO Box 7096","Hutt Street Post Office","ADELAIDE","SA",5000,"Bill Jackson","08 8404 7969","jackson.bill@electranet.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","ElectraNet"]
[null,"Endeavour Energy","Endeavour Energy",11247365823,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","51 Huntingwood Drive",null,"HUNTINGWOOD","NSW",2148,"PO Box 811",null,"SEVEN HILLS","NSW",1730,"Jon Hocking","02 9853 4386 / 0407 348 156","Jon.Hocking@Endeavourenergy.com.au","NO","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","Endeavour Energy"]
[null,"Energex","Energex",40078849055,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","26 Reddacliff Street",null,"NEWSTEAD","Qld",4006,"26 Reddacliff Street",null,"NEWSTEAD","QLD",4006,"Nicola Roscoe","07 3664 5891","nicolaroscoe@energex.com.au","YES","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural"," ","Energex"]
[null,"Ergon Energy","Ergon Energy",50087646062,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","22 Walker Street",null,"TOWNSVILLE","Qld",4810,"Po Box 264",null,"FORTITUDE VALLEY","QLD",4006,"Jenny Doyle, Group Manager Regulatory Affairs","(07) 3851 6416","jenny.doyle@ergon.com.au","NO","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","Ergon Energy"]
[null,"Essential Energy","Essential Energy",37428185226,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","8 Buller Street",null,"PORT MACQUARIE","NSW",2444,"PO Box 5730",null,"PORT MACQUARIE","NSW",2444,"Catherine Waddell","02 6338 3553","catherine.waddell@essentialenergy.com.au","NO","NO","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","Essential Energy"]
[null,"Jemena Electricity","Jemena Electricity",82064651083,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 16","567 Collins Street","MELBOURNE","VIC",3000,"PO Box 16182",null,"MELBOURNE","VIC",8001,"Matthew Serpell","03 9173 8231","matthew.serpell@jemena.com.au","NO","NO","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural"," ","Jemena Electricity"]
[null,"JGN","Jemena Gas Networks (NSW) Ltd","003 004 322","NSW","Gas","Distribution","Weighted average price cap","Financial","June",5,5,null,null,null,null,null,null,null,null,null,null,null,null,"please provide contact details",null,null,"n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","JGN"]
[null,"Multinet Gas","Multinet Gas (DB No.1) Pty Ltd (ACN 086 026 986), Multinet Gas (DB No.2) Pty Ltd (ACN 086 230 122)","086026986","Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"43-45 Centreway",null,"MT WAVERLEY","Vic",3149,null,null,null,null,null,"Andrew Schille","03 8846 9860","andrew.schille@ue.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Multinet Gas"]
[null,"Murraylink","Murraylink",79181207909,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","Level 19","580 George Street","SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Scott Young","02 9275 0031","scott.young@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Murraylink"]
[null,"Power and Water","Power and Water Corporation",15947352360,"NT","Electricity","Distribution","Revenue cap","Financial","June",5,5,"x","distribution determination","GPO Box 1921",null,"DARWIN","NT",801,"GPO Box 1921",null,"DARWIN","NT",801,"Lucy Moon","08 8924 5822","Lucy.Moon@powerwater.com.au","YES","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," "]
[null,"Powercor Australia","Powercor Australia",89064651109,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","40 Market Street",null,"MELBOURNE","Vic",3000,"Locked bag 14090",null,"MELBOURNE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","Powercor Australia"]
[null,"Powerlink","Queensland Electricity Transmission Corporation Limited trading as Powerlink Queensland",82078849233,"Qld","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","33 Harold St",null,"VIRGINIA","Qld",4014,"PO Box 1193",null,"VIRGINIA","QLD",4014,"Jennifer Harris","07 3860 2667","jharris@powerlink.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Powerlink"]
[null,"Roma to Brisbane Pipeline","APT Petroleum Pipelines Limited t/a Roma to Brisbane Pipeline","009 737 393","Qld","Gas","Transmission","Weighted average price cap","Financial","June",5,5,"x","n/a","580 George Street",null,"SYDNEY","NSW",2000,"PO Box R41",null,"ROYAL EXCHANGE","NSW",1225,"Mark Allen","02 9275 0010","mark.allen@apa.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Roma to Brisbane Pipeline"]
[null,"SA Power Networks","SA Power Networks",13332330749,"SA","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","1 Anzac Highway",null,"KESWICK","SA",5035,"GPO Box 77",null,"ADELAIDE","SA",5000,"Richard Sibly","08 8404 5613","richard.sibly@sapowernetworks.com.au","NO","NO","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural"," ","SA Power Networks"]
[null,"TasNetworks (D)","TasNetworks (D)",24167357299,"Tas","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","1-7 Maria Street",null,"LENAH VALLEY","Tas",7008,"PO Box 606",null,"MOONAH","Tas",7009,"John Sayers","03 6271 6469","john.sayers@tasnetworks.com.au","YES","YES","YES","YES","YES",null,"Critical Infrastructure","High density commercial","Urban","High density rural","Low density rural","TasNetworks (D)"]
[null,"TasNetworks (T)","TasNetworks (T)",24167357299,"Tas","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","1-7 Maria Street",null,"LENAH VALLEY","Tas",7008,"PO Box 606",null,"MOONAH","Tas",7009,"John Sayers","03 6271 6469","john.sayers@tasnetworks.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","TasNetworks (T)"]
[null,"TransGrid","NSW Electricity Networks Operations Pty Ltd trading as TransGrid",609169959,"NSW","Electricity","Transmission","Revenue cap","Financial","June",5,4,5,"transmission determination","180 Thomas Street",null,"SYDNEY","NSW",2000,"PO Box A1000",null,"SYDNEY SOUTH","NSW",1235,"Garrie Chubb","0408 210 221","garrie.chubb@transgrid.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","TransGrid"]
[null,"United Energy","United Energy",70064651029,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 3","6 Nexus Court","MULGRAVE","Vic",3149,"PO Box 449",null,"MOUNT WAVERLEY","VIC",3170,"Mathew Abraham","03 8846 9758","mathew.abraham@ue.com.au","NO","NO","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural"," ","United Energy"]
[null,"Western Power (D)","Western Power (D)",18540492861,"WA","Electricity","Distribution","Revenue cap","Financial","June",12,4,"x","distribution determination","363 Wellington Street",null,"PERTH","WA",6000,"GPO Box L921",null,"PERTH","WA",6842,"Judy Hunter","08 9326 6239","judy.hunter@westernpower.com.au","NO","NO","YES","YES","NO","NO","CBD","Urban","Short rural","Long rural"," ","Western Power (D)"]
[null,"Western Power (T)","Western Power (T)",18540492861,"WA","Electricity","Transmission","Revenue cap","Financial","June",12,4,"x","transmission determination","363 Wellington Street",null,"PERTH","WA",6000,"GPO Box L921",null,"PERTH","WA",6842,"Judy Hunter","08 9326 6239","judy.hunter@westernpower.com.au","n/a","n/a","n/a","n/a","n/a",null,"CBD","Urban","Short rural","Long rural"," ","Western Power (T)"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"For EB & Reset RINs only",null,null,null,null,"For AARs only"]
[null,"The Reg Year Ending (dms_RYE) must be set to the last year of the regulatory period. For forecast data is is usually (FRCP_y5) for actual it is a single year (CRY). For historical actual data the RYE will need to be set manually in the business details sheet by setting the dms_Multiyear_flag to 1 and putting the correct value in 'dms_Specified_FinalYear. See cells C67:C68",null,null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"00\"),VALUE(LEFT(CRCP_y1,4)-1))","v":"2014-15"},null,null,null,null,null,null,"Drop down selector box for CA & Reset RINs.","For CA & Reset RINs only",null,null,null,null,null,null,null,null,null,"for DNSP only",null,null,null,null,"For DNSPs only",null,null,null,null,null,"Reason for interruption","dms_Reason_Interruption_Detailed","dms_Reason_Interruption","dms_STPIS_Exclusion_List"]
[null,"dms_Model_List ","DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)",null,"dms_RYE_Formula_Result",null,null,null,null,null,null,null,null,"dms_0203_ProjectType","dms_020303_01_UOM","dms_020501_01_UOM","dms_020501_02_UOM","dms_020501_03_UOM","dms_020501_04_UOM","dms_020603_01_UOM","dms_020701_01_UOM","dms_020701_02_UOM","dms_040102_01_UOM","dms_040102_04_UOM","dms_030601_01_UOM","dms_030601_02_UOM","dms_030701_01_UOM","dms_030702_01_UOM","dms_030703_01_UOM","dms_030605_UOM","dms_03060703_UOM",null,null,null,null,"Animal","Animal impact","Animal","Weather"]
[null,"ARR","ANNUAL REPORTING STATEMENT",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2018"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - single circuit","Circuit line length in km","0's","0's","0's","0's","0's","km","km","0's","days","minutes/customer","minutes/customer","Customer / km","%","km","number","number",null,null,null,null,null,"Animal nesting/burrowing, etc and other","Asset failure","Equipment failure"]
[null,"CA","CATEGORY ANALYSIS",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2018"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - dual circuit","Circuit line length in km","0's","0's","0's","0's","0's","0's","0's","0's","0's","minutes/customer","minutes/customer","MWh/customer","Number of spans",null,"number","number",null,null,null,null,null,"Other","Other","Operational error"]
[null,"CPI","CPI",null,null,null,null,null,null,null,null,null,null,"New line on new route - other","Circuit line length in km","MVA added","MVA added","MVA added","MVA added","0's","km","km","0's","$0s","interruptions/customer","interruptions/customer","kVA / customer","Number of spans",null,"number","number",null,null,null,null,"Asset failure","LV","Overloads","Vegetation"]
[null,"EB","ECONOMIC BENCHMARKING",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2018"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Line rebuild over existing route - single circuit","Circuit line length in km","0's","0's","0's","0's","0's","km","km","$0s","0's","interruptions/customer","interruptions/customer",null,"Number of spans",null,"number","number",null,null,null,null,null,"Distribution substation","Planned","Animals"]
[null,"PTRM","POST TAX REVENUE MODEL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2025"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit","Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s","(per cent)","0's","0's",null,null,null,null,null,"Number of spans",null,"number","(per cent)",null,null,null,null,null,"HV","Network business","Third party impacts"]
[null,"Reset","REGULATORY REPORTING STATEMENT",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2025"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Reconductor - Single circuit","Number","net circuit km added","net circuit km added","net circuit km added","net circuit km added",null,"years","years",null,null,null,null,null,"Years",null,"number",null,null,null,null,null,null,"Zone substation","Third party","Transmission failure"]
[null,"RFM","ROLL FORWARD MODEL",null,{"$f":"LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)","v":"2018"},"=LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)",null,null,null,null,null,null,null,"Reconductor - Dual circuit","Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s",null,null,null,null,null,null,null,null,"Years",null,"number",null,null,null,null,null,null,"Subtransmission","Unknown","Load shedding"]
[null,"WACC","WEIGHTED AVERAGE COST OF CAPITAL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2025"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Other",null,"net circuit km added","net circuit km added","net circuit km added","net circuit km added",null,null,null,null,null,null,null,null,"Trees",null,"number",null,null,null,null,null,"Other","insert description of 'other'","Vegetation","Inter-distributor connection failure"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"total spend $0s","total spend $0s","total spend $0s","total spend $0s",null,null,null,null,null,null,null,null,"Trees",null,"number",null,null,null,null,null,"Overloads","-","Weather","Other"]
[null,"dms_DataQuality_List",null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,"$0s",null,null,null,null,null,null,null,null,null,"Defects",null,"number",null,null,null,null,null,"Planned","-","2 - STPIS Exclusion (3.3)(a)"]
[null,"Actual",null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,null,null,null,null,null,null,null,null,null,null,"Defects",null,"number",null,null,null,null,null,"Network business","Network error","3 - STPIS Exclusion (3.3)(a)"]
[null,"Estimate",null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,null,null,null,null,null,null,null,null,null,null,"Spans",null,"number",null,null,null,null,null,null,"Switching and protection error","4 - STPIS Exclusion (3.3)(a)"]
[null,"Consolidated",null,null,null,null,null,null,null,null,null,null,null,null,null,"$0s",null,null,null,null,null,null,null,null,null,null,null,"km",null,"(per cent)",null,null,null,null,null,"Third party","Fire","5 - STPIS Exclusion (3.3)(a)"]
[null,"Recast",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Spans",null,"(per cent)","",null,null,null,null,null,"Other","6 - STPIS Exclusion (3.3)(a)"]
[null,"Public",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dig-in","7 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Unauthorised access"]
[null,"For all files either AER or business needs to be able to specify the type of submission","For PTRM & RFM templates we must provide a choice in case they change their form of control - otherwise it is drawn from the business specific lookup table above.",null,null,null,null,null,null,null,null,null,null,null,"For PTRM files - this field set the text for the named range \"DMS_Xfactor\" which in all cases is simply the text \"x factors\" - this saves putting in each old gas PTRM file ",null,null,null,null,null,null,null,null,null,"for TNSP only",null,null,null,null,null,null,null,null,null,null,null,"Vehicle impact"]
[null,"dms_SourceList","dms_FormControl_Choices",null,null,null,null,null,null,null,null,null,null,null,"DMS_Xfactor",null,null,null,null,null,null,null,null,null,"dms_030601_01_UOM",null,"dms_030701_01_UOM","dms_030702_01_UOM",null,null,null,null,null,null,null,"Unknown","Unknown"]
[null,"After appeal","Revenue cap",null,null,null,null,null,null,null,null,null,null,null,"x factors",null,null,null,null,null,null,null,null,null,"%",null,"Number of spans","km",null,null,null,null,null,null,null,"Vegetation","Blow-in/Fall-in - NSP responsibility"]
[null,"Draft decision","Revenue yield",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Years","%",null,null,null,null,null,null,null,null,"Grow-in - NSP responsibility"]
[null,"Final decision","Weighted average price cap",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Trees","km",null,null,null,null,null,null,null,null,"Blow-in/Fall-in - Other responsible party"]
[null,"PTRM update 1",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%",null,"Defects","number",null,null,null,null,null,null,null,null,"Grow-in - Other responsible party"]
[null,"PTRM update 2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Number of spans",null,null,null,null,null,null,null,null,"Weather"]
[null,"PTRM update 3",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"km",null,null,null,null,null,null,null,null,"2 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 4",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%",null,"km",null,null,null,null,null,null,null,null,"3 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 5",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Number of spans",null,null,null,null,null,null,null,null,"4 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 6",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,null,null,null,null,null,null,null,null,null,"5 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 7",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%",null,null,null,null,null,null,null,null,null,null,"6 - STPIS Exclusion (3.3)(a)"]
[null,"Regulatory proposal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,null,null,null,null,null,null,null,null,null,"7 - STPIS Exclusion (3.3)(a)"]
[null,"Reporting",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%"]
[null,"Revised regulatory proposal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number"]
[]
[]
[]
[null,"These are indeces and lookup values for various dates. All step from the value placed in FRCP_y1 on the business and other details worksheet",{"$f":"IF(dms_FifthFeeder_flag_NSP=\"NO\",\"This NSP has only 4 feeder categories\",\"This NSP has 5 feeder categories\")","v":"This NSP has only 4 feeder categories"},null,null,null,null,null,null,null,null,"These date tables are currently used in the Recast templates to provide column headings and conditional formatting"]
[null,"dms_FRCPlength_Num_List","dms_FinalYear_List","dms_CRCPlength_Num_List","dms_CFinalYear_List","dms_FRCP_years",null,"dms_CRCP_years",null,"dms_CRCP_index",null,"CRY from input cell on business sheet","CRY - financial","dms_FinYears","CRY calendar","dms_CalYears",null,null,null,null,null,null,null,null,"These \"row descriptions\" are the column headings in the various templates but become row descriptions in the ETL process"]
[null,1,"dms_FRCP_y1",1,"CRCP_y1",{"$f":"FRCP_y1","v":"2020-21"},"dms_FRCP_y1",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)-1)&\"-\"&TEXT(VALUE(MID(dms_FRCP_y1,3,2)),\"00\"),VALUE(LEFT(dms_FRCP_y1,4)-1))","v":"2019-20"},"dms_CRCP_yZ",1,null,{"$f":"CRY","v":"2017-18"},{"$f":"VALUE(LEFT(CRY,4))&\"-\"&TEXT(MID(CRY,3,2)+1,\"00\")","v":"2017-18"},"dms_CRYf_y1",{"$f":"VALUE(LEFT(CRY,4)+1)","v":2018},"dms_CRYc_y1",null,null,null,null,null,null,null,null,null,"Table 6.3 sustained interruptions - row descriptions"]
[null,2,"dms_FRCP_y2",2,"CRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y1,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y1,4)+1))","v":"2021-22"},"dms_FRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yZ,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yZ,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yZ,4)-1))","v":"2018-19"},"dms_CRCP_yY",2,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y1,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y1,3,2)+2,\"00\")","v":"2018-19"},"dms_CRYf_y2",{"$f":"VALUE(LEFT(dms_CRYc_y1,4)+1)","v":2019},"dms_CRYc_y2",null,null,null,null,null,null,null,null,null,"dms_060301_CustNo_Affected_Row","dms_060301_Avg_Duration_Sustained_Int_Row","dms_060301_Effect_unplanned_SAIDI_Row","dms_060301_Effect_unplanned_SAIFI_Row"]
[null,3,"=IF(dms_Model=\"ARR\",15,9)",3,"=IF(dms_Model=\"ARR\",15,9)",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y2,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y2,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y2,4)+1))","v":"2022-23"},"dms_FRCP_y3",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yY,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yY,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yY,4)-1))","v":"2017-18"},"dms_CRCP_yX",3,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y2,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y2,3,2)+2,\"00\")","v":"2019-20"},"dms_CRYf_y3",{"$f":"VALUE(LEFT(dms_CRYc_y2,4)+1)","v":2020},"dms_CRYc_y3",null,null,null,null,null,null,null,null,null,"Number of customers affected by the interruption","Average duration of sustained customer interruption","Effect on unplanned SAIDI","Effect on unplanned SAIFI"]
[null,4,"dms_FRCP_y4",4,"CRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y3,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y3,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y3,4)+1))","v":"2023-24"},"dms_FRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yX,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yX,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yX,4)-1))","v":"2016-17"},"dms_CRCP_yW",4,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y3,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y3,3,2)+2,\"00\")","v":"2020-21"},"dms_CRYf_y4",{"$f":"VALUE(LEFT(dms_CRYc_y3,4)+1)","v":2021},"dms_CRYc_y4"]
[null,5,"dms_FRCP_y5",5,"CRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y4,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y4,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y4,4)+1))","v":"2024-25"},"dms_FRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yW,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yW,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yW,4)-1))","v":"2015-16"},"dms_CRCP_yV",5,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y4,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y4,3,2)+2,\"00\")","v":"2021-22"},"dms_CRYf_y5",{"$f":"VALUE(LEFT(dms_CRYc_y4,4)+1)","v":2022},"dms_CRYc_y5"]
[null,6,"dms_FRCP_y6",6,"CRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y5,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y5,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y5,4)+1))","v":"2025-26"},"dms_FRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yV,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yV,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yV,4)-1))","v":"2014-15"},"dms_CRCP_yU",6,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y5,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y5,3,2)+2,\"00\")","v":"2022-23"},"dms_CRYf_y6",{"$f":"VALUE(LEFT(dms_CRYc_y5,4)+1)","v":2023},"dms_CRYc_y6"]
[null,7,"dms_FRCP_y7",7,"CRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y6,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y6,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y6,4)+1))","v":"2026-27"},"dms_FRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yU,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yU,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yU,4)-1))","v":"2013-14"},"dms_CRCP_yT",7,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y6,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y6,3,2)+2,\"00\")","v":"2023-24"},"dms_CRYf_y7",{"$f":"VALUE(LEFT(dms_CRYc_y6,4)+1)","v":2024},"dms_CRYc_y7",null,null,null,null,null,null,null,null,null,"Table 6.1 telephone answering - row descriptions and start date"]
[null,8,"dms_FRCP_y8",8,"CRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y7,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y7,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y7,4)+1))","v":"2027-28"},"dms_FRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yT,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yT,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yT,4)-1))","v":"2012-13"},"dms_CRCP_yS",8,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y7,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y7,3,2)+2,\"00\")","v":"2024-25"},"dms_CRYf_y8",{"$f":"VALUE(LEFT(dms_CRYc_y7,4)+1)","v":2025},"dms_CRYc_y8",null,null,null,null,null,null,null,null,null,"dms_060101_Rows","dms_060102_Rows","dms_060101_StartDateTxt"]
[null,9,"dms_FRCP_y9",9,"CRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y8,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y8,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y8,4)+1))","v":"2028-29"},"dms_FRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yS,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yS,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yS,4)-1))","v":"2011-12"},"dms_CRCP_yR",9,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y8,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y8,3,2)+2,\"00\")","v":"2025-26"},"dms_CRYf_y9",{"$f":"VALUE(LEFT(dms_CRYc_y8,4)+1)","v":2026},"dms_CRYc_y9",null,null,null,null,null,null,null,null,null,"Total number of calls \n(after removing excluded events)","Number of calls answered within 30 seconds \n(after excluding excluded events) ",{"$f":"dms_060701_StartDateTxt","v":"1-Jul-2017"}]
[null,10,"=IFERROR(IF(dms_Model=\"ARR\",(MAX(0,dms_0608_LastRow-dms_0608_OffsetRows)),\"not an ARR\"),\"6.8 not present\")",10,"=IFERROR(IF(dms_Model=\"ARR\",(MAX(0,dms_0608_LastRow-dms_0608_OffsetRows)),\"not an ARR\"),\"6.8 not present\")",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y9,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y9,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y9,4)+1))","v":"2029-30"},"dms_FRCP_y10",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yR,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yR,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yR,4)-1))","v":"2010-11"},"dms_CRCP_yQ",10,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y9,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y9,3,2)+2,\"00\")","v":"2026-27"},"dms_CRYf_y10",{"$f":"VALUE(LEFT(dms_CRYc_y9,4)+1)","v":2027},"dms_CRYc_y10"]
[null,11,"dms_FRCP_y11",11,"CRCP_y11",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y10,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y10,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y10,4)+1))","v":"2030-31"},"dms_FRCP_y11",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yQ,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yQ,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yQ,4)-1))","v":"2009-10"},"dms_CRCP_yP",11,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y10,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y10,3,2)+2,\"00\")","v":"2027-28"},"dms_CRYf_y11",{"$f":"VALUE(LEFT(dms_CRYc_y10,4)+1)","v":2028},"dms_CRYc_y11"]
[null,12,"dms_FRCP_y12",12,"CRCP_y12",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y11,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y11,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y11,4)+1))","v":"2031-32"},"dms_FRCP_y12",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yP,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yP,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yP,4)-1))","v":"2008-09"},"dms_CRCP_yO",12,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y11,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y11,3,2)+2,\"00\")","v":"2028-29"},"dms_CRYf_y12",{"$f":"VALUE(LEFT(dms_CRYc_y11,4)+1)","v":2029},"dms_CRYc_y12"]
[null,13,"dms_FRCP_y13",13,"CRCP_y13",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y12,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y12,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y12,4)+1))","v":"2032-33"},"dms_FRCP_y13",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yO,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yO,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yO,4)-1))","v":"2007-08"},"dms_CRCP_yN",13,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y12,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y12,3,2)+2,\"00\")","v":"2029-30"},"dms_CRYf_y13",{"$f":"VALUE(LEFT(dms_CRYc_y12,4)+1)","v":2030},"dms_CRYc_y13",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"dms_0603_FeederList",{"$f":"INDEX(dms_FeederName_1,MATCH(dms_TradingName,dms_TradingName_List))","v":"CBD"},{"$f":"INDEX(dms_FeederName_2,MATCH(dms_TradingName,dms_TradingName_List))","v":"Urban"},{"$f":"INDEX(dms_FeederName_3,MATCH(dms_TradingName,dms_TradingName_List))","v":"Short rural"},{"$f":"INDEX(dms_FeederName_4,MATCH(dms_TradingName,dms_TradingName_List))","v":"Long rural"},{"$f":"INDEX(dms_FeederName_5,MATCH(dms_TradingName,dms_TradingName_List))","v":" "}]
[null,14,"dms_FRCP_y14",14,"CRCP_y14",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y13,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y13,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y13,4)+1))","v":"2033-34"},"dms_FRCP_y14",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yN,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yN,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yN,4)-1))","v":"2006-07"},"dms_CRCP_yM",14,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y13,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y13,3,2)+2,\"00\")","v":"2030-31"},"dms_CRYf_y14",{"$f":"VALUE(LEFT(dms_CRYc_y13,4)+1)","v":2031},"dms_CRYc_y14",null,null,null,null,null,null,null,null,null,"Table 6.7.1 - daily performance data - unplanned - MAIFI  -- row descriptions and header named range values"]
[null,15,"dms_FRCP_y15",15,"CRCP_y15",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y14,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y14,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y14,4)+1))","v":"2034-35"},"dms_FRCP_y15",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yM,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yM,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yM,4)-1))","v":"2005-06"},"dms_CRCP_yL",15,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y14,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y14,3,2)+2,\"00\")","v":"2031-32"},"dms_CRYf_y15",{"$f":"VALUE(LEFT(dms_CRYc_y14,4)+1)","v":2032},"dms_CRYc_y15",null,null,null,null,null,null,null,null,null,"These headings (Lists) are determined from the INDEX/MATCH function on the NSP selected on the Business & other details sheet"]
[null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y15,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y15,3,2)+2,\"00\")","v":"2032-33"},"dms_CRYf_y16",{"$f":"VALUE(LEFT(dms_CRYc_y15,4)+1)","v":2033},"dms_CRYc_y16",null,null,null,null,null,null,null,null,"dms_060701_Feeder_Header_Lvl4",{"$f":"INDEX(dms_FeederName_1,MATCH(dms_TradingName,dms_TradingName_List))","v":"CBD"},{"$f":"INDEX(dms_FeederName_1,MATCH(dms_TradingName,dms_TradingName_List))","v":"CBD"},{"$f":"INDEX(dms_FeederName_2,MATCH(dms_TradingName,dms_TradingName_List))","v":"Urban"},{"$f":"INDEX(dms_FeederName_2,MATCH(dms_TradingName,dms_TradingName_List))","v":"Urban"},{"$f":"INDEX(dms_FeederName_3,MATCH(dms_TradingName,dms_TradingName_List))","v":"Short rural"},{"$f":"INDEX(dms_FeederName_3,MATCH(dms_TradingName,dms_TradingName_List))","v":"Short rural"},{"$f":"INDEX(dms_FeederName_4,MATCH(dms_TradingName,dms_TradingName_List))","v":"Long rural"},{"$f":"INDEX(dms_FeederName_4,MATCH(dms_TradingName,dms_TradingName_List))","v":"Long rural"},{"$f":"IF((INDEX(dms_FeederName_5,MATCH(dms_TradingName,dms_TradingName_List))=0),\"Network\",(INDEX(dms_FeederName_5,MATCH(dms_TradingName,dms_TradingName_List))))","v":" "},{"$f":"IF((INDEX(dms_FeederName_5,MATCH(dms_TradingName,dms_TradingName_List))=0),\"Network\",(INDEX(dms_FeederName_5,MATCH(dms_TradingName,dms_TradingName_List))))","v":" "},"Network","Network"]
[null,"These are drop down lists for businesses to select the correct FRCP_y1 on the business and other details worksheet.\nThis also populates the column headings in the worksheets",null,null,null,null,null,null,null,null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y16,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y16,3,2)+2,\"00\")","v":"2033-34"},"dms_CRYf_y17",{"$f":"VALUE(LEFT(dms_CRYc_y16,4)+1)","v":2034},"dms_CRYc_y17"]
[null,"dms_RCP_fyear_list","dms_CRY_ListF","dms_CRY_ListC","dms_RCP_cyear_list","dms_FRCP_fyear_list","dms_FRCP_ListF","dms_FRCP_ListC","dms_FRCP_cyear_list",null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y17,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y17,3,2)+2,\"00\")","v":"2034-35"},"dms_CRYf_y18",{"$f":"VALUE(LEFT(dms_CRYc_y17,4)+1)","v":2035},"dms_CRYc_y18",null,null,null,null,null,null,null,null,"dms_060701_Rows","All events","After removing excluded events","All events","After removing excluded events","All events","After removing excluded events","All events","After removing excluded events","All events","After removing excluded events","All events","After removing excluded events"]
[null,"dms_fy1","2005-06","2006","dms_cy1","dms_frcp_fy1","2010-11",2011,"dms_crcp_cy1",null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y18,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y18,3,2)+2,\"00\")","v":"2035-36"},"dms_CRYf_y19",{"$f":"VALUE(LEFT(dms_CRYc_y18,4)+1)","v":2036},"dms_CRYc_y19",null,null,null,null,null,null,null,null,null,"the number of column headings changes from 10 to 12 depending on the number of feeder categories for the NSP"]
[null,"dms_fy2","2006-07","2007","dms_cy2","dms_frcp_fy2","2011-12",2012,"dms_crcp_cy2",null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y19,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y19,3,2)+2,\"00\")","v":"2036-37"},"dms_CRYf_y20",{"$f":"VALUE(LEFT(dms_CRYc_y19,4)+1)","v":2037},"dms_CRYc_y20"]
[null,"dms_fy3","2007-08","2008","dms_cy3","dms_frcp_fy3","2012-13",2013,"dms_crcp_cy3"]
[null,"dms_fy4","2008-09","2009","dms_cy4","dms_frcp_fy4","2013-14",2014,"dms_crcp_cy4"]
[null,"dms_fy5","2009-10",2010,"dms_cy5","dms_frcp_fy5","2014-15",2015,"dms_crcp_cy5"]
[null,"dms_fy6","2010-11",2011,"dms_cy6","dms_frcp_fy6","2015-16",2016,"dms_crcp_cy6",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Table 6.8.1 - row descriptions"]
[null,"dms_fy7","2011-12",2012,"dms_cy7","dms_frcp_fy7","2016-17",2017,"dms_crcp_cy7",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"dms_060801_01_Rows","dms_060801_02_Rows","dms_060801_03_Rows","dms_060801_04_Rows"]
[null,"dms_fy8","2012-13",2013,"dms_cy8","dms_frcp_fy8","2017-18",2018,"dms_crcp_cy8",null,null,"2005-06","2006",null,null,null,null,null,null,null,null,null,null,null,null,"Number of interruptions","Duration of interruptions","Total unplanned minutes off supply","Effect on unplanned MAIFI"]
[null,"dms_fy9","2013-14",2014,"dms_cy9","dms_frcp_fy9","2018-19",2019,"dms_crcp_cy9",null,null,"2006-07","2007"]
[null,"dms_fy10","2014-15",2015,"dms_cy10","dms_frcp_fy10","2019-20",2020,"dms_crcp_cy10",null,null,"2007-08","2008"]
[null,"dms_fy11","2015-16",2016,"dms_cy11","dms_frcp_fy11","2020-21",2021,"dms_crcp_cy11",null,null,"2008-09","2009"]
[null,"dms_fy12","2016-17",2017,"dms_cy12","dms_frcp_fy12","2021-22",2022,"dms_crcp_cy12",null,null,"2009-10",2010]
[null,"dms_fy13","2017-18",2018,"dms_cy13","dms_frcp_fy13","2022-23",2023,"dms_crcp_cy13",null,null,"2010-11",2011,null,null,null,null,null,null,null,null,null,null,null,null,"Table 7.9.4 - market impact component - row descriptions"]
[null,"dms_fy14","2018-19",2019,"dms_cy14","dms_frcp_fy14","2023-24",2024,"dms_crcp_cy14",null,null,"2011-12",2012,null,null,null,null,null,null,null,null,null,null,null,"dms_070904_01_Rows","without exclusions","with exclusions"]
[null,"dms_fy15","2019-20",2020,"dms_cy15","dms_frcp_fy15","2024-25",2025,"dms_crcp_cy15",null,null,"2012-13",2013]
[null,"dms_fy16","2020-21",2021,"dms_cy16",null,null,null,null,null,null,"2013-14",2014]
[null,"dms_fy17","2021-22",2022,"dms_cy17",null,null,null,null,null,null,"2014-15",2015]
[null,"dms_fy18","2022-23",2023,"dms_cy18",null,null,null,null,null,null,"2015-16",2016]
[null,"dms_fy19","2023-24",2024,"dms_cy19",null,null,null,null,null,null,"2016-17",2017,null,null,null,null,null,null,null,null,null,null,null,null,"Use this to add to existing files"]
[null,"dms_fy20","2024-25",2025,"dms_cy20",null,null,null,null,null,null,"2017-18",2018,null,null,null,null,null,null,null,null,null,null,null,null,"ARR's  6.8 STPIS exclusions"]
[null,null,null,null,null,null,null,null,null,null,null,"2018-19",2019,null,null,null,null,null,null,null,null,null,null,null,null,"dms_060801_Event_Date","dms_060801_OutageID","dms_060801_FeederID","dms_060801_FeederClass","dms_060801_CauseID","dms_060801_01_Values","dms_060801_02_Values","dms_060801_03_Values","dms_060801_Excl_Cat","dms_060801_04_Values"]
[null,null,null,null,null,null,null,null,null,null,null,"2019-20",2020]
[null,null,null,null,null,null,null,null,null,null,null,"2020-21",2021]
[null,null,null,null,null,null,null,null,null,null,null,"2021-22",2022,null,null,null,null,null,null,null,null,null,null,null,null,"CA 6.3 sustained interruptions"]
[null,null,null,null,null,null,null,null,null,null,null,"2022-23",2023,null,null,null,null,null,null,null,null,null,null,null,null,"dms_060301_Event_Date","dms_060301_Event_Time","dms_060301_AssetID","dms_060301_FeederClass","dms_060301_Reason","dms_060301_DetailedReason","dms_060301_CustNo_Affected_Values","dms_060301_Avg_Duration_Sustained_Int_Values","dms_060301_Effect_unplanned_SAIDI_Values","dms_060301_Effect_unplanned_SAIFI_Values","dms_060301_MED"]
[null,null,null,null,null,null,null,null,null,null,null,"2023-24",2024]
[null,null,null,null,null,null,null,null,null,null,null,"2024-25",2025]
[null,null,null,null,null,null,null,null,null,null,null,"2025-26",2026]
[null,null,null,null,null,null,null,null,null,null,null,"2026-27",2027]
[null,null,null,null,null,null,null,null,null,null,null,"2027-28",2028]
[null,null,null,null,null,null,null,null,null,null,null,"2028-29",2029]
[null,null,null,null,null,null,null,null,null,null,null,"2029-30",2030]
[null,null,null,null,null,null,null,null,null,null,null,"2030-31",2031]
[null,null,null,null,null,null,null,null,null,null,null,"2031-32",2032]
[null,null,null,null,null,null,null,null,null,null,null,"2032-33",2033]
[null,null,null,null,null,null,null,null,null,null,null,"2033-34",2034]
[null,null,null,null,null,null,null,null,null,null,null,"2034-35",2035]
[null,null,null,null,null,null,null,null,null,null,null,"2035-36",2036]

{"sheet":"Instructions","index":1,"n_rows":27,"n_cols":4,"rows_kept":27,"cut":false,"hidden":false,"merged":[[24,2,24,4],[25,2,25,3],[26,2,26,4],[8,2,8,4],[10,2,10,4],[12,2,12,4],[20,2,20,4],[22,2,22,4],[7,2,7,3],[1,1,1,5],[2,1,2,5],[3,2,3,4],[4,2,4,4],[5,2,5,4]]}
[]
[null,{"$f":"CONCATENATE(dms_Segment,\" Network Service Provider\")","v":"Distribution Network Service Provider"}]
[null,"Annual Reporting RIN Template"]
[null,null,{"$f":"CONCATENATE(\"This template is to be used by \",dms_TradingName,\" to fulfil its reporting obligations to the AER.\")","v":"This template is to be used by Ergon Energy to fulfil its reporting obligations to the AER."}]
[null,null,"INSTRUCTIONS"]
[null,null,"Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting."]
[]
[null,null,"Identifying CONFIDENTIAL INFORMATION:\n\nPlease use the macro at the top of each \nworksheet to identify confidential information. \n\n"]
[null,null,"-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential.\n\n-To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro"]
[]
[null,null,"UNITS OF MEASURE\n\nAll amounts are to be unrounded and reported in nominal terms on a one for one basis: that is 1000 is to be entered as '1000'.\n\n"]
[]
[null,null,"COLOUR CODING OF INPUT / NON-INPUT CELLS:"]
[null,null,null,"Yellow = Input cell (mandatory)"]
[null,null,null,"Darker yellow = input cell (mandatory)"]
[null,null,null,"Orange = input cell (if data available)"]
[null,null,null,"Grey = Not applicable/No inputs required"]
[null,null,null,"Leave coloured cells blank if no information exists. \nPLEASE DO NOT ENTER TEXT into cells that are to contain numeric data."]
[]
[]
[null,null,"WORKSHEET NAVIGATION\n\nMany tables in the worksheets have been \"grouped\" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin of excel (for Row groupings) or above the columns (for column groupings). \n\n\n\n"]
[]
[null,null,"RETURNING COMPLETED RESPONSES\n\nPlease return four (4) files to the AER: \n1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. \n\n2. An actual and an estimate version with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER.\n\n3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response.\n\n\nUse the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public. "]
[]
[null,null,"SUBMITTING AMENDED DATA TO THE AER\n\nIf an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. \n\nNSPs must identify the reason for the amendments in the Amendment Reason box on the  Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. \n\n."]
[null,null,"NSP may use Amended Data macro \nto highlight cells that contain amended data.\nNB: if data is also CONFIDENTIAL, re-apply \nthe Confidentiality macro after applying the \nAmended macro"]
[null,null,"Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER"]

{"sheet":"Contents","index":2,"n_rows":27,"n_cols":19,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"CONTENTS"]
[]
[]
[null,null,null,null,"1. Business details",null,null,null,null,null,null,"2. Expenditure"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"4. Alternative control services",null,null,null,null,null,null,"5. Network information",null,null,null,null,null,null,"6. Service & quality"]

{"sheet":"Business & other details","index":3,"n_rows":137,"n_cols":9,"rows_kept":137,"cut":false,"hidden":false,"merged":[[59,2,59,8],[18,4,18,7],[19,2,19,3],[19,4,19,7],[22,2,22,3],[22,4,22,7],[23,4,23,7],[24,2,24,3],[24,4,24,7],[32,1,32,8],[57,2,57,3],[58,4,58,8],[7,1,7,8],[11,1,11,8],[13,2,13,4],[14,2,14,4],[17,2,17,3],[17,4,17,7]]}
[null,{"$f":"IF(dms_DataQuality=\"backcast\",INDEX(dms_Worksheet_List,MATCH(dms_Model,dms_Model_List))&\" BACKCAST\",INDEX(dms_Worksheet_List,MATCH(dms_Model,dms_Model_List)))","v":"CATEGORY ANALYSIS"}]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(CRY),CONCATENATE(FRCP_y1,\" to \",dms_MultiYear_FinalYear_Result))","v":"2017-18"}]
[null,"BUSINESS & OTHER DETAILS"]
[]
[]
[null,"Instructions"]
[null,"Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells. "]
[]
[null,"SUBMISSION PARTICULARS INPUT SHEETS"]
[]
[null,"ENTITY DETAILS"]
[]
[null,"Short name","Ergon Energy",null,null,"Select business name from drop down list first"]
[null,"ACN / ABN",{"$f":"INDEX(dms_ABN_List,MATCH(dms_TradingName,dms_TradingName_List))","v":50087646062}]
[]
[]
[null,"Business address","Address 1",null,"420 Flinders Street"]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",(INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List))))","v":""}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_Suburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"TOWNSVILLE"}]
[null,null,null,"State",{"$f":"INDEX(dms_State_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Qld"},"p/code",{"$f":"INDEX(dms_PostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":4810}]
[]
[null,"Postal address","Address 1",null,"GPO Box 1461"]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",(INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List))))","v":""}]
[null,null,"Suburb",null,"BRISBANE"]
[null,null,null,"State",{"$f":"INDEX(dms_PState_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"QLD"},"p/code",4001]
[]
[]
[null,"Contact name/s","Jenny Doyle, Group Manager Regulation & Pricing"]
[null,"Contact phone/s",{"$f":"INDEX(dms_ContactPh1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"(07) 3851 6416"}]
[null,"Contact email address/s","jenny.doyle@energyq.com.au"]
[]
[null,"REGULATORY CONTROL PERIODS"]
[]
[null,"Forthcoming regulatory control period","2020-21",{"$f":"dms_FRCP_y2","v":"2021-22"},{"$f":"dms_FRCP_y3","v":"2022-23"},{"$f":"dms_FRCP_y4","v":"2023-24"},{"$f":"dms_FRCP_y5","v":"2024-25"}]
[null,null,{"$f":"dms_FRCP_y6","v":"2025-26"},{"$f":"dms_FRCP_y7","v":"2026-27"},{"$f":"dms_FRCP_y8","v":"2027-28"},{"$f":"dms_FRCP_y9","v":"2028-29"},{"$f":"dms_FRCP_y10","v":"2029-30"}]
[]
[]
[null,"Current regulatory control period",{"$f":"dms_CRCP_FirstYear_Result","v":"2015-16"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+1)&\"-\"&TEXT(MID(CRCP_y1,3,2)+2,\"00\"),VALUE(LEFT(CRCP_y1,4)+1))","v":"2016-17"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+2)&\"-\"&TEXT(VALUE(MID(CRCP_y1,3,2)+3),\"00\"),VALUE(LEFT(CRCP_y1,4)+2))","v":"2017-18"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+3)&\"-\"&TEXT(MID(CRCP_y1,3,2)+4,\"00\"),VALUE(LEFT(CRCP_y1,4)+3))","v":"2018-19"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+4)&\"-\"&TEXT(MID(CRCP_y1,3,2)+5,\"00\"),VALUE(LEFT(CRCP_y1,4)+4))","v":"2019-20"}]
[null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+5)&\"-\"&TEXT(MID(CRCP_y1,3,2)+6,\"00\"),VALUE(LEFT(CRCP_y1,4)+5))","v":"2020-21"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+6)&\"-\"&TEXT(MID(CRCP_y1,3,2)+7,\"00\"),VALUE(LEFT(CRCP_y1,4)+6))","v":"2021-22"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+7)&\"-\"&TEXT(MID(CRCP_y1,3,2)+8,\"00\"),VALUE(LEFT(CRCP_y1,4)+7))","v":"2022-23"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+8)&\"-\"&TEXT(MID(CRCP_y1,3,2)+9,\"00\"),VALUE(LEFT(CRCP_y1,4)+8))","v":"2023-24"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+9)&\"-\"&TEXT(MID(CRCP_y1,3,2)+10,\"00\"),VALUE(LEFT(CRCP_y1,4)+9))","v":"2024-25"}]
[null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+10)&\"-\"&TEXT(MID(CRCP_y1,3,2)+11,\"00\"),VALUE(LEFT(CRCP_y1,4)+10))","v":"2025-26"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+11)&\"-\"&TEXT(MID(CRCP_y1,3,2)+12,\"00\"),VALUE(LEFT(CRCP_y1,4)+11))","v":"2026-27"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+12)&\"-\"&TEXT(MID(CRCP_y1,3,2)+13,\"00\"),VALUE(LEFT(CRCP_y1,4)+12))","v":"2027-28"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+13)&\"-\"&TEXT(MID(CRCP_y1,3,2)+14,\"00\"),VALUE(LEFT(CRCP_y1,4)+13))","v":"2028-29"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+14)&\"-\"&TEXT(MID(CRCP_y1,3,2)+15,\"00\"),VALUE(LEFT(CRCP_y1,4)+14))","v":"2029-30"}]
[]
[]
[null,"Previous regulatory control period",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y2,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y2,3,2)),\"00\"),VALUE(LEFT(PRCP_y2,4)-1))","v":"2010-11"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y3,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y3,3,2)),\"00\"),VALUE(LEFT(PRCP_y3,4)-1))","v":"2011-12"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y4,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y4,3,2)),\"00\"),VALUE(LEFT(PRCP_y4,4)-1))","v":"2012-13"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y5,4)-1)&\"-\"&TEXT(VALUE(RIGHT(PRCP_y5,2)-1),\"00\"),VALUE(LEFT(PRCP_y5,4)-1))","v":"2013-14"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"00\"),VALUE(LEFT(CRCP_y1,4)-1))","v":"2014-15"}]
[]
[]
[]
[null,"Commencing regulatory year","2017-18","CRY"]
[]
[null,"Last completed regulatory year","2017-18","dms_FinalYear"]
[]
[]
[]
[null,null,"IF THIS IS AN ABC RIN - make sure the the named range CRY is applied and the named range dms_dollar_nom_UOM is applied"]
[null,null,"IF THIS IS A RESET RIN - make sure the named ranges CRY and dms_dollar_nom_UOM are NOT present in the workbook"]
[null,null,"FOR ABC RINS THAT SPAN MULTIPLE YEARS - make sure MultiYear Flag is set and final year entered as required"]
[]
[null,"Source","Reporting",null,"Please select the correct submission type from the dropdown list."]
[null,"Data quality (actual, estimate, public, consolidated)","Consolidated",null,"Use Consolidated for Consolidated Confidential version\nUse Public for Consolidated Public version"]
[null,"Amended RIN submission - amendment reason","T2.6 the descriptor Refurbishment/Rebuild EWP (HVC) was been added. T2.2 Regulators has been added to Pole Mounted <= 22kV  >600 kVA (Multiple Phase)"]
[null,"Submission Date","2018-11-26","dms_SubmissionDate","Please enter date this file submitted to AER (dd/mm/yyyy)"]
[null,"EBSS - First application of scheme in forthcoming period?","No"]
[null,"Sector",{"$f":"INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Electricity"},"dms_Sector","=INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Segment",{"$f":"INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Distribution"},"dms_Segment","=INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Regulatory Year Ending",{"$f":"IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))","v":"2018"},"dms_RYE","=IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))"]
[null,"Reporting Period Type",{"$f":"INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Financial"},"dms_RPT","=INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Model or RIN Type","CA","dms_Model","Drop down selection"]
[null,"EB/CA Unit of Measure for Monetary Values","$0s","dms_dollar_nom_UOM","If the cover sheet is attached to an ABC RIN make the NAMED RANGE on this field is set"]
[null,"Security Classification","Public","dms_Classification","Always Public"]
[null,"Dollar $ real month",{"$f":"INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"June"},"dms_RPTMonth","=INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Dollar $ real  (the last month before the FRCP_y1)",{"$f":"IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(CRY,2))&RIGHT(CRY,2)),CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2))))","v":"June 2018"},"dms_DollarReal","=IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(CRY,2))&RIGHT(CRY,2)),CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2))))"]
[null,"Dollar $ real previous year (PRCP_y5)",{"$f":"IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE(((LEFT(CRY,2))&RIGHT(CRY,2))-1),CONCATENATE(dms_RPTMonth)&\" \"&VALUE(((LEFT(dms_CRCP_FirstYear_Result,2)&RIGHT(dms_CRCP_FirstYear_Result,2))))-1)","v":"June 2017"},"dms_DollarReal_Prev","=IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE(((LEFT(CRY,2))&RIGHT(CRY,2))-1),CONCATENATE(dms_RPTMonth)&\" \"&VALUE(((LEFT(dms_CRCP_FirstYear_Result,2)&RIGHT(dms_CRCP_FirstYear_Result,2))))-1)"]
[null,"Form of control",{"$f":"INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Revenue cap"},"dms_FormControl","=INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Calendar Year for table 3.6 data",{"$f":"VALUE(dms_RYE)-1","v":2017},"dms_0306_Year","=VALUE(dms_RYE)-1"]
[null,"Jurisdiction",{"$f":"INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))","v":"Qld"},"dms_Jurisdiction","=INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"FOR ABC RINS THAT SPAN MULTIPLE YEARS"]
[null,"Is this a multi year ABC RIN?","No"]
[null,"Backcast Multiyear EB, CA or ARR?",{"$f":"IF(dms_MultiYear_ResponseFlag=\"No\",0,1)","v":0},"dms_MultiYear_Flag","This is set from the answer provided above"]
[null,null,{"$f":"IF(dms_MultiYear_Flag=1,\"Specify Final Reg Year here eg 2016 or 2015-16\",\"not a Multi Reg Year submission\")","v":"not a Multi Reg Year submission"},"dms_Specified_FinalYear","The result here is returned to dms_CRCP_FinalYear_Result if response to Q in C73 is \"yes\" and dms_MultiYear_Flag is set to 1"]
[null,"This block works out the various RYE's for both ABC RINs and Reset RINS"]
[null,"Single Year Model T/F",{"$f":"IF(dms_Model=\"EB\",1,0)","v":0},"dms_EB"]
[null,null,{"$f":"IF(dms_Model=\"CA\",1,0)","v":1},"dms_CA","=dms_SingleYear_Model"]
[null,null,{"$f":"IF(dms_Model=\"ARR\",1,0)","v":0},"dms_ARR"]
[null,"Single Year Final Year Reference","CRY","dms_SingleYear_FinalYear_Ref","This is the reference for EB, CA & ARR RINs"]
[null,"Single Year Final Year Result",{"$f":"IFERROR(IF(SUM(dms_SingleYear_Model)<>0,(INDIRECT(dms_SingleYear_FinalYear_Ref)),\"not a single year RIN\"),\"CRY not present\")","v":"2017-18"},"dms_SingleYear_FinalYear_Result","=IFERROR(IF(SUM(dms_SingleYear_Model)<>0,(INDIRECT(dms_SingleYear_FinalYear_Ref)),\"not a single year RIN\"),\"CRY not present\")"]
[null,"FRCP length in years",{"$f":"INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_FRCPlength_Num","=INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Multi Year Final Year Reference",{"$f":"INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))","v":"dms_FRCP_y5"},"dms_MultiYear_FinalYear_Ref","=INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))"]
[null,"Multi Year Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)","v":"2024-25"},"dms_MultiYear_FinalYear_Result","=IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)",null,null,null,"Formula errors OK"]
[null,"CRCP length in years",{"$f":"INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_CRCPlength_Num","=INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"CRCP Final Year Reference",{"$f":"INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))","v":"CRCP_y5"},"dms_CRCP_FinalYear_Ref","=INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))"]
[null,"CRCP First Year Result",{"$f":"INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))","v":"2015-16"},"dms_CRCP_FirstYear_Result","=INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))"]
[null,"CRCP Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)","v":"2017-18"},"dms_CRCP_FinalYear_Result","=IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)"]
[null,"FOR CATEGORY ANALYSIS FILES"]
[null,"How many rows in tables 6.3 sustained interruptions?",{"$f":"IF(dms_Model<>\"CA\",\"not a CA\",\"Is a CA\")","v":"Is a CA"},"dms_060301_MaxRows only returns a valid value when cover sheet is attached to a CA file"]
[null,"Table 6.3.1 - last row reference",{"$f":"IFERROR(IF(dms_Model=\"CA\",\nLOOKUP(2,1/(dms_060301_Avg_Duration_Sustained_Int_Values<>\"\"),\n(ROW(dms_060301_Avg_Duration_Sustained_Int_Values))),\n\"not a CA\"),\"no data in 6.3 or 6.3 not present\")","v":54305},"dms_060301_LastRow","=IFERROR(IF(dms_Model=\"CA\",LOOKUP(2,1/(dms_060301_Avg_Duration_Sustained_Int_Values<>\"\"),(ROW(dms_060301_Avg_Duration_Sustained_Int_Values))),\"not a CA\"),\"6.3 not present\")"]
[null,"Table 6.3.1 - max number rows",{"$f":"IFERROR(IF(dms_Model=\"CA\",(dms_060301_LastRow-15),\"not a CA\"),\"no data in 6.3 or 6.3 not present\")","v":54290},"dms_060301_MaxRows","=IFERROR(IF(dms_Model=\"CA\",(dms_060301_LastRow-15),\"not a CA\"),\"6.3 not present\")"]
[null,"Table 6.6.3 - Public lighting repair - no. business days",{"$f":"INDEX(dms_663_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_663","=INDEX(dms_663_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"FOR ARR or RESET FILES"]
[null,"How many rows in tables 6.1 or 6.7?  (leap year?)","insert dms_LeapYear NR if required","dms_LeapYear is used to determine dms_060701_Max_Rows BUT it is only found on worksheet 6.1 or 6.7 and the date value in the cell is used to determine whether it is a leap year"]
[null,"Is dms_LeapYear named range present?",{"$f":"IFERROR(IF(dms_LeapYear,\"yes\"),\"no\")","v":"no"}]
[null,"Table 6.7.1 - includes a leap year?",{"$f":"\nIFERROR(IF(MONTH(DATE(YEAR(dms_LeapYear),2,29))=2,\"is a leap year\",\"not a leap year\"),\n\"dms_LeapYear not present\")","v":"dms_LeapYear not present"},"dms_LeapYear_Result","=IFERROR(IF(MONTH(DATE(YEAR(dms_LeapYear),2,29))=2,\"is a leap year\",\"not a leap year\"),\"dms_LeapYear not present\")"]
[null,"Table 6.7.1 - Last row  (leap year/ non leap year)",{"$f":"\nIFERROR(IF(dms_Model=\"ARR\",\nIF(dms_LeapYear_Result=\"is a leap year\",366,365),\n(IF(dms_Model=\"Reset\",\n(IF(dms_LeapYear_Result=\"is a leap year\",1827,1826)),\n\"not a relevant RIN type\"))),\n\"dms_LeapYear in either 6.1 or 6.7 not present\")","v":"not a relevant RIN type"},"dms_060701_MaxRows","=IFERROR(IF(dms_Model=\"ARR\",IF(dms_LeapYear_Result=\"is a leap year\",366,365),(IF(dms_Model=\"Reset\",(IF(dms_LeapYear_Result=\"is a leap year\",1827,1826)),\"not a relevant RIN type\"))),\"dms_LeapYear in either 6.1 or 6.7 not present\")"]
[null,"How many columns in 6.7?   (4 or 5 feeder categories)",{"$f":"IF(dms_FifthFeeder_flag_NSP=\"NO\",\"This NSP has only 4 feeder categories\",\"This NSP has 5 feeder categories\")","v":"This NSP has only 4 feeder categories"}]
[null,"Table 6.7.1 - Last column (# of feeder categories > 4)",{"$f":"IF(dms_FifthFeeder_flag_NSP=\"NO\",10,12)","v":10},"dms_060701_MaxCols","=IF(dms_FifthFeeder_flag_NSP=\"NO\",8,10)"]
[null,"Table 6.7.1 - Number of offset rows",{"$f":"IF(dms_Model=\"ARR\",15,9)","v":9},"dms_060701_OffsetRows","=IF(dms_Model=\"ARR\",15,9)"]
[null,"Start date for telephone answering in 6.1 or 6.7?",null,null,"Using 060701 as naming standard not 060101 "]
[null,"Table 6.1.1 and 6.7.1 - Start Date as Text",{"$f":"IF(SUM(dms_SingleYear_Model)>0,(CONCATENATE(IF(LEN(CRY)=4,\"1-Jan-\",\"1-Jul-\"),LEFT(CRY,4))),(CONCATENATE(IF(LEN(CRCP_y4)=4,\"1-Jan-\",\"1-Jul-\"),LEFT(CRCP_y4,4))))","v":"1-Jul-2017"},"dms_060701_StartDateTxt","=IF(SUM(dms_SingleYear_Model)>1,(CONCATENATE(IF(LEN(CRY)=4,\"1-Jan-\",\"1-Jul-\"),LEFT(CRY,4))),(CONCATENATE(IF(LEN(CRCP_y4)=4,\"1-Jan-\",\"1-Jul-\"),LEFT(CRCP_y4,4))))"]
[null,"Table 6.1.1 and 6.7.1 - Start Date as Date Value",{"$f":"DATEVALUE(dms_060701_StartDateTxt)","v":42917},"dms_060701_StartDateVal","=DATEVALUE(dms_060701_StartDateTxt)"]
[null,"FOR ANNUAL REPORTING RINS"]
[null,"How many rows in table 6.8?","insert dms_060801_StartCell NR if required","dms_060801_StartCell is only found on worksheet 6.8 and is used to determine the starting date for the date range"]
[null,"Table 6.8 - Number of offset rows",{"$f":"IFERROR(IF(dms_Model=\"ARR\",(ROW(dms_060801_StartCell)-1),\"not an ARR\"),\"6.8 not present\")","v":"not an ARR"},"dms_0608_OffsetRows","=IFERROR(IF(dms_Model=\"ARR\",(ROW(dms_060801_StartCell)-1),\"not an ARR\"),\"6.8 not present\")"]
[null,"Table 6.8 - Last row",{"$f":"IFERROR(IF(dms_060801_StartCell<>\"\",IF(dms_Model=\"ARR\",(LOOKUP(2,1/(dms_060801_01_Values<>\"\"),(ROW(dms_060801_01_Values)))),\"not an ARR\"),0),\"6.8 not present\")","v":"6.8 not present"},"dms_0608_LastRow","=IFERROR(IF(dms_060801_StartCell<>\"\",IF(dms_Model=\"ARR\",(LOOKUP(2,1/(dms_060801_01_Values<>\"\"),(ROW(dms_060801_01_Values)))),\"not an ARR\"),0),\"6.8 not present\")"]
[null,"Table 6.8 - MaxRows",{"$f":"IFERROR(IF(dms_Model=\"ARR\",(MAX(0,dms_0608_LastRow-dms_0608_OffsetRows)),\"not an ARR\"),\"6.8 not present\")","v":"not an ARR"},"dms_060801_MaxRows","=IFERROR(IF(dms_Model=\"ARR\",(MAX(0,dms_0608_LastRow-dms_0608_OffsetRows)),\"not an ARR\"),\"6.8 not present\")"]
[null,"FOR TNSP FILES"]
[null,"Table 7.9.4 only appears in TNSPs Reset RIN"]
[null,"Table 7.9.4 - first year",{"$f":"LEFT(PRCP_y3,4)","v":"2012"},"dms_070904_Start_Year","=LEFT(PRCP_y3,4)"]
[null,"MISC"]
[null,"Distribution Determination Reference",{"$f":"INDEX(dms_DeterminationRef_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"2015-20 Distribution Determination"},"dms_DeterminationRef"]
[null,"Is this Submission File a Subset File","NO","dms_Partial"]
[null,"CBD Feeder for this business",{"$f":"INDEX(dms_CBD_flag,MATCH(dms_TradingName,dms_TradingName_List))","v":"NO"},"dms_CBD_flag_NSP"]
[null,"Urban Feeder for this business",{"$f":"INDEX(dms_Urban_flag,MATCH(dms_TradingName,dms_TradingName_List))","v":"YES"},"dms_Urban_flag_NSP"]
[null,"Short rural Feeder for this business",{"$f":"INDEX(dms_ShortRural_flag,MATCH(dms_TradingName,dms_TradingName_List))","v":"YES"},"dms_ShortRural_flag_NSP"]
[null,"Long rural Feeder for this business",{"$f":"INDEX(dms_LongRural_flag,MATCH(dms_TradingName,dms_TradingName_List))","v":"YES"},"dms_LongRural_flag_NSP"]
[null,"Fifth Feeder Category (eg. TasNetworks (D))",{"$f":"INDEX(dms_FeederType_5_flag,MATCH(dms_TradingName,dms_TradingName_List))","v":"NO"},"dms_FifthFeeder_flag_NSP","=INDEX(dms_FeederType_5_flag,MATCH(dms_TradingName,dms_TradingName_List))"]
[]
[null,"discard this record?","NO","dms_DISCARD","If record is to be discarded from DB set this flag to YES"]
[]
[null,"USES NAMED RANGES FLAG","yes","dms_Defined_Names_Used"]
[]
[null,"REGULATORY YEARS FOR MULTI RYE SUBMISSIONS"]
[null,"Multiple RYE flag","NO","dms_Multi_RYE_flag"]
[null,null,"Manually specify RYE","Named ranges to apply"]
[null,null,2013,"dms_RYE_01"]
[null,null,2014,"dms_RYE_02"]
[null,null,2015,"dms_RYE_03"]
[null,null,2016,"dms_RYE_04"]
[null,null,2017,"dms_RYE_05"]

{"sheet":"2.1 Expenditure summary","index":4,"n_rows":126,"n_cols":3,"rows_kept":126,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.1 EXPENDITURE SUMMARY & RECONCILIATION"]
[]
[null,"There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.1.1 - STANDARD CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Replacement expenditure",201511047]
[null,"Connections",50123340]
[null,"Augmentation Expenditure",39364305]
[null,"Non-network",42755543]
[null,"capitalised network overheads",77626243]
[null,"capitalised corporate overheads",101093054]
[null,"Metering",1561876]
[null,"Public Lighting",0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,"balancing item",0]
[null,"capcons (included in the above)",42755463]
[null,"TOTAL GROSS CAPEX \n(including capcons)",{"$f":"+SUM(C11:C26)","v":514035408}]
[]
[null,"2.1.2 - STANDARD CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Vegetation management",42479035]
[null,"Maintenance",81297151.529999956]
[null,"Emergency response",55329910]
[null,"Non-network",115985060]
[null,"network overheads",118237899]
[null,"corporate overheads",86554213]
[null,"Metering",2550554]
[null,"Public Lighting",0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,"balancing item",-115985060]
[null,"TOTAL OPEX",{"$f":"+SUM(C33:C48)","v":386448762.52999997}]
[]
[null,"2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Connections",25829094.750712641]
[null,"capitalised network overheads",10128154.853045648]
[null,"capitalised corporate overheads",13189948.244255053]
[null,"Metering",4756967]
[null,"Public lighting",5234897]
[null,"Fee and quoted",29587484]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,"balancing item",-18720292]
[null,"TOTAL CAPEX",{"$f":"+SUM(C54:C67)","v":70006253.848013341}]
[]
[null,"2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Connections",4908670]
[null,"network overheads",51280374]
[null,"corporate overheads",15841613]
[null,"Metering",28447982]
[null,"Public lighting",8771025]
[null,"Fee and quoted",28327013]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,"balancing item",-60315799]
[null,"TOTAL OPEX",{"$f":"+SUM(C73:C86)","v":77260878}]
[]
[null,"2.1.5 - DUAL FUNCTION ASSETS CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Replacement expenditure",0]
[null,"Connections",0]
[null,"Augmentation Expenditure",0]
[null,"Non-network",0]
[null,"Capitalised network overheads",0]
[null,"Capitalised corporate overheads",0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,"balancing item",0]
[null,"capcons (included in the above)",0]
[null,"TOTAL GROSS CAPEX (including capcons)",{"$f":"SUM(C92:C105)","v":0}]
[]
[null,"2.1.6 - DUAL FUNCTION ASSETS OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Vegetation management",0]
[null,"Maintenance",0]
[null,"Emergency response",0]
[null,"Non-network",0]
[null,"Network overheads",0]
[null,"Corporate overheads",0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,"balancing item",0]
[null,"TOTAL OPEX",{"$f":"SUM(C112:C125)","v":0}]

{"sheet":"2.2 Repex","index":5,"n_rows":172,"n_cols":7,"rows_kept":172,"cut":false,"hidden":false,"merged":[[151,1,154,1],[155,1,158,1],[166,1,169,1],[170,1,171,1],[159,1,165,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.2 REPEX"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY"]
[null,null,null,null,"EXPENDITURE ($0's)","ASSET REPLACEMENTS\n(0's)","ASSET FAILURES\n(0's)"]
[null,"ASSET GROUP","ASSET CATEGORY",null,{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole",null,5297943.3136361921,1563,0]
[null,null,"˂ = 1 kV; Wood",null,12016645.509037437,2258,6]
[null,null,"> 1 kV & < = 11 kV; Wood",null,12514760.550597647,1634,14]
[null,null,"˃ 11 kV & < = 22 kV; Wood",null,12514760.550597651,1634,31]
[null,null,"> 22 kV & < = 66 kV; Wood",null,4531095.5367945014,307,3]
[null,null,"> 66 kV & < = 132 kV; Wood",null,76769.899057732793,3,1]
[null,null,"> 132 kV; Wood",null,0,0,0]
[null,null,"˂ = 1 kV; Concrete",null,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Concrete",null,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Concrete",null,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Concrete",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Concrete",null,0,0,0]
[null,null,"> 132 kV; Concrete",null,0,0,0]
[null,null,"˂ = 1 kV; Steel",null,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Steel",null,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Steel",null,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Steel",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Steel",null,0,0,0]
[null,null,"> 132 kV; Steel",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"POLE TOP STRUCTURES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,6633430.2762640892,5368,50]
[null,null,"> 1 kV & < = 11 kV",null,10030570.640909398,6452,100]
[null,null,"˃ 11 kV & < = 22 kV",null,9464621.9983740039,4291,42]
[null,null,"> 22 kV & < = 66 kV",null,2470063.593778268,1406,25]
[null,null,"> 66 kV & < = 132 kV",null,8276.631563151861,1,0]
[null,null,"> 132 kV",null,0,0,0]
[null,null,"Other",null,0,0,3]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",null,8697093.8704923298,136,153]
[null,null,"> 1 kV & < = 11 kV",null,3060806.5050953734,87,214]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",null,1090743.3548861258,79,108]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase",null,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase",null,440726.14016127109,25,60]
[null,null,"> 22 kV & < = 66 kV",null,37923.148613930331,1,11]
[null,null,"> 66 kV & < = 132 kV",null,0,0,0]
[null,null,"> 132 kV",null,0,0,1]
[null,null,"Other",null,0,0,1]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,1607180.7633785359,7,128]
[null,null,"> 1 kV & < = 11 kV",null,774558.84523406741,3,17]
[null,null,"> 11 kV & < = 22 kV",null,3014308.0142947412,1,10]
[null,null,"> 22 kV & < = 33 kV",null,14476.620941239938,0,3]
[null,null,"> 33 kV & < = 66 kV",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV",null,0,0,0]
[null,null,">  132 kV",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",null,3498969.4585310109,5247,1780]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",null,2079843.3000910247,1790,0]
[null,null,"˂ = 11 kV ; Residential ; Complex Type",null,34313.992395772832,31,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type",null,0,0,0]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type",null,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 132 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 132 kV ; Subdivision  ",null,0,0,0]
[null,null,"Other",null,0,0,4]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,7977147.0287520299,724,349]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,722891.01970095409,15,4]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,60548.1801887888,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,3428733.7031814214,193,153]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,17443689.744059928,494,103]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,{"$f":"2901063.6540307+411106.297135292","v":3312169.9511659923},{"$f":"39+12","v":51},0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,4068182.5555196321,21,10]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,1604726.6655344216,10,7]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",null,136402.71014035286,1,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",null,395576.95531933312,2,2]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",null,560441.46862189763,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",null,3319395.9075615229,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA",null,479023.01451509964,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",null,7510.4194523706619,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",null,15791.521633969945,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA",null,0,0,0]
[null,null,"Other",null,0,0,17]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  FUSE",null,14822668.074445225,2227,80]
[null,null,"˂ = 11 kV  ; Switch",null,5432077.8435323751,228,212]
[null,null,"˂ = 11 kV ;  Circuit Breaker",null,2149448.0925222128,9,7]
[null,null,"> 11 kV & < = 22 kV  ; Switch",null,4259026.4373267209,854,133]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker",null,984068.10194437962,44,1]
[null,null,"> 22 kV & < = 33 kV ; Switch",null,273307.92577744316,20,46]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",null,817688.79741756653,16,0]
[null,null,"> 33 kV & < = 66 kV ; Switch",null,549863.63610823022,4,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",null,8656793.4269021209,55,2]
[null,null,"> 66 kV & < = 132 kV ; Switch",null,0,1,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",null,0,0,0]
[null,null,"> 132 kV ; Switch",null,0,0,0]
[null,null,"> 132 kV ; Circuit Breaker",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",null,1166392.3361796986,323,8]
[null,null,"Luminaires ;  Minor Road",null,1048984.7150160782,587,30]
[null,null,"Brackets ; Major Road",null,322731.75032642635,130,2]
[null,null,"Brackets ; Minor Road",null,244614.67829904621,273,5]
[null,null,"Lamps ; Major Road",null,93074.683614079346,393,46]
[null,null,"Lamps ; Minor Road",null,70971.826261315204,736,24]
[null,null,"Poles / Columns ; Major Road",null,174902.96769636203,31,0]
[null,null,"Poles / Columns ; Minor Road",null,284606.75528540672,105,3]
[null,null,"Other",null,0,0,0]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",null,4337894.0583582455,191,20]
[null,null,"Local Network Wiring Assets",null,0,0,0]
[null,null,"Communications Network Assets",null,2430581.6163525698,99,39]
[null,null,"Master Station Assets",null,0,0,0]
[null,null,"Communications Site Infrastructure",null,544001.26823445386,56,50]
[null,null,"Communications Linear Assets",null,0,11,0]
[null,null,"AFLC",null,378082.42742866639,0,0]
[null,null,"Other",null,0,0,0]
[null,"OTHER BY: \nDNSP DEFINED","VOLTAGE TRANSFORMERS",null,1114378.7262719835,43,0]
[]
[null,null,"CURRENT TRANSFORMER",null,2616489.1710222065,65,0]
[null,null,"CAP BANK",null,109535.46082125203,0,0]
[null,null,"SVC",null,31148.844430293037,0,0]
[null,null,"Other non AER Asset Categories",null,5155599.7503227573,0,0]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"","",""]
[]
[]
[null,"2.2.2 - SELECTED ASSET CHARACTERISTICS"]
[null,null,null,null,"ASSET VOLUMES CURRENTLY IN COMMISSION","ASSET REPLACEMENTS\n(0's)"]
[null,"ASSET GROUP","METRIC","UNITS",{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"TOTAL POLES BY: \nFEEDER TYPE","Total CBD poles","Number",0,0]
[null,null,"Total urban poles","Number",102298.030069286,613]
[null,null,"Total rural long poles","Number",443923.60514912801,2661]
[null,null,"Total rural short poles","Number",427479.36478158599,2563]
[null,"OVERHEAD CONDUCTORS BY:\nCONDUCTOR LENGTH BY FEEDER TYPE","Conductors CBD","KM",0,0]
[null,null,"Conductors urban","KM",3856.4900871710001,11.2]
[null,null,"Conductors rural long","KM",96697.700993980194,218.3]
[null,null,"Conductors rural short","KM",42611.741341285699,98.3]
[null,"OVERHEAD CONDUCTORS BY: \nCONDUCTOR LENGTH MATERIAL TYPE","OH conductor LV ABC","KM",841.89731551989701,48.3]
[null,null,"OH conductor steel","KM",63266.5371692228,124.6]
[null,null,"OH conductor ACSR","KM",46888.579943107303,44.2]
[null,null,"OH conductor AAAC","KM",7460.3593956572504,37.9]
[null,null,"OH conductor AAC","KM",15818.846977143399,68.3]
[null,null,"OH conductor HDBC","KM",8889.7116217862294,4.4000000000000004]
[null,null,"Other","KM",0,0]
[null,"UNDERGROUND CABLES BY: \nCABLE LENGTH BY FEEDER TYPE","Cable CBD","KM",0,0]
[null,null,"Cable urban","KM",3153.7451690302901,4]
[null,null,"Cable rural long","KM",400.98325642975999,0.5]
[null,null,"Cable rural short","KM",5255.3582280164301,6.5]
[null,"TRANSFORMERS BY: \nTOTAL MVA","Total MVA replaced","MVA",20976.694800000001,208.60499999999999]
[null,null,"Total MVA disposed of","MVA",137.16200000000191,137.162000000002]

{"sheet":"2.3(a) Augex","index":6,"n_rows":129,"n_cols":34,"rows_kept":129,"cut":false,"hidden":false,"merged":[[6,1,6,3],[11,21,11,22],[10,11,10,22],[12,17,12,19],[72,11,72,13],[72,14,72,16],[71,1,71,10],[72,1,73,1],[72,2,73,2],[72,3,73,3],[72,4,73,4],[72,6,73,6],[11,3,12,3],[11,4,12,4],[11,5,12,5],[11,14,11,15],[73,7,73,10],[72,7,72,10],[71,11,71,22],[72,17,72,19],[72,21,72,22],[12,30,12,31],[71,23,71,24],[71,25,73,25],[71,26,73,26],[71,30,71,31],[73,23,73,24],[73,27,73,29],[73,30,73,31],[71,29,72,29],[71,27,71,28],[11,6,12,6],[11,16,11,19],[12,23,12,24],[10,30,10,31],[10,23,10,24],[10,25,12,25],[10,26,12,26],[10,27,10,28],[10,29,11,29],[11,7,11,8],[11,9,11,10],[11,11,11,13],[10,1,10,10],[11,1,12,1],[11,2,12,2],[12,27,12,29]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.3 AUGEX PROJECT DATA"]
[]
[]
[null,"There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped.  See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS. "]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTY CONTRACTS","LAND AND EASEMENTS"]
[null,"SUBSTATION ID","SUBSTATION TYPE\n(drop down)","PROJECT ID","PROJECT TYPE\n(drop down)","PROJECT TRIGGER\n(drop down)","VOLTAGE (KV)","SUBSTATION RATING\nNORMAL CYCLIC\n(MVA)",null,"SUBSTATION RATING\nN-1 EMERGENCY\n(MVA)",null,"TRANSFORMERS",null,null,"SWITCHGEAR",null,"CAPACITORS",null,null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"PRE","POST","PRE","POST","UNITS ADDED ","MVA ADDED","EXPENDITURE ($0's)","UNITS ADDED ","EXPENDITURE ($0's)","MVAR ADDED","EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,"T083/ROMA","Subtransmission substation","NN01163","Substation upgrade - capacity","Demand growth","132/66/33",74,160,34,80,3,210,4550579,6,637892,0,0,null,null,4232181,33654,18367148,0,856768,{"$f":"SUM(N14,P14,R14,U14,W14,X14,Y14)","v":28644568},"2007,2008,2009,2010,2011,2012,2013,2013,2015,2016,2017,2018",0,0,14111955,142610,0]
[null,"SW TAPS STH TOOWOOMBA 110KV BUS  ","Subtransmission substation","00164975","Substation upgrade - voltage","Demand growth","110kV",120,120,60,60,0,0,0,7,1957868,0,0,null,null,1805850,11196,9334509,1312517,1233086,15643830,"2013,2014,2015,2016,2017",0,0,8959182,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N46,P46,R46,U46,W46,X46,Y46)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9179000,"2012,2013,2014,2015,2016,2017,2018",null,null,null,0,50.6]
[]
[]
[null,"AUG232_1","AUG232_2","AUG232_3","AUG232_4","AUG232_5","AUG232_6","ED_AUG232_00001","ED_AUG232_00002","ED_AUG232_00003","ED_AUG232_00004","ED_AUG232_00005","ED_AUG232_00006","ED_AUG232_00007","ED_AUG232_00008","ED_AUG232_00009","ED_AUG232_00010","ED_AUG232_00011","ED_AUG232_00012","ED_AUG232_00013","ED_AUG232_00014","ED_AUG232_00015","ED_AUG232_00016","ED_AUG232_00017","ED_AUG232_00018","ED_AUG232_00019","ED_AUG232_00020","ED_AUG232_00021"]
[null,"2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS."]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTY CONTRACTS","LAND AND EASEMENTS"]
[null,"LINE ID","PROJECT ID","PROJECT TYPE","PROJECT TRIGGER",null,"VOLTAGE (KV)","ROUTE LINE LENGTH ADDED",null,null,null,"POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS)",null,null,"OVERHEAD LINES",null,null,"UNDERGROUND CABLES",null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"KM ADDED",null,null,null,"POLES/TOWERS ADDED","POLES/TOWERS UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,"SW TAPS 110KV SUB TRANS LINE SOTO-CETO  ","00164985","New line on new route - dual circuit","Demand growth",null,"Other",3,null,null,null,0,0,0,0,0,0,6,0,2307931,319194,3699,13879399,0,755717,{"$f":"SUM(N75,Q75,T75,U75,W75,X75,Y75)","v":17262241},"2013,2014,2015,2016,2017",0,0,13547698,0,0,null,"New line on new route - single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line rebuild over existing route - single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - raising/retensoring"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - voltage upgrade"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - capacity"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"String spare circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N107,Q107,T107,U107,W107,X107,Y107)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2574,"2008,2009,2010,2011,2012,2013,2014,2015,2016,2017,2018",null,null,null,0,699.7]

{"sheet":"2.3(b) Augex","index":7,"n_rows":46,"n_cols":5,"rows_kept":46,"cut":false,"hidden":false,"merged":[[10,1,11,1],[21,1,22,1],[35,1,36,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.3 AUGEX  DATA"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS."]
[null,"DESCRIPTOR METRICS"]
[null,"PROJECT TYPE",null,"UNITS ADDED\n(0's)","UNITS UPGRADED\n(0's)"]
[null,null,"UNITS",{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"HV Feeder Augmentations - Overhead Lines","Circuit line length in km",10,2]
[null,"HV Feeder Augmentations - Underground Cables","Circuit line length in km",7,1]
[null,"LV Feeder Augmentations - Overhead Lines","Circuit line length in km",6,7]
[null,"LV Feeder Augmentations - Underground Cables","Circuit line length in km",1,1]
[null,"Distribution Substation Augmentations - Pole Mounted","Number",74,75]
[null,"Distribution Substation Augmentations - Ground Mounted","Number",1,2]
[null,"Distribution Substation Augmentations - Indoor","Number",0,0]
[]
[null,"COST METRICS"]
[null,"TOTAL DIRECT EXPENDITURE - Project Type",null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"HV Feeder Augmentations - Overhead Lines",null,11692760]
[null,"HV Feeder Augmentations - Underground Cables",null,601569]
[null,"HV Feeder Non-Material Projects",null,8994269]
[null,"LV Feeder Augmentations - Overhead Lines",null,1343449]
[null,"LV Feeder Augmentations - Underground Cables",null,325414]
[null,"LV Feeder Non-Material Projects",null,481707]
[null,"Distribution Substation Augmentations - Pole Mounted",null,3092420]
[null,"Distribution Substation Augmentations - Ground Mounted",null,68002]
[null,"Distribution Substation Augmentations - Indoor",null,0]
[]
[]
[null,"2.3.4 - AUGEX DATA - TOTAL EXPENDITURE"]
[null,"AUGMENTATION CAPEX (As incurred)",null,"EXPENDITURE\n ($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Subtransmission Substations, Switching Stations, Zone Substations",null,9693074]
[null,"Subtransmission Lines",null,1108607]
[null,"HV Feeders",null,21288598]
[null,"HV Feeders - Land Purchases and Easements",null,22771]
[null,"Distribution Substations",null,3160422]
[null,"Distribution Substations - Land Purchases And Easements",null,0]
[null,"LV Feeders",null,2150570]
[null,"LV Feeders - Land Purchases And Easements",null,1624]
[null,"Other Assets",null,1938639]

{"sheet":"2.5 Connections","index":8,"n_rows":73,"n_cols":5,"rows_kept":73,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.5 CONNECTIONS"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.5.1 - DESCRIPTOR METRICS"]
[null,"<<<GROUP-ROW>>>"]
[]
[null,null,null,null,"VOLUMES AND EXPENDITURE"]
[null,"CONNECTION SUBCATEGORY","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2017-18"}]
[null,"RESIDENTIAL","Underground connections","0's",5356]
[null,null,"Overhead connections","0's",3034]
[null,null,"Distribution substation installed","MVA added",23.632000000000001]
[null,null,"Distribution substations installed","0's",621]
[null,null,"Distribution substation installed","total spend $0s",6003846]
[null,null,"Augmentation HV","net circuit km added",124.202]
[null,null,"Augmentation HV","total spend $0s",5461873]
[null,null,"Augmentation LV","net circuit km added",15.617000000000001]
[null,null,"Augmentation LV","total spend $0s",6768213]
[null,null,"Mean days to connect residential customer with LV single phase connection","0's",8]
[null,null,"Volume of GSL breaches for residential customers","0's",56]
[null,null,"Volume of customer complaints relating to connection services","0's",28]
[null,null,"GSL payments","$0s",11508]
[null,"COMMERCIAL/INDUSTRIAL","Underground connections","0's",599]
[null,null,"Overhead connections","0's",1155]
[null,null,"Distribution substation installed","MVA added",157.54249999999999]
[null,null,"Distribution substations installed","0's",745]
[null,null,"Distribution substation installed","total spend $0s",14036102]
[null,null,"Augmentation HV","net circuit km added",151.053]
[null,null,"Augmentation HV","total spend $0s",13365052]
[null,null,"Augmentation LV","net circuit km added",10.987]
[null,null,"Augmentation LV","total spend $0s",6272742]
[null,"SUBDIVISION","Underground connections","0's",2974]
[null,null,"Overhead connections","0's",225]
[null,null,"Distribution substation installed","MVA added",21.358000000000001]
[null,null,"Distribution substations installed","0's",89]
[null,null,"Distribution substation installed","total spend $0s",697310]
[null,null,"Augmentation HV","net circuit km added",15.797000000000001]
[null,null,"Augmentation HV","total spend $0s",2082001]
[null,null,"Augmentation LV","net circuit km added",80.042000000000002]
[null,null,"Augmentation LV","total spend $0s",2859966]
[null,null,"Cost per lot ($)","$0s",1763]
[null,"EMBEDDED GENERATION","Underground connections","0's",3446]
[null,null,"Overhead connections","0's",6256]
[null,null,"Distribution substation installed","MVA added",0.26]
[null,null,"Distribution substations installed","0's",4]
[null,null,"Distribution substation installed","total spend $0s",4878307]
[null,null,"Augmentation HV","net circuit km added",1.11514]
[null,null,"Augmentation HV","total spend $0s",15417144]
[null,null,"Augmentation LV","net circuit km added",-0.11]
[null,null,"Augmentation LV","total spend $0s",3025429]
[]
[]
[]
[null,"2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION"]
[null,null,null,"EXPENDITURE\n($0's)","VOLUMES\n(0's)"]
[null,"CONNECTION SUBCATEGORY","CONNECTION CLASSIFICATION",{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"RESIDENTIAL","Simple connection LV",4836626,9976]
[null,null,"Complex connection LV",730895,157]
[null,null,"Complex connection HV",12666411,1039]
[null,"COMMERCIAL/INDUSTRIAL","Simple connection LV",6111346,2350]
[null,null,"Complex connection HV (customer connected at LV, minor HV works)",21534214,744]
[null,null,"Complex connection HV (customer connected at LV, upstream asset works)",4874804,89]
[null,null,"Complex connection HV (customer connected at HV)",292180,7]
[null,null,"Complex connection sub-transmission",854508,18]
[null,"SUBDIVISION","Complex connection LV",1712837,227]
[null,null,"Complex connection HV (no upstream asset works)",2395583,71]
[null,null,"Complex connection HV (with upstream asset works)",1530857,139]
[null,"EMBEDDED GENERATION","Simple connection LV",3024981,10552]
[null,null,"Complex connection HV (small capacity)",200,1]
[null,null,"Complex connection HV (large capacity)",20295663,26]

{"sheet":"2.6 Non-network","index":9,"n_rows":94,"n_cols":6,"rows_kept":94,"cut":false,"hidden":false,"merged":[[89,2,93,2],[69,2,73,2],[74,2,78,2],[79,2,83,2],[84,2,88,2],[58,5,59,5],[61,2,61,4],[62,2,62,4],[63,2,63,4],[5,1,5,2],[60,2,60,4],[9,2,9,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.6 NON NETWORK EXPENDITURE"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.6.1 - NON-NETWORK EXPENDITURE"]
[null,null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","ASSET CATEGORY",null,null,{"$f":"CRY","v":"2017-18"}]
[null,"OPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,0]
[null,null,"Recurrent expenditure",null,null,61061321.654239036]
[null,null,"Non-recurrent expenditure",null,null,0]
[null,"MOTOR VEHICLES","Car",null,null,224249.49877242383]
[null,null,"Light commercial vehicle",null,null,8069032.3188056173]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,7175654.6203540117]
[null,null,"Heavy commercial vehicle",null,null,3215953.3820501883]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,31445936]
[null,"OTHER","Other expenditure",null,null,0]
[null,"OTHER - DNSP nominated","CRANE BORER PLANT HCV",null,null,2691498.2666107845]
[null,null,"OTHER FLEET ASSETS",null,null,1872615.4808986224]
[null,null,"EWP Hired",null,null,189999.74257863997]
[null,null,"Car Hired",null,null,80.599573573492137]
[null,null,"LCV Hired",null,null,0]
[null,null,"Other Hire",null,null,38718.539813379823]
[null,null,"Office Furniture and Equipment",null,null,0]
[null,null,"Plant and equipment ",null,null,0]
[null,null,"Refurbishment/Rebuild EWP (HVC)",null,null,0]
[]
[]
[null,"CAPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,1836058.9976082568]
[null,null,"Recurrent expenditure",null,null,1038931.243997067]
[null,null,"Non-recurrent expenditure",null,null,1505777.0777754684]
[null,"MOTOR VEHICLES","Car",null,null,217233.53786098605]
[null,null,"Light commercial vehicle",null,null,1688617.5002884592]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,6149914.9338054098]
[null,null,"Heavy commercial vehicle",null,null,2363689.3160167416]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,19041767.380196515]
[null,"OTHER","Other expenditure",null,null,0]
[null,"OTHER - DNSP nominated",{"$f":"IF(ISBLANK(C22),\"\",C22)","v":"CRANE BORER PLANT HCV"},null,null,1240928.4608440828]
[null,null,{"$f":"IF(ISBLANK(C23),\"\",C23)","v":"OTHER FLEET ASSETS"},null,null,1013775.3790618678]
[null,null,"EWP Hired",null,null,0]
[null,null,"Car Hired",null,null,0]
[null,null,"LCV Hired",null,null,0]
[null,null,"Other Hire",null,null,0]
[null,null,"Office Furniture and Equipment",null,null,495168.71607295674]
[null,null,"Plant and equipment ",null,null,5394221.5745068341]
[null,null,"Refurbishment/Rebuild EWP (HVC)",null,null,769459]
[null,null,""]
[null,null,""]
[]
[]
[]
[null,"2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE"]
[null,null,null,null,null,"VOLUMES\n(0's)"]
[]
[null,"NON-NETWORK CATEGORY","DESCRIPTOR METRIC",null,null,{"$f":"CRY","v":"2017-18"}]
[null,"IT & COMMUNICATIONS","Employee numbers",null,null,2635.1812251022866]
[null,null,"User numbers",null,null,3383.5526605893451]
[null,null,"Number of devices",null,null,3957.2392053234157]
[]
[]
[null,"2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES"]
[null,null,null,null,null,"VOLUMES / %"]
[null,"NON-NETWORK CATEGORY","ASSET CATEGORY","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2017-18"}]
[null,"MOTOR VEHICLES","CAR","Average kilometres travelled","0's",14301.75]
[null,null,null,"Number purchased","0's",8]
[null,null,null,"Number leased","0's",6]
[null,null,null,"Number in fleet","0's",61]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.92779999999999996]
[null,null,"LIGHT COMMERCIAL VEHICLE","Average kilometres travelled","0's",25629.96]
[null,null,null,"Number purchased","0's",29]
[null,null,null,"Number leased","0's",10]
[null,null,null,"Number in fleet","0's",791]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.92779999999999996]
[null,null,"ELEVATED WORK PLATFORM (LCV) ","Average kilometres travelled","0's",0]
[null,null,null,"Number purchased","0's",0]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",0]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0]
[null,null,"ELEVATED WORK PLATFORM (HCV)","Average kilometres travelled","0's",16763.36]
[null,null,null,"Number purchased","0's",21]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",161]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.92779999999999996]
[null,null,"HEAVY COMMERCIAL VEHICLE ","Average kilometres travelled","0's",17333.28]
[null,null,null,"Number purchased","0's",26]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",206]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.92779999999999996]

{"sheet":"2.7 Vegetation management","index":10,"n_rows":410,"n_cols":5,"rows_kept":410,"cut":false,"hidden":false,"merged":[[405,1,405,3],[5,1,5,2],[7,1,7,2],[12,4,13,4],[124,4,125,4],[14,1,19,1],[20,1,25,1],[26,1,31,1],[32,1,37,1],[38,1,43,1],[44,1,49,1],[50,1,55,1],[56,1,61,1],[62,1,67,1],[68,1,73,1],[74,1,79,1],[80,1,85,1],[86,1,91,1],[92,1,97,1],[98,1,103,1],[104,1,109,1],[110,1,115,1],[116,1,121,1],[126,1,131,1],[132,1,137,1],[138,1,143,1],[144,1,149,1],[150,1,155,1],[156,1,161,1],[162,1,167,1],[168,1,173,1],[174,1,179,1],[180,1,185,1],[186,1,191,1],[192,1,197,1],[198,1,203,1],[240,1,248,1],[249,1,257,1],[258,1,266,1],[204,1,209,1],[210,1,215,1],[216,1,221,1],[222,1,227,1],[228,1,233,1],[267,1,275,1],[276,1,284,1],[285,1,293,1],[294,1,302,1],[303,1,311,1],[312,1,320,1],[321,1,329,1],[330,1,338,1],[339,1,347,1],[348,1,356,1],[357,1,365,1],[366,1,374,1],[375,1,383,1],[384,1,392,1],[393,1,401,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.7 VEGETATION MANAGEMENT"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"Please enter a description for each Zone in table 2.7.1 - Urban and CBD.  The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2."]
[]
[]
["`","2.7.1 - DESCRIPTOR METRICS BY ZONE"]
[null,"URBAN AND CBD"]
[null,null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"ZONES","ASSET","UNITS"]
[null,"ZONE 1","Route line length within zone","km",5826.598]
[null,null,"Number of maintenance spans","0's",40183.514643216251]
[null,null,"Total length of maintenance spans","km",1622.1315171373619]
[null,null,"Length of vegetation corridors","km",1622.1315171373619]
[null,null,"Average number of trees per maintenance span","0's",4]
[null,null,"Average frequency of cutting cycle","years",1.1000000000000001]
[null,"ZONE 2","Route line length within zone","km",4358.2039999999997]
[null,null,"Number of maintenance spans","0's",25339.468758478703]
[null,null,"Total length of maintenance spans","km",1022.9058176120734]
[null,null,"Length of vegetation corridors","km",1022.9058176120734]
[null,null,"Average number of trees per maintenance span","0's",3.1]
[null,null,"Average frequency of cutting cycle","years",1]
[null,"ZONE 3","Route line length within zone","km",6464.4790000000003]
[null,null,"Number of maintenance spans","0's",23379.566257561008]
[null,null,"Total length of maintenance spans","km",943.78830772069705]
[null,null,"Length of vegetation corridors","km",943.78830772069705]
[null,null,"Average number of trees per maintenance span","0's",3]
[null,null,"Average frequency of cutting cycle","years",2]
[null,"ZONE 4","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 5","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 6","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 7","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 8","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 9","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 10","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 11","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 12","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 13","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 14","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 15","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 16","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 17","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,"ZONE 18","Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[]
[null,"RURAL"]
[null,null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"ZONES","ASSET","UNITS"]
[null,{"$f":"B15","v":"ZONE 1"},"Route line length within zone","km",31310.905999999999]
[null,null,"Number of maintenance spans","0's",24796.742565225326]
[null,null,"Total length of maintenance spans","km",5291.3365979819155]
[null,null,"Length of vegetation corridors","km",5291.3365979819155]
[null,null,"Average number of trees per maintenance span","0's",2.2999999999999998]
[null,null,"Average frequency of cutting cycle","years",3.5]
[null,{"$f":"B21","v":"ZONE 2"},"Route line length within zone","km",38548.716]
[null,null,"Number of maintenance spans","0's",32211.948184637844]
[null,null,"Total length of maintenance spans","km",6873.6552744109413]
[null,null,"Length of vegetation corridors","km",6873.6552744109413]
[null,null,"Average number of trees per maintenance span","0's",1.8]
[null,null,"Average frequency of cutting cycle","years",3.3]
[null,{"$f":"B27","v":"ZONE 3"},"Route line length within zone","km",53848.019]
[null,null,"Number of maintenance spans","0's",45560.51413975552]
[null,null,"Total length of maintenance spans","km",9722.0840703747635]
[null,null,"Length of vegetation corridors","km",9722.0840703747635]
[null,null,"Average number of trees per maintenance span","0's",2]
[null,null,"Average frequency of cutting cycle","years",3.5]
[null,{"$f":"B33","v":"ZONE 4"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B39","v":"ZONE 5"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B45","v":"ZONE 6"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B51","v":"ZONE 7"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B57","v":"ZONE 8"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B63","v":"ZONE 9"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B69","v":"ZONE 10"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B75","v":"ZONE 11"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B81","v":"ZONE 12"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B87","v":"ZONE 13"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B93","v":"ZONE 14"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B99","v":"ZONE 15"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B105","v":"ZONE 16"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B111","v":"ZONE 17"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[null,{"$f":"B117","v":"ZONE 18"},"Route line length within zone","km",0]
[null,null,"Number of maintenance spans","0's",0]
[null,null,"Total length of maintenance spans","km",0]
[null,null,"Length of vegetation corridors","km",0]
[null,null,"Average number of trees per maintenance span","0's",0]
[null,null,"Average frequency of cutting cycle","years",0]
[]
[]
[]
[null,"2.7.2 - EXPENDITURE METRICS BY ZONE"]
[null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"ZONES","SERVICE SUBCATEGORY",null,{"$f":"CRY","v":"2017-18"}]
[null,{"$f":"B15","v":"ZONE 1"},"Tree trimming (excluding hazard trees) ",null,4181606.69]
[null,null,"Hazard tree cutting ",null,700479.89]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,6896491.6200000001]
[null,null,"Inspection ",null,3612814.56]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B21","v":"ZONE 2"},"Tree trimming (excluding hazard trees) ",null,1975973.99]
[null,null,"Hazard tree cutting ",null,195575.01]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,6441289.6200000001]
[null,null,"Inspection ",null,3545383.7]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B27","v":"ZONE 3"},"Tree trimming (excluding hazard trees) ",null,1919291.11]
[null,null,"Hazard tree cutting ",null,449138.77]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,8123608.1500000004]
[null,null,"Inspection ",null,4437382]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B33","v":"ZONE 4"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B39","v":"ZONE 5"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B45","v":"ZONE 6"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B51","v":"ZONE 7"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B57","v":"ZONE 8"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B63","v":"ZONE 9"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B69","v":"ZONE 10"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B75","v":"ZONE 11"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B81","v":"ZONE 12"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B87","v":"ZONE 13"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B93","v":"ZONE 14"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B99","v":"ZONE 15"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B105","v":"ZONE 16"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B111","v":"ZONE 17"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[null,{"$f":"B117","v":"ZONE 18"},"Tree trimming (excluding hazard trees) ",null,0]
[null,null,"Hazard tree cutting ",null,0]
[null,null,"Ground clearance ",null,0]
[null,null,"Vegetation corridor clearance ",null,0]
[null,null,"Inspection ",null,0]
[null,null,"Audit ",null,0]
[null,null,"Contractor liaison expenditure ",null,0]
[null,null,"Tree replacement program costs ",null,0]
[null,null,"Other vegetation management costs not specified in sheet ",null,0]
[]
[null,"2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS"]
[null,null,null,null,"VOLUMES\n(0's)"]
[null,"DESCRIPTOR METRIC",null,null,{"$f":"CRY","v":"2017-18"}]
[null,"Number of fire starts caused by vegetation grow-ins (NSP responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility)",null,null,8]
[null,"Number of fire starts caused by vegetation grow-ins (other party responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility)",null,null,0]

{"sheet":"2.8 Maintenance","index":11,"n_rows":85,"n_cols":10,"rows_kept":85,"cut":false,"hidden":false,"merged":[[8,7,9,7],[8,8,10,8],[8,9,10,9],[68,1,69,1],[5,1,5,2],[28,1,29,1],[48,5,48,6],[8,5,8,6]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.8 MAINTENANCE"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"ASSET QUANTITY\n(0's)",null,"AVERAGE AGE OF ASSET GROUP ","INSPECTION \nCYCLE \n(YEARS)","MAINTENANCE \nCYCLE \n(YEARS)"]
[null,null,null,null,null," AT YEAR END","INSPECTED / MAINTAINED"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units",{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",973700,15342.6,30.578484132689741,4.5,"                             -  "]
[null,null,"Service lines","Number of customers","Number",400485,140.08000000000001,31.123091161499307,4.5,"                             -  "]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",973700,273235.03999999998,30.578484132689741,4.5,"                             -  "]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",143166,70.040000000000006,28.505413296453067,0,"                             -  "]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",8720,70.040000000000006,11,0,"                             -  "]
[null,null,"33 KV and above","Length (KM)","KM",90,0,16,0,"                             -  "]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",0,0,0,0,"                             -  "]
[null,null,"Non-CBD","Length (KM)","KM",8810,70.040000000000006,11.56299659477866,0,"                             -  "]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",101308,3701.04,22.591740040273226,1,"                             -  "]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",18082,4009.04,18.177745824576927,12,"                             -  "]
[null,null,"Distribution substation - other equipment","Earth mat","Number",101308,16597.099999999999,22.908141509061476,4.5,"                             -  "]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",99515,36.020000000000003,0,0,"                             -  "]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",592,648.54999999999995,38.155405405405403,1.5,12]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",445,45.11,29.440449438202247,0.5,"                             -  "]
[null,null,"Transformers - HV","Number of HV transformers","Number",0,0,0,0,"                             -  "]
[null,null,"Zone substation - other equipment","<DNSP to nominate>","Number",17437,7123.9,22.030681883351495,1.5,12]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",465,1309.44,0,1.5,"                             -  "]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",0,0,0,0,"                             -  "]
[null,null,"Major roads","Number of public lights maintained","Number",0,0,0,0,"                             -  "]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",845,1794,13,4,"                             -  "]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",6773,1287,26.102022737339436,6,"                             -  "]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets","<DNSP to nominate>","Number",0,0,0,0,"                             -  "]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number",0,0,0,0,"                             -  "]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",0,465,0,4.5,"                             -  "]
[null,"Other","< DNSP to nominate >","< DNSP to nominate >"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"EXPENDITURE ($0'S)"]
[null,null,null,null,null," ROUTINE MAINTENANCE ","NON-ROUTINE MAINTENANCE"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units",{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",1336434.1700000002,10150111.549999984]
[null,null,"Service lines","Number of customers","Number",0,461340.23999999918]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",26197794.879999992,230670.11999999959]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",0,230670.11999999959]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",83200.3,230670.11999999959]
[null,null,"33 KV and above","Length (KM)","KM",0,0]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",0,0]
[null,null,"Non-CBD","Length (KM)","KM",83200.3,230670.11999999959]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",706946.57000000041,230670.11999999959]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",2310278.34,230670.11999999959]
[null,null,"Distribution substation - other equipment","Earth mat","Number",2947390.1200000006,576675.299999999]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",405.8,115335.05999999979]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",1002234.8300000001,585902.8679999992]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",14352.499999999998,117180.57359999983]
[null,null,"Transformers - HV","Number of HV transformers","Number",0,0]
[null,null,"Zone substation - other equipment",{"$f":"IF(ISBLANK(D27),\"\",D27)","v":"<DNSP to nominate>"},{"$f":"IF(ISBLANK(E27),\"\",E27)","v":"Number"},4167757.1199999992,10842677.723999985]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",2042068.0199999947,468722.29439999931]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",0,0]
[null,null,"Major roads","Number of public lights maintained","Number",0,0]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",1322.24,943951.94000000099]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",1453059.1600000011,1297332.17]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets",{"$f":"IF(ISBLANK(D33),\"\",D33)","v":"<DNSP to nominate>"},{"$f":"IF(ISBLANK(E33),\"\",E33)","v":"Number"},0,0]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number",6157918.21,447523.1]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",1093996.49,4621889.3600000003]
[null,"Other",{"$f":"IF(ISBLANK(C36),\"\",C36)","v":"< DNSP to nominate >"},"< DNSP to nominate >"]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]

{"sheet":"2.9 Emergency Response","index":12,"n_rows":380,"n_cols":3,"rows_kept":380,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.9 EMERGENCY RESPONSE"]
[]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2017-18"}]
[null,"(A) TOTAL EMERGENCY RESPONSE EXPENDITURE"]
[null,"Total Expenditure",55329909.979998901]
[null,"(B) MAJOR EVENTS O&M EXPENDITURE"]
[null,"PWO(00050983) CYCLONE DEBBIE- WE  F&L RESPONSE        ",969.05]
[null,"PWO(00050998) TC DEBBIE - ZONE2, BURDEKIN/WHITSUNDAYS ",71390.080000000016]
[null,"PWO(00051002) TC DEBBIE - ZONE 3, MACKAY SARINA       ",13602.35]
[null,"PWO(00051013) TC DEBBIE - ASSET MANAGEMENT RESPONSE   ",10400]
[null,"PWO(00051055) TC DEBBIE - EXTERNAL CONTRACTORS        ",28414.730000000003]
[null,"PWO(00051060) TC DEBBIE - IR ZONE FITZROY             ",6913.2999999999993]
[null,"PWO(00057181) BUNDABERG STORM 7.11.17                 ",877097.09000000299]
[null,"PWO(00060274) CYCLONE LINDA - 13.03.18                ",348258.1]
[null,"PWO(00060684) TROPICAL CYCLONE NORA                   ",517147.31999999989]
[null,"PWO(00060806) TC IRIS 2018                            ",164502.25999999983]
[]
[]
[]
[]
[]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,"(C) MAJOR EVENT DAYS O&M EXPENDITURE"]
[null,"Declared STPIS MED due to Severe Storms and Heavy Rain (19 Oct 2017)",157512.46000000072]
[null,"Declared STPIS MED due to Severe Storms, Lighting and Heavy Rain (7 Nov 2017)",200427.18000000078]
[null,"Declared STPIS MED due to Severe Storms (26 Dec 2017)",0]
[null,"Declared STPIS MED due to Severe Storms (31 Dec 2017)",-167.35999999999984]
[null,"Declared STPIS MED due to Severe Storms (1 Jan 2018)",0]
[null,"Declared STPIS MED due to Severe Storms (2 Jan 2018)",392541.14999999927]
[null,"Declared STPIS MED due to Severe Storms (16 Feb 2018)",428883.53999999881]
[null,"Declared STPIS MED due to Severe Storms (20 Feb 2018)",159081.33999999985]
[null,"Declared STPIS MED due to Fault (17 Apr 2018)",114861.03999999994]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]
[null,null,""]

{"sheet":"2.10 Overheads","index":13,"n_rows":174,"n_cols":4,"rows_kept":174,"cut":false,"hidden":false,"merged":[[5,1,8,2],[10,1,10,2],[106,1,106,3],[152,1,152,3],[17,1,17,3],[12,1,12,2],[78,1,78,3]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.10 OVERHEADS"]
[]
[null,{"$f":"CONCATENATE(\"Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. \",dms_TradingName, \" is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If \",dms_TradingName,\" is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. \n\n\",dms_TradingName, \" is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN.\")","v":"Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. Ergon Energy is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If Ergon Energy is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. \n\nErgon Energy is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN."},null,"Choose Response\ndrop down selection"]
[null,null,null,"Worksheet 2.10"]
[]
[]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,{"$f":"CONCATENATE(\"Instructions\nPlease enter a description for each expenditure category as currently reported under \",dms_TradingName,\"'s annual RIN.\")","v":"Instructions\nPlease enter a description for each expenditure category as currently reported under Ergon Energy's annual RIN."}]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"NETWORK OVERHEADS"]
[null,"Standard Control Services","NETWORK MANAGEMENT ",6987255]
[null,null,"NETWORK PLANNING ",10458117]
[null,null,"NETWORK CONTROL AND OPERATIONAL SWITCHING ",27283944]
[null,null,"QUALITY AND STANDARD FUNCTIONS ",5841869]
[null,null,"PROJECT GOVERNANCE AND RELATED FUNCTIONS ",7822644]
[null,null,"OTHER ",0]
[null,null,0,0]
[null,null,0,0]
[null,null,"   NON-NETWORK ALTERNATIVES/ DEMAND MANAGEMENT",6112985]
[null,null,"OTHER ",53731085]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","NETWORK MANAGEMENT ",1172664]
[null,null,"NETWORK PLANNING ",1533466]
[null,null,"NETWORK CONTROL AND OPERATIONAL SWITCHING ",32478]
[null,null,"QUALITY AND STANDARD FUNCTIONS ",436508]
[null,null,"PROJECT GOVERNANCE AND RELATED FUNCTIONS ",1066693]
[null,null,"OTHER ",0]
[null,null,"   METER READING",9649887]
[null,null,"   FEED-IN TARIFFS/ SOLAR BONUS",0]
[null,null,"   NON-NETWORK ALTERNATIVES/ DEMAND MANAGEMENT",0]
[null,null,"OTHER ",37388678]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total  ",0]
[null,"Unregulated Services","Total  ",9410321.5488041826]
[]
[]
[null,"CAPITALISED NETWORK OVERHEADS"]
[null,"Standard Control Services","NETWORK MANAGEMENT ",10419249]
[null,null,"NETWORK PLANNING ",15640522]
[null,null,"NETWORK CONTROL AND OPERATIONAL SWITCHING ",898711]
[null,null,"QUALITY AND STANDARD FUNCTIONS ",8985284]
[null,null,"PROJECT GOVERNANCE AND RELATED FUNCTIONS ",11831367]
[null,null,"OTHER ",0]
[null,null,"   METER READING",0]
[null,null,"   FEED-IN TARIFFS/ SOLAR BONUS",0]
[null,null,"   NON-NETWORK ALTERNATIVES/ DEMAND MANAGEMENT",0]
[null,null,"OTHER ",29851110]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"CORPORATE OVERHEADS"]
[null,"Standard Control Services","ASSET MANAGEMENT",685428]
[null,null,"CORPORATE GOVERNANCE",0]
[null,null,"CORPORATE",-2539868]
[null,null,"CUSTOMER AND STAKEHOLDER ENGAGEMENT",0]
[null,null,"CUSTOMER SERVICE/RETAIL",0]
[null,null,"EMPLOYEE AND SHARED SERVICES",8434109]
[null,null,"ENERGY SOLUTIONS AND MARKET DEVELOPMENT",0]
[null,null,"FINANCE AND STRATEGIC SERVICES",24208106]
[null,null,"OFFICE OF THE CHIEF EXECUTIVE",617228]
[null,null,"OPERATIONS",2988494]
[null,null,"SPARQ SERVICES",34635088]
[null,null,"MAJOR PROJECTS",0]
[null,null,"STRATEGY REVENUE & TRANSFORMATION",1800222]
[null,null,"Corporate Restructure",14340451]
[null,null,"Self Insurance",1384955]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","ASSET MANAGEMENT",38471]
[null,null,"CORPORATE GOVERNANCE",0]
[null,null,"CORPORATE",-585717]
[null,null,"CUSTOMER AND STAKEHOLDER ENGAGEMENT",0]
[null,null,"CUSTOMER SERVICE/RETAIL",0]
[null,null,"EMPLOYEE AND SHARED SERVICES",1944984]
[null,null,"ENERGY SOLUTIONS AND MARKET DEVELOPMENT",0]
[null,null,"FINANCE AND STRATEGIC SERVICES",5198940]
[null,null,"OFFICE OF THE CHIEF EXECUTIVE",142339]
[null,null,"OPERATIONS",700273]
[null,null,"SPARQ SERVICES",7987175]
[null,null,"MAJOR PROJECTS",0]
[null,null,"STRATEGY REVENUE & TRANSFORMATION",415148]
[null,null,"Corporate Restructure",0]
[null,null,"Self Insurance",0]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total",0]
[null,"Unregulated Services","Total",10610027.451242084]
[]
[null,"CAPITALISED CORPORATE OVERHEADS"]
[null,"Standard Control Services","ASSET MANAGEMENT",1063818]
[null,null,"CORPORATE GOVERNANCE",0]
[null,null,"CORPORATE",-3609147]
[null,null,"CUSTOMER AND STAKEHOLDER ENGAGEMENT",0]
[null,null,"CUSTOMER SERVICE/RETAIL",0]
[null,null,"EMPLOYEE AND SHARED SERVICES",11984848]
[null,null,"ENERGY SOLUTIONS AND MARKET DEVELOPMENT",0]
[null,null,"FINANCE AND STRATEGIC SERVICES",34687832]
[null,null,"OFFICE OF THE CHIEF EXECUTIVE",877079]
[null,null,"OPERATIONS",4314142]
[null,null,"SPARQ SERVICES",49216372]
[null,null,"MAJOR PROJECTS",0]
[null,null,"STRATEGY REVENUE & TRANSFORMATION",2558110]
[null,null,"Corporate Restructure",0]
[null,null,"Self Insurance",0]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]

{"sheet":"2.10(A) Overheads","index":14,"n_rows":37,"n_cols":4,"rows_kept":37,"cut":false,"hidden":false,"merged":[[8,1,8,2],[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.10(A) OVERHEADS"]
[]
[null,"This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options."]
[]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"OPEX"]
[null,"Standard Control Services","Total  ",""]
[null,"Alternative Control Services","Total  "]
[null,"CAPEX"]
[null,"Standard Control Services","Total  ",""]
[null,"Alternative Control Services","Total  ",""]
[null,"OTHER DISTRIBUTION SERVICES"]
[null,"Negotiated Services","Total  ",""]
[null,"Unregulated Services","Total  ",""]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"}]
[null,"OPEX"]
[null,"Standard Control Services","Total",""]
[null,"Alternative Control Services","Total",""]
[null,"CAPEX"]
[null,"Standard Control Services","Total",""]
[null,"Alternative Control Services","Total",""]
[null,"OTHER DISTRIBUTION SERVICES"]
[null,"Negotiated Services","Total",""]
[null,"Unregulated Services","Total",""]

{"sheet":"2.11 Labour","index":15,"n_rows":55,"n_cols":7,"rows_kept":55,"cut":false,"hidden":false,"merged":[[36,1,36,2],[5,1,5,2],[11,1,11,2],[33,5,33,6],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,6,9,6],[33,3,33,4],[10,1,10,2],[35,1,35,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.11 LABOUR"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.11.1 - COST METRICS PER ANNUM"]
[null,null,null,"ASL \n(0's)","TOTAL LABOUR EXPENDITURE\n($0's)","AVERAGE PRODUCTIVE WORK HOURS \nPER ASL \n(0's)","STAND-DOWN OCCURENCES \nPER ASL \n(0's)"]
[]
[null,null,null,{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"INTERNAL LABOUR EXPENDITURE"]
[null,"CORPORATE OVERHEADS","Executive manager",-7.2168542944492334E-2,277899,0,0]
[null,null,"Senior manager",19.122606186998389,6388136,1885,0]
[null,null,"Manager",30.150427351853342,7337826,1885,0.02]
[null,null,"Professional",133.17222600176561,25200454,1885,1.7000000000000001E-2]
[null,null,"Semi professional",36.519104290903798,6384679,1885,2.2999999999999998]
[null,null,"Support staff",121.35049735519695,15988858,1885,0]
[null,null,"Intern, junior staff, apprentice",8.1388883047878888,1013564,1885,0]
[null,"NETWORK OVERHEADS ","Executive manager",0,0,0,0]
[null,null,"Senior manager",16.354636024128933,6651082.2298515951,1885,0]
[null,null,"Manager",45.451728921334421,10263808.939461673,1885,0]
[null,null,"Professional",169.26849286754071,31962516.681812406,1885,9.3700000000000006E-2]
[null,null,"Semi professional",223.76772083255841,40569075.10477902,1885,0.39200000000000002]
[null,null,"Support staff",164.89023771200127,21596523.303754732,1885,0.27200000000000002]
[null,null,"Intern, junior staff, apprentice",211.05670276354189,25079336.108581278,1885,0]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker",667.56686769230646,107696304.39331256,1885,7.42]
[null,null,"Skilled non electical worker",291.11204737400521,48327161.875231728,1885,0]
[null,null,"Apprentice",112.15676185676394,11194243.073519651,1885,2.59]
[null,null,"Unskilled worker",64.613280848806369,8272588.3988361703,1885,1.4]
[]
[]
[null,"2.11.2 - DESCRIPTOR METRICS"]
[null,null,null,"ORDINARY TIME (0's)",null,"OVERTIME (0's)"]
[null,null,null,"PER ASL","HOURLY RATE\nPER ASL","PER ASL","HOURLY RATE\nPER ASL"]
[null,null,null,{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"AVERAGE PRODUCTIVE WORK HOURS PER ASL"]
[null,"CORPORATE OVERHEADS","Executive manager",0,0,0,0]
[null,null,"Senior manager",1885,130.20367803499198,-0.17306794224418809,142.34477416179732]
[null,null,"Manager",1881.8707997910776,108.50789007273876,3.1292002089223843,187.26952325385207]
[null,null,"Professional",1882.8061307239043,93.548913090973258,2.1938692760959384,182.50145972994079]
[null,null,"Semi professional",1787.9501761319391,88.659845540642621,97.049823868061139,168.07666319536199]
[null,null,"Support staff",1878.4382761516219,66.970762195242912,6.5617238483780511,93.820211314326144]
[null,null,"Intern, junior staff, apprentice",1636.828075239928,56.629199978733944,248.17192476007199,128.30295506939532]
[null,"NETWORK OVERHEADS ","Executive manager",0,0,0,0]
[null,null,"Senior manager",1884.4210322073491,148.92452601792533,0.57896779265092846,378.72715285303161]
[null,null,"Manager",1872.4612894145625,110.04005807527484,12.538710585437457,106.65009393095055]
[null,null,"Professional",1873.6921961331268,95.600158287190467,11.307803866873428,152.18692576180223]
[null,null,"Semi professional",1825.8662831834577,91.15755399342379,59.133716816542346,139.454959251834]
[null,null,"Support staff",1852.7852195806861,67.46752408239341,32.214780419313911,124.68327655466383]
[null,null,"Intern, junior staff, apprentice",1803.4615475144724,62.487108254773055,81.538452485527841,59.425571855239717]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker",1509.03,76.61,375.97,121.59]
[null,null,"Skilled non electical worker",1703.38,85.1,181.62,115.88]
[null,null,"Apprentice",1611.45,50.47,273.55,67.53]
[null,null,"Unskilled worker",1577.24,62.26,307.76,96.93]

{"sheet":"2.12 Input tables","index":16,"n_rows":82,"n_cols":9,"rows_kept":82,"cut":false,"hidden":false,"merged":[[9,3,9,8],[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"2.12 INPUT TABLES"]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.12.1 - INPUT TABLES"]
[null,null,null,"DIRECT MATERIAL EXPENDITURE","DIRECT LABOUR EXPENDITURE","CONTRACT EXPENDITURE","OTHER EXPENDITURE","RELATED PARTY CONTRACT EXPENDITURE","RELATED PARTY CONTRACT MARGIN\nEXPENDITURE"]
[null,null,null,"EXPENDITURE ($0's)"]
[null,null,null,{"$f":"CRY","v":"2017-18"},"2017-18","2017-18","2017-18","2017-18","2017-18"]
[null,"VEGETATION MANAGEMENT",{"$f":"'2.7 Vegetation management'!B15","v":"ZONE 1"},59930.596656088899,788640.96583308722,14340554.68102226,202266.51648856327,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B21","v":"ZONE 2"},224658.19826783508,510892.39017777174,11285227.308198757,137444.42335563712,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B27","v":"ZONE 3"},292515.47648154525,651095.56059662683,13794079.397181101,191729.59574072808,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B33","v":"ZONE 4"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B39","v":"ZONE 5"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B45","v":"ZONE 6"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B51","v":"ZONE 7"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B57","v":"ZONE 8"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B63","v":"ZONE 9"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B69","v":"ZONE 10"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B75","v":"ZONE 11"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B81","v":"ZONE 12"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B87","v":"ZONE 13"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B93","v":"ZONE 14"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B99","v":"ZONE 15"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B105","v":"ZONE 16"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B111","v":"ZONE 17"},0,0,0,0,0,0]
[null,null,{"$f":"'2.7 Vegetation management'!B117","v":"ZONE 18"},0,0,0,0,0,0]
[null,"ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",21122.599067424173,274654.30778270104,817409.96126654989,223247.3018833251,0,0]
[null,null,"Pole inspection and treatment",414061.18619434693,5383981.7775682779,16023489.206452878,4376262.709784491,0,0]
[null,null,"Overhead asset inspection",0,0,0,0,0,0]
[null,null,"Network underground cable maintenance",1314.9967418069018,17098.725337001117,50888.218459997421,13898.359461194566,0,0]
[null,null,"Distribution substation equipment & property maintenance",94278.301355407399,1225888.0412890392,3648415.728254287,996438.75910126651,0,0]
[null,null,"Zone substation equipment maintenance",81939.561037095933,1065449.0645220764,3170926.7027099077,866029.121730919,0,0]
[null,null,"Zone substation property maintenance",32275.277767604974,419671.08524192357,1249000.3462960362,341121.31069442979,0,0]
[null,null,"Public lighting maintenance",0,0,0,0,0,0]
[null,null,"Scada & network control maintenance",20.898257480883576,271.73722438015676,808.72830959199644,220.87620854696331,0,0]
[null,null,"Protection systems maintenance",22965.879462606204,298622.23423778015,888741.89118765667,242729.15511195804,0,0]
[null,null,"Subtransmission asset maintenance - for dnsps with dual function assets",0,0,0,0,0,0]
[null,null,"Other",114617.9064542024,1490361.1840661736,4435525.1063621966,1211410.5031174282,0,0]
[null,"NON-ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",1563523.7619764353,5372766.4963219995,1807896.029800911,1867265.501900638,0,0]
[null,null,"Pole inspection and treatment",33987.6409878083,116792.37836301522,39299.768061397343,40590.332587778736,0,0]
[null,null,"Overhead asset inspection",33987.6409878083,116792.37836301522,39299.768061397343,40590.332587778736,0,0]
[null,null,"Network underground cable maintenance",33987.6409878083,116792.37836301522,39299.768061397343,40590.332587778736,0,0]
[null,null,"Distribution substation equipment & property maintenance",169938.20493904152,583961.89181507612,196498.84030698671,202951.66293889366,0,0]
[null,null,"Zone substation equipment maintenance",1701187.7629724734,5845823.9261407722,1967076.3421823718,2031673.1343043651,0,0]
[null,null,"Zone substation property maintenance",69062.976449004287,237322.42197101828,79857.232723189329,82479.663256787448,0,0]
[null,null,"Public lighting maintenance",0,0,0,0,0,0]
[null,null,"SCADA & network control maintenance",139084.76592661958,477939.63142249436,160823.13696765824,166104.40568322898,0,0]
[null,null,"Protection systems maintenance",191152.88983200063,656862.31775988941,221029.29230534667,228287.67010276314,0,0]
[null,null,"Subtransmission asset maintenance - for DNSP with dual function assets",0,0,0,0,0,0]
[null,null,"Other",746942.7367081719,2566733.5591905219,863686.78303699708,892049.38106430927,0,0]
[null,"OVERHEADS","Network overheads",5254301.0469501885,136122342.36824071,21621885.745870724,84145986.462556526,0,0]
[null,null,"Corporate overheads",-932539.61922389781,62591416,12229763.645631764,129600240.44676113,0,0]
[null,"AUGMENTATION","Subtransmission substations, switching stations, zone substations",2753127.9824704072,2854367.5610440001,2274063.6781094642,1811514.7783761285,0,0]
[null,null,"Subtransmission lines",314878.12362338003,326456.99999260355,260087.03864201377,207184.83774200271,0,0]
[null,null,"HV feeders",6046609.657716793,6268959.0063282484,4994455.5741216652,3978573.7618332952,0,0]
[null,null,"Distribution substations",897656.02167228784,930665.13636538852,741457.34136539861,590643.50059692538,0,0]
[null,null,"LV feeders",610827.32322701591,633289.01087048289,504538.9237956783,401914.74210682302,0,0]
[null,null,"Other assets",550632.470030503,570880.63850278873,454818.4131129561,362307.47835375229,0,0]
[null,"CONNECTIONS","Simple and complex customer connections",26493181.52584406,26340270.605165824,17934397.364823606,8910510.7859548666,1182744.7182116276,0]
[null,"EMERGENCY RESPONSE","Major storms",210093.58325930679,1223570.5228709811,150616.23120917653,439105.96926161187,15307.973398926195,0]
[null,null,"Major event days",149750.38484759934,872135.90175173059,107356.15166328527,312985.70315993513,10911.208577449321,0]
[null,"PUBLIC LIGHTING","All public lighting services",2217142.788643159,3405841.7760471092,4931760.2347811414,1639844.9210207118,0,0]
[null,"METERING","All metering services",4721644.5396177359,10538761.892949274,19217388.646592759,2839581.2508402318,0,0]
[null,"FEE-BASED SERVICES","All fee-based services",493316.22256622859,1223362.7757319547,1285374.0749139672,336847.37141817372,23011.485369675735,0]
[null,"QUOTED SERVICES","All quoted services",8668232.4012025353,16228674.259891225,13308039.527573032,15414045.886878647,933593.92637716327,0]
[null,"REPLACEMENT","Poles",11949137.120923713,17277477.561220847,10679709.048023319,7021005.2519534593,24646.37759982295,0]
[null,null,"Pole top structures",7280386.4494471857,10526844.929838438,6506947.5938239899,4277767.5894531943,15016.578326104156,0]
[null,null,"Overhead conductors",3391756.1618579319,4904202.73753649,3031429.6843287735,1992908.5744652674,6995.8610605695876,0]
[null,null,"Underground cables",1376962.2170421239,1990975.0442093106,1230679.3117622391,809067.53849744762,2840.1323374625467,0]
[null,null,"Service lines",1428523.9483784549,2065529.1017254146,1276763.3329858398,839363.88398655353,2946.4839415453694,0]
[null,null,"Transformers",10974197.0617289,15867793.763486376,9808342.6835658383,6448155.5803264994,22635.459104793448,0]
[null,null,"Switchgear",9656874.1899428479,13963052.347613567,8630966.8738643564,5674130.5852385517,19918.339316949521,0]
[null,null,"Public lighting",866887.98601500853,1253449.3139458101,774793.30717995076,509361.05603885034,1788.0494987929549,0]
[null,null,"SCADA network control and protection systems",1957224.3286709001,2829986.724453365,1749296.7199544639,1150014.6120833189,4036.9852118873309,0]
[null,null,"Other",2402008.4596639741,3473108.2959150788,2146828.7810658957,1411358.3131460205,4954.4002128139409,0]
[null,"NON-NETWORK EXPENDITURE","IT and communications",2639133.4441470308,789566.8366761877,716543.61169517599,235523.4268623963,61061321.654239036,0]
[null,null,"Motor vehicles",17078304.578551389,0,18913688.701947834,-3.7252902984619141E-9,0,0]
[null,null,"Buildings and property",466993.00096332259,912660.5431800487,17847445.198526457,31260604.637526684,0,0]
[null,null,"Other",6818817.5874153571,0,0,0,0,0]

{"sheet":"4.1 Public lighting","index":17,"n_rows":539,"n_cols":5,"rows_kept":539,"cut":false,"hidden":false,"merged":[[6,1,6,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"4.1 PUBLIC LIGHTING"]
[]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.1.1 - DESCRIPTOR METRICS OVER YEAR"]
[null,null,null,null,"VOLUME \n(0's)"]
[null,null,"LIGHT TYPE",null,{"$f":"CRY","v":"2017-18"}]
[null,"POPULATION OF LIGHTS","C1X26",null,3]
[null,null,"C1X32",null,59]
[null,null,"C1X42",null,0]
[null,null,"C2X24",null,1]
[null,null,"F13",null,5]
[null,null,"F18",null,4]
[null,null,"F1X20",null,14]
[null,null,"F1X40",null,23]
[null,null,"F2X20",null,4]
[null,null,"F2X40",null,3]
[null,null,"F3X20",null,2]
[null,null,"F3X40",null,1]
[null,null,"H100",null,4]
[null,null,"H1000",null,2]
[null,null,"H150",null,23]
[null,null,"H1500",null,2]
[null,null,"H250",null,45]
[null,null,"H35",null,6]
[null,null,"H400",null,30]
[null,null,"H70",null,45]
[null,null,"H75",null,11]
[null,null,"I200",null,2]
[null,null,"L120525",null,0]
[null,null,"L120700",null,0]
[null,null,"L135",null,5]
[null,null,"L20D700",null,0]
[null,null,"L35",null,1]
[null,null,"L55",null,2]
[null,null,"L60D350",null,0]
[null,null,"L90",null,19]
[null,null,"LD700R",null,0]
[null,null,"LECO18",null,16]
[null,null,"LED17",null,1]
[null,null,"LED175",null,0]
[null,null,"LED25",null,32]
[null,null,"LED30",null,0]
[null,null,"LGE237",null,0]
[null,null,"LL60350",null,0]
[null,null,"LRL2120",null,0]
[null,null,"LSYL25",null,188]
[null,null,"M100",null,2]
[null,null,"M1000",null,0]
[null,null,"M125",null,2329]
[null,null,"M150",null,29]
[null,null,"M250",null,1820]
[null,null,"M400",null,1729]
[null,null,"M50",null,20806]
[null,null,"M500",null,1]
[null,null,"M70",null,31]
[null,null,"M700",null,1]
[null,null,"M80",null,35362]
[null,null,"S100",null,441]
[null,null,"S1000",null,15]
[null,null,"S125",null,7]
[null,null,"S150",null,9904]
[null,null,"S220",null,1]
[null,null,"S250",null,10937]
[null,null,"S310",null,6]
[null,null,"S360",null,10]
[null,null,"S400",null,999]
[null,null,"S50",null,69]
[null,null,"S70",null,5445]
[null,null,"S80",null,54]
[null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"4.1.2 - DESCRIPTOR METRICS ANNUALLY"]
[]
[]
[null,null,null,null,"VOLUMES \n& EXPENDITURE"]
[null,"SERVICE/SERVICE QUALITY ","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2017-18"}]
[null,"LIGHT INSTALLATION","Major road light installation","0's",493]
[null,null,"Minor road light installation","0's",300]
[null,null,"Number of poles installed","0's",167]
[null,null,"Total cost","$0s",2792234.12]
[null,"LIGHT REPLACEMENT","Major road light replacement","0's",3376]
[null,null,"Minor road light replacement","0's",5187]
[null,null,"Number of poles replaced","0's",136]
[null,null,"Total cost","$0s",2442662.39]
[null,"LIGHT MAINTENANCE","Major road light maintenance","0's",29241]
[null,null,"Minor road light maintenance","0's",45870]
[null,null,"Number of poles installed","0's",33]
[null,null,"Total cost","$0s",8771025]
[null,"QUALITY OF SUPPLY","Mean days to rectify/replace public lighting assets","days",8.8000000000000007]
[null,null,"GSO breaches","0's",0]
[null,null,"GSL payments","$0s",0]
[null,null,"Customer complaints","0's",50]
[]
[]
[null,"4.1.3 - COST METRICS"]
[null,null,null,null,"AVERAGE UNIT COST \n($)"]
[null,"ACTIVITY TYPE","LIGHT TYPE",null,{"$f":"CRY","v":"2017-18"}]
[null,"LIGHT INSTALLATION","Major road luminaire",null,2534.31]
[null,null,"Minor road luminaire",null,1216.98]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,"LIGHT REPLACEMENT","Major road luminaire",null,559.08000000000004]
[null,null,"Minor road luminaire",null,756.63]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,"LIGHT MAINTENANCE","Major road luminaire",null,265.52]
[null,null,"Minor road luminaire",null,95.2]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]

{"sheet":"4.2 Metering","index":18,"n_rows":61,"n_cols":5,"rows_kept":61,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"4.2 METERING"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.2.1 - METERING DESCRIPTOR METRIC"]
[null,null,null,"VOLUMES\n(0's)"]
[null,"Asset Category","Asset Subcategory",{"$f":"CRY","v":"2017-18"}]
[null,"Meter Type 4","Single phase meter population ",0]
[null,null,"Multi phase meter population ",0]
[null,null,"Current transformer connected meter population ",0]
[null,null,"Direct connect meter population ",0]
[null,"Meter Type 5","Single phase meter population ",0]
[null,null,"Multi phase meter population ",0]
[null,null,"Current transformer connected meter population ",0]
[null,null,"Direct connect meter population ",0]
[null,"Meter Type 6","Single phase meter population ",1072926]
[null,null,"Multi phase meter population ",75533]
[null,null,"Current transformer connected meter population ",9330]
[null,null,"Direct connect meter population ",1139129]
[]
[]
[null,"4.2.2 - COST METRICS"]
[null,null,null,"VOLUMES\n(0's)","EXPENDITURE\n($0's)"]
[null,"Service Subcategory","Meter Type",{"$f":"CRY","v":"2017-18"},{"$f":"CRY","v":"2017-18"}]
[null,"Meter purchase ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",3137,639033]
[null,"Meter testing ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",2786,1717732]
[null,"Meter investigation ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",14585,1385378]
[null,"Scheduled meter reading ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",3105992,9649887.3300000075]
[null,"Special meter reading ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",127061,2461774]
[null,"New meter installation ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",3672,1005501]
[null,"Meter replacement ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",4502,1300418]
[null,"Meter maintenance ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",9538,3401608]
[null,"Remote meter reading ","Meter Type 4",0,0]
[null,"Remote meter re-configuration ","Meter Type 4",0,0]
[null,"Other metering ","Meter Type 4",null,0]
[null,null,"Meter Type 5",null,0]
[null,null,"Meter Type 6",null,16395078]
[null,null,"Meter Type 7",null,0]
[null,"IT infrastructure capex ","Meter Type 4",null,0]
[null,"IT infrastructure opex ","Meter Type 4",null,0]
[null,"Communications infrastructure capex ","Meter Type 4",null,0]
[null,"Communications infrastructure opex ","Meter Type 4",null,0]

{"sheet":"4.3 Fee-based services","index":19,"n_rows":479,"n_cols":6,"rows_kept":479,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"4.3 ANCILLARY SERVICES - FEE BASED SERVICES"]
[]
[null,"4.3.1 - COST METRICS FOR FEE-BASED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY",{"$f":"CRY","v":"2017-18"},null,{"$f":"CRY","v":"2017-18"}]
[null,"Common Fee-Based Services","Energisation",0,"ED_FEE431_00001",0]
[null,null,"De-energisation",1443575.7799999998,"ED_FEE431_00002",37743]
[null,null,"Re-energisation",1401458.1099999999,"ED_FEE431_00003",22966]
[null,"Miscellaneous Fee-Based Services","SUBDIVISION FEES",0,"ED_FEE431_00004",0]
[null,null,"PROJECT FEES",0,"ED_FEE431_00005",0]
[null,null,"RE-TEST AT CUSTOMER'S INSTALLATION DURING BUSINESS HOURS",0,"ED_FEE431_00006",0]
[null,null,"SUPPLY ABOLISHMENT DURING BUSINESS HOURS",405977.77,"ED_FEE431_00007",2056]
[null,null,"TEMPORARY BUILDERS SUPPLY, NOT IN PERMANENT POSITION - SINGLE PHASE METERED - BUSINESS HOURS",90228.53,"ED_FEE431_00008",279]
[null,null,"TEMPORARY BUILDERS SUPPLY, NOT IN PERMANENT POSITION - MULTI PHASE METERED - BUSINESS HOURS",20671.739999999998,"ED_FEE431_00009",45]
[null,null,"RESTORATION OF SUPPLY REQUIRED DUE TO CUSTOMER ACTION, DURING BUSINESS HOURS",0,"ED_FEE431_00010",0]
[null,null,"WASTED TRUCK VISIT - ONE PERSON CREW",0,"ED_FEE431_00011",0]
[null,null,"WASTED TRUCK VISIT - TWO PERSON CREW",0,"ED_FEE431_00012",0]
[null,null,"Application fee - Basic or standard connection",0,"ED_FEE431_00013",0]
[null,null,"Call out fee for supply abolishment during business",0,"ED_FEE431_00014",0]
[null,null,"Call out fee for temporary connection, not in permanent position",0,"ED_FEE431_00015",0]
[null,null,"Prevented access - one person crew",0,"ED_FEE431_00016",0]
[null,null,"Prevented access - two person crew",0,"ED_FEE431_00017",0]
[null,null,"Supply abolishment during business",0,"ED_FEE431_00018",0]
[null,null,"Temporary connection, not in permanent position",0,"ED_FEE431_00019",0]
[null,null,"Large Cust Connection - Fee for Service",0,"ED_FEE431_00020",0]
[null,null,"Accredit alter.serv providers - Real Est",0,"ED_FEE431_00021",0]
[null,null,"No Charge Product Code",0,"ED_FEE431_00022",0]
[null,null,null,"","ED_FEE431_00023",""]
[null,null,null,"","ED_FEE431_00024",""]
[null,null,null,"","ED_FEE431_00025",""]
[null,null,null,"","ED_FEE431_00026",""]
[null,null,null,"","ED_FEE431_00027",""]
[null,null,null,"","ED_FEE431_00028",""]
[null,null,null,"","ED_FEE431_00029",""]
[null,null,null,"","ED_FEE431_00030",""]
[null,null,null,"","ED_FEE431_00031",""]
[null,null,null,"","ED_FEE431_00032",""]
[null,null,null,"","ED_FEE431_00033",""]
[null,null,null,"","ED_FEE431_00034",""]
[null,null,null,"","ED_FEE431_00035",""]
[null,null,null,"","ED_FEE431_00036",""]
[null,null,null,"","ED_FEE431_00037",""]
[null,null,null,"","ED_FEE431_00038",""]
[null,null,null,"","ED_FEE431_00039",""]
[null,null,null,"","ED_FEE431_00040",""]
[null,null,null,"","ED_FEE431_00041",""]
[null,null,null,"","ED_FEE431_00042",""]
[null,null,null,"","ED_FEE431_00043",""]
[null,null,null,"","ED_FEE431_00044",""]
[null,null,null,"","ED_FEE431_00045",""]
[null,null,null,"","ED_FEE431_00046",""]
[null,null,null,"","ED_FEE431_00047",""]
[null,null,null,"","ED_FEE431_00048",""]
[null,null,null,"","ED_FEE431_00049",""]
[null,null,null,"","ED_FEE431_00050",""]
[null,null,null,"","ED_FEE431_00051",""]
[null,null,null,"","ED_FEE431_00052",""]
[null,null,null,"","ED_FEE431_00053",""]
[null,null,null,"","ED_FEE431_00054",""]
[null,null,null,"","ED_FEE431_00055",""]
[null,null,null,"","ED_FEE431_00056",""]
[null,null,null,"","ED_FEE431_00057",""]
[null,null,null,"","ED_FEE431_00058",""]
[null,null,null,"","ED_FEE431_00059",""]
[null,null,null,"","ED_FEE431_00060",""]
[null,null,null,"","ED_FEE431_00061",""]
[null,null,null,"","ED_FEE431_00062",""]
[null,null,null,"","ED_FEE431_00063",""]
[null,null,null,"","ED_FEE431_00064",""]
[null,null,null,"","ED_FEE431_00065",""]
[null,null,null,"","ED_FEE431_00066",""]
[null,null,null,"","ED_FEE431_00067",""]
[null,null,null,"","ED_FEE431_00068",""]
[null,null,null,"","ED_FEE431_00069",""]
[null,null,null,"","ED_FEE431_00070",""]
[null,null,null,"","ED_FEE431_00071",""]
[null,null,null,"","ED_FEE431_00072",""]
[null,null,null,"","ED_FEE431_00073",""]
[null,null,null,"","ED_FEE431_00074",""]
[null,null,null,"","ED_FEE431_00075",""]
[null,null,null,"","ED_FEE431_00076",""]
[null,null,null,"","ED_FEE431_00077",""]
[null,null,null,"","ED_FEE431_00078",""]
[null,null,null,"","ED_FEE431_00079",""]
[null,null,null,"","ED_FEE431_00080",""]
[null,null,null,"","ED_FEE431_00081",""]
[null,null,null,"","ED_FEE431_00082",""]
[null,null,null,"","ED_FEE431_00083",""]
[null,null,null,"","ED_FEE431_00084",""]
[null,null,null,"","ED_FEE431_00085",""]
[null,null,null,"","ED_FEE431_00086",""]
[null,null,null,"","ED_FEE431_00087",""]
[null,null,null,"","ED_FEE431_00088",""]
[null,null,null,"","ED_FEE431_00089",""]
[null,null,null,"","ED_FEE431_00090",""]
[null,null,null,"","ED_FEE431_00091",""]
[null,null,null,"","ED_FEE431_00092",""]
[null,null,null,"","ED_FEE431_00093",""]
[null,null,null,"","ED_FEE431_00094",""]
[null,null,null,"","ED_FEE431_00095",""]
[null,null,null,"","ED_FEE431_00096",""]
[null,null,null,"","ED_FEE431_00097",""]
[null,null,null,"","ED_FEE431_00098",""]
[null,null,null,"","ED_FEE431_00099",""]
[null,null,null,"","ED_FEE431_00100",""]
[null,null,null,"","ED_FEE431_00101",""]
[null,null,null,"","ED_FEE431_00102",""]
[null,null,null,"","ED_FEE431_00103",""]
[null,null,null,"","ED_FEE431_00104",""]
[null,null,null,"","ED_FEE431_00105",""]
[null,null,null,"","ED_FEE431_00106",""]
[null,null,null,"","ED_FEE431_00107",""]
[null,null,null,"","ED_FEE431_00108",""]
[null,null,null,"","ED_FEE431_00109",""]
[null,null,null,"","ED_FEE431_00110",""]
[null,null,null,"","ED_FEE431_00111",""]
[null,null,null,"","ED_FEE431_00112",""]
[null,null,null,"","ED_FEE431_00113",""]
[null,null,null,"","ED_FEE431_00114",""]
[null,null,null,"","ED_FEE431_00115",""]
[null,null,null,"","ED_FEE431_00116",""]
[null,null,null,"","ED_FEE431_00117",""]
[null,null,null,"","ED_FEE431_00118",""]
[null,null,null,"","ED_FEE431_00119",""]
[null,null,null,"","ED_FEE431_00120",""]
[null,null,null,"","ED_FEE431_00121",""]
[null,null,null,"","ED_FEE431_00122",""]
[null,null,null,"","ED_FEE431_00123",""]
[null,null,null,"","ED_FEE431_00124",""]
[null,null,null,"","ED_FEE431_00125",""]
[null,null,null,"","ED_FEE431_00126",""]
[null,null,null,"","ED_FEE431_00127",""]
[null,null,null,"","ED_FEE431_00128",""]
[null,null,null,"","ED_FEE431_00129",""]
[null,null,null,"","ED_FEE431_00130",""]
[null,null,null,"","ED_FEE431_00131",""]
[null,null,null,"","ED_FEE431_00132",""]
[null,null,null,"","ED_FEE431_00133",""]
[null,null,null,"","ED_FEE431_00134",""]
[null,null,null,"","ED_FEE431_00135",""]
[null,null,null,"","ED_FEE431_00136",""]
[null,null,null,"","ED_FEE431_00137",""]
[null,null,null,"","ED_FEE431_00138",""]
[null,null,null,"","ED_FEE431_00139",""]
[null,null,null,"","ED_FEE431_00140",""]
[null,null,null,"","ED_FEE431_00141",""]
[null,null,null,"","ED_FEE431_00142",""]
[null,null,null,"","ED_FEE431_00143",""]
[null,null,null,"","ED_FEE431_00144",""]
[null,null,null,"","ED_FEE431_00145",""]
[null,null,null,"","ED_FEE431_00146",""]
[null,null,null,"","ED_FEE431_00147",""]
[null,null,null,"","ED_FEE431_00148",""]
[null,null,null,"","ED_FEE431_00149",""]
[null,null,null,"","ED_FEE431_00150",""]
[null,null,null,"","ED_FEE431_00151",""]
[null,null,null,"","ED_FEE431_00152",""]
[null,null,null,"","ED_FEE431_00153",""]
[null,null,null,"","ED_FEE431_00154",""]
[null,null,null,"","ED_FEE431_00155",""]
[null,null,null,"","ED_FEE431_00156",""]
[null,null,null,"","ED_FEE431_00157",""]
[null,null,null,"","ED_FEE431_00158",""]
[null,null,null,"","ED_FEE431_00159",""]
[null,null,null,"","ED_FEE431_00160",""]
[null,null,null,"","ED_FEE431_00161",""]
[null,null,null,"","ED_FEE431_00162",""]
[null,null,null,"","ED_FEE431_00163",""]
[null,null,null,"","ED_FEE431_00164",""]
[null,null,null,"","ED_FEE431_00165",""]
[null,null,null,"","ED_FEE431_00166",""]
[null,null,null,"","ED_FEE431_00167",""]
[null,null,null,"","ED_FEE431_00168",""]
[null,null,null,"","ED_FEE431_00169",""]
[null,null,null,"","ED_FEE431_00170",""]
[null,null,null,"","ED_FEE431_00171",""]
[null,null,null,"","ED_FEE431_00172",""]
[null,null,null,"","ED_FEE431_00173",""]
[null,null,null,"","ED_FEE431_00174",""]
[null,null,null,"","ED_FEE431_00175",""]
[null,null,null,"","ED_FEE431_00176",""]
[null,null,null,"","ED_FEE431_00177",""]
[null,null,null,"","ED_FEE431_00178",""]
[null,null,null,"","ED_FEE431_00179",""]
[null,null,null,"","ED_FEE431_00180",""]
[null,null,null,"","ED_FEE431_00181",""]
[null,null,null,"","ED_FEE431_00182",""]
[null,null,null,"","ED_FEE431_00183",""]
[null,null,null,"","ED_FEE431_00184",""]
[null,null,null,"","ED_FEE431_00185",""]
[null,null,null,"","ED_FEE431_00186",""]
[null,null,null,"","ED_FEE431_00187",""]
[null,null,null,"","ED_FEE431_00188",""]
[null,null,null,"","ED_FEE431_00189",""]
[null,null,null,"","ED_FEE431_00190",""]
[null,null,null,"","ED_FEE431_00191",""]
[null,null,null,"","ED_FEE431_00192",""]
[null,null,null,"","ED_FEE431_00193",""]
[null,null,null,"","ED_FEE431_00194",""]
[null,null,null,"","ED_FEE431_00195",""]
[null,null,null,"","ED_FEE431_00196",""]
[null,null,null,"","ED_FEE431_00197",""]
[null,null,null,"","ED_FEE431_00198",""]
[null,null,null,"","ED_FEE431_00199",""]
[null,null,null,"","ED_FEE431_00200",""]
[null,null,null,"","ED_FEE431_00201",""]
[null,null,null,"","ED_FEE431_00202",""]
[null,null,null,"","ED_FEE431_00203",""]
[null,null,null,"","ED_FEE431_00204",""]
[null,null,null,"","ED_FEE431_00205",""]
[null,null,null,"","ED_FEE431_00206",""]
[null,null,null,"","ED_FEE431_00207",""]
[null,null,null,"","ED_FEE431_00208",""]
[null,null,null,"","ED_FEE431_00209",""]
[null,null,null,"","ED_FEE431_00210",""]
[null,null,null,"","ED_FEE431_00211",""]
[null,null,null,"","ED_FEE431_00212",""]
[null,null,null,"","ED_FEE431_00213",""]
[null,null,null,"","ED_FEE431_00214",""]
[null,null,null,"","ED_FEE431_00215",""]
[null,null,null,"","ED_FEE431_00216",""]
[null,null,null,"","ED_FEE431_00217",""]
[null,null,null,"","ED_FEE431_00218",""]
[null,null,null,"","ED_FEE431_00219",""]
[null,null,null,"","ED_FEE431_00220",""]
[null,null,null,"","ED_FEE431_00221",""]
[null,null,null,"","ED_FEE431_00222",""]
[null,null,null,"","ED_FEE431_00223",""]
[null,null,null,"","ED_FEE431_00224",""]
[null,null,null,"","ED_FEE431_00225",""]
[null,null,null,"","ED_FEE431_00226",""]
[null,null,null,"","ED_FEE431_00227",""]
[null,null,null,"","ED_FEE431_00228",""]
[null,null,null,"","ED_FEE431_00229",""]
[null,null,null,"","ED_FEE431_00230",""]
[null,null,null,"","ED_FEE431_00231",""]
[null,null,null,"","ED_FEE431_00232",""]
[null,null,null,null,"ED_FEE431_00233"]
[null,null,null,"","ED_FEE431_00234",""]
[null,null,null,"","ED_FEE431_00235",""]
[null,null,null,"","ED_FEE431_00236",""]
[null,null,null,"","ED_FEE431_00237",""]
[null,null,null,"","ED_FEE431_00238",""]
[null,null,null,"","ED_FEE431_00239",""]
[null,null,null,"","ED_FEE431_00240",""]
[null,null,null,"","ED_FEE431_00241",""]
[null,null,null,"","ED_FEE431_00242",""]
[null,null,null,"","ED_FEE431_00243",""]
[null,null,null,"","ED_FEE431_00244",""]
[null,null,null,"","ED_FEE431_00245",""]
[null,null,null,"","ED_FEE431_00246",""]
[null,null,null,"","ED_FEE431_00247",""]
[null,null,null,"","ED_FEE431_00248",""]
[null,null,null,"","ED_FEE431_00249",""]
[null,null,null,"","ED_FEE431_00250",""]
[null,null,null,"","ED_FEE431_00251",""]
[null,null,null,"","ED_FEE431_00252",""]
[null,null,null,"","ED_FEE431_00253",""]
[null,null,null,"","ED_FEE431_00254",""]
[null,null,null,"","ED_FEE431_00255",""]
[null,null,null,"","ED_FEE431_00256",""]
[null,null,null,"","ED_FEE431_00257",""]
[null,null,null,"","ED_FEE431_00258",""]
[null,null,null,"","ED_FEE431_00259",""]
[null,null,null,"","ED_FEE431_00260",""]
[null,null,null,"","ED_FEE431_00261",""]
[null,null,null,"","ED_FEE431_00262",""]
[null,null,null,"","ED_FEE431_00263",""]
[null,null,null,"","ED_FEE431_00264",""]
[null,null,null,"","ED_FEE431_00265",""]
[null,null,null,"","ED_FEE431_00266",""]
[null,null,null,"","ED_FEE431_00267",""]
[null,null,null,"","ED_FEE431_00268",""]
[null,null,null,"","ED_FEE431_00269",""]
[null,null,null,"","ED_FEE431_00270",""]
[null,null,null,"","ED_FEE431_00271",""]
[null,null,null,"","ED_FEE431_00272",""]
[null,null,null,"","ED_FEE431_00273",""]
[null,null,null,"","ED_FEE431_00274",""]
[null,null,null,"","ED_FEE431_00275",""]
[null,null,null,"","ED_FEE431_00276",""]
[null,null,null,"","ED_FEE431_00277",""]
[null,null,null,"","ED_FEE431_00278",""]
[null,null,null,"","ED_FEE431_00279",""]
[null,null,null,"","ED_FEE431_00280",""]
[null,null,null,"","ED_FEE431_00281",""]
[null,null,null,"","ED_FEE431_00282",""]
[null,null,null,"","ED_FEE431_00283",""]
[null,null,null,"","ED_FEE431_00284",""]
[null,null,null,"","ED_FEE431_00285",""]
[null,null,null,"","ED_FEE431_00286",""]
[null,null,null,"","ED_FEE431_00287",""]
[null,null,null,"","ED_FEE431_00288",""]
[null,null,null,"","ED_FEE431_00289",""]
[null,null,null,"","ED_FEE431_00290",""]
[null,null,null,"","ED_FEE431_00291",""]
[null,null,null,"","ED_FEE431_00292",""]
[null,null,null,"","ED_FEE431_00293",""]
[null,null,null,"","ED_FEE431_00294",""]
[null,null,null,"","ED_FEE431_00295",""]
[null,null,null,"","ED_FEE431_00296",""]
[null,null,null,"","ED_FEE431_00297",""]
[null,null,null,"","ED_FEE431_00298",""]
[null,null,null,"","ED_FEE431_00299",""]
[null,null,null,"","ED_FEE431_00300",""]
[null,null,null,"","ED_FEE431_00301",""]
[null,null,null,"","ED_FEE431_00302",""]
[null,null,null,"","ED_FEE431_00303",""]
[null,null,null,"","ED_FEE431_00304",""]
[null,null,null,"","ED_FEE431_00305",""]
[null,null,null,"","ED_FEE431_00306",""]
[null,null,null,"","ED_FEE431_00307",""]
[null,null,null,"","ED_FEE431_00308",""]
[null,null,null,"","ED_FEE431_00309",""]
[null,null,null,"","ED_FEE431_00310",""]
[null,null,null,"","ED_FEE431_00311",""]
[null,null,null,"","ED_FEE431_00312",""]
[null,null,null,"","ED_FEE431_00313",""]
[null,null,null,"","ED_FEE431_00314",""]
[null,null,null,"","ED_FEE431_00315",""]
[null,null,null,"","ED_FEE431_00316",""]
[null,null,null,"","ED_FEE431_00317",""]
[null,null,null,"","ED_FEE431_00318",""]
[null,null,null,"","ED_FEE431_00319",""]
[null,null,null,"","ED_FEE431_00320",""]
[null,null,null,"","ED_FEE431_00321",""]
[null,null,null,"","ED_FEE431_00322",""]
[null,null,null,"","ED_FEE431_00323",""]
[null,null,null,"","ED_FEE431_00324",""]
[null,null,null,"","ED_FEE431_00325",""]
[null,null,null,"","ED_FEE431_00326",""]
[null,null,null,"","ED_FEE431_00327",""]
[null,null,null,"","ED_FEE431_00328",""]
[null,null,null,"","ED_FEE431_00329",""]
[null,null,null,"","ED_FEE431_00330",""]
[null,null,null,"","ED_FEE431_00331",""]
[null,null,null,"","ED_FEE431_00332",""]
[null,null,null,"","ED_FEE431_00333",""]
[null,null,null,"","ED_FEE431_00334",""]
[null,null,null,"","ED_FEE431_00335",""]
[null,null,null,"","ED_FEE431_00336",""]
[null,null,null,"","ED_FEE431_00337",""]
[null,null,null,"","ED_FEE431_00338",""]
[null,null,null,"","ED_FEE431_00339",""]
[null,null,null,"","ED_FEE431_00340",""]
[null,null,null,"","ED_FEE431_00341",""]
[null,null,null,"","ED_FEE431_00342",""]
[null,null,null,"","ED_FEE431_00343",""]
[null,null,null,"","ED_FEE431_00344",""]
[null,null,null,"","ED_FEE431_00345",""]
[null,null,null,"","ED_FEE431_00346",""]
[null,null,null,"","ED_FEE431_00347",""]
[null,null,null,"","ED_FEE431_00348",""]
[null,null,null,"","ED_FEE431_00349",""]
[null,null,null,"","ED_FEE431_00350",""]
[null,null,null,"","ED_FEE431_00351",""]
[null,null,null,"","ED_FEE431_00352",""]
[null,null,null,"","ED_FEE431_00353",""]
[null,null,null,"","ED_FEE431_00354",""]
[null,null,null,"","ED_FEE431_00355",""]
[null,null,null,"","ED_FEE431_00356",""]
[null,null,null,"","ED_FEE431_00357",""]
[null,null,null,"","ED_FEE431_00358",""]
[null,null,null,"","ED_FEE431_00359",""]
[null,null,null,"","ED_FEE431_00360",""]
[null,null,null,"","ED_FEE431_00361",""]
[null,null,null,"","ED_FEE431_00362",""]
[null,null,null,"","ED_FEE431_00363",""]
[null,null,null,"","ED_FEE431_00364",""]
[null,null,null,"","ED_FEE431_00365",""]
[null,null,null,"","ED_FEE431_00366",""]
[null,null,null,"","ED_FEE431_00367",""]
[null,null,null,"","ED_FEE431_00368",""]
[null,null,null,"","ED_FEE431_00369",""]
[null,null,null,"","ED_FEE431_00370",""]
[null,null,null,"","ED_FEE431_00371",""]
[null,null,null,"","ED_FEE431_00372",""]
[null,null,null,"","ED_FEE431_00373",""]
[null,null,null,"","ED_FEE431_00374",""]
[null,null,null,"","ED_FEE431_00375",""]
[null,null,null,"","ED_FEE431_00376",""]
[null,null,null,"","ED_FEE431_00377",""]
[null,null,null,"","ED_FEE431_00378",""]
[null,null,null,"","ED_FEE431_00379",""]
[null,null,null,"","ED_FEE431_00380",""]
[null,null,null,"","ED_FEE431_00381",""]
[null,null,null,"","ED_FEE431_00382",""]
[null,null,null,"","ED_FEE431_00383",""]
[null,null,null,"","ED_FEE431_00384",""]
[null,null,null,"","ED_FEE431_00385",""]
[null,null,null,"","ED_FEE431_00386",""]
[null,null,null,"","ED_FEE431_00387",""]
[null,null,null,"","ED_FEE431_00388",""]
[null,null,null,"","ED_FEE431_00389",""]
[null,null,null,"","ED_FEE431_00390",""]
[null,null,null,"","ED_FEE431_00391",""]
[null,null,null,"","ED_FEE431_00392",""]
[null,null,null,"","ED_FEE431_00393",""]
[null,null,null,"","ED_FEE431_00394",""]
[null,null,null,"","ED_FEE431_00395",""]
[null,null,null,"","ED_FEE431_00396",""]
[null,null,null,"","ED_FEE431_00397",""]
[null,null,null,"","ED_FEE431_00398",""]
[null,null,null,"","ED_FEE431_00399",""]
[null,null,null,"","ED_FEE431_00400",""]
[null,null,null,"","ED_FEE431_00401",""]
[null,null,null,"","ED_FEE431_00402",""]
[null,null,null,"","ED_FEE431_00403",""]
[null,null,null,"","ED_FEE431_00404",""]
[null,null,null,"","ED_FEE431_00405",""]
[null,null,null,"","ED_FEE431_00406",""]
[null,null,null,"","ED_FEE431_00407",""]
[null,null,null,"","ED_FEE431_00408",""]
[null,null,null,"","ED_FEE431_00409",""]
[null,null,null,"","ED_FEE431_00410",""]
[null,null,null,"","ED_FEE431_00411",""]
[null,null,null,"","ED_FEE431_00412",""]
[null,null,null,"","ED_FEE431_00413",""]
[null,null,null,"","ED_FEE431_00414",""]
[null,null,null,"","ED_FEE431_00415",""]
[null,null,null,"","ED_FEE431_00416",""]
[null,null,null,"","ED_FEE431_00417",""]
[null,null,null,"","ED_FEE431_00418",""]
[null,null,null,"","ED_FEE431_00419",""]
[null,null,null,"","ED_FEE431_00420",""]
[null,null,null,"","ED_FEE431_00421",""]
[null,null,null,"","ED_FEE431_00422",""]
[null,null,null,"","ED_FEE431_00423",""]
[null,null,null,"","ED_FEE431_00424",""]
[null,null,null,"","ED_FEE431_00425",""]
[null,null,null,"","ED_FEE431_00426",""]
[null,null,null,"","ED_FEE431_00427",""]
[null,null,null,"","ED_FEE431_00428",""]
[null,null,null,"","ED_FEE431_00429",""]
[null,null,null,"","ED_FEE431_00430",""]
[null,null,null,"","ED_FEE431_00431",""]
[null,null,null,"","ED_FEE431_00432",""]
[null,null,null,"","ED_FEE431_00433",""]
[null,null,null,"","ED_FEE431_00434",""]
[null,null,null,"","ED_FEE431_00435",""]
[null,null,null,"","ED_FEE431_00436",""]
[null,null,null,"","ED_FEE431_00437",""]
[null,null,null,"","ED_FEE431_00438",""]
[null,null,null,"","ED_FEE431_00439",""]
[null,null,null,"","ED_FEE431_00440",""]
[null,null,null,"","ED_FEE431_00441",""]
[null,null,null,"","ED_FEE431_00442",""]
[null,null,null,"","ED_FEE431_00443",""]
[null,null,null,"","ED_FEE431_00444",""]
[null,null,null,"","ED_FEE431_00445",""]
[null,null,null,"","ED_FEE431_00446",""]
[null,null,null,"","ED_FEE431_00447",""]
[null,null,null,"","ED_FEE431_00448",""]
[null,null,null,"","ED_FEE431_00449",""]
[null,null,null,"","ED_FEE431_00450",""]
[null,null,null,"","ED_FEE431_00451",""]
[null,null,null,"","ED_FEE431_00452",""]
[null,null,null,"","ED_FEE431_00453",""]
[null,null,null,"","ED_FEE431_00454",""]
[null,null,null,"","ED_FEE431_00455",""]
[null,null,null,"","ED_FEE431_00456",""]
[null,null,null,"","ED_FEE431_00457",""]
[null,null,null,"","ED_FEE431_00458",""]
[null,null,null,"","ED_FEE431_00459",""]
[null,null,null,"","ED_FEE431_00460",""]
[null,null,null,"","ED_FEE431_00461",""]
[null,null,null,"","ED_FEE431_00462",""]
[null,null,null,"","ED_FEE431_00463",""]
[null,null,null,"","ED_FEE431_00464",""]
[null,null,null,"","ED_FEE431_00465",""]
[null,null,null,"","ED_FEE431_00466",""]
[null,null,null,"","ED_FEE431_00467",""]
[null,null,null,"","ED_FEE431_00468",""]
[null,null,null,"","ED_FEE431_00469",""]
[null,null,null,"","ED_FEE431_00470",""]
[null,null,null,"","ED_FEE431_00471",""]

{"sheet":"4.4 Quoted services","index":20,"n_rows":481,"n_cols":6,"rows_kept":481,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"4.4 ANCILLARY SERVICES - QUOTED SERVICES"]
[]
[null,"4.4.1 - COST METRICS FOR QUOTED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY",{"$f":"CRY","v":"2017-18"},null,{"$f":"CRY","v":"2017-18"}]
[null,"Quoted Services ","application fee - negotiated - major customer connection",2440943.5299999993,"ED_QUO441_00001",87]
[null,null,"application fee - negotiated connection",0,"ED_QUO441_00002",0]
[null,null,"assessment of parallel generator applications",84992.5,"ED_QUO441_00003",107]
[null,null,"carrying out planning studies and analysis relating to connection applications",0,"ED_QUO441_00004",0]
[null,null,"change load control relay channel",15819.72,"ED_QUO441_00005",168]
[null,null,"change tariff",18941.699999999997,"ED_QUO441_00006",127]
[null,null,"change time switch",64.31,"ED_QUO441_00007",2]
[null,null,"Construction audit - Maj Cust Connect",46176.969999999994,"ED_QUO441_00008",2]
[null,null,"commissioning and energisation of major customer connections",0,"ED_QUO441_00009",0]
[null,null,"conversion of aerial bundled cables",0,"ED_QUO441_00010",0]
[null,null,"customer build, own and operate consultation services",8331.2900000000009,"ED_QUO441_00011",1]
[null,null,"customer requested appointments",59613.11,"ED_QUO441_00012",30]
[null,null,"de-energisation",0,"ED_QUO441_00013",0]
[null,null,"de-energisation after hours",8728.77,"ED_QUO441_00014",123]
[null,null,"design and construction of connection assets for major customers",0,"ED_QUO441_00015",0]
[null,null,"detailed enquiry response fee - egs 5mw & above",481009.06999999995,"ED_QUO441_00016",34]
[null,null,"emergencey recoverable works",0,"ED_QUO441_00017",0]
[null,null,"erection of extra poles (only on a customers installation",0,"ED_QUO441_00018",0]
[null,null,"exchange meter",2013.7199999999998,"ED_QUO441_00019",12]
[null,null,"exchange meter (type 5-7)",0,"ED_QUO441_00020",0]
[null,null,"feasibility and concept scoping, inc planning and design, for major customer connections",151796.37,"ED_QUO441_00021",91]
[null,null,"generic call out fee",0,"ED_QUO441_00022",0]
[null,null,"high load escorts",0,"ED_QUO441_00023",0]
[null,null,"install additional metering",2265093.5300000003,"ED_QUO441_00024",12053]
[null,null,"install metering related load control",204989.99000000002,"ED_QUO441_00025",1245]
[null,null,"large customer conections",10867192.811922574,"ED_QUO441_00026",139]
[null,null,"Meter Co-Ord Requested Appointments",3126.52,"ED_QUO441_00027",19]
[null,null,"meter inspection and investigation on request",32280.629999999997,"ED_QUO441_00028",289]
[null,null,"Meter Query",1214676.6699999997,"ED_QUO441_00029",12982]
[null,null,"meter re-seal",680149.72000000009,"ED_QUO441_00030",9678]
[null,null,"meter test",67126.34,"ED_QUO441_00031",192]
[null,null,"metering alteration",458748.93,"ED_QUO441_00032",1642]
[null,null,"move point of attachement during business hours - single / multi pase",0,"ED_QUO441_00033",0]
[null,null,"move point of attachment",723587.45999999985,"ED_QUO441_00034",1723]
[null,null,"move the meter (type 5-7)",0,"ED_QUO441_00035",0]
[null,null,"non-standard network data requests",29326.510000000002,"ED_QUO441_00036",234]
[null,null,"other recoverable works",0,"ED_QUO441_00037",0]
[null,null,"overhead service upgrade - no change to load",0,"ED_QUO441_00038",0]
[null,null,"Planning Study & Analy - Connect Applic",7286.57,"ED_QUO441_00039",1]
[null,null,"Power Quality Protct Assets after Connec",2746,"ED_QUO441_00040",1]
[null,null,"prep of preliminary designs & planning reports for major customer connections, inc project scopes and estimates",151046.60999999999,"ED_QUO441_00041",20]
[null,null,"prepayment meters at customer request",0,"ED_QUO441_00042",0]
[null,null,"project fees",0,"ED_QUO441_00043",0]
[null,null,"protection and power quality assessment after connection",0,"ED_QUO441_00044",0]
[null,null,"provision of connection services above minimum requirements",0,"ED_QUO441_00045",0]
[null,null,"provision of historical metering data",0,"ED_QUO441_00046",0]
[null,null,"provision of metering data above minimum requirements",0,"ED_QUO441_00047",0]
[null,null,"provision of service during business / after hours requiring one / two person crew",0,"ED_QUO441_00048",0]
[null,null,"provision of services for approved unmetered supplies",6072.72,"ED_QUO441_00049",15]
[null,null,"provision of site-specific connection information and advice for small or major customer connections",253658.38999999998,"ED_QUO441_00050",204]
[null,null,"provision, installation and maintenance of meters above minimum requirements",0,"ED_QUO441_00051",0]
[null,null,"re-arrange connection assets at customer's request",66799.700000000012,"ED_QUO441_00052",11]
[null,null,"rectification of illegal connections",264.95,"ED_QUO441_00053",1]
[null,null,"re-energisation",0,"ED_QUO441_00054",0]
[null,null,"re-energisation after hours",248925.94999999995,"ED_QUO441_00055",1318]
[null,null,"removal / relocation of ergon energy assets at customer request",0,"ED_QUO441_00056",0]
[null,null,"removal of a meter",0,"ED_QUO441_00057",0]
[null,null,"removal of a meter (type 5 & 6)",39917.360000000001,"ED_QUO441_00058",193]
[null,null,"removal of load control device",2431.23,"ED_QUO441_00059",44]
[null,null,"removal/rearrangement of network assets",10195635.020000005,"ED_QUO441_00060",390]
[null,null,"removal/rearrangement of public lighting assets",1803949.51,"ED_QUO441_00061",122]
[null,null,"Repairs to System Assets",0,"ED_QUO441_00062",0]
[null,null,"reprogram card meters",0,"ED_QUO441_00063",0]
[null,null,"restoration of supply required due to customer action - after hours",0,"ED_QUO441_00064",0]
[null,null,"service line drop and replace",167324.12000000002,"ED_QUO441_00065",454]
[null,null,"special meter read",2461774.35,"ED_QUO441_00066",96502]
[null,null,"subdivision fees",0,"ED_QUO441_00067",0]
[null,null,"supply enhancement",277280.44999999995,"ED_QUO441_00068",639]
[null,null,"temporary de-energisation - no dismantling",101837.40000000001,"ED_QUO441_00069",333]
[null,null,"temporary de-energisation single visit during business hours - no dismantling",0,"ED_QUO441_00070",0]
[null,null,"tiger tails",103275.84000000001,"ED_QUO441_00071",265]
[null,null,"type 5 to 7 non-standard metering services",0,"ED_QUO441_00072",0]
[null,null,"underground service upgrade",0,"ED_QUO441_00073",0]
[null,null,"upgrade from overhead to underground service",0,"ED_QUO441_00074",0]
[null,null,"witness testing",0,"ED_QUO441_00075",0]
[null,null,"aerial markers",2452.17,"ED_QUO441_00076",7]
[null,null,"Design and construction of connection assets Real Estate developments",18795177.489999998,"ED_QUO441_00077",287]
[null,null,"upgrade from overhead to underground service",0,"ED_QUO441_00078",0]
[null,null,null,"","ED_QUO441_00079",""]
[null,null,null,"","ED_QUO441_00080",""]
[null,null,null,"","ED_QUO441_00081",""]
[null,null,null,"","ED_QUO441_00082",""]
[null,null,null,"","ED_QUO441_00083",""]
[null,null,null,"","ED_QUO441_00084",""]
[null,null,null,"","ED_QUO441_00085",""]
[null,null,null,"","ED_QUO441_00086",""]
[null,null,null,"","ED_QUO441_00087",""]
[null,null,null,"","ED_QUO441_00088",""]
[null,null,null,"","ED_QUO441_00089",""]
[null,null,null,"","ED_QUO441_00090",""]
[null,null,null,"","ED_QUO441_00091",""]
[null,null,null,"","ED_QUO441_00092",""]
[null,null,null,"","ED_QUO441_00093",""]
[null,null,null,"","ED_QUO441_00094",""]
[null,null,null,"","ED_QUO441_00095",""]
[null,null,null,"","ED_QUO441_00096",""]
[null,null,null,"","ED_QUO441_00097",""]
[null,null,null,"","ED_QUO441_00098",""]
[null,null,null,"","ED_QUO441_00099",""]
[null,null,null,"","ED_QUO441_00100",""]
[null,null,null,"","ED_QUO441_00101",""]
[null,null,null,"","ED_QUO441_00102",""]
[null,null,null,"","ED_QUO441_00103",""]
[null,null,null,"","ED_QUO441_00104",""]
[null,null,null,"","ED_QUO441_00105",""]
[null,null,null,"","ED_QUO441_00106",""]
[null,null,null,"","ED_QUO441_00107",""]
[null,null,null,"","ED_QUO441_00108",""]
[null,null,null,"","ED_QUO441_00109",""]
[null,null,null,"","ED_QUO441_00110",""]
[null,null,null,"","ED_QUO441_00111",""]
[null,null,null,"","ED_QUO441_00112",""]
[null,null,null,"","ED_QUO441_00113",""]
[null,null,null,"","ED_QUO441_00114",""]
[null,null,null,"","ED_QUO441_00115",""]
[null,null,null,"","ED_QUO441_00116",""]
[null,null,null,"","ED_QUO441_00117",""]
[null,null,null,"","ED_QUO441_00118",""]
[null,null,null,"","ED_QUO441_00119",""]
[null,null,null,"","ED_QUO441_00120",""]
[null,null,null,"","ED_QUO441_00121",""]
[null,null,null,"","ED_QUO441_00122",""]
[null,null,null,"","ED_QUO441_00123",""]
[null,null,null,"","ED_QUO441_00124",""]
[null,null,null,"","ED_QUO441_00125",""]
[null,null,null,"","ED_QUO441_00126",""]
[null,null,null,"","ED_QUO441_00127",""]
[null,null,null,"","ED_QUO441_00128",""]
[null,null,null,"","ED_QUO441_00129",""]
[null,null,null,"","ED_QUO441_00130",""]
[null,null,null,"","ED_QUO441_00131",""]
[null,null,null,"","ED_QUO441_00132",""]
[null,null,null,"","ED_QUO441_00133",""]
[null,null,null,"","ED_QUO441_00134",""]
[null,null,null,"","ED_QUO441_00135",""]
[null,null,null,"","ED_QUO441_00136",""]
[null,null,null,"","ED_QUO441_00137",""]
[null,null,null,"","ED_QUO441_00138",""]
[null,null,null,"","ED_QUO441_00139",""]
[null,null,null,"","ED_QUO441_00140",""]
[null,null,null,"","ED_QUO441_00141",""]
[null,null,null,"","ED_QUO441_00142",""]
[null,null,null,"","ED_QUO441_00143",""]
[null,null,null,"","ED_QUO441_00144",""]
[null,null,null,"","ED_QUO441_00145",""]
[null,null,null,"","ED_QUO441_00146",""]
[null,null,null,"","ED_QUO441_00147",""]
[null,null,null,"","ED_QUO441_00148",""]
[null,null,null,"","ED_QUO441_00149",""]
[null,null,null,"","ED_QUO441_00150",""]
[null,null,null,"","ED_QUO441_00151",""]
[null,null,null,"","ED_QUO441_00152",""]
[null,null,null,"","ED_QUO441_00153",""]
[null,null,null,"","ED_QUO441_00154",""]
[null,null,null,"","ED_QUO441_00155",""]
[null,null,null,"","ED_QUO441_00156",""]
[null,null,null,"","ED_QUO441_00157",""]
[null,null,null,"","ED_QUO441_00158",""]
[null,null,null,"","ED_QUO441_00159",""]
[null,null,null,"","ED_QUO441_00160",""]
[null,null,null,"","ED_QUO441_00161",""]
[null,null,null,"","ED_QUO441_00162",""]
[null,null,null,"","ED_QUO441_00163",""]
[null,null,null,"","ED_QUO441_00164",""]
[null,null,null,"","ED_QUO441_00165",""]
[null,null,null,"","ED_QUO441_00166",""]
[null,null,null,"","ED_QUO441_00167",""]
[null,null,null,"","ED_QUO441_00168",""]
[null,null,null,"","ED_QUO441_00169",""]
[null,null,null,"","ED_QUO441_00170",""]
[null,null,null,"","ED_QUO441_00171",""]
[null,null,null,"","ED_QUO441_00172",""]
[null,null,null,"","ED_QUO441_00173",""]
[null,null,null,"","ED_QUO441_00174",""]
[null,null,null,"","ED_QUO441_00175",""]
[null,null,null,"","ED_QUO441_00176",""]
[null,null,null,"","ED_QUO441_00177",""]
[null,null,null,"","ED_QUO441_00178",""]
[null,null,null,"","ED_QUO441_00179",""]
[null,null,null,"","ED_QUO441_00180",""]
[null,null,null,"","ED_QUO441_00181",""]
[null,null,null,"","ED_QUO441_00182",""]
[null,null,null,"","ED_QUO441_00183",""]
[null,null,null,"","ED_QUO441_00184",""]
[null,null,null,"","ED_QUO441_00185",""]
[null,null,null,"","ED_QUO441_00186",""]
[null,null,null,"","ED_QUO441_00187",""]
[null,null,null,"","ED_QUO441_00188",""]
[null,null,null,"","ED_QUO441_00189",""]
[null,null,null,"","ED_QUO441_00190",""]
[null,null,null,"","ED_QUO441_00191",""]
[null,null,null,"","ED_QUO441_00192",""]
[null,null,null,"","ED_QUO441_00193",""]
[null,null,null,"","ED_QUO441_00194",""]
[null,null,null,"","ED_QUO441_00195",""]
[null,null,null,"","ED_QUO441_00196",""]
[null,null,null,"","ED_QUO441_00197",""]
[null,null,null,"","ED_QUO441_00198",""]
[null,null,null,"","ED_QUO441_00199",""]
[null,null,null,"","ED_QUO441_00200",""]
[null,null,null,"","ED_QUO441_00201",""]
[null,null,null,"","ED_QUO441_00202",""]
[null,null,null,"","ED_QUO441_00203",""]
[null,null,null,"","ED_QUO441_00204",""]
[null,null,null,"","ED_QUO441_00205",""]
[null,null,null,"","ED_QUO441_00206",""]
[null,null,null,"","ED_QUO441_00207",""]
[null,null,null,"","ED_QUO441_00208",""]
[null,null,null,"","ED_QUO441_00209",""]
[null,null,null,"","ED_QUO441_00210",""]
[null,null,null,"","ED_QUO441_00211",""]
[null,null,null,"","ED_QUO441_00212",""]
[null,null,null,"","ED_QUO441_00213",""]
[null,null,null,"","ED_QUO441_00214",""]
[null,null,null,"","ED_QUO441_00215",""]
[null,null,null,"","ED_QUO441_00216",""]
[null,null,null,"","ED_QUO441_00217",""]
[null,null,null,"","ED_QUO441_00218",""]
[null,null,null,"","ED_QUO441_00219",""]
[null,null,null,"","ED_QUO441_00220",""]
[null,null,null,"","ED_QUO441_00221",""]
[null,null,null,"","ED_QUO441_00222",""]
[null,null,null,"","ED_QUO441_00223",""]
[null,null,null,"","ED_QUO441_00224",""]
[null,null,null,"","ED_QUO441_00225",""]
[null,null,null,"","ED_QUO441_00226",""]
[null,null,null,"","ED_QUO441_00227",""]
[null,null,null,"","ED_QUO441_00228",""]
[null,null,null,"","ED_QUO441_00229",""]
[null,null,null,"","ED_QUO441_00230",""]
[null,null,null,"","ED_QUO441_00231",""]
[null,null,null,"","ED_QUO441_00232",""]
[null,null,null,"","ED_QUO441_00233",""]
[null,null,null,"","ED_QUO441_00234",""]
[null,null,null,"","ED_QUO441_00235",""]
[null,null,null,"","ED_QUO441_00236",""]
[null,null,null,"","ED_QUO441_00237",""]
[null,null,null,"","ED_QUO441_00238",""]
[null,null,null,"","ED_QUO441_00239",""]
[null,null,null,"","ED_QUO441_00240",""]
[null,null,null,"","ED_QUO441_00241",""]
[null,null,null,"","ED_QUO441_00242",""]
[null,null,null,"","ED_QUO441_00243",""]
[null,null,null,"","ED_QUO441_00244",""]
[null,null,null,"","ED_QUO441_00245",""]
[null,null,null,"","ED_QUO441_00246",""]
[null,null,null,"","ED_QUO441_00247",""]
[null,null,null,"","ED_QUO441_00248",""]
[null,null,null,"","ED_QUO441_00249",""]
[null,null,null,"","ED_QUO441_00250",""]
[null,null,null,"","ED_QUO441_00251",""]
[null,null,null,"","ED_QUO441_00252",""]
[null,null,null,"","ED_QUO441_00253",""]
[null,null,null,"","ED_QUO441_00254",""]
[null,null,null,"","ED_QUO441_00255",""]
[null,null,null,"","ED_QUO441_00256",""]
[null,null,null,"","ED_QUO441_00257",""]
[null,null,null,"","ED_QUO441_00258",""]
[null,null,null,"","ED_QUO441_00259",""]
[null,null,null,"","ED_QUO441_00260",""]
[null,null,null,"","ED_QUO441_00261",""]
[null,null,null,"","ED_QUO441_00262",""]
[null,null,null,"","ED_QUO441_00263",""]
[null,null,null,"","ED_QUO441_00264",""]
[null,null,null,"","ED_QUO441_00265",""]
[null,null,null,"","ED_QUO441_00266",""]
[null,null,null,"","ED_QUO441_00267",""]
[null,null,null,"","ED_QUO441_00268",""]
[null,null,null,"","ED_QUO441_00269",""]
[null,null,null,"","ED_QUO441_00270",""]
[null,null,null,"","ED_QUO441_00271",""]
[null,null,null,"","ED_QUO441_00272",""]
[null,null,null,"","ED_QUO441_00273",""]
[null,null,null,"","ED_QUO441_00274",""]
[null,null,null,"","ED_QUO441_00275",""]
[null,null,null,"","ED_QUO441_00276",""]
[null,null,null,"","ED_QUO441_00277",""]
[null,null,null,"","ED_QUO441_00278",""]
[null,null,null,"","ED_QUO441_00279",""]
[null,null,null,"","ED_QUO441_00280",""]
[null,null,null,"","ED_QUO441_00281",""]
[null,null,null,"","ED_QUO441_00282",""]
[null,null,null,"","ED_QUO441_00283",""]
[null,null,null,"","ED_QUO441_00284",""]
[null,null,null,"","ED_QUO441_00285",""]
[null,null,null,"","ED_QUO441_00286",""]
[null,null,null,"","ED_QUO441_00287",""]
[null,null,null,"","ED_QUO441_00288",""]
[null,null,null,"","ED_QUO441_00289",""]
[null,null,null,"","ED_QUO441_00290",""]
[null,null,null,"","ED_QUO441_00291",""]
[null,null,null,"","ED_QUO441_00292",""]
[null,null,null,"","ED_QUO441_00293",""]
[null,null,null,"","ED_QUO441_00294",""]
[null,null,null,"","ED_QUO441_00295",""]
[null,null,null,"","ED_QUO441_00296",""]
[null,null,null,"","ED_QUO441_00297",""]
[null,null,null,"","ED_QUO441_00298",""]
[null,null,null,"","ED_QUO441_00299",""]
[null,null,null,"","ED_QUO441_00300",""]
[null,null,null,"","ED_QUO441_00301",""]
[null,null,null,"","ED_QUO441_00302",""]
[null,null,null,"","ED_QUO441_00303",""]
[null,null,null,"","ED_QUO441_00304",""]
[null,null,null,"","ED_QUO441_00305",""]
[null,null,null,"","ED_QUO441_00306",""]
[null,null,null,"","ED_QUO441_00307",""]
[null,null,null,"","ED_QUO441_00308",""]
[null,null,null,"","ED_QUO441_00309",""]
[null,null,null,"","ED_QUO441_00310",""]
[null,null,null,"","ED_QUO441_00311",""]
[null,null,null,"","ED_QUO441_00312",""]
[null,null,null,"","ED_QUO441_00313",""]
[null,null,null,"","ED_QUO441_00314",""]
[null,null,null,"","ED_QUO441_00315",""]
[null,null,null,"","ED_QUO441_00316",""]
[null,null,null,"","ED_QUO441_00317",""]
[null,null,null,"","ED_QUO441_00318",""]
[null,null,null,"","ED_QUO441_00319",""]
[null,null,null,"","ED_QUO441_00320",""]
[null,null,null,"","ED_QUO441_00321",""]
[null,null,null,"","ED_QUO441_00322",""]
[null,null,null,"","ED_QUO441_00323",""]
[null,null,null,"","ED_QUO441_00324",""]
[null,null,null,"","ED_QUO441_00325",""]
[null,null,null,"","ED_QUO441_00326",""]
[null,null,null,"","ED_QUO441_00327",""]
[null,null,null,"","ED_QUO441_00328",""]
[null,null,null,"","ED_QUO441_00329",""]
[null,null,null,"","ED_QUO441_00330",""]
[null,null,null,"","ED_QUO441_00331",""]
[null,null,null,"","ED_QUO441_00332",""]
[null,null,null,"","ED_QUO441_00333",""]
[null,null,null,"","ED_QUO441_00334",""]
[null,null,null,"","ED_QUO441_00335",""]
[null,null,null,"","ED_QUO441_00336",""]
[null,null,null,"","ED_QUO441_00337",""]
[null,null,null,"","ED_QUO441_00338",""]
[null,null,null,"","ED_QUO441_00339",""]
[null,null,null,"","ED_QUO441_00340",""]
[null,null,null,"","ED_QUO441_00341",""]
[null,null,null,"","ED_QUO441_00342",""]
[null,null,null,"","ED_QUO441_00343",""]
[null,null,null,"","ED_QUO441_00344",""]
[null,null,null,"","ED_QUO441_00345",""]
[null,null,null,"","ED_QUO441_00346",""]
[null,null,null,"","ED_QUO441_00347",""]
[null,null,null,"","ED_QUO441_00348",""]
[null,null,null,"","ED_QUO441_00349",""]
[null,null,null,"","ED_QUO441_00350",""]
[null,null,null,"","ED_QUO441_00351",""]
[null,null,null,"","ED_QUO441_00352",""]
[null,null,null,"","ED_QUO441_00353",""]
[null,null,null,"","ED_QUO441_00354",""]
[null,null,null,"","ED_QUO441_00355",""]
[null,null,null,"","ED_QUO441_00356",""]
[null,null,null,"","ED_QUO441_00357",""]
[null,null,null,"","ED_QUO441_00358",""]
[null,null,null,"","ED_QUO441_00359",""]
[null,null,null,"","ED_QUO441_00360",""]
[null,null,null,"","ED_QUO441_00361",""]
[null,null,null,"","ED_QUO441_00362",""]
[null,null,null,"","ED_QUO441_00363",""]
[null,null,null,"","ED_QUO441_00364",""]
[null,null,null,"","ED_QUO441_00365",""]
[null,null,null,"","ED_QUO441_00366",""]
[null,null,null,"","ED_QUO441_00367",""]
[null,null,null,"","ED_QUO441_00368",""]
[null,null,null,"","ED_QUO441_00369",""]
[null,null,null,"","ED_QUO441_00370",""]
[null,null,null,"","ED_QUO441_00371",""]
[null,null,null,"","ED_QUO441_00372",""]
[null,null,null,"","ED_QUO441_00373",""]
[null,null,null,"","ED_QUO441_00374",""]
[null,null,null,"","ED_QUO441_00375",""]
[null,null,null,"","ED_QUO441_00376",""]
[null,null,null,"","ED_QUO441_00377",""]
[null,null,null,"","ED_QUO441_00378",""]
[null,null,null,"","ED_QUO441_00379",""]
[null,null,null,"","ED_QUO441_00380",""]
[null,null,null,"","ED_QUO441_00381",""]
[null,null,null,"","ED_QUO441_00382",""]
[null,null,null,"","ED_QUO441_00383",""]
[null,null,null,"","ED_QUO441_00384",""]
[null,null,null,"","ED_QUO441_00385",""]
[null,null,null,"","ED_QUO441_00386",""]
[null,null,null,"","ED_QUO441_00387",""]
[null,null,null,"","ED_QUO441_00388",""]
[null,null,null,"","ED_QUO441_00389",""]
[null,null,null,"","ED_QUO441_00390",""]
[null,null,null,"","ED_QUO441_00391",""]
[null,null,null,"","ED_QUO441_00392",""]
[null,null,null,"","ED_QUO441_00393",""]
[null,null,null,"","ED_QUO441_00394",""]
[null,null,null,"","ED_QUO441_00395",""]
[null,null,null,"","ED_QUO441_00396",""]
[null,null,null,"","ED_QUO441_00397",""]
[null,null,null,"","ED_QUO441_00398",""]
[null,null,null,"","ED_QUO441_00399",""]
[null,null,null,"","ED_QUO441_00400",""]
[null,null,null,"","ED_QUO441_00401",""]
[null,null,null,"","ED_QUO441_00402",""]
[null,null,null,"","ED_QUO441_00403",""]
[null,null,null,"","ED_QUO441_00404",""]
[null,null,null,"","ED_QUO441_00405",""]
[null,null,null,"","ED_QUO441_00406",""]
[null,null,null,"","ED_QUO441_00407",""]
[null,null,null,"","ED_QUO441_00408",""]
[null,null,null,"","ED_QUO441_00409",""]
[null,null,null,"","ED_QUO441_00410",""]
[null,null,null,"","ED_QUO441_00411",""]
[null,null,null,"","ED_QUO441_00412",""]
[null,null,null,"","ED_QUO441_00413",""]
[null,null,null,"","ED_QUO441_00414",""]
[null,null,null,"","ED_QUO441_00415",""]
[null,null,null,"","ED_QUO441_00416",""]
[null,null,null,"","ED_QUO441_00417",""]
[null,null,null,"","ED_QUO441_00418",""]
[null,null,null,"","ED_QUO441_00419",""]
[null,null,null,"","ED_QUO441_00420",""]
[null,null,null,"","ED_QUO441_00421",""]
[null,null,null,"","ED_QUO441_00422",""]
[null,null,null,"","ED_QUO441_00423",""]
[null,null,null,"","ED_QUO441_00424",""]
[null,null,null,"","ED_QUO441_00425",""]
[null,null,null,"","ED_QUO441_00426",""]
[null,null,null,"","ED_QUO441_00427",""]
[null,null,null,"","ED_QUO441_00428",""]
[null,null,null,"","ED_QUO441_00429",""]
[null,null,null,"","ED_QUO441_00430",""]
[null,null,null,"","ED_QUO441_00431",""]
[null,null,null,"","ED_QUO441_00432",""]
[null,null,null,"","ED_QUO441_00433",""]
[null,null,null,"","ED_QUO441_00434",""]
[null,null,null,"","ED_QUO441_00435",""]
[null,null,null,"","ED_QUO441_00436",""]
[null,null,null,"","ED_QUO441_00437",""]
[null,null,null,"","ED_QUO441_00438",""]
[null,null,null,"","ED_QUO441_00439",""]
[null,null,null,"","ED_QUO441_00440",""]
[null,null,null,"","ED_QUO441_00441",""]
[null,null,null,"","ED_QUO441_00442",""]
[null,null,null,"","ED_QUO441_00443",""]
[null,null,null,"","ED_QUO441_00444",""]
[null,null,null,"","ED_QUO441_00445",""]
[null,null,null,"","ED_QUO441_00446",""]
[null,null,null,"","ED_QUO441_00447",""]
[null,null,null,"","ED_QUO441_00448",""]
[null,null,null,"","ED_QUO441_00449",""]
[null,null,null,"","ED_QUO441_00450",""]
[null,null,null,"","ED_QUO441_00451",""]
[null,null,null,"","ED_QUO441_00452",""]
[null,null,null,"","ED_QUO441_00453",""]
[null,null,null,"","ED_QUO441_00454",""]
[null,null,null,"","ED_QUO441_00455",""]
[null,null,null,"","ED_QUO441_00456",""]
[null,null,null,"","ED_QUO441_00457",""]
[null,null,null,"","ED_QUO441_00458",""]
[null,null,null,"","ED_QUO441_00459",""]
[null,null,null,"","ED_QUO441_00460",""]
[null,null,null,"","ED_QUO441_00461",""]
[null,null,null,"","ED_QUO441_00462",""]
[null,null,null,"","ED_QUO441_00463",""]
[null,null,null,"","ED_QUO441_00464",""]
[null,null,null,"","ED_QUO441_00465",""]
[null,null,null,"","ED_QUO441_00466",""]
[null,null,null,"","ED_QUO441_00467",""]
[null,null,null,"","ED_QUO441_00468",""]
[null,null,null,"","ED_QUO441_00469",""]
[null,null,null,"","ED_QUO441_00470",""]
[null,null,null,"","ED_QUO441_00471",""]
[null,null,null,"","ED_QUO441_00472",""]
[null,null,null,"","ED_QUO441_00473",""]

{"sheet":"5.2 Asset Age Profile","index":21,"n_rows":127,"n_cols":114,"rows_kept":127,"cut":false,"hidden":false,"merged":[[8,3,8,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"5.2 ASSET AGE PROFILE"]
[]
[null,"There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.2.1 - ASSET AGE PROFILE"]
[null,null,null,"ECONOMIC LIFE (YEARS)",null,"INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR"]
[null,"ASSET GROUP","ASSET CATEGORY","MEAN ","STANDARD DEVIATION ",{"$f":"CRY","v":"2017-18"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(F10,4)-1)&\"-\"&MID(F10,3,2)),VALUE(LEFT(F10,4)-1))","v":"2016-17"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(G10,4)-1)&\"-\"&MID(G10,3,2)),VALUE(LEFT(G10,4)-1))","v":"2015-16"},"2014-15","2013-14","2012-13","2011-12","2010-11","2009-10","2008-09","2007-08","2006-07","2005-06","2004-05","2003-04","2002-03","2001-02","2000-01","1999-00","1998-99","1997-98","1996-97","1995-96","1994-95","1993-94","1992-93","1991-92","1990-91","1989-90","1988-89","1987-88","1986-87","1985-86",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(AL10,4)-1)&\"-\"&MID(AL10,3,2)),VALUE(LEFT(AL10,4)-1))","v":"1984-85"},"1983-84","1982-83","1981-82","1980-81","1979-80","1978-79","1977-78","1976-77","1975-76","1974-75","1973-74","1972-73","1971-72","1970-71","1969-70","1968-69","1967-68","1966-67","1965-66","1964-65","1963-64","1962-63","1961-62","1960-61","1959-60","1958-59","1957-58","1956-57","1955-56","1954-55","1953-54",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(BR10,4)-1)&\"-\"&MID(BR10,3,2)),VALUE(LEFT(BR10,4)-1))","v":"1952-53"},"1951-52","1950-51","1949-50","1948-49","1947-48","1946-47","1945-46","1944-45","1943-44","1942-43","1941-42","1940-41","1939-40","1938-39","1937-38","1936-37","1935-36","1934-35","1933-34","1932-33","1931-32","1930-31","1929-30","1928-29","1927-28","1926-27","1925-26","1924-25","1923-24","1922-23","1921-22",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(CX10,4)-1)&\"-\"&MID(CX10,3,2)),VALUE(LEFT(CX10,4)-1))","v":"1920-21"},"1919-20","1918-19","1917-18","1916-17","1915-16","1914-15","1913-14","1912-13",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DG10,4)-1)&\"-\"&MID(DG10,3,2)),VALUE(LEFT(DG10,4)-1))","v":"1911-12"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DH10,4)-1)&\"-\"&MID(DH10,3,2)),VALUE(LEFT(DH10,4)-1))","v":"1910-11"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(DI10,4)-1)&\"-\"&MID(DI10,3,2)),VALUE(LEFT(DI10,4)-1))","v":"1909-10"}]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole",15,3.87,1563,1461,1873,1332,2428,4000,2595,2595,2840,2768,2616,2547,4195,2500,2000,1700,1500,1500,1500,1500,800,800,800,800,800,800,400,400,400,200,100,100,100,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 1 kV; Wood",50,7.07,70,1219,1167,1776,2435,2147,2623,1880,2205,2112,2286,4549,4670,5541,5397,4705,4763,4343,4275,3858,4258,4298,4707,5617,5179,5051,5559,5162,5023,4738,3659,3235,4578,5240,4944,4344,5806,4843,4403,3314,4121,4128,4140,3941,4099,3231,3354,3394,3911,3238,2751,2123,2168,2031,1751,2757,1605,1604,1599,1559,1559,1574,1585,1551,1519,1527,1502,1519,1550,1,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Wood",50,7.07,143,1625,1764,3461,4606,4467,4960,3967,3425,3942,5298,7498,6351,5740,5316,4286,4472,4084,4326,3892,4506,4824,5259,6864,5591,5119,5434,5055,4823,4227,3002,3889,4863,5880,5905,4899,7141,5747,5654,3648,4213,4129,3861,3376,3867,2380,3015,3452,4070,3641,3372,2798,2592,3148,3580,3838,2122,2074,2150,2045,2064,2041,2045,2036,2074,2085,2082,2096,2066,1,0,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Wood",50,7.07,74,1784,1720,2504,2907,3278,4384,3587,2566,3658,4086,5282,5165,6250,5651,5246,6193,5920,5840,5882,3761,3154,3360,4004,3889,3903,4114,5323,5901,8026,7022,9959,13104,8547,9219,8673,12888,13917,8443,3880,2615,4644,5018,9601,8690,3409,3787,5249,6874,4798,4490,3647,4022,4200,3416,3178,1389,1218,1020,1025,949,952,922,935,924,927,958,952,950,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Wood",50,7.07,6,213,248,483,686,759,593,640,414,400,421,851,805,770,757,870,954,1111,1334,825,875,678,488,689,878,564,752,882,893,624,632,908,961,929,1527,1094,1588,953,829,610,527,701,1045,913,565,1365,1183,528,1382,1189,1925,2136,580,1823,998,1636,256,501,270,339,788,212,261,423,354,624,353,272,472,45,56,38,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Wood",50,7.07,0,1,1,2,20,1,1,2,33,14,15,22,21,7,5,15,101,36,7,8,3,6,3,4,3,136,9,8,3,2,3,9,2,15,8,4,203,17,4,143,38,280,90,268,78,7,2,250,39,460,632,13,851,142,0,2,3,3,1,0,215,3,1,2,3,3,2,2,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; Wood",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 1 kV; Concrete",70,8.3699999999999992,0,1,2,8,3,49,43,62,77,63,79,52,103,65,51,57,128,87,170,114,89,106,86,184,164,103,186,61,96,196,215,60,66,40,33,29,33,33,27,2,5,4,3,1,3,5,7,15,18,9,5,9,3,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Concrete",70,8.3699999999999992,0,2,1,1,1,4,3,5,8,2,8,51,164,3,1,2,6,2,124,33,244,16,17,15,46,34,80,37,23,28,45,49,103,133,19,14,2,0,5,2,2,1,0,1,2,0,1,2,0,3,1,1,1,1,1,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Concrete",70,8.3699999999999992,0,0,0,0,10,34,1,62,2,40,4,1,13,16,6,2,14,7,3370,2416,19,11,54,203,156,124,184,215,277,748,118,28,66,72,1,0,2,2,2,1,1,1,0,3,1,0,2,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Concrete",70,8.3699999999999992,0,17,38,10,19,55,97,84,78,142,184,298,249,242,359,87,335,205,449,855,339,936,258,442,102,101,52,147,1359,239,484,1387,2234,660,735,127,215,2,3,1,3,5,5,2,5,3,6,3,2,2,2,2,5,4,3,3,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Concrete",70,8.3699999999999992,0,0,0,3,44,10,33,14,39,57,266,249,146,259,481,144,441,14,14,13,10,11,37,81,40,11,20,10,293,11,25,891,9,759,640,39,24,12,12,0,0,3,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; Concrete",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 1 kV; Steel",60,7.75,11,732,976,1179,2062,3377,3613,3413,2813,3335,5439,4751,5067,3583,3434,2470,1953,2142,1810,1932,2007,1993,1951,1675,1464,1442,1386,1331,1327,45,47,25,54,49,48,36,39,43,46,40,50,44,42,34,41,32,30,39,53,54,46,20,20,14,19,13,1,0,1,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV; Steel",60,7.75,0,0,3,1,8,30,37,28,21,47,49,71,84,31,52,34,23,43,60,42,57,26,38,39,27,31,39,30,28,21,15,10,16,15,6,6,20,17,9,8,5,4,5,8,12,8,8,19,18,11,12,3,4,9,3,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; Steel",60,7.75,0,2,0,1,5,0,15,39,30,4,142,4,1,2,8,2,3,4,2,2,1,3,2,3,1,0,0,0,1,2,5,0,0,0,1,0,1,0,0,0,0,0,4,1,0,3,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; Steel",60,7.75,0,0,1,3,4,32,39,42,35,50,37,29,26,26,53,29,24,29,33,34,33,29,31,27,28,25,31,26,28,0,0,0,4,5,3,1,2,2,5,0,2,0,1,0,0,2,52,0,2,73,4,1,0,0,1,0,0,0,0,0,554,453,0,0,0,0,0,0,37,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; Steel",60,7.75,0,0,0,0,0,6,9,7,7,5,3,8,3,3,3,6,6,3,3,3,4,6,159,14,2,4,3,3,3,11,0,0,288,0,0,24,197,0,2,1,0,0,0,0,0,0,16,0,0,0,0,0,0,48,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; Steel",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",60,7.75,29.207205083787301,65.698176429739604,147.63806071689501,140.05164967920001,135.89775367109499,162.873756638114,185.62901676322801,167.57451511583301,185.260681517808,226.73283835284099,224.797511760812,269.13285232704999,239.60295798472501,209.15435855742601,120.03775272927101,102.70560871415501,128.92760635442801,121.926741148118,145.13967300625799,132.18566823255,154.06140477791899,156.79747338842901,169.59076476231701,224.88858545601201,218.49938369601699,209.98712189371599,265.024100409526,255.58979018746899,277.42964293841101,299.02769129822201,207.10284883105601,205.59174749172601,286.53064271136202,372.83295479465602,362.968875803147,312.43054943718198,420.49351579380101,417.95559951630702,349.39428821163602,256.31551456244398,320.88512877708598,360.16346854646099,346.254500385136,350.62798275107502,353.70925242611298,313.71193101659497,343.14412859657801,329.175885978964,382.84218744305099,346.89271079970803,306.20044274090202,257.56175848125599,249.295494635918,267.736832139694,234.830466963834,277.70418570004301,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,223.69858247481895,0.94636610512538599,0,4.9545483431545101,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",60,7.75,67.659840461326397,199.974043747682,313.92436910111599,402.391722042852,350.64222990748601,409.283806806087,483.59141987543802,425.35001120484401,396.36622326965301,583.43570064317998,483.10812561783598,616.93810780600904,397.33533073187198,277.71223024872,128.61128301565699,100.982382899168,144.68606160309099,190.666395090424,228.24613847297101,220.11467976719999,280.62519564409899,314.67952384375701,374.28051044894403,591.40369408205004,433.31750312899601,442.05891809422701,541.776335540736,490.51786191674302,481.10090764479799,435.21122716823999,245.45735292110001,340.70350040500398,469.77574157137502,592.39946972561802,607.59931849272903,533.66866756744196,872.62029157756103,787.94451567294198,860.00925877565999,447.99221550764003,510.00764742823901,573.71764832268798,570.44790309944597,468.61952143118702,607.50905442913995,339.67316458215203,484.78034342456698,598.137183752483,734.75604245623799,642.48148228917705,681.90306315287,698.77748466687399,642.106763689319,948.10792976560799,1012.59206014888,677.30536190932003,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,616.03663871793935,0.21806107195507499,15.6673773698933,3.9072536412967001,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",60,7.75,16.845263076737702,102.26467397511399,94.828745847989595,83.686079682631004,145.82116956051601,219.24175151709801,219.15222803936999,160.930314029111,141.99482701253899,179.88630957856401,178.843089250915,239.814895501872,239.62934267613099,203.493289532755,56.812925828486598,141.94312551020101,237.372197834882,192.06165614426899,1020.27800037984,1764.1142925250199,206.328131241726,203.87020488040801,203.28147203764499,260.77970414298301,343.55651467971001,363.76156504922102,644.58449046393002,572.50619798712103,632.59787636964597,1335.4277882087999,1268.6830211210599,1499.9822077582401,3087.9338624971801,2205.0973561361102,1867.8729923941901,2354.60487936543,3754.27220592607,4843.2695523197599,2969.4015665597599,971.45471509961499,669.23681807461799,871.389145887724,1233.5662150902599,2033.9943745994201,2817.2564543189801,1155.0966794214301,997.14877577685797,1580.3460945214999,2069.2303516207298,1395.0050118636,1081.68445228673,1311.8499685459799,1194.3769750296101,1479.0531819544999,1325.05317710956,1482.53192337976,220.48620512023601,143.30416132007201,147.18082916972401,211.952941280517,203.414858096556,226.485255811705,293.80397149606199,284.25762581170397,333.48231233703399,347.81694042505302,439.44757000459998,460.73148440269699,880.21537423031805,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase",60,7.75,4.2797065762345898,5.0735700276721802,15.3889103100977,25.888860502015199,34.357695055344998,46.446057757929999,92.778769320759196,49.300868128162797,41.2984465987833,30.533983950341799,50.572688001291901,64.783044462441097,60.3069920555808,26.773895131993601,17.425899761396401,10.5614973866236,26.2280768897086,16.476561876461101,25.672101300027901,38.120722778110597,44.935101293746897,21.590887866262602,20.304609029742199,54.778673507028003,51.5661284625143,35.023757000195197,38.372661010849697,38.111131296798298,47.207215325106198,97.846942462231993,52.683430515488503,41.526516994318399,86.229142343671597,66.524980266382002,61.536376349075901,61.443345833789401,109.14269848661399,126.29269662206001,82.252390667457306,53.806714781605102,54.443860160285702,43.489701472161897,37.947546879238097,50.9970388413265,65.563723153680598,90.483615776511797,61.2125777755667,110.11209239534701,97.005094832402804,55.966086902237301,48.318857786104999,66.9609892267314,60.631766884535899,56.963918101845998,36.867306181788202,32.301541762671498,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,20.740878173028424,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase",60,7.75,31.508058273945601,59.610367345129802,71.132779976543205,144.208179960639,129.80122029647899,118.359763447883,198.848763161969,139.85966766542501,158.93795041571801,162.21309318236001,130.18145198753501,146.28607598551201,90.730566712952395,77.884412680135696,32.059727548588903,54.386010776064303,42.629796170563999,74.118857783794496,122.289994648589,112.971561398707,69.123366666906193,80.597838852980601,54.950916900151597,150.706673078666,121.739533893222,133.46720526903101,120.277087829255,231.38764968007101,203.010820885296,373.18718269464699,249.02906112896801,225.5687315548,314.23774191740898,248.22345045787901,213.38964752348201,172.32372042502999,291.032117747889,360.06036893955502,285.49959122311299,173.69570768854899,142.67949728596699,147.694013385603,154.52903344181999,177.22879221823399,263.25851053525702,160.56251190233601,225.38489333985299,247.85355565891501,253.72560048773499,366.41594866695698,331.30667738929998,275.56477862642498,270.62150515570102,426.342592827055,247.076673251127,223.09860093704199,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,127.97210456239233,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV",60,7.75,5.0092360392128699,22.856699152689298,132.20596896607,68.949305512922294,60.676691770400801,41.164604972510901,86.214406715982506,134.780007144047,142.70856269595799,102.15865437428501,61.635620367442897,155.79667671169099,88.048912413363993,45.446615362344303,46.054526286339403,34.257253985454398,77.785645959949207,112.85607973528001,121.951924385989,367.95975074832,99.979914339544493,390.61473932542299,50.178583625925803,229.698231809216,99.756611919151993,78.937270189087897,91.794654667969297,44.342425495888797,453.70352552780702,201.58957909040799,41.3446649573645,364.116631767586,618.67383333264604,318.78862927719598,253.50466891328301,119.001694657708,335.31508556415002,171.86330003650599,96.447002806390202,98.447647825409902,87.892628746579504,160.963101336525,101.996283098996,108.033324893588,64.162642363651699,189.42090265449301,203.23354665929699,89.204800429640002,280.41472942334099,225.27288405344899,264.05376790955398,372.120984021124,221.03858264620999,480.66969372255198,316.48771410478798,377.51591234697901,50.2102850493199,52.198280892201097,71.412701867796997,131.71985724378399,373.99432537806399,160.51578482283901,71.560854621020596,125.351894036639,106.825203695846,190.35759294278199,121.529668498352,109.908733601677,749.35461546693602,16.563647407224099,24.756090572295602,4.6834146729962702,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",60,7.75,0,0.15178562602572601,4.8058529003122397,1.86362265960096,14.8458501699696,3.7313150768560699,0.22827660014843101,83.233130163080702,62.1838047021945,5.3957201715641103,170.05811893464499,12.2928455545128,1.9408421536561,8.2853029977602993E-2,15.5517372940676,89.250982190095698,166.62268395148399,8.2866717895856006,0,5.3339026938957899,0,0.12503386703429301,163.05545878331,0,27.090095894814201,0.38699942508507801,2.51934583342784,0,104.85004373586899,23.953020220468201,2.4788652809240199,234.39226548319999,289.730413709299,236.69356278654101,119.146071582231,10.0820309496505,123.23677086491401,17.007515724552601,155.52738638218199,26.7652123839549,4.8492834309158201,1.9954285612024301E-3,58.787695556289798,9.93862967773739E-2,9.4117710848216198,72.941754371390402,4.8890171172713597,5.6249162910825596,40.073082208725999,42.212112710871303,39.243974114806797,39.256980544734503,85.278143379380097,143.71652594757401,0,0,18.287939712234699,39.892501700624003,0,0,63.333026303842203,20.933768934721101,0,0,0,13.001452477470201,1.13211521855525E-3,14.387247752802001,19.4811007295582,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",50,7.07,90.838021704744804,84.060684318798295,164.88806107014199,250.265751789864,280.87553180584803,380.46564002662399,399.092885817114,355.31298799884399,519.15087073873997,1142.05177161809,1247.6042833675699,639.22016306138096,222.73705476544799,309.50671688907403,83.816864369257999,17.521103126609901,13.2223043200788,4.4606020818557299,6.1606578308530802,3.8147353965525999,2.13422256733132,3.5671193149662201,6.2233274823091003E-2,3.19359752248609,10.725162535364101,8.1257547506409704,1.6433762209768401,5.3403123997091999,0,1.2248835764739701,0.55106181834834,0,0.72374090956245596,0,0.51273954040696701,0,0,0.25763769231734202,0,0,0,3.7643552106549502E-2,0,0,0.19264538287171701,0,0,8.3831512743969397E-2,0.44816924166260302,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",50,7.07,19.117165335113999,16.416048218534499,24.147628831524699,33.707653101923,72.455802791765095,104.486689075022,91.539114924817298,109.32150717445499,143.72185610373899,175.48887542459801,164.43260136995301,87.065064133790401,46.256020217887396,58.076917553153898,45.991630357212202,64.198004608179403,40.8312851215032,14.720599591653301,32.498330611929099,106.90790670448899,17.680448592162399,15.282539405188601,12.247540925182699,11.1332189213717,23.215472623943,18.092382669469298,27.927570964187399,15.750362059945999,11.5247942823069,8.0515912894435093,3.7546593604992098,4.4089174482702704,20.2673307834513,20.4449864866491,10.829461191614801,6.4180800829529101,17.0291524992967,10.030213210565901,7.7901017769036702,2.89703407179061,4.5450270252038001,2.3694503440716499,2.62752634338647,26.088363820241099,1.52047481396659,0.62518155166634204,3.9299569372026499,2.4489768820179099,1.8945307148650199,1.5062183577994499,0.43222137656990101,0.54845261216993302,0.492823266127284,3.5328440227881202,0.133458806478258,0.45618423588122398,0,0,1.48144375876072E-2,0.24145654270589001,0,0.34070946325752999,0,0.80598707781338896,0,0,0,0,3.3049564517901198E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0.40443216055912901,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV",50,7.07,4.2225562338453502,5.4346554032136103,12.1132319601393,13.687795579529601,22.062256095492,17.3094147979903,23.696584989450098,21.3238496432026,35.052816969218703,74.728558208194997,97.690369787090304,32.668777666275098,16.107345179929901,23.2305239284638,15.318276373066301,3.8348112752266599,4.1231826846089001,5.7426547208191296,16.9344819075774,12.050351360612099,13.7180957036935,11.455645559353,7.26577555502171,22.157125613024,20.7953528232071,10.0777460272482,14.710809839448601,6.9488220828704197,7.5814108323527201,11.0591455892728,1.7159041199107401,13.7270002759545,5.3408171133021201,51.969318835300101,3.9361944462431402,3.02517742036689,5.1807775139793204,2.13318955263854,6.8651571395078799,1.1548056301138401,5.0402506134824498E-2,1.90176964688252,0.13130770225826299,4.3650618983715503,0,0.250455747956774,7.5104695918251793E-2,0.65133623067927104,1.860577673344,0.73524176685040099,0.34183043802843599,0.125393518353272,0,3.0514493331271502,0,1.16349770838247,7.4312866713299397E-2,0,0.23272882526698599,0.126073975403967,4.1643223701118497E-2,0.34040836559855803,0.67083654897418199,0,0,0.189520263433577,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV",50,7.07,0.16733503520749199,5.8113263574902999E-3,0.69293151046854096,6.0226095334950996E-3,0.60152302058329898,3.6830476738103202,2.3484394451239701,10.5154102300689,5.91556872815248,5.2113166473932599,0.51759023752129796,0.98962232790326798,0.75443089619590098,6.0205335934685102,1.487743665122,0.26267015386091003,2.4334446087822301,0,0.122012376486293,0.42603694919887602,0.26540267246356197,1.7712262207323901E-2,1.0490834305488601E-2,3.1096066461492801E-2,0,0.62888288730671604,6.2241207395040798E-2,0.44658429599389199,0.55733164465955498,0.16177353732317101,0,0.129444667248831,0.62803617598334505,0.51577344403629899,0,0.29206429972067399,1.38414067765312,0.25175630840940999,0.12805941230477699,0,0,0.83922647824891805,0,4.29324706095632,1.2703419136877301,0.83917634238010896,0,0,0,0,0,0.53165514951391202,0,0.75401863234659505,0,0,0,0,0,0,0,0,0,0,0,0,0,0,5.03969671732062E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV",50,7.07,0.10441356930825001,0,0,0,0,0,0,0.149177868000059,1.17444143715778,8.9123204673752205,3.5243288295832298,0.84439275703413197,0,0,0,0,0,0,0,2.5999667936901698,7.7207298759787999E-3,0,0,0.161020121170977,0,0,0,0,0.35475174781080399,0,0,0.64638511960175904,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0.72048821440070099,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",60,7.75,0,0,0,6.1438109193959596,0,0,0,0,0,8.8804522499539509,4.3395143367189998E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,">  132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",35,5.92,82.056005668866504,1603.09415953078,1734.1836320017801,2803.9137546849302,4035.7545227138799,4214.8767789910398,4545.1021676584296,3737.5509899172698,3879.6479753438498,3774.5762607678598,4332.9573725145301,6596.5023093801001,7169.8936660662002,7651.2221871238198,7753.29185271192,6314.3097045188697,6336.3247304300303,5642.8514142285103,5757.9299587641199,5413.6950081532696,5646.8541462123603,5483.7428178705904,6034.1184656495698,6865.6860352938202,6346.3315603896499,6309.3062895390603,7684.2447259905603,7066.8233174821398,6798.64027456438,6128.1826672699799,4965.3890259623804,4358.9751304095398,6714.5829029035904,8974.1251077852994,8083.5172413793098,6806.64573853207,10017.837472573399,8116.5397802460502,6878.6949142413196,5002.41429681297,6694.5692429843502,7690.2488239663298,7640.21467416824,7695.2522389461401,8399.7330681032308,6831.6628134311204,6714.5829029035904,6848.6744243624698,7245.9455737592998,6460.4094219292901,5030.4334206999001,3925.6793931580901,3765.5701138042,3362.2948664316,2488.6986109569598,3890.6554882994301,2361.6118704698201,2242.5305939503601,2341.59821055058,2274.5524498211398,2236.52649597459,2262.5442538696002,2230.52239799882,2196.4991761361198,2194.4978101441998,2186.4923461765002,2216.5128360553599,2187.49302917246,2272.5510838292198,9.0061469636560805,0,73.049858705210397,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",35,5.92,16.018033895526401,244.27501690677701,273.30770334241902,442.49818636391598,623.70219480705805,596.67176260835697,635.71572022870305,529.59624567083995,551.62104227718896,637.71797446564301,927.04371170358797,1345.5148472242099,1127.26913539767,1157.3029489517801,1082.2184150665,950.06963542840697,1044.1755845646201,1014.14177101051,1004.13049982581,950.06963542840697,1015.1428981289801,1023.15191507675,1205.3570506383601,1432.61290653114,1033.1631862614499,1019.14740660286,954.07414390228905,1073.2082710002701,1138.2815337008401,1049.1812201569801,741.83519478656501,873.98397442465705,978.10119474557905,1052.1846015123899,952.07188966534795,841.94790663360504,1157.3029489517801,1090.2274320142601,995.12035575957498,723.81490665409797,830.93550833043003,757.85322868209096,696.784474455397,695.783347336926,720.81152529868598,611.68866938541305,626.70557616246901,667.75178801975505,739.83294054962403,662.74615242740299,605.681906674591,452.50945754861999,449.50607619320903,431.48578806074102,399.44972026968901,490.55228805049501,282.31784740865203,269.30319486853699,268.30206775006701,273.30770334241902,252.28403385454001,255.28741520995101,301.33926265959002,257.28966944689199,261.29417792077402,268.30206775006701,242.272762669836,270.30432198700697,300.33813554111902,2.0022542369408001,0,5.0056355923519904,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Residential ; Complex Type",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Commercial & Industrial  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Subdivision  ",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",40,6.32,337.97194264974598,719.19624700764496,814.75379031635305,1137.63769981209,1065.2151406728599,852.97680763983601,895.22330047105504,1007.88061468764,1425.3161986151499,1846.7752580504,1534.95590620093,1082.31491158074,1078.2914360730001,1009.8923524415,933.446317794538,671.92040979175795,677.95562305336,677.95562305336,605.533063914129,654.82063888388404,553.22788231357299,583.40394862158598,700.08473834590302,842.91811887049903,721.20798476151299,657.83824551468501,693.04365620736701,716.17864037684399,783.57185513140598,817.77139694715402,689.02018069963196,823.80661020875698,744.34296893098895,828.83595459342598,825.81834796262501,689.02018069963196,943.50500656387601,895.22330047105504,683.99083631496296,452.64099462019601,367.14214008082598,404.35928852737499,312.82522072640199,407.37689515817698,501.928569589951,298.743056449329,330.93086051121003,330.93086051121003,364.12453345002399,286.67262992612399,255.49069474117701,217.26767741769399,191.11508661741601,664.87932765322103,250.461350356509,119.698396355119,28.164328554145499,11.064557646271499,12.070426523205199,14.082164277072801,5.0293443846688497,1.00586887693377,1.00586887693377,20.117377538675399,1.00586887693377,0,1.00586887693377,1.00586887693377,0,0,0,0,2.0117377538675401,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",40,6.32,12,24,26,30,29,26,18,17,19,80,55,47,26,17,15,10,10,8,13,9,8,6,3,14,6,6,14,12,10,8,12,20,21,11,9,17,15,9,3,2,8,1,0,4,7,3,7,2,4,3,0,2,0,2,4,2,1,0,1,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",40,6.32,70.230452674897094,38.677640603566502,53.945130315500698,66.159122085047997,60.052126200274301,60.052126200274301,44.784636488340198,49.873799725651601,26.4636488340192,28.499314128943698,21.3744855967078,35.624142661179697,30.5349794238683,18.320987654321002,25.4458161865569,14.249657064471901,20.3566529492455,10.1783264746228,11.196159122085,2.03566529492455,7.1248285322359397,3.05349794238683,3.05349794238683,3.05349794238683,0,3.05349794238683,2.03566529492455,1.0178326474622801,4.0713305898491097,3.05349794238683,2.03566529492455,9.1604938271604901,1.0178326474622801,3.05349794238683,3.05349794238683,3.05349794238683,0,0,1.0178326474622801,0,0,0,0,0,0,0,0,1.0178326474622801,0,0,0,1.0178326474622801,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",40,6.32,160.036029273785,274.06170013135699,374.08421842747202,505.11371739538401,422.09502720960802,337.07588665791002,365.08219178082197,441.09930568586998,1228.2765246762999,551.12407581159698,527.11867142052904,333.07498592606498,309.06958153499698,333.07498592606498,320.07205854757001,372.08376806155002,488.10988928504401,500.11259148057798,522.117545505723,471.106061174704,621.139838618878,589.13263276412101,772.17384124601199,817.18397447926395,866.19500844436095,750.16888722086696,719.16190654907098,733.16505911052695,778.17519234377903,609.13713642334403,463.104259711015,502.11304184649998,612.13781197222704,602.13556014261599,648.14591855882895,594.13375867892705,718.16168136610997,632.14231563145097,604.13601050853799,389.08759617189003,432.09727903921902,383.08624507412298,326.07340964533699,273.06147494839598,302.068005254269,241.05426909363899,327.073634828298,245.05516982548301,330.07431037718101,281.06327641208497,268.06034903359,272.06124976543401,267.060123850629,360.08106586601599,235.05291799587201,106.023869393883,22.004954025145398,24.0054043910677,16.003602927378498,18.0040532933008,13.002927378495,5.0011259148057796,3.00067554888347,33.007431037718099,1.0002251829611599,0,2.0004503659223101,1.0002251829611599,3.00067554888347,0,2.0004503659223101,0,2.0004503659223101,0,0,0,1.0002251829611599,0,0,0,0,0,1.0002251829611599,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",40,6.32,205,704,783,1052,928,907,778,805,1452,1691,1485,838,733,662,535,464,478,400,450,413,492,506,477,542,469,312,334,342,383,290,253,221,289,342,284,271,381,384,342,188,204,240,212,198,186,148,152,139,159,137,113,96,115,264,78,43,9,11,20,11,17,8,2,106,2,4,2,3,1,4,1,2,6,0,0,1,0,1,2,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",40,6.32,108.24197162061201,108.24197162061201,72.161314413741593,75.168035847647502,75.168035847647502,84.188200149365201,63.141150112023901,82.183719193427905,70.156833457804296,66.147871545929803,70.156833457804296,75.168035847647502,95.212845407020197,49.109783420463003,52.116504854368898,23.0515309932786,39.087378640776699,18.040328603435398,6.0134428678117997,11.024645257654999,33.073935772964902,14.031366691560899,7.0156833457804302,10.022404779686299,4.0089619118745299,1.00224047796863,1.00224047796863,1.00224047796863,2.0044809559372698,0,0,3.0067214339058999,0,3.0067214339058999,3.0067214339058999,3.0067214339058999,4.0089619118745299,3.0067214339058999,1.00224047796863,0,0,0,0,1.00224047796863,0,0,1.00224047796863,2.0044809559372698,0,0,1.00224047796863,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",40,6.32,0,1.0097087378640801,1.0097087378640801,1.0097087378640801,0,1.0097087378640801,1.0097087378640801,1.0097087378640801,17.165048543689299,3.0291262135922299,2.0194174757281602,6.0582524271844704,3.0291262135922299,2.0194174757281602,0,3.0291262135922299,5.0485436893203897,2.0194174757281602,2.0194174757281602,1.0097087378640801,6.0582524271844704,3.0291262135922299,5.0485436893203897,1.0097087378640801,1.0097087378640801,1.0097087378640801,2.0194174757281602,1.0097087378640801,6.0582524271844704,3.0291262135922299,3.0291262135922299,1.0097087378640801,0,0,3.0291262135922299,1.0097087378640801,2.0194174757281602,0,1.0097087378640801,0,2.0194174757281602,1.0097087378640801,1.0097087378640801,1.0097087378640801,1.0097087378640801,0,1.0097087378640801,1.0097087378640801,0,0,0,1.0097087378640801,0,0,1.0097087378640801,0,0,0,0,0,0,0,0,1.0097087378640801,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",40,6.32,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",40,6.32,0,0,0,1,0,0,0,0,0,0,0,1,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",40,6.32,1.00501253132832,3.0150375939849599,11.055137844611499,12.0601503759398,7.0350877192982502,12.0601503759398,13.065162907268199,12.0601503759398,16.080200501253099,12.0601503759398,24.1203007518797,18.090225563909801,22.110275689222998,7.0350877192982502,10.0501253132832,11.055137844611499,10.0501253132832,7.0350877192982502,7.0350877192982502,5.0250626566415999,7.0350877192982502,0,6.0300751879699197,5.0250626566415999,2.01002506265664,2.01002506265664,5.0250626566415999,6.0300751879699197,9.0451127819548898,3.0150375939849599,7.0350877192982502,7.0350877192982502,8.0401002506265709,19.095238095238098,1.00501253132832,7.0350877192982502,6.0300751879699197,7.0350877192982502,0,3.0150375939849599,2.01002506265664,2.01002506265664,5.0250626566415999,2.01002506265664,2.01002506265664,4.0200501253132801,5.0250626566415999,3.0150375939849599,1.00501253132832,3.0150375939849599,2.01002506265664,5.0250626566415999,2.01002506265664,4.0200501253132801,3.0150375939849599,2.01002506265664,3.0150375939849599,2.01002506265664,4.0200501253132801,3.0150375939849599,0,2.01002506265664,1.00501253132832,1.00501253132832,1.00501253132832,0,1.00501253132832,0,3.0150375939849599,0,1.00501253132832,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",40,6.32,16.018720748829899,84.098283931357201,93.1088143525741,129.150936037441,192.22464898595899,255.29836193447699,193.225819032761,220.25741029641199,225.26326053042101,270.315912636505,405.47386895475802,327.38260530421201,368.43057722308902,342.40015600624002,300.35101404056201,191.22347893915801,112.13104524181,90.105304212168505,99.115834633385305,71.083073322932904,67.078393135725406,61.071372854914202,63.073712948517901,101.118174726989,104.121684867395,89.104134165366602,71.083073322932904,63.073712948517901,55.064352574102998,49.057332293291701,29.0339313572543,24.028081123244899,27.031591263650501,18.021060842433702,31.036271450857999,28.0327613104524,42.049141965678601,43.050312012480497,19.022230889235601,10.011700468018701,16.018720748829899,5.00585023400936,13.015210608424301,10.011700468018701,9.0105304212168509,12.014040561622499,2.0023400936037401,10.011700468018701,12.014040561622499,7.0081903276131001,2.0023400936037401,12.014040561622499,2.0023400936037401,7.0081903276131001,3.0035101404056199,11.0128705148206,0,3.0035101404056199,1.0011700468018701,1.0011700468018701,0,0,0,0,0,0,0,0,0,0,0,0,4.00468018720749,0,0,0,0,0,1.0011700468018701,0,0,0,8.0093603744149799,0,0,0,0,0,0,0,0,0,0,1.0011700468018701,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",40,6.32,36.191556967771199,55.838402178846998,68.246935996368606,73.417158420335895,69.280980481162004,85.825692237857496,77.5533363595098,92.029959146618197,147.868361325465,142.698138901498,194.400363141171,162.344984112574,85.825692237857496,137.52791647753099,98.234226055378997,78.587380844303198,56.872446663640503,45.497957330912399,45.497957330912399,36.191556967771199,41.361779391738501,47.566046300499302,57.906491148433901,21.714934180662699,32.0553790285974,5.1702224239673198,10.340444847934601,16.544711756695399,16.544711756695399,31.021334543803899,4.1361779391738498,17.5787562414889,16.544711756695399,20.6808896958693,14.4766227871085,11.3744893327281,7.2383113935542402,10.340444847934601,4.1361779391738498,5.1702224239673198,20.6808896958693,10.340444847934601,5.1702224239673198,6.20426690876078,0,7.2383113935542402,2.0680889695869298,3.10213345438039,1.03404448479346,2.0680889695869298,4.1361779391738498,11.3744893327281,2.0680889695869298,4.1361779391738498,3.10213345438039,3.10213345438039,0,0,2.0680889695869298,0,0,3.10213345438039,0,0,0,0,0,0,3.10213345438039,0,0,0,1.03404448479346,0,0,0,0,1.03404448479346,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",40,6.32,0,0,0,0,0,0,0,0,0,0,0,0,1,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",40,6.32,0,0,0,0,0,0,5,2,0,0,1,1,1,0,0,0,0,2,1,0,2,2,0,3,0,0,0,0,0,0,0,1,0,2,2,0,3,0,0,2,3,0,2,0,0,2,0,0,0,0,0,2,0,0,2,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",60,7.75,0,1,0,0,1,5,1,2,0,1,2,1,3,1,3,0,1,0,3,4,4,1,0,4,2,2,2,0,0,0,4,3,1,4,3,0,2,2,0,4,0,1,1,8,0,2,1,7,1,2,2,9,3,3,2,2,2,0,0,2,0,0,0,0,0,1,1,0,0,3,0,0,0,0,5,1,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",60,7.75,0,0,0,0,0,2,2,0,0,0,0,2,0,0,5,0,0,0,0,1,2,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA",60,7.75,0,1,1,1,1,4,2,2,1,5,2,6,2,1,3,3,2,3,9,4,5,6,4,3,0,0,5,10,5,1,3,6,11,8,5,8,6,5,12,3,0,5,6,4,1,1,5,3,2,3,2,4,2,3,5,1,1,0,0,0,2,3,1,0,1,0,4,0,1,0,0,0,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",60,7.75,0,0,0,0,1,1,0,3,4,2,11,6,3,8,2,0,4,2,3,0,1,1,6,0,1,1,2,1,1,0,0,2,8,0,2,4,2,5,1,6,2,1,0,2,0,0,2,0,1,0,1,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA",60,7.75,0,0,0,0,1,0,1,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",60,7.75,0,0,0,1,1,1,6,0,2,4,5,6,3,4,3,3,0,0,2,1,2,3,0,0,0,1,1,3,0,2,0,0,0,1,3,1,0,1,0,0,0,0,0,0,0,0,1,2,0,1,0,3,0,3,0,1,0,0,0,0,0,2,0,0,0,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",60,7.75,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,4,1,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  Fuse",30,5.48,1249.0511960973599,1795.4464169253599,2272.50739571648,2920.3168810163602,3150.0512352281298,3180.0615787963402,3687.13290115566,3659.1922364542302,4717.8329768084895,6902.3790206871399,6339.4263689249501,2871.6794276472001,1827.52643936034,1894.79100253046,1681.6140792528599,1351.5003000026099,1001.72457151801,914.798059113558,989.30649831737696,814.41863407507901,841.324459343125,733.70115827094105,781.30377220671505,915.83289854694397,912.72838024678504,777.16441447316902,892.03159157905702,835.115422742806,835.115422742806,805.105079174602,655.05336133357696,702.65597526935005,804.070239741215,869.26512404455696,953.08711814885305,725.42244280385,1108.31303315681,883.75287611196597,755.43278637205503,511.21068009287001,612.62494456473496,629.18237549891705,553.63909686171201,562.95265176218902,601.24171079748498,444.98095635614197,559.84813346202998,537.08166592753003,584.684279863303,455.32935069000598,436.70224088905098,402.552539587301,314.59118774945898,346.67121018443601,413.93577335455097,365.298319985391,147.98203897425199,180.06206140923001,158.330433308116,138.66848407377501,169.713667075366,141.77300237393399,136.59880520700199,133.494286906843,166.60914877520699,189.375616309707,139.703323507161,163.504630475048,129.35492917329699,0,0,0,0,0,0,0,0,0,0,0,0,0,1.03483943338638,0,0,0,0,0,0,0,0,0,1.03483943338638,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV  ; Switch",40,6.32,478.898394577239,979.75501248662101,1722.1520870495899,2906.8505173028898,3176.62297538352,3907.5181234391698,4570.4473421334296,4188.7925080271098,4965.6953621120201,5954.86104174099,4488.8882268997504,2499.0549411345,1937.5518016410999,1542.3037816624999,1549.62318943989,981.84627185158797,631.56032821976498,359.69661077417101,512.35854441669596,437.07320727791699,464.25957902247598,467.39646806992499,414.06935426328897,406.74994648590803,451.712022832679,335.64712807706002,423.48002140563699,329.37334998216198,226.90164109882301,256.17927220834798,238.40356760613599,216.44534427399199,324.14520156974697,392.111130931145,305.32386728505202,237.357937923653,351.33157331430601,259.316161255797,257.22490189083101,149.52504459507699,207.034677131645,238.40356760613599,214.354084909026,225.85601141634001,230.038530146272,205.989047449162,185.076453799501,287.54816268283997,250.951123795933,249.90549411345,189.25897252943301,143.25126650017799,124.42993221548301,155.798822689975,141.160007135212,148.479414912594,88.878523011059599,81.559115233678199,88.878523011059599,102.47170888333901,73.194077773813802,94.106671423474793,84.696004281127401,81.559115233678199,78.422226186228997,93.061041740991797,80.513485551195103,77.376596503746001,82.604744916161295,0,1.04562968248305,8.3650374598644301,1.04562968248305,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2.0912593649661102,2.0912593649661102,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ;  Circuit Breaker",50,7.07,28.832535885167498,57.665071770334897,116.35987696514,423.22043745728001,119.449077238551,130.77614490772399,114.3004101162,89.586807928913203,129.74641148325401,107.092276144908,137.98427887901599,119.449077238551,111.211209842789,62.813738892686203,79.289473684210506,27.802802460697201,194.61961722487999,53.5461380724539,90.616541353383397,21.624401913875602,39.129870129870099,9.2676008202323992,30.892002734108001,38.100136705399898,6.1784005468216003,8.2378673957621302,23.6838687628161,23.6838687628161,23.6838687628161,9.2676008202323992,6.1784005468216003,26.7730690362269,29.8622693096377,31.921736158578302,43.248803827751203,42.219070403280902,74.140806561859193,49.427204374572803,37.070403280929597,19.564935064935099,11.3270676691729,1.0297334244702701,15.446001367054,15.446001367054,1.0297334244702701,14.416267942583699,0,15.446001367054,14.416267942583699,24.713602187286401,12.356801093643201,25.743335611756699,14.416267942583699,21.624401913875602,12.356801093643201,1.0297334244702701,6.1784005468216003,1.0297334244702701,5.1486671223513296,4.1189336978810704,1.0297334244702701,1.0297334244702701,0,0,1.0297334244702701,0,0,3.0892002734108002,1.0297334244702701,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Switch",40,6.32,377.68485707536001,972.22722824069399,1032.40778239006,1642.5140899733401,1442.2581080625,1706.8450271674899,2083.4922884816601,1920.5897539738801,2398.9213998852601,2959.2231109311201,1823.0557524214501,750.18173534473999,734.61779892679999,598.69275421011798,618.40707367284301,317.50430292598998,405.699942627653,351.74496304545897,698.30194728493802,406.73753838885,223.08308865715,223.08308865715,146.301002328642,271.85008943336402,226.19587594073801,189.88002429887601,174.31608788093601,241.759812358678,223.08308865715,259.39894029901097,183.6544497317,305.05315379163699,319.57949444838198,214.78232256758099,258.361344537815,239.684620836286,336.18102662751801,344.48179271708699,212.70713104518899,128.66187438831,97.534001552428194,139.03783200026999,94.421214268840103,195.06800310485599,195.06800310485599,116.21072525395699,138.00023623907401,180.54166244811199,211.66953528399301,176.39127940332801,104.797171880801,132.812257433094,115.17312949276101,155.63936417940701,129.699470149506,93.383618507644002,44.616617731429898,37.353447403057601,47.729405015018102,47.729405015018102,26.977489791097199,37.353447403057601,30.0902770746853,38.391043164253603,45.654213492625999,31.127872835881298,25.939894029901101,44.616617731429898,44.616617731429898,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,4.1503830447841796,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker",50,7.07,20.263736263736298,79.028571428571396,53.698901098901104,144.88571428571399,93.213186813186795,54.712087912087902,83.081318681318706,71.936263736263697,34.448351648351597,96.252747252747298,54.712087912087902,81.054945054944994,84.094505494505498,63.830769230769199,28.3692307692308,29.382417582417599,103.345054945055,74.975824175824201,49.646153846153801,32.421978021977999,35.461538461538503,20.263736263736298,51.672527472527499,17.224175824175799,7.0923076923076902,8.1054945054945104,15.197802197802201,28.3692307692308,41.540659340659303,5.0659340659340701,6.0791208791208797,20.263736263736298,35.461538461538503,36.474725274725301,27.356043956044001,28.3692307692308,16.210989010989,13.171428571428599,3.0395604395604399,10.131868131868099,3.0395604395604399,1.01318681318681,4.0527472527472499,15.197802197802201,6.0791208791208797,2.0263736263736298,4.0527472527472499,2.0263736263736298,5.0659340659340701,8.1054945054945104,4.0527472527472499,15.197802197802201,2.0263736263736298,0,4.0527472527472499,2.0263736263736298,0,0,2.0263736263736298,0,1.01318681318681,0,1.01318681318681,0,1.01318681318681,1.01318681318681,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Switch",40,6.32,86.017204301075296,112.64157706093199,104.449462365591,266.24372759856601,196.610752688172,229.379211469534,233.47526881720401,198.65878136200701,100.35340501792101,169.98637992831499,86.017204301075296,78.849103942652306,34.816487455197098,39.936559139784897,36.864516129032303,20.4802867383513,38.912544802867401,31.744444444444401,23.552329749103901,14.3362007168459,29.696415770609299,19.456272401433701,18.432258064516098,18.432258064516098,8.1921146953405,9.2161290322580598,17.408243727598599,12.2881720430107,26.624372759856598,24.5763440860215,12.2881720430107,20.4802867383513,7.1681003584229401,18.432258064516098,76.8010752688172,22.528315412186402,32.768458781362,32.768458781362,25.600358422939099,6.1440860215053803,2.0480286738351299,5.1200716845878098,17.408243727598599,9.2161290322580598,6.1440860215053803,2.0480286738351299,6.1440860215053803,31.744444444444401,23.552329749103901,30.720430107526902,32.768458781362,27.648387096774201,8.1921146953405,39.936559139784897,17.408243727598599,10.2401433691756,6.1440860215053803,8.1921146953405,4.09605734767025,1.0240143369175601,5.1200716845878098,3.0720430107526902,2.0480286738351299,1.0240143369175601,3.0720430107526902,3.0720430107526902,1.0240143369175601,2.0480286738351299,2.0480286738351299,0,0,0,0,0,0,0,0,2.0480286738351299,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",55,7.42,9.0688775510204103,19.145408163265301,11.084183673469401,11.084183673469401,35.267857142857103,24.183673469387799,13.0994897959184,8.0612244897959204,3.0229591836734699,34.2602040816327,11.084183673469401,25.191326530612201,6.0459183673469399,7.0535714285714297,18.137755102040799,6.0459183673469399,21.160714285714299,18.137755102040799,7.0535714285714297,5.03826530612245,5.03826530612245,0,4.0306122448979602,16.122448979591798,2.0153061224489801,0,1.0076530612244901,0,0,1.0076530612244901,0,0,6.0459183673469399,0,3.0229591836734699,0,2.0153061224489801,1.0076530612244901,0,1.0076530612244901,3.0229591836734699,1.0076530612244901,0,1.0076530612244901,0,0,0,0,5.03826530612245,0,12.091836734693899,6.0459183673469399,0,13.0994897959184,1.0076530612244901,0,0,0,0,2.0153061224489801,0,0,0,1.0076530612244901,0,0,10.0765306122449,4.0306122448979602,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Switch",50,7.07,3.07832898172324,4.1044386422976498,6.15665796344648,12.3133159268929,22.574412532637101,50.279373368146203,61.566579634464702,40.018276762402103,54.383812010443897,86.193211488250597,80.036553524804205,30.783289817232401,54.383812010443897,44.122715404699697,43.096605744125299,32.835509138381198,25.652741514360301,50.279373368146203,41.044386422976501,30.783289817232401,43.096605744125299,23.6005221932115,18.4699738903394,36.9399477806788,11.287206266318501,14.3655352480418,29.757180156657999,60.540469973890303,7.1827676240208902,27.704960835509102,33.861618798955597,37.966057441253298,53.357702349869399,50.279373368146203,103.63707571801601,31.809399477806799,62.5926892950392,42.0704960835509,35.913838120104401,71.827676240208902,69.775456919060005,18.4699738903394,8.2088772845952995,33.861618798955597,5.13054830287206,16.417754569190599,9.2349869451697106,52.331592689295,8.2088772845952995,14.3655352480418,15.3916449086162,11.287206266318501,4.1044386422976498,57.4621409921671,21.548302872062699,8.2088772845952995,10.2610966057441,9.2349869451697106,7.1827676240208902,3.07832898172324,0,0,9.2349869451697106,0,0,0,0,0,0,0,0,0,2.0522193211488302,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",55,7.42,26.467320261437902,42.754901960784302,3.0539215686274499,9.1617647058823497,15.2696078431372,16.287581699346401,20.359477124183002,5.0898692810457504,19.341503267973799,27.485294117647001,24.431372549019599,24.431372549019599,21.377450980392201,35.629084967320303,16.287581699346401,21.377450980392201,19.341503267973799,6.1078431372548998,18.323529411764699,4.0718954248366002,10.179738562091501,11.1977124183006,3.0539215686274499,6.1078431372548998,5.0898692810457504,9.1617647058823497,3.0539215686274499,27.485294117647001,7.1258169934640501,1.01797385620915,2.0359477124183001,7.1258169934640501,8.1437908496732003,16.287581699346401,17.3055555555555,7.1258169934640501,8.1437908496732003,6.1078431372548998,13.233660130718899,7.1258169934640501,12.2156862745098,0,0,1.01797385620915,8.1437908496732003,2.0359477124183001,3.0539215686274499,9.1617647058823497,8.1437908496732003,1.01797385620915,2.0359477124183001,6.1078431372548998,0,2.0359477124183001,0,4.0718954248366002,0,0,0,1.01797385620915,0,0,7.1258169934640501,1.01797385620915,2.0359477124183001,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Switch",50,7.07,1.0471698113207499,6.2830188679245298,0,19.896226415094301,17.801886792452802,2.0943396226415101,39.792452830188701,6.2830188679245298,4.1886792452830202,21.9905660377358,10.4716981132075,13.6132075471698,31.415094339622598,12.566037735848999,0,4.1886792452830202,8.3773584905660403,1.0471698113207499,0,1.0471698113207499,10.4716981132075,1.0471698113207499,2.0943396226415101,5.2358490566037696,12.566037735848999,0,7.3301886792452802,8.3773584905660403,3.14150943396226,3.14150943396226,0,4.1886792452830202,3.14150943396226,1.0471698113207499,26.179245283018901,0,10.4716981132075,1.0471698113207499,5.2358490566037696,0,0,2.0943396226415101,0,0,0,0,0,0,0,21.9905660377358,0,0,0,0,0,0,2.0943396226415101,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",55,7.42,0,2.1259842519685002,0,15.944881889763799,8.5039370078740202,0,10.629921259842501,0,3.18897637795276,9.5669291338582703,4.2519685039370101,3.18897637795276,10.629921259842501,12.755905511810999,6.3779527559055103,3.18897637795276,3.18897637795276,0,0,0,0,0,2.1259842519685002,2.1259842519685002,0,0,2.1259842519685002,3.18897637795276,0,10.629921259842501,4.2519685039370101,0,0,0,4.2519685039370101,0,5.3149606299212602,0,0,0,1.0629921259842501,0,0,0,0,0,0,0,0,0,2.1259842519685002,1.0629921259842501,0,2.1259842519685002,0,0,1.0629921259842501,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Switch",0,0,0,7.6956521739130404,1.2826086956521701,0,0,0,0,0,6.4130434782608701,0,0,0,0,0,0,0,0,0,0,1.2826086956521701,2.5652173913043499,16.673913043478301,1.2826086956521701,2.5652173913043499,1.2826086956521701,0,8.9782608695652204,5.1304347826086998,0,1.2826086956521701,1.2826086956521701,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.2826086956521701,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV ; Circuit Breaker",0,0,0,2.8571428571428599,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.4285714285714299,0,5.71428571428571,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Luminaires ;  Minor Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Brackets ; Major Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Brackets ; Minor Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Lamps ; Major Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Lamps ; Minor Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Poles / Columns ; Major Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Poles / Columns ; Minor Road",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",30,5.47,62,300,147,180,249,212,197,187,213,251,485,493,374,363,430,134,176,205,367,222,430,206,144,106,157,179,162,210,144,259,77,225,284,250,186,227,169,154,194,204,112,172,72,108,196,69,74,129,37,164,111,127,136,109,170,68,33,43,52,102,4,3,64,25,0,2,0,6,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Local Network Wiring Assets",40,6.32,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Network Assets",15,3.87,99,123,425,1647,258,741,4906,2159,1745,0,1656,1095,322,382,0,1,406,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Master Station Assets",5,2.23,0,0,14,2,0,28,0,0,0,0,0,0,117,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Site Infrastructure",25,5,56,183,61,209,26,126,712,177,6,56,152,361,5,29,2,1,0,0,2,0,0,0,0,0,0,1,1,1,0,1,2,1,1,3,0,1,1,1,0,1,0,1,0,1,0,0,0,0,2,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Linear Assets",30,5.47,11,11,7,53,31,200,253,104,1654,1297,1,17,115,82,67,67,66,68,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"AFLC",25,5,0,0,0,3,5,0,2,5,4,5,10,0,1,3,1,0,1,0,1,1,2,0,0,0,0,0,0,2,3,6,0,0,0,0,1,5,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,"OTHER BY: \nDNSP DEFINED","CURRENT TRANSFORMERS",45,6.71,54.744650499286699,69.951497860199694,55.7584403233476,311.23347598668602,123.682358535426,152.06847360913,159.16500237755599,59.813599619591102,110.50309082263399,217.96481217308599,468.37089871612,199.71659533998999,182.482168330956,161.19258202567801,237.22681883024299,139.90299572039899,146.99952448882499,212.895863052782,174.371849738469,53.730860675225898,65.896338563956206,95.296243461721303,110.50309082263399,132.80646695197299,10.1378982406086,27.372325249643399,76.034236804564898,379.157394198764,149.027104136947,25.344745601521598,65.896338563956206,81.103185924869194,165.24774132192101,175.38563956253,69.951497860199694,160.178792201617,104.420351878269,76.034236804564898,99.351402757964806,21.289586305278199,98.337612933903898,45.620542082738901,5.06894912030433,10.1378982406086,23.317165953399901,3.0413694721826001,3.0413694721826001,71.979077508321396,36.496433666191102,45.620542082738901,35.482643842130301,207.826913932477,50.689491203043303,59.813599619591102,48.661911554921502,14.1930575368521,10.1378982406086,3.0413694721826001,21.289586305278199,15.206847360913001,3.0413694721826001,53.730860675225898,58.799809795530201,0,0,0,7.0965287684260598,0,0,0,0,0,6.0827389443651896,27.372325249643399,0,0,48.661911554921502,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"VOLTAGE TRANSFORMERS",45,6.71,16.603773584905699,38.396226415094297,20.754716981132098,69.528301886792406,66.415094339622598,77.830188679245296,72.641509433962298,32.169811320754697,50.849056603773597,88.207547169811306,78.867924528301899,83.018867924528294,97.5471698113207,153.58490566037699,119.339622641509,51.8867924528302,71.603773584905696,36.320754716981099,37.358490566037702,28.018867924528301,35.283018867924497,13.4905660377358,52.924528301886802,16.603773584905699,23.867924528301899,8.3018867924528301,32.169811320754697,81.981132075471706,30.094339622641499,7.2641509433962304,44.622641509433997,29.0566037735849,32.169811320754697,72.641509433962298,56.037735849056602,45.660377358490599,94.433962264150907,25.9433962264151,32.169811320754697,24.905660377358501,56.037735849056602,15.566037735848999,8.3018867924528301,7.2641509433962304,20.754716981132098,3.11320754716981,49.811320754717002,20.754716981132098,14.5283018867924,9.3396226415094308,17.641509433962302,45.660377358490599,17.641509433962302,30.094339622641499,25.9433962264151,4.1509433962264204,11.4150943396226,0,1.0377358490566,2.0754716981132102,3.11320754716981,19.7169811320755,1.0377358490566,0,2.0754716981132102,1.0377358490566,2.0754716981132102,0,16.603773584905699,2.0754716981132102,1.0377358490566,0,2.0754716981132102,3.11320754716981,2.0754716981132102,1.0377358490566,4.1509433962264204,1.0377358490566,0,0,0,0,1.0377358490566,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"CAPACITOR BANKS",30,5.48,0,0,0,1.1229508196721301,0,0,2.2459016393442601,5.6147540983606596,2.2459016393442601,0,2.2459016393442601,12.3524590163934,4.4918032786885203,8.9836065573770494,20.213114754098399,2.2459016393442601,2.2459016393442601,1.1229508196721301,0,2.2459016393442601,2.2459016393442601,2.2459016393442601,8.9677419349999994,8.9836065573770494,4.4918032786885203,1.1229508196721301,0,2.2459016393442601,0,4.4918032786885203,0,0,2.2459016389999999,0,4.4918032786885203,14.5983606557377,3.3688524590163902,4.4918032786885203,5.6147540983606596,0,2.2459016393442601,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"STATIC VAR COMPENSATOR",30,5.48,0,0,0,0,0,0,0,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]

{"sheet":"5.3 MD - Network level","index":22,"n_rows":15,"n_cols":4,"rows_kept":15,"cut":false,"hidden":false,"merged":[[6,1,6,3]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"5.3 MAXIMUM DEMAND AT NETWORK LEVEL"]
[]
[]
[null,"5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL\n              (Summed at transmission connection point)"]
[null,null,"UNIT",{"$f":"CRY","v":"2017-18"}]
[null,"Raw network coincident MD","MW",2597.2460000000001]
[null,"Date MD occurred",null,"2018-02-15"]
[null,"Half hour time period MD occurred",null,"19:00:00"]
[null,"Winter/summer peaking",null,"SUMMER"]
[null,"Embedded generation","MW",-373.42399999999998]
[null,"Weather corrected (10% POE) network coincident MD","MW",2759.491271196976]
[null,"Weather corrected (50% POE) network coincident MD","MW",2564.0460971680177]

{"sheet":"5.4 MD & utilisation-Spatial","index":23,"n_rows":11431,"n_cols":7,"rows_kept":11431,"cut":false,"hidden":false,"merged":[[5,1,5,2],[25,3,26,3],[25,4,26,4],[27,3,28,3],[27,4,28,4],[29,3,30,3],[29,4,30,4],[17,4,18,4],[19,3,20,3],[19,4,20,4],[21,3,22,3],[21,4,22,4],[23,3,24,3],[23,4,24,4],[9,2,30,2],[9,3,10,3],[9,4,10,4],[11,3,12,3],[11,4,12,4],[13,3,14,3],[13,4,14,4],[15,3,16,3],[15,4,16,4],[17,3,18,3],[69,3,70,3],[69,4,70,4],[71,3,72,3],[71,4,72,4],[73,3,74,3],[73,4,74,4],[61,4,62,4],[63,3,64,3],[63,4,64,4],[65,3,66,3],[65,4,66,4],[67,3,68,3],[67,4,68,4],[53,2,74,2],[53,3,54,3],[53,4,54,4],[55,3,56,3],[55,4,56,4],[57,3,58,3],[57,4,58,4],[59,3,60,3],[59,4,60,4],[61,3,62,3],[47,3,48,3],[47,4,48,4],[49,3,50,3],[49,4,50,4],[51,3,52,3],[51,4,52,4],[39,4,40,4],[41,3,42,3],[41,4,42,4],[43,3,44,3],[43,4,44,4],[45,3,46,3],[45,4,46,4],[31,2,52,2],[31,3,32,3],[31,4,32,4],[33,3,34,3],[33,4,34,4],[35,3,36,3],[35,4,36,4],[37,3,38,3],[37,4,38,4],[39,3,40,3],[113,3,114,3],[113,4,114,4],[115,3,116,3],[115,4,116,4],[117,3,118,3],[117,4,118,4],[105,4,106,4],[107,3,108,3],[107,4,108,4],[109,3,110,3],[109,4,110,4],[111,3,112,3],[111,4,112,4],[97,2,118,2],[97,3,98,3],[97,4,98,4],[99,3,100,3],[99,4,100,4],[101,3,102,3],[101,4,102,4],[103,3,104,3],[103,4,104,4],[105,3,106,3],[91,3,92,3],[91,4,92,4],[93,3,94,3],[93,4,94,4],[95,3,96,3],[95,4,96,4],[83,4,84,4],[85,3,86,3],[85,4,86,4],[87,3,88,3],[87,4,88,4],[89,3,90,3],[89,4,90,4],[75,2,96,2],[75,3,76,3],[75,4,76,4],[77,3,78,3],[77,4,78,4],[79,3,80,3],[79,4,80,4],[81,3,82,3],[81,4,82,4],[83,3,84,3],[157,3,158,3],[157,4,158,4],[159,3,160,3],[159,4,160,4],[161,3,162,3],[161,4,162,4],[149,4,150,4],[151,3,152,3],[151,4,152,4],[153,3,154,3],[153,4,154,4],[155,3,156,3],[155,4,156,4],[141,2,162,2],[141,3,142,3],[141,4,142,4],[143,3,144,3],[143,4,144,4],[145,3,146,3],[145,4,146,4],[147,3,148,3],[147,4,148,4],[149,3,150,3],[135,3,136,3],[135,4,136,4],[137,3,138,3],[137,4,138,4],[139,3,140,3],[139,4,140,4],[127,4,128,4],[129,3,130,3],[129,4,130,4],[131,3,132,3],[131,4,132,4],[133,3,134,3],[133,4,134,4],[119,2,140,2],[119,3,120,3],[119,4,120,4],[121,3,122,3],[121,4,122,4],[123,3,124,3],[123,4,124,4],[125,3,126,3],[125,4,126,4],[127,3,128,3],[201,3,202,3],[201,4,202,4],[203,3,204,3],[203,4,204,4],[205,3,206,3],[205,4,206,4],[193,4,194,4],[195,3,196,3],[195,4,196,4],[197,3,198,3],[197,4,198,4],[199,3,200,3],[199,4,200,4],[185,2,206,2],[185,3,186,3],[185,4,186,4],[187,3,188,3],[187,4,188,4],[189,3,190,3],[189,4,190,4],[191,3,192,3],[191,4,192,4],[193,3,194,3],[179,3,180,3],[179,4,180,4],[181,3,182,3],[181,4,182,4],[183,3,184,3],[183,4,184,4],[171,4,172,4],[173,3,174,3],[173,4,174,4],[175,3,176,3],[175,4,176,4],[177,3,178,3],[177,4,178,4],[163,2,184,2],[163,3,164,3],[163,4,164,4],[165,3,166,3],[165,4,166,4],[167,3,168,3],[167,4,168,4],[169,3,170,3],[169,4,170,4],[171,3,172,3],[245,3,246,3],[245,4,246,4],[247,3,248,3],[247,4,248,4],[249,3,250,3],[249,4,250,4],[237,4,238,4],[239,3,240,3],[239,4,240,4],[241,3,242,3],[241,4,242,4],[243,3,244,3],[243,4,244,4],[229,2,250,2],[229,3,230,3],[229,4,230,4],[231,3,232,3],[231,4,232,4],[233,3,234,3],[233,4,234,4],[235,3,236,3],[235,4,236,4],[237,3,238,3],[223,3,224,3],[223,4,224,4],[225,3,226,3],[225,4,226,4],[227,3,228,3],[227,4,228,4],[215,4,216,4],[217,3,218,3],[217,4,218,4],[219,3,220,3],[219,4,220,4],[221,3,222,3],[221,4,222,4],[207,2,228,2],[207,3,208,3],[207,4,208,4],[209,3,210,3],[209,4,210,4],[211,3,212,3],[211,4,212,4],[213,3,214,3],[213,4,214,4],[215,3,216,3],[289,3,290,3],[289,4,290,4],[291,3,292,3],[291,4,292,4],[293,3,294,3],[293,4,294,4],[281,4,282,4],[283,3,284,3],[283,4,284,4],[285,3,286,3],[285,4,286,4],[287,3,288,3],[287,4,288,4],[273,2,294,2],[273,3,274,3],[273,4,274,4],[275,3,276,3],[275,4,276,4],[277,3,278,3],[277,4,278,4],[279,3,280,3],[279,4,280,4],[281,3,282,3],[267,3,268,3],[267,4,268,4],[269,3,270,3],[269,4,270,4],[271,3,272,3],[271,4,272,4],[259,4,260,4],[261,3,262,3],[261,4,262,4],[263,3,264,3],[263,4,264,4],[265,3,266,3],[265,4,266,4],[251,2,272,2],[251,3,252,3],[251,4,252,4],[253,3,254,3],[253,4,254,4],[255,3,256,3],[255,4,256,4],[257,3,258,3],[257,4,258,4],[259,3,260,3],[333,3,334,3],[333,4,334,4],[335,3,336,3],[335,4,336,4],[337,3,338,3],[337,4,338,4],[325,4,326,4],[327,3,328,3],[327,4,328,4],[329,3,330,3],[329,4,330,4],[331,3,332,3],[331,4,332,4],[317,2,338,2],[317,3,318,3],[317,4,318,4],[319,3,320,3],[319,4,320,4],[321,3,322,3],[321,4,322,4],[323,3,324,3],[323,4,324,4],[325,3,326,3],[311,3,312,3],[311,4,312,4],[313,3,314,3],[313,4,314,4],[315,3,316,3],[315,4,316,4],[303,4,304,4],[305,3,306,3],[305,4,306,4],[307,3,308,3],[307,4,308,4],[309,3,310,3],[309,4,310,4],[295,2,316,2],[295,3,296,3],[295,4,296,4],[297,3,298,3],[297,4,298,4],[299,3,300,3],[299,4,300,4],[301,3,302,3],[301,4,302,4],[303,3,304,3],[377,3,378,3],[377,4,378,4],[379,3,380,3],[379,4,380,4],[381,3,382,3],[381,4,382,4],[369,4,370,4],[371,3,372,3],[371,4,372,4],[373,3,374,3],[373,4,374,4],[375,3,376,3],[375,4,376,4],[361,2,382,2],[361,3,362,3],[361,4,362,4],[363,3,364,3],[363,4,364,4],[365,3,366,3],[365,4,366,4],[367,3,368,3],[367,4,368,4],[369,3,370,3],[355,3,356,3],[355,4,356,4],[357,3,358,3],[357,4,358,4],[359,3,360,3],[359,4,360,4],[347,4,348,4],[349,3,350,3],[349,4,350,4],[351,3,352,3],[351,4,352,4],[353,3,354,3],[353,4,354,4],[339,2,360,2],[339,3,340,3],[339,4,340,4],[341,3,342,3],[341,4,342,4],[343,3,344,3],[343,4,344,4],[345,3,346,3],[345,4,346,4],[347,3,348,3],[421,3,422,3],[421,4,422,4],[423,3,424,3],[423,4,424,4],[425,3,426,3],[425,4,426,4],[413,4,414,4],[415,3,416,3],[415,4,416,4],[417,3,418,3],[417,4,418,4],[419,3,420,3],[419,4,420,4],[405,2,426,2],[405,3,406,3],[405,4,406,4],[407,3,408,3],[407,4,408,4],[409,3,410,3],[409,4,410,4],[411,3,412,3],[411,4,412,4],[413,3,414,3],[399,3,400,3],[399,4,400,4],[401,3,402,3],[401,4,402,4],[403,3,404,3],[403,4,404,4],[391,4,392,4],[393,3,394,3],[393,4,394,4],[395,3,396,3],[395,4,396,4],[397,3,398,3],[397,4,398,4],[383,2,404,2],[383,3,384,3],[383,4,384,4],[385,3,386,3],[385,4,386,4],[387,3,388,3],[387,4,388,4],[389,3,390,3],[389,4,390,4],[391,3,392,3],[465,3,466,3],[465,4,466,4],[467,3,468,3],[467,4,468,4],[469,3,470,3],[469,4,470,4],[457,4,458,4],[459,3,460,3],[459,4,460,4],[461,3,462,3],[461,4,462,4],[463,3,464,3],[463,4,464,4],[449,2,470,2],[449,3,450,3],[449,4,450,4],[451,3,452,3],[451,4,452,4],[453,3,454,3],[453,4,454,4],[455,3,456,3],[455,4,456,4],[457,3,458,3],[443,3,444,3],[443,4,444,4],[445,3,446,3],[445,4,446,4],[447,3,448,3],[447,4,448,4],[435,4,436,4],[437,3,438,3],[437,4,438,4],[439,3,440,3],[439,4,440,4],[441,3,442,3],[441,4,442,4],[427,2,448,2],[427,3,428,3],[427,4,428,4],[429,3,430,3],[429,4,430,4],[431,3,432,3],[431,4,432,4],[433,3,434,3],[433,4,434,4],[435,3,436,3],[509,3,510,3],[509,4,510,4],[511,3,512,3],[511,4,512,4],[513,3,514,3],[513,4,514,4],[501,4,502,4],[503,3,504,3],[503,4,504,4],[505,3,506,3],[505,4,506,4],[507,3,508,3],[507,4,508,4],[493,2,514,2],[493,3,494,3],[493,4,494,4],[495,3,496,3],[495,4,496,4],[497,3,498,3],[497,4,498,4],[499,3,500,3],[499,4,500,4],[501,3,502,3],[487,3,488,3],[487,4,488,4],[489,3,490,3],[489,4,490,4],[491,3,492,3],[491,4,492,4],[479,4,480,4],[481,3,482,3],[481,4,482,4],[483,3,484,3],[483,4,484,4],[485,3,486,3],[485,4,486,4],[471,2,492,2],[471,3,472,3],[471,4,472,4],[473,3,474,3],[473,4,474,4],[475,3,476,3],[475,4,476,4],[477,3,478,3],[477,4,478,4],[479,3,480,3],[553,3,554,3],[553,4,554,4],[555,3,556,3],[555,4,556,4],[557,3,558,3],[557,4,558,4],[545,4,546,4],[547,3,548,3],[547,4,548,4],[549,3,550,3],[549,4,550,4],[551,3,552,3],[551,4,552,4],[537,2,558,2],[537,3,538,3],[537,4,538,4],[539,3,540,3],[539,4,540,4],[541,3,542,3],[541,4,542,4],[543,3,544,3],[543,4,544,4],[545,3,546,3],[531,3,532,3],[531,4,532,4],[533,3,534,3],[533,4,534,4],[535,3,536,3],[535,4,536,4],[523,4,524,4],[525,3,526,3],[525,4,526,4],[527,3,528,3],[527,4,528,4],[529,3,530,3],[529,4,530,4],[515,2,536,2],[515,3,516,3],[515,4,516,4],[517,3,518,3],[517,4,518,4],[519,3,520,3],[519,4,520,4],[521,3,522,3],[521,4,522,4],[523,3,524,3],[597,3,598,3],[597,4,598,4],[599,3,600,3],[599,4,600,4],[601,3,602,3],[601,4,602,4],[589,4,590,4],[591,3,592,3],[591,4,592,4],[593,3,594,3],[593,4,594,4],[595,3,596,3],[595,4,596,4],[581,2,602,2],[581,3,582,3],[581,4,582,4],[583,3,584,3],[583,4,584,4],[585,3,586,3],[585,4,586,4],[587,3,588,3],[587,4,588,4],[589,3,590,3],[575,3,576,3],[575,4,576,4],[577,3,578,3],[577,4,578,4],[579,3,580,3],[579,4,580,4],[567,4,568,4],[569,3,570,3],[569,4,570,4],[571,3,572,3],[571,4,572,4],[573,3,574,3],[573,4,574,4],[559,2,580,2],[559,3,560,3],[559,4,560,4],[561,3,562,3],[561,4,562,4],[563,3,564,3],[563,4,564,4],[565,3,566,3],[565,4,566,4],[567,3,568,3],[641,3,642,3],[641,4,642,4],[643,3,644,3],[643,4,644,4],[645,3,646,3],[645,4,646,4],[633,4,634,4],[635,3,636,3],[635,4,636,4],[637,3,638,3],[637,4,638,4],[639,3,640,3],[639,4,640,4],[625,2,646,2],[625,3,626,3],[625,4,626,4],[627,3,628,3],[627,4,628,4],[629,3,630,3],[629,4,630,4],[631,3,632,3],[631,4,632,4],[633,3,634,3],[619,3,620,3],[619,4,620,4],[621,3,622,3],[621,4,622,4],[623,3,624,3],[623,4,624,4],[611,4,612,4],[613,3,614,3],[613,4,614,4],[615,3,616,3],[615,4,616,4],[617,3,618,3],[617,4,618,4],[603,2,624,2],[603,3,604,3],[603,4,604,4],[605,3,606,3],[605,4,606,4],[607,3,608,3],[607,4,608,4],[609,3,610,3],[609,4,610,4],[611,3,612,3],[685,3,686,3],[685,4,686,4],[687,3,688,3],[687,4,688,4],[689,3,690,3],[689,4,690,4],[677,4,678,4],[679,3,680,3],[679,4,680,4],[681,3,682,3],[681,4,682,4],[683,3,684,3],[683,4,684,4],[669,2,690,2],[669,3,670,3],[669,4,670,4],[671,3,672,3],[671,4,672,4],[673,3,674,3],[673,4,674,4],[675,3,676,3],[675,4,676,4],[677,3,678,3],[663,3,664,3],[663,4,664,4],[665,3,666,3],[665,4,666,4],[667,3,668,3],[667,4,668,4],[655,4,656,4],[657,3,658,3],[657,4,658,4],[659,3,660,3],[659,4,660,4],[661,3,662,3],[661,4,662,4],[647,2,668,2],[647,3,648,3],[647,4,648,4],[649,3,650,3],[649,4,650,4],[651,3,652,3],[651,4,652,4],[653,3,654,3],[653,4,654,4],[655,3,656,3],[729,3,730,3],[729,4,730,4],[731,3,732,3],[731,4,732,4],[733,3,734,3],[733,4,734,4],[721,4,722,4],[723,3,724,3],[723,4,724,4],[725,3,726,3],[725,4,726,4],[727,3,728,3],[727,4,728,4],[713,2,734,2],[713,3,714,3],[713,4,714,4],[715,3,716,3],[715,4,716,4],[717,3,718,3],[717,4,718,4],[719,3,720,3],[719,4,720,4],[721,3,722,3],[707,3,708,3],[707,4,708,4],[709,3,710,3],[709,4,710,4],[711,3,712,3],[711,4,712,4],[699,4,700,4],[701,3,702,3],[701,4,702,4],[703,3,704,3],[703,4,704,4],[705,3,706,3],[705,4,706,4],[691,2,712,2],[691,3,692,3],[691,4,692,4],[693,3,694,3],[693,4,694,4],[695,3,696,3],[695,4,696,4],[697,3,698,3],[697,4,698,4],[699,3,700,3],[773,3,774,3],[773,4,774,4],[775,3,776,3],[775,4,776,4],[777,3,778,3],[777,4,778,4],[765,4,766,4],[767,3,768,3],[767,4,768,4],[769,3,770,3],[769,4,770,4],[771,3,772,3],[771,4,772,4],[757,2,778,2],[757,3,758,3],[757,4,758,4],[759,3,760,3],[759,4,760,4],[761,3,762,3],[761,4,762,4],[763,3,764,3],[763,4,764,4],[765,3,766,3],[751,3,752,3],[751,4,752,4],[753,3,754,3],[753,4,754,4],[755,3,756,3],[755,4,756,4],[743,4,744,4],[745,3,746,3],[745,4,746,4],[747,3,748,3],[747,4,748,4],[749,3,750,3],[749,4,750,4],[735,2,756,2],[735,3,736,3],[735,4,736,4],[737,3,738,3],[737,4,738,4],[739,3,740,3],[739,4,740,4],[741,3,742,3],[741,4,742,4],[743,3,744,3],[817,3,818,3],[817,4,818,4],[819,3,820,3],[819,4,820,4],[821,3,822,3],[821,4,822,4],[809,4,810,4],[811,3,812,3],[811,4,812,4],[813,3,814,3],[813,4,814,4],[815,3,816,3],[815,4,816,4],[801,2,822,2],[801,3,802,3],[801,4,802,4],[803,3,804,3],[803,4,804,4],[805,3,806,3],[805,4,806,4],[807,3,808,3],[807,4,808,4],[809,3,810,3],[795,3,796,3],[795,4,796,4],[797,3,798,3],[797,4,798,4],[799,3,800,3],[799,4,800,4],[787,4,788,4],[789,3,790,3],[789,4,790,4],[791,3,792,3],[791,4,792,4],[793,3,794,3],[793,4,794,4],[779,2,800,2],[779,3,780,3],[779,4,780,4],[781,3,782,3],[781,4,782,4],[783,3,784,3],[783,4,784,4],[785,3,786,3],[785,4,786,4],[787,3,788,3],[861,3,862,3],[861,4,862,4],[863,3,864,3],[863,4,864,4],[865,3,866,3],[865,4,866,4],[853,4,854,4],[855,3,856,3],[855,4,856,4],[857,3,858,3],[857,4,858,4],[859,3,860,3],[859,4,860,4],[845,2,866,2],[845,3,846,3],[845,4,846,4],[847,3,848,3],[847,4,848,4],[849,3,850,3],[849,4,850,4],[851,3,852,3],[851,4,852,4],[853,3,854,3],[839,3,840,3],[839,4,840,4],[841,3,842,3],[841,4,842,4],[843,3,844,3],[843,4,844,4],[831,4,832,4],[833,3,834,3],[833,4,834,4],[835,3,836,3],[835,4,836,4],[837,3,838,3],[837,4,838,4],[823,2,844,2],[823,3,824,3],[823,4,824,4],[825,3,826,3],[825,4,826,4],[827,3,828,3],[827,4,828,4],[829,3,830,3],[829,4,830,4],[831,3,832,3],[905,3,906,3],[905,4,906,4],[907,3,908,3],[907,4,908,4],[909,3,910,3],[909,4,910,4],[897,4,898,4],[899,3,900,3],[899,4,900,4],[901,3,902,3],[901,4,902,4],[903,3,904,3],[903,4,904,4],[889,2,910,2],[889,3,890,3],[889,4,890,4],[891,3,892,3],[891,4,892,4],[893,3,894,3],[893,4,894,4],[895,3,896,3],[895,4,896,4],[897,3,898,3],[883,3,884,3],[883,4,884,4],[885,3,886,3],[885,4,886,4],[887,3,888,3],[887,4,888,4],[875,4,876,4],[877,3,878,3],[877,4,878,4],[879,3,880,3],[879,4,880,4],[881,3,882,3],[881,4,882,4],[867,2,888,2],[867,3,868,3],[867,4,868,4],[869,3,870,3],[869,4,870,4],[871,3,872,3],[871,4,872,4],[873,3,874,3],[873,4,874,4],[875,3,876,3],[949,3,950,3],[949,4,950,4],[951,3,952,3],[951,4,952,4],[953,3,954,3],[953,4,954,4],[941,4,942,4],[943,3,944,3],[943,4,944,4],[945,3,946,3],[945,4,946,4],[947,3,948,3],[947,4,948,4],[933,2,954,2],[933,3,934,3],[933,4,934,4],[935,3,936,3],[935,4,936,4],[937,3,938,3],[937,4,938,4],[939,3,940,3],[939,4,940,4],[941,3,942,3],[927,3,928,3],[927,4,928,4],[929,3,930,3],[929,4,930,4],[931,3,932,3],[931,4,932,4],[919,4,920,4],[921,3,922,3],[921,4,922,4],[923,3,924,3],[923,4,924,4],[925,3,926,3],[925,4,926,4],[911,2,932,2],[911,3,912,3],[911,4,912,4],[913,3,914,3],[913,4,914,4],[915,3,916,3],[915,4,916,4],[917,3,918,3],[917,4,918,4],[919,3,920,3],[993,3,994,3],[993,4,994,4],[995,3,996,3],[995,4,996,4],[997,3,998,3],[997,4,998,4],[985,4,986,4],[987,3,988,3],[987,4,988,4],[989,3,990,3]],"merged_total":11938,"flags":["merged_cut"]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL"]
[]
[null,"There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND"]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND",{"$f":"CRY","v":"2017-18"}]
[null,"SUBTRANSMISSION SUBSTATION","Barcaldine BSP","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.690000534057617]
[null,null,null,null,null,"Coincident",20.177000045776367]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.712764739990234]
[null,null,null,null,null,"Coincident",20.275388717651367]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-20.420000076293945]
[null,null,null,null,null,"Coincident",-0.5220000147819519]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.522426605224609]
[null,null,null,null,null,"Coincident",19.090871810913086]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.543966293334961]
[null,null,null,null,null,"Coincident",19.183963775634766]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.12602424621582]
[null,null,null,null,null,"Coincident",17.791875839233398]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.146099090576172]
[null,null,null,null,null,"Coincident",17.878635406494141]
[null,null,"Boat Creek BSP","Substation Rating","MVA","Non-Coincident",160]
[null,null,null,null,null,"Coincident",160]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",41]
[null,null,null,null,null,"Coincident",38.400001525878906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.358131408691406]
[null,null,null,null,null,"Coincident",42.58074951171875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",45.100002288818359]
[null,null,null,null,null,"Coincident",42.240001678466797]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.893943786621094]
[null,null,null,null,null,"Coincident",46.838825225830078]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",41]
[null,null,null,null,null,"Coincident",38.400001525878906]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",45.358131408691406]
[null,null,null,null,null,"Coincident",42.58074951171875]
[null,null,"Broadlea BSP","Substation Rating","MVA","Non-Coincident",241.39999389648437]
[null,null,null,null,null,"Coincident",200]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",43.604999542236328]
[null,null,null,null,null,"Coincident",21.665000915527344]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",44.476016998291016]
[null,null,null,null,null,"Coincident",22.063041687011719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",46.979587554931641]
[null,null,null,null,null,"Coincident",23.831501007080078]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",47.918014526367188]
[null,null,null,null,null,"Coincident",24.269346237182617]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",43.604999542236328]
[null,null,null,null,null,"Coincident",21.665000915527344]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",44.476016998291016]
[null,null,null,null,null,"Coincident",22.063041687011719]
[null,null,"Bundaberg BSP","Substation Rating","MVA","Non-Coincident",180]
[null,null,null,null,null,"Coincident",180]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",123.15200042724609]
[null,null,null,null,null,"Coincident",123.15200042724609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",125.94570159912109]
[null,null,null,null,null,"Coincident",125.94570159912109]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-2.3499999046325684]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",122.55225372314453]
[null,null,null,null,null,"Coincident",122.55225372314453]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",125.33234405517578]
[null,null,null,null,null,"Coincident",125.33234405517578]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",113.85402679443359]
[null,null,null,null,null,"Coincident",113.85402679443359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",116.43679809570312]
[null,null,null,null,null,"Coincident",116.43679809570312]
[null,null,"Chinchilla BSP","Substation Rating","MVA","Non-Coincident",66]
[null,null,null,null,null,"Coincident",66]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.472000122070312]
[null,null,null,null,null,"Coincident",21.357000350952148]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.19268798828125]
[null,null,null,null,null,"Coincident",21.981170654296875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-0.20600000023841858]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.925102233886719]
[null,null,null,null,null,"Coincident",20.859382629394531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.628997802734375]
[null,null,null,null,null,"Coincident",21.469009399414063]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.076213836669922]
[null,null,null,null,null,"Coincident",19.177091598510742]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.72334098815918]
[null,null,null,null,null,"Coincident",19.737552642822266]
[null,null,"Chumvale BSP","Substation Rating","MVA","Non-Coincident",49.799999237060547]
[null,null,null,null,null,"Coincident",49.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.4000000953674316]
[null,null,null,null,null,"Coincident",6.9140000343322754]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.5614099502563477]
[null,null,null,null,null,"Coincident",7.0271568298339844]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.5042657852172852]
[null,null,null,null,null,"Coincident",7.0114178657531738]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.6679496765136719]
[null,null,null,null,null,"Coincident",7.1261692047119141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.0551600456237793]
[null,null,null,null,null,"Coincident",6.5918078422546387]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2090482711791992]
[null,null,null,null,null,"Coincident",6.6996912956237793]
[null,null,"Clermont BSP","Substation Rating","MVA","Non-Coincident",80.900001525878906]
[null,null,null,null,null,"Coincident",80.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.455999374389648]
[null,null,null,null,null,"Coincident",15.300000190734863]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.781723022460938]
[null,null,null,null,null,"Coincident",15.45018482208252]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.234237670898438]
[null,null,null,null,null,"Coincident",15.911999702453613]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.572990417480469]
[null,null,null,null,null,"Coincident",16.068191528320313]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.455999374389648]
[null,null,null,null,null,"Coincident",15.300000190734863]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.781723022460938]
[null,null,null,null,null,"Coincident",15.45018482208252]
[null,null,"Columboola BSP","Substation Rating","MVA","Non-Coincident",32]
[null,null,null,null,null,"Coincident",32]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.36400032043457]
[null,null,null,null,null,"Coincident",11.73799991607666]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.600445747375488]
[null,null,null,null,null,"Coincident",11.819076538085938]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.235706329345703]
[null,null,null,null,null,"Coincident",11.62531566619873]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.469882011413574]
[null,null,null,null,null,"Coincident",11.705613136291504]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.40165901184082]
[null,null,null,null,null,"Coincident",10.892746925354004]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.621077537536621]
[null,null,null,null,null,"Coincident",10.967985153198242]
[null,null,"Daandine BSP","Substation Rating","MVA","Non-Coincident",40.5]
[null,null,null,null,null,"Coincident",32]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0539999008178711]
[null,null,null,null,null,"Coincident",0.93300002813339233]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.7817785739898682]
[null,null,null,null,null,"Coincident",2.8047306537628174]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-30.304000854492188]
[null,null,null,null,null,"Coincident",-29.104999542236328]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2593998908996582]
[null,null,null,null,null,"Coincident",1.0263000726699829]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.0599565505981445]
[null,null,null,null,null,"Coincident",3.0852038860321045]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0539999008178711]
[null,null,null,null,null,"Coincident",0.93300002813339233]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7817785739898682]
[null,null,null,null,null,"Coincident",2.8047306537628174]
[null,null,"Dalby East BSP","Substation Rating","MVA","Non-Coincident",126]
[null,null,null,null,null,"Coincident",126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.949001312255859]
[null,null,null,null,null,"Coincident",31.645000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",36.146873474121094]
[null,null,null,null,null,"Coincident",31.645002365112305]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.631572723388672]
[null,null,null,null,null,"Coincident",31.365573883056641]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.82769775390625]
[null,null,null,null,null,"Coincident",31.365575790405273]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.633068084716797]
[null,null,null,null,null,"Coincident",28.726066589355469]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",32.812686920166016]
[null,null,null,null,null,"Coincident",28.726068496704102]
[null,null,"Georgetown BSP","Substation Rating","MVA","Non-Coincident",16.700000762939453]
[null,null,null,null,null,"Coincident",16.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.1149997711181641]
[null,null,null,null,null,"Coincident",6.0890002250671387]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.8280792236328125]
[null,null,null,null,null,"Coincident",6.8744750022888184]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.3595995903015137]
[null,null,null,null,null,"Coincident",6.3325600624084473]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.1012020111083984]
[null,null,null,null,null,"Coincident",7.1494536399841309]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.1149997711181641]
[null,null,null,null,null,"Coincident",6.0890002250671387]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.8280792236328125]
[null,null,null,null,null,"Coincident",6.8744750022888184]
[null,null,"Gladstone North BSP","Substation Rating","MVA","Non-Coincident",160]
[null,null,null,null,null,"Coincident",160]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",56.7239990234375]
[null,null,null,null,null,"Coincident",50.342998504638672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",56.742504119873047]
[null,null,null,null,null,"Coincident",50.40478515625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",56.869213104248047]
[null,null,null,null,null,"Coincident",50.471878051757813]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",56.887767791748047]
[null,null,null,null,null,"Coincident",50.533821105957031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",53.659770965576172]
[null,null,null,null,null,"Coincident",47.623470306396484]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",53.677276611328125]
[null,null,null,null,null,"Coincident",47.681919097900391]
[null,null,"Granite Creek BSP","Substation Rating","MVA","Non-Coincident",32]
[null,null,null,null,null,"Coincident",32]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.5399999618530273]
[null,null,null,null,null,"Coincident",4.564000129699707]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.0571608543395996]
[null,null,null,null,null,"Coincident",5.2952170372009277]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.6991090774536133]
[null,null,null,null,null,"Coincident",4.6950783729553223]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.2311224937438965]
[null,null,null,null,null,"Coincident",5.4472956657409668]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.2763514518737793]
[null,null,null,null,null,"Coincident",4.346799373626709]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.7689003944396973]
[null,null,null,null,null,"Coincident",5.043217658996582]
[null,null,"Isis BSP","Substation Rating","MVA","Non-Coincident",134]
[null,null,null,null,null,"Coincident",134]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",46.328998565673828]
[null,null,null,null,null,"Coincident",31.013999938964844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",47.018043518066406]
[null,null,null,null,null,"Coincident",31.148174285888672]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-24"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-17.299999237060547]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",50.961898803710937]
[null,null,null,null,null,"Coincident",34.115402221679688]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",51.7198486328125]
[null,null,null,null,null,"Coincident",34.262992858886719]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",48.006111145019531]
[null,null,null,null,null,"Coincident",32.136707305908203]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",48.720100402832031]
[null,null,null,null,null,"Coincident",32.275737762451172]
[null,null,"Kilkivan BSP","Substation Rating","MVA","Non-Coincident",34]
[null,null,null,null,null,"Coincident",34]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.87600040435791]
[null,null,null,null,null,"Coincident",13.421999931335449]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.633771896362305]
[null,null,null,null,null,"Coincident",13.84520435333252]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.955232620239258]
[null,null,null,null,null,"Coincident",13.498640060424805]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.717330932617188]
[null,null,null,null,null,"Coincident",13.924260139465332]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.850564002990723]
[null,null,null,null,null,"Coincident",12.43011474609375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.552336692810059]
[null,null,null,null,null,"Coincident",12.822044372558594]
[null,null,"Lakeland BSP","Substation Rating","MVA","Non-Coincident",49.799999237060547]
[null,null,null,null,null,"Coincident",49.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.7750000953674316]
[null,null,null,null,null,"Coincident",5.6409997940063477]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.7765083312988281]
[null,null,null,null,null,"Coincident",5.6472678184509277]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.2369422912597656]
[null,null,null,null,null,"Coincident",6.0922236442565918]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.2385711669921875]
[null,null,null,null,null,"Coincident",6.0989928245544434]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.8870930671691895]
[null,null,null,null,null,"Coincident",5.7504916191101074]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.8886303901672363]
[null,null,null,null,null,"Coincident",5.7568812370300293]
[null,null,"Louisa Creek BSP","Substation Rating","MVA","Non-Coincident",160]
[null,null,null,null,null,"Coincident",160]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",39.965000152587891]
[null,null,null,null,null,"Coincident",20.295000076293945]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",41.229343414306641]
[null,null,null,null,null,"Coincident",21.105314254760742]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",43.961502075195313]
[null,null,null,null,null,"Coincident",22.324501037597656]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",45.352279663085937]
[null,null,null,null,null,"Coincident",23.215847015380859]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",39.965000152587891]
[null,null,null,null,null,"Coincident",20.295000076293945]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",41.229343414306641]
[null,null,null,null,null,"Coincident",21.105314254760742]
[null,null,"Maryborough BSP","Substation Rating","MVA","Non-Coincident",270]
[null,null,null,null,null,"Coincident",270]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",121.85700225830078]
[null,null,null,null,null,"Coincident",120.72299957275391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",124.25587463378906]
[null,null,null,null,null,"Coincident",123.07382202148437]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-2.255000114440918]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",126.29747009277344]
[null,null,null,null,null,"Coincident",125.12214660644531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",128.78376770019531]
[null,null,null,null,null,"Coincident",127.55863189697266]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",116.86573791503906]
[null,null,null,null,null,"Coincident",115.77818298339844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",119.16635131835937]
[null,null,null,null,null,"Coincident",118.03271484375]
[null,null,"Millchester BSP","Substation Rating","MVA","Non-Coincident",68]
[null,null,null,null,null,"Coincident",68]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.999000549316406]
[null,null,null,null,null,"Coincident",22.242000579833984]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.362133026123047]
[null,null,null,null,null,"Coincident",22.50813102722168]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",30.798900604248047]
[null,null,null,null,null,"Coincident",24.466201782226563]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.198347091674805]
[null,null,null,null,null,"Coincident",24.758945465087891]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.47930908203125]
[null,null,null,null,null,"Coincident",23.417936325073242]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.861640930175781]
[null,null,null,null,null,"Coincident",23.698137283325195]
[null,null,"Oakey BSP","Substation Rating","MVA","Non-Coincident",126]
[null,null,null,null,null,"Coincident",126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.465000152587891]
[null,null,null,null,null,"Coincident",19.799999237060547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.196983337402344]
[null,null,null,null,null,"Coincident",21.332315444946289]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.271997451782227]
[null,null,null,null,null,"Coincident",21.205007553100586]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",30.197841644287109]
[null,null,null,null,null,"Coincident",22.846057891845703]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.240907669067383]
[null,null,null,null,null,"Coincident",19.625759124755859]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.948848724365234]
[null,null,null,null,null,"Coincident",21.144590377807617]
[null,null,"Rolleston BSP","Substation Rating","MVA","Non-Coincident",75]
[null,null,null,null,null,"Coincident",75]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.66200065612793]
[null,null,null,null,null,"Coincident",13.373000144958496]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.16431999206543]
[null,null,null,null,null,"Coincident",13.384719848632813]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.528202056884766]
[null,null,null,null,null,"Coincident",14.710300445556641]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.080753326416016]
[null,null,null,null,null,"Coincident",14.72319221496582]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.66200065612793]
[null,null,null,null,null,"Coincident",13.373000144958496]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.16431999206543]
[null,null,null,null,null,"Coincident",13.384719848632813]
[null,null,"Roma 33kV BSP","Substation Rating","MVA","Non-Coincident",80]
[null,null,null,null,null,"Coincident",80]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.006000518798828]
[null,null,null,null,null,"Coincident",23.461000442504883]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.700897216796875]
[null,null,null,null,null,"Coincident",23.620807647705078]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.493618011474609]
[null,null,null,null,null,"Coincident",23.918489456176758]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.202064514160156]
[null,null,null,null,null,"Coincident",24.081413269042969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.356103897094727]
[null,null,null,null,null,"Coincident",21.913043975830078]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.005151748657227]
[null,null,null,null,null,"Coincident",22.062305450439453]
[null,null,"Roma 66kV BSP","Substation Rating","MVA","Non-Coincident",80]
[null,null,null,null,null,"Coincident",80]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.257999420166016]
[null,null,null,null,null,"Coincident",28.933000564575195]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.162410736083984]
[null,null,null,null,null,"Coincident",30.089519500732422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.788007736206055]
[null,null,null,null,null,"Coincident",24.92375373840332]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.567094802856445]
[null,null,null,null,null,"Coincident",25.920015335083008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.32414436340332]
[null,null,null,null,null,"Coincident",22.71385383605957]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.034151077270508]
[null,null,null,null,null,"Coincident",23.62177848815918]
[null,null,"South Toowoomba BSP","Substation Rating","MVA","Non-Coincident",120]
[null,null,null,null,null,"Coincident",120]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",68.936996459960938]
[null,null,null,null,null,"Coincident",47.583999633789063]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",71.740982055664063]
[null,null,null,null,null,"Coincident",49.449985504150391]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",75.830696105957031]
[null,null,null,null,null,"Coincident",52.342399597167969]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",78.915084838867188]
[null,null,null,null,null,"Coincident",54.394985198974609]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",68.936996459960938]
[null,null,null,null,null,"Coincident",47.583999633789063]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",71.740982055664063]
[null,null,null,null,null,"Coincident",49.449985504150391]
[null,null,"Stanthorpe BSP","Substation Rating","MVA","Non-Coincident",80.400001525878906]
[null,null,null,null,null,"Coincident",71.300003051757813]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.645000457763672]
[null,null,null,null,null,"Coincident",13.748000144958496]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.645000457763672]
[null,null,null,null,null,"Coincident",13.784539222717285]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.805031776428223]
[null,null,null,null,null,"Coincident",14.084413528442383]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.805031776428223]
[null,null,null,null,null,"Coincident",14.121846199035645]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.18715763092041]
[null,null,null,null,null,"Coincident",13.362093925476074]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.18715763092041]
[null,null,null,null,null,"Coincident",13.397607803344727]
[null,null,"Torrington BSP","Substation Rating","MVA","Non-Coincident",212]
[null,null,null,null,null,"Coincident",212]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",90.003997802734375]
[null,null,null,null,null,"Coincident",78.788002014160156]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",93.737052917480469]
[null,null,null,null,null,"Coincident",80.663909912109375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",96.52569580078125]
[null,null,null,null,null,"Coincident",84.496986389160156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",100.52924346923828]
[null,null,null,null,null,"Coincident",86.508819580078125]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",85.980819702148438]
[null,null,null,null,null,"Coincident",75.26617431640625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",89.547004699707031]
[null,null,null,null,null,"Coincident",77.0582275390625]
[null,null,"Waggamba BSP","Substation Rating","MVA","Non-Coincident",71.300003051757813]
[null,null,null,null,null,"Coincident",71.300003051757813]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.350000381469727]
[null,null,null,null,null,"Coincident",20.332000732421875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.432876586914063]
[null,null,null,null,null,"Coincident",20.416446685791016]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.173896789550781]
[null,null,null,null,null,"Coincident",21.116611480712891]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.259969711303711]
[null,null,null,null,null,"Coincident",21.204317092895508]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.453086853027344]
[null,null,null,null,null,"Coincident",19.477853775024414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.532482147216797]
[null,null,null,null,null,"Coincident",19.558752059936523]
[null,null,"Warwick BSP","Substation Rating","MVA","Non-Coincident",100]
[null,null,null,null,null,"Coincident",100]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.832000732421875]
[null,null,null,null,null,"Coincident",30.319000244140625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.840465545654297]
[null,null,null,null,null,"Coincident",30.355199813842773]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",34.337387084960937]
[null,null,null,null,null,"Coincident",29.888471603393555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",34.345733642578125]
[null,null,null,null,null,"Coincident",29.924156188964844]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",31.73682975769043]
[null,null,null,null,null,"Coincident",27.624855041503906]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",31.744543075561523]
[null,null,null,null,null,"Coincident",27.6578369140625]
[null,null,"Yarranlea BSP","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.610000610351562]
[null,null,null,null,null,"Coincident",13.436000823974609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.279008865356445]
[null,null,null,null,null,"Coincident",14.622157096862793]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.619718551635742]
[null,null,null,null,null,"Coincident",14.127820014953613]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.374664306640625]
[null,null,null,null,null,"Coincident",15.375051498413086]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.209453582763672]
[null,null,null,null,null,"Coincident",12.476401329040527]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.759262084960937]
[null,null,null,null,null,"Coincident",13.577842712402344]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[]
[]
[]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND",{"$f":"CRY","v":"2017-18"}]
[null,"ZONE SUBSTATION","(1) Private Substation","Substation Rating","MVA","Non-Coincident",9]
[null,null,null,null,null,"Coincident",9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.8769998550415039]
[null,null,null,null,null,"Coincident",0.37000000476837158]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8795161247253418]
[null,null,null,null,null,"Coincident",0.57565701007843018]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-24"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","04:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9357700347900391]
[null,null,null,null,null,"Coincident",0.37369999289512634]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9383111000061035]
[null,null,null,null,null,"Coincident",0.58141356706619263]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.924015998840332]
[null,null,null,null,null,"Coincident",0.37296000123023987]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.9265522956848145]
[null,null,null,null,null,"Coincident",0.58026230335235596]
[null,null,"(10) Private Substation","Substation Rating","MVA","Non-Coincident",18.700000762939453]
[null,null,null,null,null,"Coincident",18.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.315999984741211]
[null,null,null,null,null,"Coincident",10.685000419616699]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.947662353515625]
[null,null,null,null,null,"Coincident",12.78474235534668]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.469160079956055]
[null,null,null,null,null,"Coincident",10.791850090026855]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.137138366699219]
[null,null,null,null,null,"Coincident",12.912590026855469]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.438528060913086]
[null,null,null,null,null,"Coincident",10.770480155944824]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.0992431640625]
[null,null,null,null,null,"Coincident",12.887020111083984]
[null,null,"(102) Private Substation","Substation Rating","MVA","Non-Coincident",1.5]
[null,null,null,null,null,"Coincident",1.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.95399999618530273]
[null,null,null,null,null,"Coincident",0.58499997854232788]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1460108757019043]
[null,null,null,null,null,"Coincident",0.5960041880607605]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.96353995800018311]
[null,null,null,null,null,"Coincident",0.59084999561309814]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1574709415435791]
[null,null,null,null,null,"Coincident",0.60196423530578613]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.96163201332092285]
[null,null,null,null,null,"Coincident",0.589680016040802]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.1551790237426758]
[null,null,null,null,null,"Coincident",0.6007722020149231]
[null,null,"(103) Private Substation","Substation Rating","MVA","Non-Coincident",5.5999999046325684]
[null,null,null,null,null,"Coincident",5.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8359999656677246]
[null,null,null,null,null,"Coincident",1.6549999713897705]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8628268241882324]
[null,null,null,null,null,"Coincident",1.7832332849502563]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8643598556518555]
[null,null,null,null,null,"Coincident",1.671549916267395]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8914551734924316]
[null,null,null,null,null,"Coincident",1.8010655641555786]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8586881160736084]
[null,null,null,null,null,"Coincident",1.668239951133728]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8857295513153076]
[null,null,null,null,null,"Coincident",1.7974991798400879]
[null,null,"(107) Private Substation","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.185999870300293]
[null,null,null,null,null,"Coincident",2.6140000820159912]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.3319535255432129]
[null,null,null,null,null,"Coincident",2.7037894725799561]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2278599739074707]
[null,null,null,null,null,"Coincident",2.6401400566101074]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3752732276916504]
[null,null,null,null,null,"Coincident",2.7308273315429687]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2194881439208984]
[null,null,null,null,null,"Coincident",2.6349120140075684]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.3666090965270996]
[null,null,null,null,null,"Coincident",2.7254197597503662]
[null,null,"(122) Private Substation","Substation Rating","MVA","Non-Coincident",51.5]
[null,null,null,null,null,"Coincident",51.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",43.145999908447266]
[null,null,null,null,null,"Coincident",21.118000030517578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",44.432357788085937]
[null,null,null,null,null,"Coincident",21.777305603027344]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",43.577461242675781]
[null,null,null,null,null,"Coincident",21.329179763793945]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",44.876682281494141]
[null,null,null,null,null,"Coincident",21.995079040527344]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",43.491168975830078]
[null,null,null,null,null,"Coincident",21.286943435668945]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",44.787818908691406]
[null,null,null,null,null,"Coincident",21.95152473449707]
[null,null,"(127) Private Substation","Substation Rating","MVA","Non-Coincident",39.099998474121094]
[null,null,null,null,null,"Coincident",39.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.895000457763672]
[null,null,null,null,null,"Coincident",4.2659997940063477]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.941156387329102]
[null,null,null,null,null,"Coincident",4.4047884941101074]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.1739501953125]
[null,null,null,null,null,"Coincident",4.308659553527832]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.230567932128906]
[null,null,null,null,null,"Coincident",4.4488363265991211]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.118160247802734]
[null,null,null,null,null,"Coincident",4.3001279830932617]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.172685623168945]
[null,null,null,null,null,"Coincident",4.4400267601013184]
[null,null,"(1294) Private Substation","Substation Rating","MVA","Non-Coincident",16.200000762939453]
[null,null,null,null,null,"Coincident",16.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.456000328063965]
[null,null,null,null,null,"Coincident",2.6960000991821289]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.910645484924316]
[null,null,null,null,null,"Coincident",2.6967597007751465]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","05:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.580560684204102]
[null,null,null,null,null,"Coincident",2.7229599952697754]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.039752006530762]
[null,null,null,null,null,"Coincident",2.7237272262573242]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.555648803710937]
[null,null,null,null,null,"Coincident",2.7175681591033936]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.013931274414063]
[null,null,null,null,null,"Coincident",2.7183337211608887]
[null,null,"(1295) Private Substation","Substation Rating","MVA","Non-Coincident",16.200000762939453]
[null,null,null,null,null,"Coincident",16.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.5999998450279236E-2]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.13875158131122589]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-09"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.63599993288517E-2]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.14013910293579102]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6288000643253326E-2]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.13986159861087799]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,"(1321) Private Substation","Substation Rating","MVA","Non-Coincident",8.5]
[null,null,null,null,null,"Coincident",8.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.265000343322754]
[null,null,null,null,null,"Coincident",1.9429999589920044]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.362428665161133]
[null,null,null,null,null,"Coincident",2.1963207721710205]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.387650489807129]
[null,null,null,null,null,"Coincident",1.9624298810958862]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.486052513122559]
[null,null,null,null,null,"Coincident",2.2182838916778564]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.363120079040527]
[null,null,null,null,null,"Coincident",1.9585440158843994]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.461328506469727]
[null,null,null,null,null,"Coincident",2.2138912677764893]
[null,null,"(1324) Private Substation","Substation Rating","MVA","Non-Coincident",8.1000003814697266]
[null,null,null,null,null,"Coincident",8.1000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.3280000686645508]
[null,null,null,null,null,"Coincident",1.1529999971389771]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.4008369445800781]
[null,null,null,null,null,"Coincident",1.3749217987060547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.3812799453735352]
[null,null,null,null,null,"Coincident",1.1645300388336182]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.4548454284667969]
[null,null,null,null,null,"Coincident",1.3886710405349731]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3706240653991699]
[null,null,null,null,null,"Coincident",1.1622240543365479]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.4440436363220215]
[null,null,null,null,null,"Coincident",1.3859212398529053]
[null,null,"(1332) Private Substation","Substation Rating","MVA","Non-Coincident",45.799999237060547]
[null,null,null,null,null,"Coincident",45.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38.251998901367188]
[null,null,null,null,null,"Coincident",25.947000503540039]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",40.151016235351563]
[null,null,null,null,null,"Coincident",27.697694778442383]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.634517669677734]
[null,null,null,null,null,"Coincident",26.206470489501953]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",40.552524566650391]
[null,null,null,null,null,"Coincident",27.974672317504883]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",38.558013916015625]
[null,null,null,null,null,"Coincident",26.154577255249023]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",40.472225189208984]
[null,null,null,null,null,"Coincident",27.919277191162109]
[null,null,"(1333) Private Substation","Substation Rating","MVA","Non-Coincident",2.7000000476837158]
[null,null,null,null,null,"Coincident",2.7000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5780000686645508]
[null,null,null,null,null,"Coincident",2.8000000864267349E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6037106513977051]
[null,null,null,null,null,"Coincident",2.8000000864267349E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","02:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.6037800312042236]
[null,null,null,null,null,"Coincident",2.8280001133680344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6297476291656494]
[null,null,null,null,null,"Coincident",2.8280001133680344E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5986242294311523]
[null,null,null,null,null,"Coincident",2.8224000707268715E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.6245403289794922]
[null,null,null,null,null,"Coincident",2.8224000707268715E-2]
[null,null,"(1334) Private Substation","Substation Rating","MVA","Non-Coincident",2.4000000953674316]
[null,null,null,null,null,"Coincident",2.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4440000057220459]
[null,null,null,null,null,"Coincident",4.1999999433755875E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5111880302429199]
[null,null,null,null,null,"Coincident",4.7885280102491379E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","06:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.468440055847168]
[null,null,null,null,null,"Coincident",4.2419999837875366E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5362999439239502]
[null,null,null,null,null,"Coincident",4.8364132642745972E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4635519981384277]
[null,null,null,null,null,"Coincident",4.2335998266935349E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5312776565551758]
[null,null,null,null,null,"Coincident",4.8268362879753113E-2]
[null,null,"(1369) Private Substation","Substation Rating","MVA","Non-Coincident",26.299999237060547]
[null,null,null,null,null,"Coincident",26.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.389999389648438]
[null,null,null,null,null,"Coincident",18.868000030517578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.731454849243164]
[null,null,null,null,null,"Coincident",19.419223785400391]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-10"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","02:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.643899917602539]
[null,null,null,null,null,"Coincident",19.056680679321289]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.98876953125]
[null,null,null,null,null,"Coincident",19.61341667175293]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.593120574951172]
[null,null,null,null,null,"Coincident",19.018943786621094]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.937307357788086]
[null,null,null,null,null,"Coincident",19.574577331542969]
[null,null,"(1372) Private Substation","Substation Rating","MVA","Non-Coincident",0.80000001192092896]
[null,null,null,null,null,"Coincident",0.80000001192092896]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.40599998831748962]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.47419509291648865]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.41005998849868774]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.47893702983856201]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.4092479944229126]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.47798866033554077]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,"(1379) Private Substation","Substation Rating","MVA","Non-Coincident",3.4000000953674316]
[null,null,null,null,null,"Coincident",3.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.190000057220459]
[null,null,null,null,null,"Coincident",0.4440000057220459]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.6365666389465332]
[null,null,null,null,null,"Coincident",0.52705979347229004]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.3494999408721924]
[null,null,null,null,null,"Coincident",0.46619999408721924]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.8183948993682861]
[null,null,null,null,null,"Coincident",0.55341273546218872]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.190000057220459]
[null,null,null,null,null,"Coincident",0.4440000057220459]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.6365666389465332]
[null,null,null,null,null,"Coincident",0.52705979347229004]
[null,null,"(140) Private Substation","Substation Rating","MVA","Non-Coincident",2]
[null,null,null,null,null,"Coincident",2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4299999475479126]
[null,null,null,null,null,"Coincident",0.21400000154972076]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8090229034423828]
[null,null,null,null,null,"Coincident",0.3298439085483551]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4442999362945557]
[null,null,null,null,null,"Coincident",0.21614000201225281]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.827113151550293]
[null,null,null,null,null,"Coincident",0.33314234018325806]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4414399862289429]
[null,null,null,null,null,"Coincident",0.21571201086044312]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8234951496124268]
[null,null,null,null,null,"Coincident",0.33248266577720642]
[null,null,"(1410) Private Substation","Substation Rating","MVA","Non-Coincident",24.200000762939453]
[null,null,null,null,null,"Coincident",24.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",54.078998565673828]
[null,null,null,null,null,"Coincident",31.797000885009766]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",64.987289428710937]
[null,null,null,null,null,"Coincident",39.81671142578125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","22:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-61.765998840332031]
[null,null,null,null,null,"Coincident",-61.062999725341797]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",54.619789123535156]
[null,null,null,null,null,"Coincident",32.114971160888672]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",65.637161254882813]
[null,null,null,null,null,"Coincident",40.214878082275391]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",54.511631011962891]
[null,null,null,null,null,"Coincident",32.051376342773437]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",65.507186889648438]
[null,null,null,null,null,"Coincident",40.135246276855469]
[null,null,"(1417) Private Substation","Substation Rating","MVA","Non-Coincident",4.4000000953674316]
[null,null,null,null,null,"Coincident",4.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.37099999189376831]
[null,null,null,null,null,"Coincident",2.6000000536441803E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.39181244373321533]
[null,null,null,null,null,"Coincident",2.6019224897027016E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.37470999360084534]
[null,null,null,null,null,"Coincident",2.6259999722242355E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.39573055505752563]
[null,null,null,null,null,"Coincident",2.6279417797923088E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.37396800518035889]
[null,null,null,null,null,"Coincident",2.6208000257611275E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.39494696259498596]
[null,null,null,null,null,"Coincident",2.6227379217743874E-2]
[null,null,"(1422) Private Substation","Substation Rating","MVA","Non-Coincident",4.1999998092651367]
[null,null,null,null,null,"Coincident",4.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.2160000801086426]
[null,null,null,null,null,"Coincident",3.8989999294281006]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.3268218040466309]
[null,null,null,null,null,"Coincident",4.0256929397583008]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2581601142883301]
[null,null,null,null,null,"Coincident",3.9379899501800537]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3700900077819824]
[null,null,null,null,null,"Coincident",4.0659499168395996]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2497282028198242]
[null,null,null,null,null,"Coincident",3.9301919937133789]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.3614363670349121]
[null,null,null,null,null,"Coincident",4.0578985214233398]
[null,null,"(1430) Private Substation","Substation Rating","MVA","Non-Coincident",15.699999809265137]
[null,null,null,null,null,"Coincident",15.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.060999870300293]
[null,null,null,null,null,"Coincident",6.8930001258850098]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.721779823303223]
[null,null,null,null,null,"Coincident",7.7470474243164062]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.171609878540039]
[null,null,null,null,null,"Coincident",6.9619302749633789]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.838997840881348]
[null,null,null,null,null,"Coincident",7.8245177268981934]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.14948844909668]
[null,null,null,null,null,"Coincident",6.9481444358825684]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.815554618835449]
[null,null,null,null,null,"Coincident",7.8090238571166992]
[null,null,"(1437) Private Substation","Substation Rating","MVA","Non-Coincident",3.4000000953674316]
[null,null,null,null,null,"Coincident",3.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2920000553131104]
[null,null,null,null,null,"Coincident",1.8999999389052391E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.337958812713623]
[null,null,null,null,null,"Coincident",0.10768936574459076]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.3249199390411377]
[null,null,null,null,null,"Coincident",1.9189998507499695E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.3713383674621582]
[null,null,null,null,null,"Coincident",0.10876625776290894]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.318336009979248]
[null,null,null,null,null,"Coincident",1.9152000546455383E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3646626472473145]
[null,null,null,null,null,"Coincident",0.10855088382959366]
[null,null,"(1444) Private Substation","Substation Rating","MVA","Non-Coincident",17.700000762939453]
[null,null,null,null,null,"Coincident",17.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.520999908447266]
[null,null,null,null,null,"Coincident",6.9739999771118164]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.347651481628418]
[null,null,null,null,null,"Coincident",6.9752874374389648]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","22:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.666210174560547]
[null,null,null,null,null,"Coincident",7.0437397956848145]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.501128196716309]
[null,null,null,null,null,"Coincident",7.0450401306152344]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.637167930603027]
[null,null,null,null,null,"Coincident",7.029792308807373]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.470433235168457]
[null,null,null,null,null,"Coincident",7.0310897827148437]
[null,null,"(1454) Private Substation","Substation Rating","MVA","Non-Coincident",4.8000001907348633]
[null,null,null,null,null,"Coincident",4.8000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.3229999542236328]
[null,null,null,null,null,"Coincident",1.3789999485015869]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.0733842849731445]
[null,null,null,null,null,"Coincident",1.3891957998275757]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","22:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.3962297439575195]
[null,null,null,null,null,"Coincident",1.3927899599075317]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.1541175842285156]
[null,null,null,null,null,"Coincident",1.4030877351760864]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3815841674804687]
[null,null,null,null,null,"Coincident",1.3900319337844849]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.1379718780517578]
[null,null,null,null,null,"Coincident",1.4003094434738159]
[null,null,"(151) Private Substation","Substation Rating","MVA","Non-Coincident",24.299999237060547]
[null,null,null,null,null,"Coincident",24.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.854000091552734]
[null,null,null,null,null,"Coincident",6.6550002098083496]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.193096160888672]
[null,null,null,null,null,"Coincident",6.7684402465820313]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-10"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.00253963470459]
[null,null,null,null,null,"Coincident",6.7215499877929687]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.345026969909668]
[null,null,null,null,null,"Coincident",6.8361244201660156]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.972832679748535]
[null,null,null,null,null,"Coincident",6.7082405090332031]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.314640998840332]
[null,null,null,null,null,"Coincident",6.8225879669189453]
[null,null,"(1544) Private Substation","Substation Rating","MVA","Non-Coincident",100]
[null,null,null,null,null,"Coincident",100]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.652000427246094]
[null,null,null,null,null,"Coincident",1.8090000152587891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.753227233886719]
[null,null,null,null,null,"Coincident",1.8095847368240356]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.758520126342773]
[null,null,null,null,null,"Coincident",1.8270900249481201]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.860759735107422]
[null,null,null,null,null,"Coincident",1.8276805877685547]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.737216949462891]
[null,null,null,null,null,"Coincident",1.8234720230102539]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.839253425598145]
[null,null,null,null,null,"Coincident",1.824061393737793]
[null,null,"(1545) Private Substation","Substation Rating","MVA","Non-Coincident",1.7000000476837158]
[null,null,null,null,null,"Coincident",1.7000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.12600000202655792]
[null,null,null,null,null,"Coincident",2.500000037252903E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.14714618027210236]
[null,null,null,null,null,"Coincident",2.5961510837078094E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.1272599995136261]
[null,null,null,null,null,"Coincident",2.525000087916851E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.14861764013767242]
[null,null,null,null,null,"Coincident",2.6221126317977905E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.12700800597667694]
[null,null,null,null,null,"Coincident",2.5200000032782555E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.14832335710525513]
[null,null,null,null,null,"Coincident",2.6169203221797943E-2]
[null,null,"(1551) Private Substation","Substation Rating","MVA","Non-Coincident",3.2000000476837158]
[null,null,null,null,null,"Coincident",3.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0840001106262207]
[null,null,null,null,null,"Coincident",0.13899999856948853]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6630847454071045]
[null,null,null,null,null,"Coincident",0.17181967198848724]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1048400402069092]
[null,null,null,null,null,"Coincident",0.14038999378681183]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6897156238555908]
[null,null,null,null,null,"Coincident",0.17353786528110504]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1006722450256348]
[null,null,null,null,null,"Coincident",0.14011199772357941]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.6843893527984619]
[null,null,null,null,null,"Coincident",0.17319422960281372]
[null,null,"(161) Private Substation","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.208999633789063]
[null,null,null,null,null,"Coincident",24.770999908447266]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.246185302734375]
[null,null,null,null,null,"Coincident",27.341117858886719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.471090316772461]
[null,null,null,null,null,"Coincident",25.018709182739258]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.518646240234375]
[null,null,null,null,null,"Coincident",27.614528656005859]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.418672561645508]
[null,null,null,null,null,"Coincident",24.969167709350586]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.464155197143555]
[null,null,null,null,null,"Coincident",27.559846878051758]
[null,null,"(164) Private Substation","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5889999866485596]
[null,null,null,null,null,"Coincident",2.4260001182556152]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.7227871417999268]
[null,null,null,null,null,"Coincident",2.5192296504974365]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.6148898601531982]
[null,null,null,null,null,"Coincident",2.4502601623535156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7500150203704834]
[null,null,null,null,null,"Coincident",2.544421911239624]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6097121238708496]
[null,null,null,null,null,"Coincident",2.4454081058502197]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7445695400238037]
[null,null,null,null,null,"Coincident",2.5393834114074707]
[null,null,"(1643) Private Substation","Substation Rating","MVA","Non-Coincident",0.5]
[null,null,null,null,null,"Coincident",0.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.5]
[null,null,null,null,null,"Coincident",0.5]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.58830267190933228]
[null,null,null,null,null,"Coincident",0.58830267190933228]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.51999998092651367]
[null,null,null,null,null,"Coincident",0.51999998092651367]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.61183476448059082]
[null,null,null,null,null,"Coincident",0.61183476448059082]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.5]
[null,null,null,null,null,"Coincident",0.5]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.58830267190933228]
[null,null,null,null,null,"Coincident",0.58830267190933228]
[null,null,"(1644) Private Substation","Substation Rating","MVA","Non-Coincident",60]
[null,null,null,null,null,"Coincident",60]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.376998901367188]
[null,null,null,null,null,"Coincident",25.243999481201172]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.6075439453125]
[null,null,null,null,null,"Coincident",25.946319580078125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",34.720767974853516]
[null,null,null,null,null,"Coincident",25.496438980102539]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",34.953620910644531]
[null,null,null,null,null,"Coincident",26.205781936645508]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.652015686035156]
[null,null,null,null,null,"Coincident",25.445951461791992]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.884403228759766]
[null,null,null,null,null,"Coincident",26.153890609741211]
[null,null,"(171) Private Substation","Substation Rating","MVA","Non-Coincident",65.599998474121094]
[null,null,null,null,null,"Coincident",65.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",48.738998413085938]
[null,null,null,null,null,"Coincident",25.552999496459961]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",54.778099060058594]
[null,null,null,null,null,"Coincident",31.297811508178711]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","03:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-40.683998107910156]
[null,null,null,null,null,"Coincident",-32.521999359130859]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",49.226387023925781]
[null,null,null,null,null,"Coincident",25.808528900146484]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",55.325878143310547]
[null,null,null,null,null,"Coincident",31.610790252685547]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",49.128910064697266]
[null,null,null,null,null,"Coincident",25.757423400878906]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",55.216323852539062]
[null,null,null,null,null,"Coincident",31.548194885253906]
[null,null,"(172) Private Substation","Substation Rating","MVA","Non-Coincident",0.89999997615814209]
[null,null,null,null,null,"Coincident",0.89999997615814209]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.68800002336502075]
[null,null,null,null,null,"Coincident",0.40000000596046448]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.7600480318069458]
[null,null,null,null,null,"Coincident",0.42281082272529602]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.69488000869750977]
[null,null,null,null,null,"Coincident",0.40400001406669617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.76764851808547974]
[null,null,null,null,null,"Coincident",0.42703893780708313]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.69350403547286987]
[null,null,null,null,null,"Coincident",0.40320000052452087]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.76612842082977295]
[null,null,null,null,null,"Coincident",0.42619332671165466]
[null,null,"(1726) Private Substation","Substation Rating","MVA","Non-Coincident",3.2000000476837158]
[null,null,null,null,null,"Coincident",3.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5080000162124634]
[null,null,null,null,null,"Coincident",0.22800000011920929]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8398315906524658]
[null,null,null,null,null,"Coincident",0.26548069715499878]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5230799913406372]
[null,null,null,null,null,"Coincident",0.23027999699115753]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8582298755645752]
[null,null,null,null,null,"Coincident",0.26813548803329468]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5200639963150024]
[null,null,null,null,null,"Coincident",0.2298240065574646]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8545502424240112]
[null,null,null,null,null,"Coincident",0.26760455965995789]
[null,null,"(1735) Private Substation","Substation Rating","MVA","Non-Coincident",4.4000000953674316]
[null,null,null,null,null,"Coincident",4.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.2140002250671387]
[null,null,null,null,null,"Coincident",3.6180000305175781]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.5215296745300293]
[null,null,null,null,null,"Coincident",3.8701162338256836]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-05"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.2661399841308594]
[null,null,null,null,null,"Coincident",3.6541800498962402]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.5767450332641602]
[null,null,null,null,null,"Coincident",3.9088172912597656]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.2557125091552734]
[null,null,null,null,null,"Coincident",3.6469440460205078]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.565701961517334]
[null,null,null,null,null,"Coincident",3.9010772705078125]
[null,null,"(1745) Private Substation","Substation Rating","MVA","Non-Coincident",12.5]
[null,null,null,null,null,"Coincident",12.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.4130001068115234]
[null,null,null,null,null,"Coincident",0.91399997472763062]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.594627857208252]
[null,null,null,null,null,"Coincident",1.1117936372756958]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.4871301651000977]
[null,null,null,null,null,"Coincident",0.95055991411209106]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.6705741882324219]
[null,null,null,null,null,"Coincident",1.1562653779983521]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4723043441772461]
[null,null,null,null,null,"Coincident",0.91399997472763062]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.6553850173950195]
[null,null,null,null,null,"Coincident",1.1117936372756958]
[null,null,"(1748) Private Substation","Substation Rating","MVA","Non-Coincident",3.2000000476837158]
[null,null,null,null,null,"Coincident",3.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.3229999542236328]
[null,null,null,null,null,"Coincident",2.9920001029968262]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9693286418914795]
[null,null,null,null,null,"Coincident",3.6061382293701172]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-16"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.3562300205230713]
[null,null,null,null,null,"Coincident",3.0219199657440186]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.0090217590332031]
[null,null,null,null,null,"Coincident",3.6421995162963867]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3495841026306152]
[null,null,null,null,null,"Coincident",3.0159361362457275]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.0010833740234375]
[null,null,null,null,null,"Coincident",3.6349873542785645]
[null,null,"(1755) Private Substation","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9919999837875366]
[null,null,null,null,null,"Coincident",0.91200000047683716]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.024268627166748]
[null,null,null,null,null,"Coincident",0.91703873872756958]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0119199752807617]
[null,null,null,null,null,"Coincident",0.92111998796463013]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0445113182067871]
[null,null,null,null,null,"Coincident",0.92620909214019775]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0079360008239746]
[null,null,null,null,null,"Coincident",0.9192960262298584]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0404627323150635]
[null,null,null,null,null,"Coincident",0.92437505722045898]
[null,null,"(1758) Private Substation","Substation Rating","MVA","Non-Coincident",7.0999999046325684]
[null,null,null,null,null,"Coincident",7.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1149997711181641]
[null,null,null,null,null,"Coincident",1.2009999752044678]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.2840795516967773]
[null,null,null,null,null,"Coincident",1.4293445348739624]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1661496162414551]
[null,null,null,null,null,"Coincident",1.2130099534988403]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.3369202613830566]
[null,null,null,null,null,"Coincident",1.4436379671096802]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1559200286865234]
[null,null,null,null,null,"Coincident",1.2106080055236816]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.3263521194458008]
[null,null,null,null,null,"Coincident",1.4407793283462524]
[null,null,"(1765) Private Substation","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.0000002160668373E-3]
[null,null,null,null,null,"Coincident",4.999999888241291E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.280109915882349E-3]
[null,null,null,null,null,"Coincident",4.999999888241291E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.2800000198185444E-3]
[null,null,null,null,null,"Coincident",5.1999995484948158E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.5713139958679676E-3]
[null,null,null,null,null,"Coincident",5.1999995484948158E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.0000002160668373E-3]
[null,null,null,null,null,"Coincident",4.999999888241291E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.280109915882349E-3]
[null,null,null,null,null,"Coincident",4.999999888241291E-3]
[null,null,"(1792) Private Substation","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4030001163482666]
[null,null,null,null,null,"Coincident",2.0889999866485596]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.7259454727172852]
[null,null,null,null,null,"Coincident",2.3539638519287109]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.427030086517334]
[null,null,null,null,null,"Coincident",2.1098899841308594]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7532048225402832]
[null,null,null,null,null,"Coincident",2.3775033950805664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4222240447998047]
[null,null,null,null,null,"Coincident",2.1057119369506836]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7477531433105469]
[null,null,null,null,null,"Coincident",2.372795581817627]
[null,null,"(1808) Private Substation","Substation Rating","MVA","Non-Coincident",7.3000001907348633]
[null,null,null,null,null,"Coincident",7.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.6279997825622559]
[null,null,null,null,null,"Coincident",0.58300000429153442]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.7795858383178711]
[null,null,null,null,null,"Coincident",0.77590787410736084]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","22:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-14.788000106811523]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.6842799186706543]
[null,null,null,null,null,"Coincident",0.58882999420166016]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.847381591796875]
[null,null,null,null,null,"Coincident",0.78366696834564209]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.6730237007141113]
[null,null,null,null,null,"Coincident",0.58766400814056396]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.8338227272033691]
[null,null,null,null,null,"Coincident",0.78211516141891479]
[null,null,"(1813) Private Substation","Substation Rating","MVA","Non-Coincident",42.900001525878906]
[null,null,null,null,null,"Coincident",42.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",30.933000564575195]
[null,null,null,null,null,"Coincident",6.8550000190734863]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.898574829101563]
[null,null,null,null,null,"Coincident",6.8853716850280762]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.170318603515625]
[null,null,null,null,null,"Coincident",7.1291999816894531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.174514770507813]
[null,null,null,null,null,"Coincident",7.1607861518859863]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.933000564575195]
[null,null,null,null,null,"Coincident",6.8550000190734863]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",31.898574829101563]
[null,null,null,null,null,"Coincident",6.8853716850280762]
[null,null,"(1814) Private Substation","Substation Rating","MVA","Non-Coincident",5.6999998092651367]
[null,null,null,null,null,"Coincident",5.6999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.2899999618530273]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.6949539184570312]
[null,null,null,null,null,"Coincident",1.1860421895980835]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-31.00200080871582]
[null,null,null,null,null,"Coincident",-15.366000175476074]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.3628997802734375]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.7819032669067383]
[null,null,null,null,null,"Coincident",1.1979025602340698]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3483200073242187]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.7645139694213867]
[null,null,null,null,null,"Coincident",1.1955305337905884]
[null,null,"(1818) Private Substation","Substation Rating","MVA","Non-Coincident",5.4000000953674316]
[null,null,null,null,null,"Coincident",5.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.380000114440918]
[null,null,null,null,null,"Coincident",3.1140000820159912]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.8103125095367432]
[null,null,null,null,null,"Coincident",3.4955315589904785]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-27"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4138000011444092]
[null,null,null,null,null,"Coincident",3.1451401710510254]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.8484156131744385]
[null,null,null,null,null,"Coincident",3.5304868221282959]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.4070401191711426]
[null,null,null,null,null,"Coincident",3.1389122009277344]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.8407950401306152]
[null,null,null,null,null,"Coincident",3.5234959125518799]
[null,null,"(1819) Private Substation","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9999999552965164E-2]
[null,null,null,null,null,"Coincident",6.0000000521540642E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4999998509883881E-2]
[null,null,null,null,null,"Coincident",1.5231546945869923E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0199999213218689E-2]
[null,null,null,null,null,"Coincident",6.0600000433623791E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5249999016523361E-2]
[null,null,null,null,null,"Coincident",1.538386195898056E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0160000771284103E-2]
[null,null,null,null,null,"Coincident",6.0479999519884586E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5199998170137405E-2]
[null,null,null,null,null,"Coincident",1.5353399328887463E-2]
[null,null,"(1822) Private Substation","Substation Rating","MVA","Non-Coincident",19.899999618530273]
[null,null,null,null,null,"Coincident",19.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.564000129699707]
[null,null,null,null,null,"Coincident",0.13600000739097595]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.595934867858887]
[null,null,null,null,null,"Coincident",0.21151833236217499]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.67963981628418]
[null,null,null,null,null,"Coincident",0.13736000657081604]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.711894035339355]
[null,null,null,null,null,"Coincident",0.21363350749015808]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.656512260437012]
[null,null,null,null,null,"Coincident",0.13708801567554474]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.688702583312988]
[null,null,null,null,null,"Coincident",0.21321047842502594]
[null,null,"(1833) Private Substation","Substation Rating","MVA","Non-Coincident",31.600000381469727]
[null,null,null,null,null,"Coincident",31.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.24899999797344208]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.99854391813278198]
[null,null,null,null,null,"Coincident",7.4810066223144531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-08"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-30.304000854492188]
[null,null,null,null,null,"Coincident",-29.104999542236328]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.25895997881889343]
[null,null,null,null,null,"Coincident",1.0399999096989632E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0384856462478638]
[null,null,null,null,null,"Coincident",7.7802467346191406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.24899999797344208]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.99854391813278198]
[null,null,null,null,null,"Coincident",7.4810066223144531]
[null,null,"(1859) Private Substation","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1349999904632568]
[null,null,null,null,null,"Coincident",0.53200000524520874]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3560194969177246]
[null,null,null,null,null,"Coincident",0.74113422632217407]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-0.20600000023841858]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1463500261306763]
[null,null,null,null,null,"Coincident",0.53732001781463623]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3695796728134155]
[null,null,null,null,null,"Coincident",0.74854558706283569]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1440800428390503]
[null,null,null,null,null,"Coincident",0.53625601530075073]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3668676614761353]
[null,null,null,null,null,"Coincident",0.74706333875656128]
[null,null,"(187) Private Substation","Substation Rating","MVA","Non-Coincident",38.5]
[null,null,null,null,null,"Coincident",38.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",26.764999389648438]
[null,null,null,null,null,"Coincident",7.9310002326965332]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.976913452148438]
[null,null,null,null,null,"Coincident",8.3998241424560547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.032649993896484]
[null,null,null,null,null,"Coincident",8.010310173034668]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",31.28668212890625]
[null,null,null,null,null,"Coincident",8.4838218688964844]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.979120254516602]
[null,null,null,null,null,"Coincident",7.994448184967041]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",31.224729537963867]
[null,null,null,null,null,"Coincident",8.4670228958129883]
[null,null,"(1893) Private Substation","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.34200000762939453]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.2653412818908691]
[null,null,null,null,null,"Coincident",0.84405922889709473]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.34200000762939453]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.2653412818908691]
[null,null,null,null,null,"Coincident",0.84405922889709473]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.34200000762939453]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.2653412818908691]
[null,null,null,null,null,"Coincident",0.84405922889709473]
[null,null,"(1894) Private Substation","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.3000001460313797E-2]
[null,null,null,null,null,"Coincident",1.0000000474974513E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.4817881435155869E-2]
[null,null,null,null,null,"Coincident",1.0000000474974513E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-17"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3000001460313797E-2]
[null,null,null,null,null,"Coincident",1.0000000474974513E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.4817881435155869E-2]
[null,null,null,null,null,"Coincident",1.0000000474974513E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.3000001460313797E-2]
[null,null,null,null,null,"Coincident",1.0000000474974513E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.4817881435155869E-2]
[null,null,null,null,null,"Coincident",1.0000000474974513E-3]
[null,null,"(2) Private Substation","Substation Rating","MVA","Non-Coincident",25.100000381469727]
[null,null,null,null,null,"Coincident",25.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.791999816894531]
[null,null,null,null,null,"Coincident",12.204999923706055]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.945886611938477]
[null,null,null,null,null,"Coincident",14.771066665649414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.939919471740723]
[null,null,null,null,null,"Coincident",12.32705020904541]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.115345001220703]
[null,null,null,null,null,"Coincident",14.918777465820313]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.910336494445801]
[null,null,null,null,null,"Coincident",12.302639961242676]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.081453323364258]
[null,null,null,null,null,"Coincident",14.889235496520996]
[null,null,"(205) Private Substation","Substation Rating","MVA","Non-Coincident",13]
[null,null,null,null,null,"Coincident",13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.954000473022461]
[null,null,null,null,null,"Coincident",13.708000183105469]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.827775955200195]
[null,null,null,null,null,"Coincident",14.452243804931641]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","03:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.113540649414063]
[null,null,null,null,null,"Coincident",13.845080375671387]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.996053695678711]
[null,null,null,null,null,"Coincident",14.596766471862793]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.081632614135742]
[null,null,null,null,null,"Coincident",13.81766414642334]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.962398529052734]
[null,null,null,null,null,"Coincident",14.567861557006836]
[null,null,"(248) Private Substation","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5880000591278076]
[null,null,null,null,null,"Coincident",7.0000000298023224E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.6457120180130005]
[null,null,null,null,null,"Coincident",0.72439008951187134]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","04:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6038800477981567]
[null,null,null,null,null,"Coincident",7.0699997246265411E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6621690988540649]
[null,null,null,null,null,"Coincident",0.73163396120071411]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6007040739059448]
[null,null,null,null,null,"Coincident",7.0560000836849213E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6588777303695679]
[null,null,null,null,null,"Coincident",0.73018521070480347]
[null,null,"(251) Private Substation","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.497999906539917]
[null,null,null,null,null,"Coincident",0.3059999942779541]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8586890697479248]
[null,null,null,null,null,"Coincident",0.32724913954734802]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5229799747467041]
[null,null,null,null,null,"Coincident",0.30905997753143311]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8872759342193604]
[null,null,null,null,null,"Coincident",0.33052161335945129]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5179839134216309]
[null,null,null,null,null,"Coincident",0.30844798684120178]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8815586566925049]
[null,null,null,null,null,"Coincident",0.32986712455749512]
[null,null,"(257) Private Substation","Substation Rating","MVA","Non-Coincident",15.600000381469727]
[null,null,null,null,null,"Coincident",15.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4079999923706055]
[null,null,null,null,null,"Coincident",0.12099999934434891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.037822961807251]
[null,null,null,null,null,"Coincident",0.190394327044487]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4320800304412842]
[null,null,null,null,null,"Coincident",0.12220999598503113]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.0682010650634766]
[null,null,null,null,null,"Coincident",0.19229826331138611]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4272639751434326]
[null,null,null,null,null,"Coincident",0.12196800112724304]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.0621256828308105]
[null,null,null,null,null,"Coincident",0.19191747903823853]
[null,null,"(292) Private Substation","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.2529997825622559]
[null,null,null,null,null,"Coincident",5.7150001525878906]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.630704402923584]
[null,null,null,null,null,"Coincident",6.0571675300598145]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.2529997825622559]
[null,null,null,null,null,"Coincident",5.7721500396728516]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.630704402923584]
[null,null,null,null,null,"Coincident",6.117739200592041]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.2529997825622559]
[null,null,null,null,null,"Coincident",5.7607202529907227]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.630704402923584]
[null,null,null,null,null,"Coincident",6.1056251525878906]
[null,null,"(312) Private Substation","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.61100000143051147]
[null,null,null,null,null,"Coincident",6.7000001668930054E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.73973643779754639]
[null,null,null,null,null,"Coincident",9.8351411521434784E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.61711001396179199]
[null,null,null,null,null,"Coincident",6.7670002579689026E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.74713379144668579]
[null,null,null,null,null,"Coincident",9.9334925413131714E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.61588799953460693]
[null,null,null,null,null,"Coincident",6.7536003887653351E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.74565434455871582]
[null,null,null,null,null,"Coincident",9.9138222634792328E-2]
[null,null,"(321) Private Substation","Substation Rating","MVA","Non-Coincident",24.700000762939453]
[null,null,null,null,null,"Coincident",24.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.892000198364258]
[null,null,null,null,null,"Coincident",0.85600000619888306]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.025725364685059]
[null,null,null,null,null,"Coincident",1.0857992172241211]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-05"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","02:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.000920295715332]
[null,null,null,null,null,"Coincident",0.86456000804901123]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.135982513427734]
[null,null,null,null,null,"Coincident",1.0966571569442749]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.97913646697998]
[null,null,null,null,null,"Coincident",0.86284804344177246]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.113931655883789]
[null,null,null,null,null,"Coincident",1.0944856405258179]
[null,null,"(326) Private Substation","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6069999933242798]
[null,null,null,null,null,"Coincident",4.6999998390674591E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.6355013847351074]
[null,null,null,null,null,"Coincident",0.52311569452285767]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6230700016021729]
[null,null,null,null,null,"Coincident",4.7469999641180038E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6518564224243164]
[null,null,null,null,null,"Coincident",0.52834683656692505]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6198559999465942]
[null,null,null,null,null,"Coincident",4.7375999391078949E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6485854387283325]
[null,null,null,null,null,"Coincident",0.52730065584182739]
[null,null,"(333) Private Substation","Substation Rating","MVA","Non-Coincident",69.300003051757812]
[null,null,null,null,null,"Coincident",69.300003051757812]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.322999954223633]
[null,null,null,null,null,"Coincident",13.489999771118164]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.377029418945313]
[null,null,null,null,null,"Coincident",13.676351547241211]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.516229629516602]
[null,null,null,null,null,"Coincident",13.624899864196777]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.570798873901367]
[null,null,null,null,null,"Coincident",13.813115119934082]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.477584838867188]
[null,null,null,null,null,"Coincident",13.597920417785645]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.532045364379883]
[null,null,null,null,null,"Coincident",13.785762786865234]
[null,null,"(334) Private Substation","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.9399995803833008]
[null,null,null,null,null,"Coincident",1.7999999523162842]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.302329063415527]
[null,null,null,null,null,"Coincident",1.9697715044021606]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-17"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.0293998718261719]
[null,null,null,null,null,"Coincident",1.8179999589920044]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.405352592468262]
[null,null,null,null,null,"Coincident",1.9894691705703735]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.0115194320678711]
[null,null,null,null,null,"Coincident",1.8143999576568604]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.384747505187988]
[null,null,null,null,null,"Coincident",1.9855296611785889]
[null,null,"(341) Private Substation","Substation Rating","MVA","Non-Coincident",29.399999618530273]
[null,null,null,null,null,"Coincident",29.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.2740000486373901]
[null,null,null,null,null,"Coincident",0.97399997711181641]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2815604209899902]
[null,null,null,null,null,"Coincident",1.0458666086196899]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2867400646209717]
[null,null,null,null,null,"Coincident",0.98373997211456299]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.294376015663147]
[null,null,null,null,null,"Coincident",1.0563253164291382]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2841920852661133]
[null,null,null,null,null,"Coincident",0.98179197311401367]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2918128967285156]
[null,null,null,null,null,"Coincident",1.0542335510253906]
[null,null,"(346) Private Substation","Substation Rating","MVA","Non-Coincident",33.700000762939453]
[null,null,null,null,null,"Coincident",33.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",37.528999328613281]
[null,null,null,null,null,"Coincident",17.066999435424805]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.598636627197266]
[null,null,null,null,null,"Coincident",20.782073974609375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-17.062999725341797]
[null,null,null,null,null,"Coincident",-14.845999717712402]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",37.904289245605469]
[null,null,null,null,null,"Coincident",17.237668991088867]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",46.054622650146484]
[null,null,null,null,null,"Coincident",20.989894866943359]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",37.829231262207031]
[null,null,null,null,null,"Coincident",17.203535079956055]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",45.963424682617188]
[null,null,null,null,null,"Coincident",20.948331832885742]
[null,null,"(349) Private Substation","Substation Rating","MVA","Non-Coincident",8.5]
[null,null,null,null,null,"Coincident",8.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.1160001754760742]
[null,null,null,null,null,"Coincident",2.6679999828338623]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.5023889541625977]
[null,null,null,null,null,"Coincident",2.669353723526001]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","05:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.1971597671508789]
[null,null,null,null,null,"Coincident",2.6946799755096436]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.5874128341674805]
[null,null,null,null,null,"Coincident",2.696047306060791]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.1809282302856445]
[null,null,null,null,null,"Coincident",2.6893439292907715]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.5704078674316406]
[null,null,null,null,null,"Coincident",2.6907086372375488]
[null,null,"(360) Private Substation","Substation Rating","MVA","Non-Coincident",56]
[null,null,null,null,null,"Coincident",56]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.310999870300293]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.8645858764648437]
[null,null,null,null,null,"Coincident",1.5980312824249268]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-16"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-46.995998382568359]
[null,null,null,null,null,"Coincident",-28.878999710083008]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.3841099739074707]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.9532318115234375]
[null,null,null,null,null,"Coincident",1.6140115261077881]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3694877624511719]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.9355030059814453]
[null,null,null,null,null,"Coincident",1.6108155250549316]
[null,null,"(368) Private Substation","Substation Rating","MVA","Non-Coincident",80]
[null,null,null,null,null,"Coincident",80]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.267999649047852]
[null,null,null,null,null,"Coincident",5.9140000343322754]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.748605728149414]
[null,null,null,null,null,"Coincident",6.3268394470214844]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","06:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.430679321289063]
[null,null,null,null,null,"Coincident",5.973139762878418]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.936092376708984]
[null,null,null,null,null,"Coincident",6.3901076316833496]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.398143768310547]
[null,null,null,null,null,"Coincident",5.9613122940063477]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.898595809936523]
[null,null,null,null,null,"Coincident",6.3774542808532715]
[null,null,"(376) Private Substation","Substation Rating","MVA","Non-Coincident",22.299999237060547]
[null,null,null,null,null,"Coincident",22.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.580999374389648]
[null,null,null,null,null,"Coincident",3.2850000858306885]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.799240112304687]
[null,null,null,null,null,"Coincident",3.6478242874145508]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-27"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.746809005737305]
[null,null,null,null,null,"Coincident",3.3178501129150391]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.987232208251953]
[null,null,null,null,null,"Coincident",3.6843025684356689]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.713647842407227]
[null,null,null,null,null,"Coincident",3.3112802505493164]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.949634552001953]
[null,null,null,null,null,"Coincident",3.6770069599151611]
[null,null,"(40) Private Substation","Substation Rating","MVA","Non-Coincident",29.700000762939453]
[null,null,null,null,null,"Coincident",29.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.696000099182129]
[null,null,null,null,null,"Coincident",6.3020000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.06867790222168]
[null,null,null,null,null,"Coincident",6.406247615814209]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-17"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","02:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.812959671020508]
[null,null,null,null,null,"Coincident",6.3650197982788086]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.189364433288574]
[null,null,null,null,null,"Coincident",6.4703102111816406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.789567947387695]
[null,null,null,null,null,"Coincident",6.3524160385131836]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.165227890014648]
[null,null,null,null,null,"Coincident",6.4574975967407227]
[null,null,"(400) Private Substation","Substation Rating","MVA","Non-Coincident",49.200000762939453]
[null,null,null,null,null,"Coincident",49.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",32.143001556396484]
[null,null,null,null,null,"Coincident",11.137999534606934]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",32.993495941162109]
[null,null,null,null,null,"Coincident",13.136978149414063]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.464431762695313]
[null,null,null,null,null,"Coincident",11.24937915802002]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.323429107666016]
[null,null,null,null,null,"Coincident",13.26834774017334]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.400146484375]
[null,null,null,null,null,"Coincident",11.227104187011719]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",33.2574462890625]
[null,null,null,null,null,"Coincident",13.242074012756348]
[null,null,"(402) Private Substation","Substation Rating","MVA","Non-Coincident",11.699999809265137]
[null,null,null,null,null,"Coincident",11.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3299999237060547]
[null,null,null,null,null,"Coincident",0.25200000405311584]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.7192835807800293]
[null,null,null,null,null,"Coincident",0.40183702111244202]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3532998561859131]
[null,null,null,null,null,"Coincident",0.2545199990272522]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.746476411819458]
[null,null,null,null,null,"Coincident",0.40585538744926453]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.348639965057373]
[null,null,null,null,null,"Coincident",0.25401601195335388]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7410378456115723]
[null,null,null,null,null,"Coincident",0.40505173802375793]
[null,null,"(413) Private Substation","Substation Rating","MVA","Non-Coincident",6.4000000953674316]
[null,null,null,null,null,"Coincident",6.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.4330000877380371]
[null,null,null,null,null,"Coincident",3.0559999942779541]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1835832595825195]
[null,null,null,null,null,"Coincident",3.7342269420623779]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","05:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4673299789428711]
[null,null,null,null,null,"Coincident",3.0865600109100342]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.2254190444946289]
[null,null,null,null,null,"Coincident",3.7715692520141602]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.4604642391204834]
[null,null,null,null,null,"Coincident",3.0804481506347656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.2170519828796387]
[null,null,null,null,null,"Coincident",3.7641007900238037]
[null,null,"(414) Private Substation","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5320000648498535]
[null,null,null,null,null,"Coincident",1.7280000448226929]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9501221179962158]
[null,null,null,null,null,"Coincident",2.0142514705657959]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5573201179504395]
[null,null,null,null,null,"Coincident",1.7452800273895264]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.9796233177185059]
[null,null,null,null,null,"Coincident",2.0343940258026123]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5522561073303223]
[null,null,null,null,null,"Coincident",1.7418240308761597]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9737231731414795]
[null,null,null,null,null,"Coincident",2.0303654670715332]
[null,null,"(424) Private Substation","Substation Rating","MVA","Non-Coincident",2.5999999046325684]
[null,null,null,null,null,"Coincident",2.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.42599999904632568]
[null,null,null,null,null,"Coincident",0.11800000071525574]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.54380142688751221]
[null,null,null,null,null,"Coincident",0.20041956007480621]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.43026000261306763]
[null,null,null,null,null,"Coincident",0.11918000131845474]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.54923945665359497]
[null,null,null,null,null,"Coincident",0.20242375135421753]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.42940801382064819]
[null,null,null,null,null,"Coincident",0.11894400417804718]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.54815185070037842]
[null,null,null,null,null,"Coincident",0.20202292501926422]
[null,null,"(426) Private Substation","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8489999771118164]
[null,null,null,null,null,"Coincident",8.5000000894069672E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9148902893066406]
[null,null,null,null,null,"Coincident",0.5140758752822876]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8674899339675903]
[null,null,null,null,null,"Coincident",8.5850000381469727E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9340391159057617]
[null,null,null,null,null,"Coincident",0.51921665668487549]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8637920618057251]
[null,null,null,null,null,"Coincident",8.5680000483989716E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9302093982696533]
[null,null,null,null,null,"Coincident",0.5181884765625]
[null,null,"(455) Private Substation","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.3920001983642578]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.6717252731323242]
[null,null,null,null,null,"Coincident",1.044030673801899E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-06"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.4659199714660645]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.7584428787231445]
[null,null,null,null,null,"Coincident",1.0544709861278534E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4511361122131348]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.7410993576049805]
[null,null,null,null,null,"Coincident",1.0523829609155655E-2]
[null,null,"(476) Private Substation","Substation Rating","MVA","Non-Coincident",6]
[null,null,null,null,null,"Coincident",6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.7960000038146973]
[null,null,null,null,null,"Coincident",1.0850000381469727]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1489570140838623]
[null,null,null,null,null,"Coincident",1.3043776750564575]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8139599561691284]
[null,null,null,null,null,"Coincident",1.0958499908447266]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.1704466342926025]
[null,null,null,null,null,"Coincident",1.3174214363098145]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8103680610656738]
[null,null,null,null,null,"Coincident",1.0936800241470337]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1661486625671387]
[null,null,null,null,null,"Coincident",1.3148126602172852]
[null,null,"(50) Private Substation","Substation Rating","MVA","Non-Coincident",14]
[null,null,null,null,null,"Coincident",14]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.7179999351501465]
[null,null,null,null,null,"Coincident",1.937999963760376]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.7185506820678711]
[null,null,null,null,null,"Coincident",1.9584095478057861]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.7551798820495605]
[null,null,null,null,null,"Coincident",1.957379937171936]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.7557361125946045]
[null,null,null,null,null,"Coincident",1.9779936075210571]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.747744083404541]
[null,null,null,null,null,"Coincident",1.9535039663314819]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.7482991218566895]
[null,null,null,null,null,"Coincident",1.9740768671035767]
[null,null,"(69) Private Substation","Substation Rating","MVA","Non-Coincident",14]
[null,null,null,null,null,"Coincident",14]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.218000411987305]
[null,null,null,null,null,"Coincident",0.6119999885559082]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.580550193786621]
[null,null,null,null,null,"Coincident",0.64354097843170166]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.32017993927002]
[null,null,null,null,null,"Coincident",0.61811995506286621]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.686355590820313]
[null,null,null,null,null,"Coincident",0.64997637271881104]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.299744606018066]
[null,null,null,null,null,"Coincident",0.61689597368240356]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.665194511413574]
[null,null,null,null,null,"Coincident",0.64868932962417603]
[null,null,"(77) Private Substation","Substation Rating","MVA","Non-Coincident",18.5]
[null,null,null,null,null,"Coincident",18.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.560000419616699]
[null,null,null,null,null,"Coincident",6.000999927520752]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.490118026733398]
[null,null,null,null,null,"Coincident",6.2189569473266602]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-05"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.695600509643555]
[null,null,null,null,null,"Coincident",6.0610098838806152]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.64501953125]
[null,null,null,null,null,"Coincident",6.2811465263366699]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.66848087310791]
[null,null,null,null,null,"Coincident",6.0490078926086426]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.614039421081543]
[null,null,null,null,null,"Coincident",6.2687087059020996]
[null,null,"(885) Private Substation","Substation Rating","MVA","Non-Coincident",37.200000762939453]
[null,null,null,null,null,"Coincident",37.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.961000442504883]
[null,null,null,null,null,"Coincident",12.678000450134277]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.151613235473633]
[null,null,null,null,null,"Coincident",14.172646522521973]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-27"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","03:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",30.260610580444336]
[null,null,null,null,null,"Coincident",12.804780006408691]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",30.453128814697266]
[null,null,null,null,null,"Coincident",14.314373016357422]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.200689315795898]
[null,null,null,null,null,"Coincident",12.779424667358398]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.392826080322266]
[null,null,null,null,null,"Coincident",14.286027908325195]
[null,null,"(899) Private Substation","Substation Rating","MVA","Non-Coincident",1.7000000476837158]
[null,null,null,null,null,"Coincident",1.7000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.30099999904632568]
[null,null,null,null,null,"Coincident",0.23899999260902405]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.32669559121131897]
[null,null,null,null,null,"Coincident",0.26024988293647766]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-24"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","10:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.32409572601318359]
[null,null,null,null,null,"Coincident",0.25733846426010132]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.35176295042037964]
[null,null,null,null,null,"Coincident",0.28021886944770813]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.30099999904632568]
[null,null,null,null,null,"Coincident",0.23899999260902405]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.32669559121131897]
[null,null,null,null,null,"Coincident",0.26024988293647766]
[null,null,"(953) Private Substation","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.3270000219345093]
[null,null,null,null,null,"Coincident",0.18899999558925629]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5818501710891724]
[null,null,null,null,null,"Coincident",0.20890668034553528]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","22:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-4.1469998359680176]
[null,null,null,null,null,"Coincident",-4.999999888241291E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3402700424194336]
[null,null,null,null,null,"Coincident",0.19088999927043915]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5976686477661133]
[null,null,null,null,null,"Coincident",0.21099574863910675]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3376160860061646]
[null,null,null,null,null,"Coincident",0.19051200151443481]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5945049524307251]
[null,null,null,null,null,"Coincident",0.21057793498039246]
[null,null,"Agnes Water","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.2369999885559082]
[null,null,null,null,null,"Coincident",4.2719998359680176]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.263249397277832]
[null,null,null,null,null,"Coincident",4.2832326889038086]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.5282816886901855]
[null,null,null,null,null,"Coincident",4.509608268737793]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.5559911727905273]
[null,null,null,null,null,"Coincident",4.5214657783508301]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1048178672790527]
[null,null,null,null,null,"Coincident",4.1641745567321777]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.1304049491882324]
[null,null,null,null,null,"Coincident",4.1751236915588379]
[null,null,"Aitkenvale","Substation Rating","MVA","Non-Coincident",61.599998474121094]
[null,null,null,null,null,"Coincident",61.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20]
[null,null,null,null,null,"Coincident",17.600000381469727]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.690336227416992]
[null,null,null,null,null,"Coincident",17.992988586425781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.339200973510742]
[null,null,null,null,null,"Coincident",17.898496627807617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.041244506835938]
[null,null,null,null,null,"Coincident",18.298151016235352]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.838399887084961]
[null,null,null,null,null,"Coincident",16.577791213989258]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.488641738891602]
[null,null,null,null,null,"Coincident",16.947956085205078]
[null,null,"Alan Sherriff","Substation Rating","MVA","Non-Coincident",70]
[null,null,null,null,null,"Coincident",70]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.781000137329102]
[null,null,null,null,null,"Coincident",25.781000137329102]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",26.811546325683594]
[null,null,null,null,null,"Coincident",26.811546325683594]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.50080680847168]
[null,null,null,null,null,"Coincident",26.50080680847168]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.560125350952148]
[null,null,null,null,null,"Coincident",27.560125350952148]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.073524475097656]
[null,null,null,null,null,"Coincident",24.073524475097656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.035818099975586]
[null,null,null,null,null,"Coincident",25.035818099975586]
[null,null,"Alfred Street","Substation Rating","MVA","Non-Coincident",90.699996948242188]
[null,null,null,null,null,"Coincident",90.699996948242188]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.945999145507813]
[null,null,null,null,null,"Coincident",19.629999160766602]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.232389450073242]
[null,null,null,null,null,"Coincident",19.676433563232422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.706569671630859]
[null,null,null,null,null,"Coincident",19.415836334228516]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.989833831787109]
[null,null,null,null,null,"Coincident",19.461763381958008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.58293342590332]
[null,null,null,null,null,"Coincident",18.41077995300293]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.851535797119141]
[null,null,null,null,null,"Coincident",18.454330444335938]
[null,null,"Allora","Substation Rating","MVA","Non-Coincident",7.3000001907348633]
[null,null,null,null,null,"Coincident",7.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.2960000038146973]
[null,null,null,null,null,"Coincident",3.7309999465942383]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.667182445526123]
[null,null,null,null,null,"Coincident",4.0564546585083008]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.7049365043640137]
[null,null,null,null,null,"Coincident",4.0861539840698242]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.1114516258239746]
[null,null,null,null,null,"Coincident",4.4425888061523437]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2932934761047363]
[null,null,null,null,null,"Coincident",3.728649377822876]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.6642417907714844]
[null,null,null,null,null,"Coincident",4.053898811340332]
[null,null,"Atherton","Substation Rating","MVA","Non-Coincident",88.099998474121094]
[null,null,null,null,null,"Coincident",88.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.062999725341797]
[null,null,null,null,null,"Coincident",23.062999725341797]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.07109260559082]
[null,null,null,null,null,"Coincident",23.07109260559082]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",-4.999999888241291E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.753725051879883]
[null,null,null,null,null,"Coincident",22.753725051879883]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.761709213256836]
[null,null,null,null,null,"Coincident",22.761709213256836]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.899009704589844]
[null,null,null,null,null,"Coincident",21.899009704589844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.906694412231445]
[null,null,null,null,null,"Coincident",21.906694412231445]
[null,null,"Awoonga","Substation Rating","MVA","Non-Coincident",24.399999618530273]
[null,null,null,null,null,"Coincident",24.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.2529997825622559]
[null,null,null,null,null,"Coincident",4.745999813079834]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.5018038749694824]
[null,null,null,null,null,"Coincident",4.8909749984741211]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-1.0299999713897705]
[null,null,null,null,null,"Coincident",-1.0180000066757202]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.9322724342346191]
[null,null,null,null,null,"Coincident",4.5361318588256836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.170074462890625]
[null,null,null,null,null,"Coincident",4.6746964454650879]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.7268671989440918]
[null,null,null,null,null,"Coincident",4.4017252922058105]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.9576230049133301]
[null,null,null,null,null,"Coincident",4.5361838340759277]
[null,null,"Ayr","Substation Rating","MVA","Non-Coincident",23.899999618530273]
[null,null,null,null,null,"Coincident",23.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.5900001525878906]
[null,null,null,null,null,"Coincident",7.4800000190734863]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.711234092712402]
[null,null,null,null,null,"Coincident",8.2990617752075195]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.54900074005127]
[null,null,null,null,null,"Coincident",8.2280006408691406]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.782358169555664]
[null,null,null,null,null,"Coincident",9.1289682388305664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.357200622558594]
[null,null,null,null,null,"Coincident",8.0784006118774414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.568133354187012]
[null,null,null,null,null,"Coincident",8.962986946105957]
[null,null,"Balberra","Substation Rating","MVA","Non-Coincident",7]
[null,null,null,null,null,"Coincident",7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4549999237060547]
[null,null,null,null,null,"Coincident",1.5019999742507935]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5753269195556641]
[null,null,null,null,null,"Coincident",1.553836464881897]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4939360618591309]
[null,null,null,null,null,"Coincident",1.5258216857910156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6161715984344482]
[null,null,null,null,null,"Coincident",1.5784802436828613]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1974213123321533]
[null,null,null,null,null,"Coincident",1.3444100618362427]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3051235675811768]
[null,null,null,null,null,"Coincident",1.3908078670501709]
[null,null,"Bambaroo","Substation Rating","MVA","Non-Coincident",2.2000000476837158]
[null,null,null,null,null,"Coincident",2.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.59700000286102295]
[null,null,null,null,null,"Coincident",0.26899999380111694]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.6641460657119751]
[null,null,null,null,null,"Coincident",0.27078035473823547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.60297000408172607]
[null,null,null,null,null,"Coincident",0.27168998122215271]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.670787513256073]
[null,null,null,null,null,"Coincident",0.27348816394805908]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.54923999309539795]
[null,null,null,null,null,"Coincident",0.24748000502586365]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.61101436614990234]
[null,null,null,null,null,"Coincident",0.24911792576313019]
[null,null,"Barcaldine","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.5840001106262207]
[null,null,null,null,null,"Coincident",6.8369998931884766]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.5842070579528809]
[null,null,null,null,null,"Coincident",6.8387794494628906]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-20.420000076293945]
[null,null,null,null,null,"Coincident",-0.5220000147819519]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3424005508422852]
[null,null,null,null,null,"Coincident",7.5206999778747559]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.3426275253295898]
[null,null,null,null,null,"Coincident",7.5226573944091797]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.5840001106262207]
[null,null,null,null,null,"Coincident",6.8369998931884766]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.5842070579528809]
[null,null,null,null,null,"Coincident",6.8387794494628906]
[null,null,"Bargara","Substation Rating","MVA","Non-Coincident",69.900001525878906]
[null,null,null,null,null,"Coincident",69.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.744999885559082]
[null,null,null,null,null,"Coincident",12.484999656677246]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.750340461730957]
[null,null,null,null,null,"Coincident",12.49750804901123]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.21019172668457]
[null,null,null,null,null,"Coincident",12.940701484680176]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.215727806091309]
[null,null,null,null,null,"Coincident",12.953666687011719]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.327728271484375]
[null,null,null,null,null,"Coincident",12.076240539550781]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.332894325256348]
[null,null,null,null,null,"Coincident",12.088339805603027]
[null,null,"Barratta","Substation Rating","MVA","Non-Coincident",4]
[null,null,null,null,null,"Coincident",4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0980000495910645]
[null,null,null,null,null,"Coincident",1.8309999704360962]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4036500453948975]
[null,null,null,null,null,"Coincident",2.0715987682342529]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3078000545501709]
[null,null,null,null,null,"Coincident",2.0141000747680664]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6440150737762451]
[null,null,null,null,null,"Coincident",2.2787587642669678]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2658400535583496]
[null,null,null,null,null,"Coincident",1.9774800539016724]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5959422588348389]
[null,null,null,null,null,"Coincident",2.2373268604278564]
[null,null,"Bedford Weir","Substation Rating","MVA","Non-Coincident",20.899999618530273]
[null,null,null,null,null,"Coincident",20.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.1520004272460937]
[null,null,null,null,null,"Coincident",7.3379998207092285]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.4965362548828125]
[null,null,null,null,null,"Coincident",7.603571891784668]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.7353515625]
[null,null,null,null,null,"Coincident",6.9629545211791992]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.0622777938842773]
[null,null,null,null,null,"Coincident",7.2149529457092285]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.216395378112793]
[null,null,null,null,null,"Coincident",6.4958176612854004]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.5213890075683594]
[null,null,null,null,null,"Coincident",6.7309098243713379]
[null,null,"Belgian Gardens","Substation Rating","MVA","Non-Coincident",73.900001525878906]
[null,null,null,null,null,"Coincident",73.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.147000312805176]
[null,null,null,null,null,"Coincident",9.2040004730224609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.250645637512207]
[null,null,null,null,null,"Coincident",9.2899808883666992]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.161700248718262]
[null,null,null,null,null,"Coincident",10.124401092529297]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.275710105895996]
[null,null,null,null,null,"Coincident",10.218978881835937]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.093221664428711]
[null,null,null,null,null,"Coincident",9.1552190780639648]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.196317672729492]
[null,null,null,null,null,"Coincident",9.2407445907592773]
[null,null,"Benarkin","Substation Rating","MVA","Non-Coincident",4.9000000953674316]
[null,null,null,null,null,"Coincident",4.9000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.3730000257492065]
[null,null,null,null,null,"Coincident",3.7000000476837158E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5722229480743408]
[null,null,null,null,null,"Coincident",4.4102154672145844E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-05"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3867299556732178]
[null,null,null,null,null,"Coincident",3.7370000034570694E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5879451036453247]
[null,null,null,null,null,"Coincident",4.4543176889419556E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3839840888977051]
[null,null,null,null,null,"Coincident",3.7296000868082047E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5848007202148437]
[null,null,null,null,null,"Coincident",4.4454973191022873E-2]
[null,null,"Berserker","Substation Rating","MVA","Non-Coincident",78.5]
[null,null,null,null,null,"Coincident",78.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.906000137329102]
[null,null,null,null,null,"Coincident",20.420000076293945]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.17793083190918]
[null,null,null,null,null,"Coincident",20.540430068969727]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.906000137329102]
[null,null,null,null,null,"Coincident",20.420000076293945]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.17793083190918]
[null,null,null,null,null,"Coincident",20.540430068969727]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.531641006469727]
[null,null,null,null,null,"Coincident",19.194799423217773]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.787254333496094]
[null,null,null,null,null,"Coincident",19.308004379272461]
[null,null,"Biloela","Substation Rating","MVA","Non-Coincident",47.299999237060547]
[null,null,null,null,null,"Coincident",47.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.785999298095703]
[null,null,null,null,null,"Coincident",15.461999893188477]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.65104866027832]
[null,null,null,null,null,"Coincident",16.168132781982422]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.477472305297852]
[null,null,null,null,null,"Coincident",15.17780876159668]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.326622009277344]
[null,null,null,null,null,"Coincident",15.870963096618652]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.054859161376953]
[null,null,null,null,null,"Coincident",13.867403984069824]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.830696105957031]
[null,null,null,null,null,"Coincident",14.500713348388672]
[null,null,"Bingegang","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8270000219345093]
[null,null,null,null,null,"Coincident",1.6139999628067017]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8717846870422363]
[null,null,null,null,null,"Coincident",1.641279935836792]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0097000598907471]
[null,null,null,null,null,"Coincident",1.7754000425338745]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0589632987976074]
[null,null,null,null,null,"Coincident",1.8054080009460449]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9731601476669312]
[null,null,null,null,null,"Coincident",1.7431200742721558]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0215275287628174]
[null,null,null,null,null,"Coincident",1.7725824117660522]
[null,null,"Black River","Substation Rating","MVA","Non-Coincident",56]
[null,null,null,null,null,"Coincident",56]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.593000411987305]
[null,null,null,null,null,"Coincident",16.451000213623047]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.69158935546875]
[null,null,null,null,null,"Coincident",16.510463714599609]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.228034973144531]
[null,null,null,null,null,"Coincident",17.823835372924805]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.33485221862793]
[null,null,null,null,null,"Coincident",17.888261795043945]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.194673538208008]
[null,null,null,null,null,"Coincident",16.116550445556641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.291259765625]
[null,null,null,null,null,"Coincident",16.174806594848633]
[null,null,"Blackall","Substation Rating","MVA","Non-Coincident",13.899999618530273]
[null,null,null,null,null,"Coincident",13.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.4010000228881836]
[null,null,null,null,null,"Coincident",4.0910000801086426]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.4013071060180664]
[null,null,null,null,null,"Coincident",4.0910491943359375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.1822261810302734]
[null,null,null,null,null,"Coincident",3.887636661529541]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.1825180053710938]
[null,null,null,null,null,"Coincident",3.8876831531524658]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.8670265674591064]
[null,null,null,null,null,"Coincident",3.5946390628814697]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.8672964572906494]
[null,null,null,null,null,"Coincident",3.5946822166442871]
[null,null,"Blackwater","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.800999641418457]
[null,null,null,null,null,"Coincident",8.5719995498657227]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.064745903015137]
[null,null,null,null,null,"Coincident",8.7571029663085938]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.781100273132324]
[null,null,null,null,null,"Coincident",9.4292001724243164]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.071220397949219]
[null,null,null,null,null,"Coincident",9.6328134536743164]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9970197677612305]
[null,null,null,null,null,"Coincident",8.7434396743774414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.266040802001953]
[null,null,null,null,null,"Coincident",8.9322452545166016]
[null,null,"Blue Valley","Substation Rating","MVA","Non-Coincident",15.199999809265137]
[null,null,null,null,null,"Coincident",15]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.7750000953674316]
[null,null,null,null,null,"Coincident",3.0999999493360519E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8933348655700684]
[null,null,null,null,null,"Coincident",0.12975746393203735]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-05"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8027501106262207]
[null,null,null,null,null,"Coincident",3.1309999525547028E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.9222681522369385]
[null,null,null,null,null,"Coincident",0.13105504214763641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.7972002029418945]
[null,null,null,null,null,"Coincident",3.1247999519109726E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9164814949035645]
[null,null,null,null,null,"Coincident",0.13079552352428436]
[null,null,"Bluewater","Substation Rating","MVA","Non-Coincident",5.3000001907348633]
[null,null,null,null,null,"Coincident",5.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.5160000324249268]
[null,null,null,null,null,"Coincident",3.1180000305175781]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.5484781265258789]
[null,null,null,null,null,"Coincident",3.1458938121795654]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.8676002025604248]
[null,null,null,null,null,"Coincident",3.4298000335693359]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9033260345458984]
[null,null,null,null,null,"Coincident",3.4604833126068115]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.4618537425994873]
[null,null,null,null,null,"Coincident",3.0699827671051025]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.4938316345214844]
[null,null,null,null,null,"Coincident",3.0974471569061279]
[null,null,"Bocoolima Pumps","Substation Rating","MVA","Non-Coincident",8]
[null,null,null,null,null,"Coincident",8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1399998664855957]
[null,null,null,null,null,"Coincident",2.6000000536441803E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.875798225402832]
[null,null,null,null,null,"Coincident",8.507055789232254E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1914000511169434]
[null,null,null,null,null,"Coincident",2.6259999722242355E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9345560073852539]
[null,null,null,null,null,"Coincident",8.5921265184879303E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1811199188232422]
[null,null,null,null,null,"Coincident",2.6208000257611275E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.9228048324584961]
[null,null,null,null,null,"Coincident",8.575112372636795E-2]
[null,null,"Bohle","Substation Rating","MVA","Non-Coincident",52.700000762939453]
[null,null,null,null,null,"Coincident",52.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.243000030517578]
[null,null,null,null,null,"Coincident",19.764999389648437]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.994474411010742]
[null,null,null,null,null,"Coincident",19.946269989013672]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.170017242431641]
[null,null,null,null,null,"Coincident",19.702938079833984]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.919132232666016]
[null,null,null,null,null,"Coincident",19.883638381958008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.945575714111328]
[null,null,null,null,null,"Coincident",18.661716461181641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.65510368347168]
[null,null,null,null,null,"Coincident",18.832868576049805]
[null,null,"Boondooma Dam","Substation Rating","MVA","Non-Coincident",5.1999998092651367]
[null,null,null,null,null,"Coincident",5.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9769999980926514]
[null,null,null,null,null,"Coincident",1.9129999876022339]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2003829479217529]
[null,null,null,null,null,"Coincident",1.945478081703186]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9921834468841553]
[null,null,null,null,null,"Coincident",1.9276919364929199]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2172820568084717]
[null,null,null,null,null,"Coincident",1.9604194164276123]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9745090007781982]
[null,null,null,null,null,"Coincident",1.9105896949768066]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.19761061668396]
[null,null,null,null,null,"Coincident",1.9430267810821533]
[null,null,"Bowen","Substation Rating","MVA","Non-Coincident",39.799999237060547]
[null,null,null,null,null,"Coincident",39.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.284999847412109]
[null,null,null,null,null,"Coincident",9.7019996643066406]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.289566993713379]
[null,null,null,null,null,"Coincident",9.7117462158203125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.327381134033203]
[null,null,null,null,null,"Coincident",10.525214195251465]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.33233642578125]
[null,null,null,null,null,"Coincident",10.535787582397461]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.289913177490234]
[null,null,null,null,null,"Coincident",9.7058801651000977]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.294482231140137]
[null,null,null,null,null,"Coincident",9.7156305313110352]
[null,null,"Boyne Residential","Substation Rating","MVA","Non-Coincident",26]
[null,null,null,null,null,"Coincident",26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.694999694824219]
[null,null,null,null,null,"Coincident",9.7089996337890625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.842770576477051]
[null,null,null,null,null,"Coincident",9.8878240585327148]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.561526298522949]
[null,null,null,null,null,"Coincident",9.5878314971923828]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.707452774047852]
[null,null,null,null,null,"Coincident",9.7644233703613281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9195051193237305]
[null,null,null,null,null,"Coincident",9.005000114440918]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.056561470031738]
[null,null,null,null,null,"Coincident",9.1708574295043945]
[null,null,"Broxburn","Substation Rating","MVA","Non-Coincident",11]
[null,null,null,null,null,"Coincident",11]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.9600000381469727]
[null,null,null,null,null,"Coincident",6.320000171661377]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.3197355270385742]
[null,null,null,null,null,"Coincident",6.6854171752929687]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.9317421913146973]
[null,null,null,null,null,"Coincident",6.2975640296936035]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.2902002334594727]
[null,null,null,null,null,"Coincident",6.6616840362548828]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3235983848571777]
[null,null,null,null,null,"Coincident",5.8147163391113281]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.6545729637145996]
[null,null,null,null,null,"Coincident",6.1509180068969727]
[null,null,"Bullyard","Substation Rating","MVA","Non-Coincident",14.199999809265137]
[null,null,null,null,null,"Coincident",14.199999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.9639999866485596]
[null,null,null,null,null,"Coincident",2.4440000057220459]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2619533538818359]
[null,null,null,null,null,"Coincident",2.6483080387115479]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.2604000568389893]
[null,null,null,null,null,"Coincident",2.6884000301361084]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.588148832321167]
[null,null,null,null,null,"Coincident",2.9131388664245605]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.9795906543731689]
[null,null,null,null,null,"Coincident",2.4568555355072021]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.2791111469268799]
[null,null,null,null,null,"Coincident",2.6622381210327148]
[null,null,"Bundaberg Central","Substation Rating","MVA","Non-Coincident",64]
[null,null,null,null,null,"Coincident",64]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.215999603271484]
[null,null,null,null,null,"Coincident",14.77299976348877]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.552978515625]
[null,null,null,null,null,"Coincident",14.826720237731934]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.961339950561523]
[null,null,null,null,null,"Coincident",14.566473960876465]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.293607711791992]
[null,null,null,null,null,"Coincident",14.619442939758301]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.998077392578125]
[null,null,null,null,null,"Coincident",13.785276412963867]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.312526702880859]
[null,null,null,null,null,"Coincident",13.835405349731445]
[null,null,"Caboonbah","Substation Rating","MVA","Non-Coincident",6.9000000953674316]
[null,null,null,null,null,"Coincident",6.9000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5429999828338623]
[null,null,null,null,null,"Coincident",8.0000003799796104E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7990202903747559]
[null,null,null,null,null,"Coincident",1.3601470738649368E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","06:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5584299564361572]
[null,null,null,null,null,"Coincident",8.0800000578165054E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8170105218887329]
[null,null,null,null,null,"Coincident",1.3737485744059086E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5553439855575562]
[null,null,null,null,null,"Coincident",8.0640008673071861E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8134124279022217]
[null,null,null,null,null,"Coincident",1.3710282742977142E-2]
[null,null,"Cairns City","Substation Rating","MVA","Non-Coincident",160]
[null,null,null,null,null,"Coincident",160]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",44.898998260498047]
[null,null,null,null,null,"Coincident",36.338001251220703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.012317657470703]
[null,null,null,null,null,"Coincident",36.399559020996094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",48.110622406005859]
[null,null,null,null,null,"Coincident",38.937259674072266]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",48.232048034667969]
[null,null,null,null,null,"Coincident",39.003219604492188]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",46.194332122802734]
[null,null,null,null,null,"Coincident",37.3863525390625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.310920715332031]
[null,null,null,null,null,"Coincident",37.449684143066406]
[null,null,"Cairns North","Substation Rating","MVA","Non-Coincident",126]
[null,null,null,null,null,"Coincident",126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",41.234001159667969]
[null,null,null,null,null,"Coincident",39.550998687744141]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",41.577442169189453]
[null,null,null,null,null,"Coincident",39.669506072998047]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",43.891532897949219]
[null,null,null,null,null,"Coincident",42.100063323974609]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",44.257110595703125]
[null,null,null,null,null,"Coincident",42.226207733154297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",41.718914031982422]
[null,null,null,null,null,"Coincident",40.016117095947266]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",42.066390991210937]
[null,null,null,null,null,"Coincident",40.136020660400391]
[null,null,"Calen","Substation Rating","MVA","Non-Coincident",11]
[null,null,null,null,null,"Coincident",11]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.8559999465942383]
[null,null,null,null,null,"Coincident",2.3550000190734863]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1309876441955566]
[null,null,null,null,null,"Coincident",2.4104399681091309]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.1859965324401855]
[null,null,null,null,null,"Coincident",2.5565409660339355]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.4845175743103027]
[null,null,null,null,null,"Coincident",2.6167254447937012]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7076210975646973]
[null,null,null,null,null,"Coincident",2.2643797397613525]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9720273017883301]
[null,null,null,null,null,"Coincident",2.3176863193511963]
[null,null,"Calliope","Substation Rating","MVA","Non-Coincident",26.700000762939453]
[null,null,null,null,null,"Coincident",26.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.7659997940063477]
[null,null,null,null,null,"Coincident",8.7659997940063477]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.0284366607666016]
[null,null,null,null,null,"Coincident",9.0284366607666016]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.7413673400878906]
[null,null,null,null,null,"Coincident",8.7413673400878906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.0030670166015625]
[null,null,null,null,null,"Coincident",9.0030670166015625]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.9575114250183105]
[null,null,null,null,null,"Coincident",7.9575114250183105]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.1957435607910156]
[null,null,null,null,null,"Coincident",8.1957435607910156]
[null,null,"Canning Street","Substation Rating","MVA","Non-Coincident",46.299999237060547]
[null,null,null,null,null,"Coincident",46.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.840000152587891]
[null,null,null,null,null,"Coincident",22.791999816894531]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.587841033935547]
[null,null,null,null,null,"Coincident",23.473703384399414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.786121368408203]
[null,null,null,null,null,"Coincident",22.740489959716797]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.532272338867188]
[null,null,null,null,null,"Coincident",23.420652389526367]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.765920639038086]
[null,null,null,null,null,"Coincident",20.80909538269043]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.448698043823242]
[null,null,null,null,null,"Coincident",21.431491851806641]
[null,null,"Cannonvale","Substation Rating","MVA","Non-Coincident",34.900001525878906]
[null,null,null,null,null,"Coincident",34.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.168999671936035]
[null,null,null,null,null,"Coincident",14.342000007629395]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.473576545715332]
[null,null,null,null,null,"Coincident",14.561708450317383]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.905514717102051]
[null,null,null,null,null,"Coincident",14.092879295349121]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.204800605773926]
[null,null,null,null,null,"Coincident",14.308772087097168]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.024346351623535]
[null,null,null,null,null,"Coincident",13.25975227355957]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.305940628051758]
[null,null,null,null,null,"Coincident",13.462882041931152]
[null,null,"Cape Ferguson","Substation Rating","MVA","Non-Coincident",4.4000000953674316]
[null,null,null,null,null,"Coincident",4.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8990000486373901]
[null,null,null,null,null,"Coincident",1.746999979019165]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9252766370773315]
[null,null,null,null,null,"Coincident",1.7672854661941528]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9804670810699463]
[null,null,null,null,null,"Coincident",1.8219462633132935]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0078709125518799]
[null,null,null,null,null,"Coincident",1.843101978302002]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8983163833618164]
[null,null,null,null,null,"Coincident",1.7463710308074951]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9245835542678833]
[null,null,null,null,null,"Coincident",1.7666492462158203]
[null,null,"Cape River","Substation Rating","MVA","Non-Coincident",1.1000000238418579]
[null,null,null,null,null,"Coincident",1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.70999997854232788]
[null,null,null,null,null,"Coincident",0.19799999892711639]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.74978727102279663]
[null,null,null,null,null,"Coincident",0.19842630624771118]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.78100001811981201]
[null,null,null,null,null,"Coincident",0.20528838038444519]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.82476603984832764]
[null,null,null,null,null,"Coincident",0.20573039352893829]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.70999997854232788]
[null,null,null,null,null,"Coincident",0.18606060743331909]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.74978727102279663]
[null,null,null,null,null,"Coincident",0.1864611953496933]
[null,null,"Carmila","Substation Rating","MVA","Non-Coincident",1.2999999523162842]
[null,null,null,null,null,"Coincident",1.2999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.66600000858306885]
[null,null,null,null,null,"Coincident",0.52100002765655518]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.69538193941116333]
[null,null,null,null,null,"Coincident",0.54530912637710571]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.64676594734191895]
[null,null,null,null,null,"Coincident",0.50595355033874512]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.67529928684234619]
[null,null,null,null,null,"Coincident",0.5295606255531311]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.58598673343658447]
[null,null,null,null,null,"Coincident",0.45840707421302795]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.61183875799179077]
[null,null,null,null,null,"Coincident",0.4797956645488739]
[null,null,"Cawdor","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.3090000152587891]
[null,null,null,null,null,"Coincident",2.8710000514984131]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.9513835906982422]
[null,null,null,null,null,"Coincident",3.4711730480194092]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.5911531448364258]
[null,null,null,null,null,"Coincident",2.8177142143249512]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.2755999565124512]
[null,null,null,null,null,"Coincident",3.4067480564117432]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.3531670570373535]
[null,null,null,null,null,"Coincident",2.6142177581787109]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.0021352767944336]
[null,null,null,null,null,"Coincident",3.1607112884521484]
[null,null,"Cecil Plains","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9679999351501465]
[null,null,null,null,null,"Coincident",1.1629999876022339]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9883112907409668]
[null,null,null,null,null,"Coincident",1.2683079242706299]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.364799976348877]
[null,null,null,null,null,"Coincident",1.2589010000228882]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3871426582336426]
[null,null,null,null,null,"Coincident",1.3728926181793213]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.9679999351501465]
[null,null,null,null,null,"Coincident",1.1431243419647217]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9883112907409668]
[null,null,null,null,null,"Coincident",1.24663245677948]
[null,null,"Charleville","Substation Rating","MVA","Non-Coincident",17]
[null,null,null,null,null,"Coincident",17]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.607999801635742]
[null,null,null,null,null,"Coincident",9.3470001220703125]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.629199981689453]
[null,null,null,null,null,"Coincident",10.94737434387207]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.563234329223633]
[null,null,null,null,null,"Coincident",9.30755615234375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.584344863891602]
[null,null,null,null,null,"Coincident",10.901176452636719]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.7961702346801758]
[null,null,null,null,null,"Coincident",8.6316747665405273]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.8157472610473633]
[null,null,null,null,null,"Coincident",10.109572410583496]
[null,null,"Charlton","Substation Rating","MVA","Non-Coincident",11]
[null,null,null,null,null,"Coincident",11]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.5269999504089355]
[null,null,null,null,null,"Coincident",1.7719999551773071]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1259675025939941]
[null,null,null,null,null,"Coincident",1.8302316665649414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5269999504089355]
[null,null,null,null,null,"Coincident",1.7719999551773071]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.1259675025939941]
[null,null,null,null,null,"Coincident",1.8302316665649414]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.5269999504089355]
[null,null,null,null,null,"Coincident",1.7719999551773071]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.1259675025939941]
[null,null,null,null,null,"Coincident",1.8302316665649414]
[null,null,"Charters Towers","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.135000228881836]
[null,null,null,null,null,"Coincident",8.4870004653930664]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.455770492553711]
[null,null,null,null,null,"Coincident",8.6977348327636719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.456989288330078]
[null,null,null,null,null,"Coincident",8.7566328048706055]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.78795051574707]
[null,null,null,null,null,"Coincident",8.9740619659423828]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.6030139923095703]
[null,null,null,null,null,"Coincident",8.0415182113647461]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.906947135925293]
[null,null,null,null,null,"Coincident",8.2411909103393555]
[null,null,"Childers","Substation Rating","MVA","Non-Coincident",20.899999618530273]
[null,null,null,null,null,"Coincident",20.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.3400001525878906]
[null,null,null,null,null,"Coincident",7.0229997634887695]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7872204780578613]
[null,null,null,null,null,"Coincident",7.4057426452636719]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.3461651802062988]
[null,null,null,null,null,"Coincident",7.0288987159729004]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.7937612533569336]
[null,null,null,null,null,"Coincident",7.4119629859924316]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.6948142051696777]
[null,null,null,null,null,"Coincident",6.4056782722473145]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.1027240753173828]
[null,null,null,null,null,"Coincident",6.7547779083251953]
[null,null,"Chillagoe","Substation Rating","MVA","Non-Coincident",9.1999998092651367]
[null,null,null,null,null,"Coincident",8.8999996185302734]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.59299999475479126]
[null,null,null,null,null,"Coincident",0.4440000057220459]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.59344583749771118]
[null,null,null,null,null,"Coincident",0.44445022940635681]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.64183950424194336]
[null,null,null,null,null,"Coincident",0.44305428862571716]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.64232206344604492]
[null,null,null,null,null,"Coincident",0.44350355863571167]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.59299999475479126]
[null,null,null,null,null,"Coincident",0.42334955930709839]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.59344583749771118]
[null,null,null,null,null,"Coincident",0.42377886176109314]
[null,null,"Chinchilla Skid","Substation Rating","MVA","Non-Coincident",7.5]
[null,null,null,null,null,"Coincident",7.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.4250001907348633]
[null,null,null,null,null,"Coincident",4.8850002288818359]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.5110368728637695]
[null,null,null,null,null,"Coincident",4.9767084121704102]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.2973499298095703]
[null,null,null,null,null,"Coincident",4.7700562477111816]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.3813619613647461]
[null,null,null,null,null,"Coincident",4.8596062660217285]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.8403477668762207]
[null,null,null,null,null,"Coincident",4.3585433959960938]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.9171123504638672]
[null,null,null,null,null,"Coincident",4.44036865234375]
[null,null,"Chinchilla Town","Substation Rating","MVA","Non-Coincident",13.699999809265137]
[null,null,null,null,null,"Coincident",13.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.2309999465942383]
[null,null,null,null,null,"Coincident",6.8730001449584961]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.6330862045288086]
[null,null,null,null,null,"Coincident",7.1636953353881836]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.8033995628356934]
[null,null,null,null,null,"Coincident",6.5159478187561035]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.1845979690551758]
[null,null,null,null,null,"Coincident",6.791541576385498]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.2037715911865234]
[null,null,null,null,null,"Coincident",6.0152497291564941]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.5556774139404297]
[null,null,null,null,null,"Coincident",6.2696661949157715]
[null,null,"Clare South","Substation Rating","MVA","Non-Coincident",6.3000001907348633]
[null,null,null,null,null,"Coincident",6.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2269999980926514]
[null,null,null,null,null,"Coincident",1.7680000066757202]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5354433059692383]
[null,null,null,null,null,"Coincident",1.9948935508728027]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4497001171112061]
[null,null,null,null,null,"Coincident",1.9448000192642212]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7889876365661621]
[null,null,null,null,null,"Coincident",2.194382905960083]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.3087754249572754]
[null,null,null,null,null,"Coincident",1.832921028137207]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.628544807434082]
[null,null,null,null,null,"Coincident",2.0681462287902832]
[null,null,"Clermont","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.144000053405762]
[null,null,null,null,null,"Coincident",8.9899997711181641]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.229007720947266]
[null,null,null,null,null,"Coincident",9.0484704971313477]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.7639045715332031]
[null,null,null,null,null,"Coincident",8.6531448364257813]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.8457269668579102]
[null,null,null,null,null,"Coincident",8.7094240188598633]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.8656530380249023]
[null,null,null,null,null,"Coincident",7.8570799827575684]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.9399480819702148]
[null,null,null,null,null,"Coincident",7.9081821441650391]
[null,null,"Clifton","Substation Rating","MVA","Non-Coincident",8]
[null,null,null,null,null,"Coincident",8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.1079998016357422]
[null,null,null,null,null,"Coincident",3.2139999866485596]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1319241523742676]
[null,null,null,null,null,"Coincident",3.2229483127593994]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.9315202236175537]
[null,null,null,null,null,"Coincident",3.0759265422821045]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9544167518615723]
[null,null,null,null,null,"Coincident",3.0844905376434326]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6455624103546143]
[null,null,null,null,null,"Coincident",2.8522000312805176]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.6667935848236084]
[null,null,null,null,null,"Coincident",2.8601410388946533]
[null,null,"Clinton","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.063999176025391]
[null,null,null,null,null,"Coincident",16.871000289916992]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.064149856567383]
[null,null,null,null,null,"Coincident",16.871631622314453]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.846670150756836]
[null,null,null,null,null,"Coincident",16.678670883178711]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.846818923950195]
[null,null,null,null,null,"Coincident",16.679294586181641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.491220474243164]
[null,null,null,null,null,"Coincident",15.479143142700195]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.491357803344727]
[null,null,null,null,null,"Coincident",15.479722023010254]
[null,null,"Cloncurry","Substation Rating","MVA","Non-Coincident",6.6999998092651367]
[null,null,null,null,null,"Coincident",6.6999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.5490000247955322]
[null,null,null,null,null,"Coincident",3.0230000019073486]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.648672342300415]
[null,null,null,null,null,"Coincident",3.0878784656524658]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.6619644165039062]
[null,null,null,null,null,"Coincident",3.1192219257354736]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.7648093700408936]
[null,null,null,null,null,"Coincident",3.1861655712127686]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.4553065299987793]
[null,null,null,null,null,"Coincident",2.9431929588317871]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5523474216461182]
[null,null,null,null,null,"Coincident",3.0063586235046387]
[null,null,"Comet","Substation Rating","MVA","Non-Coincident",5.5]
[null,null,null,null,null,"Coincident",5.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.121999979019165]
[null,null,null,null,null,"Coincident",1.1540000438690186]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.3938562870025635]
[null,null,null,null,null,"Coincident",1.2260147333145142]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3342001438140869]
[null,null,null,null,null,"Coincident",1.2694001197814941]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6332418918609619]
[null,null,null,null,null,"Coincident",1.3486162424087524]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.121999979019165]
[null,null,null,null,null,"Coincident",1.1540000438690186]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3938562870025635]
[null,null,null,null,null,"Coincident",1.2260147333145142]
[null,null,"Cooktown","Substation Rating","MVA","Non-Coincident",21.5]
[null,null,null,null,null,"Coincident",21.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9470000267028809]
[null,null,null,null,null,"Coincident",3.8250000476837158]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0465383529663086]
[null,null,null,null,null,"Coincident",3.927858829498291]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.103024959564209]
[null,null,null,null,null,"Coincident",3.9762024879455566]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.2064981460571289]
[null,null,null,null,null,"Coincident",4.0831270217895508]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.9016094207763672]
[null,null,null,null,null,"Coincident",3.7810125350952148]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.0000033378601074]
[null,null,null,null,null,"Coincident",3.8826885223388672]
[null,null,"Coominglah","Substation Rating","MVA","Non-Coincident",2.5999999046325684]
[null,null,null,null,null,"Coincident",2.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4049999713897705]
[null,null,null,null,null,"Coincident",1.1779999732971191]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4815279245376587]
[null,null,null,null,null,"Coincident",1.3034753799438477]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3881258964538574]
[null,null,null,null,null,"Coincident",1.1638522148132324]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4637348651885986]
[null,null,null,null,null,"Coincident",1.2878206968307495]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2736746072769165]
[null,null,null,null,null,"Coincident",1.06789231300354]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3430495262145996]
[null,null,null,null,null,"Coincident",1.181639552116394]
[null,null,"Craiglie","Substation Rating","MVA","Non-Coincident",47.099998474121094]
[null,null,null,null,null,"Coincident",47.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.972999572753906]
[null,null,null,null,null,"Coincident",12.553000450134277]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.19178581237793]
[null,null,null,null,null,"Coincident",12.653171539306641]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.677207946777344]
[null,null,null,null,null,"Coincident",13.073823928833008]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.905073165893555]
[null,null,null,null,null,"Coincident",13.17815113067627]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.206668853759766]
[null,null,null,null,null,"Coincident",11.986232757568359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.415576934814453]
[null,null,null,null,null,"Coincident",12.081881523132324]
[null,null,"Cranbrook","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.944999694824219]
[null,null,null,null,null,"Coincident",15.081999778747559]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.472940444946289]
[null,null,null,null,null,"Coincident",15.488003730773926]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.874912261962891]
[null,null,null,null,null,"Coincident",15.961583137512207]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.433643341064453]
[null,null,null,null,null,"Coincident",16.391263961791992]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.18187141418457]
[null,null,null,null,null,"Coincident",14.360175132751465]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.684545516967773]
[null,null,null,null,null,"Coincident",14.746747016906738]
[null,null,"Crediton","Substation Rating","MVA","Non-Coincident",1.1000000238418579]
[null,null,null,null,null,"Coincident",1.1000000238418579]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.41899999976158142]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.44850975275039673]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.45681893825531006]
[null,null,null,null,null,"Coincident",1.0902600362896919E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.48899224400520325]
[null,null,null,null,null,"Coincident",1.0902600362896919E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.41899999976158142]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.44850975275039673]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,"Cressbrook No. 1","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3980000019073486]
[null,null,null,null,null,"Coincident",4.0000001899898052E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6932284832000732]
[null,null,null,null,null,"Coincident",4.4721360318362713E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4219799041748047]
[null,null,null,null,null,"Coincident",4.0400000289082527E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7201607227325439]
[null,null,null,null,null,"Coincident",4.5168572105467319E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4171841144561768]
[null,null,null,null,null,"Coincident",4.0320004336535931E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7147743701934814]
[null,null,null,null,null,"Coincident",4.5079132542014122E-3]
[null,null,"Cressbrook No. 2","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8159999847412109]
[null,null,null,null,null,"Coincident",6.0000000521540642E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.016676664352417]
[null,null,null,null,null,"Coincident",6.0000000521540642E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","01:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8341599702835083]
[null,null,null,null,null,"Coincident",6.0600000433623791E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0368432998657227]
[null,null,null,null,null,"Coincident",6.0600000433623791E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8305280208587646]
[null,null,null,null,null,"Coincident",6.0479999519884586E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0328102111816406]
[null,null,null,null,null,"Coincident",6.0479999519884586E-3]
[null,null,"Crows Nest","Substation Rating","MVA","Non-Coincident",9.3999996185302734]
[null,null,null,null,null,"Coincident",8.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.0300002098083496]
[null,null,null,null,null,"Coincident",3.1540000438690186]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0423703193664551]
[null,null,null,null,null,"Coincident",3.1949672698974609]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.292151927947998]
[null,null,null,null,null,"Coincident",3.0929069519042969]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3053264617919922]
[null,null,null,null,null,"Coincident",3.1330807209014893]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.1311936378479004]
[null,null,null,null,null,"Coincident",2.9463090896606445]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.1438741683959961]
[null,null,null,null,null,"Coincident",2.9845786094665527]
[null,null,"Croydon","Substation Rating","MVA","Non-Coincident",5.0999999046325684]
[null,null,null,null,null,"Coincident",5.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.30199998617172241]
[null,null,null,null,null,"Coincident",0.26100000739097595]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.30504587292671204]
[null,null,null,null,null,"Coincident",0.26673209667205811]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.30503207445144653]
[null,null,null,null,null,"Coincident",0.26362046599388123]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.30810853838920593]
[null,null,null,null,null,"Coincident",0.26941010355949402]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.28805059194564819]
[null,null,null,null,null,"Coincident",0.24894441664218903]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.2909558117389679]
[null,null,null,null,null,"Coincident",0.2544117271900177]
[null,null,"Cunnamulla","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.2890000343322754]
[null,null,null,null,null,"Coincident",3.4000000953674316]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.4114108085632324]
[null,null,null,null,null,"Coincident",3.404921293258667]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3812994956970215]
[null,null,null,null,null,"Coincident",3.4731681346893311]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.5063443183898926]
[null,null,null,null,null,"Coincident",3.4781951904296875]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.0323891639709473]
[null,null,null,null,null,"Coincident",3.1965780258178711]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.1474761962890625]
[null,null,null,null,null,"Coincident",3.201204776763916]
[null,null,"Dalby Central","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.777000427246094]
[null,null,null,null,null,"Coincident",14.798999786376953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.61577033996582]
[null,null,null,null,null,"Coincident",15.392212867736816]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.285266876220703]
[null,null,null,null,null,"Coincident",14.365241050720215]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.099452972412109]
[null,null,null,null,null,"Coincident",14.941067695617676]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.883213043212891]
[null,null,null,null,null,"Coincident",13.128488540649414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.627302169799805]
[null,null,null,null,null,"Coincident",13.654740333557129]
[null,null,"Dan Gleeson","Substation Rating","MVA","Non-Coincident",42.599998474121094]
[null,null,null,null,null,"Coincident",42.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.288000106811523]
[null,null,null,null,null,"Coincident",24.406999588012695]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.717412948608398]
[null,null,null,null,null,"Coincident",24.836883544921875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.816801071166992]
[null,null,null,null,null,"Coincident",26.847700119018555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.289154052734375]
[null,null,null,null,null,"Coincident",27.320571899414063]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.073810577392578]
[null,null,null,null,null,"Coincident",24.200271606445313]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.49958610534668]
[null,null,null,null,null,"Coincident",24.626514434814453]
[null,null,"Degilbo","Substation Rating","MVA","Non-Coincident",5.0999999046325684]
[null,null,null,null,null,"Coincident",5.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4289999008178711]
[null,null,null,null,null,"Coincident",2.2320001125335693]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5312020778656006]
[null,null,null,null,null,"Coincident",2.3261232376098633]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4427964687347412]
[null,null,null,null,null,"Coincident",2.2446777820587158]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.545579195022583]
[null,null,null,null,null,"Coincident",2.3393354415893555]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2617146968841553]
[null,null,null,null,null,"Coincident",2.078282356262207]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3568782806396484]
[null,null,null,null,null,"Coincident",2.1659231185913086]
[null,null,"Dimbulah","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.1979999542236328]
[null,null,null,null,null,"Coincident",2.0910000801086426]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.6761956214904785]
[null,null,null,null,null,"Coincident",2.1611101627349854]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-23"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2744874954223633]
[null,null,null,null,null,"Coincident",2.1290979385375977]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.7613954544067383]
[null,null,null,null,null,"Coincident",2.2004854679107666]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.8237061500549316]
[null,null,null,null,null,"Coincident",1.9045664072036743]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.2592658996582031]
[null,null,null,null,null,"Coincident",1.9684255123138428]
[null,null,"Duchess Road","Substation Rating","MVA","Non-Coincident",129.30000305175781]
[null,null,null,null,null,"Coincident",129.30000305175781]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.877998352050781]
[null,null,null,null,null,"Coincident",31.035999298095703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",35.456363677978516]
[null,null,null,null,null,"Coincident",31.296810150146484]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",34.682682037353516]
[null,null,null,null,null,"Coincident",30.862197875976562]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.257808685302734]
[null,null,null,null,null,"Coincident",31.121549606323242]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",32.717655181884766]
[null,null,null,null,null,"Coincident",29.113628387451172]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",33.260196685791016]
[null,null,null,null,null,"Coincident",29.358285903930664]
[null,null,"Dysart","Substation Rating","MVA","Non-Coincident",44]
[null,null,null,null,null,"Coincident",44]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.6350002288818359]
[null,null,null,null,null,"Coincident",5.1529998779296875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.6470432281494141]
[null,null,null,null,null,"Coincident",5.1538572311401367]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.158881664276123]
[null,null,null,null,null,"Coincident",4.8316588401794434]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.1701736450195312]
[null,null,null,null,null,"Coincident",4.8324627876281738]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.618934154510498]
[null,null,null,null,null,"Coincident",4.4672384262084961]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.6293745040893555]
[null,null,null,null,null,"Coincident",4.4679818153381348]
[null,null,"East Ayr","Substation Rating","MVA","Non-Coincident",64.900001525878906]
[null,null,null,null,null,"Coincident",64.900001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.289999961853027]
[null,null,null,null,null,"Coincident",12.690999984741211]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.95820140838623]
[null,null,null,null,null,"Coincident",12.771310806274414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.619000434875488]
[null,null,null,null,null,"Coincident",13.960100173950195]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.354022026062012]
[null,null,null,null,null,"Coincident",14.048441886901855]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.061013221740723]
[null,null,null,null,null,"Coincident",12.472333908081055]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.71770191192627]
[null,null,null,null,null,"Coincident",12.551261901855469]
[null,null,"East Bundaberg","Substation Rating","MVA","Non-Coincident",32]
[null,null,null,null,null,"Coincident",32]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.538000106811523]
[null,null,null,null,null,"Coincident",19.538000106811523]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.538509368896484]
[null,null,null,null,null,"Coincident",19.538509368896484]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-2.3499999046325684]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.413543701171875]
[null,null,null,null,null,"Coincident",19.413543701171875]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.41404914855957]
[null,null,null,null,null,"Coincident",19.41404914855957]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.235012054443359]
[null,null,null,null,null,"Coincident",18.235012054443359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.23548698425293]
[null,null,null,null,null,"Coincident",18.23548698425293]
[null,null,"East Toowoomba","Substation Rating","MVA","Non-Coincident",56.299999237060547]
[null,null,null,null,null,"Coincident",56.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.934999465942383]
[null,null,null,null,null,"Coincident",22.593999862670898]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.521442413330078]
[null,null,null,null,null,"Coincident",23.112680435180664]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.802028656005859]
[null,null,null,null,null,"Coincident",22.486452102661133]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.385679244995117]
[null,null,null,null,null,"Coincident",23.002662658691406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.970609664916992]
[null,null,null,null,null,"Coincident",21.005189895629883]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.515813827514648]
[null,null,null,null,null,"Coincident",21.487396240234375]
[null,null,"Eidsvold","Substation Rating","MVA","Non-Coincident",4.5]
[null,null,null,null,null,"Coincident",4.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5420000553131104]
[null,null,null,null,null,"Coincident",1.0670000314712524]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5673943758010864]
[null,null,null,null,null,"Coincident",1.0672699213027954]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6427850723266602]
[null,null,null,null,null,"Coincident",1.1367391347885132]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6698391437530518]
[null,null,null,null,null,"Coincident",1.1370266675949097]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4799038171768188]
[null,null,null,null,null,"Coincident",1.0240319967269897]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5042754411697388]
[null,null,null,null,null,"Coincident",1.0242910385131836]
[null,null,"Ellwoods Road","Substation Rating","MVA","Non-Coincident",6.0999999046325684]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8239998817443848]
[null,null,null,null,null,"Coincident",2.121999979019165]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9731926918029785]
[null,null,null,null,null,"Coincident",2.3640322685241699]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.1064000129699707]
[null,null,null,null,null,"Coincident",2.2969801425933838]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.2705121040344238]
[null,null,null,null,null,"Coincident",2.5589704513549805]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8239998817443848]
[null,null,null,null,null,"Coincident",2.121999979019165]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9731926918029785]
[null,null,null,null,null,"Coincident",2.3640322685241699]
[null,null,"Emerald","Substation Rating","MVA","Non-Coincident",69.599998474121094]
[null,null,null,null,null,"Coincident",69.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",36.534000396728516]
[null,null,null,null,null,"Coincident",35.116001129150391]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",36.580909729003906]
[null,null,null,null,null,"Coincident",35.153347015380859]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",37.630020141601563]
[null,null,null,null,null,"Coincident",36.169479370117188]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.678337097167969]
[null,null,null,null,null,"Coincident",36.20794677734375]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.707298278808594]
[null,null,null,null,null,"Coincident",33.360198974609375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",34.751865386962891]
[null,null,null,null,null,"Coincident",33.395679473876953]
[null,null,"Eton","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.6770000457763672]
[null,null,null,null,null,"Coincident",5.1370000839233398]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.6910190582275391]
[null,null,null,null,null,"Coincident",5.4971466064453125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.2911605834960937]
[null,null,null,null,null,"Coincident",5.5479602813720703]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.3863010406494141]
[null,null,null,null,null,"Coincident",5.9369187355041504]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.5234603881835938]
[null,null,null,null,null,"Coincident",5.0342602729797363]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.5171985626220703]
[null,null,null,null,null,"Coincident",5.3872036933898926]
[null,null,"Eungella Dam","Substation Rating","MVA","Non-Coincident",6.5999999046325684]
[null,null,null,null,null,"Coincident",6.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.80000001192092896]
[null,null,null,null,null,"Coincident",0.80000001192092896]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.94339627027511597]
[null,null,null,null,null,"Coincident",0.94339627027511597]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.83199995756149292]
[null,null,null,null,null,"Coincident",0.83199995756149292]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.98113209009170532]
[null,null,null,null,null,"Coincident",0.98113209009170532]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.80000001192092896]
[null,null,null,null,null,"Coincident",0.80000001192092896]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.94339627027511597]
[null,null,null,null,null,"Coincident",0.94339627027511597]
[null,null,"Evelyn","Substation Rating","MVA","Non-Coincident",6.3000001907348633]
[null,null,null,null,null,"Coincident",6.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8279999494552612]
[null,null,null,null,null,"Coincident",0.90100002288818359]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9220873117446899]
[null,null,null,null,null,"Coincident",0.90428429841995239]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-08"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9658128023147583]
[null,null,null,null,null,"Coincident",0.96892637014389038]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0669934749603271]
[null,null,null,null,null,"Coincident",0.97245830297470093]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8279999494552612]
[null,null,null,null,null,"Coincident",0.90100002288818359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9220873117446899]
[null,null,null,null,null,"Coincident",0.90428429841995239]
[null,null,"Farleigh","Substation Rating","MVA","Non-Coincident",16.5]
[null,null,null,null,null,"Coincident",16.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.1059999465942383]
[null,null,null,null,null,"Coincident",3.5639998912811279]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1750173568725586]
[null,null,null,null,null,"Coincident",3.6518092155456543]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-1.2769999504089355]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.9654104709625244]
[null,null,null,null,null,"Coincident",3.4419684410095215]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.0320649147033691]
[null,null,null,null,null,"Coincident",3.5267713069915771]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7098119258880615]
[null,null,null,null,null,"Coincident",3.2201094627380371]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.772169828414917]
[null,null,null,null,null,"Coincident",3.2994461059570313]
[null,null,"Farnsfield","Substation Rating","MVA","Non-Coincident",28.899999618530273]
[null,null,null,null,null,"Coincident",28.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.8409996032714844]
[null,null,null,null,null,"Coincident",7.6719999313354492]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.296115875244141]
[null,null,null,null,null,"Coincident",8.7430448532104492]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-24"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.7250995635986328]
[null,null,null,null,null,"Coincident",8.4392004013061523]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.325727462768555]
[null,null,null,null,null,"Coincident",9.6173496246337891]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.2830495834350586]
[null,null,null,null,null,"Coincident",8.0555992126464844]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.810920715332031]
[null,null,null,null,null,"Coincident",9.1801967620849609]
[null,null,"Fig Tree","Substation Rating","MVA","Non-Coincident",15.699999809265137]
[null,null,null,null,null,"Coincident",14.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2630000114440918]
[null,null,null,null,null,"Coincident",6.0000000521540642E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.3095283508300781]
[null,null,null,null,null,"Coincident",6.0000000521540642E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.2956299781799316]
[null,null,null,null,null,"Coincident",6.0600000433623791E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.3426237106323242]
[null,null,null,null,null,"Coincident",6.0600000433623791E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2891039848327637]
[null,null,null,null,null,"Coincident",6.0479999519884586E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3360047340393066]
[null,null,null,null,null,"Coincident",6.0479999519884586E-3]
[null,null,"Frenchville","Substation Rating","MVA","Non-Coincident",48]
[null,null,null,null,null,"Coincident",48]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.791999816894531]
[null,null,null,null,null,"Coincident",20.054000854492188]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.810825347900391]
[null,null,null,null,null,"Coincident",20.085029602050781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.915927886962891]
[null,null,null,null,null,"Coincident",18.327552795410156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.933132171630859]
[null,null,null,null,null,"Coincident",18.35590934753418]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.763530731201172]
[null,null,null,null,null,"Coincident",16.346818923950195]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.778877258300781]
[null,null,null,null,null,"Coincident",16.372110366821289]
[null,null,"Friend Street","Substation Rating","MVA","Non-Coincident",47.400001525878906]
[null,null,null,null,null,"Coincident",47.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.639999389648437]
[null,null,null,null,null,"Coincident",16.808000564575195]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.686891555786133]
[null,null,null,null,null,"Coincident",16.808626174926758]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.349775314331055]
[null,null,null,null,null,"Coincident",16.546300888061523]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.395936965942383]
[null,null,null,null,null,"Coincident",16.546916961669922]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.194467544555664]
[null,null,null,null,null,"Coincident",15.50454044342041]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.237722396850586]
[null,null,null,null,null,"Coincident",15.505117416381836]
[null,null,"Garbutt","Substation Rating","MVA","Non-Coincident",53.799999237060547]
[null,null,null,null,null,"Coincident",53.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.028999328613281]
[null,null,null,null,null,"Coincident",20.777999877929688]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.094589233398438]
[null,null,null,null,null,"Coincident",21.747516632080078]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.334501266479492]
[null,null,null,null,null,"Coincident",21.781578063964844]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",30.499858856201172]
[null,null,null,null,null,"Coincident",22.797922134399414]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",26.966022491455078]
[null,null,null,null,null,"Coincident",20.729587554931641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.026798248291016]
[null,null,null,null,null,"Coincident",21.696844100952148]
[null,null,"Gayndah","Substation Rating","MVA","Non-Coincident",24.600000381469727]
[null,null,null,null,null,"Coincident",24.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.8460001945495605]
[null,null,null,null,null,"Coincident",4.6399998664855957]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8591952323913574]
[null,null,null,null,null,"Coincident",4.72705078125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.0062975883483887]
[null,null,null,null,null,"Coincident",4.7672290802001953]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0198545455932617]
[null,null,null,null,null,"Coincident",4.8566665649414062]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3986058235168457]
[null,null,null,null,null,"Coincident",4.2849006652832031]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.4107909202575684]
[null,null,null,null,null,"Coincident",4.3652896881103516]
[null,null,"Georgetown","Substation Rating","MVA","Non-Coincident",4]
[null,null,null,null,null,"Coincident",4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.3619999885559082]
[null,null,null,null,null,"Coincident",1.2289999723434448]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3774904012680054]
[null,null,null,null,null,"Coincident",1.2655611038208008]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-10"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4500941038131714]
[null,null,null,null,null,"Coincident",1.3084917068481445]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4665864706039429]
[null,null,null,null,null,"Coincident",1.3474175930023193]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3690824508666992]
[null,null,null,null,null,"Coincident",1.2353907823562622]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3846534490585327]
[null,null,null,null,null,"Coincident",1.2721420526504517]
[null,null,"Giru","Substation Rating","MVA","Non-Coincident",10.5]
[null,null,null,null,null,"Coincident",9.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6440000534057617]
[null,null,null,null,null,"Coincident",2.0160000324249268]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9755606651306152]
[null,null,null,null,null,"Coincident",2.2698249816894531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8555202484130859]
[null,null,null,null,null,"Coincident",2.2176001071929932]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.2136056423187256]
[null,null,null,null,null,"Coincident",2.4968075752258301]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5911200046539307]
[null,null,null,null,null,"Coincident",1.8406885862350464]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9160494804382324]
[null,null,null,null,null,"Coincident",2.0724408626556396]
[null,null,"Givelda","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.554999828338623]
[null,null,null,null,null,"Coincident",3.5490000247955322]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.3839907646179199]
[null,null,null,null,null,"Coincident",4.0298490524291992]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.1104998588562012]
[null,null,null,null,null,"Coincident",3.903900146484375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.0223898887634277]
[null,null,null,null,null,"Coincident",4.4328341484069824]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.554999828338623]
[null,null,null,null,null,"Coincident",3.5490000247955322]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.3839907646179199]
[null,null,null,null,null,"Coincident",4.0298490524291992]
[null,null,"Gladstone South","Substation Rating","MVA","Non-Coincident",54.700000762939453]
[null,null,null,null,null,"Coincident",54.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.049999237060547]
[null,null,null,null,null,"Coincident",18.045999526977539]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.31800651550293]
[null,null,null,null,null,"Coincident",18.302261352539063]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.654342651367188]
[null,null,null,null,null,"Coincident",17.650430679321289]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.916475296020508]
[null,null,null,null,null,"Coincident",17.90107536315918]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.222618103027344]
[null,null,null,null,null,"Coincident",16.219022750854492]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.463491439819336]
[null,null,null,null,null,"Coincident",16.4493408203125]
[null,null,"Glenden","Substation Rating","MVA","Non-Coincident",15]
[null,null,null,null,null,"Coincident",15]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9609999656677246]
[null,null,null,null,null,"Coincident",1.215999960899353]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9758757352828979]
[null,null,null,null,null,"Coincident",1.2163950204849243]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-08"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8626558780670166]
[null,null,null,null,null,"Coincident",1.155017614364624]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8767856359481812]
[null,null,null,null,null,"Coincident",1.1553928852081299]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7196204662322998]
[null,null,null,null,null,"Coincident",1.0663224458694458]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.7326651811599731]
[null,null,null,null,null,"Coincident",1.0666688680648804]
[null,null,"Glenelg","Substation Rating","MVA","Non-Coincident",0.60000002384185791]
[null,null,null,null,null,"Coincident",0.60000002384185791]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.51099997758865356]
[null,null,null,null,null,"Coincident",0.45500001311302185]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.52536177635192871]
[null,null,null,null,null,"Coincident",0.48003542423248291]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-16"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.53143996000289917]
[null,null,null,null,null,"Coincident",0.4731999933719635]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.54637622833251953]
[null,null,null,null,null,"Coincident",0.4992368221282959]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.51099997758865356]
[null,null,null,null,null,"Coincident",0.45500001311302185]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.52536177635192871]
[null,null,null,null,null,"Coincident",0.48003542423248291]
[null,null,"Glenella 11kV","Substation Rating","MVA","Non-Coincident",75.199996948242187]
[null,null,null,null,null,"Coincident",75.199996948242187]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8409996032714844]
[null,null,null,null,null,"Coincident",9.8409996032714844]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.042572975158691]
[null,null,null,null,null,"Coincident",10.042572975158691]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.4431276321411133]
[null,null,null,null,null,"Coincident",9.4431276321411133]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.6365518569946289]
[null,null,null,null,null,"Coincident",9.6365518569946289]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.8149776458740234]
[null,null,null,null,null,"Coincident",8.8149776458740234]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.9955348968505859]
[null,null,null,null,null,"Coincident",8.9955348968505859]
[null,null,"Glenella 33kV","Substation Rating","MVA","Non-Coincident",126]
[null,null,null,null,null,"Coincident",126]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",41.634998321533203]
[null,null,null,null,null,"Coincident",38.66400146484375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.143039703369141]
[null,null,null,null,null,"Coincident",38.984550476074219]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",42.266181945800781]
[null,null,null,null,null,"Coincident",39.250144958496094]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",42.781925201416016]
[null,null,null,null,null,"Coincident",39.575553894042969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",38.969940185546875]
[null,null,null,null,null,"Coincident",36.189117431640625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",39.445461273193359]
[null,null,null,null,null,"Coincident",36.489147186279297]
[null,null,"Gooburrum","Substation Rating","MVA","Non-Coincident",14.300000190734863]
[null,null,null,null,null,"Coincident",14.300000190734863]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.5720000267028809]
[null,null,null,null,null,"Coincident",4.3670001029968262]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.0956535339355469]
[null,null,null,null,null,"Coincident",4.8409309387207031]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.9843487739562988]
[null,null,null,null,null,"Coincident",4.7608599662780762]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.5552306175231934]
[null,null,null,null,null,"Coincident",5.2775349617004395]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.4871435165405273]
[null,null,null,null,null,"Coincident",4.2859487533569336]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.0010781288146973]
[null,null,null,null,null,"Coincident",4.7510833740234375]
[null,null,"Gooburrum 3.3kV","Substation Rating","MVA","Non-Coincident",4.5]
[null,null,null,null,null,"Coincident",4.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.284000039100647]
[null,null,null,null,null,"Coincident",2.0000000949949026E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.492064356803894]
[null,null,null,null,null,"Coincident",6.3245552591979504E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2968400716781616]
[null,null,null,null,null,"Coincident",2.0200000144541264E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5069849491119385]
[null,null,null,null,null,"Coincident",6.3878009095788002E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2942720651626587]
[null,null,null,null,null,"Coincident",2.0160002168267965E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5040009021759033]
[null,null,null,null,null,"Coincident",6.3751516863703728E-3]
[null,null,"Gootchie","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.6180000305175781]
[null,null,null,null,null,"Coincident",3.0520000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.7590322494506836]
[null,null,null,null,null,"Coincident",3.147634744644165]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4523317813873291]
[null,null,null,null,null,"Coincident",2.9122488498687744]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.5869061946868896]
[null,null,null,null,null,"Coincident",3.0035045146942139]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.1484923362731934]
[null,null,null,null,null,"Coincident",2.6559419631958008]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.2712225914001465]
[null,null,null,null,null,"Coincident",2.739166259765625]
[null,null,"Granite Creek","Substation Rating","MVA","Non-Coincident",3.7999999523162842]
[null,null,null,null,null,"Coincident",3.7999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.25900000333786011]
[null,null,null,null,null,"Coincident",0.23999999463558197]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.27419152855873108]
[null,null,null,null,null,"Coincident",0.25738880038261414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.26755478978157043]
[null,null,null,null,null,"Coincident",0.24792720377445221]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.28324809670448303]
[null,null,null,null,null,"Coincident",0.26589035987854004]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.25458404421806335]
[null,null,null,null,null,"Coincident",0.23590798676013947]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.26951655745506287]
[null,null,null,null,null,"Coincident",0.25300031900405884]
[null,null,"Greenvale","Substation Rating","MVA","Non-Coincident",0.69999998807907104]
[null,null,null,null,null,"Coincident",0.69999998807907104]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.47999998927116394]
[null,null,null,null,null,"Coincident",0.43000000715255737]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.48507729172706604]
[null,null,null,null,null,"Coincident",0.43267077207565308]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.51008158922195435]
[null,null,null,null,null,"Coincident",0.45694810152053833]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.51547706127166748]
[null,null,null,null,null,"Coincident",0.45978623628616333]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.47363036870956421]
[null,null,null,null,null,"Coincident",0.42429390549659729]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.47864031791687012]
[null,null,null,null,null,"Coincident",0.42692923545837402]
[null,null,"Gumlu","Substation Rating","MVA","Non-Coincident",1.6000000238418579]
[null,null,null,null,null,"Coincident",1.2999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1890000104904175]
[null,null,null,null,null,"Coincident",0.37099999189376831]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.373204231262207]
[null,null,null,null,null,"Coincident",0.3730442225933075]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2692456245422363]
[null,null,null,null,null,"Coincident",0.36915239691734314]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4658817052841187]
[null,null,null,null,null,"Coincident",0.37118646502494812]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1794761419296265]
[null,null,null,null,null,"Coincident",0.32906216382980347]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3622047901153564]
[null,null,null,null,null,"Coincident",0.33087530732154846]
[null,null,"Guthalungra","Substation Rating","MVA","Non-Coincident",0.60000002384185791]
[null,null,null,null,null,"Coincident",0.60000002384185791]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.43700000643730164]
[null,null,null,null,null,"Coincident",0.43700000643730164]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.51411765813827515]
[null,null,null,null,null,"Coincident",0.51411765813827515]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.45447999238967896]
[null,null,null,null,null,"Coincident",0.45447999238967896]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.53468233346939087]
[null,null,null,null,null,"Coincident",0.53468233346939087]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.43700000643730164]
[null,null,null,null,null,"Coincident",0.43700000643730164]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.51411765813827515]
[null,null,null,null,null,"Coincident",0.51411765813827515]
[null,null,"Haughton","Substation Rating","MVA","Non-Coincident",6.1999998092651367]
[null,null,null,null,null,"Coincident",6.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.054999828338623]
[null,null,null,null,null,"Coincident",3.6779999732971191]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.8364777565002441]
[null,null,null,null,null,"Coincident",4.4148664474487305]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2719020843505859]
[null,null,null,null,null,"Coincident",3.8747363090515137]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.0951809883117676]
[null,null,null,null,null,"Coincident",4.6510176658630371]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.0277500152587891]
[null,null,null,null,null,"Coincident",3.6532838344573975]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.8039765357971191]
[null,null,null,null,null,"Coincident",4.3851985931396484]
[null,null,"Havilah (T184)","Substation Rating","MVA","Non-Coincident",14.899999618530273]
[null,null,null,null,null,"Coincident",13.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3889999389648437]
[null,null,null,null,null,"Coincident",2.0000000949949026E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4196646213531494]
[null,null,null,null,null,"Coincident",2.0000000949949026E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4128899574279785]
[null,null,null,null,null,"Coincident",2.0200000144541264E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4438612461090088]
[null,null,null,null,null,"Coincident",2.0200000144541264E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4081120491027832]
[null,null,null,null,null,"Coincident",2.0160002168267965E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.4390220642089844]
[null,null,null,null,null,"Coincident",2.0160002168267965E-3]
[null,null,"Helenvale","Substation Rating","MVA","Non-Coincident",5.6999998092651367]
[null,null,null,null,null,"Coincident",5.6999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.6809999942779541]
[null,null,null,null,null,"Coincident",0.50499999523162842]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.69626575708389282]
[null,null,null,null,null,"Coincident",0.51662945747375488]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.74910002946853638]
[null,null,null,null,null,"Coincident",0.55550003051757813]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.76589232683181763]
[null,null,null,null,null,"Coincident",0.56829243898391724]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.6809999942779541]
[null,null,null,null,null,"Coincident",0.50499999523162842]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.69626575708389282]
[null,null,null,null,null,"Coincident",0.51662945747375488]
[null,null,"Hermit Park","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.327999114990234]
[null,null,null,null,null,"Coincident",18.902000427246094]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.336147308349609]
[null,null,null,null,null,"Coincident",19.427268981933594]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.570775985717773]
[null,null,null,null,null,"Coincident",19.954086303710937]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.635038375854492]
[null,null,null,null,null,"Coincident",20.508590698242188]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.625112533569336]
[null,null,null,null,null,"Coincident",18.306964874267578]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.601524353027344]
[null,null,null,null,null,"Coincident",18.815698623657227]
[null,null,"Highfields","Substation Rating","MVA","Non-Coincident",5.5]
[null,null,null,null,null,"Coincident",5.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0559999942779541]
[null,null,null,null,null,"Coincident",1.628000020980835]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0872795581817627]
[null,null,null,null,null,"Coincident",1.6761816740036011]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-10"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6171879768371582]
[null,null,null,null,null,"Coincident",1.6027334928512573]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6417914628982544]
[null,null,null,null,null,"Coincident",1.6501673460006714]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.518006443977356]
[null,null,null,null,null,"Coincident",1.5002346038818359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5411010980606079]
[null,null,null,null,null,"Coincident",1.5446349382400513]
[null,null,"Hillsborough","Substation Rating","MVA","Non-Coincident",0.10000000149011612]
[null,null,null,null,null,"Coincident",0.10000000149011612]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.000000074505806E-2]
[null,null,null,null,null,"Coincident",5.000000074505806E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8823529630899429E-2]
[null,null,null,null,null,"Coincident",5.8823529630899429E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1999997347593307E-2]
[null,null,null,null,null,"Coincident",5.1999997347593307E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.1176467686891556E-2]
[null,null,null,null,null,"Coincident",6.1176467686891556E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.000000074505806E-2]
[null,null,null,null,null,"Coincident",5.000000074505806E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.8823529630899429E-2]
[null,null,null,null,null,"Coincident",5.8823529630899429E-2]
[null,null,"Home Hill","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.057999610900879]
[null,null,null,null,null,"Coincident",12.015999794006348]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.547340393066406]
[null,null,null,null,null,"Coincident",13.356950759887695]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-2.2060000896453857]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.363800048828125]
[null,null,null,null,null,"Coincident",13.217599868774414]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.0020751953125]
[null,null,null,null,null,"Coincident",14.692646026611328]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.969186782836914]
[null,null,null,null,null,"Coincident",12.854475975036621]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.562453269958496]
[null,null,null,null,null,"Coincident",14.288998603820801]
[null,null,"Howard","Substation Rating","MVA","Non-Coincident",16.100000381469727]
[null,null,null,null,null,"Coincident",16.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.2800002098083496]
[null,null,null,null,null,"Coincident",7.000999927520752]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.4166226387023926]
[null,null,null,null,null,"Coincident",7.1411809921264648]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.5089564323425293]
[null,null,null,null,null,"Coincident",7.2211813926696777]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.6498756408691406]
[null,null,null,null,null,"Coincident",7.3657712936401367]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.0212693214416504]
[null,null,null,null,null,"Coincident",6.7521843910217285]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.1530361175537109]
[null,null,null,null,null,"Coincident",6.8873834609985352]
[null,null,"Hughenden","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.4389998912811279]
[null,null,null,null,null,"Coincident",3.2179999351501465]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.4394721984863281]
[null,null,null,null,null,"Coincident",3.2291402816772461]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5978128910064697]
[null,null,null,null,null,"Coincident",3.3666071891784668]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.5983071327209473]
[null,null,null,null,null,"Coincident",3.3782620429992676]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3573236465454102]
[null,null,null,null,null,"Coincident",3.1415724754333496]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3577847480773926]
[null,null,null,null,null,"Coincident",3.1524481773376465]
[null,null,"ICI","Substation Rating","MVA","Non-Coincident",20.799999237060547]
[null,null,null,null,null,"Coincident",19.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1360001564025879]
[null,null,null,null,null,"Coincident",3.8059999942779541]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8496580123901367]
[null,null,null,null,null,"Coincident",4.3595309257507324]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","05:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1873602867126465]
[null,null,null,null,null,"Coincident",3.844059944152832]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9081544876098633]
[null,null,null,null,null,"Coincident",4.4031262397766113]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1770882606506348]
[null,null,null,null,null,"Coincident",3.8364479541778564]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.8964552879333496]
[null,null,null,null,null,"Coincident",4.3944072723388672]
[null,null,"Ilbilbie","Substation Rating","MVA","Non-Coincident",1.2000000476837158]
[null,null,null,null,null,"Coincident",1.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.67400002479553223]
[null,null,null,null,null,"Coincident",0.54699999094009399]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.71216291189193726]
[null,null,null,null,null,"Coincident",0.56614923477172852]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-08"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.62018108367919922]
[null,null,null,null,null,"Coincident",0.50332200527191162]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.6552966833114624]
[null,null,null,null,null,"Coincident",0.52094221115112305]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.54869669675827026]
[null,null,null,null,null,"Coincident",0.44530722498893738]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.579764723777771]
[null,null,null,null,null,"Coincident",0.46089643239974976]
[null,null,"Ingham","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8620004653930664]
[null,null,null,null,null,"Coincident",9.3929996490478516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.375607490539551]
[null,null,null,null,null,"Coincident",9.7419452667236328]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.650960922241211]
[null,null,null,null,null,"Coincident",10.144439697265625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.205657005310059]
[null,null,null,null,null,"Coincident",10.52130126953125]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.8620004653930664]
[null,null,null,null,null,"Coincident",9.3929996490478516]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.375607490539551]
[null,null,null,null,null,"Coincident",9.7419452667236328]
[null,null,"Isis Central Mill","Substation Rating","MVA","Non-Coincident",44.700000762939453]
[null,null,null,null,null,"Coincident",42.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0580000877380371]
[null,null,null,null,null,"Coincident",0.27500000596046448]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9765725135803223]
[null,null,null,null,null,"Coincident",0.33596727252006531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-26"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-14.642000198364258]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.0885801315307617]
[null,null,null,null,null,"Coincident",0.27775001525878906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.0163383483886719]
[null,null,null,null,null,"Coincident",0.33932694792747498]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.0824642181396484]
[null,null,null,null,null,"Coincident",0.27720001339912415]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.008385181427002]
[null,null,null,null,null,"Coincident",0.338655024766922]
[null,null,"Jandowae","Substation Rating","MVA","Non-Coincident",3.2000000476837158]
[null,null,null,null,null,"Coincident",3.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.3609999418258667]
[null,null,null,null,null,"Coincident",1.2640000581741333]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4055325984954834]
[null,null,null,null,null,"Coincident",1.2988830804824829]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3277778625488281]
[null,null,null,null,null,"Coincident",1.2331458330154419]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3712235689163208]
[null,null,null,null,null,"Coincident",1.2671773433685303]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2185713052749634]
[null,null,null,null,null,"Coincident",1.1317224502563477]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2584435939788818]
[null,null,null,null,null,"Coincident",1.1629549264907837]
[null,null,"Jarvisfield","Substation Rating","MVA","Non-Coincident",12.100000381469727]
[null,null,null,null,null,"Coincident",12.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.2810001373291016]
[null,null,null,null,null,"Coincident",4.6030001640319824]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.379514217376709]
[null,null,null,null,null,"Coincident",5.5697493553161621]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.386620044708252]
[null,null,null,null,null,"Coincident",4.6950602531433105]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.5071043968200684]
[null,null,null,null,null,"Coincident",5.6811442375183105]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.0169501304626465]
[null,null,null,null,null,"Coincident",4.3728499412536621]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.0605382919311523]
[null,null,null,null,null,"Coincident",5.2912616729736328]
[null,null,"Jubilee Pocket","Substation Rating","MVA","Non-Coincident",32]
[null,null,null,null,null,"Coincident",32]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.0399999618530273]
[null,null,null,null,null,"Coincident",4.5679998397827148]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.120607852935791]
[null,null,null,null,null,"Coincident",4.6302990913391113]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.4908280372619629]
[null,null,null,null,null,"Coincident",4.9766073226928711]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.578646183013916]
[null,null,null,null,null,"Coincident",5.0444793701171875]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.9963536262512207]
[null,null,null,null,null,"Coincident",4.5284409523010254]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.076263427734375]
[null,null,null,null,null,"Coincident",4.5902004241943359]
[null,null,"Julia Creek","Substation Rating","MVA","Non-Coincident",7.4000000953674316]
[null,null,null,null,null,"Coincident",7.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5369999408721924]
[null,null,null,null,null,"Coincident",2.4590001106262207]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6086044311523438]
[null,null,null,null,null,"Coincident",2.4679508209228516]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5780231952667236]
[null,null,null,null,null,"Coincident",2.4987621307373047]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6507856845855713]
[null,null,null,null,null,"Coincident",2.5078575611114502]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4526193141937256]
[null,null,null,null,null,"Coincident",2.377213716506958]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5218422412872314]
[null,null,null,null,null,"Coincident",2.3858668804168701]
[null,null,"Kaimkillenbun","Substation Rating","MVA","Non-Coincident",1]
[null,null,null,null,null,"Coincident",1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.90399998426437378]
[null,null,null,null,null,"Coincident",0.84799998998641968]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.92829787731170654]
[null,null,null,null,null,"Coincident",0.87811613082885742]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.88295483589172363]
[null,null,null,null,null,"Coincident",0.82825851440429688]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.90668708086013794]
[null,null,null,null,null,"Coincident",0.85767358541488647]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.82319146394729614]
[null,null,null,null,null,"Coincident",0.77219730615615845]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.84531736373901367]
[null,null,null,null,null,"Coincident",0.7996213436126709]
[null,null,"Kalamia","Substation Rating","MVA","Non-Coincident",13]
[null,null,null,null,null,"Coincident",13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.5170001983642578]
[null,null,null,null,null,"Coincident",3.750999927520752]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8007373809814453]
[null,null,null,null,null,"Coincident",4.2336001396179199]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-2.6610000133514404]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.8936457633972168]
[null,null,null,null,null,"Coincident",4.0070805549621582]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.1967535018920898]
[null,null,null,null,null,"Coincident",4.5226278305053711]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.4547686576843262]
[null,null,null,null,null,"Coincident",3.7086887359619141]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.7353048324584961]
[null,null,null,null,null,"Coincident",4.185844898223877]
[null,null,"Kearneys Spring","Substation Rating","MVA","Non-Coincident",89.800003051757812]
[null,null,null,null,null,"Coincident",79.099998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.179000854492188]
[null,null,null,null,null,"Coincident",15.586999893188477]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.226413726806641]
[null,null,null,null,null,"Coincident",15.653191566467285]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.995904922485352]
[null,null,null,null,null,"Coincident",15.055327415466309]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.047203063964844]
[null,null,null,null,null,"Coincident",15.119260787963867]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.45091438293457]
[null,null,null,null,null,"Coincident",14.06227970123291]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.498908996582031]
[null,null,null,null,null,"Coincident",14.121996879577637]
[null,null,"Kelsey Creek East","Substation Rating","MVA","Non-Coincident",36.799999237060547]
[null,null,null,null,null,"Coincident",36.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.76099967956543]
[null,null,null,null,null,"Coincident",9.6619997024536133]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.480267524719238]
[null,null,null,null,null,"Coincident",9.9359312057495117]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.137100219726563]
[null,null,null,null,null,"Coincident",10.628199577331543]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.92829418182373]
[null,null,null,null,null,"Coincident",10.929524421691895]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.102823257446289]
[null,null,null,null,null,"Coincident",9.902003288269043]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.839957237243652]
[null,null,null,null,null,"Coincident",10.1827392578125]
[null,null,"Kidston","Substation Rating","MVA","Non-Coincident",42.5]
[null,null,null,null,null,"Coincident",42.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.32699999213218689]
[null,null,null,null,null,"Coincident",0.15999999642372131]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.35115951299667358]
[null,null,null,null,null,"Coincident",0.17232526838779449]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.34007999300956726]
[null,null,null,null,null,"Coincident",0.16639998555183411]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.36520588397979736]
[null,null,null,null,null,"Coincident",0.17921827733516693]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.32699999213218689]
[null,null,null,null,null,"Coincident",0.15999999642372131]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.35115951299667358]
[null,null,null,null,null,"Coincident",0.17232526838779449]
[null,null,"Kilkivan Town","Substation Rating","MVA","Non-Coincident",2]
[null,null,null,null,null,"Coincident",2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.93199998140335083]
[null,null,null,null,null,"Coincident",0.90600001811981201]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.96341061592102051]
[null,null,null,null,null,"Coincident",0.94509100914001465]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.96517914533615112]
[null,null,null,null,null,"Coincident",0.93825358152389526]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.99770796298980713]
[null,null,null,null,null,"Coincident",0.97873622179031372]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.88779526948928833]
[null,null,null,null,null,"Coincident",0.86302846670150757]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.91771608591079712]
[null,null,null,null,null,"Coincident",0.90026533603668213]
[null,null,"Killarney","Substation Rating","MVA","Non-Coincident",8.8999996185302734]
[null,null,null,null,null,"Coincident",7.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9910000562667847]
[null,null,null,null,null,"Coincident",1.4270000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0953495502471924]
[null,null,null,null,null,"Coincident",1.4944782257080078]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.076453685760498]
[null,null,null,null,null,"Coincident",1.5102797746658325]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.1852819919586182]
[null,null,null,null,null,"Coincident",1.5816959142684937]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0016319751739502]
[null,null,null,null,null,"Coincident",1.4234610795974731]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1065387725830078]
[null,null,null,null,null,"Coincident",1.490772008895874]
[null,null,"Kingaroy","Substation Rating","MVA","Non-Coincident",57.400001525878906]
[null,null,null,null,null,"Coincident",57.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.256999969482422]
[null,null,null,null,null,"Coincident",20.166000366210937]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.23954963684082]
[null,null,null,null,null,"Coincident",20.907844543457031]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.908010482788086]
[null,null,null,null,null,"Coincident",19.849796295166016]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.875152587890625]
[null,null,null,null,null,"Coincident",20.580009460449219]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.664510726928711]
[null,null,null,null,null,"Coincident",18.723123550415039]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.576759338378906]
[null,null,null,null,null,"Coincident",19.411888122558594]
[null,null,"Kirknie","Substation Rating","MVA","Non-Coincident",9.6999998092651367]
[null,null,null,null,null,"Coincident",9.6999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.5450000762939453]
[null,null,null,null,null,"Coincident",6.0809998512268066]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.7989063262939453]
[null,null,null,null,null,"Coincident",7.0278081893920898]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.2995004653930664]
[null,null,null,null,null,"Coincident",6.6890997886657715]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.6787967681884766]
[null,null,null,null,null,"Coincident",7.7305893898010254]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.0727729797363281]
[null,null,null,null,null,"Coincident",6.5063657760620117]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.4143896102905273]
[null,null,null,null,null,"Coincident",7.5194034576416016]
[null,null,"Kogan Creek","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.0000003799796104E-3]
[null,null,null,null,null,"Coincident",4.0000001899898052E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.9442720636725426E-3]
[null,null,null,null,null,"Coincident",5.6568547151982784E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.4201609715819359E-3]
[null,null,null,null,null,"Coincident",4.2100804857909679E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.4140255823731422E-3]
[null,null,null,null,null,"Coincident",5.9539531357586384E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.7314404770731926E-3]
[null,null,null,null,null,"Coincident",3.8657202385365963E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.6440127342939377E-3]
[null,null,null,null,null,"Coincident",5.4669543169438839E-3]
[null,null,"Koumala","Substation Rating","MVA","Non-Coincident",7.5]
[null,null,null,null,null,"Coincident",7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.7220000028610229]
[null,null,null,null,null,"Coincident",1.2079999446868896]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9686036109924316]
[null,null,null,null,null,"Coincident",1.295849084854126]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-24"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.7220000028610229]
[null,null,null,null,null,"Coincident",1.3287999629974365]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9686036109924316]
[null,null,null,null,null,"Coincident",1.4254339933395386]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.549799919128418]
[null,null,null,null,null,"Coincident",1.1737411022186279]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.7717431783676147]
[null,null,null,null,null,"Coincident",1.2590987682342529]
[null,null,"Laguna Quays","Substation Rating","MVA","Non-Coincident",17.600000381469727]
[null,null,null,null,null,"Coincident",17.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0439999103546143]
[null,null,null,null,null,"Coincident",1.437000036239624]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.092519998550415]
[null,null,null,null,null,"Coincident",1.4402701854705811]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-10"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2188231945037842]
[null,null,null,null,null,"Coincident",1.5599067211151123]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2714934349060059]
[null,null,null,null,null,"Coincident",1.5634565353393555]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.926878809928894]
[null,null,null,null,null,"Coincident",1.3546600341796875]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9726186990737915]
[null,null,null,null,null,"Coincident",1.3577427864074707]
[null,null,"Lakeland","Substation Rating","MVA","Non-Coincident",16]
[null,null,null,null,null,"Coincident",16]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.7860000133514404]
[null,null,null,null,null,"Coincident",1.1490000486373901]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8028621673583984]
[null,null,null,null,null,"Coincident",1.1497673988342285]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-06"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9646000862121582]
[null,null,null,null,null,"Coincident",1.2639000415802002]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.983148455619812]
[null,null,null,null,null,"Coincident",1.2647441625595093]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9288800954818726]
[null,null,null,null,null,"Coincident",1.2409200668334961]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9470912218093872]
[null,null,null,null,null,"Coincident",1.2417488098144531]
[null,null,"Lakes Creek","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.854000091552734]
[null,null,null,null,null,"Coincident",12.73799991607666]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.85400390625]
[null,null,null,null,null,"Coincident",12.952595710754395]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.339401245117187]
[null,null,null,null,null,"Coincident",14.011799812316895]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.339405059814453]
[null,null,null,null,null,"Coincident",14.247855186462402]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.854000091552734]
[null,null,null,null,null,"Coincident",12.73799991607666]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.85400390625]
[null,null,null,null,null,"Coincident",12.952595710754395]
[null,null,"Landing Road","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.7829999923706055]
[null,null,null,null,null,"Coincident",1.1380000114440918]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0170121192932129]
[null,null,null,null,null,"Coincident",1.3130381107330322]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9613000154495239]
[null,null,null,null,null,"Coincident",1.1374651193618774]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2187132835388184]
[null,null,null,null,null,"Coincident",1.3124209642410278]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7829999923706055]
[null,null,null,null,null,"Coincident",1.0503284931182861]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0170121192932129]
[null,null,null,null,null,"Coincident",1.2118816375732422]
[null,null,"Lannercost","Substation Rating","MVA","Non-Coincident",6.3000001907348633]
[null,null,null,null,null,"Coincident",6.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9859999418258667]
[null,null,null,null,null,"Coincident",1.9329999685287476]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0203557014465332]
[null,null,null,null,null,"Coincident",1.9647881984710693]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0282816886901855]
[null,null,null,null,null,"Coincident",1.9741533994674683]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0633690357208252]
[null,null,null,null,null,"Coincident",2.0066184997558594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8398898839950562]
[null,null,null,null,null,"Coincident",1.7907891273498535]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8717180490493774]
[null,null,null,null,null,"Coincident",1.8202387094497681]
[null,null,"Littlemore","Substation Rating","MVA","Non-Coincident",2.2000000476837158]
[null,null,null,null,null,"Coincident",2.2000000476837158]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.57599997520446777]
[null,null,null,null,null,"Coincident",0.32400000095367432]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.64944279193878174]
[null,null,null,null,null,"Coincident",0.38075715303421021]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.63359999656677246]
[null,null,null,null,null,"Coincident",0.3564000129699707]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.71438705921173096]
[null,null,null,null,null,"Coincident",0.41883286833763123]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.57599997520446777]
[null,null,null,null,null,"Coincident",0.32400000095367432]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.64944279193878174]
[null,null,null,null,null,"Coincident",0.38075715303421021]
[null,null,"Longreach","Substation Rating","MVA","Non-Coincident",24.399999618530273]
[null,null,null,null,null,"Coincident",24.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8170003890991211]
[null,null,null,null,null,"Coincident",8.7910003662109375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.9515657424926758]
[null,null,null,null,null,"Coincident",8.8126258850097656]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.3867216110229492]
[null,null,null,null,null,"Coincident",8.4056911468505859]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.5153884887695313]
[null,null,null,null,null,"Coincident",8.4263687133789062]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.7462596893310547]
[null,null,null,null,null,"Coincident",7.8321657180786133]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.8661479949951172]
[null,null,null,null,null,"Coincident",7.8514328002929687]
[null,null,"Louisa Creek","Substation Rating","MVA","Non-Coincident",7.4000000953674316]
[null,null,null,null,null,"Coincident",7.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3269999027252197]
[null,null,null,null,null,"Coincident",2.1710000038146973]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.3282735347747803]
[null,null,null,null,null,"Coincident",2.1710746288299561]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3010306358337402]
[null,null,null,null,null,"Coincident",2.1467716693878174]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3022899627685547]
[null,null,null,null,null,"Coincident",2.1468453407287598]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1692061424255371]
[null,null,null,null,null,"Coincident",2.0237843990325928]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1703932285308838]
[null,null,null,null,null,"Coincident",2.0238540172576904]
[null,null,"Lucinda","Substation Rating","MVA","Non-Coincident",6]
[null,null,null,null,null,"Coincident",5.9000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.874000072479248]
[null,null,null,null,null,"Coincident",0.67000001668930054]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.233604907989502]
[null,null,null,null,null,"Coincident",0.67225366830825806]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.1614000797271729]
[null,null,null,null,null,"Coincident",0.73700004816055298]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.5569655895233154]
[null,null,null,null,null,"Coincident",0.73947906494140625]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.874000072479248]
[null,null,null,null,null,"Coincident",0.67649906873703003]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.233604907989502]
[null,null,null,null,null,"Coincident",0.67877459526062012]
[null,null,"Lyndley Lane","Substation Rating","MVA","Non-Coincident",1.1000000238418579]
[null,null,null,null,null,"Coincident",1.1000000238418579]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.55199998617172241]
[null,null,null,null,null,"Coincident",0.49799999594688416]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.5544438362121582]
[null,null,null,null,null,"Coincident",0.50148278474807739]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.59580671787261963]
[null,null,null,null,null,"Coincident",0.53752130270004272]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.59844452142715454]
[null,null,null,null,null,"Coincident",0.54128044843673706]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.55427974462509155]
[null,null,null,null,null,"Coincident",0.50005674362182617]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.55673366785049438]
[null,null,null,null,null,"Coincident",0.50355392694473267]
[null,null,"Macknade","Substation Rating","MVA","Non-Coincident",13.899999618530273]
[null,null,null,null,null,"Coincident",13.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.6649999618530273]
[null,null,null,null,null,"Coincident",2.6579999923706055]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.7066347599029541]
[null,null,null,null,null,"Coincident",2.8020944595336914]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-1.1770000457763672]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0314998626708984]
[null,null,null,null,null,"Coincident",2.6012783050537109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.0772981643676758]
[null,null,null,null,null,"Coincident",2.7422976493835449]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6649999618530273]
[null,null,null,null,null,"Coincident",2.3982336521148682]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.7066347599029541]
[null,null,null,null,null,"Coincident",2.5282459259033203]
[null,null,"Malchi","Substation Rating","MVA","Non-Coincident",23.799999237060547]
[null,null,null,null,null,"Coincident",23.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.561000823974609]
[null,null,null,null,null,"Coincident",18.929000854492188]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.036026000976563]
[null,null,null,null,null,"Coincident",19.424640655517578]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.349784851074219]
[null,null,null,null,null,"Coincident",17.756917953491211]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.795394897460938]
[null,null,null,null,null,"Coincident",18.221866607666016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.389772415161133]
[null,null,null,null,null,"Coincident",15.860231399536133]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.787786483764648]
[null,null,null,null,null,"Coincident",16.275518417358398]
[null,null,"Mareeba","Substation Rating","MVA","Non-Coincident",54.799999237060547]
[null,null,null,null,null,"Coincident",54.799999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.003000259399414]
[null,null,null,null,null,"Coincident",20.003000259399414]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.007972717285156]
[null,null,null,null,null,"Coincident",20.007972717285156]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.029352188110352]
[null,null,null,null,null,"Coincident",21.029352188110352]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.034580230712891]
[null,null,null,null,null,"Coincident",21.034580230712891]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.689151763916016]
[null,null,null,null,null,"Coincident",19.689151763916016]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.694047927856445]
[null,null,null,null,null,"Coincident",19.694047927856445]
[null,null,"Marian South","Substation Rating","MVA","Non-Coincident",15]
[null,null,null,null,null,"Coincident",15]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.4260001182556152]
[null,null,null,null,null,"Coincident",5.6459999084472656]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.4531002044677734]
[null,null,null,null,null,"Coincident",5.6887373924255371]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-08"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.1686000823974609]
[null,null,null,null,null,"Coincident",6.2105998992919922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.1984100341796875]
[null,null,null,null,null,"Coincident",6.2576112747192383]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4260001182556152]
[null,null,null,null,null,"Coincident",5.6459999084472656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.4531002044677734]
[null,null,null,null,null,"Coincident",5.6887373924255371]
[null,null,"Maryborough City","Substation Rating","MVA","Non-Coincident",39.599998474121094]
[null,null,null,null,null,"Coincident",39.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.133000373840332]
[null,null,null,null,null,"Coincident",12.217000007629395]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.177943229675293]
[null,null,null,null,null,"Coincident",12.228232383728027]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-2.255000114440918]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.061063766479492]
[null,null,null,null,null,"Coincident",12.154815673828125]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.105777740478516]
[null,null,null,null,null,"Coincident",12.165990829467773]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.00419807434082]
[null,null,null,null,null,"Coincident",11.241228103637695]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.045551300048828]
[null,null,null,null,null,"Coincident",11.251564025878906]
[null,null,"Max Fulton","Substation Rating","MVA","Non-Coincident",76.300003051757813]
[null,null,null,null,null,"Coincident",76.300003051757813]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.380000114440918]
[null,null,null,null,null,"Coincident",10.510000228881836]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.109781265258789]
[null,null,null,null,null,"Coincident",10.804171562194824]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.050996780395508]
[null,null,null,null,null,"Coincident",11.079643249511719]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.820332527160645]
[null,null,null,null,null,"Coincident",11.389758110046387]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.317728996276855]
[null,null,null,null,null,"Coincident",10.457135200500488]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.043839454650879]
[null,null,null,null,null,"Coincident",10.749826431274414]
[null,null,"McKinley Creek","Substation Rating","MVA","Non-Coincident",15.100000381469727]
[null,null,null,null,null,"Coincident",15.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.5799999237060547]
[null,null,null,null,null,"Coincident",3.255000114440918]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.6882474422454834]
[null,null,null,null,null,"Coincident",3.3405129909515381]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5521116256713867]
[null,null,null,null,null,"Coincident",3.2296435832977295]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.6595158576965332]
[null,null,null,null,null,"Coincident",3.3144903182983398]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.270866870880127]
[null,null,null,null,null,"Coincident",2.973930835723877]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3697671890258789]
[null,null,null,null,null,"Coincident",3.0520596504211426]
[null,null,"Meadowvale","Substation Rating","MVA","Non-Coincident",14]
[null,null,null,null,null,"Coincident",14]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.390000343322754]
[null,null,null,null,null,"Coincident",10.274999618530273]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.430917739868164]
[null,null,null,null,null,"Coincident",10.305478096008301]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.513745307922363]
[null,null,null,null,null,"Coincident",10.397374153137207]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.555150032043457]
[null,null,null,null,null,"Coincident",10.428215980529785]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.6762075424194336]
[null,null,null,null,null,"Coincident",9.5691070556640625]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.7143135070800781]
[null,null,null,null,null,"Coincident",9.5974912643432617]
[null,null,"Meandarra","Substation Rating","MVA","Non-Coincident",1]
[null,null,null,null,null,"Coincident",1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.86900001764297485]
[null,null,null,null,null,"Coincident",0.84200000762939453]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.86905753612518311]
[null,null,null,null,null,"Coincident",0.84205937385559082]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.80872613191604614]
[null,null,null,null,null,"Coincident",0.78359889984130859]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.80877971649169922]
[null,null,null,null,null,"Coincident",0.78365409374237061]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.74209129810333252]
[null,null,null,null,null,"Coincident",0.71903437376022339]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.74214041233062744]
[null,null,null,null,null,"Coincident",0.71908503770828247]
[null,null,"Melrose","Substation Rating","MVA","Non-Coincident",5.6999998092651367]
[null,null,null,null,null,"Coincident",4.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5839999914169312]
[null,null,null,null,null,"Coincident",1.5700000524520874]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.835821270942688]
[null,null,null,null,null,"Coincident",1.821216344833374]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-22"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5998399257659912]
[null,null,null,null,null,"Coincident",1.5857000350952148]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8541795015335083]
[null,null,null,null,null,"Coincident",1.8394285440444946]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5966720581054687]
[null,null,null,null,null,"Coincident",1.5825600624084473]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8505078554153442]
[null,null,null,null,null,"Coincident",1.8357861042022705]
[null,null,"Merinda","Substation Rating","MVA","Non-Coincident",8.3000001907348633]
[null,null,null,null,null,"Coincident",6.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.815000057220459]
[null,null,null,null,null,"Coincident",1.7419999837875366]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.5125384330749512]
[null,null,null,null,null,"Coincident",1.8443969488143921]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.2965002059936523]
[null,null,null,null,null,"Coincident",1.9162000417709351]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0637922286987305]
[null,null,null,null,null,"Coincident",2.028836727142334]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1640872955322266]
[null,null,null,null,null,"Coincident",1.7419999837875366]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.9121975898742676]
[null,null,null,null,null,"Coincident",1.8443969488143921]
[null,null,"Meringandan","Substation Rating","MVA","Non-Coincident",18.5]
[null,null,null,null,null,"Coincident",16.899999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.9739999771118164]
[null,null,null,null,null,"Coincident",7.3579998016357422]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.9983243942260742]
[null,null,null,null,null,"Coincident",7.4412541389465332]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.504018783569336]
[null,null,null,null,null,"Coincident",7.2045855522155762]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.529635429382324]
[null,null,null,null,null,"Coincident",7.2861042022705078]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9777908325195312]
[null,null,null,null,null,"Coincident",6.7121148109436035]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.002123832702637]
[null,null,null,null,null,"Coincident",6.7880606651306152]
[null,null,"Middlemount","Substation Rating","MVA","Non-Coincident",12.5]
[null,null,null,null,null,"Coincident",12.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.9899997711181641]
[null,null,null,null,null,"Coincident",3.687000036239624]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.0395560264587402]
[null,null,null,null,null,"Coincident",3.7506418228149414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.7450904846191406]
[null,null,null,null,null,"Coincident",3.5060420036315918]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.7922143936157227]
[null,null,null,null,null,"Coincident",3.5665602684020996]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.4460897445678711]
[null,null,null,null,null,"Coincident",3.2851171493530273]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.4902443885803223]
[null,null,null,null,null,"Coincident",3.3418219089508057]
[null,null,"Miles","Substation Rating","MVA","Non-Coincident",8.1000003814697266]
[null,null,null,null,null,"Coincident",8.1000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3589999675750732]
[null,null,null,null,null,"Coincident",2.1319999694824219]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4195711612701416]
[null,null,null,null,null,"Coincident",2.1823334693908691]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2828986644744873]
[null,null,null,null,null,"Coincident",2.0632216930389404]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3415157794952393]
[null,null,null,null,null,"Coincident",2.111931324005127]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1168015003204346]
[null,null,null,null,null,"Coincident",1.9131075143814087]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1711537837982178]
[null,null,null,null,null,"Coincident",1.9582732915878296]
[null,null,"Miles-Condamine","Substation Rating","MVA","Non-Coincident",0.80000001192092896]
[null,null,null,null,null,"Coincident",0.80000001192092896]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.68699997663497925]
[null,null,null,null,null,"Coincident",0.6029999852180481]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.69236189126968384]
[null,null,null,null,null,"Coincident",0.60841596126556396]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.70346736907958984]
[null,null,null,null,null,"Coincident",0.61745387315750122]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.70895779132843018]
[null,null,null,null,null,"Coincident",0.62299966812133789]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.6440693736076355]
[null,null,null,null,null,"Coincident",0.5653185248374939]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.64909619092941284]
[null,null,null,null,null,"Coincident",0.5703960657119751]
[null,null,"Millaroo","Substation Rating","MVA","Non-Coincident",5.5999999046325684]
[null,null,null,null,null,"Coincident",5.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.934999942779541]
[null,null,null,null,null,"Coincident",1.6629999876022339]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2145323753356934]
[null,null,null,null,null,"Coincident",1.8861783742904663]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1284999847412109]
[null,null,null,null,null,"Coincident",1.8293000459671021]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4359855651855469]
[null,null,null,null,null,"Coincident",2.074796199798584]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.934999942779541]
[null,null,null,null,null,"Coincident",1.6629999876022339]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2145323753356934]
[null,null,null,null,null,"Coincident",1.8861783742904663]
[null,null,"Millchester","Substation Rating","MVA","Non-Coincident",10.600000381469727]
[null,null,null,null,null,"Coincident",10.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1589999198913574]
[null,null,null,null,null,"Coincident",4.5430002212524414]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3695812225341797]
[null,null,null,null,null,"Coincident",4.6814260482788086]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.0715031623840332]
[null,null,null,null,null,"Coincident",4.4659509658813477]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.2785129547119141]
[null,null,null,null,null,"Coincident",4.6020288467407227]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.7130045890808105]
[null,null,null,null,null,"Coincident",4.1502580642700195]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.9053812026977539]
[null,null,null,null,null,"Coincident",4.2767167091369629]
[null,null,"Millmerran","Substation Rating","MVA","Non-Coincident",7.5999999046325684]
[null,null,null,null,null,"Coincident",7.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9000000953674316]
[null,null,null,null,null,"Coincident",3.4909999370574951]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9776279926300049]
[null,null,null,null,null,"Coincident",3.6406276226043701]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-17"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2899999618530273]
[null,null,null,null,null,"Coincident",3.8401000499725342]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3753910064697266]
[null,null,null,null,null,"Coincident",4.0046906471252441]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2120003700256348]
[null,null,null,null,null,"Coincident",3.770280122756958]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.2958383560180664]
[null,null,null,null,null,"Coincident",3.9318780899047852]
[null,null,"Mingela","Substation Rating","MVA","Non-Coincident",0.30000001192092896]
[null,null,null,null,null,"Coincident",0.30000001192092896]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.21249997615814209]
[null,null,null,null,null,"Coincident",-8.250001072883606E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.24999995529651642]
[null,null,null,null,null,"Coincident",-0.13142462074756622]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-25"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.23374998569488525]
[null,null,null,null,null,"Coincident",-9.0750016272068024E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.2749999463558197]
[null,null,null,null,null,"Coincident",-0.1445670872926712]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.21249997615814209]
[null,null,null,null,null,"Coincident",-8.250001072883606E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.24999995529651642]
[null,null,null,null,null,"Coincident",-0.13142462074756622]
[null,null,"Mirani","Substation Rating","MVA","Non-Coincident",6.0999999046325684]
[null,null,null,null,null,"Coincident",6.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.0819997787475586]
[null,null,null,null,null,"Coincident",2.7539999485015869]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.2782802581787109]
[null,null,null,null,null,"Coincident",2.7976024150848389]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2860994338989258]
[null,null,null,null,null,"Coincident",2.8916997909545898]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.4921941757202148]
[null,null,null,null,null,"Coincident",2.9374823570251465]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6737997531890869]
[null,null,null,null,null,"Coincident",2.4785997867584229]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.850452184677124]
[null,null,null,null,null,"Coincident",2.5178420543670654]
[null,null,"Miriam Vale","Substation Rating","MVA","Non-Coincident",9.1000003814697266]
[null,null,null,null,null,"Coincident",9.1000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0889999866485596]
[null,null,null,null,null,"Coincident",2.0889999866485596]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1002404689788818]
[null,null,null,null,null,"Coincident",2.1002404689788818]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1934499740600586]
[null,null,null,null,null,"Coincident",2.1934499740600586]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2052524089813232]
[null,null,null,null,null,"Coincident",2.2052524089813232]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0889999866485596]
[null,null,null,null,null,"Coincident",2.0889999866485596]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1002404689788818]
[null,null,null,null,null,"Coincident",2.1002404689788818]
[null,null,"Mitchell","Substation Rating","MVA","Non-Coincident",2.2999999523162842]
[null,null,null,null,null,"Coincident",2.2999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9199999570846558]
[null,null,null,null,null,"Coincident",1.7039999961853027]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1251637935638428]
[null,null,null,null,null,"Coincident",1.7639591693878174]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9108799695968628]
[null,null,null,null,null,"Coincident",1.6959059238433838]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.1150691509246826]
[null,null,null,null,null,"Coincident",1.7555803060531616]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7457791566848755]
[null,null,null,null,null,"Coincident",1.5493789911270142]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9323264360427856]
[null,null,null,null,null,"Coincident",1.6038974523544312]
[null,null,"Mona Park","Substation Rating","MVA","Non-Coincident",7.5999999046325684]
[null,null,null,null,null,"Coincident",7.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.745999813079834]
[null,null,null,null,null,"Coincident",5.2389998435974121]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.861414909362793]
[null,null,null,null,null,"Coincident",6.1462926864624023]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.3206000328063965]
[null,null,null,null,null,"Coincident",5.7628998756408691]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.5475564002990723]
[null,null,null,null,null,"Coincident",6.7609219551086426]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.2056798934936523]
[null,null,null,null,null,"Coincident",5.6581201553344727]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.4103283882141113]
[null,null,null,null,null,"Coincident",6.6379961967468262]
[null,null,"Monduran Dam","Substation Rating","MVA","Non-Coincident",1.5]
[null,null,null,null,null,"Coincident",1.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.22400000691413879]
[null,null,null,null,null,"Coincident",0.19300000369548798]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.22437691688537598]
[null,null,null,null,null,"Coincident",0.19350710511207581]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-07-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.24640001356601715]
[null,null,null,null,null,"Coincident",0.1938125342130661]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.24681460857391357]
[null,null,null,null,null,"Coincident",0.19432176649570465]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.2331324964761734]
[null,null,null,null,null,"Coincident",0.18048781156539917]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.23352476954460144]
[null,null,null,null,null,"Coincident",0.18096204102039337]
[null,null,"Monduran Dam DNR","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6299999952316284]
[null,null,null,null,null,"Coincident",0.77399998903274536]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0006248950958252]
[null,null,null,null,null,"Coincident",0.96242403984069824]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6462999582290649]
[null,null,null,null,null,"Coincident",0.78174000978469849]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0206310749053955]
[null,null,null,null,null,"Coincident",0.97204828262329102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6430400609970093]
[null,null,null,null,null,"Coincident",0.78019201755523682]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0166299343109131]
[null,null,null,null,null,"Coincident",0.97012346982955933]
[null,null,"Monto","Substation Rating","MVA","Non-Coincident",14]
[null,null,null,null,null,"Coincident",14]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9619998931884766]
[null,null,null,null,null,"Coincident",3.3320000171661377]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9625663757324219]
[null,null,null,null,null,"Coincident",3.3468565940856934]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-27"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3582000732421875]
[null,null,null,null,null,"Coincident",3.6651999950408936]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.358823299407959]
[null,null,null,null,null,"Coincident",3.6815423965454102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.0412397384643555]
[null,null,null,null,null,"Coincident",3.3986399173736572]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.0418176651000977]
[null,null,null,null,null,"Coincident",3.4137935638427734]
[null,null,"Moore","Substation Rating","MVA","Non-Coincident",4.4000000953674316]
[null,null,null,null,null,"Coincident",4.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6019999980926514]
[null,null,null,null,null,"Coincident",4.0000001899898052E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9628183841705322]
[null,null,null,null,null,"Coincident",5.6568547151982784E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.6280200481414795]
[null,null,null,null,null,"Coincident",4.0400000289082527E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.9924464225769043]
[null,null,null,null,null,"Coincident",5.7134232483804226E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6228160858154297]
[null,null,null,null,null,"Coincident",4.0320004336535931E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9865210056304932]
[null,null,null,null,null,"Coincident",5.7021095417439938E-3]
[null,null,"Moorvale","Substation Rating","MVA","Non-Coincident",10.5]
[null,null,null,null,null,"Coincident",10.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.5789999961853027]
[null,null,null,null,null,"Coincident",4.8270001411437988]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.7388381958007812]
[null,null,null,null,null,"Coincident",4.9720010757446289]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.6347899436950684]
[null,null,null,null,null,"Coincident",4.875269889831543]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.7962265014648437]
[null,null,null,null,null,"Coincident",5.0217208862304687]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.6236319541931152]
[null,null,null,null,null,"Coincident",4.8656163215637207]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.7847490310668945]
[null,null,null,null,null,"Coincident",5.011777400970459]
[null,null,"Moranbah Skid J","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.9510002136230469]
[null,null,null,null,null,"Coincident",4.7859997749328613]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.0316605567932129]
[null,null,null,null,null,"Coincident",5.3460001945495605]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.2290401458740234]
[null,null,null,null,null,"Coincident",4.9774394035339355]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.3129267692565918]
[null,null,null,null,null,"Coincident",5.559840202331543]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.9510002136230469]
[null,null,null,null,null,"Coincident",4.7859997749328613]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.0316605567932129]
[null,null,null,null,null,"Coincident",5.3460001945495605]
[null,null,"Mossman","Substation Rating","MVA","Non-Coincident",18.5]
[null,null,null,null,null,"Coincident",18.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.2150001525878906]
[null,null,null,null,null,"Coincident",6.3930001258850098]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.2775359153747559]
[null,null,null,null,null,"Coincident",6.4835829734802246]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-3.3499999046325684]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.3828210830688477]
[null,null,null,null,null,"Coincident",6.5417013168334961]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.4468111991882324]
[null,null,null,null,null,"Coincident",6.6343913078308105]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.0366454124450684]
[null,null,null,null,null,"Coincident",6.2349648475646973]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.0976352691650391]
[null,null,null,null,null,"Coincident",6.3233089447021484]
[null,null,"Mount Fox","Substation Rating","MVA","Non-Coincident",0.69999998807907104]
[null,null,null,null,null,"Coincident",0.69999998807907104]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.8999998271465302E-2]
[null,null,null,null,null,"Coincident",4.3999999761581421E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.2377180457115173E-2]
[null,null,null,null,null,"Coincident",5.946427583694458E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.590000331401825E-2]
[null,null,null,null,null,"Coincident",4.8399999737739563E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.061489999294281E-2]
[null,null,null,null,null,"Coincident",6.5410703420639038E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.8999998271465302E-2]
[null,null,null,null,null,"Coincident",4.3999999761581421E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.2377180457115173E-2]
[null,null,null,null,null,"Coincident",5.946427583694458E-2]
[null,null,"Mount Leyshon","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.34799998998641968]
[null,null,null,null,null,"Coincident",9.9999997764825821E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.41935664415359497]
[null,null,null,null,null,"Coincident",1.166190393269062E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.35147997736930847]
[null,null,null,null,null,"Coincident",1.0099999606609344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.42355021834373474]
[null,null,null,null,null,"Coincident",1.1778523214161396E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.35078400373458862]
[null,null,null,null,null,"Coincident",1.0080000385642052E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.42271149158477783]
[null,null,null,null,null,"Coincident",1.1755199171602726E-2]
[null,null,"Mount Leyshon Pump","Substation Rating","MVA","Non-Coincident",0.60000002384185791]
[null,null,null,null,null,"Coincident",0.60000002384185791]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.000000074505806E-2]
[null,null,null,null,null,"Coincident",5.000000074505806E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.0975611209869385E-2]
[null,null,null,null,null,"Coincident",6.0975611209869385E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1999997347593307E-2]
[null,null,null,null,null,"Coincident",5.1999997347593307E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.3414633274078369E-2]
[null,null,null,null,null,"Coincident",6.3414633274078369E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.000000074505806E-2]
[null,null,null,null,null,"Coincident",5.000000074505806E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.0975611209869385E-2]
[null,null,null,null,null,"Coincident",6.0975611209869385E-2]
[null,null,"Mount Rooper","Substation Rating","MVA","Non-Coincident",5.8000001907348633]
[null,null,null,null,null,"Coincident",5.8000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.40000000596046448]
[null,null,null,null,null,"Coincident",0.35400000214576721]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.41329893469810486]
[null,null,null,null,null,"Coincident",0.36382964253425598]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-04"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.4400000274181366]
[null,null,null,null,null,"Coincident",0.38940000534057617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.45462882518768311]
[null,null,null,null,null,"Coincident",0.4002126157283783]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.41999998688697815]
[null,null,null,null,null,"Coincident",0.3716999888420105]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.43396386504173279]
[null,null,null,null,null,"Coincident",0.38202109932899475]
[null,null,"Moura","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.008000373840332]
[null,null,null,null,null,"Coincident",7.620999813079834]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.2559413909912109]
[null,null,null,null,null,"Coincident",7.7406959533691406]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.8824291229248047]
[null,null,null,null,null,"Coincident",7.514763355255127]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.1269140243530273]
[null,null,null,null,null,"Coincident",7.6327910423278809]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.1308012008666992]
[null,null,null,null,null,"Coincident",6.8788671493530273]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.3545980453491211]
[null,null,null,null,null,"Coincident",6.9869070053100586]
[null,null,"Mt Bassett","Substation Rating","MVA","Non-Coincident",39]
[null,null,null,null,null,"Coincident",39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.864999771118164]
[null,null,null,null,null,"Coincident",10.364999771118164]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.143553733825684]
[null,null,null,null,null,"Coincident",10.679826736450195]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.740921020507813]
[null,null,null,null,null,"Coincident",10.246631622314453]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.016294479370117]
[null,null,null,null,null,"Coincident",10.557863235473633]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.099452018737793]
[null,null,null,null,null,"Coincident",9.6346817016601562]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.358378410339355]
[null,null,null,null,null,"Coincident",9.9273262023925781]
[null,null,"Mt Garnet","Substation Rating","MVA","Non-Coincident",9.3000001907348633]
[null,null,null,null,null,"Coincident",8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6759999990463257]
[null,null,null,null,null,"Coincident",1.0039999485015869]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7278240919113159]
[null,null,null,null,null,"Coincident",1.0295629501342773]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-17"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8436000347137451]
[null,null,null,null,null,"Coincident",1.1043999195098877]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9006065130233765]
[null,null,null,null,null,"Coincident",1.1325192451477051]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6759999990463257]
[null,null,null,null,null,"Coincident",1.0843199491500854]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.7278240919113159]
[null,null,null,null,null,"Coincident",1.1119279861450195]
[null,null,"Mt Molloy","Substation Rating","MVA","Non-Coincident",18]
[null,null,null,null,null,"Coincident",16.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0379999876022339]
[null,null,null,null,null,"Coincident",0.88200002908706665]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0389750003814697]
[null,null,null,null,null,"Coincident",0.88562071323394775]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0530718564987183]
[null,null,null,null,null,"Coincident",0.92886954545974731]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0540609359741211]
[null,null,null,null,null,"Coincident",0.93268263339996338]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0296752452850342]
[null,null,null,null,null,"Coincident",0.88200002908706665]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0306423902511597]
[null,null,null,null,null,"Coincident",0.88562071323394775]
[null,null,"Mt Morgan","Substation Rating","MVA","Non-Coincident",15.800000190734863]
[null,null,null,null,null,"Coincident",15.800000190734863]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.312999963760376]
[null,null,null,null,null,"Coincident",3.2579998970031738]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.4484515190124512]
[null,null,null,null,null,"Coincident",3.3870398998260498]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.1266438961029053]
[null,null,null,null,null,"Coincident",3.074737548828125]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.2544763088226318]
[null,null,null,null,null,"Coincident",3.1965188980102539]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8994712829589844]
[null,null,null,null,null,"Coincident",2.8513364791870117]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.0180158615112305]
[null,null,null,null,null,"Coincident",2.9642696380615234]
[null,null,"Mt Mowbullan","Substation Rating","MVA","Non-Coincident",1]
[null,null,null,null,null,"Coincident",1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.68900001049041748]
[null,null,null,null,null,"Coincident",0.38199999928474426]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.69621908664703369]
[null,null,null,null,null,"Coincident",0.38668334484100342]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-24"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.75789999961853027]
[null,null,null,null,null,"Coincident",0.39783006906509399]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.76584100723266602]
[null,null,null,null,null,"Coincident",0.40270751714706421]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.72619915008544922]
[null,null,null,null,null,"Coincident",0.37695378065109253]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.73380798101425171]
[null,null,null,null,null,"Coincident",0.38157525658607483]
[null,null,"Mt Sibley","Substation Rating","MVA","Non-Coincident",6.3000001907348633]
[null,null,null,null,null,"Coincident",6.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.6469998359680176]
[null,null,null,null,null,"Coincident",3.7260000705718994]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.0414910316467285]
[null,null,null,null,null,"Coincident",4.1182026863098145]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.6505312919616699]
[null,null,null,null,null,"Coincident",3.7288317680358887]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.0453224182128906]
[null,null,null,null,null,"Coincident",4.1213321685791016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2593936920166016]
[null,null,null,null,null,"Coincident",3.4152143001556396]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.6209802627563477]
[null,null,null,null,null,"Coincident",3.7747032642364502]
[null,null,"Mundubbera Town","Substation Rating","MVA","Non-Coincident",49.400001525878906]
[null,null,null,null,null,"Coincident",49.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.809999942779541]
[null,null,null,null,null,"Coincident",4.0120000839233398]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.6625986099243164]
[null,null,null,null,null,"Coincident",4.2811422348022461]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.3910002708435059]
[null,null,null,null,null,"Coincident",4.4132003784179687]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.3288588523864746]
[null,null,null,null,null,"Coincident",4.709256649017334]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.8711209297180176]
[null,null,null,null,null,"Coincident",4.054206371307373]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.7326889038085938]
[null,null,null,null,null,"Coincident",4.3261799812316895]
[null,null,"Murgon","Substation Rating","MVA","Non-Coincident",25]
[null,null,null,null,null,"Coincident",25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.234000205993652]
[null,null,null,null,null,"Coincident",10.340000152587891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.086212158203125]
[null,null,null,null,null,"Coincident",10.827694892883301]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.874787330627441]
[null,null,null,null,null,"Coincident",10.929793357849121]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.775609016418457]
[null,null,null,null,null,"Coincident",11.445306777954102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.903720855712891]
[null,null,null,null,null,"Coincident",10.036004066467285]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.730877876281738]
[null,null,null,null,null,"Coincident",10.509360313415527]
[null,null,"Mutarnee","Substation Rating","MVA","Non-Coincident",1.1000000238418579]
[null,null,null,null,null,"Coincident",1.1000000238418579]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.38100001215934753]
[null,null,null,null,null,"Coincident",0.33899998664855957]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.39441731572151184]
[null,null,null,null,null,"Coincident",0.35372588038444519]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.40982645750045776]
[null,null,null,null,null,"Coincident",0.3646487295627594]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.42425891757011414]
[null,null,null,null,null,"Coincident",0.38048878312110901]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.37206935882568359]
[null,null,null,null,null,"Coincident",0.33105382323265076]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.38517215847969055]
[null,null,null,null,null,"Coincident",0.34543454647064209]
[null,null,"Nanango","Substation Rating","MVA","Non-Coincident",13.699999809265137]
[null,null,null,null,null,"Coincident",13.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.2870001792907715]
[null,null,null,null,null,"Coincident",5.7360000610351562]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.5228071212768555]
[null,null,null,null,null,"Coincident",5.9060430526733398]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.5094342231750488]
[null,null,null,null,null,"Coincident",5.9389395713806152]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.7535839080810547]
[null,null,null,null,null,"Coincident",6.1149988174438477]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.9961633682250977]
[null,null,null,null,null,"Coincident",5.4706525802612305]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.221062183380127]
[null,null,null,null,null,"Coincident",5.6328296661376953]
[null,null,"Nandi","Substation Rating","MVA","Non-Coincident",2]
[null,null,null,null,null,"Coincident",2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4570000171661377]
[null,null,null,null,null,"Coincident",1.2779999971389771]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5877689123153687]
[null,null,null,null,null,"Coincident",1.3782379627227783]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6026999950408936]
[null,null,null,null,null,"Coincident",1.4057999849319458]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.7465457916259766]
[null,null,null,null,null,"Coincident",1.5160617828369141]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5735601186752319]
[null,null,null,null,null,"Coincident",1.3802400827407837]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.7147904634475708]
[null,null,null,null,null,"Coincident",1.4884970188140869]
[null,null,"Nebo","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.1510000228881836]
[null,null,null,null,null,"Coincident",2.1779999732971191]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.1807479858398437]
[null,null,null,null,null,"Coincident",2.1893863677978516]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.1008360385894775]
[null,null,null,null,null,"Coincident",2.1433262825012207]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.130110502243042]
[null,null,null,null,null,"Coincident",2.1545314788818359]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.9333920478820801]
[null,null,null,null,null,"Coincident",2.0275874137878418]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9610855579376221]
[null,null,null,null,null,"Coincident",2.0381875038146973]
[null,null,"Neil Smith","Substation Rating","MVA","Non-Coincident",65.5]
[null,null,null,null,null,"Coincident",65.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.902000427246094]
[null,null,null,null,null,"Coincident",11.197999954223633]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.92017650604248]
[null,null,null,null,null,"Coincident",11.730441093444824]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-16"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.799846649169922]
[null,null,null,null,null,"Coincident",11.872679710388184]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.879367828369141]
[null,null,null,null,null,"Coincident",12.437200546264648]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.027027130126953]
[null,null,null,null,null,"Coincident",11.291950225830078]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.053745269775391]
[null,null,null,null,null,"Coincident",11.828859329223633]
[null,null,"Normanton","Substation Rating","MVA","Non-Coincident",9.5]
[null,null,null,null,null,"Coincident",8.1999998092651367]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.1589999198913574]
[null,null,null,null,null,"Coincident",4.060999870300293]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.2118291854858398]
[null,null,null,null,null,"Coincident",4.0847668647766113]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-06"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3046479225158691]
[null,null,null,null,null,"Coincident",4.2234396934509277]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3593273162841797]
[null,null,null,null,null,"Coincident",4.2481575012207031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.1178674697875977]
[null,null,null,null,null,"Coincident",4.060999870300293]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.1701741218566895]
[null,null,null,null,null,"Coincident",4.0847668647766113]
[null,null,"North Cloncurry","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.0339999198913574]
[null,null,null,null,null,"Coincident",3.7929999828338623]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0689287185668945]
[null,null,null,null,null,"Coincident",3.8119223117828369]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-21"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.9605813026428223]
[null,null,null,null,null,"Coincident",3.7239675521850586]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9948742389678955]
[null,null,null,null,null,"Coincident",3.7425453662872314]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6895768642425537]
[null,null,null,null,null,"Coincident",3.4691536426544189]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.7215235233306885]
[null,null,null,null,null,"Coincident",3.4864602088928223]
[null,null,"North Mackay","Substation Rating","MVA","Non-Coincident",47.700000762939453]
[null,null,null,null,null,"Coincident",47.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.280000686645508]
[null,null,null,null,null,"Coincident",22.280000686645508]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.335954666137695]
[null,null,null,null,null,"Coincident",22.335954666137695]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.290027618408203]
[null,null,null,null,null,"Coincident",22.290027618408203]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.346006393432617]
[null,null,null,null,null,"Coincident",22.346006393432617]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.633508682250977]
[null,null,null,null,null,"Coincident",20.633508682250977]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.685327529907227]
[null,null,null,null,null,"Coincident",20.685327529907227]
[null,null,"North Street","Substation Rating","MVA","Non-Coincident",34.5]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.346000671386719]
[null,null,null,null,null,"Coincident",15.307000160217285]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.609521865844727]
[null,null,null,null,null,"Coincident",15.670577049255371]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.346000671386719]
[null,null,null,null,null,"Coincident",15.949128150939941]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.609521865844727]
[null,null,null,null,null,"Coincident",16.327957153320312]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.378700256347656]
[null,null,null,null,null,"Coincident",14.612062454223633]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.629045486450195]
[null,null,null,null,null,"Coincident",14.959132194519043]
[null,null,"Norwin","Substation Rating","MVA","Non-Coincident",6]
[null,null,null,null,null,"Coincident",6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1549999713897705]
[null,null,null,null,null,"Coincident",1.5659999847412109]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4773592948913574]
[null,null,null,null,null,"Coincident",1.7789580821990967]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3705000877380371]
[null,null,null,null,null,"Coincident",1.722599983215332]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.725095272064209]
[null,null,null,null,null,"Coincident",1.956853985786438]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1549999713897705]
[null,null,null,null,null,"Coincident",1.5659999847412109]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.4773592948913574]
[null,null,null,null,null,"Coincident",1.7789580821990967]
[null,null,"Oakey","Substation Rating","MVA","Non-Coincident",49.700000762939453]
[null,null,null,null,null,"Coincident",49.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.136999130249023]
[null,null,null,null,null,"Coincident",14.357000350952148]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.17192268371582]
[null,null,null,null,null,"Coincident",15.051405906677246]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.683155059814453]
[null,null,null,null,null,"Coincident",14.814558029174805]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.751062393188477]
[null,null,null,null,null,"Coincident",15.531094551086426]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.384513854980469]
[null,null,null,null,null,"Coincident",13.726584434509277]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.373992919921875]
[null,null,null,null,null,"Coincident",14.390498161315918]
[null,null,"Oonoonba","Substation Rating","MVA","Non-Coincident",64]
[null,null,null,null,null,"Coincident",64]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.621000289916992]
[null,null,null,null,null,"Coincident",13.017999649047852]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.810009956359863]
[null,null,null,null,null,"Coincident",13.22929859161377]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-19"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.983100891113281]
[null,null,null,null,null,"Coincident",14.31980037689209]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.191011428833008]
[null,null,null,null,null,"Coincident",14.552228927612305]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.337820053100586]
[null,null,null,null,null,"Coincident",12.747355461120605]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.522900581359863]
[null,null,null,null,null,"Coincident",12.954261779785156]
[null,null,"Owanyilla","Substation Rating","MVA","Non-Coincident",22]
[null,null,null,null,null,"Coincident",22]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.1599998474121094]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.0461621284484863]
[null,null,null,null,null,"Coincident",6.6555237770080566]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.9640350341796875]
[null,null,null,null,null,"Coincident",6.5997624397277832]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.5491876602172852]
[null,null,null,null,null,"Coincident",7.1306619644165039]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.1055150032043457]
[null,null,null,null,null,"Coincident",5.7861495018005371]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.6185307502746582]
[null,null,null,null,null,"Coincident",6.2516002655029297]
[null,null,"Pajingo","Substation Rating","MVA","Non-Coincident",11.600000381469727]
[null,null,null,null,null,"Coincident",10.699999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.815000057220459]
[null,null,null,null,null,"Coincident",5.8439998626708984]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7546262741088867]
[null,null,null,null,null,"Coincident",6.5495176315307617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-16"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.8831501007080078]
[null,null,null,null,null,"Coincident",5.9024395942687988]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.8321723937988281]
[null,null,null,null,null,"Coincident",6.6150126457214355]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.8695201873779297]
[null,null,null,null,null,"Coincident",5.890751838684082]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.8166632652282715]
[null,null,null,null,null,"Coincident",6.6019139289855957]
[null,null,"Pampas","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.5669999122619629]
[null,null,null,null,null,"Coincident",4.4010000228881836]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.6733717918395996]
[null,null,null,null,null,"Coincident",5.0394272804260254]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.5669999122619629]
[null,null,null,null,null,"Coincident",4.8411002159118652]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.6733717918395996]
[null,null,null,null,null,"Coincident",5.543370246887207]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.2886500358581543]
[null,null,null,null,null,"Coincident",4.7530803680419922]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.3397030830383301]
[null,null,null,null,null,"Coincident",5.4425816535949707]
[null,null,"Pandoin","Substation Rating","MVA","Non-Coincident",23.200000762939453]
[null,null,null,null,null,"Coincident",23.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.100000381469727]
[null,null,null,null,null,"Coincident",8.8420000076293945]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.441861152648926]
[null,null,null,null,null,"Coincident",8.9727163314819336]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.874337196350098]
[null,null,null,null,null,"Coincident",8.6622419357299805]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.209247589111328]
[null,null,null,null,null,"Coincident",8.7903013229370117]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.055046081542969]
[null,null,null,null,null,"Coincident",8.0096139907836914]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.364724159240723]
[null,null,null,null,null,"Coincident",8.1280250549316406]
[null,null,"Parkhurst","Substation Rating","MVA","Non-Coincident",48.299999237060547]
[null,null,null,null,null,"Coincident",48.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.590999603271484]
[null,null,null,null,null,"Coincident",13.576000213623047]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.645853996276855]
[null,null,null,null,null,"Coincident",13.634623527526855]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.041572570800781]
[null,null,null,null,null,"Coincident",13.09758186340332]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.094493865966797]
[null,null,null,null,null,"Coincident",13.154139518737793]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.718988418579102]
[null,null,null,null,null,"Coincident",11.945930480957031]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.767256736755371]
[null,null,null,null,null,"Coincident",11.997514724731445]
[null,null,"Peranga","Substation Rating","MVA","Non-Coincident",5.0999999046325684]
[null,null,null,null,null,"Coincident",3.7999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.465999960899353]
[null,null,null,null,null,"Coincident",0.99099999666213989]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.6359193325042725]
[null,null,null,null,null,"Coincident",1.0686819553375244]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-06"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5056846141815186]
[null,null,null,null,null,"Coincident",1.0901000499725342]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6802037954330444]
[null,null,null,null,null,"Coincident",1.1755502223968506]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4523954391479492]
[null,null,null,null,null,"Coincident",0.99099999666213989]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6207379102706909]
[null,null,null,null,null,"Coincident",1.0686819553375244]
[null,null,"Perseverance Creek","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.621999979019165]
[null,null,null,null,null,"Coincident",4.0000001899898052E-3]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8330848217010498]
[null,null,null,null,null,"Coincident",4.0000001899898052E-3]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-03-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.638219952583313]
[null,null,null,null,null,"Coincident",4.0400000289082527E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8514156341552734]
[null,null,null,null,null,"Coincident",4.0400000289082527E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6349760293960571]
[null,null,null,null,null,"Coincident",4.0320004336535931E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8477494716644287]
[null,null,null,null,null,"Coincident",4.0320004336535931E-3]
[null,null,"Peter Arlett","Substation Rating","MVA","Non-Coincident",70]
[null,null,null,null,null,"Coincident",70]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.225000381469727]
[null,null,null,null,null,"Coincident",20.216999053955078]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.817495346069336]
[null,null,null,null,null,"Coincident",20.75590705871582]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.110507965087891]
[null,null,null,null,null,"Coincident",21.060453414916992]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.72772216796875]
[null,null,null,null,null,"Coincident",21.621843338012695]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.663387298583984]
[null,null,null,null,null,"Coincident",19.682058334350586]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",21.240203857421875]
[null,null,null,null,null,"Coincident",20.206705093383789]
[null,null,"Pialba","Substation Rating","MVA","Non-Coincident",33.200000762939453]
[null,null,null,null,null,"Coincident",33.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.701999664306641]
[null,null,null,null,null,"Coincident",13.25100040435791]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.024652481079102]
[null,null,null,null,null,"Coincident",13.478690147399902]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-0.27300000190734863]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.921779632568359]
[null,null,null,null,null,"Coincident",13.463545799255371]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.249607086181641]
[null,null,null,null,null,"Coincident",13.694888114929199]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.17036247253418]
[null,null,null,null,null,"Coincident",12.736861228942871]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.480496406555176]
[null,null,null,null,null,"Coincident",12.955717086791992]
[null,null,"Pinnacle","Substation Rating","MVA","Non-Coincident",11]
[null,null,null,null,null,"Coincident",11]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2950000762939453]
[null,null,null,null,null,"Coincident",1.8789999485015869]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.5525496006011963]
[null,null,null,null,null,"Coincident",1.9266854524612427]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5409059524536133]
[null,null,null,null,null,"Coincident",2.0192296504974365]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.8176765441894531]
[null,null,null,null,null,"Coincident",2.0704741477966309]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.120826244354248]
[null,null,null,null,null,"Coincident",1.7796759605407715]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.3647618293762207]
[null,null,null,null,null,"Coincident",1.824840784072876]
[null,null,"Pirrinuan","Substation Rating","MVA","Non-Coincident",2.5]
[null,null,null,null,null,"Coincident",2.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.87999999523162842]
[null,null,null,null,null,"Coincident",0.73900002241134644]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.10481858253479]
[null,null,null,null,null,"Coincident",1.1384538412094116]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.88173365592956543]
[null,null,null,null,null,"Coincident",0.74045586585998535]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1069951057434082]
[null,null,null,null,null,"Coincident",1.14069664478302]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.82624959945678711]
[null,null,null,null,null,"Coincident",0.69386190176010132]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0373362302780151]
[null,null,null,null,null,"Coincident",1.0689171552658081]
[null,null,"Planella","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.593999862670898]
[null,null,null,null,null,"Coincident",15.593999862670898]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.683380126953125]
[null,null,null,null,null,"Coincident",15.683380126953125]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.191095352172852]
[null,null,null,null,null,"Coincident",16.191095352172852]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.283897399902344]
[null,null,null,null,null,"Coincident",16.283897399902344]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.926733016967773]
[null,null,null,null,null,"Coincident",14.926733016967773]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.012288093566895]
[null,null,null,null,null,"Coincident",15.012288093566895]
[null,null,"Pleystowe","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.5789999961853027]
[null,null,null,null,null,"Coincident",6.6669998168945313]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.8263368606567383]
[null,null,null,null,null,"Coincident",6.7807855606079102]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3147687911987305]
[null,null,null,null,null,"Coincident",7.3142318725585938]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.5861177444458008]
[null,null,null,null,null,"Coincident",7.4390640258789062]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3875546455383301]
[null,null,null,null,null,"Coincident",6.498591423034668]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.6286439895629883]
[null,null,null,null,null,"Coincident",6.6095032691955566]
[null,null,"Point Vernon","Substation Rating","MVA","Non-Coincident",84.599998474121094]
[null,null,null,null,null,"Coincident",84.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.63599967956543]
[null,null,null,null,null,"Coincident",19.618000030517578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.661439895629883]
[null,null,null,null,null,"Coincident",19.618309020996094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.810787200927734]
[null,null,null,null,null,"Coincident",19.78416633605957]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.836442947387695]
[null,null,null,null,null,"Coincident",19.784477233886719]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.521244049072266]
[null,null,null,null,null,"Coincident",18.558235168457031]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.545309066772461]
[null,null,null,null,null,"Coincident",18.558528900146484]
[null,null,"Pozieres","Substation Rating","MVA","Non-Coincident",7.0999999046325684]
[null,null,null,null,null,"Coincident",7.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.4960000514984131]
[null,null,null,null,null,"Coincident",3.0499999523162842]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0182557106018066]
[null,null,null,null,null,"Coincident",3.4276225566864014]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4364981651306152]
[null,null,null,null,null,"Coincident",2.998089075088501]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9498651027679443]
[null,null,null,null,null,"Coincident",3.3692843914031982]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2169842720031738]
[null,null,null,null,null,"Coincident",2.8065793514251709]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.6975586414337158]
[null,null,null,null,null,"Coincident",3.1540639400482178]
[null,null,"Proserpine Mill","Substation Rating","MVA","Non-Coincident",14.399999618530273]
[null,null,null,null,null,"Coincident",14.399999618530273]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.8280000686645508]
[null,null,null,null,null,"Coincident",1.2400000095367432]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9214520454406738]
[null,null,null,null,null,"Coincident",1.3366379737854004]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-08"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-7.2160000801086426]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.8662800788879395]
[null,null,null,null,null,"Coincident",1.2524000406265259]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9606664180755615]
[null,null,null,null,null,"Coincident",1.3500043153762817]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.8586242198944092]
[null,null,null,null,null,"Coincident",1.2499200105667114]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9528236389160156]
[null,null,null,null,null,"Coincident",1.3473310470581055]
[null,null,"Proston","Substation Rating","MVA","Non-Coincident",5.4000000953674316]
[null,null,null,null,null,"Coincident",5.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.340999960899353]
[null,null,null,null,null,"Coincident",1.3250000476837158]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3940738439559937]
[null,null,null,null,null,"Coincident",1.3524297475814819]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4031956195831299]
[null,null,null,null,null,"Coincident",1.3864536285400391]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4587310552597046]
[null,null,null,null,null,"Coincident",1.4151555299758911]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3086282014846802]
[null,null,null,null,null,"Coincident",1.2930145263671875]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3604209423065186]
[null,null,null,null,null,"Coincident",1.3197821378707886]
[null,null,"Purrawunda","Substation Rating","MVA","Non-Coincident",14]
[null,null,null,null,null,"Coincident",14]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.7090001106262207]
[null,null,null,null,null,"Coincident",6.2880001068115234]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.7131147384643555]
[null,null,null,null,null,"Coincident",6.3056154251098633]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.3799004554748535]
[null,null,null,null,null,"Coincident",6.9168004989624023]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.3844265937805176]
[null,null,null,null,null,"Coincident",6.9361772537231445]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.245720386505127]
[null,null,null,null,null,"Coincident",6.7910404205322266]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2501640319824219]
[null,null,null,null,null,"Coincident",6.8100647926330566]
[null,null,"Quilpie","Substation Rating","MVA","Non-Coincident",6]
[null,null,null,null,null,"Coincident",6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2750000953674316]
[null,null,null,null,null,"Coincident",2.0369999408721924]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.3104186058044434]
[null,null,null,null,null,"Coincident",2.0852541923522949]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3979637622833252]
[null,null,null,null,null,"Coincident",2.1470997333526611]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4352967739105225]
[null,null,null,null,null,"Coincident",2.1979620456695557]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2176699638366699]
[null,null,null,null,null,"Coincident",1.9856674671173096]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2521960735321045]
[null,null,null,null,null,"Coincident",2.0327057838439941]
[null,null,"Raglan","Substation Rating","MVA","Non-Coincident",12.5]
[null,null,null,null,null,"Coincident",12.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.8210000991821289]
[null,null,null,null,null,"Coincident",3.437000036239624]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.8801631927490234]
[null,null,null,null,null,"Coincident",3.5003626346588135]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.7435867786407471]
[null,null,null,null,null,"Coincident",3.3673665523529053]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.8015511035919189]
[null,null,null,null,null,"Coincident",3.4294452667236328]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.5110023021697998]
[null,null,null,null,null,"Coincident",3.158156156539917]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5653655529022217]
[null,null,null,null,null,"Coincident",3.2163782119750977]
[null,null,"Rasmussen","Substation Rating","MVA","Non-Coincident",80.400001525878906]
[null,null,null,null,null,"Coincident",80.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.982999801635742]
[null,null,null,null,null,"Coincident",16.180999755859375]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.993173599243164]
[null,null,null,null,null,"Coincident",16.187507629394531]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-18"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.781299591064453]
[null,null,null,null,null,"Coincident",17.799100875854492]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.792491912841797]
[null,null,null,null,null,"Coincident",17.806259155273438]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.421211242675781]
[null,null,null,null,null,"Coincident",15.675505638122559]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.431066513061523]
[null,null,null,null,null,"Coincident",15.68181037902832]
[null,null,"Ravenshoe","Substation Rating","MVA","Non-Coincident",22.299999237060547]
[null,null,null,null,null,"Coincident",19.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3610000610351562]
[null,null,null,null,null,"Coincident",1.9079999923706055]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6385612487792969]
[null,null,null,null,null,"Coincident",1.9526108503341675]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-11.897000312805176]
[null,null,null,null,null,"Coincident",-0.22100000083446503]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5652737617492676]
[null,null,null,null,null,"Coincident",2.0987999439239502]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.866849422454834]
[null,null,null,null,null,"Coincident",2.1478719711303711]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4620742797851562]
[null,null,null,null,null,"Coincident",1.9079999923706055]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7515180110931396]
[null,null,null,null,null,"Coincident",1.9526108503341675]
[null,null,"Ravenswood","Substation Rating","MVA","Non-Coincident",2.5]
[null,null,null,null,null,"Coincident",2.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1979999542236328]
[null,null,null,null,null,"Coincident",0.53600001335144043]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2547242641448975]
[null,null,null,null,null,"Coincident",0.54333877563476563]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3177999258041382]
[null,null,null,null,null,"Coincident",0.58960002660751343]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3801966905593872]
[null,null,null,null,null,"Coincident",0.59767264127731323]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1979999542236328]
[null,null,null,null,null,"Coincident",0.53600001335144043]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2547242641448975]
[null,null,null,null,null,"Coincident",0.54333877563476563]
[null,null,"Richmond","Substation Rating","MVA","Non-Coincident",14.600000381469727]
[null,null,null,null,null,"Coincident",14.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2149999141693115]
[null,null,null,null,null,"Coincident",1.9789999723434448]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2206993103027344]
[null,null,null,null,null,"Coincident",1.9859498739242554]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1980330944061279]
[null,null,null,null,null,"Coincident",1.9638408422470093]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2036888599395752]
[null,null,null,null,null,"Coincident",1.9707375764846802]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0611681938171387]
[null,null,null,null,null,"Coincident",1.8415583372116089]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0664718151092529]
[null,null,null,null,null,"Coincident",1.8480255603790283]
[null,null,"Rockhampton Glenmore","Substation Rating","MVA","Non-Coincident",54.299999237060547]
[null,null,null,null,null,"Coincident",54.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.141000747680664]
[null,null,null,null,null,"Coincident",19.069999694824219]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.304254531860352]
[null,null,null,null,null,"Coincident",19.881160736083984]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.255102157592773]
[null,null,null,null,null,"Coincident",20.976999282836914]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.53468132019043]
[null,null,null,null,null,"Coincident",21.869277954101563]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.352411270141602]
[null,null,null,null,null,"Coincident",19.260700225830078]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.52729606628418]
[null,null,null,null,null,"Coincident",20.079971313476562]
[null,null,"Rockhampton South","Substation Rating","MVA","Non-Coincident",32.700000762939453]
[null,null,null,null,null,"Coincident",32.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.359999656677246]
[null,null,null,null,null,"Coincident",10.600000381469727]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.173002243041992]
[null,null,null,null,null,"Coincident",11.563061714172363]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.895999908447266]
[null,null,null,null,null,"Coincident",11.660000801086426]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.890302658081055]
[null,null,null,null,null,"Coincident",12.719367980957031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.66719913482666]
[null,null,null,null,null,"Coincident",10.812000274658203]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.516462326049805]
[null,null,null,null,null,"Coincident",11.794322967529297]
[null,null,"Rocky Street","Substation Rating","MVA","Non-Coincident",57.5]
[null,null,null,null,null,"Coincident",57.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.246999740600586]
[null,null,null,null,null,"Coincident",21.035999298095703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.358646392822266]
[null,null,null,null,null,"Coincident",21.140064239501953]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.776899337768555]
[null,null,null,null,null,"Coincident",21.560636520385742]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.891330718994141]
[null,null,null,null,null,"Coincident",21.66729736328125]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.092437744140625]
[null,null,null,null,null,"Coincident",19.892902374267578]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.198017120361328]
[null,null,null,null,null,"Coincident",19.991313934326172]
[null,null,"Rolleston","Substation Rating","MVA","Non-Coincident",25]
[null,null,null,null,null,"Coincident",25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.9679999351501465]
[null,null,null,null,null,"Coincident",6.4029998779296875]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.0004253387451172]
[null,null,null,null,null,"Coincident",6.4407162666320801]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.1628947257995605]
[null,null,null,null,null,"Coincident",6.5820913314819336]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.1962270736694336]
[null,null,null,null,null,"Coincident",6.6208629608154297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.7511558532714844]
[null,null,null,null,null,"Coincident",6.2037386894226074]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.7825722694396973]
[null,null,null,null,null,"Coincident",6.2402811050415039]
[null,null,"Rollingstone","Substation Rating","MVA","Non-Coincident",3.7999999523162842]
[null,null,null,null,null,"Coincident",3.7999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.3339999914169312]
[null,null,null,null,null,"Coincident",1.0290000438690186]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3670979738235474]
[null,null,null,null,null,"Coincident",1.0486396551132202]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4367046356201172]
[null,null,null,null,null,"Coincident",1.1082227230072021]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4723508358001709]
[null,null,null,null,null,"Coincident",1.1293743848800659]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2795860767364502]
[null,null,null,null,null,"Coincident",0.98702710866928101]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3113340139389038]
[null,null,null,null,null,"Coincident",1.0058655738830566]
[null,null,"Roma East","Substation Rating","MVA","Non-Coincident",14]
[null,null,null,null,null,"Coincident",14]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.425999641418457]
[null,null,null,null,null,"Coincident",7.245999813079834]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.9199104309082031]
[null,null,null,null,null,"Coincident",7.4965724945068359]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.8456993103027344]
[null,null,null,null,null,"Coincident",7.6069235801696777]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.3642120361328125]
[null,null,null,null,null,"Coincident",7.8699769973754883]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.1010093688964844]
[null,null,null,null,null,"Coincident",6.9665217399597168]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.5758695602416992]
[null,null,null,null,null,"Coincident",7.2074298858642578]
[null,null,"Roma West","Substation Rating","MVA","Non-Coincident",6.3000001907348633]
[null,null,null,null,null,"Coincident",6.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.8610000610351562]
[null,null,null,null,null,"Coincident",4.3159999847412109]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.0836467742919922]
[null,null,null,null,null,"Coincident",4.4430708885192871]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.7902727127075195]
[null,null,null,null,null,"Coincident",4.2532024383544922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.0096797943115234]
[null,null,null,null,null,"Coincident",4.3784241676330566]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.3787403106689453]
[null,null,null,null,null,"Coincident",3.8878095149993896]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.5792980194091797]
[null,null,null,null,null,"Coincident",4.0022735595703125]
[null,null,"Roo Works","Substation Rating","MVA","Non-Coincident",2.4000000953674316]
[null,null,null,null,null,"Coincident",2.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.97500002384185791]
[null,null,null,null,null,"Coincident",0.65499997138977051]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0755189657211304]
[null,null,null,null,null,"Coincident",0.69095945358276367]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-20"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.98671948909759521]
[null,null,null,null,null,"Coincident",0.66287308931350708]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0884467363357544]
[null,null,null,null,null,"Coincident",0.6992647647857666]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.87491625547409058]
[null,null,null,null,null,"Coincident",0.5877642035484314]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.96511697769165039]
[null,null,null,null,null,"Coincident",0.62003248929977417]
[null,null,"Rosella","Substation Rating","MVA","Non-Coincident",9]
[null,null,null,null,null,"Coincident",9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.8410000801086426]
[null,null,null,null,null,"Coincident",2.815000057220459]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.1083698272705078]
[null,null,null,null,null,"Coincident",2.8906528949737549]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.9875369071960449]
[null,null,null,null,null,"Coincident",2.9002101421356201]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.2630000114440918]
[null,null,null,null,null,"Coincident",2.9781529903411865]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.4782638549804687]
[null,null,null,null,null,"Coincident",2.604072093963623]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.7255997657775879]
[null,null,null,null,null,"Coincident",2.6740562915802002]
[null,null,"Ross Plains","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.12399959564209]
[null,null,null,null,null,"Coincident",12.677000045776367]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.406895637512207]
[null,null,null,null,null,"Coincident",12.886103630065918]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-16"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.013388633728027]
[null,null,null,null,null,"Coincident",13.475271224975586]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.314098358154297]
[null,null,null,null,null,"Coincident",13.697542190551758]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.432065010070801]
[null,null,null,null,null,"Coincident",12.055953979492188]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.701101303100586]
[null,null,null,null,null,"Coincident",12.254813194274902]
[null,null,"Sarina","Substation Rating","MVA","Non-Coincident",24]
[null,null,null,null,null,"Coincident",24]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.883999824523926]
[null,null,null,null,null,"Coincident",13.28600025177002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.318605422973633]
[null,null,null,null,null,"Coincident",13.712907791137695]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-3.005000114440918]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.231099128723145]
[null,null,null,null,null,"Coincident",13.618149757385254]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.676569938659668]
[null,null,null,null,null,"Coincident",14.055729866027832]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.467480659484863]
[null,null,null,null,null,"Coincident",12.887420654296875]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.889047622680664]
[null,null,null,null,null,"Coincident",13.301521301269531]
[null,null,"Saunders","Substation Rating","MVA","Non-Coincident",5.0999999046325684]
[null,null,null,null,null,"Coincident",5.0999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.2680000066757202]
[null,null,null,null,null,"Coincident",0.75199997425079346]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2894107103347778]
[null,null,null,null,null,"Coincident",0.76841914653778076]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-30"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2749993801116943]
[null,null,null,null,null,"Coincident",0.75615102052688599]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.2965282201766968]
[null,null,null,null,null,"Coincident",0.77266079187393188]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1633518934249878]
[null,null,null,null,null,"Coincident",0.68993741273880005]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.1829955577850342]
[null,null,null,null,null,"Coincident",0.70500147342681885]
[null,null,"Shutehaven","Substation Rating","MVA","Non-Coincident",25]
[null,null,null,null,null,"Coincident",25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.1780004501342773]
[null,null,null,null,null,"Coincident",6.5069999694824219]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.2685003280639648]
[null,null,null,null,null,"Coincident",6.5150117874145508]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.2597799301147461]
[null,null,null,null,null,"Coincident",6.5720701217651367]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.3511848449707031]
[null,null,null,null,null,"Coincident",6.5801620483398438]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.2434244155883789]
[null,null,null,null,null,"Coincident",6.559056282043457]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.3346481323242187]
[null,null,null,null,null,"Coincident",6.5671319961547852]
[null,null,"South Blackwater","Substation Rating","MVA","Non-Coincident",16.200000762939453]
[null,null,null,null,null,"Coincident",16.200000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.30700001120567322]
[null,null,null,null,null,"Coincident",0.26899999380111694]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.36156603693962097]
[null,null,null,null,null,"Coincident",0.31662279367446899]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.31007000803947449]
[null,null,null,null,null,"Coincident",0.27168998122215271]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.36518168449401855]
[null,null,null,null,null,"Coincident",0.31978902220726013]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.30945602059364319]
[null,null,null,null,null,"Coincident",0.27115198969841003]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.36445856094360352]
[null,null,null,null,null,"Coincident",0.31915578246116638]
[null,null,"South Bundaberg","Substation Rating","MVA","Non-Coincident",42.400001525878906]
[null,null,null,null,null,"Coincident",42.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.177000045776367]
[null,null,null,null,null,"Coincident",12.855999946594238]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.177515983581543]
[null,null,null,null,null,"Coincident",12.863527297973633]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.962690353393555]
[null,null,null,null,null,"Coincident",13.568479537963867]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.963234901428223]
[null,null,null,null,null,"Coincident",13.576424598693848]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.68278980255127]
[null,null,null,null,null,"Coincident",12.407839775085449]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.683287620544434]
[null,null,null,null,null,"Coincident",12.415104866027832]
[null,null,"South Kolan","Substation Rating","MVA","Non-Coincident",27.5]
[null,null,null,null,null,"Coincident",27.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.0339999198913574]
[null,null,null,null,null,"Coincident",5.7760000228881836]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.343113899230957]
[null,null,null,null,null,"Coincident",6.0650372505187988]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",-0.74299997091293335]
[null,null,null,null,null,"Coincident",-9.9999997764825821E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9868745803833008]
[null,null,null,null,null,"Coincident",5.7308893203735352]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.293574333190918]
[null,null,null,null,null,"Coincident",6.0176692008972168]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.4282464981079102]
[null,null,null,null,null,"Coincident",5.1961474418640137]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.7063283920288086]
[null,null,null,null,null,"Coincident",5.4561681747436523]
[null,null,"South Mackay","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.458000183105469]
[null,null,null,null,null,"Coincident",10.451000213623047]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.462697982788086]
[null,null,null,null,null,"Coincident",11.472368240356445]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.203800201416016]
[null,null,null,null,null,"Coincident",11.496100425720215]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.208969116210938]
[null,null,null,null,null,"Coincident",12.61960506439209]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.458000183105469]
[null,null,null,null,null,"Coincident",10.451000213623047]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.462697982788086]
[null,null,null,null,null,"Coincident",11.472368240356445]
[null,null,"South Toowoomba","Substation Rating","MVA","Non-Coincident",37.400001525878906]
[null,null,null,null,null,"Coincident",37.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.672000885009766]
[null,null,null,null,null,"Coincident",17.545999526977539]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.413381576538086]
[null,null,null,null,null,"Coincident",18.171327590942383]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.827009201049805]
[null,null,null,null,null,"Coincident",16.861881256103516]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.539484024047852]
[null,null,null,null,null,"Coincident",17.462827682495117]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.636350631713867]
[null,null,null,null,null,"Coincident",15.897903442382813]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.30809211730957]
[null,null,null,null,null,"Coincident",16.464494705200195]
[null,null,"St. George","Substation Rating","MVA","Non-Coincident",55.900001525878906]
[null,null,null,null,null,"Coincident",48.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.225000381469727]
[null,null,null,null,null,"Coincident",9.7889995574951172]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.365678787231445]
[null,null,null,null,null,"Coincident",10.367251396179199]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-04-09"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.547500610351563]
[null,null,null,null,null,"Coincident",10.426361083984375]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.802247047424316]
[null,null,null,null,null,"Coincident",11.042263031005859]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.283000946044922]
[null,null,null,null,null,"Coincident",9.5875415802001953]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.514933586120605]
[null,null,null,null,null,"Coincident",10.15389347076416]
[null,null,"St. George Town","Substation Rating","MVA","Non-Coincident",6.5999999046325684]
[null,null,null,null,null,"Coincident",6.5999999046325684]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.8229999542236328]
[null,null,null,null,null,"Coincident",4.065000057220459]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.1437606811523437]
[null,null,null,null,null,"Coincident",4.2935009002685547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.9799885749816895]
[null,null,null,null,null,"Coincident",4.1973156929016113]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.311190128326416]
[null,null,null,null,null,"Coincident",4.4332542419433594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.5588927268981934]
[null,null,null,null,null,"Coincident",3.8424007892608643]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.862088680267334]
[null,null,null,null,null,"Coincident",4.0583887100219727]
[null,null,"Stamford","Substation Rating","MVA","Non-Coincident",0.60000002384185791]
[null,null,null,null,null,"Coincident",0.60000002384185791]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.30099999904632568]
[null,null,null,null,null,"Coincident",0.20399999618530273]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.31813520193099976]
[null,null,null,null,null,"Coincident",0.22023850679397583]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.30863335728645325]
[null,null,null,null,null,"Coincident",0.20917344093322754]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.3262031078338623]
[null,null,null,null,null,"Coincident",0.22582376003265381]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.28100758790969849]
[null,null,null,null,null,"Coincident",0.19045031070709229]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.29700466990470886]
[null,null,null,null,null,"Coincident",0.20561026036739349]
[null,null,"Stanthorpe Town","Substation Rating","MVA","Non-Coincident",29.200000762939453]
[null,null,null,null,null,"Coincident",27.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.039999961853027]
[null,null,null,null,null,"Coincident",10.215000152587891]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.305213928222656]
[null,null,null,null,null,"Coincident",10.769771575927734]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.050275802612305]
[null,null,null,null,null,"Coincident",10.137263298034668]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",13.33774471282959]
[null,null,null,null,null,"Coincident",10.687813758850098]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.486202239990234]
[null,null,null,null,null,"Coincident",9.6061859130859375]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.761245727539063]
[null,null,null,null,null,"Coincident",10.127893447875977]
[null,null,"Stuart","Substation Rating","MVA","Non-Coincident",76.699996948242188]
[null,null,null,null,null,"Coincident",76.699996948242188]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.14900016784668]
[null,null,null,null,null,"Coincident",21.181999206542969]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.217273712158203]
[null,null,null,null,null,"Coincident",22.303348541259766]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-10-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.029232025146484]
[null,null,null,null,null,"Coincident",21.954084396362305]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",26.136444091796875]
[null,null,null,null,null,"Coincident",23.116306304931641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.765514373779297]
[null,null,null,null,null,"Coincident",20.84562873840332]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.816823959350586]
[null,null,null,null,null,"Coincident",21.94917106628418]
[null,null,"Tanby","Substation Rating","MVA","Non-Coincident",50.400001525878906]
[null,null,null,null,null,"Coincident",50.400001525878906]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.569999694824219]
[null,null,null,null,null,"Coincident",10.927000045776367]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.652008056640625]
[null,null,null,null,null,"Coincident",11.236480712890625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.72700023651123]
[null,null,null,null,null,"Coincident",12.019700050354004]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.817209243774414]
[null,null,null,null,null,"Coincident",12.360129356384277]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.350285530090332]
[null,null,null,null,null,"Coincident",10.719496726989746]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.430736541748047]
[null,null,null,null,null,"Coincident",11.023099899291992]
[null,null,"Tara","Substation Rating","MVA","Non-Coincident",2]
[null,null,null,null,null,"Coincident",2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4199999570846558]
[null,null,null,null,null,"Coincident",1.3259999752044678]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5061221122741699]
[null,null,null,null,null,"Coincident",1.3924442529678345]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4865411520004272]
[null,null,null,null,null,"Coincident",1.3881362676620483]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5766990184783936]
[null,null,null,null,null,"Coincident",1.4576941728591919]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3683545589447021]
[null,null,null,null,null,"Coincident",1.277773380279541]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4513444900512695]
[null,null,null,null,null,"Coincident",1.3418010473251343]
[null,null,"Tennyson Street","Substation Rating","MVA","Non-Coincident",37.5]
[null,null,null,null,null,"Coincident",37.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.378999710083008]
[null,null,null,null,null,"Coincident",12.062999725341797]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.865205764770508]
[null,null,null,null,null,"Coincident",12.5408935546875]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.165416717529297]
[null,null,null,null,null,"Coincident",11.905697822570801]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.632244110107422]
[null,null,null,null,null,"Coincident",12.377360343933105]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.245080947875977]
[null,null,null,null,null,"Coincident",11.227877616882324]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.628396987915039]
[null,null,null,null,null,"Coincident",11.672687530517578]
[null,null,"Thalanga","Substation Rating","MVA","Non-Coincident",6.4000000953674316]
[null,null,null,null,null,"Coincident",6.4000000953674316]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0299999713897705]
[null,null,null,null,null,"Coincident",2.625999927520752]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.6212136745452881]
[null,null,null,null,null,"Coincident",3.0724420547485352]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-10"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","23:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.0602998733520508]
[null,null,null,null,null,"Coincident",2.6522598266601562]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.6574258804321289]
[null,null,null,null,null,"Coincident",3.1031663417816162]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.0542399883270264]
[null,null,null,null,null,"Coincident",2.647007942199707]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.6501834392547607]
[null,null,null,null,null,"Coincident",3.0970215797424316]
[null,null,"Theodore","Substation Rating","MVA","Non-Coincident",16.600000381469727]
[null,null,null,null,null,"Coincident",16.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.621000289916992]
[null,null,null,null,null,"Coincident",9.7600002288818359]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.664117813110352]
[null,null,null,null,null,"Coincident",9.7654762268066406]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.265800476074219]
[null,null,null,null,null,"Coincident",10.352529525756836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.311535835266113]
[null,null,null,null,null,"Coincident",10.35833740234375]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.754400253295898]
[null,null,null,null,null,"Coincident",9.8825855255126953]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.798059463500977]
[null,null,null,null,null,"Coincident",9.8881311416625977]
[null,null,"Tieri","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1549999713897705]
[null,null,null,null,null,"Coincident",1.3530000448226929]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1742920875549316]
[null,null,null,null,null,"Coincident",1.3669799566268921]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0127699375152588]
[null,null,null,null,null,"Coincident",1.2637020349502563]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0307888984680176]
[null,null,null,null,null,"Coincident",1.2767592668533325]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8376116752624512]
[null,null,null,null,null,"Coincident",1.1537302732467651]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8540624380111694]
[null,null,null,null,null,"Coincident",1.1656512022018433]
[null,null,"Toowoomba Central","Substation Rating","MVA","Non-Coincident",84]
[null,null,null,null,null,"Coincident",84]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.572000503540039]
[null,null,null,null,null,"Coincident",13.468000411987305]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.396778106689453]
[null,null,null,null,null,"Coincident",13.629815101623535]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-09-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.336139678955078]
[null,null,null,null,null,"Coincident",13.825844764709473]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.113666534423828]
[null,null,null,null,null,"Coincident",13.991958618164063]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.70429801940918]
[null,null,null,null,null,"Coincident",13.022883415222168]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.457666397094727]
[null,null,null,null,null,"Coincident",13.179349899291992]
[null,null,"Torquay","Substation Rating","MVA","Non-Coincident",70]
[null,null,null,null,null,"Coincident",70]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.833999633789063]
[null,null,null,null,null,"Coincident",27.833999633789063]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",27.886968612670898]
[null,null,null,null,null,"Coincident",27.886968612670898]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",29.1572265625]
[null,null,null,null,null,"Coincident",29.1572265625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.212713241577148]
[null,null,null,null,null,"Coincident",29.212713241577148]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",27.397006988525391]
[null,null,null,null,null,"Coincident",27.397006988525391]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",27.44914436340332]
[null,null,null,null,null,"Coincident",27.44914436340332]
[null,null,"Torrington","Substation Rating","MVA","Non-Coincident",67.5]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.655000686645508]
[null,null,null,null,null,"Coincident",17.485000610351562]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.006298065185547]
[null,null,null,null,null,"Coincident",17.710470199584961]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.434535980224609]
[null,null,null,null,null,"Coincident",17.637645721435547]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.773239135742188]
[null,null,null,null,null,"Coincident",17.865083694458008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.415241241455078]
[null,null,null,null,null,"Coincident",16.488180160522461]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.695718765258789]
[null,null,null,null,null,"Coincident",16.700796127319336]
[null,null,"Townsville Port","Substation Rating","MVA","Non-Coincident",83.199996948242187]
[null,null,null,null,null,"Coincident",83.199996948242187]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.8439998626708984]
[null,null,null,null,null,"Coincident",7.3299999237060547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.1570854187011719]
[null,null,null,null,null,"Coincident",7.5914111137390137]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-03"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.0268058776855469]
[null,null,null,null,null,"Coincident",7.4815115928649902]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.3463630676269531]
[null,null,null,null,null,"Coincident",7.7483258247375488]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.3795127868652344]
[null,null,null,null,null,"Coincident",6.9450283050537109]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.6761550903320312]
[null,null,null,null,null,"Coincident",7.1927103996276855]
[null,null,"Tuan","Substation Rating","MVA","Non-Coincident",11.399999618530273]
[null,null,null,null,null,"Coincident",10.800000190734863]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.880000114440918]
[null,null,null,null,null,"Coincident",5.2439999580383301]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.9597997665405273]
[null,null,null,null,null,"Coincident",6.1641817092895508]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-05-31"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.568000316619873]
[null,null,null,null,null,"Coincident",5.7684001922607422]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.7557802200317383]
[null,null,null,null,null,"Coincident",6.7806000709533691]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.880000114440918]
[null,null,null,null,null,"Coincident",5.2439999580383301]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.9597997665405273]
[null,null,null,null,null,"Coincident",6.1641817092895508]
[null,null,"Vermont","Substation Rating","MVA","Non-Coincident",24.299999237060547]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.322999954223633]
[null,null,null,null,null,"Coincident",8.3610000610351562]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.909221649169922]
[null,null,null,null,null,"Coincident",9.1177902221679687]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.426229476928711]
[null,null,null,null,null,"Coincident",8.4446096420288086]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.018313407897949]
[null,null,null,null,null,"Coincident",9.2089681625366211]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.405584335327148]
[null,null,null,null,null,"Coincident",8.4278879165649414]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.996495246887207]
[null,null,null,null,null,"Coincident",9.1907329559326172]
[null,null,"Victoria","Substation Rating","MVA","Non-Coincident",13]
[null,null,null,null,null,"Coincident",13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8320000171661377]
[null,null,null,null,null,"Coincident",1.5399999618530273]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9057410955429077]
[null,null,null,null,null,"Coincident",1.6095415353775024]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",-4.999999888241291E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.947232723236084]
[null,null,null,null,null,"Coincident",1.6368658542633057]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0256121158599854]
[null,null,null,null,null,"Coincident",1.7107815742492676]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7485157251358032]
[null,null,null,null,null,"Coincident",1.4698221683502197]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8188964128494263]
[null,null,null,null,null,"Coincident",1.5361946821212769]
[null,null,"Waggamba 132/33kV","Substation Rating","MVA","Non-Coincident",15]
[null,null,null,null,null,"Coincident",15]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.1700000762939453]
[null,null,null,null,null,"Coincident",5.8379998207092285]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.1780357360839844]
[null,null,null,null,null,"Coincident",5.8454484939575195]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.650334358215332]
[null,null,null,null,null,"Coincident",6.2924880981445312]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.6589956283569336]
[null,null,null,null,null,"Coincident",6.3005166053771973]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.0446257591247559]
[null,null,null,null,null,"Coincident",5.7193717956542969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.0524978637695313]
[null,null,null,null,null,"Coincident",5.7266688346862793]
[null,null,"Waggamba 132/66kV","Substation Rating","MVA","Non-Coincident",33]
[null,null,null,null,null,"Coincident",33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.136999130249023]
[null,null,null,null,null,"Coincident",14.494999885559082]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.154020309448242]
[null,null,null,null,null,"Coincident",14.578704833984375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-02"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.850700378417969]
[null,null,null,null,null,"Coincident",15.122053146362305]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.869422912597656]
[null,null,null,null,null,"Coincident",15.209379196166992]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.507959365844727]
[null,null,null,null,null,"Coincident",13.922738075256348]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.526342391967773]
[null,null,null,null,null,"Coincident",14.003137588500977]
[null,null,"Wallaville","Substation Rating","MVA","Non-Coincident",25.600000381469727]
[null,null,null,null,null,"Coincident",25.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.875999927520752]
[null,null,null,null,null,"Coincident",7.8410000801086426]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.8916025161743164]
[null,null,null,null,null,"Coincident",7.8556785583496094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.663599967956543]
[null,null,null,null,null,"Coincident",8.6251001358032227]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.6807632446289063]
[null,null,null,null,null,"Coincident",8.6412467956542969]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.9666528701782227]
[null,null,null,null,null,"Coincident",7.9312500953674316]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.9824347496032715]
[null,null,null,null,null,"Coincident",7.9460973739624023]
[null,null,"Wandoan","Substation Rating","MVA","Non-Coincident",12.199999809265137]
[null,null,null,null,null,"Coincident",12.199999809265137]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.687999963760376]
[null,null,null,null,null,"Coincident",2.3989999294281006]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6898224353790283]
[null,null,null,null,null,"Coincident",2.4060459136962891]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8949761390686035]
[null,null,null,null,null,"Coincident",2.5837230682373047]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8969388008117676]
[null,null,null,null,null,"Coincident",2.5913114547729492]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.7551999092102051]
[null,null,null,null,null,"Coincident",2.4589748382568359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7570679187774658]
[null,null,null,null,null,"Coincident",2.4661970138549805]
[null,null,"Warwick East","Substation Rating","MVA","Non-Coincident",69.599998474121094]
[null,null,null,null,null,"Coincident",69.599998474121094]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.055999755859375]
[null,null,null,null,null,"Coincident",19.261999130249023]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.113523483276367]
[null,null,null,null,null,"Coincident",19.270849227905273]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.055099487304688]
[null,null,null,null,null,"Coincident",18.387889862060547]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.110012054443359]
[null,null,null,null,null,"Coincident",18.396337509155273]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.083292007446289]
[null,null,null,null,null,"Coincident",16.665866851806641]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.133062362670898]
[null,null,null,null,null,"Coincident",16.673524856567383]
[null,null,"West Bundaberg","Substation Rating","MVA","Non-Coincident",61.299999237060547]
[null,null,null,null,null,"Coincident",61.299999237060547]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.402000427246094]
[null,null,null,null,null,"Coincident",25.357999801635742]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.587047576904297]
[null,null,null,null,null,"Coincident",26.641948699951172]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",29.883312225341797]
[null,null,null,null,null,"Coincident",25.773111343383789]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.104129791259766]
[null,null,null,null,null,"Coincident",27.078079223632813]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.091259002685547]
[null,null,null,null,null,"Coincident",24.227540969848633]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.178897857666016]
[null,null,null,null,null,"Coincident",25.454250335693359]
[null,null,"West Dalby","Substation Rating","MVA","Non-Coincident",14.600000381469727]
[null,null,null,null,null,"Coincident",14.600000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.9770002365112305]
[null,null,null,null,null,"Coincident",4.0399999618530273]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.619842529296875]
[null,null,null,null,null,"Coincident",4.3224954605102539]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.7989230155944824]
[null,null,null,null,null,"Coincident",3.8954486846923828]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.418764591217041]
[null,null,null,null,null,"Coincident",4.1678366661071777]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.3731904029846191]
[null,null,null,null,null,"Coincident",3.5498671531677246]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.9380431175231934]
[null,null,null,null,null,"Coincident",3.7980902194976807]
[null,null,"West Mackay","Substation Rating","MVA","Non-Coincident",38.700000762939453]
[null,null,null,null,null,"Coincident",38.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.444000244140625]
[null,null,null,null,null,"Coincident",16.174999237060547]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.053133010864258]
[null,null,null,null,null,"Coincident",16.548070907592773]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.900094985961914]
[null,null,null,null,null,"Coincident",15.670661926269531]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.490236282348633]
[null,null,null,null,null,"Coincident",16.032102584838867]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.74216365814209]
[null,null,null,null,null,"Coincident",14.596966743469238]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.2918701171875]
[null,null,null,null,null,"Coincident",14.93364143371582]
[null,null,"West Toowoomba","Substation Rating","MVA","Non-Coincident",36.200000762939453]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.676000595092773]
[null,null,null,null,null,"Coincident",15.859999656677246]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.964614868164063]
[null,null,null,null,null,"Coincident",16.373897552490234]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-08-28"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.543601989746094]
[null,null,null,null,null,"Coincident",16.81159782409668]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.861076354980469]
[null,null,null,null,null,"Coincident",17.356330871582031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.23628044128418]
[null,null,null,null,null,"Coincident",15.859999656677246]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.533552169799805]
[null,null,null,null,null,"Coincident",16.373897552490234]
[null,null,"West Warwick","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",27]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.866999626159668]
[null,null,null,null,null,"Coincident",4.9559998512268066]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.267924308776855]
[null,null,null,null,null,"Coincident",5.0230526924133301]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-06-07"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","WINTER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.777437210083008]
[null,null,null,null,null,"Coincident",5.193392276763916]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.21195125579834]
[null,null,null,null,null,"Coincident",5.2636566162109375]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.128893852233887]
[null,null,null,null,null,"Coincident",4.7313942909240723]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.539480209350586]
[null,null,null,null,null,"Coincident",4.7954082489013672]
[null,null,"Winton","Substation Rating","MVA","Non-Coincident",8]
[null,null,null,null,null,"Coincident",8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8819999694824219]
[null,null,null,null,null,"Coincident",2.7439999580383301]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8944339752197266]
[null,null,null,null,null,"Coincident",2.7584524154663086]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.9972798824310303]
[null,null,null,null,null,"Coincident",2.853759765625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.0102112293243408]
[null,null,null,null,null,"Coincident",2.8687903881072998]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8819999694824219]
[null,null,null,null,null,"Coincident",2.7439999580383301]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8944339752197266]
[null,null,null,null,null,"Coincident",2.7584524154663086]
[null,null,"Wirralie","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.30700001120567322]
[null,null,null,null,null,"Coincident",0.25400000810623169]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.33261540532112122]
[null,null,null,null,null,"Coincident",0.2708357572555542]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.329813152551651]
[null,null,null,null,null,"Coincident",0.27287474274635315]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.35733205080032349]
[null,null,null,null,null,"Coincident",0.29096153378486633]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.30427691340446472]
[null,null,null,null,null,"Coincident",0.2517470121383667]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.32966509461402893]
[null,null,null,null,null,"Coincident",0.26843345165252686]
[null,null,"Wooderson Pumps","Substation Rating","MVA","Non-Coincident",4]
[null,null,null,null,null,"Coincident",4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6819999217987061]
[null,null,null,null,null,"Coincident",2.8000000864267349E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.273568868637085]
[null,null,null,null,null,"Coincident",5.7306196540594101E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-11-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","09:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.7088198661804199]
[null,null,null,null,null,"Coincident",2.8280001133680344E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.3063044548034668]
[null,null,null,null,null,"Coincident",5.7879257947206497E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.703455924987793]
[null,null,null,null,null,"Coincident",2.8224000707268715E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.2997574806213379]
[null,null,null,null,null,"Coincident",5.7764645665884018E-2]
[null,null,"Woodgate","Substation Rating","MVA","Non-Coincident",5.3000001907348633]
[null,null,null,null,null,"Coincident",5.3000001907348633]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4800000190734863]
[null,null,null,null,null,"Coincident",1.9270000457763672]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5398235321044922]
[null,null,null,null,null,"Coincident",1.9895613193511963]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-12-29"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.7280001640319824]
[null,null,null,null,null,"Coincident",2.1197001934051514]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7938058376312256]
[null,null,null,null,null,"Coincident",2.1885175704956055]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5118930339813232]
[null,null,null,null,null,"Coincident",1.9517813920974731]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5724859237670898]
[null,null,null,null,null,"Coincident",2.0151472091674805]
[null,null,"Woodhouse Station","Substation Rating","MVA","Non-Coincident",0.30000001192092896]
[null,null,null,null,null,"Coincident",0.30000001192092896]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.000000074505806E-2]
[null,null,null,null,null,"Coincident",5.000000074505806E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8823529630899429E-2]
[null,null,null,null,null,"Coincident",5.8823529630899429E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-01"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1999997347593307E-2]
[null,null,null,null,null,"Coincident",5.1999997347593307E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.1176467686891556E-2]
[null,null,null,null,null,"Coincident",6.1176467686891556E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.000000074505806E-2]
[null,null,null,null,null,"Coincident",5.000000074505806E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.8823529630899429E-2]
[null,null,null,null,null,"Coincident",5.8823529630899429E-2]
[null,null,"Woodstock South","Substation Rating","MVA","Non-Coincident",8.6000003814697266]
[null,null,null,null,null,"Coincident",8.6000003814697266]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0399999618530273]
[null,null,null,null,null,"Coincident",0.93999999761581421]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0630145072937012]
[null,null,null,null,null,"Coincident",0.96540147066116333]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1439999341964722]
[null,null,null,null,null,"Coincident",1.034000039100647]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1693159341812134]
[null,null,null,null,null,"Coincident",1.0619416236877441]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0521367788314819]
[null,null,null,null,null,"Coincident",0.95096981525421143]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0754199028015137]
[null,null,null,null,null,"Coincident",0.97666770219802856]
[null,null,"Woolooga","Substation Rating","MVA","Non-Coincident",17.700000762939453]
[null,null,null,null,null,"Coincident",17.700000762939453]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.877000093460083]
[null,null,null,null,null,"Coincident",3.2760000228881836]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.048253059387207]
[null,null,null,null,null,"Coincident",3.3992388248443604]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-11"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2040247917175293]
[null,null,null,null,null,"Coincident",3.552330493927002]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.3897233009338379]
[null,null,null,null,null,"Coincident",3.6859645843505859]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7551848888397217]
[null,null,null,null,null,"Coincident",3.1730680465698242]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9210569858551025]
[null,null,null,null,null,"Coincident",3.2924346923828125]
[null,null,"Wowan","Substation Rating","MVA","Non-Coincident",16.100000381469727]
[null,null,null,null,null,"Coincident",16.100000381469727]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.3680000305175781]
[null,null,null,null,null,"Coincident",5.2680001258850098]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.5427384376525879]
[null,null,null,null,null,"Coincident",5.3390307426452637]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-14"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9070839881896973]
[null,null,null,null,null,"Coincident",4.8867020606994629]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0691747665405273]
[null,null,null,null,null,"Coincident",4.9525918960571289]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3924860954284668]
[null,null,null,null,null,"Coincident",4.4609951972961426]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.5404562950134277]
[null,null,null,null,null,"Coincident",4.5211443901062012]
[null,null,"Yarraman","Substation Rating","MVA","Non-Coincident",12]
[null,null,null,null,null,"Coincident",12]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9360001087188721]
[null,null,null,null,null,"Coincident",3.3650000095367432]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1169099807739258]
[null,null,null,null,null,"Coincident",3.5173571109771729]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-01-13"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.9929540157318115]
[null,null,null,null,null,"Coincident",3.413691520690918]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.1764817237854004]
[null,null,null,null,null,"Coincident",3.5682532787322998]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7246761322021484]
[null,null,null,null,null,"Coincident",3.1843330860137939]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.8958730697631836]
[null,null,null,null,null,"Coincident",3.328510046005249]
[null,null,"Yarranlea South","Substation Rating","MVA","Non-Coincident",2.7999999523162842]
[null,null,null,null,null,"Coincident",2.7999999523162842]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5269999504089355]
[null,null,null,null,null,"Coincident",1.2879999876022339]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7962863445281982]
[null,null,null,null,null,"Coincident",1.5151726007461548]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-15"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5586394071578979]
[null,null,null,null,null,"Coincident",1.3146873712539673]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.833505392074585]
[null,null,null,null,null,"Coincident",1.5465669631958008]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4222782850265503]
[null,null,null,null,null,"Coincident",1.1996688842773437]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6730970144271851]
[null,null,null,null,null,"Coincident",1.411262035369873]
[null,null,"Yeppoon","Substation Rating","MVA","Non-Coincident",59]
[null,null,null,null,null,"Coincident",59]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.896999359130859]
[null,null,null,null,null,"Coincident",22.048999786376953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.940311431884766]
[null,null,null,null,null,"Coincident",22.101743698120117]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2018-02-12"]
[null,null,null,null,null,"Coincident","2018-02-15"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00"]
[null,null,null,null,null,"Coincident","19:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","SUMMER"]
[null,null,null,null,null,"Coincident","SUMMER"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.186698913574219]
[null,null,null,null,null,"Coincident",24.253900527954102]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.234342575073242]
[null,null,null,null,null,"Coincident",24.311918258666992]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.127660751342773]
[null,null,null,null,null,"Coincident",21.30815315246582]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.169517517089844]
[null,null,null,null,null,"Coincident",21.359125137329102]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Date MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:00:00"]
[null,null,null,null,null,"Coincident","00:00:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]

{"sheet":"6.3 Sustained interruptionss","index":24,"n_rows":60016,"n_cols":12,"rows_kept":4500,"cut":true,"hidden":false,"merged":[[13,7,14,7],[13,11,14,11],[13,10,14,10],[13,9,14,9],[7,1,7,4],[11,1,11,4],[11,10,11,11],[10,1,10,4],[10,10,10,11],[10,8,10,9],[11,8,11,9],[10,6,10,7]],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Ergon Energy"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2017-18"}]
[null,"6.3 SUSTAINED INTERRUPTIONS TO SUPPLY"]
[]
[null,{"$f":"CONCATENATE(\"6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for \",CRY,\")\")","v":"6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2017-18)"}]
[]
[null,"There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data."]
[]
[null,"Definitions:"]
[null,"Feeder classification definitions\n(column E)",null,null,null,null,"Average duration of sustained customer interruption \n(column I)",null,"Effect on unplanned SAIDI \n(column J)",null,"Effect on unplanned SAIFI \n(column K)"]
[null,"CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.\nUrban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km.\nShort rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km.\nLong rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km.\n",null,null,null,null,"The average duration of an  interruption experienced by an affected customer.",null,"The sum of the duration of each unplanned sustained customer\ninterruption (in minutes) divided by the total number of distribution\ncustomers. Unplanned SAIDI excludes momentary interruptions (one minute or less).",null,"The total number of unplanned sustained customer interruptions\ndivided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions."]
[]
[null,"Date of event","Time of interruption","Asset ID","Feeder classification","Reason for interruption","Detailed reason for interruption","Number of customers affected by the interruption","Average duration of sustained customer interruption","Effect on unplanned SAIDI","Effect on unplanned SAIFI","MED"]
[null,"(DD/MM/YYYY)","(HH:MM)","(eg. feeder ID)","(drop down)","(select from options in drop-down box)","(select from options in column 'O' that correspond with reason in column 'F')",null,"(minutes)"]
[null,"2017-07-01","00:00:00",40001116,"Long Rural","Other","Forced Corrective Maintenance",1,525599.96666666691,6.8741821431685395,1.30787339785509E-5,"NO"]
[null,"2017-07-01","02:18:00",60026658,"Short Rural","Animal","Animal impact",1,286.26666666666705,7.0839674507038204E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","06:30:00",10020809,"Urban","Planned",null,56,28,0,0,"NO"]
[null,"2017-07-01","06:51:00",40000978,"Long Rural","Other","Vibration",1,197.51666666666699,2.5832679396634401E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","06:53:00",60322052,"Short Rural","Other","Service Fuse",1,93.966666666666697,2.3253032421441603E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","06:58:00",60026682,"Long Rural","Other","Fuse Operator - No Trigger Found",1,75.05,9.815589850902431E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-01","07:25:00",30053778,"Long Rural","Other","Forced Corrective Maintenance",15,426,8.3573110122940109E-2,1.9618100967826299E-4,"NO"]
[null,"2017-07-01","07:40:00",20005577,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-01","07:50:00",20008226,"Short Rural","Animal","Animal impact",1,50.199999999999996,1.2422513950582201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","07:51:00",10020855,"Short Rural","Animal","Animal impact",1,126.366666666667,3.1270750588749602E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","07:59:00",60026787,"Long Rural","Overloads",null,1,218.28333333333299,2.8548696486180099E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","08:01:00",83850831,"Short Rural","Planned",null,3,29,0,0,"NO"]
[null,"2017-07-01","08:05:00",50000144,"Short Rural","Planned",null,2,105,0,0,"NO"]
[null,"2017-07-01","08:25:00",20005577,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-01","08:30:00",84326665,"Short Rural","Planned",null,278,354.85611510791404,0,0,"NO"]
[null,"2017-07-01","08:35:00",82563612,"Long Rural","Planned",null,2,138,0,0,"NO"]
[null,"2017-07-01","08:52:00",10020809,"Urban","Planned",null,8,127,0,0,"NO"]
[null,"2017-07-01","09:00:00",20005577,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-01","09:00:00",50000170,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-01","09:04:00",20001353,"Short Rural","Other","Service Fuse",1,45.5833333333333,1.12800715985532E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","09:10:00",60026840,"Urban","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-01","09:13:00",60026696,"Long Rural","Other","Forced Corrective Maintenance",1,93,1.21632226000523E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","09:14:00",30053835,"Urban","Other","Service Fuse",2,79.900000000000006,7.0647320441744705E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-01","09:15:00",50000169,"Short Rural","Planned",null,12,15,0,0,"NO"]
[null,"2017-07-01","09:25:00",50000170,"Short Rural","Planned",null,3,10,0,0,"NO"]
[null,"2017-07-01","09:30:00",60026734,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005133,"Long Rural","2 or 3 - STPIS Exclusion (3.3)(a)",null,1137,14.866666666666699,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005188,"Short Rural","2 or 3 - STPIS Exclusion (3.3)(a)",null,537,13.1,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005265,"Short Rural","2 or 3 - STPIS Exclusion (3.3)(a)",null,1210,13.15,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005314,"Short Rural","2 or 3 - STPIS Exclusion (3.3)(a)",null,792,13.533333333333299,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005336,"Urban","2 or 3 - STPIS Exclusion (3.3)(a)",null,888,14,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005357,"Urban","2 or 3 - STPIS Exclusion (3.3)(a)",null,673,14.3,0,0,"NO"]
[null,"2017-07-01","09:35:00",20005412,"Urban","2 or 3 - STPIS Exclusion (3.3)(a)",null,1641,14.5833333333333,0,0,"NO"]
[null,"2017-07-01","09:35:00",25273020,"Urban","2 or 3 - STPIS Exclusion (3.3)(a)",null,998,13,0,0,"NO"]
[null,"2017-07-01","09:45:00",20005577,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-01","09:56:00",20013260,"Short Rural","Other","Fuse Operator - No Trigger Found",1,54.016666666666701,1.3366987952800999E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","10:00:00",40001139,"Long Rural","Planned",null,43,244,0,0,"NO"]
[null,"2017-07-01","10:04:00",30053845,"Short Rural","Overloads",null,1,148.98333333333301,3.6867480811505294E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","10:06:00",60026997,"Long Rural","Other","Fuse Operator - No Trigger Found",1,71.983333333333306,9.4145086755602098E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-01","10:12:00",40000974,"Long Rural","Other","Fuse Operator - No Trigger Found",1,114.883333333333,1.5025285552358501E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","10:20:00",83879351,"Short Rural","Other","Forced Corrective Maintenance",21,26,1.3511339874537601E-3,5.1966691825144498E-5,"NO"]
[null,"2017-07-01","10:21:00",10020835,"Urban","Asset failure","LV",2,123.7,1.0937513815574202E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-01","10:30:00",20002622,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-01","10:30:00",20005577,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-01","10:30:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-01","10:43:00",60026734,"Long Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-07-01","10:58:00",20005412,"Urban","Overloads",null,1,422,1.8656551455830002E-3,4.4209837573056797E-6,"NO"]
[null,"2017-07-01","11:00:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-01","11:17:00",60026734,"Long Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-01","11:30:00",20005577,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-01","11:30:00",50000167,"Short Rural","Planned",null,3,10,0,0,"NO"]
[null,"2017-07-01","11:30:00",82563612,"Long Rural","Planned",null,1,68,0,0,"NO"]
[null,"2017-07-01","11:47:00",20002698,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-01","12:00:00",10020809,"Urban","Planned",null,43,29,0,0,"NO"]
[null,"2017-07-01","12:00:00",20002622,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-01","12:00:00",50000170,"Short Rural","Planned",null,3,15,0,0,"NO"]
[null,"2017-07-01","12:10:00",20005577,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-01","12:11:00",82563612,"Long Rural","Other","Fuse Operator - No Trigger Found",1,97.466666666666697,1.2747406051094301E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","12:25:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-01","12:33:00",20007111,"Short Rural","Other","Service Fuse",1,49.050000000000004,1.2137934447730201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","12:40:00",20005577,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-01","12:41:00",50000043,"Short Rural","Other","Fuse Operator - No Trigger Found",1,68.266666666666708,1.6893299183793001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","12:41:00",60026822,"Urban","Animal","Animal impact",53,65.6666666666667,1.5386497136676202E-2,2.34312139137201E-4,"NO"]
[null,"2017-07-01","12:50:00",60026734,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-01","13:00:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-01","13:30:00",60026699,"Short Rural","Other","Service Fuse",1,115.566666666667,2.8598177866313602E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","13:33:00",60026718,"Short Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-01","13:40:00",50000169,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-01","13:58:00",50000195,"Urban","Overloads",null,1,67.8,2.9974269874532498E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-01","14:00:00",50000170,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-01","14:02:00",20009806,"Short Rural","Exclusion - Customer Installation Fault",null,1,49.95,0,0,"NO"]
[null,"2017-07-01","14:20:00",60026791,"Urban","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-01","14:32:00",30053837,"Short Rural","Animal","Animal impact",112,65.976488095238111,1.8285759064269602E-2,2.7715568973410399E-4,"NO"]
[null,"2017-07-01","14:35:00",60026701,"Long Rural","Other","Forced Corrective Maintenance",2,155,4.0544075333507701E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-01","14:49:00",20001353,"Short Rural","Other","Fuse Operator - No Trigger Found",1,63.5833333333333,1.5734359469279802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","14:49:00",60026791,"Urban","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-01","14:51:00",60026677,"Short Rural","Other","Service Fuse",1,122.05,3.02025463678994E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","15:01:00",82912904,"Urban","Other","Service Fuse",1,90.533333333333303,4.0024639616140705E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-01","15:20:00",60026791,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-01","15:32:00",40001118,"Long Rural","Other","Service Fuse",1,193.63333333333301,2.5324788560467304E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","16:30:00",30053848,"Short Rural","Other","Fuse Operator - No Trigger Found",1,167.86666666666699,4.1540358735147199E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","17:10:00",60026650,"Long Rural","Overloads",null,1,139.25,1.8212137065132103E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-01","17:54:00",82914591,"Urban","Other","Service Fuse",1,88.85,3.9280440683660901E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-01","18:42:00",83022298,"Short Rural","Asset failure","LV",1,133.94999999999999,3.31473255713243E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","18:55:00",60026699,"Short Rural","Other","Service Fuse",1,68.683333333333294,1.6996407699319103E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","18:58:00",40000974,"Long Rural","Other","Service Fuse",1,75.5,9.874444153805909E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-01","20:05:00",82773016,"Urban","Overloads",null,2,81,7.1619936868351909E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-01","20:40:00",85081013,"Short Rural","Other","Service Fuse",1,91.733333333333306,2.2700370778221802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-01","20:45:00",60026822,"Urban","Other","Service Fuse",2,52.5,4.6420329451709599E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-01","21:29:00",60026840,"Urban","Other","Fuse Operator - No Trigger Found",1,91.966666666666697,4.0658313954687896E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-01","22:05:00",20010920,"Long Rural","Other","Fuse Operator - No Trigger Found",31,78.2,3.1705466910802997E-2,4.0544075333507701E-4,"NO"]
[null,"2017-07-02","01:28:00",50000065,"Long Rural","Asset failure","HV",568,356.95176056337999,2.6516950039236198,7.4287208998168996E-3,"NO"]
[null,"2017-07-02","02:14:00",50000066,"Short Rural","Asset failure","Distribution substation",17,282.98333333333301,1.1904620498797799E-2,4.2068274334640702E-5,"NO"]
[null,"2017-07-02","03:17:00",20002622,"Short Rural","Asset failure","LV",1,108.933333333333,2.6956690299138403E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","04:17:00",50000066,"Short Rural","Other","Forced Corrective Maintenance",945,75,0.175387584909863,2.3385011321315004E-3,"NO"]
[null,"2017-07-02","05:10:00",20002698,"Short Rural","Other","Service Fuse",1,57.449999999999996,1.42166021207359E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","05:14:00",20002698,"Short Rural","Other","Service Fuse",2,111.05,5.4960963116021801E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-02","06:07:00",50000159,"Long Rural","Animal","Animal impact",181,291.86666666666702,0.69092161478768899,2.3672508501177106E-3,"NO"]
[null,"2017-07-02","06:15:00",10020796,"Urban","Other","Service Fuse",1,90.633333333333297,4.0068849453713803E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-02","06:15:00",20001488,"Short Rural","Other","Service Fuse",1,50.183333333333302,1.24183896099611E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","06:24:00",20001488,"Short Rural","Other","Service Fuse",1,41.966666666666697,1.0385089683786801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","06:31:00",20001488,"Short Rural","Other","Service Fuse",1,34.299999999999997,8.4878929981069295E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","06:37:00",50000241,"Long Rural","Third party","Other - Third Party",1,149.26666666666699,1.9522190251983599E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-02","07:00:00",10020809,"Urban","Planned",null,17,75,0,0,"NO"]
[null,"2017-07-02","07:01:00",83864041,"Short Rural","Animal","Animal impact",86,140.53333333333299,2.9907738500307302E-2,2.1281597604583E-4,"NO"]
[null,"2017-07-02","07:17:00",30053833,"Short Rural","Asset failure","HV",1,214.01666666666699,5.2960657914815897E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","07:33:00",82563612,"Long Rural","Other","Fuse Operator - No Trigger Found",1,97.8,1.2791001831022801E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-02","07:37:00",20007427,"Urban","Other","Service Fuse",3,93.733333333333306,1.24318063255436E-3,1.3262951271916999E-5,"NO"]
[null,"2017-07-02","07:56:00",82556066,"Short Rural","Other","Service Fuse",1,95.066666666666706,2.3525238902430499E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","08:00:00",20007373,"Urban","Planned",null,3,380,0,0,"NO"]
[null,"2017-07-02","08:00:00",30053832,"Short Rural","Planned",null,10,180,0,0,"NO"]
[null,"2017-07-02","08:01:00",25267746,"Short Rural","Planned",null,14,318,0,0,"NO"]
[null,"2017-07-02","08:11:00",30053830,"Short Rural","Planned",null,3,329,0,0,"NO"]
[null,"2017-07-02","08:21:00",60331115,"Urban","Planned",null,45,103,0,0,"NO"]
[null,"2017-07-02","08:30:00",10020809,"Urban","Planned",null,55,190,0,0,"NO"]
[null,"2017-07-02","08:30:00",40001146,"Urban","Planned",null,104,206,0,0,"NO"]
[null,"2017-07-02","08:30:00",82921017,"Urban","Planned",null,73,93,0,0,"NO"]
[null,"2017-07-02","08:38:00",10020809,"Urban","Planned",null,16,208,0,0,"NO"]
[null,"2017-07-02","08:41:00",20004592,"Short Rural","Other","Service Fuse",1,81.6666666666667,2.02092690431117E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","08:52:00",60026819,"Long Rural","Asset failure","HV",1,313.01666666666705,4.0938617141860712E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-02","09:02:00",50000025,"Long Rural","Planned",null,17,257,0,0,"NO"]
[null,"2017-07-02","09:07:00",60026666,"Long Rural","Other","Forced Corrective Maintenance",4,199,1.0410672246926501E-2,5.2314935914203499E-5,"NO"]
[null,"2017-07-02","09:10:00",50000211,"Short Rural","Animal","Animal impact",1,102.316666666667,2.5319327072584297E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","09:36:00",85081013,"Short Rural","Planned",null,5,352,0,0,"NO"]
[null,"2017-07-02","10:07:00",10020659,"Long Rural","Other","Service Fuse",2,129.23333333333301,3.3804167756561199E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-02","10:34:00",60026730,"Urban","Planned",null,1,42,0,0,"NO"]
[null,"2017-07-02","10:51:00",20011656,"Urban","Other","Service Fuse",1,121.433333333333,5.3685479426215303E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-02","10:52:00",30053777,"Short Rural","Other","Forced Corrective Maintenance",72,104.258333333333,1.8575865183553801E-2,1.7817151482906702E-4,"NO"]
[null,"2017-07-02","11:38:00",83868949,"Short Rural","Other","Forced Corrective Maintenance",61,1527,0.23050197349698698,1.5095086673018202E-4,"NO"]
[null,"2017-07-02","11:51:00",84023546,"Short Rural","Asset failure","HV",301,162.95880398671099,0.12138082923992501,7.4485591616040394E-4,"NO"]
[null,"2017-07-02","12:25:00",60026840,"Urban","Planned",null,15,129,0,0,"NO"]
[null,"2017-07-02","12:30:00",82888836,"Urban","Exclusion - Customer Installation Fault",null,1,20,0,0,"NO"]
[null,"2017-07-02","12:55:00",20001649,"Short Rural","Other","Forced Corrective Maintenance",66,25.633333333333301,4.1865356776085404E-3,1.6332388859331099E-4,"NO"]
[null,"2017-07-02","13:59:00",84965685,"Short Rural","Other","Fuse Operator - No Trigger Found",2,101.26666666666701,5.0118987226917104E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-02","15:41:00",30188733,"Short Rural","Asset failure","LV",1,63.949999999999996,1.5825094962942802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","16:14:00",30189394,"Short Rural","Third party","Vehicle impact",1,110.633333333333,2.7377373042484804E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","16:14:00",50000142,"Short Rural","Other","Service Fuse",1,79.383333333333297,1.96442343780288E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","16:54:00",60026662,"Long Rural","Asset failure","LV",1,255.583333333333,3.34270642601796E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-02","17:46:00",30186258,"Urban","Asset failure","HV",655,99.599618320610688,0.28841503311316802,2.89574436103522E-3,"NO"]
[null,"2017-07-02","18:38:00",20004592,"Short Rural","Asset failure","LV",1,41.1666666666667,1.01871213339767E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","18:43:00",30187535,"Short Rural","Other","Service Fuse",1,297.90000000000003,7.3718464260526294E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","19:15:00",10020669,"Long Rural","Asset failure","LV",2,358.68333333333305,9.3822477984131097E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-02","19:36:00",30053769,"Short Rural","Other","Service Fuse",1,37.0833333333333,9.1766578818211394E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-02","19:48:00",20006666,"Short Rural","Other","Service Fuse",2,50.050000000000004,2.4770789769985499E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-02","22:19:00",82647147,"Urban","Other","Service Fuse",1,125.416666666667,5.54465046228753E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-03","00:33:00",40001215,"Urban","Exclusion - Customer Installation Fault",null,1,28,0,0,"NO"]
[null,"2017-07-03","05:13:00",30053867,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",93,101.066666666667,2.3259301419185599E-2,2.3013820665421101E-4,"NO"]
[null,"2017-07-03","05:26:00",60026784,"Urban","Planned",null,36,31,0,0,"NO"]
[null,"2017-07-03","05:30:00",20006023,"Short Rural","Asset failure","HV",1,92.066666666666706,2.27828575906427E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","05:46:00",20006023,"Short Rural","Asset failure","HV",1,94.8333333333333,2.3467498133735901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","06:24:00",60026997,"Long Rural","Overloads",null,1,214.28333333333299,2.8025547127038101E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-03","06:59:00",20003294,"Urban","Other","Service Fuse",2,109.85000000000001,9.7129013148005696E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-03","07:18:00",82920985,"Urban","Other","Fuse Operator - No Trigger Found",1,65.033333333333303,2.8751131035011199E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-03","07:43:00",50000126,"Short Rural","Animal","Animal impact",38,18.466666666666701,1.73651237508403E-3,9.4034966159785207E-5,"NO"]
[null,"2017-07-03","08:00:00",50000074,"Short Rural","Planned",null,1,360,0,0,"NO"]
[null,"2017-07-03","08:00:00",84666984,"Urban","Planned",null,3,240,0,0,"NO"]
[null,"2017-07-03","08:05:00",82552955,"Short Rural","Planned",null,3,195,0,0,"NO"]
[null,"2017-07-03","08:10:00",83877404,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-03","08:15:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-03","08:15:00",82915271,"Urban","Planned",null,3,15,0,0,"NO"]
[null,"2017-07-03","08:15:00",84064752,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-03","08:16:00",50000139,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-03","08:25:00",82915231,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","08:27:00",20002437,"Short Rural","Other","Service Fuse",1,67,1.6579849296593702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","08:30:00",20002622,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-03","08:30:00",40001116,"Long Rural","Planned",null,1,242,0,0,"NO"]
[null,"2017-07-03","08:30:00",40001120,"Short Rural","Planned",null,59,278,0,0,"NO"]
[null,"2017-07-03","08:30:00",50000166,"Urban","Planned",null,8,240,0,0,"NO"]
[null,"2017-07-03","08:30:00",50000180,"Short Rural","Planned",null,2,29.016666666666698,0,0,"NO"]
[null,"2017-07-03","08:31:00",10020774,"Short Rural","Planned",null,50,123,0,0,"NO"]
[null,"2017-07-03","08:37:00",20008110,"Short Rural","Planned",null,28,337.78571428571399,0,0,"NO"]
[null,"2017-07-03","08:37:00",30053771,"Short Rural","Animal","Animal impact",1,38.316666666666698,9.4818590877783401E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","08:39:00",50000175,"Short Rural","Planned",null,1,56.05,0,0,"NO"]
[null,"2017-07-03","08:40:00",50000167,"Short Rural","Planned",null,2,11,0,0,"NO"]
[null,"2017-07-03","08:45:00",82915231,"Urban","Planned",null,1,54.999999999999993,0,0,"NO"]
[null,"2017-07-03","08:47:00",40001063,"Long Rural","Asset failure","LV",1,398.93333333333305,5.2175429418432305E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-03","08:50:00",82915231,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-03","08:53:00",10020804,"Short Rural","Other","Service Fuse",1,123.666666666667,3.0602607408140598E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","08:55:00",20002622,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","08:55:00",60026840,"Urban","Planned",null,1,45.999999999999993,0,0,"NO"]
[null,"2017-07-03","09:00:00",60026666,"Long Rural","Planned",null,40,55,0,0,"NO"]
[null,"2017-07-03","09:00:00",82773016,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-03","09:02:00",10020826,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-03","09:02:00",60026711,"Short Rural","Planned",null,7,125,0,0,"NO"]
[null,"2017-07-03","09:06:00",50000180,"Short Rural","Planned",null,12,86,0,0,"NO"]
[null,"2017-07-03","09:10:00",40001009,"Long Rural","Planned",null,7,298,0,0,"NO"]
[null,"2017-07-03","09:15:00",50000167,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-03","09:15:00",50000180,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-03","09:30:00",82563099,"Urban","Planned",null,3,10,0,0,"NO"]
[null,"2017-07-03","09:30:00",83877341,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","09:31:00",40001063,"Long Rural","Planned",null,1,201,0,0,"NO"]
[null,"2017-07-03","09:31:00",60026783,"Long Rural","Other","Service Fuse",1,58.050000000000004,7.5922050745487804E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-03","09:32:00",20002698,"Short Rural","Planned",null,2,6,0,0,"NO"]
[null,"2017-07-03","09:33:00",84332614,"Short Rural","Third party","Vehicle impact",1,60.199999999999996,1.48971183232081E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","09:38:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","09:40:00",50000096,"Urban","Other","Service Fuse",1,96,4.2441444070134496E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-03","09:40:00",83022292,"Long Rural","Other","Forced Corrective Maintenance",1,8,1.0462987182840701E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-03","09:45:00",20004592,"Short Rural","Other","Service Fuse",2,22.6,1.1185211764269201E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-03","09:50:00",50000167,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-03","09:55:00",10020832,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","10:10:00",50000167,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-03","10:10:00",50000170,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-03","10:15:00",40223076,"Long Rural","Planned",null,1,150.13333333333301,0,0,"NO"]
[null,"2017-07-03","10:15:00",50000180,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-03","10:27:00",85081013,"Short Rural","Planned",null,2,18,0,0,"NO"]
[null,"2017-07-03","10:30:00",20013064,"Short Rural","Other","Service Fuse",1,105.3,2.6057584043751004E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","10:30:00",82915259,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-03","10:33:00",50000170,"Short Rural","Planned",null,2,19,0,0,"NO"]
[null,"2017-07-03","10:36:00",50000175,"Short Rural","Planned",null,1,69.649999999999991,0,0,"NO"]
[null,"2017-07-03","10:37:00",30053847,"Short Rural","Other","Fuse Operator - No Trigger Found",1,52.633333333333304,1.3024667681254501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","10:40:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","10:40:00",60026819,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-03","10:45:00",20002698,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-03","10:54:00",50000180,"Short Rural","Planned",null,1,59.633333333333304,0,0,"NO"]
[null,"2017-07-03","10:55:00",10020832,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-03","11:00:00",50000170,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-03","11:00:00",82773016,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","11:00:00",83877341,"Urban","Planned",null,1,54.999999999999993,0,0,"NO"]
[null,"2017-07-03","11:03:00",20003349,"Urban","Other","Forced Corrective Maintenance",223,26,2.5632863824858302E-2,9.8587937787916594E-4,"NO"]
[null,"2017-07-03","11:04:00",50000113,"Short Rural","Asset failure","HV",4,373.96666666666704,3.7016781941986996E-3,9.8984174905037098E-6,"NO"]
[null,"2017-07-03","11:05:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","11:07:00",50000118,"Long Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-03","11:10:00",82915271,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-03","11:11:00",60026644,"Long Rural","Other","Vibration",2,177.316666666667,4.6381550265934312E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-03","11:13:00",50000169,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-03","11:15:00",50000180,"Short Rural","Planned",null,2,35,0,0,"NO"]
[null,"2017-07-03","11:15:00",60026730,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-03","11:20:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","11:25:00",50000175,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","11:30:00",83877341,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","11:32:00",50000170,"Short Rural","Planned",null,2,24,0,0,"NO"]
[null,"2017-07-03","11:32:00",82563099,"Urban","Asset failure","LV",4,95.6666666666667,1.69176311779564E-3,1.7683935029222702E-5,"NO"]
[null,"2017-07-03","11:33:00",40001129,"Short Rural","Third party","Vehicle impact",1,188.01666666666699,4.6526686545988501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","11:35:00",50000118,"Long Rural","Planned",null,1,54.999999999999993,0,0,"NO"]
[null,"2017-07-03","11:40:00",40001227,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","11:45:00",10020826,"Short Rural","Planned",null,2,2,0,0,"NO"]
[null,"2017-07-03","11:50:00",50000175,"Short Rural","Planned",null,1,54.866666666666696,0,0,"NO"]
[null,"2017-07-03","11:50:00",60026819,"Long Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-03","12:00:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","12:05:00",20002622,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","12:06:00",50000213,"Urban","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-03","12:10:00",50000170,"Short Rural","Planned",null,2,16,0,0,"NO"]
[null,"2017-07-03","12:14:00",25273220,"Short Rural","Other","Service Fuse",1,128.36666666666699,3.1765671463274798E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","12:15:00",50000175,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-03","12:15:00",50000180,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-03","12:35:00",50000169,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-03","12:38:00",60026847,"Long Rural","Asset failure","HV",1,42.949999999999996,5.6173162437875995E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-03","12:40:00",10020783,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-03","12:50:00",40001156,"Short Rural","Other","Fuse Operator - No Trigger Found",46,163.9,1.8657032206975902E-2,1.13831801140793E-4,"NO"]
[null,"2017-07-03","12:50:00",50000169,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-03","13:00:00",50000117,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","13:00:00",60026641,"Long Rural","Planned",null,12,39,0,0,"NO"]
[null,"2017-07-03","13:05:00",50000167,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-03","13:10:00",50000169,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-03","13:10:00",82915271,"Urban","Planned",null,8,30,0,0,"NO"]
[null,"2017-07-03","13:15:00",50000175,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-03","13:17:00",40001091,"Urban","Other","Forced Corrective Maintenance",1,146.683333333333,6.4848463413412103E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-03","13:20:00",60330968,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","13:30:00",40001116,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-03","13:35:00",40001174,"Short Rural","Other","Forced Corrective Maintenance",1,5,1.2373021863129598E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","13:40:00",50000169,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-03","13:55:00",50000175,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-03","14:00:00",50000170,"Short Rural","Planned",null,3,9,0,0,"NO"]
[null,"2017-07-03","14:05:00",60330968,"Short Rural","Planned",null,5,48,0,0,"NO"]
[null,"2017-07-03","14:13:00",50000118,"Long Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-03","14:20:00",50000169,"Short Rural","Planned",null,2,9,0,0,"NO"]
[null,"2017-07-03","14:25:00",60026774,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-03","14:28:00",30053746,"Short Rural","Asset failure","LV",1,67.716666666666711,1.6757195943298601E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","14:30:00",50000169,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-03","14:33:00",10020679,"Short Rural","Other","Forced Corrective Maintenance",123,75.407317073170688,2.2952203016542699E-2,3.0437633783298899E-4,"NO"]
[null,"2017-07-03","14:40:00",60026805,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-03","14:45:00",50000073,"Short Rural","Asset failure","HV",1,128.583333333333,3.18192878913484E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","14:48:00",60026644,"Long Rural","Planned",null,6,111,0,0,"NO"]
[null,"2017-07-03","14:54:00",50000118,"Long Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-03","15:00:00",50000169,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-03","15:00:00",50000175,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-03","15:07:00",50000180,"Short Rural","Planned",null,2,27,0,0,"NO"]
[null,"2017-07-03","15:09:00",60026747,"Long Rural","Third party","Vehicle impact",1,58.266666666666701,7.6205423315023107E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-03","15:10:00",60026805,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-03","15:15:00",60330968,"Short Rural","Planned",null,1,28,0,0,"NO"]
[null,"2017-07-03","15:20:00",10020786,"Urban","Planned",null,3,5,0,0,"NO"]
[null,"2017-07-03","15:25:00",50000166,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-03","15:31:00",60027003,"Long Rural","Overloads",null,1,61.599999999999994,8.0565001307873394E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-03","15:52:00",20006799,"Short Rural","Other","Service Fuse",1,172.566666666667,4.2703422790281404E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","15:55:00",50000170,"Short Rural","Planned",null,3,44,0,0,"NO"]
[null,"2017-07-03","16:00:00",82647147,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","16:22:00",30053882,"Short Rural","Asset failure","LV",1,65.433333333333294,1.61921612782156E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","16:40:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-03","16:43:00",20004751,"Urban","Other","Service Fuse",1,101.183333333333,4.4732987317671295E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-03","17:00:00",60026734,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-03","17:04:00",40001191,"Short Rural","Other","Service Fuse",1,74.783333333333303,1.8505916366620901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","17:05:00",20001649,"Short Rural","Other","Fuse Operator - No Trigger Found",1,46.966666666666697,1.1622391870099801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","17:18:00",10020777,"Short Rural","Third party","Fire",1,100.583333333333,2.4890395647995798E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","17:21:00",50000142,"Short Rural","Other","Service Fuse",2,64.2,3.1773920144516896E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-03","18:29:00",10020787,"Short Rural","Other","Service Fuse",1,104.5,2.5859615693940905E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","18:31:00",20013273,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",17,131.988235294118,5.5525172912980507E-3,4.2068274334640702E-5,"NO"]
[null,"2017-07-03","18:43:00",50000127,"Long Rural","Other","Fuse Operator - No Trigger Found",1,95.133333333333297,1.2442235591594698E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-03","19:07:00",10020826,"Short Rural","Other","Service Fuse",1,99.1666666666667,2.4539826695207099E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-03","19:08:00",40001009,"Long Rural","Animal","Animal impact",1,78.8,1.0306042375098103E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-03","20:26:00",60026802,"Short Rural","Animal","Other",5,80.016666666666708,9.9004796608142317E-4,1.2373021863129598E-5,"NO"]
[null,"2017-07-03","21:06:00",60026770,"Urban","Other","Fuse Operator - No Trigger Found",1,85.366666666666703,3.7740464674866099E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-03","21:56:00",50000092,"Short Rural","Other","Service Fuse",1,63.933333333333302,1.5820970622321801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","06:00:00",10020822,"Urban","Planned",null,1,175,0,0,"NO"]
[null,"2017-07-04","06:20:00",40001095,"Urban","Asset failure","LV",1,181.28333333333299,8.0145067213689702E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-04","07:01:00",82912277,"Short Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-04","08:00:00",40001116,"Long Rural","Planned",null,1,185,0,0,"NO"]
[null,"2017-07-04","08:00:00",50000170,"Short Rural","Planned",null,3,25,0,0,"NO"]
[null,"2017-07-04","08:00:00",60026649,"Urban","Planned",null,2,143,0,0,"NO"]
[null,"2017-07-04","08:00:00",83022292,"Long Rural","Planned",null,2,132,0,0,"NO"]
[null,"2017-07-04","08:02:00",60026840,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","08:10:00",20002622,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-04","08:10:00",30053775,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","08:10:00",40223076,"Long Rural","Planned",null,1,163,0,0,"NO"]
[null,"2017-07-04","08:10:00",50000169,"Short Rural","Planned",null,7,19,0,0,"NO"]
[null,"2017-07-04","08:11:00",10020809,"Urban","Planned",null,5,14,0,0,"NO"]
[null,"2017-07-04","08:15:00",20002652,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","08:28:00",30053834,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-04","08:29:00",50000170,"Short Rural","Planned",null,3,12,0,0,"NO"]
[null,"2017-07-04","08:30:00",10020781,"Short Rural","Planned",null,4,166,0,0,"NO"]
[null,"2017-07-04","08:30:00",10020798,"Short Rural","Planned",null,39,300,0,0,"NO"]
[null,"2017-07-04","08:30:00",10020807,"Urban","Planned",null,14,240,0,0,"NO"]
[null,"2017-07-04","08:30:00",10020856,"Short Rural","Planned",null,2,270,0,0,"NO"]
[null,"2017-07-04","08:30:00",20005447,"Short Rural","Planned",null,5,240,0,0,"NO"]
[null,"2017-07-04","08:30:00",20007427,"Urban","Planned",null,6,241,0,0,"NO"]
[null,"2017-07-04","08:30:00",20008110,"Short Rural","Planned",null,77,324,0,0,"NO"]
[null,"2017-07-04","08:30:00",40001237,"Urban","Planned",null,104,331.63461538461502,0,0,"NO"]
[null,"2017-07-04","08:30:00",50000175,"Short Rural","Planned",null,3,50,0,0,"NO"]
[null,"2017-07-04","08:30:00",50000180,"Short Rural","Planned",null,2,75.600000000000009,0,0,"NO"]
[null,"2017-07-04","08:30:00",82915271,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-04","08:33:00",50000040,"Long Rural","Planned",null,5,100,0,0,"NO"]
[null,"2017-07-04","08:37:00",82920985,"Urban","Planned",null,80,214,0,0,"NO"]
[null,"2017-07-04","08:38:00",60026741,"Short Rural","Planned",null,23,302,0,0,"NO"]
[null,"2017-07-04","08:41:00",50000067,"Short Rural","Planned",null,1,360,0,0,"NO"]
[null,"2017-07-04","08:41:00",82915271,"Urban","Planned",null,2,19,0,0,"NO"]
[null,"2017-07-04","08:42:00",50000043,"Short Rural","Other","Fuse Operator - No Trigger Found",1,95.5,2.3632471758577603E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","08:45:00",60026702,"Short Rural","Planned",null,1,24,0,0,"NO"]
[null,"2017-07-04","08:46:00",50000170,"Short Rural","Planned",null,2,14,0,0,"NO"]
[null,"2017-07-04","08:47:00",60026691,"Short Rural","Planned",null,1,319,0,0,"NO"]
[null,"2017-07-04","08:50:00",30053819,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-04","08:55:00",40000969,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","08:58:00",20006948,"Short Rural","Other","Fuse Operator - No Trigger Found",1,47.1666666666667,1.1671883957552301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","09:00:00",10020722,"Short Rural","Planned",null,66,327,0,0,"NO"]
[null,"2017-07-04","09:00:00",10020857,"Short Rural","Planned",null,46,229,0,0,"NO"]
[null,"2017-07-04","09:00:00",30053847,"Short Rural","Planned",null,73,351,0,0,"NO"]
[null,"2017-07-04","09:00:00",50000044,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","09:00:00",50000057,"Long Rural","Planned",null,1,183,0,0,"NO"]
[null,"2017-07-04","09:00:00",60026649,"Urban","Planned",null,1,201,0,0,"NO"]
[null,"2017-07-04","09:00:00",60026670,"Long Rural","Planned",null,1,36.999999999999993,0,0,"NO"]
[null,"2017-07-04","09:00:00",60026758,"Short Rural","Planned",null,5,153.21666666666698,0,0,"NO"]
[null,"2017-07-04","09:00:00",83850831,"Short Rural","Planned",null,4,360,0,0,"NO"]
[null,"2017-07-04","09:00:00",83909007,"Short Rural","Planned",null,75,60,0,0,"NO"]
[null,"2017-07-04","09:02:00",50000061,"Short Rural","Planned",null,6,46,0,0,"NO"]
[null,"2017-07-04","09:02:00",50000175,"Short Rural","Planned",null,53,123,0,0,"NO"]
[null,"2017-07-04","09:04:00",50000145,"Long Rural","Planned",null,7,86,0,0,"NO"]
[null,"2017-07-04","09:05:00",50000170,"Short Rural","Planned",null,2,11,0,0,"NO"]
[null,"2017-07-04","09:05:00",60026823,"Urban","Planned",null,14,340,0,0,"NO"]
[null,"2017-07-04","09:10:00",50000170,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","09:13:00",10020809,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-04","09:14:00",50000142,"Short Rural","Overloads",null,2,45.783333333333303,2.2659127372011401E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-04","09:18:00",85068151,"Short Rural","Planned",null,8,391.5,0,0,"NO"]
[null,"2017-07-04","09:19:00",50000170,"Short Rural","Planned",null,2,21,0,0,"NO"]
[null,"2017-07-04","09:21:00",60026641,"Long Rural","Planned",null,1,157,0,0,"NO"]
[null,"2017-07-04","09:25:00",30053773,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","09:27:00",40001175,"Urban","Asset failure","LV",1,186.73333333333301,8.2554503361421299E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-04","09:30:00",10134518,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-04","09:30:00",20009493,"Short Rural","Planned",null,5,165,0,0,"NO"]
[null,"2017-07-04","09:30:00",40001001,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","09:30:00",50000025,"Long Rural","Planned",null,3,250,0,0,"NO"]
[null,"2017-07-04","09:30:00",60026734,"Long Rural","Planned",null,2,148,0,0,"NO"]
[null,"2017-07-04","09:30:00",82915271,"Urban","Planned",null,10,30,0,0,"NO"]
[null,"2017-07-04","09:32:00",20010298,"Urban","Planned",null,48,98,0,0,"NO"]
[null,"2017-07-04","09:35:00",50000175,"Short Rural","Planned",null,3,35,0,0,"NO"]
[null,"2017-07-04","09:40:00",20007229,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","09:40:00",60026678,"Short Rural","Other","Forced Corrective Maintenance",1,15,3.7119065589388895E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","09:45:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-04","09:46:00",60026670,"Long Rural","Planned",null,1,191,0,0,"NO"]
[null,"2017-07-04","09:47:00",30053819,"Short Rural","Planned",null,1,29,0,0,"NO"]
[null,"2017-07-04","09:50:00",50000170,"Short Rural","Planned",null,5,22,0,0,"NO"]
[null,"2017-07-04","09:50:00",60322052,"Short Rural","Overloads",null,1,268.14999999999998,6.6356516251964202E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","09:53:00",60026741,"Short Rural","Other","Fuse Operator - No Trigger Found",1,171.8,4.2513703121713404E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","09:56:00",83877341,"Urban","Planned",null,1,63.999999999999993,0,0,"NO"]
[null,"2017-07-04","10:00:00",40001066,"Long Rural","Planned",null,13,315,0,0,"NO"]
[null,"2017-07-04","10:00:00",40001116,"Long Rural","Planned",null,3,138,0,0,"NO"]
[null,"2017-07-04","10:02:00",82651966,"Short Rural","Planned",null,4,231,0,0,"NO"]
[null,"2017-07-04","10:05:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","10:12:00",50000066,"Short Rural","Other","Service Fuse",1,269.03333333333302,6.6575106304879504E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","10:13:00",30053773,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-04","10:18:00",30053780,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-04","10:20:00",50000233,"Short Rural","Planned",null,2,26.5,0,0,"NO"]
[null,"2017-07-04","10:25:00",50000175,"Short Rural","Planned",null,3,35,0,0,"NO"]
[null,"2017-07-04","10:26:00",30053773,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-04","10:26:00",50000116,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-04","10:30:00",20007229,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-04","10:31:00",40001193,"Short Rural","Planned",null,1,62,0,0,"NO"]
[null,"2017-07-04","10:31:00",50000167,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-04","10:35:00",50000035,"Short Rural","Planned",null,4,35,0,0,"NO"]
[null,"2017-07-04","10:40:00",10020783,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","10:40:00",50000126,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","10:40:00",82915271,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-04","10:45:00",30053773,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","10:47:00",60026644,"Long Rural","Planned",null,1,103,0,0,"NO"]
[null,"2017-07-04","10:47:00",83877341,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-04","10:50:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","10:55:00",10020809,"Urban","Planned",null,16,11,0,0,"NO"]
[null,"2017-07-04","11:00:00",50000167,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-04","11:02:00",30053868,"Short Rural","Planned",null,3,172,0,0,"NO"]
[null,"2017-07-04","11:02:00",60026840,"Urban","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-04","11:04:00",40000964,"Long Rural","Overloads",null,24,132.25,4.1511901647920492E-2,3.1388961548522103E-4,"NO"]
[null,"2017-07-04","11:05:00",82647141,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","11:10:00",50000167,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-04","11:10:00",60026837,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-04","11:10:00",82841186,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","11:10:00",82914179,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-04","11:15:00",50000175,"Short Rural","Planned",null,3,35,0,0,"NO"]
[null,"2017-07-04","11:18:00",50000116,"Short Rural","Planned",null,1,38,0,0,"NO"]
[null,"2017-07-04","11:24:00",20007334,"Urban","Planned",null,2,13,0,0,"NO"]
[null,"2017-07-04","11:30:00",20007229,"Short Rural","Planned",null,2,40,0,0,"NO"]
[null,"2017-07-04","11:30:00",30053752,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","11:30:00",40000977,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","11:30:00",60026649,"Urban","Planned",null,1,56.999999999999993,0,0,"NO"]
[null,"2017-07-04","11:31:00",10020800,"Urban","Other","Service Fuse",1,182.95000000000002,8.0881897839907312E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-04","11:31:00",50000167,"Short Rural","Planned",null,1,29,0,0,"NO"]
[null,"2017-07-04","11:32:00",83879351,"Short Rural","Other","Service Fuse",1,247.55,6.125883124435481E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","11:36:00",40001174,"Short Rural","Third party","Vehicle impact",1,98.316666666666706,2.4329485323533901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","11:40:00",10134518,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","11:41:00",50000235,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-04","11:45:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-04","11:45:00",20010779,"Short Rural","Other","Forced Corrective Maintenance",1,79,1.95493745437448E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","11:45:00",50000167,"Short Rural","Planned",null,15,5,0,0,"NO"]
[null,"2017-07-04","11:46:00",50000074,"Short Rural","Other","Service Fuse",1,154.71666666666698,3.8286253985144098E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","11:53:00",20007334,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","11:55:00",82915231,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-04","12:00:00",50000116,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","12:00:00",82564420,"Short Rural","Other","Forced Corrective Maintenance",2,10,4.94920874525185E-5,4.9492087452518498E-6,"NO"]
[null,"2017-07-04","12:00:00",83022292,"Long Rural","Planned",null,2,129,0,0,"NO"]
[null,"2017-07-04","12:00:00",84965669,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","12:05:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-04","12:05:00",50000167,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-04","12:06:00",10020783,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","12:10:00",40001105,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","12:10:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","12:16:00",60026839,"Short Rural","Animal","Animal impact",1,130.19999999999999,3.2219348931589599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","12:18:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","12:27:00",40001006,"Short Rural","Animal","Other",1,139.70000000000002,3.4570223085584196E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","12:30:00",60026831,"Short Rural","Planned",null,2,21,0,0,"NO"]
[null,"2017-07-04","12:32:00",50000054,"Short Rural","Planned",null,23,51,0,0,"NO"]
[null,"2017-07-04","12:35:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-04","12:35:00",50000116,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-04","12:39:00",10020808,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-04","12:40:00",20005944,"Short Rural","Planned",null,4,7,0,0,"NO"]
[null,"2017-07-04","12:40:00",50000167,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-04","12:41:00",84965669,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-04","12:47:00",50000235,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-04","12:52:00",10134605,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-04","13:00:00",40001116,"Long Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-04","13:00:00",50000175,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-04","13:00:00",60026758,"Short Rural","Planned",null,4,104.05,0,0,"NO"]
[null,"2017-07-04","13:00:00",82917286,"Short Rural","Planned",null,1,140,0,0,"NO"]
[null,"2017-07-04","13:03:00",50000235,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-04","13:05:00",50000167,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-04","13:10:00",50000116,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","13:10:00",82915271,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-04","13:13:00",10020808,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-04","13:15:00",40001204,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-04","13:15:00",50000167,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-04","13:18:00",50000175,"Short Rural","Planned",null,3,37.6,0,0,"NO"]
[null,"2017-07-04","13:20:00",40001175,"Urban","Other","Service Fuse",1,104.51666666666701,4.6206648570106494E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-04","13:20:00",83029792,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","13:23:00",50000046,"Short Rural","Other","Forced Corrective Maintenance",1,38,9.4034966159785207E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","13:27:00",20003349,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-04","13:27:00",84000793,"Long Rural","Other","Forced Corrective Maintenance",63,258.93333333333305,0.213350771645305,8.2396024064870506E-4,"NO"]
[null,"2017-07-04","13:31:00",50000169,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","13:34:00",20005577,"Urban","Other","Service Fuse",1,41.8,1.8479712105537701E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-04","13:35:00",40000977,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","13:35:00",82915231,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","13:37:00",30053752,"Long Rural","Other","Service Fuse",1,71.8,9.3905309965995295E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-04","13:40:00",50000116,"Short Rural","Planned",null,1,33,0,0,"NO"]
[null,"2017-07-04","13:40:00",60026837,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","13:45:00",50000170,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","13:48:00",40000978,"Long Rural","Planned",null,1,40.999999999999993,0,0,"NO"]
[null,"2017-07-04","13:50:00",60026670,"Long Rural","Planned",null,1,75,0,0,"NO"]
[null,"2017-07-04","13:55:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-04","13:55:00",50000180,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","14:00:00",50000170,"Short Rural","Planned",null,2,27,0,0,"NO"]
[null,"2017-07-04","14:10:00",60026779,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","14:14:00",25274650,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-04","14:15:00",60026701,"Long Rural","Planned",null,2,64,0,0,"NO"]
[null,"2017-07-04","14:25:00",40001204,"Short Rural","Planned",null,2,45,0,0,"NO"]
[null,"2017-07-04","14:32:00",85081013,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-04","14:33:00",60026779,"Short Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-04","14:40:00",50000167,"Short Rural","Planned",null,16,10,0,0,"NO"]
[null,"2017-07-04","14:40:00",60026779,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","14:45:00",40001110,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-04","14:46:00",40001116,"Long Rural","Planned",null,1,40.999999999999993,0,0,"NO"]
[null,"2017-07-04","14:49:00",82564200,"Short Rural","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-04","14:56:00",50000116,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-04","15:00:00",10134605,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-04","15:00:00",20006666,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-04","15:00:00",50000180,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-04","15:00:00",82552955,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-04","15:05:00",82564447,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-04","15:07:00",60026805,"Urban","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-04","15:14:00",50000150,"Short Rural","Other","Forced Corrective Maintenance",4,36,3.5634302965813301E-4,9.8984174905037098E-6,"NO"]
[null,"2017-07-04","15:15:00",85081013,"Short Rural","Planned",null,2,6,0,0,"NO"]
[null,"2017-07-04","15:21:00",82647141,"Urban","Other","Forced Corrective Maintenance",1,99.55,4.4010893303978002E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-04","15:43:00",60026844,"Urban","Planned",null,2,26,0,0,"NO"]
[null,"2017-07-04","15:50:00",85081013,"Short Rural","Planned",null,2,19,0,0,"NO"]
[null,"2017-07-04","16:00:00",50000116,"Short Rural","Planned",null,2,16,0,0,"NO"]
[null,"2017-07-04","16:13:00",85081013,"Short Rural","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-04","16:16:00",82563086,"Short Rural","Other","Service Fuse",1,134.81666666666698,3.3361791283618503E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","16:37:00",50000116,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-04","16:40:00",60026666,"Long Rural","Overloads",null,1,56.599999999999994,7.4025634318597997E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-04","16:41:00",60026741,"Short Rural","Other","Fuse Operator - No Trigger Found",4,149.683333333333,1.48162812470356E-3,9.8984174905037098E-6,"NO"]
[null,"2017-07-04","16:45:00",82921011,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-04","17:02:00",60026717,"Urban","Planned",null,1,33,0,0,"NO"]
[null,"2017-07-04","17:08:00",20005314,"Short Rural","Animal","Animal nesting/burrowing, etc and other",5,158.13333333333301,1.9565871906228999E-3,1.2373021863129598E-5,"NO"]
[null,"2017-07-04","17:20:00",10020806,"Long Rural","Animal","Animal impact",1,72.216666666666711,9.4450257215101597E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-04","18:18:00",30053771,"Short Rural","Other","Forced Corrective Maintenance",1,119.283333333333,2.9517905824806302E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","18:44:00",10020772,"Long Rural","Other","Fuse Operator - No Trigger Found",10,195.03333333333299,2.5507890836167103E-2,1.3078733978550902E-4,"NO"]
[null,"2017-07-04","19:00:00",85206371,"Short Rural","Asset failure","Distribution substation",1,88.149999999999991,2.1813637544697501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","19:50:00",50000036,"Short Rural","Other","Service Fuse",1,117.76666666666701,2.9142590828291302E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","19:56:00",40001066,"Long Rural","Overloads",null,1,191.683333333333,2.50697532478856E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-04","20:35:00",82556066,"Short Rural","Other","Service Fuse",1,107.416666666667,2.6581375302623501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-04","21:00:00",40001132,"Urban","Other","Forced Corrective Maintenance",1,45.999999999999993,2.0336525283606101E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-05","00:36:00",83864058,"Short Rural","Other","Fuse Operator - No Trigger Found",12,143.666666666667,4.2662179384070995E-3,2.9695252471511097E-5,"NO"]
[null,"2017-07-05","02:38:00",20005188,"Short Rural","Asset failure","LV",1,626.01666666666711,1.5491435806700401E-3,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","05:45:00",20005265,"Short Rural","Other","Service Fuse",2,268.48333333333301,1.3287800612877001E-3,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","06:04:00",82915259,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-05","06:23:00",20006666,"Short Rural","Other","Service Fuse",2,155.78333333333299,7.7100423569781797E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","06:35:00",50000211,"Short Rural","Planned",null,2,16,0,0,"NO"]
[null,"2017-07-05","06:40:00",60026735,"Short Rural","Animal","Animal impact",1,118.866666666667,2.94147973092802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","06:41:00",60026740,"Short Rural","Other","Fuse Operator - No Trigger Found",9,84.566666666666706,1.88342138800559E-3,2.2271439353633299E-5,"NO"]
[null,"2017-07-05","07:03:00",20005265,"Short Rural","Other","Service Fuse",2,170.13333333333301,8.4202538119218203E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","07:05:00",82912996,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-05","07:08:00",40001106,"Short Rural","Other","Vibration",1,263.55,6.5218198240556298E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","07:25:00",20009515,"Short Rural","Other","Service Fuse",2,90.966666666666697,4.50213022193077E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","07:25:00",30053867,"Short Rural","Other","Service Fuse",1,88.149999999999991,2.1813637544697501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","07:25:00",60026765,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","07:30:00",10020814,"Urban","Planned",null,5,50,0,0,"NO"]
[null,"2017-07-05","08:00:00",20010327,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-05","08:00:00",40001116,"Long Rural","Planned",null,1,186,0,0,"NO"]
[null,"2017-07-05","08:00:00",50000118,"Long Rural","Planned",null,1,75,0,0,"NO"]
[null,"2017-07-05","08:01:00",20005314,"Short Rural","Asset failure","LV",1,424.16666666666703,1.0496446880554999E-3,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","08:04:00",60026987,"Short Rural","Asset failure","LV",2,75.233333333333306,3.7234547126778104E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","08:06:00",20005265,"Short Rural","Other","Vibration",3,210.36666666666699,1.5617228195642201E-3,7.4238131178777803E-6,"NO"]
[null,"2017-07-05","08:09:00",30053746,"Short Rural","Other","Service Fuse",1,94.25,2.3323146211999399E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","08:09:00",50000167,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-05","08:10:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","08:12:00",50000169,"Short Rural","Planned",null,1,33.999999999999993,0,0,"NO"]
[null,"2017-07-05","08:14:00",50000020,"Short Rural","Planned",null,4,223.61666666666699,0,0,"NO"]
[null,"2017-07-05","08:16:00",30053746,"Short Rural","Other","Service Fuse",2,147.61666666666699,7.305856976115941E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","08:17:00",50000167,"Short Rural","Planned",null,1,29,0,0,"NO"]
[null,"2017-07-05","08:18:00",30184151,"Short Rural","Other","Service Fuse",1,177.23333333333301,4.38582381641735E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","08:19:00",60300323,"Long Rural","Other","Forced Corrective Maintenance",4,114,5.9639026942192004E-3,5.2314935914203499E-5,"NO"]
[null,"2017-07-05","08:25:00",20006666,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-05","08:25:00",50000235,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-05","08:30:00",40000969,"Short Rural","Planned",null,9,209,0,0,"NO"]
[null,"2017-07-05","08:30:00",50000169,"Short Rural","Planned",null,18,250,0,0,"NO"]
[null,"2017-07-05","08:30:00",50000170,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-05","08:30:00",60026755,"Long Rural","Planned",null,198,58,0,0,"NO"]
[null,"2017-07-05","08:30:00",60026765,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","08:32:00",20001488,"Short Rural","Planned",null,13,103,0,0,"NO"]
[null,"2017-07-05","08:40:00",10020786,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","08:40:00",40001156,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-05","08:40:00",40001193,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-05","08:40:00",50000035,"Short Rural","Planned",null,2,40,0,0,"NO"]
[null,"2017-07-05","08:45:00",20002652,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-05","08:45:00",50000235,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-05","08:45:00",60026799,"Urban","Planned",null,143,100,0,0,"NO"]
[null,"2017-07-05","08:55:00",50000170,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-07-05","09:00:00",10020781,"Short Rural","Planned",null,35,133,0,0,"NO"]
[null,"2017-07-05","09:00:00",20004751,"Urban","Planned",null,3,25,0,0,"NO"]
[null,"2017-07-05","09:00:00",20006212,"Short Rural","Planned",null,17,172,0,0,"NO"]
[null,"2017-07-05","09:00:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","09:00:00",50000057,"Long Rural","Planned",null,1,350,0,0,"NO"]
[null,"2017-07-05","09:00:00",50000067,"Short Rural","Planned",null,2,156,0,0,"NO"]
[null,"2017-07-05","09:00:00",50000170,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-05","09:00:00",50000175,"Short Rural","Planned",null,33,322,0,0,"NO"]
[null,"2017-07-05","09:00:00",60026765,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-05","09:00:00",82561856,"Long Rural","Planned",null,110,351.53636363636406,0,0,"NO"]
[null,"2017-07-05","09:00:00",82912289,"Urban","Planned",null,105,22.8857142857143,0,0,"NO"]
[null,"2017-07-05","09:00:00",83022298,"Short Rural","Planned",null,65,104,0,0,"NO"]
[null,"2017-07-05","09:01:00",50000094,"Long Rural","Planned",null,4,257,0,0,"NO"]
[null,"2017-07-05","09:02:00",10020778,"Short Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-07-05","09:02:00",50000167,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-05","09:02:00",60026747,"Long Rural","Planned",null,1,107,0,0,"NO"]
[null,"2017-07-05","09:04:00",50000235,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-05","09:06:00",60026667,"Long Rural","Planned",null,1,208,0,0,"NO"]
[null,"2017-07-05","09:09:00",20005265,"Short Rural","Other","Service Fuse",2,393.15000000000003,1.9457814181957701E-3,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","09:12:00",20005265,"Short Rural","Other","Fuse Operator - No Trigger Found",1,92.366666666666703,2.28570957218215E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","09:15:00",10020806,"Long Rural","Planned",null,2,107,0,0,"NO"]
[null,"2017-07-05","09:15:00",30053752,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-05","09:15:00",60026765,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","09:18:00",50000170,"Short Rural","Planned",null,2,26,0,0,"NO"]
[null,"2017-07-05","09:20:00",10020786,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-05","09:20:00",50000118,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","09:20:00",50000170,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","09:25:00",20006666,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-05","09:26:00",50000234,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","09:29:00",20010573,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-05","09:30:00",50000025,"Long Rural","Planned",null,4,290,0,0,"NO"]
[null,"2017-07-05","09:30:00",60026644,"Long Rural","Planned",null,28,181,0,0,"NO"]
[null,"2017-07-05","09:30:00",60026888,"Long Rural","Planned",null,29,214,0,0,"NO"]
[null,"2017-07-05","09:35:00",50000015,"Short Rural","Planned",null,1,124.566666666667,0,0,"NO"]
[null,"2017-07-05","09:36:00",10020655,"Short Rural","Planned",null,1,235,0,0,"NO"]
[null,"2017-07-05","09:40:00",60026697,"Short Rural","Planned",null,108,151,0,0,"NO"]
[null,"2017-07-05","09:48:00",50000169,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-05","09:50:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","09:50:00",50000118,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","10:00:00",30053752,"Long Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-05","10:00:00",40000977,"Long Rural","Planned",null,2,45,0,0,"NO"]
[null,"2017-07-05","10:00:00",50000170,"Short Rural","Planned",null,2,3,0,0,"NO"]
[null,"2017-07-05","10:00:00",50000180,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-05","10:05:00",10020786,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-05","10:12:00",50000167,"Short Rural","Planned",null,3,11,0,0,"NO"]
[null,"2017-07-05","10:15:00",50000170,"Short Rural","Planned",null,4,11.25,0,0,"NO"]
[null,"2017-07-05","10:23:00",60026670,"Long Rural","Planned",null,1,63,0,0,"NO"]
[null,"2017-07-05","10:26:00",84965685,"Short Rural","Other","Forced Corrective Maintenance",1,11,2.7220648098885201E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","10:27:00",20005188,"Short Rural","Third party","Fire",1,160.85,3.9804011333688003E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","10:27:00",40000998,"Short Rural","Animal","Animal impact",18,79.1666666666667,3.5263112309919502E-3,4.4542878707266693E-5,"NO"]
[null,"2017-07-05","10:30:00",10020786,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-05","10:30:00",50000167,"Short Rural","Planned",null,3,18,0,0,"NO"]
[null,"2017-07-05","10:33:00",60026644,"Long Rural","Planned",null,7,97,0,0,"NO"]
[null,"2017-07-05","10:34:00",50000234,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-05","10:35:00",50000170,"Short Rural","Planned",null,3,14.9166666666667,0,0,"NO"]
[null,"2017-07-05","10:38:00",20005188,"Short Rural","Other","Service Fuse",2,232.25,1.14945373108474E-3,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","10:45:00",50000169,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-05","10:45:00",50000170,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-05","10:46:00",60026716,"Long Rural","Planned",null,1,70,0,0,"NO"]
[null,"2017-07-05","10:47:00",83897502,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-05","10:50:00",50000035,"Short Rural","Planned",null,3,30,0,0,"NO"]
[null,"2017-07-05","10:50:00",50000118,"Long Rural","Planned",null,2,33.999999999999993,0,0,"NO"]
[null,"2017-07-05","10:53:00",20011420,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-05","10:55:00",40001204,"Short Rural","Planned",null,1,38,0,0,"NO"]
[null,"2017-07-05","10:55:00",50000180,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-05","11:00:00",20004751,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","11:00:00",20006799,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-05","11:00:00",50000034,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","11:00:00",50000234,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","11:04:00",50000169,"Short Rural","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-05","11:05:00",30053770,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","11:05:00",30184151,"Short Rural","Other","Service Fuse",2,41.883333333333304,2.0728935961363202E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","11:05:00",50000167,"Short Rural","Planned",null,3,38,0,0,"NO"]
[null,"2017-07-05","11:08:00",20005265,"Short Rural","Asset failure","Distribution substation",27,153.416666666667,1.0250429962509699E-2,6.6814318060900006E-5,"NO"]
[null,"2017-07-05","11:08:00",30053839,"Short Rural","Other","Forced Corrective Maintenance",1,23,5.6915900570396305E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","11:10:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-05","11:11:00",40000978,"Long Rural","Planned",null,3,45,0,0,"NO"]
[null,"2017-07-05","11:19:00",60300323,"Long Rural","Other","Forced Corrective Maintenance",1,18,2.3541721161391601E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-05","11:22:00",20006799,"Short Rural","Asset failure","LV",1,97.3,2.4077900545650303E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","11:24:00",83877341,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-05","11:28:00",40000978,"Long Rural","Other","Forced Corrective Maintenance",11,11,1.5825268114046599E-3,1.4386607376406E-4,"NO"]
[null,"2017-07-05","11:39:00",50000074,"Short Rural","Other","Service Fuse",1,164.01666666666699,4.0587636051686197E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","11:40:00",82909162,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-05","11:44:00",40001100,"Short Rural","Asset failure","LV",1,210.51666666666699,5.2094546384396799E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","11:44:00",50000235,"Short Rural","Planned",null,2,7,0,0,"NO"]
[null,"2017-07-05","11:45:00",50000180,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","11:45:00",82914591,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","11:48:00",83016237,"Long Rural","Other","Service Fuse",1,212.1,2.7739994768506402E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-05","11:50:00",50000118,"Long Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-05","12:00:00",25273358,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","12:00:00",40000977,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","12:00:00",50000167,"Short Rural","Planned",null,3,14,0,0,"NO"]
[null,"2017-07-05","12:00:00",60026670,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-05","12:04:00",82987762,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-05","12:05:00",50000170,"Short Rural","Planned",null,1,9.9166666666666696,0,0,"NO"]
[null,"2017-07-05","12:07:00",30053825,"Urban","Asset failure","LV",16,109.683333333333,7.7585317618209708E-3,7.0735740116890795E-5,"NO"]
[null,"2017-07-05","12:17:00",50000167,"Short Rural","Planned",null,3,23,0,0,"NO"]
[null,"2017-07-05","12:20:00",60026807,"Short Rural","Other","Forced Corrective Maintenance",1,10,2.4746043726259301E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","12:25:00",30053745,"Short Rural","Asset failure","LV",1,165.083333333333,4.0851593851433003E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","12:25:00",50000118,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","12:25:00",50000180,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","12:32:00",30053822,"Short Rural","Planned",null,33,84,0,0,"NO"]
[null,"2017-07-05","12:35:00",20003306,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","12:36:00",50000235,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-05","12:40:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-05","12:42:00",50000167,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-05","13:00:00",10020660,"Short Rural","Planned",null,2,70,0,0,"NO"]
[null,"2017-07-05","13:00:00",20006212,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-05","13:00:00",40216323,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-05","13:00:00",50000118,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","13:03:00",60026670,"Long Rural","Planned",null,2,144,0,0,"NO"]
[null,"2017-07-05","13:06:00",50000235,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-05","13:10:00",50000034,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","13:10:00",50000167,"Short Rural","Planned",null,1,14.9166666666667,0,0,"NO"]
[null,"2017-07-05","13:14:00",50000167,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-05","13:16:00",30053837,"Short Rural","Asset failure","LV",2,80.100000000000009,3.9643162049467304E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-05","13:20:00",50000170,"Short Rural","Planned",null,2,13,0,0,"NO"]
[null,"2017-07-05","13:23:00",60026821,"Long Rural","Overloads",null,1360,68.316176470588204,1.2151451739471599,1.7787078210829203E-2,"NO"]
[null,"2017-07-05","13:25:00",25274650,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","13:30:00",40000978,"Long Rural","Planned",null,1,40.999999999999993,0,0,"NO"]
[null,"2017-07-05","13:30:00",50000167,"Short Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-07-05","13:30:00",60026774,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-05","13:33:00",60026781,"Urban","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-05","13:39:00",82773016,"Urban","Other","Service Fuse",2,71.383333333333297,6.3116911441800697E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-05","13:40:00",40000977,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","13:40:00",50000118,"Long Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-05","13:40:00",82773016,"Urban","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-05","13:45:00",10134499,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-05","13:45:00",30053752,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","13:51:00",20001148,"Urban","Asset failure","LV",1,144.05000000000001,6.3684271023988295E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-05","13:52:00",20008154,"Short Rural","Planned",null,5,68,0,0,"NO"]
[null,"2017-07-05","13:54:00",60026770,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-05","13:55:00",50000034,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-05","13:55:00",60026774,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","13:57:00",50000169,"Short Rural","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-05","14:00:00",20010102,"Short Rural","Other","Forced Corrective Maintenance",4,61,6.0380346692072602E-4,9.8984174905037098E-6,"NO"]
[null,"2017-07-05","14:00:00",50000175,"Short Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-05","14:05:00",60026805,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-05","14:10:00",60026750,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","14:11:00",60026770,"Urban","Planned",null,2,17,0,0,"NO"]
[null,"2017-07-05","14:14:00",60026765,"Urban","Planned",null,4,45,0,0,"NO"]
[null,"2017-07-05","14:15:00",40216323,"Long Rural","Planned",null,1,75,0,0,"NO"]
[null,"2017-07-05","14:20:00",20002948,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","14:30:00",30053770,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","14:30:00",40001140,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-05","14:30:00",50000169,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-05","14:35:00",20005577,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-05","14:40:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","14:40:00",60026774,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","14:46:00",50000159,"Long Rural","Other","Service Fuse",1,147.6,1.9304211352341102E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-05","14:55:00",10134499,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-05","14:55:00",50000167,"Short Rural","Planned",null,3,9.9166666666666696,0,0,"NO"]
[null,"2017-07-05","15:00:00",25267735,"Short Rural","Planned",null,2,55,0,0,"NO"]
[null,"2017-07-05","15:00:00",30053770,"Long Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-05","15:00:00",50000175,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-05","15:03:00",50000169,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-05","15:05:00",60026781,"Urban","Planned",null,3,10,0,0,"NO"]
[null,"2017-07-05","15:07:00",82773016,"Urban","Planned",null,11,89,0,0,"NO"]
[null,"2017-07-05","15:10:00",50000118,"Long Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-05","15:15:00",50000167,"Short Rural","Planned",null,3,14.9166666666667,0,0,"NO"]
[null,"2017-07-05","15:20:00",20003792,"Short Rural","Other","Fuse Operator - No Trigger Found",1,41.983333333333299,1.03892140244078E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","15:30:00",50000165,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-05","15:40:00",60026750,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-05","15:45:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-05","15:47:00",60026801,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-05","15:50:00",50000118,"Long Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-05","15:57:00",60322053,"Short Rural","Other","Service Fuse",1,160.01666666666699,3.9597794302635898E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","16:00:00",85081013,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-05","16:11:00",10020799,"Short Rural","Other","Service Fuse",1,122.51666666666701,3.03180279052886E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","16:11:00",60026801,"Short Rural","Planned",null,4,4,0,0,"NO"]
[null,"2017-07-05","16:18:00",50000165,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-05","16:31:00",50000165,"Short Rural","Planned",null,2,28,0,0,"NO"]
[null,"2017-07-05","16:33:00",20020666,"Long Rural","Asset failure","HV",16,1320.0333333333301,0.27622983695178299,2.0925974365681402E-4,"NO"]
[null,"2017-07-05","17:10:00",60026678,"Short Rural","Asset failure","LV",40,176.46666666666698,1.74674073982422E-2,9.8984174905037095E-5,"NO"]
[null,"2017-07-05","17:21:00",20010779,"Short Rural","Other","Forced Corrective Maintenance",23,49,2.7888791279494199E-3,5.6915900570396305E-5,"NO"]
[null,"2017-07-05","17:24:00",25280122,"Short Rural","Other","Service Fuse",1,83.883333333333297,2.0757806345710501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","17:30:00",30053771,"Short Rural","Other","Fuse Operator - No Trigger Found",1,72.699999999999989,1.79903737889905E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","17:34:00",50000095,"Long Rural","Other","Service Fuse",1,65.9166666666667,8.6210654808614501E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-05","17:54:00",10020787,"Short Rural","Other","Forced Corrective Maintenance",351,46,3.99549622004182E-2,8.6858613479170001E-4,"NO"]
[null,"2017-07-05","18:28:00",20012410,"Short Rural","Other","Service Fuse",1,194.78333333333299,4.8201168838132001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","18:37:00",82561865,"Short Rural","Asset failure","LV",1,88.616666666666703,2.1929119082086802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","18:42:00",25279698,"Urban","Other","Service Fuse",1,76.7,3.3908945418534503E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-05","18:44:00",82647141,"Urban","Other","Forced Corrective Maintenance",1,102.583333333333,4.5351925043694098E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-05","20:41:00",60026652,"Short Rural","Overloads",null,1,59.183333333333302,1.4645533545324399E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","22:02:00",10020800,"Urban","Asset failure","HV",435,81.156245210728002,0.156073842218037,1.9231279344279701E-3,"NO"]
[null,"2017-07-05","22:15:00",40001121,"Short Rural","Other","Service Fuse",1,91.966666666666697,2.2758111546916402E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-05","23:45:00",40001226,"Short Rural","Other","Service Fuse",1,134.583333333333,3.33040505149239E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","00:30:00",20007229,"Short Rural","Other","Service Fuse",2,125.166666666667,6.1947596128069011E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-06","02:24:00",40000977,"Long Rural","Animal","Animal impact",1,332.85,4.3532566047606597E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","04:49:00",10020828,"Long Rural","Other","Fuse Operator - No Trigger Found",1,89.216666666666697,1.1668410497863802E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","04:53:00",30053817,"Urban","Asset failure","LV",132,220.9,0.12891058118252499,5.8356985596434902E-4,"NO"]
[null,"2017-07-06","05:30:00",25273220,"Short Rural","Planned",null,1,123,0,0,"NO"]
[null,"2017-07-06","05:37:00",25267746,"Short Rural","Planned",null,26,124,0,0,"NO"]
[null,"2017-07-06","05:40:00",50000185,"Short Rural","Asset failure","LV",1,133.9,3.3134952549461195E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","06:11:00",30053770,"Long Rural","Other","Service Fuse",1,173.96666666666698,2.2752637544685701E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","06:13:00",20007292,"Urban","Asset failure","Zone substation",1013,76.433333333333294,0.34230336201078104,4.4784565461506503E-3,"NO"]
[null,"2017-07-06","06:13:00",20007314,"Urban","Asset failure","Zone substation",988,76.433333333333294,0.33385559888119598,4.3679319522180095E-3,"NO"]
[null,"2017-07-06","06:13:00",20007334,"Urban","Asset failure","Zone substation",1304,76.433333333333294,0.44063532483915002,5.7649628195266004E-3,"NO"]
[null,"2017-07-06","06:13:00",20007358,"Urban","Asset failure","Zone substation",734,71.433333333333294,0.231801315095302,3.2450020778623705E-3,"NO"]
[null,"2017-07-06","06:13:00",20007373,"Urban","Asset failure","Zone substation",723,74.433333333333294,0.237916567194532,3.196371256532E-3,"NO"]
[null,"2017-07-06","06:13:00",20007392,"Short Rural","Asset failure","Zone substation",582,74.433333333333294,0.10720035634303,1.4402197448682901E-3,"NO"]
[null,"2017-07-06","06:13:00",20007427,"Urban","Asset failure","Zone substation",1286,74.433333333333294,0.42318216516205903,5.6853851118950994E-3,"NO"]
[null,"2017-07-06","06:13:00",20007445,"Urban","Asset failure","Zone substation",261,74.433333333333294,8.5886893551553101E-2,1.15387676065678E-3,"NO"]
[null,"2017-07-06","06:13:00",25276037,"Urban","Asset failure","Zone substation",9,74.433333333333294,2.9616170190190699E-3,3.9788853815751098E-5,"NO"]
[null,"2017-07-06","06:46:00",30053746,"Short Rural","Other","Service Fuse",2,148.433333333333,7.3462755142021695E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-06","06:53:00",40223073,"Long Rural","Animal","Animal impact",1,139.26666666666699,1.82143168541285E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","07:19:00",30053847,"Short Rural","Other","Service Fuse",1,5991.55,1.4826715828806901E-2,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","07:43:00",10020806,"Long Rural","Other","Fuse Operator - No Trigger Found",6,79.733333333333306,6.2568663353387401E-3,7.8472403871305299E-5,"NO"]
[null,"2017-07-06","07:54:00",25275672,"Urban","Other","Service Fuse",1,167.5,7.4051477934870098E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","07:57:00",20004751,"Urban","Other","Service Fuse",1,237.75,1.0510888882994201E-3,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","08:00:00",20007427,"Urban","Planned",null,23,389,0,0,"NO"]
[null,"2017-07-06","08:00:00",30053752,"Long Rural","Planned",null,22,404.15454545454503,0,0,"NO"]
[null,"2017-07-06","08:00:00",40001116,"Long Rural","Planned",null,1,200,0,0,"NO"]
[null,"2017-07-06","08:00:00",82912274,"Short Rural","Planned",null,3,140,0,0,"NO"]
[null,"2017-07-06","08:00:00",82917286,"Short Rural","Planned",null,1,70,0,0,"NO"]
[null,"2017-07-06","08:03:00",50000169,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-06","08:05:00",25280514,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","08:05:00",60026842,"Urban","Planned",null,1,85,0,0,"NO"]
[null,"2017-07-06","08:10:00",10020772,"Long Rural","Planned",null,2,110,0,0,"NO"]
[null,"2017-07-06","08:15:00",50000020,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-06","08:15:00",50000170,"Short Rural","Planned",null,2,14.9166666666667,0,0,"NO"]
[null,"2017-07-06","08:20:00",10020761,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-06","08:20:00",10020783,"Urban","Planned",null,10,12,0,0,"NO"]
[null,"2017-07-06","08:20:00",50000169,"Short Rural","Planned",null,2,14,0,0,"NO"]
[null,"2017-07-06","08:25:00",82649845,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-06","08:30:00",10020825,"Short Rural","Planned",null,3,348,0,0,"NO"]
[null,"2017-07-06","08:30:00",20002652,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-06","08:30:00",40001189,"Short Rural","Planned",null,56,307,0,0,"NO"]
[null,"2017-07-06","08:30:00",50000169,"Short Rural","Planned",null,83,160,0,0,"NO"]
[null,"2017-07-06","08:30:00",60026649,"Urban","Planned",null,2,115.183333333333,0,0,"NO"]
[null,"2017-07-06","08:30:00",60026670,"Long Rural","Planned",null,1,47.999999999999993,0,0,"NO"]
[null,"2017-07-06","08:30:00",60026755,"Long Rural","Planned",null,159,203,0,0,"NO"]
[null,"2017-07-06","08:30:00",60026773,"Short Rural","Planned",null,1,318,0,0,"NO"]
[null,"2017-07-06","08:30:00",83022292,"Long Rural","Planned",null,2,120,0,0,"NO"]
[null,"2017-07-06","08:31:00",20008373,"Short Rural","Planned",null,182,120.791208791209,0,0,"NO"]
[null,"2017-07-06","08:32:00",82909162,"Urban","Planned",null,1,305,0,0,"NO"]
[null,"2017-07-06","08:35:00",50000095,"Long Rural","Planned",null,50,295,0,0,"NO"]
[null,"2017-07-06","08:35:00",50000230,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-06","08:38:00",82554089,"Urban","Planned",null,12,14,0,0,"NO"]
[null,"2017-07-06","08:40:00",10020782,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","08:40:00",40000966,"Long Rural","Animal","Animal impact",1,77.033333333333303,1.0074984741477002E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","08:40:00",50000075,"Short Rural","Planned",null,20,305,0,0,"NO"]
[null,"2017-07-06","08:40:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","08:45:00",10020808,"Urban","Planned",null,1,245,0,0,"NO"]
[null,"2017-07-06","08:45:00",10020855,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",135,147.74629629629601,4.9357840165303597E-2,3.3407159030450002E-4,"NO"]
[null,"2017-07-06","08:45:00",50000195,"Urban","Other","Forced Corrective Maintenance",1,42.999999999999993,1.9010230156414401E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","08:46:00",30053837,"Short Rural","Asset failure","LV",63,153.75,2.3969636604347904E-2,1.55900075475433E-4,"NO"]
[null,"2017-07-06","08:50:00",50000166,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-06","08:50:00",50000169,"Short Rural","Planned",null,4,9.9166666666666696,0,0,"NO"]
[null,"2017-07-06","08:50:00",83922716,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","08:55:00",10020797,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","08:57:00",10020783,"Urban","Planned",null,6,13,0,0,"NO"]
[null,"2017-07-06","09:00:00",10020848,"Short Rural","Planned",null,24,301.83333333333303,0,0,"NO"]
[null,"2017-07-06","09:00:00",20006212,"Short Rural","Planned",null,1,155,0,0,"NO"]
[null,"2017-07-06","09:00:00",40001010,"Long Rural","Planned",null,8,192,0,0,"NO"]
[null,"2017-07-06","09:00:00",40200483,"Long Rural","Planned",null,13,300,0,0,"NO"]
[null,"2017-07-06","09:00:00",50000208,"Short Rural","Planned",null,99,125.683333333333,0,0,"NO"]
[null,"2017-07-06","09:00:00",83022292,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-06","09:01:00",30053833,"Short Rural","Planned",null,93,268,0,0,"NO"]
[null,"2017-07-06","09:01:00",50000015,"Short Rural","Planned",null,3,208,0,0,"NO"]
[null,"2017-07-06","09:01:00",60026758,"Short Rural","Planned",null,4,181,0,0,"NO"]
[null,"2017-07-06","09:03:00",60026667,"Long Rural","Planned",null,1,141,0,0,"NO"]
[null,"2017-07-06","09:04:00",40000978,"Long Rural","Animal","Animal impact",1,287.2,3.7562123986398105E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","09:05:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","09:05:00",50000175,"Short Rural","Planned",null,3,68,0,0,"NO"]
[null,"2017-07-06","09:08:00",50000067,"Short Rural","Planned",null,1,223,0,0,"NO"]
[null,"2017-07-06","09:09:00",82912996,"Urban","Planned",null,2,42.999999999999993,0,0,"NO"]
[null,"2017-07-06","09:10:00",20012370,"Short Rural","7 - STPIS Exclusion (3.3)(a)",null,1,4,0,0,"NO"]
[null,"2017-07-06","09:15:00",50000165,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-06","09:15:00",60026836,"Urban","Planned",null,180,282,0,0,"NO"]
[null,"2017-07-06","09:20:00",50000170,"Short Rural","Other","Forced Corrective Maintenance",2,102,5.0481929201568907E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-06","09:20:00",83922716,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","09:21:00",50000059,"Short Rural","Planned",null,23,189,0,0,"NO"]
[null,"2017-07-06","09:25:00",10129324,"Short Rural","Planned",null,18,150,0,0,"NO"]
[null,"2017-07-06","09:25:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","09:25:00",60026670,"Long Rural","Planned",null,1,69,0,0,"NO"]
[null,"2017-07-06","09:26:00",40000961,"Long Rural","Planned",null,2,42.999999999999993,0,0,"NO"]
[null,"2017-07-06","09:30:00",20005577,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-06","09:30:00",50000170,"Short Rural","Planned",null,2,14.9166666666667,0,0,"NO"]
[null,"2017-07-06","09:30:00",83022292,"Long Rural","Planned",null,2,90,0,0,"NO"]
[null,"2017-07-06","09:32:00",40001063,"Long Rural","Planned",null,23,291,0,0,"NO"]
[null,"2017-07-06","09:32:00",60026764,"Short Rural","Planned",null,1,148,0,0,"NO"]
[null,"2017-07-06","09:49:00",10020783,"Urban","Planned",null,10,10,0,0,"NO"]
[null,"2017-07-06","09:50:00",82772982,"Short Rural","Asset failure","HV",1089,83.116666666666703,0.223986463914082,2.6948441617896299E-3,"NO"]
[null,"2017-07-06","09:55:00",50000165,"Short Rural","Planned",null,2,9,0,0,"NO"]
[null,"2017-07-06","09:55:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","10:00:00",40001116,"Long Rural","Planned",null,2,187,0,0,"NO"]
[null,"2017-07-06","10:00:00",50000116,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","10:00:00",50000170,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-07-06","10:00:00",60026649,"Urban","Planned",null,1,60.699999999999996,0,0,"NO"]
[null,"2017-07-06","10:00:00",60026825,"Short Rural","Planned",null,1,36.999999999999993,0,0,"NO"]
[null,"2017-07-06","10:03:00",10020783,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","10:05:00",30053770,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","10:05:00",60026842,"Urban","Planned",null,1,80,0,0,"NO"]
[null,"2017-07-06","10:07:00",30053863,"Short Rural","Third party","Vehicle impact",276,205.35000000000002,0.14025216218557102,6.8299080684475601E-4,"NO"]
[null,"2017-07-06","10:08:00",50000165,"Short Rural","Planned",null,2,32,0,0,"NO"]
[null,"2017-07-06","10:10:00",82554089,"Urban","Planned",null,12,10,0,0,"NO"]
[null,"2017-07-06","10:15:00",60026666,"Long Rural","Planned",null,7,93,0,0,"NO"]
[null,"2017-07-06","10:15:00",83022292,"Long Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-06","10:17:00",60331113,"Short Rural","Planned",null,1,44,0,0,"NO"]
[null,"2017-07-06","10:20:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","10:25:00",50000050,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-07-06","10:25:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","10:27:00",60026757,"Long Rural","Asset failure","Distribution substation",1,1695.4333333333302,2.2174121545034401E-2,1.30787339785509E-5,"NO"]
[null,"2017-07-06","10:30:00",60026644,"Long Rural","Planned",null,2,67,0,0,"NO"]
[null,"2017-07-06","10:30:00",60026649,"Urban","Planned",null,1,240,0,0,"NO"]
[null,"2017-07-06","10:31:00",50000206,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","10:35:00",30053770,"Long Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","10:41:00",20005447,"Short Rural","Asset failure","Distribution substation",15,58.766666666666701,2.1813637544697501E-3,3.7119065589388895E-5,"NO"]
[null,"2017-07-06","10:44:00",50000165,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-06","10:45:00",50000170,"Short Rural","Planned",null,2,35,0,0,"NO"]
[null,"2017-07-06","10:45:00",50000234,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","10:45:00",82552955,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","10:50:00",10020783,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","10:55:00",50000116,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-06","11:00:00",10020655,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-06","11:00:00",20005605,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-06","11:00:00",50000148,"Short Rural","Other","Service Fuse",1,109.433333333333,2.7080420517769697E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","11:00:00",60026649,"Urban","Planned",null,3,84.366666666666703,0,0,"NO"]
[null,"2017-07-06","11:00:00",60026805,"Urban","Planned",null,1,36.999999999999993,0,0,"NO"]
[null,"2017-07-06","11:00:00",60026816,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-06","11:00:00",82912274,"Short Rural","Planned",null,2,125,0,0,"NO"]
[null,"2017-07-06","11:00:00",83022292,"Long Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-06","11:00:00",85081013,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-06","11:01:00",50000175,"Short Rural","Planned",null,7,62,0,0,"NO"]
[null,"2017-07-06","11:05:00",50000050,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-06","11:05:00",60026842,"Urban","Planned",null,2,94,0,0,"NO"]
[null,"2017-07-06","11:05:00",82552955,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","11:08:00",50000235,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-06","11:13:00",20005336,"Urban","Planned",null,5,7,0,0,"NO"]
[null,"2017-07-06","11:15:00",30053770,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","11:15:00",50000167,"Short Rural","Planned",null,3,20,0,0,"NO"]
[null,"2017-07-06","11:23:00",85081013,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","11:24:00",10020806,"Long Rural","Planned",null,2,47,0,0,"NO"]
[null,"2017-07-06","11:24:00",20012587,"Short Rural","Other","Forced Corrective Maintenance",1,4,9.8984174905037098E-6,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","11:25:00",84965685,"Short Rural","Planned",null,1,28,0,0,"NO"]
[null,"2017-07-06","11:30:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","11:30:00",82552955,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","11:30:00",83022292,"Long Rural","Planned",null,2,120,0,0,"NO"]
[null,"2017-07-06","11:31:00",50000235,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-06","11:33:00",10020783,"Urban","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-06","11:33:00",10020809,"Urban","Other","Service Fuse",1,131.25,5.8025411814636996E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","11:35:00",50000050,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-06","11:35:00",50000140,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-06","11:35:00",60026842,"Urban","Planned",null,1,80,0,0,"NO"]
[null,"2017-07-06","11:35:00",85081013,"Short Rural","Planned",null,2,24,0,0,"NO"]
[null,"2017-07-06","11:40:00",20005605,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-06","11:40:00",40001109,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-06","11:40:00",83922716,"Short Rural","Planned",null,1,42.999999999999993,0,0,"NO"]
[null,"2017-07-06","11:48:00",50000235,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-06","11:50:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","11:50:00",60026773,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","12:00:00",40001116,"Long Rural","Planned",null,1,185,0,0,"NO"]
[null,"2017-07-06","12:00:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","12:00:00",50000169,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","12:00:00",60026670,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-06","12:00:00",83022292,"Long Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-06","12:01:00",60026842,"Urban","Planned",null,2,19,0,0,"NO"]
[null,"2017-07-06","12:05:00",85081013,"Short Rural","Planned",null,2,19,0,0,"NO"]
[null,"2017-07-06","12:10:00",60026713,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-06","12:10:00",60026816,"Long Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-06","12:13:00",50000208,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","12:19:00",50000235,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-06","12:25:00",10020786,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","12:29:00",85081013,"Short Rural","Planned",null,2,21,0,0,"NO"]
[null,"2017-07-06","12:30:00",40001002,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","12:30:00",50000195,"Urban","Planned",null,8,37,0,0,"NO"]
[null,"2017-07-06","12:33:00",60026837,"Short Rural","Planned",null,2,11,0,0,"NO"]
[null,"2017-07-06","12:36:00",82917286,"Short Rural","Planned",null,2,143.46666666666698,0,0,"NO"]
[null,"2017-07-06","12:40:00",20002698,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","12:41:00",10020783,"Urban","Planned",null,2,7,0,0,"NO"]
[null,"2017-07-06","12:45:00",60026773,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","12:50:00",30053752,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","12:53:00",30053830,"Short Rural","Asset failure","LV",1,31,7.6712735551403687E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","12:56:00",60026816,"Long Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-07-06","13:00:00",10020783,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","13:00:00",20006212,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-06","13:00:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","13:01:00",50000175,"Short Rural","Planned",null,3,64,0,0,"NO"]
[null,"2017-07-06","13:04:00",20005265,"Short Rural","Animal","Animal impact",28,51.616666666666696,3.5764632129438303E-3,6.9288922433525889E-5,"NO"]
[null,"2017-07-06","13:08:00",30053748,"Urban","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-06","13:10:00",40000998,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-06","13:10:00",50000117,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","13:12:00",10020781,"Short Rural","Other","Forced Corrective Maintenance",85,112.083333333333,2.3575762075038302E-2,2.10341371673204E-4,"NO"]
[null,"2017-07-06","13:14:00",20010573,"Short Rural","Other","Forced Corrective Maintenance",22,50,2.7220648098885197E-3,5.4441296197770402E-5,"NO"]
[null,"2017-07-06","13:14:00",20010596,"Short Rural","Other","Forced Corrective Maintenance",42,50,5.1966691825144507E-3,1.0393338365028901E-4,"NO"]
[null,"2017-07-06","13:14:00",20010627,"Short Rural","Other","Forced Corrective Maintenance",1,49.999999999999993,1.2373021863129599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","13:20:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","13:20:00",50000170,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-06","13:30:00",82912274,"Short Rural","Planned",null,2,90,0,0,"NO"]
[null,"2017-07-06","13:30:00",83022292,"Long Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-06","13:31:00",85081013,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","13:32:00",10020771,"Long Rural","Asset failure","LV",1,126.583333333333,1.6555497427849001E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","13:33:00",60026842,"Urban","Planned",null,1,51.999999999999993,0,0,"NO"]
[null,"2017-07-06","13:34:00",30053770,"Long Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-06","13:35:00",82563108,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","13:40:00",60026670,"Long Rural","Planned",null,1,73,0,0,"NO"]
[null,"2017-07-06","13:45:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-06","13:57:00",20005336,"Urban","Planned",null,4,9,0,0,"NO"]
[null,"2017-07-06","13:57:00",20007716,"Short Rural","Other","Service Fuse",1,90.266666666666708,2.2337428803570001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","14:00:00",20005605,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-06","14:00:00",60026741,"Short Rural","Planned",null,1,29,0,0,"NO"]
[null,"2017-07-06","14:00:00",83022292,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-06","14:00:00",85081013,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-06","14:03:00",30053770,"Long Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-06","14:10:00",40000998,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","14:10:00",50000034,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-06","14:18:00",10020808,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-06","14:20:00",20002622,"Short Rural","Planned",null,2,70,0,0,"NO"]
[null,"2017-07-06","14:24:00",84670103,"Urban","Planned",null,1,29,0,0,"NO"]
[null,"2017-07-06","14:28:00",60026805,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-06","14:30:00",85081013,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-06","14:34:00",10020808,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-06","14:35:00",60026842,"Urban","Planned",null,2,49.999999999999993,0,0,"NO"]
[null,"2017-07-06","14:38:00",40001175,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-06","14:43:00",20005336,"Urban","Planned",null,4,50,0,0,"NO"]
[null,"2017-07-06","14:46:00",50000145,"Long Rural","Other","Forced Corrective Maintenance",592,79.868243243243185,0.61838869997384305,7.74261051530212E-3,"NO"]
[null,"2017-07-06","14:58:00",60026649,"Urban","Planned",null,1,31.883333333333297,0,0,"NO"]
[null,"2017-07-06","15:00:00",20007229,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-06","15:00:00",50000117,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-06","15:00:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-06","15:02:00",50000236,"Long Rural","Other","Fuse Operator - No Trigger Found",1,81.516666666666708,1.0661347981515399E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","15:05:00",84670103,"Urban","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-06","15:10:00",60026837,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-06","15:20:00",85081013,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-06","15:25:00",20003088,"Short Rural","Other","Service Fuse",1,51.783333333333303,1.2814326309581301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","15:25:00",50000021,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-06","15:26:00",20007373,"Urban","Other","Service Fuse",2,153.80000000000001,1.3598946037472301E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-06","15:29:00",20007292,"Urban","Other","Service Fuse",1,152.05000000000001,6.7221058029832796E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","15:31:00",40001226,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-06","15:40:00",50000117,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","15:45:00",85081013,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-06","15:49:00",20007373,"Urban","Other","Fuse Operator - No Trigger Found",2,125.48333333333299,1.1095195569584798E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-06","16:00:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","16:00:00",50000117,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-06","16:00:00",85081013,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-06","16:04:00",30053834,"Urban","Other","Service Fuse",1,72.183333333333294,3.1912134421484799E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","16:08:00",40001226,"Short Rural","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-06","16:29:00",60026774,"Short Rural","Planned",null,2,21,0,0,"NO"]
[null,"2017-07-06","16:30:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-06","16:41:00",40001038,"Long Rural","Other","Fuse Operator - No Trigger Found",1,88.433333333333294,1.15659604150318E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-06","16:50:00",20007334,"Urban","Other","Service Fuse",1,66.199999999999989,2.9266912473363598E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","17:18:00",50000168,"Short Rural","Planned",null,1,47,0,0,"NO"]
[null,"2017-07-06","17:19:00",40001067,"Urban","Other","Forced Corrective Maintenance",1,60,2.65259025438341E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-06","17:58:00",40001189,"Short Rural","Other","Service Fuse",1,77.75,1.9240048997166601E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","18:02:00",30053841,"Short Rural","Other","Service Fuse",1,163.76666666666699,4.0525770942370599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","18:05:00",83868946,"Short Rural","Third party","Other - Third Party",1,53.683333333333302,1.3284501140380201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","18:15:00",30053808,"Short Rural","Exclusion - Customer Installation Fault",null,1,107,0,0,"NO"]
[null,"2017-07-06","18:48:00",25266408,"Short Rural","Other","Service Fuse",1,52.233333333333299,1.29256835063494E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-06","20:23:00",10020839,"Urban","Other","Service Fuse",2,126.5,1.1185088905983401E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-06","22:00:00",20003281,"Short Rural","Other","Forced Corrective Maintenance",2,32,1.58374679848059E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-06","23:42:00",30053772,"Short Rural","Other","Service Fuse",1,127.583333333333,3.1571827454085797E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","05:02:00",60026644,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",14,145,2.6549829976458304E-2,1.8310227569971198E-4,"NO"]
[null,"2017-07-07","06:01:00",82920985,"Urban","Other","Service Fuse",1,119.98333333333299,5.3044436781405897E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","06:03:00",25273020,"Urban","Overloads",null,2,70.266666666666708,6.2129558402669106E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-07","06:13:00",83864041,"Short Rural","Other","Service Fuse",1,136.183333333333,3.3699987214544098E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","06:15:00",25274647,"Urban","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-07","06:30:00",85081013,"Short Rural","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-07","06:35:00",82699749,"Short Rural","Other","Service Fuse",1,159.666666666667,3.9511183149593999E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","06:47:00",60026750,"Short Rural","Planned",null,2,28,0,0,"NO"]
[null,"2017-07-07","06:58:00",30053817,"Urban","Asset failure","LV",1,89.95,3.9766748896964601E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","07:30:00",25274647,"Urban","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-07","07:41:00",60026745,"Short Rural","Weather",null,3,359.38333333333304,2.66799470434664E-3,7.4238131178777803E-6,"NO"]
[null,"2017-07-07","07:45:00",85081013,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-07","07:53:00",60026745,"Short Rural","Weather",null,1,168.21666666666698,4.1626969888189103E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","08:00:00",10020772,"Long Rural","Planned",null,15,73,0,0,"NO"]
[null,"2017-07-07","08:00:00",20003435,"Long Rural","Planned",null,2,48.699999999999996,0,0,"NO"]
[null,"2017-07-07","08:00:00",50000169,"Short Rural","Planned",null,4,90,0,0,"NO"]
[null,"2017-07-07","08:05:00",20007634,"Long Rural","Other","Vibration",1,195.183333333333,2.5527508937134903E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","08:05:00",50000035,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-07","08:05:00",50000153,"Short Rural","Planned",null,16,155,0,0,"NO"]
[null,"2017-07-07","08:05:00",83922716,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-07","08:07:00",85081013,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-07","08:10:00",20008686,"Long Rural","Other","Forced Corrective Maintenance",2,112,2.9296364111954E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-07","08:10:00",30053878,"Short Rural","Asset failure","LV",1,103.45,2.5599782234815197E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","08:10:00",83022292,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-07","08:14:00",20005133,"Long Rural","Other","Fuse Operator - No Trigger Found",1,20,2.6157467957101799E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-07","08:15:00",10020808,"Urban","Planned",null,2,275,0,0,"NO"]
[null,"2017-07-07","08:19:00",60026662,"Long Rural","Overloads",null,1,188.15,2.4607637980643502E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","08:25:00",85081013,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-07","08:26:00",60026745,"Short Rural","Other","Fuse Operator - No Trigger Found",1,94.883333333333297,2.3479871155599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","08:30:00",10020673,"Long Rural","Planned",null,4,147,0,0,"NO"]
[null,"2017-07-07","08:30:00",10020781,"Short Rural","Planned",null,2,240,0,0,"NO"]
[null,"2017-07-07","08:30:00",10020835,"Urban","Planned",null,19,95,0,0,"NO"]
[null,"2017-07-07","08:30:00",30053744,"Short Rural","Asset failure","Distribution substation",1,6324.25,1.5650016703579499E-2,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","08:30:00",30053835,"Urban","Planned",null,94,158,0,0,"NO"]
[null,"2017-07-07","08:30:00",50000108,"Short Rural","Planned",null,5,360,0,0,"NO"]
[null,"2017-07-07","08:30:00",50000170,"Short Rural","Planned",null,19,285,0,0,"NO"]
[null,"2017-07-07","08:30:00",82912280,"Urban","Planned",null,8,183.21666666666698,0,0,"NO"]
[null,"2017-07-07","08:30:00",82912289,"Urban","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-07","08:30:00",82920982,"Short Rural","Planned",null,4,240,0,0,"NO"]
[null,"2017-07-07","08:30:00",83022292,"Long Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-07","08:32:00",30053744,"Short Rural","Overloads",null,1,270.33333333333303,6.6896804873320902E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","08:40:00",40001237,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-07","08:47:00",84375978,"Short Rural","Planned",null,3,131,0,0,"NO"]
[null,"2017-07-07","08:49:00",10020770,"Short Rural","Planned",null,10,198,0,0,"NO"]
[null,"2017-07-07","08:52:00",20011545,"Long Rural","Asset failure","LV",31,83.387096774193495,3.3808527334554E-2,4.0544075333507701E-4,"NO"]
[null,"2017-07-07","08:55:00",60026786,"Short Rural","Other","Service Fuse",1,169.05,4.1833186919241301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","09:00:00",10020806,"Long Rural","Planned",null,34,229.529411764706,0,0,"NO"]
[null,"2017-07-07","09:00:00",40000985,"Long Rural","Planned",null,34,352,0,0,"NO"]
[null,"2017-07-07","09:00:00",40001139,"Long Rural","Planned",null,16,127,0,0,"NO"]
[null,"2017-07-07","09:00:00",82912317,"Urban","Planned",null,81,290.25925925925901,0,0,"NO"]
[null,"2017-07-07","09:02:00",50000067,"Short Rural","Planned",null,2,200,0,0,"NO"]
[null,"2017-07-07","09:05:00",20008373,"Short Rural","Planned",null,62,96,0,0,"NO"]
[null,"2017-07-07","09:05:00",30053770,"Long Rural","Other","Service Fuse",13,50,8.5011770860580708E-3,1.7002354172116101E-4,"NO"]
[null,"2017-07-07","09:06:00",60026757,"Long Rural","Planned",null,45,96,0,0,"NO"]
[null,"2017-07-07","09:09:00",20005336,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-07","09:10:00",60026670,"Long Rural","Planned",null,1,89,0,0,"NO"]
[null,"2017-07-07","09:16:00",60026701,"Long Rural","Planned",null,1,62,0,0,"NO"]
[null,"2017-07-07","09:20:00",85081013,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-07","09:23:00",40001189,"Short Rural","Planned",null,1,33.999999999999993,0,0,"NO"]
[null,"2017-07-07","09:24:00",50000151,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-07","09:30:00",30053744,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-07","09:30:00",83022292,"Long Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-07","09:31:00",30053864,"Short Rural","Planned",null,26,20,0,0,"NO"]
[null,"2017-07-07","09:40:00",83922716,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-07","09:45:00",20006023,"Short Rural","Planned",null,6,45,0,0,"NO"]
[null,"2017-07-07","09:45:00",40001003,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-07","09:46:00",30053822,"Short Rural","Asset failure","LV",1,94.616666666666703,2.3413881705662299E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","09:48:00",85081013,"Short Rural","Planned",null,2,18,0,0,"NO"]
[null,"2017-07-07","09:50:00",10020783,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-07","09:55:00",20005336,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-07","10:00:00",50000034,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-07","10:00:00",50000212,"Urban","Planned",null,2,14,0,0,"NO"]
[null,"2017-07-07","10:00:00",84332376,"Short Rural","Planned",null,14,199,0,0,"NO"]
[null,"2017-07-07","10:05:00",50000240,"Long Rural","Planned",null,3,62,0,0,"NO"]
[null,"2017-07-07","10:10:00",50000034,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-07","10:11:00",82556069,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-07","10:12:00",60026984,"Short Rural","Planned",null,16,97,0,0,"NO"]
[null,"2017-07-07","10:20:00",82889348,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-07","10:21:00",50000208,"Short Rural","Planned",null,2,28,0,0,"NO"]
[null,"2017-07-07","10:29:00",82556069,"Short Rural","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-07","10:30:00",50000118,"Long Rural","Planned",null,2,40,0,0,"NO"]
[null,"2017-07-07","10:30:00",83022292,"Long Rural","Planned",null,4,120,0,0,"NO"]
[null,"2017-07-07","10:35:00",50000167,"Short Rural","Planned",null,1,38,0,0,"NO"]
[null,"2017-07-07","10:38:00",60026767,"Urban","Planned",null,2,21,0,0,"NO"]
[null,"2017-07-07","10:45:00",82556069,"Short Rural","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-07","10:50:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-07","10:50:00",84670103,"Urban","Planned",null,1,36,0,0,"NO"]
[null,"2017-07-07","10:58:00",60026730,"Urban","Other","Service Fuse",1,67,2.9620591173947999E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","10:59:00",60026647,"Short Rural","Overloads",null,1,115.583333333333,2.86023022069347E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","11:00:00",20006023,"Short Rural","Planned",null,1,51.983333333333299,0,0,"NO"]
[null,"2017-07-07","11:00:00",50000169,"Short Rural","Planned",null,1,110,0,0,"NO"]
[null,"2017-07-07","11:06:00",60026758,"Short Rural","Other","Fuse Operator - No Trigger Found",2,108.3,5.3599930711077594E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-07","11:14:00",10020818,"Urban","Asset failure","Distribution substation",374,144.71836007130099,0.23928427220291701,1.6534479252323202E-3,"NO"]
[null,"2017-07-07","11:15:00",20005336,"Urban","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-07","11:15:00",50000118,"Long Rural","Planned",null,2,35,0,0,"NO"]
[null,"2017-07-07","11:18:00",50000057,"Long Rural","Other","Forced Corrective Maintenance",4,163,8.5273345540151698E-3,5.2314935914203499E-5,"NO"]
[null,"2017-07-07","11:20:00",50000167,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-07","11:20:00",60026765,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-07","11:25:00",10020783,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-07","11:27:00",40001232,"Short Rural","Asset failure","HV",1,166.38333333333301,4.11732924198744E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","11:30:00",50000030,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-07","11:30:00",83022292,"Long Rural","Planned",null,3,120,0,0,"NO"]
[null,"2017-07-07","11:33:00",20006666,"Short Rural","Asset failure","LV",1,103.566666666667,2.5628652619162499E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","11:39:00",20005133,"Long Rural","Other","Service Fuse",1,84.133333333333297,1.10035748539541E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","11:40:00",84670103,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-07","11:42:00",10020784,"Urban","Other","Service Fuse",1,402.15000000000003,1.77789861800048E-3,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","11:45:00",10020783,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-07","11:47:00",60026791,"Urban","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-07","11:50:00",60026837,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-07-07","12:00:00",50000170,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-07","12:08:00",50000092,"Short Rural","Third party","Vehicle impact",2,130.6,6.4636666212989193E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-07","12:15:00",60026837,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-07","12:20:00",50000170,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-07","12:23:00",60026770,"Urban","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-07","12:30:00",30053756,"Short Rural","Other","Fuse Operator - No Trigger Found",1,276.3,6.8373318815654303E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","12:30:00",50000118,"Long Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-07","12:32:00",30053756,"Short Rural","Other","Service Fuse",1,205.566666666667,5.0869617219946996E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","12:45:00",10020783,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-07","12:45:00",30053769,"Short Rural","Other","Forced Corrective Maintenance",11,102,2.7765061060862901E-3,2.7220648098885201E-5,"NO"]
[null,"2017-07-07","12:45:00",60026701,"Long Rural","Other","Forced Corrective Maintenance",1,105,1.3732670677478402E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","13:00:00",20001353,"Short Rural","Other","Forced Corrective Maintenance",3,95,7.0526224619838905E-4,7.4238131178777803E-6,"NO"]
[null,"2017-07-07","13:00:00",83022292,"Long Rural","Planned",null,2,115.5,0,0,"NO"]
[null,"2017-07-07","13:05:00",10020799,"Short Rural","Other","Service Fuse",2,145.55000000000001,7.2035733287140701E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-07","13:05:00",50000118,"Long Rural","Planned",null,1,31,0,0,"NO"]
[null,"2017-07-07","13:07:00",82536638,"Short Rural","Planned",null,2,38.999999999999993,0,0,"NO"]
[null,"2017-07-07","13:08:00",40001011,"Long Rural","Other","Service Fuse",1,67.516666666666708,8.8303252245182698E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-07","13:15:00",82912280,"Urban","Planned",null,10,87,0,0,"NO"]
[null,"2017-07-07","13:30:00",20004796,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-07","13:30:00",50000208,"Short Rural","Planned",null,9,53.4,0,0,"NO"]
[null,"2017-07-07","13:30:00",60026640,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-07","13:31:00",20005133,"Long Rural","Asset failure","LV",1,136.416666666667,1.78415729357398E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","13:31:00",50000169,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-07","13:36:00",20005605,"Urban","Asset failure","LV",1,72.783333333333303,3.2177393446923102E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","13:40:00",50000118,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-07","13:44:00",60330968,"Short Rural","Other","Forced Corrective Maintenance",59,31,4.5260513975328197E-3,1.4600165798493001E-4,"NO"]
[null,"2017-07-07","13:49:00",10020662,"Short Rural","Other","Service Fuse",1,107.466666666667,2.6593748324486605E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","13:59:00",50000169,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-07","14:04:00",40001231,"Short Rural","Asset failure","LV",1,85.516666666666708,2.1161991726572699E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","14:08:00",20005851,"Urban","Third party","Vehicle impact",413,27.870661824051698,5.0888101953780095E-2,1.8258662917672401E-3,"NO"]
[null,"2017-07-07","14:10:00",30053765,"Long Rural","Third party","Vehicle impact",8,483.36666666666702,5.0574592379457703E-2,1.0462987182840701E-4,"NO"]
[null,"2017-07-07","14:17:00",50000169,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-07","14:20:00",20002622,"Short Rural","Other","Service Fuse",2,58.15,2.8779648853639503E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-07","14:30:00",60026805,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-07","14:40:00",50000169,"Short Rural","Planned",null,3,10,0,0,"NO"]
[null,"2017-07-07","15:20:00",20005851,"Urban","Asset failure","HV",93,55.062903225806501,2.26391946735988E-2,4.1115148942942804E-4,"NO"]
[null,"2017-07-07","15:22:00",20007736,"Long Rural","Animal","Animal impact",1,75.349999999999994,9.8548260528380895E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-07","15:26:00",60026888,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",18,80.45,1.89393146743395E-2,2.3541721161391601E-4,"NO"]
[null,"2017-07-07","15:30:00",50000165,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-07","15:50:00",82917289,"Urban","Vegetation","Grow-in - NSP responsibility",1,67.966666666666711,3.0047952937154197E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","15:56:00",60026697,"Short Rural","Other","Service Fuse",2,28.5,1.4105244923967803E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-07","16:00:00",30053807,"Short Rural","Other","Service Fuse",1,4206.0666666666693,1.04083509648895E-2,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","16:03:00",30053765,"Long Rural","Asset failure","LV",1,208.03333333333299,2.72081262533787E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","16:07:00",30053833,"Short Rural","Other","Service Fuse",1,116.48333333333299,2.8825016600471002E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","16:15:00",60026746,"Urban","Other","Service Fuse",2,68.933333333333294,6.095062940072091E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-07","16:19:00",50000166,"Urban","Planned",null,2,14,0,0,"NO"]
[null,"2017-07-07","16:46:00",82921011,"Urban","Asset failure","LV",1,152.36666666666699,6.7361055848814098E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","17:10:00",50000192,"Urban","Other","Service Fuse",1,86.05,3.8042565231615302E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-07","17:25:00",10020800,"Urban","Other","Forced Corrective Maintenance",16,195,1.3793469322793701E-2,7.0735740116890795E-5,"NO"]
[null,"2017-07-07","17:46:00",60026762,"Urban","Other","Service Fuse",2,47.099999999999994,4.1645666993819503E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-07","17:49:00",83850831,"Short Rural","Animal","Animal impact",1,37.699999999999996,9.3292584847997411E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","18:07:00",40001038,"Long Rural","Other","Fuse Operator - No Trigger Found",1,84.783333333333303,1.10885866248147E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","18:11:00",60026762,"Urban","Other","Service Fuse",2,41.033333333333303,3.6281540034955201E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-07","19:50:00",20012370,"Short Rural","Other","Service Fuse",1,123.933333333333,3.06685968580773E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","20:07:00",40001059,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",49,99.5833333333333,1.20750382532593E-2,1.2125561425867E-4,"NO"]
[null,"2017-07-07","20:26:00",20002064,"Short Rural","Asset failure","Zone substation",103,97.65,2.4889447049652898E-2,2.5488425038046997E-4,"NO"]
[null,"2017-07-07","20:26:00",20007497,"Short Rural","Asset failure","Zone substation",26,96.65,6.2184333279716904E-3,6.4339713688274083E-5,"NO"]
[null,"2017-07-07","20:26:00",84579665,"Short Rural","Asset failure","Zone substation",102,97.65,2.4647801932666E-2,2.5240964600784405E-4,"NO"]
[null,"2017-07-07","20:55:00",60026783,"Long Rural","Other","Vibration",1,76.766666666666708,1.0040108117534202E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-07","20:57:00",40001046,"Short Rural","Other","Service Fuse",1,179.8,4.4493386619814197E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","21:57:00",20007716,"Short Rural","Other","Service Fuse",1,107.783333333333,2.66721107962864E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-07","23:33:00",20002985,"Urban","Other","Forced Corrective Maintenance",45,82,1.6313430064457901E-2,1.9894426907875502E-4,"NO"]
[null,"2017-07-07","23:33:00",20020964,"Short Rural","Other","Forced Corrective Maintenance",1,82,2.0291755855532601E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","00:45:00",40001035,"Short Rural","Other","Forced Corrective Maintenance",1,71,1.7569691045644101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","04:28:00",40001116,"Long Rural","Asset failure","Distribution substation",736,242.31431159420299,2.3325050135146896,9.62594820821344E-3,"NO"]
[null,"2017-07-08","06:09:00",30053840,"Short Rural","Asset failure","Distribution substation",1,101.116666666667,2.5022374547869201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","06:30:00",60026781,"Urban","Planned",null,1,42.999999999999993,0,0,"NO"]
[null,"2017-07-08","07:06:00",40001062,"Long Rural","Overloads",null,1,131.11666666666699,1.7148400034876601E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-08","07:14:00",84332230,"Short Rural","Asset failure","HV",16,180.8,7.1585355291322803E-3,3.9593669962014799E-5,"NO"]
[null,"2017-07-08","07:36:00",50000061,"Short Rural","Other","Service Fuse",1,180.46666666666698,4.4658360244655896E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","07:51:00",30053840,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",3,338.91666666666703,2.5160539958674101E-3,7.4238131178777803E-6,"NO"]
[null,"2017-07-08","08:00:00",60026774,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-08","08:05:00",50000111,"Urban","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-08","08:08:00",30053830,"Short Rural","Planned",null,36,463,0,0,"NO"]
[null,"2017-07-08","08:15:00",20006666,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-08","08:30:00",10020798,"Short Rural","Planned",null,9,100,0,0,"NO"]
[null,"2017-07-08","08:30:00",10020826,"Short Rural","Other","Service Fuse",1,81.266666666666708,2.0110284868206702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","08:40:00",50000111,"Urban","Planned",null,4,11,0,0,"NO"]
[null,"2017-07-08","08:45:00",50000096,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","08:48:00",60026647,"Short Rural","Animal","Animal impact",1,46.599999999999994,1.15316563764368E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","08:50:00",60026774,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-08","08:51:00",60026666,"Long Rural","Animal","Animal impact",3,95.466666666666697,3.7457494114569701E-3,3.9236201935652595E-5,"NO"]
[null,"2017-07-08","08:54:00",20007716,"Short Rural","Animal","Animal impact",1,114.25,2.8272354957251203E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","08:55:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","09:00:00",20007229,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-08","09:00:00",50000096,"Urban","Planned",null,3,35,0,0,"NO"]
[null,"2017-07-08","09:00:00",50000208,"Short Rural","Planned",null,18,150,0,0,"NO"]
[null,"2017-07-08","09:05:00",40001215,"Urban","Other","Vibration",1,166.083333333333,7.3425171902585101E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-08","09:06:00",60026774,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-08","09:08:00",40001053,"Short Rural","Other","Forced Corrective Maintenance",160,75,2.9695252471511099E-2,3.9593669962014805E-4,"NO"]
[null,"2017-07-08","09:26:00",20005919,"Urban","Asset failure","LV",2,244.55,2.1623031556982104E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-08","09:30:00",60026798,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-08","09:33:00",50000169,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-08","09:45:00",20005336,"Urban","Planned",null,5,45,0,0,"NO"]
[null,"2017-07-08","09:50:00",50000169,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-07-08","10:00:00",60026798,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-08","10:03:00",50000096,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-08","10:10:00",50000195,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","10:15:00",50000092,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-08","10:18:00",10020839,"Urban","Other","Service Fuse",3,115.533333333333,1.5323129702821501E-3,1.3262951271916999E-5,"NO"]
[null,"2017-07-08","10:30:00",50000169,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-08","10:35:00",50000195,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-08","10:41:00",10020774,"Short Rural","Other","Forced Corrective Maintenance",7,49,8.4878929981069306E-4,1.7322230608381499E-5,"NO"]
[null,"2017-07-08","10:45:00",50000170,"Short Rural","Planned",null,3,15,0,0,"NO"]
[null,"2017-07-08","10:55:00",20011824,"Long Rural","Asset failure","HV",31,309.93333333333305,0.12565960415031802,4.0544075333507701E-4,"NO"]
[null,"2017-07-08","11:00:00",60026798,"Short Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-07-08","11:12:00",50000096,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-08","11:20:00",50000170,"Short Rural","Planned",null,3,20,0,0,"NO"]
[null,"2017-07-08","11:21:00",50000092,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-08","11:30:00",10128810,"Short Rural","Other","Forced Corrective Maintenance",8,13,2.5735885475309601E-4,1.9796834981007399E-5,"NO"]
[null,"2017-07-08","11:30:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","11:31:00",60026774,"Short Rural","Planned",null,3,9,0,0,"NO"]
[null,"2017-07-08","11:34:00",83016237,"Long Rural","Planned",null,1,42.999999999999993,0,0,"NO"]
[null,"2017-07-08","11:40:00",20005336,"Urban","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-08","11:48:00",50000096,"Urban","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-08","11:52:00",20005447,"Short Rural","Other","Forced Corrective Maintenance",1,81,2.0044295418270001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","11:55:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","11:59:00",50000092,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","12:00:00",50000092,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-08","12:00:00",50000167,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-08","12:06:00",30184151,"Short Rural","Planned",null,1,71,0,0,"NO"]
[null,"2017-07-08","12:18:00",50000092,"Short Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-08","12:22:00",50000170,"Short Rural","Planned",null,2,14,0,0,"NO"]
[null,"2017-07-08","12:24:00",60026774,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","12:41:00",50000167,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-08","12:50:00",60026774,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-08","13:00:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","13:08:00",50000090,"Urban","Planned",null,2,7,0,0,"NO"]
[null,"2017-07-08","13:09:00",50000167,"Short Rural","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-08","13:13:00",20010102,"Short Rural","Asset failure","LV",1,86.3333333333333,2.1364084417003798E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","13:20:00",82773016,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-08","13:30:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","13:30:00",60026774,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-08","13:38:00",20005336,"Urban","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-08","13:38:00",50000096,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-08","13:45:00",50000096,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-08","13:50:00",50000167,"Short Rural","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-08","14:05:00",82773016,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-08","14:25:00",50000096,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","14:25:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","14:30:00",60026798,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","14:32:00",85081013,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-08","14:45:00",40001189,"Short Rural","Other","Service Fuse",1,92.866666666666703,2.2980825940452802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","14:50:00",60026798,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-08","15:02:00",40001176,"Short Rural","Other","Service Fuse",1,104.366666666667,2.5826620968972597E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","15:06:00",50000096,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-08","15:10:00",60026798,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-08","15:20:00",50000096,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","15:30:00",50000096,"Urban","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-08","15:30:00",82773016,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-08","15:41:00",50000096,"Urban","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-08","15:44:00",50000096,"Urban","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-08","15:51:00",50000178,"Urban","Other","Service Fuse",1,51.716666666666697,2.28638543315325E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-08","15:54:00",60026773,"Short Rural","Other","Service Fuse",1,180.73333333333301,4.4724349694592598E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","16:00:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-08","16:14:00",82563086,"Short Rural","Other","Fuse Operator - No Trigger Found",1,85.4166666666667,2.1137245682846501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","16:40:00",50000096,"Urban","Planned",null,5,20,0,0,"NO"]
[null,"2017-07-08","17:46:00",50000161,"Short Rural","Other","Fuse Operator - No Trigger Found",1,80.75,1.99824303089544E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","18:35:00",30053770,"Long Rural","Other","Service Fuse",1,102.566666666667,1.3414421484000301E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-08","18:56:00",82912277,"Short Rural","Other","Forced Corrective Maintenance",1,60,1.4847626235755599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","19:13:00",60026718,"Short Rural","Other","Service Fuse",1,69.633333333333297,1.7231495114718501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","19:16:00",40001067,"Urban","Other","Fuse Operator - No Trigger Found",1,37.366666666666696,1.65197426397989E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-08","19:53:00",83864041,"Short Rural","Asset failure","LV",1,134.833333333333,3.3365915624239601E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","19:58:00",20013064,"Short Rural","Other","Service Fuse",1,113.45,2.8074386607441105E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-08","20:09:00",40001094,"Urban","Other","Forced Corrective Maintenance",1,91.5833333333333,4.0488842910657802E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-08","21:39:00",60026660,"Short Rural","Asset failure","LV",1,48.849999999999994,1.20884423602777E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","06:14:00",20002744,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20002752,"Short Rural","Planned",null,2035,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20002914,"Urban","Planned",null,339,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20002948,"Short Rural","Planned",null,1076,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20002985,"Urban","Planned",null,55,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20003026,"Short Rural","Planned",null,1320,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20003061,"Urban","Planned",null,260,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20003088,"Short Rural","Planned",null,1118,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20004903,"Short Rural","Planned",null,203,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",20020964,"Short Rural","Planned",null,44,25,0,0,"NO"]
[null,"2017-07-09","06:14:00",82982249,"Short Rural","Planned",null,154,25,0,0,"NO"]
[null,"2017-07-09","06:32:00",20008189,"Short Rural","Other","Service Fuse",1,64.099999999999994,1.5862214028532201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","06:56:00",25273354,"Urban","Asset failure","LV",1,65.883333333333297,2.9126914654382203E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-09","07:35:00",60026676,"Long Rural","Other","Forced Corrective Maintenance",3,152,5.9639026942192004E-3,3.9236201935652595E-5,"NO"]
[null,"2017-07-09","07:40:00",60026666,"Long Rural","Planned",null,1,298,0,0,"NO"]
[null,"2017-07-09","07:41:00",40001046,"Short Rural","Other","Fuse Operator - No Trigger Found",1,105.26666666666701,2.6049335362508905E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","07:43:00",40001119,"Short Rural","Overloads",null,1,73.899999999999991,1.8287326313705599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","08:00:00",50000165,"Short Rural","Planned",null,3,300,0,0,"NO"]
[null,"2017-07-09","08:00:00",84247259,"Urban","Planned",null,90,187,0,0,"NO"]
[null,"2017-07-09","08:17:00",83016237,"Long Rural","Planned",null,1,47,0,0,"NO"]
[null,"2017-07-09","08:24:00",30053824,"Urban","Planned",null,53,298,0,0,"NO"]
[null,"2017-07-09","08:26:00",40001038,"Long Rural","Asset failure","HV",4,108.116666666667,5.6561164879239696E-3,5.2314935914203499E-5,"NO"]
[null,"2017-07-09","08:30:00",10020809,"Urban","Planned",null,31,156,0,0,"NO"]
[null,"2017-07-09","08:35:00",10020857,"Short Rural","Other","Vibration",4,175.98333333333301,1.74195650470381E-3,9.8984174905037098E-6,"NO"]
[null,"2017-07-09","08:35:00",84000793,"Long Rural","Other","Fuse Operator - No Trigger Found",1,70.383333333333297,9.20524893190339E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-09","09:00:00",60026730,"Urban","Planned",null,1,149,0,0,"NO"]
[null,"2017-07-09","09:00:00",60026759,"Urban","Planned",null,17,360,0,0,"NO"]
[null,"2017-07-09","09:00:00",60026777,"Urban","Planned",null,7,360,0,0,"NO"]
[null,"2017-07-09","09:06:00",60026734,"Long Rural","Planned",null,9,225.888888888889,0,0,"NO"]
[null,"2017-07-09","09:40:00",60026755,"Long Rural","Exclusion - Customer Installation Fault",null,1,6,0,0,"NO"]
[null,"2017-07-09","10:00:00",60026818,"Urban","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-09","10:23:00",40000974,"Long Rural","Other","Service Fuse",1,201.933333333333,2.6410323480687103E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-09","10:40:00",82921002,"Urban","Other","Service Fuse",1,111.116666666667,4.9124497849928209E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-09","10:48:00",20003550,"Short Rural","Overloads",null,1,191.25,4.7326808626470799E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","10:50:00",40000965,"Short Rural","Other","Fuse Operator - No Trigger Found",9,103.25,2.2995261132626398E-3,2.2271439353633299E-5,"NO"]
[null,"2017-07-09","11:05:00",40000977,"Long Rural","Asset failure","Distribution substation",1,97.616666666666703,1.2767024152062101E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-09","11:07:00",40001116,"Long Rural","Planned",null,1,54,0,0,"NO"]
[null,"2017-07-09","11:26:00",50000124,"Short Rural","Overloads",null,1,42.133333333333304,1.04263330899972E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","11:27:00",40001091,"Urban","Overloads",null,1,83.949999999999989,3.7114158642581103E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-09","11:30:00",60026666,"Long Rural","Overloads",null,1,170.45000000000002,2.2292702066440003E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-09","12:00:00",83016237,"Long Rural","Planned",null,1,44,0,0,"NO"]
[null,"2017-07-09","12:30:00",10020809,"Urban","Planned",null,10,151,0,0,"NO"]
[null,"2017-07-09","12:34:00",50000031,"Short Rural","Other","Service Fuse",2,92.15,4.5606958587495806E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-09","12:40:00",30053832,"Short Rural","Planned",null,2,237,0,0,"NO"]
[null,"2017-07-09","12:48:00",60026755,"Long Rural","Overloads",null,13,60.783333333333303,1.0334597610951299E-2,1.7002354172116101E-4,"NO"]
[null,"2017-07-09","13:20:00",83016237,"Long Rural","Planned",null,2,49,0,0,"NO"]
[null,"2017-07-09","13:31:00",50000241,"Long Rural","Third party","Vehicle impact",1,162.23333333333301,2.1218066091202403E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-09","13:50:00",60026641,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",43,216.179457364341,0.12157620542331501,5.6238556107768799E-4,"NO"]
[null,"2017-07-09","15:13:00",40001029,"Short Rural","Other","Forced Corrective Maintenance",1,78,1.9301914106482202E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","15:17:00",40001116,"Long Rural","Planned",null,1,54,0,0,"NO"]
[null,"2017-07-09","15:38:00",10020797,"Short Rural","Other","Service Fuse",1,98.866666666666703,2.4465588564028299E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","16:51:00",10020816,"Urban","Overloads",null,34,121.133333333333,1.8207968970588698E-2,1.50313447748393E-4,"NO"]
[null,"2017-07-09","18:01:00",20004751,"Urban","Third party","Other - Third Party",67,107.033333333333,3.1703906086515701E-2,2.9620591173947999E-4,"NO"]
[null,"2017-07-09","18:05:00",60026819,"Long Rural","Other","Fuse Operator - No Trigger Found",2,138.6,3.6254250588543002E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-09","18:10:00",20002652,"Short Rural","Overloads",null,1,55.066666666666698,1.3626821411926801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-09","18:33:00",82773016,"Urban","Other","Service Fuse",3,88.7,1.1764237778190401E-3,1.3262951271916999E-5,"NO"]
[null,"2017-07-09","19:00:00",50000229,"Long Rural","Overloads",null,14,98.133333333333297,1.79684366553318E-2,1.8310227569971198E-4,"NO"]
[null,"2017-07-09","19:02:00",40001116,"Long Rural","Asset failure","HV",84,269.25,0.29580172639288499,1.09861365419827E-3,"NO"]
[null,"2017-07-09","19:20:00",50000059,"Short Rural","Overloads",null,11,136.80000000000001,3.7237846599274902E-3,2.7220648098885201E-5,"NO"]
[null,"2017-07-09","19:27:00",40001210,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",5,92.1666666666667,6.0271165751155306E-3,6.5393669892754389E-5,"NO"]
[null,"2017-07-09","19:33:00",50000124,"Short Rural","Other","Fuse Operator - No Trigger Found",2,46.183333333333302,2.28570957218215E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-09","19:52:00",10020786,"Urban","Other","Service Fuse",1,70.899999999999991,3.1344774839297201E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-09","19:56:00",40001066,"Long Rural","Asset failure","LV",1,760.71666666666715,9.9492109163832904E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","06:01:00",20002744,"Urban","Planned",null,1,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20002752,"Short Rural","Planned",null,2034,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20002914,"Urban","Planned",null,339,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20002948,"Short Rural","Planned",null,1075,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20002985,"Urban","Planned",null,55,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20003026,"Short Rural","Planned",null,1320,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20003061,"Urban","Planned",null,260,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20003088,"Short Rural","Planned",null,1118,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",20020964,"Short Rural","Planned",null,44,38,0,0,"NO"]
[null,"2017-07-10","06:01:00",82982249,"Short Rural","Planned",null,154,38,0,0,"NO"]
[null,"2017-07-10","06:53:00",50000129,"Short Rural","Asset failure","HV",19,60.051754385964898,2.8234823457599701E-3,4.7017483079892603E-5,"NO"]
[null,"2017-07-10","06:57:00",60026685,"Urban","Animal","Animal impact",76,29,9.7438482011017111E-3,3.3599476555523102E-4,"NO"]
[null,"2017-07-10","06:57:00",60026687,"Urban","Animal","Animal impact",602,28.45,7.5717746712998607E-2,2.66143222189802E-3,"NO"]
[null,"2017-07-10","06:57:00",60026690,"Urban","Animal","Animal impact",213,29,2.7308416668877202E-2,9.41669540306109E-4,"NO"]
[null,"2017-07-10","07:30:00",40000998,"Short Rural","Other","Forced Corrective Maintenance",1,32,7.9187339924029597E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","07:38:00",20001488,"Short Rural","Other","Service Fuse",1,219.583333333333,5.4338187682244311E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","07:45:00",50000155,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-10","08:00:00",20003435,"Long Rural","Planned",null,3,87.683333333333294,0,0,"NO"]
[null,"2017-07-10","08:00:00",40001129,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-10","08:16:00",60026649,"Urban","Planned",null,1,224,0,0,"NO"]
[null,"2017-07-10","08:25:00",50000234,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-10","08:30:00",10020829,"Short Rural","Planned",null,10,145,0,0,"NO"]
[null,"2017-07-10","08:30:00",20005962,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","08:30:00",60026755,"Long Rural","Planned",null,1,99,0,0,"NO"]
[null,"2017-07-10","08:30:00",60026836,"Urban","Other","Forced Corrective Maintenance",1,15,6.63147563595851E-5,4.4209837573056797E-6,"NO"]
[null,"2017-07-10","08:30:00",60026838,"Urban","Planned",null,6,198,0,0,"NO"]
[null,"2017-07-10","08:30:00",82649838,"Short Rural","Planned",null,3,95,0,0,"NO"]
[null,"2017-07-10","08:31:00",50000054,"Short Rural","Other","Fuse Operator - No Trigger Found",1,117.7,2.9126093465807202E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","08:40:00",40001066,"Long Rural","Other","Service Fuse",1,162.433333333333,2.1244223559159499E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","08:41:00",20010779,"Short Rural","Other","Service Fuse",1,258.83333333333303,6.4051009844801109E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","08:43:00",60026819,"Long Rural","Other","Fuse Operator - No Trigger Found",115,104.25217391304299,0.15680094166884601,1.5040544075333501E-3,"NO"]
[null,"2017-07-10","08:54:00",20001488,"Short Rural","Third party","Vehicle impact",42,121.62142857142901,1.2640526595810501E-2,1.0393338365028901E-4,"NO"]
[null,"2017-07-10","09:00:00",10020835,"Urban","Planned",null,11,95,0,0,"NO"]
[null,"2017-07-10","09:00:00",20005962,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-10","09:00:00",30053842,"Short Rural","Third party","Vehicle impact",117,126.893447293447,3.6739296305003201E-2,2.8952871159723301E-4,"NO"]
[null,"2017-07-10","09:02:00",50000175,"Short Rural","Planned",null,8,79,0,0,"NO"]
[null,"2017-07-10","09:03:00",50000151,"Short Rural","Planned",null,2,291,0,0,"NO"]
[null,"2017-07-10","09:05:00",25273354,"Urban","Planned",null,2,13,0,0,"NO"]
[null,"2017-07-10","09:05:00",60026891,"Long Rural","Other","Fuse Operator - No Trigger Found",1,159.26666666666699,2.08300636498387E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","09:10:00",60026649,"Urban","Planned",null,2,199.45000000000002,0,0,"NO"]
[null,"2017-07-10","09:20:00",40001010,"Long Rural","Other","Forced Corrective Maintenance",1,29,3.79283285377975E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-10","09:23:00",30053871,"Short Rural","Planned",null,5,135,0,0,"NO"]
[null,"2017-07-10","09:30:00",40001129,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-10","09:40:00",60026779,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-10","09:41:00",40001042,"Long Rural","Third party","Vehicle impact",1,347.78333333333302,4.5485656988403502E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","10:00:00",25273362,"Short Rural","Planned",null,7,10,0,0,"NO"]
[null,"2017-07-10","10:00:00",60026747,"Long Rural","Other","Forced Corrective Maintenance",2,36.999999999999993,9.67826314412765E-4,2.61574679571018E-5,"NO"]
[null,"2017-07-10","10:00:00",60026836,"Urban","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-10","10:10:00",60322053,"Short Rural","Planned",null,4,20,0,0,"NO"]
[null,"2017-07-10","10:11:00",10020806,"Long Rural","Planned",null,4,149,0,0,"NO"]
[null,"2017-07-10","10:18:00",60026990,"Long Rural","Animal","Animal impact",1,85.316666666666706,1.1158339872700299E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","10:24:00",50000234,"Short Rural","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-10","10:25:00",40001145,"Urban","Asset failure","LV",1,80.233333333333306,3.5471026346115897E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-10","10:30:00",40001053,"Short Rural","Planned",null,4,100.75,0,0,"NO"]
[null,"2017-07-10","10:31:00",60026666,"Long Rural","Planned",null,14,29,0,0,"NO"]
[null,"2017-07-10","10:33:00",40001040,"Short Rural","Planned",null,6,97,0,0,"NO"]
[null,"2017-07-10","10:40:00",82649838,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-10","10:46:00",60026649,"Urban","Planned",null,1,134,0,0,"NO"]
[null,"2017-07-10","10:51:00",50000096,"Urban","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-10","10:56:00",40000998,"Short Rural","Other","Forced Corrective Maintenance",2,26,1.28679427376548E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-10","11:00:00",20003435,"Long Rural","Planned",null,2,72,0,0,"NO"]
[null,"2017-07-10","11:00:00",40001129,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-10","11:03:00",25273354,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-10","11:09:00",50000032,"Short Rural","Planned",null,1,2,0,0,"NO"]
[null,"2017-07-10","11:12:00",82649845,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-10","11:16:00",40001030,"Short Rural","Other","Forced Corrective Maintenance",17,2,8.4136548669281499E-5,4.2068274334640702E-5,"NO"]
[null,"2017-07-10","11:16:00",40001031,"Short Rural","Other","Forced Corrective Maintenance",6,2,2.9695252471511097E-5,1.4847626235755599E-5,"NO"]
[null,"2017-07-10","11:16:00",40001032,"Short Rural","Other","Forced Corrective Maintenance",30,2,1.4847626235755599E-4,7.4238131178777804E-5,"NO"]
[null,"2017-07-10","11:16:00",83864041,"Short Rural","Animal","Other",1,135.15,3.3444278096039402E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","11:20:00",50000234,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-10","11:20:00",84670103,"Urban","Planned",null,1,28,0,0,"NO"]
[null,"2017-07-10","11:23:00",30053871,"Short Rural","Planned",null,10,111,0,0,"NO"]
[null,"2017-07-10","11:25:00",50000034,"Short Rural","Planned",null,1,28,0,0,"NO"]
[null,"2017-07-10","11:26:00",30053774,"Short Rural","Other","Service Fuse",1,251.86666666666699,6.2327035465205001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","11:33:00",85081013,"Short Rural","Other","Forced Corrective Maintenance",1,72.283333333333303,1.7887265273464401E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","11:35:00",50000154,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-10","11:43:00",30053837,"Short Rural","Asset failure","LV",1,424.21666666666704,1.0497684182741301E-3,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","11:45:00",82564420,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","11:53:00",50000169,"Short Rural","Planned",null,3,74,0,0,"NO"]
[null,"2017-07-10","11:55:00",40001033,"Long Rural","Other","Forced Corrective Maintenance",94,248.88333333333301,0.30597741738599699,1.2294009939837799E-3,"NO"]
[null,"2017-07-10","11:55:00",40001052,"Long Rural","Other","Forced Corrective Maintenance",50,248.88333333333301,0.16275394541808402,6.5393669892754402E-4,"NO"]
[null,"2017-07-10","11:55:00",82649845,"Short Rural","Planned",null,2,17,0,0,"NO"]
[null,"2017-07-10","11:57:00",50000096,"Urban","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-10","11:57:00",50000148,"Short Rural","Asset failure","HV",1,320.066666666667,7.9203837286513797E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","12:00:00",50000169,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","12:08:00",60026670,"Long Rural","Animal","Other",1,73.449999999999989,9.6063301072456199E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-10","12:20:00",10020842,"Short Rural","Other","Forced Corrective Maintenance",29,85,6.09989977852291E-3,7.1763526806151894E-5,"NO"]
[null,"2017-07-10","12:20:00",50000034,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-10","12:30:00",40001129,"Short Rural","Planned",null,2,35,0,0,"NO"]
[null,"2017-07-10","12:30:00",81669226,"Short Rural","Planned",null,5,50,0,0,"NO"]
[null,"2017-07-10","12:32:00",60026667,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-10","12:42:00",60026836,"Urban","Other","Service Fuse",1,25.466666666666701,1.12587719686051E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-10","12:45:00",10020829,"Short Rural","Planned",null,12,75,0,0,"NO"]
[null,"2017-07-10","12:47:00",84670103,"Urban","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-10","12:50:00",60322051,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-10","13:06:00",10020767,"Short Rural","Other","Service Fuse",1,104.433333333333,2.58431183314568E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","13:13:00",83016237,"Long Rural","Planned",null,1,45.999999999999993,0,0,"NO"]
[null,"2017-07-10","13:15:00",60322051,"Urban","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-10","13:25:00",50000096,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-10","13:25:00",50000127,"Long Rural","Other","Service Fuse",1,71.433333333333294,9.3425756386781797E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-10","13:29:00",30053841,"Short Rural","Planned",null,1,81,0,0,"NO"]
[null,"2017-07-10","13:36:00",30053776,"Short Rural","Asset failure","Distribution substation",1,103.783333333333,2.5682269047236101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","13:38:00",40001184,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-10","13:40:00",50000155,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","13:44:00",60026667,"Long Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-10","13:45:00",40001029,"Short Rural","Other","Forced Corrective Maintenance",1,75,1.85595327946944E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","13:45:00",50000034,"Short Rural","Planned",null,1,40.999999999999993,0,0,"NO"]
[null,"2017-07-10","13:45:00",83924127,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-10","13:50:00",60026667,"Long Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-10","14:00:00",20003435,"Long Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-10","14:00:00",40001129,"Short Rural","Planned",null,1,44,0,0,"NO"]
[null,"2017-07-10","14:00:00",50000109,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-10","14:00:00",82907503,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-10","14:04:00",40001006,"Short Rural","Animal","Animal nesting/burrowing, etc and other",63,295.066666666667,4.6000915603617895E-2,1.55900075475433E-4,"NO"]
[null,"2017-07-10","14:10:00",60322051,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-10","14:10:00",82773016,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","14:18:00",50000096,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-10","14:20:00",84670103,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","14:24:00",10020850,"Short Rural","Other","Forced Corrective Maintenance",16,86,3.4050556167332701E-3,3.9593669962014799E-5,"NO"]
[null,"2017-07-10","14:25:00",84962745,"Long Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-10","14:30:00",50000035,"Short Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-10","14:30:00",82773016,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-10","14:45:00",50000234,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-10","14:45:00",60026837,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-10","14:45:00",82649838,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-10","14:55:00",60322053,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-10","15:02:00",60026764,"Short Rural","Other","Fuse Operator - No Trigger Found",1,119.966666666667,2.9687003790269001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","15:04:00",82563612,"Long Rural","Other","Service Fuse",1,47.233333333333299,6.1775220158688602E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-10","15:10:00",82773016,"Urban","Planned",null,14,20,0,0,"NO"]
[null,"2017-07-10","15:15:00",82773016,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-10","15:23:00",40001184,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-10","15:41:00",10020774,"Short Rural","Other","Service Fuse",1,24.516666666666698,6.0669050535545602E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","16:05:00",40001038,"Long Rural","Asset failure","LV",1,218.23333333333301,2.8542157119190899E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","16:14:00",50000061,"Short Rural","Animal","Animal impact",1,70.9166666666667,1.7549069342538901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","16:40:00",30053783,"Urban","Other","Forced Corrective Maintenance",2,54,4.7746624578901302E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-10","16:56:00",60331115,"Urban","Other","Service Fuse",2,56.8333333333333,5.02518487080412E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-10","17:12:00",50000109,"Short Rural","Other","Service Fuse",2,127.166666666667,6.2937437877119402E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-10","17:46:00",82889011,"Short Rural","Other","Service Fuse",1,63.966666666666697,1.5829219303563802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","18:10:00",85221946,"Short Rural","Asset failure","LV",2,79.716666666666697,3.9453442380899402E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-10","18:26:00",20002698,"Short Rural","Overloads",null,2,62.35,3.08583165266453E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-10","18:27:00",50000016,"Short Rural","Asset failure","LV",1,210.65,5.2127541109365095E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","18:40:00",40001038,"Long Rural","Other","Service Fuse",1,79.25,1.0364896678001598E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","18:54:00",82563117,"Short Rural","Third party","Vehicle impact",1,124.2,3.0734586308014001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","19:33:00",83022292,"Long Rural","Asset failure","LV",1,225.96666666666698,2.9553579213532099E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","20:48:00",50000193,"Short Rural","Other","Service Fuse",1,54.749999999999993,1.3548458940126901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","20:55:00",30053747,"Short Rural","Asset failure","HV",22,1054.2166666666701,5.7392921806626196E-2,5.4441296197770402E-5,"NO"]
[null,"2017-07-10","21:17:00",40001111,"Long Rural","Asset failure","LV",1,118.916666666667,1.5552794489493401E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-10","21:20:00",30053771,"Short Rural","Asset failure","LV",1,74.55,1.8448175597926301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-10","22:32:00",50000149,"Short Rural","Overloads",null,7,133.55000000000001,2.3133838977493501E-3,1.7322230608381499E-5,"NO"]
[null,"2017-07-11","00:13:00",20013273,"Short Rural","Asset failure","HV",65,779.85,0.125438314299501,1.6084928422068501E-4,"NO"]
[null,"2017-07-11","01:10:00",40001226,"Short Rural","Other","Service Fuse",1,121.5,3.0066443127404997E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","02:47:00",30053824,"Urban","Other","Service Fuse",1,324.10000000000002,1.43284083574277E-3,4.4209837573056797E-6,"NO"]
[null,"2017-07-11","06:00:00",82915256,"Urban","Planned",null,1,179.916666666667,0,0,"NO"]
[null,"2017-07-11","06:30:00",60327522,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-11","06:59:00",10020670,"Long Rural","Animal","Animal impact",1,20.316666666666698,2.6571627866422498E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-11","07:05:00",82982249,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-11","07:17:00",84119480,"Short Rural","Other","Fuse Operator - No Trigger Found",1,98.766666666666708,2.4440842520302101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","07:21:00",50000015,"Short Rural","Asset failure","HV",1,353.76666666666705,8.7543254022263203E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","07:33:00",50000236,"Long Rural","Overloads",null,1,53.016666666666701,6.9339087976283908E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-11","08:00:00",40001129,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-11","08:00:00",50000234,"Short Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-11","08:00:00",60026836,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","08:00:00",82991938,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-11","08:00:00",85161218,"Short Rural","Planned",null,16,386,0,0,"NO"]
[null,"2017-07-11","08:01:00",50000175,"Short Rural","Planned",null,2,146,0,0,"NO"]
[null,"2017-07-11","08:04:00",40001045,"Short Rural","Other","Service Fuse",1,97.899999999999991,2.4226376808007802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","08:07:00",20003435,"Long Rural","Planned",null,3,222.13333333333301,0,0,"NO"]
[null,"2017-07-11","08:24:00",30053832,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-11","08:25:00",20002698,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-11","08:30:00",10020673,"Long Rural","Planned",null,1,88,0,0,"NO"]
[null,"2017-07-11","08:30:00",10020780,"Short Rural","Planned",null,5,23,0,0,"NO"]
[null,"2017-07-11","08:30:00",10020786,"Urban","Planned",null,93,246.77419354838702,0,0,"NO"]
[null,"2017-07-11","08:30:00",20005447,"Short Rural","Planned",null,4,210,0,0,"NO"]
[null,"2017-07-11","08:30:00",50000125,"Long Rural","Planned",null,7,131,0,0,"NO"]
[null,"2017-07-11","08:30:00",50000174,"Short Rural","Planned",null,5,197,0,0,"NO"]
[null,"2017-07-11","08:30:00",60026751,"Long Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-11","08:30:00",82912323,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-11","08:30:00",83864058,"Short Rural","Other","Forced Corrective Maintenance",533,8,1.0551713044877E-2,1.3189641306096199E-3,"NO"]
[null,"2017-07-11","08:30:00",83897502,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","08:30:00",84659987,"Urban","Planned",null,1,165,0,0,"NO"]
[null,"2017-07-11","08:32:00",10020842,"Short Rural","Planned",null,1,206,0,0,"NO"]
[null,"2017-07-11","08:32:00",40000963,"Long Rural","Planned",null,16,60,0,0,"NO"]
[null,"2017-07-11","08:33:00",20001488,"Short Rural","Asset failure","LV",1,83.233333333333306,2.0596957061489802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","08:34:00",40001094,"Urban","Other","Service Fuse",1,34.366666666666696,1.51934475126072E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-11","08:37:00",20008373,"Short Rural","Planned",null,32,152,0,0,"NO"]
[null,"2017-07-11","08:41:00",50000234,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-11","08:42:00",83864058,"Short Rural","Planned",null,16,165,0,0,"NO"]
[null,"2017-07-11","08:42:00",84737242,"Short Rural","Planned",null,4,272,0,0,"NO"]
[null,"2017-07-11","08:45:00",10020772,"Long Rural","Planned",null,4,150,0,0,"NO"]
[null,"2017-07-11","08:50:00",20002698,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","08:55:00",50000035,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-11","09:00:00",10020809,"Urban","Planned",null,16,335,0,0,"NO"]
[null,"2017-07-11","09:00:00",10020857,"Short Rural","Planned",null,3,92,0,0,"NO"]
[null,"2017-07-11","09:00:00",50000034,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-11","09:00:00",60026670,"Long Rural","Planned",null,1,84,0,0,"NO"]
[null,"2017-07-11","09:00:00",60026671,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-11","09:00:00",60026758,"Short Rural","Planned",null,9,293.88888888888903,0,0,"NO"]
[null,"2017-07-11","09:00:00",82536638,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-11","09:00:00",82912274,"Short Rural","Planned",null,1,85,0,0,"NO"]
[null,"2017-07-11","09:01:00",20009493,"Short Rural","Planned",null,17,412,0,0,"NO"]
[null,"2017-07-11","09:01:00",20011334,"Short Rural","Planned",null,1,412,0,0,"NO"]
[null,"2017-07-11","09:01:00",30053820,"Urban","Planned",null,2,40,0,0,"NO"]
[null,"2017-07-11","09:01:00",40001120,"Short Rural","Planned",null,30,213,0,0,"NO"]
[null,"2017-07-11","09:01:00",82561856,"Long Rural","Planned",null,13,164,0,0,"NO"]
[null,"2017-07-11","09:05:00",50000094,"Long Rural","Planned",null,26,311,0,0,"NO"]
[null,"2017-07-11","09:06:00",40001038,"Long Rural","Planned",null,16,37,0,0,"NO"]
[null,"2017-07-11","09:08:00",25273358,"Urban","Planned",null,2,13,0,0,"NO"]
[null,"2017-07-11","09:10:00",20005887,"Short Rural","Planned",null,1,75,0,0,"NO"]
[null,"2017-07-11","09:15:00",25280514,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","09:15:00",82773016,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-11","09:18:00",60026839,"Short Rural","Planned",null,10,232,0,0,"NO"]
[null,"2017-07-11","09:20:00",20010327,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-11","09:20:00",50000236,"Long Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-11","09:20:00",60026675,"Long Rural","Planned",null,13,52,0,0,"NO"]
[null,"2017-07-11","09:27:00",60026666,"Long Rural","Other","Fuse Operator - No Trigger Found",1,223.15,2.9185194873136305E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","09:28:00",60026672,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-11","09:30:00",40000966,"Long Rural","Planned",null,1,272,0,0,"NO"]
[null,"2017-07-11","09:33:00",50000026,"Short Rural","Planned",null,3,169,0,0,"NO"]
[null,"2017-07-11","09:35:00",50000035,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-11","09:38:00",60026774,"Short Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-11","09:40:00",40001105,"Urban","Asset failure","LV",1,71.3333333333333,3.15363508021138E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-11","09:40:00",82915256,"Urban","Planned",null,1,80,0,0,"NO"]
[null,"2017-07-11","09:44:00",25273358,"Urban","Planned",null,2,9,0,0,"NO"]
[null,"2017-07-11","09:46:00",20007634,"Long Rural","Planned",null,9,196,0,0,"NO"]
[null,"2017-07-11","09:48:00",50000234,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-11","09:50:00",60026672,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","09:58:00",60026755,"Long Rural","Other","Service Fuse",1,41.8333333333333,5.4712703810271197E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-11","10:00:00",40001129,"Short Rural","Planned",null,1,45.999999999999993,0,0,"NO"]
[null,"2017-07-11","10:00:00",40001208,"Long Rural","Other","Service Fuse",1,84.35,1.1031912110907698E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","10:10:00",40001144,"Urban","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-11","10:13:00",10020783,"Urban","Planned",null,3,13,0,0,"NO"]
[null,"2017-07-11","10:15:00",50000234,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-11","10:20:00",20007736,"Long Rural","Other","Forced Corrective Maintenance",4,29,1.5171331415118998E-3,5.2314935914203499E-5,"NO"]
[null,"2017-07-11","10:23:00",20008471,"Short Rural","Other","Service Fuse",1,102.366666666667,2.5331700094447402E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","10:25:00",82554089,"Urban","Other","Service Fuse",2,80.733333333333306,7.1384151067962304E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-11","10:29:00",10020832,"Urban","Asset failure","LV",2,143.51666666666699,1.2689697044719701E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-11","10:30:00",50000035,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-11","10:30:00",60026640,"Short Rural","Planned",null,1,62,0,0,"NO"]
[null,"2017-07-11","10:30:00",83850831,"Short Rural","Planned",null,3,150,0,0,"NO"]
[null,"2017-07-11","10:36:00",40001066,"Long Rural","Other","Fuse Operator - No Trigger Found",1,89.649999999999991,1.1725085011770899E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","10:40:00",20007229,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-11","10:40:00",40001061,"Long Rural","Planned",null,1,72,0,0,"NO"]
[null,"2017-07-11","10:40:00",60026671,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","10:42:00",50000021,"Short Rural","Planned",null,7,295,0,0,"NO"]
[null,"2017-07-11","10:49:00",82915259,"Short Rural","Asset failure","LV",1,70.650000000000006,1.74830798926022E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","10:49:00",83864058,"Short Rural","Asset failure","LV",1,111.55,2.7604211776642205E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","10:50:00",20002622,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-07-11","10:50:00",30053847,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","10:50:00",82773016,"Urban","Planned",null,3,35,0,0,"NO"]
[null,"2017-07-11","11:00:00",30053848,"Short Rural","Planned",null,51,95,0,0,"NO"]
[null,"2017-07-11","11:00:00",50000170,"Short Rural","Planned",null,3,23,0,0,"NO"]
[null,"2017-07-11","11:00:00",60026717,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-11","11:01:00",50000175,"Short Rural","Planned",null,49,68,0,0,"NO"]
[null,"2017-07-11","11:06:00",50000234,"Short Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-11","11:08:00",60026671,"Short Rural","Planned",null,2,42,0,0,"NO"]
[null,"2017-07-11","11:09:00",30053833,"Short Rural","Planned",null,2,36.999999999999993,0,0,"NO"]
[null,"2017-07-11","11:13:00",20005628,"Short Rural","Other","Service Fuse",1,98.866666666666703,2.4465588564028299E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","11:20:00",20002698,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-11","11:20:00",40001010,"Long Rural","Planned",null,1,74,0,0,"NO"]
[null,"2017-07-11","11:20:00",50000037,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-11","11:22:00",40001116,"Long Rural","Planned",null,2,64,0,0,"NO"]
[null,"2017-07-11","11:23:00",10020771,"Long Rural","Animal","Animal impact",1,196.76666666666699,2.5734588891795302E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","11:25:00",60026652,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-11","11:25:00",60026774,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-11","11:25:00",84670103,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-11","11:27:00",50000175,"Short Rural","Planned",null,1,52.983333333333299,0,0,"NO"]
[null,"2017-07-11","11:30:00",40001129,"Short Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-11","11:35:00",20002698,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","11:40:00",60026717,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-11","11:45:00",20006212,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-11","11:51:00",40001230,"Short Rural","Planned",null,2,7,0,0,"NO"]
[null,"2017-07-11","12:00:00",20007334,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-11","12:00:00",60026671,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-11","12:05:00",82914179,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","12:06:00",25274647,"Urban","Planned",null,1,44,0,0,"NO"]
[null,"2017-07-11","12:06:00",60026774,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-11","12:10:00",50000166,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-11","12:15:00",20007334,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-11","12:15:00",40001067,"Urban","Exclusion - Customer Installation Fault",null,1,3,0,0,"NO"]
[null,"2017-07-11","12:20:00",60026672,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-11","12:29:00",82649838,"Short Rural","Other","Forced Corrective Maintenance",1,3,7.4238131178777803E-6,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","12:30:00",10020675,"Short Rural","Other","Forced Corrective Maintenance",1,10,2.4746043726259301E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","12:30:00",20002622,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-11","12:36:00",30053846,"Short Rural","Planned",null,1,29,0,0,"NO"]
[null,"2017-07-11","12:40:00",10020808,"Urban","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-11","12:40:00",50000169,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-11","12:46:00",60026774,"Short Rural","Planned",null,2,23,0,0,"NO"]
[null,"2017-07-11","12:51:00",60026672,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-07-11","12:51:00",84670103,"Urban","Planned",null,1,38,0,0,"NO"]
[null,"2017-07-11","12:59:00",20010327,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-11","12:59:00",60026994,"Long Rural","Other","Forced Corrective Maintenance",406,78,0.41417734763274899,5.3099659952916605E-3,"NO"]
[null,"2017-07-11","12:59:00",60300323,"Long Rural","Other","Forced Corrective Maintenance",42,78,4.2845932513732699E-2,5.4930682709913696E-4,"NO"]
[null,"2017-07-11","13:00:00",20011656,"Urban","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-11","13:00:00",40001129,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-07-11","13:00:00",50000030,"Short Rural","Planned",null,7,20,0,0,"NO"]
[null,"2017-07-11","13:00:00",60026767,"Urban","Planned",null,2,120,0,0,"NO"]
[null,"2017-07-11","13:01:00",40001010,"Long Rural","Planned",null,1,38.999999999999993,0,0,"NO"]
[null,"2017-07-11","13:01:00",50000234,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-11","13:02:00",10132687,"Short Rural","Animal","Animal impact",1,137.70000000000002,3.4075302211059001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","13:10:00",82649838,"Short Rural","Planned",null,9,25,0,0,"NO"]
[null,"2017-07-11","13:15:00",50000193,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","13:20:00",50000035,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-11","13:20:00",50000170,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","13:22:00",82889011,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-11","13:24:00",10020778,"Short Rural","Planned",null,1,82,0,0,"NO"]
[null,"2017-07-11","13:25:00",60026666,"Long Rural","Planned",null,1,36.999999999999993,0,0,"NO"]
[null,"2017-07-11","13:30:00",20005577,"Urban","Planned",null,2,120,0,0,"NO"]
[null,"2017-07-11","13:30:00",50000175,"Short Rural","Planned",null,3,61,0,0,"NO"]
[null,"2017-07-11","13:33:00",60026759,"Urban","Other","Service Fuse",1,86.283333333333303,3.8145721519285798E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-11","13:40:00",10020783,"Urban","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-11","13:40:00",20002267,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-11","13:40:00",50000193,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-11","13:42:00",82889011,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-11","13:44:00",50000232,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-11","13:45:00",50000236,"Long Rural","Planned",null,1,33,0,0,"NO"]
[null,"2017-07-11","13:49:00",60026774,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-11","13:54:00",50000170,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-11","13:58:00",20003792,"Short Rural","Exclusion - Customer Installation Fault",null,1,7,0,0,"NO"]
[null,"2017-07-11","14:00:00",40001010,"Long Rural","Planned",null,1,40.999999999999993,0,0,"NO"]
[null,"2017-07-11","14:00:00",40001129,"Short Rural","Planned",null,1,58.999999999999993,0,0,"NO"]
[null,"2017-07-11","14:00:00",60026675,"Long Rural","Other","Forced Corrective Maintenance",1,16,2.0925974365681402E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-11","14:00:00",60322053,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-11","14:02:00",82649838,"Short Rural","Planned",null,4,21,0,0,"NO"]
[null,"2017-07-11","14:10:00",82554089,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-11","14:11:00",82915271,"Urban","Other","Service Fuse",1,123.083333333333,5.4414941746170698E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-11","14:15:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-11","14:17:00",20011656,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-11","14:17:00",30053832,"Short Rural","Planned",null,4,14,0,0,"NO"]
[null,"2017-07-11","14:25:00",50000193,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-11","14:36:00",40001005,"Long Rural","Other","Forced Corrective Maintenance",2,1489,3.8948469788124503E-2,2.61574679571018E-5,"NO"]
[null,"2017-07-11","14:40:00",10020783,"Urban","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-11","14:45:00",50000233,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-11","14:50:00",60322051,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-11","14:55:00",82561865,"Short Rural","Planned",null,2,36,0,0,"NO"]
[null,"2017-07-11","15:00:00",10020772,"Long Rural","Other","Service Fuse",1,88.55,1.15812189380068E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","15:01:00",50000139,"Short Rural","Exclusion - Customer Installation Fault",null,1,1466.6166666666702,0,0,"NO"]
[null,"2017-07-11","15:03:00",50000090,"Urban","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-11","15:03:00",83868949,"Short Rural","Asset failure","LV",1,2374.7333333333299,5.8765254904872104E-3,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","15:05:00",50000232,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-11","15:09:00",82912323,"Urban","Planned",null,2,33.999999999999993,0,0,"NO"]
[null,"2017-07-11","15:14:00",60026819,"Long Rural","Animal","Animal impact",1,114.166666666667,1.4931554625512301E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","15:19:00",60026774,"Short Rural","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-11","15:29:00",82649845,"Short Rural","Planned",null,1,2,0,0,"NO"]
[null,"2017-07-11","15:30:00",60026751,"Long Rural","Other","Forced Corrective Maintenance",1,21,2.7465341354956799E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-11","16:21:00",60026823,"Urban","Other","Forced Corrective Maintenance",1,2,8.8419675146113493E-6,4.4209837573056797E-6,"NO"]
[null,"2017-07-11","16:45:00",50000037,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-11","17:41:00",50000035,"Short Rural","Asset failure","LV",2,82.600000000000009,4.0880464235780299E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-11","18:18:00",40000966,"Long Rural","Other","Fuse Operator - No Trigger Found",1,83.25,1.08880460371436E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-11","19:07:00",40001135,"Short Rural","Overloads",null,1,48.266666666666701,1.1944090438541101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","19:52:00",20007111,"Short Rural","Other","Service Fuse",1,985.28333333333308,2.4381864449421098E-3,2.4746043726259304E-6,"NO"]
[null,"2017-07-11","20:26:00",60026678,"Short Rural","Overloads",null,113,56.483333333333299,1.5794451112128401E-2,2.7963029410672997E-4,"NO"]
[null,"2017-07-11","23:52:00",50000127,"Long Rural","Asset failure","HV",25,272.14999999999998,8.8984436306565509E-2,3.2696834946377201E-4,"NO"]
[null,"2017-07-12","05:30:00",20005832,"Urban","Planned",null,5,70,0,0,"NO"]
[null,"2017-07-12","05:45:00",20007716,"Short Rural","Animal","Animal impact",1,132.19999999999999,3.2714269806114702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","05:45:00",50000095,"Long Rural","Other","Service Fuse",1,128.23333333333301,1.6771296538495102E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-12","06:00:00",30053840,"Short Rural","Asset failure","LV",1,148.65,3.6784993999084396E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","06:20:00",10020828,"Long Rural","Asset failure","HV",14,349.48333333333306,6.3991193652454398E-2,1.8310227569971198E-4,"NO"]
[null,"2017-07-12","06:30:00",20001081,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","07:04:00",60026763,"Urban","Other","Service Fuse",1,52.283333333333303,2.31143767444465E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-12","07:21:00",20010920,"Long Rural","Animal","Animal impact",31,178.38333333333301,7.2323873049088799E-2,4.0544075333507701E-4,"NO"]
[null,"2017-07-12","07:36:00",84023546,"Short Rural","Other","Vibration",1,82.033333333333303,2.03000045367747E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","07:45:00",82772982,"Short Rural","Asset failure","LV",1,117.416666666667,2.9055979675249397E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","07:53:00",20001263,"Short Rural","Third party","Vehicle impact",242,93.104407713498603,5.5755971014134105E-2,5.9885425817547396E-4,"NO"]
[null,"2017-07-12","07:53:00",20008189,"Short Rural","Third party","Vehicle impact",172,77.133333333333297,3.2830411238003294E-2,4.2563195209165903E-4,"NO"]
[null,"2017-07-12","07:53:00",20008471,"Short Rural","Third party","Vehicle impact",133,80.133333333333297,2.6373673508947801E-2,3.2912238155924801E-4,"NO"]
[null,"2017-07-12","07:53:00",20010779,"Short Rural","Asset failure","HV",30,80.133333333333297,5.9489489117927306E-3,7.4238131178777804E-5,"NO"]
[null,"2017-07-12","08:00:00",10020777,"Short Rural","Planned",null,4,31,0,0,"NO"]
[null,"2017-07-12","08:00:00",10020832,"Urban","Planned",null,2,12,0,0,"NO"]
[null,"2017-07-12","08:00:00",20003435,"Long Rural","Planned",null,1,159.45000000000002,0,0,"NO"]
[null,"2017-07-12","08:00:00",40001129,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-12","08:01:00",40001194,"Urban","Planned",null,53,98,0,0,"NO"]
[null,"2017-07-12","08:02:00",30053848,"Short Rural","Planned",null,55,176,0,0,"NO"]
[null,"2017-07-12","08:04:00",82921882,"Urban","Asset failure","LV",1,360.21666666666704,1.59251203244413E-3,4.4209837573056797E-6,"NO"]
[null,"2017-07-12","08:10:00",50000035,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","08:10:00",50000037,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","08:13:00",20005978,"Urban","Planned",null,2,137,0,0,"NO"]
[null,"2017-07-12","08:13:00",40001208,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","08:16:00",20006350,"Short Rural","Other","Fuse Operator - No Trigger Found",1,105.833333333333,2.6189562943624396E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","08:16:00",60026740,"Short Rural","Animal","Animal impact",1,80.899999999999991,2.0019549374543702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","08:16:00",83016237,"Long Rural","Planned",null,1,47.999999999999993,0,0,"NO"]
[null,"2017-07-12","08:20:00",60026821,"Long Rural","Planned",null,1,68,0,0,"NO"]
[null,"2017-07-12","08:21:00",50000020,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","08:25:00",50000232,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-12","08:28:00",20001081,"Urban","Other","Service Fuse",1,213.666666666667,9.4461686281097903E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-12","08:30:00",10020798,"Short Rural","Planned",null,75,260,0,0,"NO"]
[null,"2017-07-12","08:30:00",10134499,"Short Rural","Planned",null,6,332,0,0,"NO"]
[null,"2017-07-12","08:30:00",20005944,"Short Rural","Planned",null,5,305,0,0,"NO"]
[null,"2017-07-12","08:30:00",20006023,"Short Rural","Planned",null,38,300,0,0,"NO"]
[null,"2017-07-12","08:30:00",20010961,"Short Rural","Planned",null,49,136,0,0,"NO"]
[null,"2017-07-12","08:30:00",40216323,"Long Rural","Planned",null,1,26,0,0,"NO"]
[null,"2017-07-12","08:30:00",83850831,"Short Rural","Planned",null,9,240,0,0,"NO"]
[null,"2017-07-12","08:34:00",40001010,"Long Rural","Planned",null,26,352,0,0,"NO"]
[null,"2017-07-12","08:35:00",60026670,"Long Rural","Planned",null,4,235,0,0,"NO"]
[null,"2017-07-12","08:36:00",10020657,"Short Rural","Asset failure","HV",725,127.24436781609201,0.22828761501754899,1.7940881701538E-3,"NO"]
[null,"2017-07-12","08:38:00",83864058,"Short Rural","Planned",null,21,324.09523809523802,0,0,"NO"]
[null,"2017-07-12","08:40:00",50000094,"Long Rural","Planned",null,4,26,0,0,"NO"]
[null,"2017-07-12","08:40:00",84119480,"Short Rural","Planned",null,109,230,0,0,"NO"]
[null,"2017-07-12","08:45:00",20001649,"Short Rural","Planned",null,6,167,0,0,"NO"]
[null,"2017-07-12","08:45:00",20002698,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","08:45:00",20008226,"Short Rural","Planned",null,20,222,0,0,"NO"]
[null,"2017-07-12","08:45:00",60026670,"Long Rural","Asset failure","LV",1,379.88333333333304,4.9683930595518398E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-12","08:47:00",20010779,"Short Rural","Asset failure","LV",1,225.20000000000002,5.57280904715359E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","08:50:00",50000037,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-12","08:50:00",60322052,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","08:52:00",20020964,"Short Rural","Planned",null,1,123,0,0,"NO"]
[null,"2017-07-12","08:53:00",85221946,"Short Rural","Third party","Fire",1,113.9,2.8185743804209304E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","08:55:00",60026667,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-12","08:56:00",30053776,"Short Rural","Other","Service Fuse",1,124.51666666666701,3.0812948779813801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","08:58:00",50000074,"Short Rural","Third party","Vehicle impact",1,270.85000000000002,6.7024659432573207E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","09:00:00",10020783,"Urban","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-12","09:00:00",30053863,"Short Rural","Planned",null,78,372.435897435897,0,0,"NO"]
[null,"2017-07-12","09:00:00",50000117,"Long Rural","Planned",null,28,238,0,0,"NO"]
[null,"2017-07-12","09:00:00",50000180,"Short Rural","Planned",null,7,100,0,0,"NO"]
[null,"2017-07-12","09:00:00",50000234,"Short Rural","Planned",null,12,426,0,0,"NO"]
[null,"2017-07-12","09:00:00",60026793,"Urban","Planned",null,13,15,0,0,"NO"]
[null,"2017-07-12","09:00:00",60026841,"Short Rural","Planned",null,1,178,0,0,"NO"]
[null,"2017-07-12","09:01:00",40000966,"Long Rural","Planned",null,3,138,0,0,"NO"]
[null,"2017-07-12","09:02:00",50000090,"Urban","Planned",null,1,51,0,0,"NO"]
[null,"2017-07-12","09:02:00",50000175,"Short Rural","Planned",null,71,63,0,0,"NO"]
[null,"2017-07-12","09:03:00",60026764,"Short Rural","Planned",null,1,42,0,0,"NO"]
[null,"2017-07-12","09:05:00",82563086,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","09:07:00",40200483,"Long Rural","Planned",null,6,173,0,0,"NO"]
[null,"2017-07-12","09:10:00",40001227,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-12","09:10:00",60026734,"Long Rural","Planned",null,2,71,0,0,"NO"]
[null,"2017-07-12","09:11:00",10020655,"Short Rural","Other","Forced Corrective Maintenance",3,22,1.6332388859331099E-4,7.4238131178777803E-6,"NO"]
[null,"2017-07-12","09:15:00",10020842,"Short Rural","Planned",null,1,230,0,0,"NO"]
[null,"2017-07-12","09:15:00",20002622,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-07-12","09:15:00",50000062,"Urban","Planned",null,1,314,0,0,"NO"]
[null,"2017-07-12","09:15:00",83022295,"Short Rural","Planned",null,1,75,0,0,"NO"]
[null,"2017-07-12","09:20:00",50000233,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2017-07-12","09:25:00",40001116,"Long Rural","Planned",null,1,58,0,0,"NO"]
[null,"2017-07-12","09:30:00",40001005,"Long Rural","Planned",null,2,138,0,0,"NO"]
[null,"2017-07-12","09:30:00",40001129,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-12","09:30:00",60026731,"Short Rural","Planned",null,1,56.999999999999993,0,0,"NO"]
[null,"2017-07-12","09:31:00",50000025,"Long Rural","Planned",null,2,278,0,0,"NO"]
[null,"2017-07-12","09:33:00",10020783,"Urban","Planned",null,1,3,0,0,"NO"]
[null,"2017-07-12","09:35:00",40001010,"Long Rural","Planned",null,1,36,0,0,"NO"]
[null,"2017-07-12","09:40:00",50000074,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","09:40:00",50000155,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","09:45:00",30053829,"Short Rural","Asset failure","LV",1,121.433333333333,3.00499457649208E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","09:49:00",60026731,"Short Rural","Other","Service Fuse",1,9.0333333333333297,2.23539261660542E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","09:50:00",84965685,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-12","09:53:00",50000233,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-12","10:00:00",40000985,"Long Rural","Planned",null,33,135,0,0,"NO"]
[null,"2017-07-12","10:00:00",40001116,"Long Rural","Planned",null,1,190,0,0,"NO"]
[null,"2017-07-12","10:00:00",60026696,"Long Rural","Planned",null,7,172,0,0,"NO"]
[null,"2017-07-12","10:00:00",60026697,"Short Rural","Planned",null,30,225,0,0,"NO"]
[null,"2017-07-12","10:10:00",60322052,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-12","10:15:00",30053781,"Long Rural","Planned",null,1,69,0,0,"NO"]
[null,"2017-07-12","10:15:00",50000232,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-07-12","10:19:00",60026891,"Long Rural","Other","Service Fuse",1,107.283333333333,1.40313017699887E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-12","10:20:00",50000208,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","10:20:00",85081013,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-12","10:21:00",50000096,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-12","10:30:00",10020833,"Short Rural","Other","Forced Corrective Maintenance",95,35,8.2280595389812115E-3,2.3508741539946302E-4,"NO"]
[null,"2017-07-12","10:30:00",30053752,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-12","10:30:00",40001200,"Short Rural","Planned",null,4,7,0,0,"NO"]
[null,"2017-07-12","10:30:00",50000094,"Long Rural","Planned",null,3,22,0,0,"NO"]
[null,"2017-07-12","10:30:00",50000233,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-12","10:39:00",60026667,"Long Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-12","10:43:00",20001962,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",308,20.866666666666699,1.5904117329242001E-2,7.6217814676878503E-4,"NO"]
[null,"2017-07-12","10:43:00",20006136,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",87,19.966666666666701,4.2986352556885011E-3,2.1529058041845601E-4,"NO"]
[null,"2017-07-12","10:48:00",40001207,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","10:55:00",50000095,"Long Rural","Asset failure","LV",1,93.699999999999989,1.2254773737902201E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-12","10:55:00",60026667,"Long Rural","Planned",null,1,28,0,0,"NO"]
[null,"2017-07-12","10:55:00",82912274,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","10:56:00",50000233,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-07-12","10:58:00",20006478,"Short Rural","Asset failure","Distribution substation",1,114.116666666667,2.8239360232282901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","11:00:00",40001129,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-07-12","11:00:00",50000090,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-12","11:00:00",50000093,"Long Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-12","11:00:00",50000208,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","11:05:00",30053752,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-12","11:10:00",50000208,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-12","11:11:00",83850831,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","11:14:00",60026734,"Long Rural","Planned",null,8,80,0,0,"NO"]
[null,"2017-07-12","11:15:00",20002652,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-12","11:15:00",50000170,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-07-12","11:28:00",20003281,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-12","11:28:00",40001207,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-12","11:30:00",50000175,"Short Rural","Planned",null,1,130.44999999999999,0,0,"NO"]
[null,"2017-07-12","11:30:00",50000208,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-12","11:34:00",25273020,"Urban","Other","Forced Corrective Maintenance",23,23,2.3387004076146998E-3,1.0168262641803101E-4,"NO"]
[null,"2017-07-12","11:34:00",30053824,"Urban","Planned",null,4,16,0,0,"NO"]
[null,"2017-07-12","11:36:00",10020783,"Urban","Planned",null,1,2,0,0,"NO"]
[null,"2017-07-12","11:40:00",20001148,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","11:40:00",50000208,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-12","11:40:00",82554035,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","11:45:00",40001010,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","11:45:00",60026774,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","11:48:00",50000093,"Long Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-12","11:49:00",30053773,"Short Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-07-12","11:50:00",40001207,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-12","11:50:00",50000096,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-12","11:55:00",40001063,"Long Rural","Planned",null,1,54,0,0,"NO"]
[null,"2017-07-12","12:00:00",60026731,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-12","12:00:00",82912329,"Short Rural","Planned",null,1,51,0,0,"NO"]
[null,"2017-07-12","12:10:00",50000170,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-12","12:10:00",60322053,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-12","12:15:00",50000208,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-12","12:16:00",10020783,"Urban","Planned",null,1,2,0,0,"NO"]
[null,"2017-07-12","12:20:00",20001148,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","12:20:00",40001207,"Short Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-07-12","12:25:00",60026774,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","12:29:00",25268407,"Short Rural","Other","Service Fuse",1,144.6,3.57827792281709E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","12:40:00",20001962,"Short Rural","Overloads",null,7,129.19999999999999,2.2380321946028903E-3,1.7322230608381499E-5,"NO"]
[null,"2017-07-12","13:00:00",40001129,"Short Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-12","13:12:00",50000233,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-12","13:14:00",83909007,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-12","13:15:00",20001263,"Short Rural","Asset failure","Distribution substation",1,21.4166666666667,5.2997776980405295E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","13:20:00",40001006,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-12","13:20:00",50000167,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-12","13:21:00",50000096,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-12","13:25:00",10020808,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-12","13:26:00",50000092,"Short Rural","Planned",null,1,56.999999999999993,0,0,"NO"]
[null,"2017-07-12","13:29:00",50000096,"Urban","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-12","13:30:00",50000208,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-12","13:30:00",60026677,"Short Rural","Planned",null,1,106.666666666667,0,0,"NO"]
[null,"2017-07-12","13:35:00",20005944,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-12","13:35:00",50000230,"Short Rural","Other","Forced Corrective Maintenance",1,25,6.18651093156482E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","13:37:00",40001063,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-12","13:38:00",30053744,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-07-12","13:44:00",82563099,"Urban","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-12","13:45:00",50000193,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-12","13:45:00",82554089,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","13:52:00",50000169,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-12","13:55:00",20005944,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","13:57:00",60026774,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-12","14:00:00",50000167,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","14:12:00",50000233,"Short Rural","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-12","14:13:00",20003435,"Long Rural","Asset failure","LV",2,59.5,1.5563693434475501E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-12","14:15:00",20002622,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-12","14:24:00",60026667,"Long Rural","Planned",null,1,38,0,0,"NO"]
[null,"2017-07-12","14:26:00",60026837,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-12","14:27:00",60026667,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","14:30:00",30053752,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-12","14:30:00",50000035,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-07-12","14:30:00",50000090,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-12","14:30:00",60026667,"Long Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-12","14:30:00",60026675,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","14:40:00",82773016,"Urban","Planned",null,3,15,0,0,"NO"]
[null,"2017-07-12","14:47:00",50000169,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-07-12","14:50:00",20001962,"Short Rural","Other","Fuse Operator - No Trigger Found",308,38.537229437229399,2.9372234114071E-2,7.6217814676878503E-4,"NO"]
[null,"2017-07-12","14:50:00",20006136,"Short Rural","Other","Fuse Operator - No Trigger Found",87,37.433333333333302,8.0590440603308493E-3,2.1529058041845601E-4,"NO"]
[null,"2017-07-12","14:55:00",30053752,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-12","15:00:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-12","15:00:00",50000195,"Urban","Planned",null,3,30,0,0,"NO"]
[null,"2017-07-12","15:05:00",60026994,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","15:13:00",60026837,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-12","15:13:00",85068151,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-07-12","15:14:00",82552955,"Short Rural","Asset failure","LV",1,76.433333333333294,1.8914226088104203E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","15:28:00",10020772,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",2,55.783333333333303,1.45915075420699E-3,2.61574679571018E-5,"NO"]
[null,"2017-07-12","15:29:00",50000180,"Short Rural","Other","Service Fuse",1,50.65,1.2533871147350301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","15:30:00",60322051,"Urban","Planned",null,3,60,0,0,"NO"]
[null,"2017-07-12","15:39:00",25267731,"Short Rural","Overloads",null,1,34.216666666666697,8.4672712950017089E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","16:05:00",50000236,"Long Rural","Animal","Animal impact",11,115.366666666667,1.6597349376580299E-2,1.4386607376406E-4,"NO"]
[null,"2017-07-12","16:12:00",50000108,"Short Rural","Other","Service Fuse",1,84.116666666666703,2.0815547114405101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","16:21:00",83850808,"Short Rural","Asset failure","LV",1,146.30000000000001,3.6203461971517301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","16:22:00",20010298,"Urban","Animal","Animal impact",327,50.75,7.3367330698427005E-2,1.4456616886389599E-3,"NO"]
[null,"2017-07-12","16:28:00",10020850,"Short Rural","Other","Service Fuse",2,59.9166666666667,2.96540090653007E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-12","16:37:00",84587749,"Urban","Other","Service Fuse",1,76.149999999999991,3.36657913118827E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-12","17:05:00",84023546,"Short Rural","Other","Service Fuse",1,158.26666666666699,3.91647385374263E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","17:11:00",30053747,"Short Rural","Overloads",null,1,77.850000000000009,1.9264795040892802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","17:15:00",82920982,"Short Rural","Exclusion - Customer Installation Fault",null,29,56,0,0,"NO"]
[null,"2017-07-12","17:33:00",20008226,"Short Rural","Asset failure","Distribution substation",2,98.45,4.8724960097004498E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-12","18:38:00",60026677,"Short Rural","Overloads",null,43,49.866666666666696,5.3062116694093508E-3,1.0640798802291501E-4,"NO"]
[null,"2017-07-12","18:58:00",20009806,"Short Rural","Other","Fuse Operator - No Trigger Found",1,70.383333333333297,1.7417090442665501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-12","19:21:00",20003349,"Urban","Asset failure","LV",1,128.38333333333301,5.6758063137542702E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-12","19:27:00",60026767,"Urban","Other","Service Fuse",2,45.3,4.0054112841189399E-4,8.8419675146113493E-6,"NO"]
[null,"2017-07-12","23:28:00",82563612,"Long Rural","Other","Fuse Operator - No Trigger Found",1,77.683333333333294,1.0159996512337601E-3,1.30787339785509E-5,"NO"]
[null,"2017-07-13","01:51:00",20009615,"Short Rural","Other","Fuse Operator - No Trigger Found",2,79.9166666666667,3.95524265558044E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-13","03:09:00",60026754,"Short Rural","Other","Service Fuse",1,338.83333333333303,8.3847844825808509E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-13","03:25:00",10020722,"Short Rural","Animal","Other",506,228.827173913043,0.28652590292127,1.2521498125487199E-3,"NO"]
[null,"2017-07-13","07:02:00",85068151,"Short Rural","Asset failure","LV",11,164.96666666666698,4.4904995813794301E-3,2.7220648098885201E-5,"NO"]
[null,"2017-07-13","07:30:00",40001247,"Urban","Planned",null,1,180,0,0,"NO"]
[null,"2017-07-13","07:33:00",84119480,"Short Rural","Asset failure","HV",31,148.90322580645199,1.1422773784041301E-2,7.6712735551403687E-5,"NO"]
[null,"2017-07-13","07:39:00",82563105,"Short Rural","Asset failure","LV",2,49,2.4251122851734101E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-13","07:41:00",20008154,"Short Rural","Planned",null,1,2,0,0,"NO"]
[null,"2017-07-13","07:49:00",30053771,"Short Rural","Other","Service Fuse",1,46.35,1.1469791267121201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-13","07:55:00",20007334,"Urban","Planned",null,2,5,0,0,"NO"]
[null,"2017-07-13","08:00:00",20003435,"Long Rural","Planned",null,2,209.01666666666699,0,0,"NO"]
[null,"2017-07-13","08:00:00",30053747,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-13","08:00:00",40001129,"Short Rural","Planned",null,6,60,0,0,"NO"]
[null,"2017-07-13","08:00:00",82912289,"Urban","Planned",null,34,240,0,0,"NO"]
[null,"2017-07-13","08:00:00",85161218,"Short Rural","Planned",null,16,370,0,0,"NO"]
[null,"2017-07-13","08:04:00",50000208,"Short Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-07-13","08:04:00",82563086,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-13","08:10:00",10020808,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-13","08:10:00",20002652,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-13","08:10:00",50000208,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-07-13","08:11:00",20011865,"Short Rural","Other","Fuse Operator - No Trigger Found",2,126.566666666667,6.26404853524043E-4,4.9492087452518498E-6,"NO"]
[null,"2017-07-13","08:12:00",50000167,"Short Rural","Planned",null,3,16,0,0,"NO"]
[null,"2017-07-13","08:29:00",50000167,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-07-13","08:30:00",10020774,"Short Rural","Planned",null,146,98,0,0,"NO"]
[null,"2017-07-13","08:30:00",10020841,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-07-13","08:30:00",20005978,"Urban","Planned",null,16,190,0,0,"NO"]
[null,"2017-07-13","08:30:00",50000067,"Short Rural","Planned",null,2,150,0,0,"NO"]
[null,"2017-07-13","08:30:00",50000169,"Short Rural","Planned",null,1,95,0,0,"NO"]
[null,"2017-07-13","08:30:00",60026845,"Urban","Planned",null,6,25,0,0,"NO"]
[null,"2017-07-13","08:30:00",83864041,"Short Rural","Planned",null,2,38,0,0,"NO"]
[null,"2017-07-13","08:30:00",84326665,"Short Rural","Planned",null,241,350.21991701244798,0,0,"NO"]
[null,"2017-07-13","08:30:00",84332614,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-13","08:31:00",20008154,"Short Rural","Planned",null,70,418,0,0,"NO"]
[null,"2017-07-13","08:35:00",20003088,"Short Rural","Planned",null,1,15.133333333333299,0,0,"NO"]
[null,"2017-07-13","08:36:00",50000025,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-13","08:36:00",60026782,"Short Rural","Other","Service Fuse",1,117.75,2.9138466487670296E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-13","08:42:00",60026743,"Short Rural","Other","Forced Corrective Maintenance",1,33,8.1661944296655602E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-13","08:43:00",20005628,"Short Rural","Planned",null,2,202,0,0,"NO"]
[null,"2017-07-13","08:44:00",50000233,"Short Rural","Planned",null,64,196,0,0,"NO"]
[null,"2017-07-13","08:45:00",20011656,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-13","08:45:00",60026667,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-13","08:47:00",30053814,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-13","08:50:00",82912323,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-13","08:52:00",10134605,"Urban","Planned",null,1,23,0,0,"NO"]
[null,"2017-07-13","08:54:00",40001200,"Short Rural","Other","Service Fuse",1,55.3333333333333,1.36928108618635E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-13","08:56:00",20007334,"Urban","Planned",null,2,14,0,0,"NO"]
[null,"2017-07-13","08:58:00",50000167,"Short Rural","Planned",null,3,27,0,0,"NO"]
[null,"2017-07-13","09:00:00",10129324,"Short Rural","Planned",null,164,372,0,0,"NO"]
[null,"2017-07-13","09:00:00",40000966,"Long Rural","Planned",null,3,92,0,0,"NO"]
[null,"2017-07-13","09:00:00",50000031,"Short Rural","Planned",null,115,284.8,0,0,"NO"]
[null,"2017-07-13","09:00:00",50000208,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-13","09:00:00",60026678,"Short Rural","Planned",null,2,165,0,0,"NO"]
[null,"2017-07-13","09:00:00",60026697,"Short Rural","Planned",null,4,60,0,0,"NO"]
[null,"2017-07-13","09:00:00",84332614,"Short Rural","Planned",null,26,304,0,0,"NO"]
[null,"2017-07-13","09:00:00",85221077,"Short Rural","Planned",null,15,284.41666666666703,0,0,"NO"]
[null,"2017-07-13","09:53:00",20012370,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-13","10:19:00",20012370,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-07-13","11:15:00",50000143,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-13","11:51:00",50000090,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-13","13:40:00",30053752,"Long Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-07-13","14:35:00",50000208,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-14","08:30:00",40000985,"Long Rural","Planned",null,1,80,0,0,"NO"]
[null,"2017-07-14","09:15:00",20002267,"Short Rural","Planned",null,1,15.133333333333299,0,0,"NO"]
[null,"2017-07-14","10:15:00",50000195,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-14","11:10:00",40000960,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-07-14","12:56:00",20004054,"Long Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-07-14","14:11:00",40000985,"Long Rural","Other","Fuse Operator - No Trigger Found",1,43.066666666666698,5.6325747667625799E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-14","18:07:00",84119480,"Short Rural","Asset failure","LV",1,133.98333333333301,3.3155574252566398E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-15","12:04:00",60026641,"Long Rural","Other","Forced Corrective Maintenance",93,15.4,1.8731362804080599E-2,1.21632226000523E-3,"NO"]
[null,"2017-07-16","10:48:00",25273354,"Urban","Other","Service Fuse",2,156.61666666666699,1.38479947891338E-3,8.8419675146113493E-6,"NO"]
[null,"2017-07-16","12:00:00",60026808,"Urban","Planned",null,1,120,0,0,"NO"]
[null,"2017-07-17","05:30:00",85161218,"Short Rural","Animal","Other",1,75.616666666666703,1.8712133397673001E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-17","09:02:00",50000090,"Urban","Planned",null,1,4.1333333333333293,0,0,"NO"]
[null,"2017-07-17","10:50:00",30053819,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-17","11:36:00",50000094,"Long Rural","Other","Forced Corrective Maintenance",1,16,2.0925974365681402E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-17","14:16:00",40200483,"Long Rural","Planned",null,1,104,0,0,"NO"]
[null,"2017-07-17","15:08:00",10020786,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-07-18","07:34:00",10020844,"Short Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",1,182.066666666667,4.5054296944275997E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-18","08:32:00",82649845,"Short Rural","Planned",null,2,87,0,0,"NO"]
[null,"2017-07-18","09:05:00",50000149,"Short Rural","Planned",null,1,44,0,0,"NO"]
[null,"2017-07-18","11:03:00",50000090,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-07-18","11:07:00",40001010,"Long Rural","Planned",null,2,55,0,0,"NO"]
[null,"2017-07-18","13:30:00",50000118,"Long Rural","Planned",null,4,79.900000000000006,0,0,"NO"]
[null,"2017-07-18","15:03:00",50000204,"Urban","Planned",null,1,6,0,0,"NO"]
[null,"2017-07-18","17:17:00",10020795,"Urban","Other","Service Fuse",1,26.8333333333333,1.18629730821036E-4,4.4209837573056797E-6,"NO"]
[null,"2017-07-19","08:17:00",82921017,"Urban","Planned",null,19,62,0,0,"NO"]
[null,"2017-07-19","09:00:00",82917286,"Short Rural","Planned",null,24,313.70833333333303,0,0,"NO"]
[null,"2017-07-19","09:30:00",20006023,"Short Rural","Planned",null,75,283,0,0,"NO"]
[null,"2017-07-19","11:10:00",30053820,"Urban","Planned",null,3,10,0,0,"NO"]
[null,"2017-07-19","11:35:00",30053820,"Urban","Planned",null,3,15,0,0,"NO"]
[null,"2017-07-19","13:45:00",30053820,"Urban","Planned",null,3,25,0,0,"NO"]
[null,"2017-07-19","16:20:00",30053819,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-19","19:06:00",60026889,"Long Rural","Overloads",null,1,47.199999999999996,6.1731624378760102E-4,1.30787339785509E-5,"NO"]
[null,"2017-07-20","08:10:00",30053819,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-20","09:00:00",40001062,"Long Rural","Planned",null,20,240,0,0,"NO"]
[null,"2017-07-20","09:10:00",30053745,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-20","10:50:00",40000977,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-20","12:55:00",82888836,"Urban","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-20","13:00:00",50000140,"Short Rural","Planned",null,3,60,0,0,"NO"]
[null,"2017-07-20","15:29:00",10020855,"Short Rural","Other","Forced Corrective Maintenance",625,42,6.4958364781430605E-2,1.5466277328912003E-3,"NO"]
[null,"2017-07-21","07:43:00",50000186,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-21","09:15:00",30053745,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-21","10:50:00",50000166,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-07-21","11:30:00",20003411,"Urban","Asset failure","Zone substation",382,6.4666666666666694,1.0921008809547E-2,1.6888157952907698E-3,"NO"]
[null,"2017-07-21","13:34:00",60026734,"Long Rural","Planned",null,1,56,0,0,"NO"]
[null,"2017-07-21","19:27:00",60026735,"Short Rural","Animal","Animal impact",1,70.616666666666703,1.7474831211360101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-22","10:40:00",50000169,"Short Rural","Other","Service Fuse",1,132.833333333333,3.28709947497144E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-22","18:25:00",20007634,"Long Rural","Other","Vibration",1,916.51666666666711,1.1986877670241499E-2,1.30787339785509E-5,"NO"]
[null,"2017-07-23","19:12:00",50000174,"Short Rural","Other","Service Fuse",1,91.199999999999989,2.2568391878348399E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-24","07:21:00",30053777,"Short Rural","Other","Fuse Operator - No Trigger Found",1,124,3.0685094220561497E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-24","10:22:00",50000021,"Short Rural","Overloads",null,1,262.75,6.5020229890746205E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-24","12:10:00",60026837,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-24","13:05:00",50000075,"Short Rural","Planned",null,2,29,0,0,"NO"]
[null,"2017-07-24","23:14:00",83868949,"Short Rural","Other","Fuse Operator - No Trigger Found",73,104.45,1.88684871506168E-2,1.80646119201693E-4,"NO"]
[null,"2017-07-25","08:30:00",60026755,"Long Rural","Planned",null,21,197.01666666666699,0,0,"NO"]
[null,"2017-07-25","09:00:00",50000117,"Long Rural","Planned",null,2,136.71666666666698,0,0,"NO"]
[null,"2017-07-25","10:00:00",50000159,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-07-25","10:20:00",50000154,"Short Rural","Asset failure","Zone substation",1443,23.45,8.3736528872446495E-2,3.5708541096992103E-3,"NO"]
[null,"2017-07-25","11:13:00",84326665,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-07-25","12:45:00",30053745,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-25","14:00:00",40001121,"Short Rural","Planned",null,2,45,0,0,"NO"]
[null,"2017-07-25","15:27:00",60026775,"Short Rural","Other","Fuse Operator - No Trigger Found",1,94,2.3261281102683701E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-25","23:47:00",10020836,"Short Rural","Other","Fuse Operator - No Trigger Found",1,80.383333333333297,1.98916948152914E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-26","08:30:00",40001193,"Short Rural","Planned",null,62,430,0,0,"NO"]
[null,"2017-07-26","08:52:00",10020655,"Short Rural","Planned",null,1,68,0,0,"NO"]
[null,"2017-07-26","09:28:00",60026672,"Short Rural","Planned",null,2,29,0,0,"NO"]
[null,"2017-07-26","10:05:00",60026775,"Short Rural","Other","Forced Corrective Maintenance",1,15,3.7119065589388895E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-26","11:00:00",60026703,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-07-26","12:30:00",50000015,"Short Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-26","14:40:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-07-27","07:42:00",82604748,"Short Rural","Planned",null,2,44,0,0,"NO"]
[null,"2017-07-27","08:30:00",50000143,"Short Rural","Planned",null,1,70,0,0,"NO"]
[null,"2017-07-27","09:05:00",60026844,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-27","10:55:00",50000213,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-07-27","11:07:00",60026699,"Short Rural","Other","Forced Corrective Maintenance",31,157,1.20438994815704E-2,7.6712735551403687E-5,"NO"]
[null,"2017-07-27","12:35:00",20001108,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-27","14:45:00",20002752,"Short Rural","Other","Forced Corrective Maintenance",1,10,2.4746043726259301E-5,2.4746043726259304E-6,"NO"]
[null,"2017-07-28","08:00:00",20003435,"Long Rural","Planned",null,1,162,0,0,"NO"]
[null,"2017-07-28","08:30:00",40001042,"Long Rural","Planned",null,1,82,0,0,"NO"]
[null,"2017-07-28","09:20:00",20004700,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-28","10:30:00",50000209,"Urban","Planned",null,2,25,0,0,"NO"]
[null,"2017-07-28","11:36:00",50000213,"Urban","Planned",null,1,22,0,0,"NO"]
[null,"2017-07-28","12:35:00",10020779,"Short Rural","Other","Forced Corrective Maintenance",3,34,2.5240964600784405E-4,7.4238131178777803E-6,"NO"]
[null,"2017-07-28","14:22:00",82564200,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-07-29","07:41:00",20008745,"Long Rural","Asset failure","Zone substation",36,58.316666666666698,2.74574941145697E-2,4.7083442322783201E-4,"NO"]
[null,"2017-07-29","09:29:00",50000090,"Urban","Planned",null,1,16,0,0,"NO"]
[null,"2017-07-29","18:58:00",20010596,"Short Rural","Overloads",null,1,108.866666666667,2.6940192936654298E-4,2.4746043726259304E-6,"NO"]
[null,"2017-07-30","16:57:00",30053765,"Long Rural","Other","Vibration",1,1217.5166666666703,1.5923576597785302E-2,1.30787339785509E-5,"NO"]
[null,"2017-07-31","08:50:00",10020808,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-07-31","09:00:00",30053785,"Short Rural","Planned",null,3,60,0,0,"NO"]
[null,"2017-07-31","11:05:00",20002652,"Short Rural","5 - STPIS Exclusion (3.3)(a)",null,915,11.8,0,0,"NO"]
[null,"2017-07-31","12:30:00",60026844,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-07-31","14:00:00",20007427,"Urban","Planned",null,3,90,0,0,"NO"]
[null,"2017-07-31","17:23:00",60026821,"Long Rural","Other","Service Fuse",1,53.550000000000004,7.0036620455139905E-4,1.30787339785509E-5,"NO"]
[null,"2017-08-01","08:30:00",10020673,"Long Rural","Planned",null,12,60,0,0,"NO"]
[null,"2017-08-01","08:40:00",40000979,"Long Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-08-01","09:10:00",82563099,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-01","10:02:00",82920982,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-01","11:00:00",20001148,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-08-01","12:20:00",84737242,"Short Rural","Other","Forced Corrective Maintenance",148,132.13513513513499,4.8393363111072604E-2,3.6624144714863702E-4,"NO"]
[null,"2017-08-01","13:15:00",83879448,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-01","14:48:00",85221946,"Short Rural","Asset failure","LV",1,1163.3,2.87870726667574E-3,2.4746043726259304E-6,"NO"]
[null,"2017-08-01","19:42:00",40200483,"Long Rural","Other","Service Fuse",1,157.03333333333299,2.0537971924317697E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-02","08:24:00",40000975,"Long Rural","Animal","Animal impact",1,87.4166666666667,1.1432993286249902E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-02","09:00:00",20011656,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-02","09:20:00",83897502,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-02","10:15:00",30053824,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-08-02","11:08:00",84326665,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-08-02","13:19:00",85068151,"Short Rural","Other","Service Fuse",1,144.45000000000002,3.57456601625815E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-02","14:56:00",82921882,"Urban","Planned",null,6,9,0,0,"NO"]
[null,"2017-08-02","16:01:00",85221077,"Short Rural","Asset failure","LV",1,73.1666666666667,1.81058553263797E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-03","08:22:00",20003792,"Short Rural","Planned",null,3,345,0,0,"NO"]
[null,"2017-08-03","09:00:00",10020722,"Short Rural","Planned",null,18,321,0,0,"NO"]
[null,"2017-08-03","09:15:00",50000113,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-03","10:35:00",20012370,"Short Rural","Planned",null,3,25,0,0,"NO"]
[null,"2017-08-03","11:05:00",60026839,"Short Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-08-03","13:31:00",40001091,"Urban","Planned",null,78,51,0,0,"NO"]
[null,"2017-08-03","13:45:00",40001105,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-03","17:37:00",50000160,"Long Rural","Asset failure","HV",4,72.766666666666708,3.8067835033568803E-3,5.2314935914203499E-5,"NO"]
[null,"2017-08-04","09:00:00",84668557,"Long Rural","Planned",null,134,244.15671641790999,0,0,"NO"]
[null,"2017-08-04","10:15:00",40001129,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-08-04","11:01:00",10020828,"Long Rural","Planned",null,5,65,0,0,"NO"]
[null,"2017-08-04","14:09:00",10020831,"Short Rural","Other","Fuse Operator - No Trigger Found",32,54.1666666666667,4.2893142458849398E-3,7.9187339924029597E-5,"NO"]
[null,"2017-08-05","01:23:00",60026792,"Short Rural","Asset failure","HV",49,304.41258503401406,3.6911734986369099E-2,1.2125561425867E-4,"NO"]
[null,"2017-08-05","11:00:00",20010480,"Short Rural","Other","Forced Corrective Maintenance",3,32,2.37562019772089E-4,7.4238131178777803E-6,"NO"]
[null,"2017-08-06","06:00:00",40001215,"Urban","Planned",null,4,249,0,0,"NO"]
[null,"2017-08-06","15:29:00",50000127,"Long Rural","Weather",null,248,236.271169354839,0.766351687156683,3.24352602668062E-3,"NO"]
[null,"2017-08-07","06:14:00",40000978,"Long Rural","Other","Fuse Operator - No Trigger Found",1,256.63333333333304,3.35643909669544E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-07","06:58:00",50000241,"Long Rural","Asset failure","Distribution substation",1,241.333333333333,3.1563344668236099E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-07","09:55:00",83868952,"Short Rural","Planned",null,8,20,0,0,"NO"]
[null,"2017-08-07","12:27:00",20011515,"Short Rural","Animal","Animal impact",1,212.23333333333301,5.2519353468364206E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-07","13:10:00",50000233,"Short Rural","Planned",null,1,102,0,0,"NO"]
[null,"2017-08-07","15:40:00",40000975,"Long Rural","Animal","Animal impact",1,36.716666666666697,4.8020751591246002E-4,1.30787339785509E-5,"NO"]
[null,"2017-08-08","07:37:00",60026647,"Short Rural","Other","Service Fuse",2,207.86666666666699,1.0287755245130198E-3,4.9492087452518498E-6,"NO"]
[null,"2017-08-08","08:30:00",83850831,"Short Rural","Planned",null,52,283,0,0,"NO"]
[null,"2017-08-08","09:15:00",82980894,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-08-08","10:00:00",10020673,"Long Rural","Planned",null,3,111,0,0,"NO"]
[null,"2017-08-08","12:00:00",60026839,"Short Rural","Planned",null,1,125,0,0,"NO"]
[null,"2017-08-08","13:50:00",10020842,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-08-08","13:59:00",84579665,"Short Rural","Other","Service Fuse",1,85.883333333333297,2.1252727220235702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-08","20:43:00",60026712,"Long Rural","Asset failure","LV",1,214.98333333333301,2.8117098264888005E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-09","08:30:00",10020804,"Short Rural","Planned",null,14,148,0,0,"NO"]
[null,"2017-08-09","08:52:00",10020842,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2017-08-09","09:45:00",20007373,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-09","11:01:00",83868946,"Short Rural","Planned",null,4,157,0,0,"NO"]
[null,"2017-08-09","12:00:00",10020832,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-08-09","14:00:00",20011217,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-09","17:21:00",60026688,"Short Rural","Other","Service Fuse",1,38.15,9.4406156815679112E-5,2.4746043726259304E-6,"NO"]
[null,"2017-08-10","08:15:00",20002652,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-08-10","09:00:00",82561856,"Long Rural","Planned",null,10,255,0,0,"NO"]
[null,"2017-08-10","09:20:00",82920985,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-08-10","10:14:00",82843815,"Urban","Planned",null,131,19,0,0,"NO"]
[null,"2017-08-10","10:40:00",82921017,"Urban","Planned",null,2,2,0,0,"NO"]
[null,"2017-08-10","11:53:00",10020806,"Long Rural","Other","Fuse Operator - No Trigger Found",19,208.28333333333299,5.1757563867817595E-2,2.4849594559246701E-4,"NO"]
[null,"2017-08-10","13:00:00",30053765,"Long Rural","Planned",null,5,32.200000000000003,0,0,"NO"]
[null,"2017-08-10","14:39:00",50000093,"Long Rural","Planned",null,1,4,0,0,"NO"]
[null,"2017-08-10","15:15:00",20006666,"Short Rural","Planned",null,2,25,0,0,"NO"]
[null,"2017-08-10","18:39:00",60026786,"Short Rural","Other","Fuse Operator - No Trigger Found",5,126.383333333333,1.56374374646853E-3,1.2373021863129598E-5,"NO"]
[null,"2017-08-11","08:31:00",84928162,"Short Rural","Planned",null,5,374,0,0,"NO"]
[null,"2017-08-11","09:30:00",20007634,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-11","11:03:00",20005887,"Short Rural","Planned",null,5,7,0,0,"NO"]
[null,"2017-08-11","12:01:00",20001196,"Urban","Planned",null,1,14,0,0,"NO"]
[null,"2017-08-11","13:30:00",40001061,"Long Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-11","15:00:00",82915271,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-12","08:03:00",10020838,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-08-12","12:45:00",40216323,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-14","07:15:00",60026812,"Short Rural","Asset failure","HV",1,185.066666666667,4.5796678256063801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-14","09:03:00",60026724,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-08-14","09:50:00",30053746,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-08-14","11:30:00",60026788,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-08-14","13:46:00",84326662,"Urban","Third party","Vehicle impact",1,103.083333333333,4.5572974231559299E-4,4.4209837573056797E-6,"NO"]
[null,"2017-08-14","15:45:00",85068151,"Short Rural","Planned",null,1,13,0,0,"NO"]
[null,"2017-08-15","08:00:00",85081026,"Short Rural","Planned",null,15,224.933333333333,0,0,"NO"]
[null,"2017-08-15","08:31:00",82912289,"Urban","Planned",null,117,118,0,0,"NO"]
[null,"2017-08-15","09:00:00",50000211,"Short Rural","Planned",null,16,54,0,0,"NO"]
[null,"2017-08-15","10:00:00",60026650,"Long Rural","Planned",null,19,233,0,0,"NO"]
[null,"2017-08-15","11:34:00",84668557,"Long Rural","Animal","Animal impact",1,33.366666666666696,4.36393757084314E-4,1.30787339785509E-5,"NO"]
[null,"2017-08-15","13:54:00",20006799,"Short Rural","Third party","Vehicle impact",165,89.065151515151499,3.6366167209017496E-2,4.08309721483278E-4,"NO"]
[null,"2017-08-15","15:40:00",60026791,"Urban","Planned",null,1,35,0,0,"NO"]
[null,"2017-08-16","07:40:00",25273540,"Urban","Planned",null,1,17,0,0,"NO"]
[null,"2017-08-16","08:30:00",40001061,"Long Rural","Planned",null,3,552.66666666666708,0,0,"NO"]
[null,"2017-08-16","08:50:00",20007334,"Urban","Other","Forced Corrective Maintenance",2,20,1.7683935029222701E-4,8.8419675146113493E-6,"NO"]
[null,"2017-08-16","09:35:00",40001060,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-16","11:00:00",10134499,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-08-16","11:45:00",20007334,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-16","13:00:00",40000966,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-08-16","14:40:00",30053812,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-08-16","23:00:00",82564423,"Urban","Other","Forced Corrective Maintenance",5,116,2.5641705792372902E-3,2.21049187865284E-5,"NO"]
[null,"2017-08-17","08:30:00",25273350,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-17","08:50:00",40000973,"Long Rural","Other","Fuse Operator - No Trigger Found",1,420.66666666666703,5.5017874269770702E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-17","09:20:00",60026844,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-08-17","10:30:00",20003281,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-17","11:22:00",10134499,"Short Rural","Planned",null,1,2,0,0,"NO"]
[null,"2017-08-17","13:35:00",40001130,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-08-17","15:24:00",10134499,"Short Rural","Planned",null,1,3,0,0,"NO"]
[null,"2017-08-18","08:00:00",30053775,"Short Rural","Planned",null,4,105,0,0,"NO"]
[null,"2017-08-18","08:00:00",82563108,"Urban","Planned",null,4,177,0,0,"NO"]
[null,"2017-08-18","09:00:00",40000985,"Long Rural","Planned",null,120,305,0,0,"NO"]
[null,"2017-08-18","10:13:00",50000075,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-18","11:33:00",60026793,"Urban","Other","Service Fuse",1,161.35,7.13325729241271E-4,4.4209837573056797E-6,"NO"]
[null,"2017-08-18","12:31:00",60026792,"Short Rural","Asset failure","HV",2,256.66666666666703,1.2702969112813099E-3,4.9492087452518498E-6,"NO"]
[null,"2017-08-18","14:10:00",50000211,"Short Rural","Other","Forced Corrective Maintenance",2,20,9.8984174905037095E-5,4.9492087452518498E-6,"NO"]
[null,"2017-08-18","16:25:00",10020780,"Short Rural","Other","Fuse Operator - No Trigger Found",18,104.716666666667,4.6643817819626097E-3,4.4542878707266693E-5,"NO"]
[null,"2017-08-19","08:36:00",40001001,"Urban","Planned",null,50,208,0,0,"NO"]
[null,"2017-08-19","16:12:00",82563086,"Short Rural","Animal","Animal impact",1,2700.85,6.6835352198067301E-3,2.4746043726259304E-6,"NO"]
[null,"2017-08-20","10:53:00",50000053,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",547,15.4,0.110172639288517,7.1540674862673303E-3,"NO"]
[null,"2017-08-21","03:36:00",50000240,"Long Rural","Overloads",null,1,190.23333333333301,2.4880111605196601E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-21","08:00:00",50000095,"Long Rural","Planned",null,1,22,0,0,"NO"]
[null,"2017-08-21","10:02:00",10020788,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-21","10:50:00",30053769,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-21","12:05:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-08-21","13:28:00",60026777,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-08-21","15:00:00",20007427,"Urban","Planned",null,3,10,0,0,"NO"]
[null,"2017-08-21","20:11:00",10020840,"Short Rural","Other","Service Fuse",1,90.683333333333294,2.2440537319096099E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-22","09:00:00",10020836,"Short Rural","Planned",null,9,159.12037037037001,0,0,"NO"]
[null,"2017-08-22","09:33:00",40001004,"Urban","Planned",null,1,88,0,0,"NO"]
[null,"2017-08-22","10:41:00",60026701,"Long Rural","Planned",null,2,298,0,0,"NO"]
[null,"2017-08-22","11:50:00",10020817,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-22","12:00:00",20008892,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-22","13:40:00",50000090,"Urban","Planned",null,1,45,0,0,"NO"]
[null,"2017-08-22","15:08:00",82920985,"Urban","Planned",null,1,7,0,0,"NO"]
[null,"2017-08-22","18:21:00",40001227,"Short Rural","Other","Service Fuse",1,53.199999999999996,1.31648952623699E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-23","08:30:00",83897505,"Short Rural","Planned",null,43,181,0,0,"NO"]
[null,"2017-08-23","09:11:00",50000240,"Long Rural","Asset failure","Distribution substation",1,286.2,3.7431336646612601E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-23","09:15:00",20008110,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-08-23","10:20:00",60026845,"Urban","Planned",null,1,40,0,0,"NO"]
[null,"2017-08-23","11:50:00",83879451,"Urban","Planned",null,2,8,0,0,"NO"]
[null,"2017-08-23","13:00:00",83850831,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-08-23","14:12:00",30053833,"Short Rural","Planned",null,1,51,0,0,"NO"]
[null,"2017-08-23","15:30:00",83921739,"Short Rural","Other","Forced Corrective Maintenance",10,55,1.3610324049442601E-3,2.4746043726259301E-5,"NO"]
[null,"2017-08-24","01:14:00",20010359,"Urban","Network business","Switching and protection error",291,2.35,3.0232897424334899E-3,1.2865062733759499E-3,"NO"]
[null,"2017-08-24","08:06:00",25273354,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-24","09:00:00",40000961,"Long Rural","Planned",null,49,304,0,0,"NO"]
[null,"2017-08-24","09:57:00",20011656,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-24","11:30:00",10134499,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-24","12:15:00",40000977,"Long Rural","Planned",null,1,25,0,0,"NO"]
[null,"2017-08-24","14:20:00",40000982,"Short Rural","Planned",null,12,30,0,0,"NO"]
[null,"2017-08-24","17:53:00",10020850,"Short Rural","Other","Fuse Operator - No Trigger Found",1,106.9,2.6453520743371196E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-25","08:30:00",85068151,"Short Rural","Planned",null,4,61,0,0,"NO"]
[null,"2017-08-25","09:00:00",40001237,"Urban","Planned",null,7,293,0,0,"NO"]
[null,"2017-08-25","09:54:00",10020764,"Short Rural","Network business","Switching and protection error",2079,8,4.1157619925514408E-2,5.1447024906893001E-3,"NO"]
[null,"2017-08-25","11:00:00",82554089,"Urban","Planned",null,2,150,0,0,"NO"]
[null,"2017-08-25","12:00:00",10020675,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-08-25","13:20:00",10020842,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-08-26","08:12:00",50082888,"Short Rural","Planned",null,1,158,0,0,"NO"]
[null,"2017-08-26","15:06:00",40001118,"Long Rural","Animal","Animal impact",1,133.38333333333301,1.7444851338390402E-3,1.30787339785509E-5,"NO"]
[null,"2017-08-27","09:01:00",60026724,"Short Rural","Planned",null,56,262,0,0,"NO"]
[null,"2017-08-27","19:09:00",50000138,"Short Rural","Other","Service Fuse",1,76.4166666666667,1.8910101747483099E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-28","08:33:00",60026888,"Long Rural","Planned",null,1,65,0,0,"NO"]
[null,"2017-08-28","09:09:00",25275672,"Urban","Planned",null,2,14,0,0,"NO"]
[null,"2017-08-28","10:32:00",25275672,"Urban","Planned",null,1,8,0,0,"NO"]
[null,"2017-08-28","11:40:00",50000074,"Short Rural","Other","Service Fuse",1,49.866666666666696,1.23400271381613E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-28","12:58:00",40001091,"Urban","Other","Service Fuse",1,145.30000000000001,6.4236893993651495E-4,4.4209837573056797E-6,"NO"]
[null,"2017-08-28","15:48:00",40001010,"Long Rural","Planned",null,1,44,0,0,"NO"]
[null,"2017-08-29","06:17:00",40001231,"Short Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-08-29","08:59:00",20007736,"Long Rural","Planned",null,59,280.38983050847509,0,0,"NO"]
[null,"2017-08-29","09:40:00",60330968,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-08-29","10:20:00",40001140,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-29","11:21:00",40001068,"Long Rural","Planned",null,1,78,0,0,"NO"]
[null,"2017-08-29","12:45:00",50000192,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-29","13:30:00",10130452,"Urban","Planned",null,32,80,0,0,"NO"]
[null,"2017-08-29","15:00:00",20005482,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-30","07:30:00",83897505,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-30","08:20:00",83897505,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-08-30","09:00:00",60026729,"Short Rural","Planned",null,6,271,0,0,"NO"]
[null,"2017-08-30","10:05:00",50000030,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-08-30","11:30:00",10020799,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-08-30","12:30:00",40001116,"Long Rural","Planned",null,1,60.999999999999993,0,0,"NO"]
[null,"2017-08-30","13:45:00",10020824,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2017-08-30","19:06:00",20012178,"Short Rural","Other","Service Fuse",1,225.36666666666699,5.5769333877746306E-4,2.4746043726259304E-6,"NO"]
[null,"2017-08-31","08:00:00",20005336,"Urban","Planned",null,1,120,0,0,"NO"]
[null,"2017-08-31","09:05:00",50000194,"Urban","Planned",null,3,15,0,0,"NO"]
[null,"2017-08-31","09:25:00",60026842,"Urban","Planned",null,1,22,0,0,"NO"]
[null,"2017-08-31","11:00:00",20005577,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-31","12:30:00",82552955,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-08-31","12:50:00",60026767,"Urban","Planned",null,2,25,0,0,"NO"]
[null,"2017-08-31","17:45:00",25273540,"Urban","Exclusion - Customer Installation Fault",null,4,19,0,0,"NO"]
[null,"2017-09-01","08:15:00",20011656,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-09-01","08:45:00",60026756,"Short Rural","Planned",null,1,75,0,0,"NO"]
[null,"2017-09-01","10:00:00",40001138,"Short Rural","Planned",null,6,15,0,0,"NO"]
[null,"2017-09-01","12:03:00",40001068,"Long Rural","Planned",null,1,33.999999999999993,0,0,"NO"]
[null,"2017-09-01","13:18:00",40001068,"Long Rural","Planned",null,1,27,0,0,"NO"]
[null,"2017-09-01","18:04:00",83877341,"Urban","Overloads",null,95,55.649999999999991,2.3372635878935802E-2,4.1999345694403899E-4,"NO"]
[null,"2017-09-02","15:39:00",30053744,"Short Rural","Asset failure","LV",1,112.01666666666701,2.77196933140314E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-02","18:52:00",82563612,"Long Rural","Other","Service Fuse",1,141.166666666667,1.8462812799720999E-3,1.30787339785509E-5,"NO"]
[null,"2017-09-04","08:12:00",30053847,"Short Rural","Planned",null,1,33,0,0,"NO"]
[null,"2017-09-04","08:55:00",60026823,"Urban","Planned",null,2,25,0,0,"NO"]
[null,"2017-09-04","10:15:00",50000109,"Short Rural","Planned",null,1,35,0,0,"NO"]
[null,"2017-09-04","11:00:00",82556060,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-09-04","12:40:00",82917286,"Short Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",1,55.533333333333303,1.3742302949316002E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-04","14:29:00",20006212,"Short Rural","Animal","Animal impact",54,148.92962962963,1.9901263285532201E-2,1.3362863612180001E-4,"NO"]
[null,"2017-09-04","16:29:00",20011656,"Urban","Other","Service Fuse",1,91.133333333333297,4.0289898641579101E-4,4.4209837573056797E-6,"NO"]
[null,"2017-09-05","08:39:00",40001226,"Short Rural","Planned",null,26,173,0,0,"NO"]
[null,"2017-09-05","09:00:00",50000205,"Urban","Planned",null,5,65,0,0,"NO"]
[null,"2017-09-05","10:35:00",50000025,"Long Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-09-05","12:00:00",10134605,"Urban","Planned",null,1,35,0,0,"NO"]
[null,"2017-09-05","12:30:00",20001488,"Short Rural","Other","Service Fuse",3,111.75,8.2961111592284192E-4,7.4238131178777803E-6,"NO"]
[null,"2017-09-05","16:35:00",40000963,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-09-06","08:00:00",84023546,"Short Rural","Planned",null,7,180,0,0,"NO"]
[null,"2017-09-06","08:30:00",84659987,"Urban","Planned",null,3,360,0,0,"NO"]
[null,"2017-09-06","09:30:00",83896573,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-09-06","10:20:00",50000194,"Urban","Planned",null,4,25,0,0,"NO"]
[null,"2017-09-06","12:20:00",10020799,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-09-06","12:20:00",50000127,"Long Rural","Planned",null,1,40,0,0,"NO"]
[null,"2017-09-06","16:25:00",60026837,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2017-09-07","07:12:00",10020805,"Urban","Asset failure","HV",431,62.220765661252898,0.11855818456723,1.9054439993987499E-3,"NO"]
[null,"2017-09-07","08:30:00",83022301,"Short Rural","Planned",null,166,292,0,0,"NO"]
[null,"2017-09-07","09:00:00",82915256,"Urban","Planned",null,1,33.999999999999993,0,0,"NO"]
[null,"2017-09-07","10:00:00",60026994,"Long Rural","Planned",null,7,186,0,0,"NO"]
[null,"2017-09-07","11:06:00",40001009,"Long Rural","Other","Forced Corrective Maintenance",1,38.999999999999993,5.1007062516348408E-4,1.30787339785509E-5,"NO"]
[null,"2017-09-07","13:00:00",40001029,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-09-07","15:15:00",50000213,"Urban","Planned",null,4,15,0,0,"NO"]
[null,"2017-09-08","08:30:00",60026837,"Short Rural","Planned",null,2,27,0,0,"NO"]
[null,"2017-09-08","09:11:00",50000151,"Short Rural","Planned",null,19,269,0,0,"NO"]
[null,"2017-09-08","09:32:00",20001178,"Urban","Animal","Animal impact",31,78.3333333333333,1.0735622223990599E-2,1.37050496476476E-4,"NO"]
[null,"2017-09-08","12:05:00",40001208,"Long Rural","Other","Forced Corrective Maintenance",1,10,1.3078733978550902E-4,1.30787339785509E-5,"NO"]
[null,"2017-09-08","14:33:00",60026667,"Long Rural","Planned",null,22,14,0,0,"NO"]
[null,"2017-09-09","10:01:00",60026768,"Urban","Other","Service Fuse",1,60.300000000000004,2.6658532056553203E-4,4.4209837573056797E-6,"NO"]
[null,"2017-09-09","18:56:00",30053835,"Urban","Other","Service Fuse",1,91.966666666666697,4.0658313954687896E-4,4.4209837573056797E-6,"NO"]
[null,"2017-09-10","09:39:00",85221077,"Short Rural","Planned",null,73,322,0,0,"NO"]
[null,"2017-09-10","18:30:00",30053752,"Long Rural","Other","Fuse Operator - No Trigger Found",1,122.75,1.6054145958671201E-3,1.30787339785509E-5,"NO"]
[null,"2017-09-11","09:00:00",10020780,"Short Rural","Planned",null,34,169,0,0,"NO"]
[null,"2017-09-11","09:40:00",85206371,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-09-11","12:30:00",30053817,"Urban","Planned",null,3,120.01666666666701,0,0,"NO"]
[null,"2017-09-11","14:35:00",50000035,"Short Rural","Planned",null,3,35,0,0,"NO"]
[null,"2017-09-11","19:26:00",50000113,"Short Rural","Other","Service Fuse",1,145.03333333333299,3.5890012084318002E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-12","08:15:00",60026764,"Short Rural","Other","Fuse Operator - No Trigger Found",1,88.0833333333333,2.1797140182213401E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-12","09:00:00",60026667,"Long Rural","Planned",null,29,325.55172413793105,0,0,"NO"]
[null,"2017-09-12","09:30:00",30053863,"Short Rural","Planned",null,20,143.55000000000001,0,0,"NO"]
[null,"2017-09-12","10:50:00",50000209,"Urban","Planned",null,2,40,0,0,"NO"]
[null,"2017-09-12","13:01:00",50000160,"Long Rural","Planned",null,2,49.999999999999993,0,0,"NO"]
[null,"2017-09-12","14:14:00",82921882,"Urban","Planned",null,1,23,0,0,"NO"]
[null,"2017-09-12","18:53:00",60026649,"Urban","Other","Service Fuse",1,61.066666666666698,2.6997474144613298E-4,4.4209837573056797E-6,"NO"]
[null,"2017-09-13","09:00:00",10020689,"Short Rural","Planned",null,4,327,0,0,"NO"]
[null,"2017-09-13","10:00:00",60026650,"Long Rural","Planned",null,2,204,0,0,"NO"]
[null,"2017-09-13","11:18:00",82552955,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-09-13","12:18:00",25273350,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-09-13","14:30:00",60026771,"Long Rural","Asset failure","LV",1,212.833333333333,2.7835905484349102E-3,1.30787339785509E-5,"NO"]
[null,"2017-09-13","15:24:00",10132687,"Short Rural","Animal","Animal impact",1,122.76666666666701,3.0379893014604301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-14","06:40:00",20006009,"Urban","Planned",null,1,31,0,0,"NO"]
[null,"2017-09-14","08:35:00",10020775,"Short Rural","Planned",null,8,74,0,0,"NO"]
[null,"2017-09-14","10:00:00",60026650,"Long Rural","Planned",null,28,199,0,0,"NO"]
[null,"2017-09-14","10:20:00",50000206,"Urban","Planned",null,5,35,0,0,"NO"]
[null,"2017-09-14","11:30:00",82915259,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-09-14","14:00:00",82915259,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-09-14","18:15:00",82987762,"Short Rural","Other","Service Fuse",1,148.81666666666698,3.6826237405294802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-15","08:15:00",50000127,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-09-15","09:00:00",40001072,"Long Rural","Planned",null,16,210,0,0,"NO"]
[null,"2017-09-15","10:15:00",50000127,"Long Rural","Planned",null,3,15,0,0,"NO"]
[null,"2017-09-15","11:05:00",50000170,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-09-15","13:00:00",40001139,"Long Rural","Planned",null,1,73,0,0,"NO"]
[null,"2017-09-15","19:27:00",20005787,"Short Rural","Other","Service Fuse",1,843.95,2.08844236027765E-3,2.4746043726259304E-6,"NO"]
[null,"2017-09-16","14:32:00",20003435,"Long Rural","Other","Service Fuse",1,64.8,8.4750196181009702E-4,1.30787339785509E-5,"NO"]
[null,"2017-09-17","09:00:00",30053756,"Short Rural","Planned",null,54,267,0,0,"NO"]
[null,"2017-09-17","17:03:00",60026725,"Short Rural","Other","Service Fuse",1,110.76666666666701,2.7410367767453198E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-18","08:34:00",10020761,"Short Rural","Asset failure","HV",932,128.92539341917001,0.29734466702135998,2.3063312752873602E-3,"NO"]
[null,"2017-09-18","10:33:00",10020673,"Long Rural","Planned",null,2,92,0,0,"NO"]
[null,"2017-09-18","11:18:00",60026844,"Urban","Planned",null,1,17,0,0,"NO"]
[null,"2017-09-18","14:25:00",40001116,"Long Rural","Asset failure","LV",1,169.46666666666698,2.2164094515650904E-3,1.30787339785509E-5,"NO"]
[null,"2017-09-18","15:20:00",50000095,"Long Rural","Planned",null,1,18,0,0,"NO"]
[null,"2017-09-18","20:49:00",10020808,"Urban","Other","Service Fuse",1,263.21666666666704,1.1636766079854799E-3,4.4209837573056797E-6,"NO"]
[null,"2017-09-19","07:23:00",10020795,"Urban","Other","Service Fuse",1,312.71666666666704,1.38251530397211E-3,4.4209837573056797E-6,"NO"]
[null,"2017-09-19","08:28:00",82561865,"Short Rural","Other","Fuse Operator - No Trigger Found",56,75,1.0393338365028901E-2,1.38577844867052E-4,"NO"]
[null,"2017-09-19","09:30:00",30053820,"Urban","Planned",null,4,60,0,0,"NO"]
[null,"2017-09-19","11:00:00",20006023,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-09-19","11:30:00",40001096,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-09-19","12:30:00",82915259,"Short Rural","Planned",null,1,24.9166666666667,0,0,"NO"]
[null,"2017-09-19","13:34:00",60026774,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-09-19","15:00:00",60026774,"Short Rural","Planned",null,1,21,0,0,"NO"]
[null,"2017-09-19","18:50:00",30053807,"Short Rural","Other","Service Fuse",1,913.56666666666706,2.2607160680186305E-3,2.4746043726259304E-6,"NO"]
[null,"2017-09-20","07:01:00",20010573,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",23,2.8666666666666702,1.6315891496846902E-4,5.6915900570396305E-5,"NO"]
[null,"2017-09-20","09:02:00",82980894,"Short Rural","Planned",null,13,213,0,0,"NO"]
[null,"2017-09-20","10:00:00",10020679,"Short Rural","Planned",null,1,120,0,0,"NO"]
[null,"2017-09-20","11:15:00",10020817,"Short Rural","Other","Service Fuse",1,171.15,4.23528538374927E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-20","13:01:00",50000037,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-09-20","14:00:00",50000127,"Long Rural","Planned",null,3,15,0,0,"NO"]
[null,"2017-09-21","04:52:00",10134518,"Urban","Asset failure","HV",2625,82.932482539682496,0.96243829043505402,1.1605082362927401E-2,"NO"]
[null,"2017-09-21","08:30:00",40001210,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-09-21","09:00:00",30053863,"Short Rural","Planned",null,23,402.65217391304304,0,0,"NO"]
[null,"2017-09-21","10:15:00",50000127,"Long Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-09-21","12:45:00",10020767,"Short Rural","Planned",null,1,65,0,0,"NO"]
[null,"2017-09-21","15:20:00",30053824,"Urban","Planned",null,5,20,0,0,"NO"]
[null,"2017-09-21","15:30:00",82921017,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2017-09-22","07:40:00",10020807,"Urban","Planned",null,2,5,0,0,"NO"]
[null,"2017-09-22","09:00:00",50000073,"Short Rural","Planned",null,2,61,0,0,"NO"]
[null,"2017-09-22","10:00:00",50000166,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-09-22","11:00:00",25280122,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-09-22","12:40:00",84668557,"Long Rural","Planned",null,1,23,0,0,"NO"]
[null,"2017-09-22","14:15:00",30053824,"Urban","Planned",null,5,15,0,0,"NO"]
[null,"2017-09-22","22:49:00",30053769,"Short Rural","Other","Forced Corrective Maintenance",136,45,1.5144578760470701E-2,3.36546194677126E-4,"NO"]
[null,"2017-09-23","13:21:00",20001488,"Short Rural","Other","Service Fuse",1,69.0833333333333,1.70953918742241E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-24","11:13:00",82889348,"Urban","Other","Forced Corrective Maintenance",51,132,2.9762062654181801E-2,2.2547017162258899E-4,"NO"]
[null,"2017-09-25","06:45:00",10020689,"Short Rural","Animal","Animal impact",1,121.033333333333,2.9950961590015802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-25","08:30:00",60026677,"Short Rural","Overloads",null,1,97,2.4003662414471503E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-25","10:14:00",30053771,"Short Rural","Other","Service Fuse",1,139.5,3.4520730998131703E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-25","10:59:00",50000196,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-09-25","14:03:00",50000167,"Short Rural","Planned",null,2,20,0,0,"NO"]
[null,"2017-09-26","07:50:00",20006799,"Short Rural","Animal","Animal impact",1,73.516666666666708,1.8192466479421602E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-26","08:46:00",60026819,"Long Rural","Asset failure","Subtransmission",1,271,3.5443369081872901E-3,1.30787339785509E-5,"NO"]
[null,"2017-09-26","09:50:00",50000178,"Urban","Planned",null,1,70,0,0,"NO"]
[null,"2017-09-26","10:50:00",10020796,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-09-26","14:48:00",60026644,"Long Rural","Other","Fuse Operator - No Trigger Found",1,54.999999999999993,7.1933036882029799E-4,1.30787339785509E-5,"NO"]
[null,"2017-09-27","08:00:00",10020771,"Long Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-09-27","08:52:00",50000167,"Short Rural","Planned",null,1,28,0,0,"NO"]
[null,"2017-09-27","09:44:00",10020847,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2017-09-27","10:42:00",25273020,"Urban","Planned",null,1,6,0,0,"NO"]
[null,"2017-09-27","12:00:00",10020796,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-09-27","13:00:00",50000124,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-09-27","14:54:00",84670103,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-09-28","07:48:00",60026994,"Long Rural","Other","Forced Corrective Maintenance",76,150.05000000000001,0.14914726654459801,9.9398378236986696E-4,"NO"]
[null,"2017-09-28","07:58:00",40001156,"Short Rural","Other","Service Fuse",1,188.566666666667,4.6662789786482898E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-28","08:40:00",50000129,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-09-28","10:30:00",30053808,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-09-28","12:55:00",40001110,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-09-28","14:38:00",30053845,"Short Rural","Other","Service Fuse",1,217.333333333333,5.3781401698403501E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-28","20:11:00",40001174,"Short Rural","Other","Service Fuse",1,55.516666666666701,1.3738178608694901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-29","08:30:00",10020771,"Long Rural","Planned",null,5,115,0,0,"NO"]
[null,"2017-09-29","08:30:00",83897505,"Short Rural","Planned",null,8,30,0,0,"NO"]
[null,"2017-09-29","09:55:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-09-29","12:00:00",10020797,"Short Rural","Planned",null,2,40,0,0,"NO"]
[null,"2017-09-29","14:05:00",60026731,"Short Rural","Other","Fuse Operator - No Trigger Found",1,249.20000000000002,6.1667140965838095E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-29","18:38:00",30187535,"Short Rural","Asset failure","LV",1,115.883333333333,2.8676540338113402E-4,2.4746043726259304E-6,"NO"]
[null,"2017-09-30","18:16:00",60330968,"Short Rural","Other","Service Fuse",1,60.9166666666667,1.5074464969912901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-01","07:24:00",50000130,"Long Rural","Asset failure","HV",687,25,0.22462725608161099,8.9850902432644514E-3,"NO"]
[null,"2017-10-01","14:39:00",83864041,"Short Rural","Other","Service Fuse",1,111.666666666667,2.7633082160989506E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-01","18:32:00",82912289,"Urban","Other","Trip & Manual Reclose - No Trigger Found",1391,118.408183560987,0.72816159285097504,6.1495884064121896E-3,"NO"]
[null,"2017-10-01","23:07:00",60026725,"Short Rural","Other","Forced Corrective Maintenance",322,8,6.3745808638843906E-3,7.9682260798554806E-4,"NO"]
[null,"2017-10-02","00:55:00",50000177,"Short Rural","Asset failure","LV",1,118.283333333333,2.9270445387543698E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-02","06:57:00",60026650,"Long Rural","Asset failure","LV",1,275.28333333333302,3.6003574853954103E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-02","09:23:00",40216325,"Short Rural","Other","Service Fuse",1,149.36666666666699,3.6962340645789297E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-02","14:11:00",82915259,"Short Rural","Weather",null,2803,406.30154001664903,2.81823589578616,6.9363160564704703E-3,"NO"]
[null,"2017-10-02","17:59:00",60026745,"Short Rural","Other","Service Fuse",1,203.316666666667,5.0312831236106099E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-02","19:28:00",20008837,"Long Rural","Asset failure","HV",34,64,2.8459325137326699E-2,4.4467695527073E-4,"NO"]
[null,"2017-10-02","19:28:00",25268407,"Short Rural","Asset failure","HV",137,63.999999999999993,2.1697331139184102E-2,3.3902079904975197E-4,"NO"]
[null,"2017-10-03","05:25:00",30053744,"Short Rural","Other","Fuse Operator - No Trigger Found",56,115.433333333333,1.59965025591534E-2,1.38577844867052E-4,"NO"]
[null,"2017-10-03","07:59:00",20001488,"Short Rural","Other","Fuse Operator - No Trigger Found",6,374,5.5530122121725803E-3,1.4847626235755599E-5,"NO"]
[null,"2017-10-03","10:23:00",82980894,"Short Rural","Other","Service Fuse",1,75.3333333333333,1.8642019607115301E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-03","13:30:00",40001230,"Short Rural","Planned",null,2,30,0,0,"NO"]
[null,"2017-10-03","14:20:00",40001230,"Short Rural","Planned",null,2,10,0,0,"NO"]
[null,"2017-10-03","20:32:00",50000092,"Short Rural","Asset failure","LV",64,416.63333333333304,6.5984170780696391E-2,1.58374679848059E-4,"NO"]
[null,"2017-10-04","08:30:00",82564420,"Short Rural","Planned",null,246,144,0,0,"NO"]
[null,"2017-10-04","09:55:00",25280514,"Short Rural","Other","Vibration",1,64.0833333333333,1.5858089687911101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-04","13:30:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-10-04","15:30:00",50000193,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-05","08:00:00",82915259,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-10-05","09:01:00",10020842,"Short Rural","Planned",null,15,59,0,0,"NO"]
[null,"2017-10-05","10:02:00",40001175,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-05","12:02:00",30053745,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2017-10-06","00:30:00",82564420,"Short Rural","Other","Service Fuse",1,64.116666666666703,1.5866338369153202E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-06","08:30:00",50000151,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-10-06","08:30:00",60026783,"Long Rural","Planned",null,1,198,0,0,"NO"]
[null,"2017-10-06","10:55:00",20005577,"Urban","Planned",null,2,65,0,0,"NO"]
[null,"2017-10-06","13:40:00",50000169,"Short Rural","Planned",null,3,5,0,0,"NO"]
[null,"2017-10-06","15:12:00",60026743,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",84,15.4333333333333,3.2080771086722502E-3,2.0786676730057802E-4,"NO"]
[null,"2017-10-06","19:02:00",60026667,"Long Rural","Other","Fuse Operator - No Trigger Found",1,166.666666666667,2.1797889964251501E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-07","08:13:00",30184151,"Short Rural","Other","Fuse Operator - No Trigger Found",26,116.616666666667,7.50308294461423E-3,6.4339713688274083E-5,"NO"]
[null,"2017-10-07","10:10:00",60026740,"Short Rural","Other","Service Fuse",1,118.316666666667,2.9278694068785797E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-07","15:57:00",60026713,"Short Rural","Other","Fuse Operator - No Trigger Found",11,302.566666666667,8.2360607597860309E-3,2.7220648098885201E-5,"NO"]
[null,"2017-10-07","18:02:00",60026644,"Long Rural","Other","Fuse Operator - No Trigger Found",1,2385.6,3.1200627779231001E-2,1.30787339785509E-5,"NO"]
[null,"2017-10-08","08:35:00",40001096,"Urban","Planned",null,51,120,0,0,"NO"]
[null,"2017-10-08","17:36:00",40001116,"Long Rural","Asset failure","HV",20,104.485,2.7330630394977802E-2,2.6157467957101799E-4,"NO"]
[null,"2017-10-09","07:56:00",50000025,"Long Rural","Asset failure","HV",2,331.8,8.6790478681663605E-3,2.61574679571018E-5,"NO"]
[null,"2017-10-09","08:54:00",30053848,"Short Rural","Asset failure","LV",1,154.416666666667,3.8212015853965298E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-09","10:21:00",30053765,"Long Rural","Planned",null,1,9,0,0,"NO"]
[null,"2017-10-09","11:12:00",60026840,"Urban","Other","Service Fuse",2,82.566666666666706,7.3005178445641097E-4,8.8419675146113493E-6,"NO"]
[null,"2017-10-09","13:15:00",10020783,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-10-09","15:19:00",20006212,"Short Rural","Other","Forced Corrective Maintenance",66,69.484848484848499,1.1348535652862502E-2,1.6332388859331099E-4,"NO"]
[null,"2017-10-09","16:47:00",85212266,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1,15.516666666666699,3.8397611181912296E-5,2.4746043726259304E-6,"NO"]
[null,"2017-10-10","06:30:00",60026845,"Urban","Asset failure","LV",1,52.366666666666696,2.3151218275757401E-4,4.4209837573056797E-6,"NO"]
[null,"2017-10-10","09:00:00",40001246,"Short Rural","Planned",null,4,254,0,0,"NO"]
[null,"2017-10-10","09:47:00",82556060,"Short Rural","Planned",null,3,33,0,0,"NO"]
[null,"2017-10-10","10:55:00",20007373,"Urban","Planned",null,1,12,0,0,"NO"]
[null,"2017-10-10","12:00:00",20007373,"Urban","Planned",null,1,19,0,0,"NO"]
[null,"2017-10-10","14:02:00",20007373,"Urban","Planned",null,1,13,0,0,"NO"]
[null,"2017-10-10","14:56:00",30053771,"Short Rural","Other","Service Fuse",1,50.466666666666697,1.24885034005188E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-11","02:30:00",10020810,"Urban","Planned",null,1,245,0,0,"NO"]
[null,"2017-10-11","08:30:00",10130404,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-10-11","08:54:00",60026685,"Urban","Planned",null,1,69,0,0,"NO"]
[null,"2017-10-11","10:30:00",10020800,"Urban","Other","Forced Corrective Maintenance",1,15,6.63147563595851E-5,4.4209837573056797E-6,"NO"]
[null,"2017-10-11","10:55:00",60026715,"Short Rural","Animal","Other",1,117.166666666667,2.8994114565933799E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-11","13:05:00",30053765,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-11","14:25:00",10020796,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-10-11","14:39:00",30053744,"Short Rural","Other","Fuse Operator - No Trigger Found",1,32.183333333333302,7.9641017392344392E-5,2.4746043726259304E-6,"NO"]
[null,"2017-10-11","20:50:00",60026666,"Long Rural","Other","Fuse Operator - No Trigger Found",1,635.75,8.3148051268637224E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-12","08:19:00",10020755,"Long Rural","Animal","Animal impact",1,75.3333333333333,9.8526462638416591E-4,1.30787339785509E-5,"NO"]
[null,"2017-10-12","08:36:00",60322052,"Short Rural","Overloads",null,2,491.58333333333303,2.43294853235339E-3,4.9492087452518498E-6,"NO"]
[null,"2017-10-12","09:55:00",40000969,"Short Rural","Other","Forced Corrective Maintenance",1,15,3.7119065589388895E-5,2.4746043726259304E-6,"NO"]
[null,"2017-10-12","11:15:00",20007373,"Urban","Planned",null,2,15,0,0,"NO"]
[null,"2017-10-12","14:19:00",50000130,"Long Rural","Other","Fuse Operator - No Trigger Found",2,141.76666666666699,3.7082570407184602E-3,2.61574679571018E-5,"NO"]
[null,"2017-10-12","14:23:00",60026666,"Long Rural","Animal","Animal impact",1,114.8,1.5014386607376401E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-13","05:50:00",40001038,"Long Rural","Other","Fuse Operator - No Trigger Found",1,179.35,2.3456709390530998E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-13","08:30:00",30053837,"Short Rural","Planned",null,101,389,0,0,"NO"]
[null,"2017-10-13","09:59:00",30053883,"Short Rural","Planned",null,1,38,0,0,"NO"]
[null,"2017-10-13","10:41:00",20009306,"Short Rural","Other","Fuse Operator - No Trigger Found",1,246.46666666666698,6.0990749103987003E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-13","13:45:00",40001191,"Short Rural","Other","Forced Corrective Maintenance",2,10,4.94920874525185E-5,4.9492087452518498E-6,"NO"]
[null,"2017-10-13","14:33:00",50000142,"Short Rural","Weather",null,849,82.5833333333333,0.17350255502901502,2.10093911235941E-3,"NO"]
[null,"2017-10-13","15:56:00",60026733,"Long Rural","Other","Forced Corrective Maintenance",38,172,8.5482605283808508E-2,4.9699189118493305E-4,"NO"]
[null,"2017-10-13","17:34:00",60026888,"Long Rural","Other","Fuse Operator - No Trigger Found",1,1035.2,1.35391054145959E-2,1.30787339785509E-5,"NO"]
[null,"2017-10-13","21:14:00",84962745,"Long Rural","Overloads",null,1,23.183333333333298,3.0320864940273798E-4,1.30787339785509E-5,"NO"]
[null,"2017-10-14","06:57:00",50000142,"Short Rural","Asset failure","Distribution substation",1,142.03333333333299,3.5147630772530203E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-14","08:03:00",50000129,"Short Rural","Overloads",null,1,136.88333333333301,3.3873209520627896E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-14","11:42:00",82980894,"Short Rural","Other","Service Fuse",1,134.86666666666699,3.33741643054817E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-14","14:56:00",60026670,"Long Rural","Weather",null,55,454.35909090909104,0.326834292440492,7.1933036882029799E-4,"NO"]
[null,"2017-10-14","19:48:00",40001177,"Short Rural","Other","Service Fuse",1,50.366666666666696,1.2463757356792602E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-14","22:48:00",60026783,"Long Rural","Weather",null,1,158.166666666667,2.0686197576074601E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-15","08:49:00",40000966,"Long Rural","Other","Fuse Operator - No Trigger Found",1,436.8,5.7127910018310206E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-15","12:59:00",40001038,"Long Rural","Other","Fuse Operator - No Trigger Found",2,145.96666666666698,3.8181184061382907E-3,2.61574679571018E-5,"NO"]
[null,"2017-10-15","16:44:00",20002494,"Short Rural","Other","Fuse Operator - No Trigger Found",14,70.95,2.45802452332933E-3,3.4644461216762992E-5,"NO"]
[null,"2017-10-15","21:05:00",10020825,"Short Rural","Other","Service Fuse",2,105.366666666667,5.2148162812470401E-4,4.9492087452518498E-6,"NO"]
[null,"2017-10-16","08:20:00",20011235,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-16","09:25:00",82912289,"Urban","Planned",null,3,10,0,0,"NO"]
[null,"2017-10-16","09:57:00",50000165,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-10-16","11:01:00",10020857,"Short Rural","Animal","Other",1,262.05,6.4847007584662407E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-16","13:15:00",40001191,"Short Rural","Planned",null,3,15,0,0,"NO"]
[null,"2017-10-16","14:20:00",30185760,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-10-16","18:14:00",60026733,"Long Rural","Other","Service Fuse",1,361.13333333333304,4.7231667974540099E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-17","00:21:00",85212266,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1,36.133333333333304,8.9415704664216799E-5,2.4746043726259304E-6,"NO"]
[null,"2017-10-17","02:02:00",20012587,"Short Rural","Asset failure","LV",1,477.35,1.1812523972729902E-3,2.4746043726259304E-6,"NO"]
[null,"2017-10-17","08:15:00",50000193,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2017-10-17","09:10:00",40001175,"Urban","Planned",null,4,15,0,0,"NO"]
[null,"2017-10-17","10:49:00",20002652,"Short Rural","Other","Service Fuse",2,105.60000000000001,5.2263644349859607E-4,4.9492087452518498E-6,"NO"]
[null,"2017-10-17","12:00:00",30053840,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-17","13:00:00",20005978,"Urban","Planned",null,1,75,0,0,"NO"]
[null,"2017-10-17","15:48:00",40001204,"Short Rural","Other","Service Fuse",1,133.61666666666699,3.3064838758903401E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-17","18:16:00",82649845,"Short Rural","Asset failure","LV",1,92.216666666666697,2.28199766562321E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-18","05:42:00",20008892,"Short Rural","Other","Vibration",1,359.5,8.8962027195902099E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-18","08:16:00",60026840,"Urban","Asset failure","HV",1850,13.027027027027,0.10654570855106701,8.1788199510155011E-3,"NO"]
[null,"2017-10-18","10:00:00",30053822,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-10-18","10:07:00",60026731,"Short Rural","Planned",null,1,7,0,0,"NO"]
[null,"2017-10-18","11:40:00",50000126,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2017-10-18","14:15:00",40001177,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2017-10-18","17:11:00",40001060,"Short Rural","Other","Service Fuse",2,124.566666666667,6.1650643603353898E-4,4.9492087452518498E-6,"NO"]
[null,"2017-10-18","20:26:00",30053824,"Urban","Overloads",null,1,49.3,2.1795449923516999E-4,4.4209837573056797E-6,"NO"]
[null,"2017-10-19","03:28:00",10020772,"Long Rural","Other","Service Fuse",1,174.3,2.2796233324614201E-3,1.30787339785509E-5,"YES"]
[null,"2017-10-19","06:30:00",60026747,"Long Rural","Animal","Animal impact",1,353.6,4.6246403348155895E-3,1.30787339785509E-5,"YES"]
[null,"2017-10-19","07:45:00",10020850,"Short Rural","Overloads",null,1,160.01666666666699,3.9597794302635898E-4,2.4746043726259304E-6,"YES"]
[null,"2017-10-19","08:45:00",40001176,"Short Rural","Planned",null,1,10,0,0,"YES"]
[null,"2017-10-19","09:34:00",20008373,"Short Rural","Planned",null,2,21,0,0,"YES"]
[null,"2017-10-19","10:27:00",50000030,"Short Rural","Other","Service Fuse",4,126.966666666667,1.25676907404429E-3,9.8984174905037098E-6,"YES"]
[null,"2017-10-19","11:34:00",10134605,"Urban","Asset failure","HV",1,4387,1.9394855743300004E-2,4.4209837573056797E-6,"YES"]
[null,"2017-10-19","11:50:00",40001177,"Short Rural","Planned",null,1,127,0,0,"YES"]
[null,"2017-10-19","13:39:00",20005412,"Urban","Asset failure","LV",1,114.133333333333,5.0458161283382106E-4,4.4209837573056797E-6,"YES"]
[null,"2017-10-19","15:00:00",82773016,"Urban","Planned",null,1,5,0,0,"YES"]
[null,"2017-10-19","16:07:00",40001010,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",1,8.4,1.09861365419827E-4,1.30787339785509E-5,"YES"]
[null,"2017-10-19","20:52:00",20004893,"Urban","Other","Service Fuse",2,199.183333333333,1.7611725627853401E-3,8.8419675146113493E-6,"YES"]
[null,"2017-10-20","07:02:00",30053831,"Urban","Other","Fuse Operator - No Trigger Found",4,122.116666666667,2.15950319931858E-3,1.7683935029222702E-5,"NO"]
[null,"2017-10-20","08:30:00",60026788,"Short Rural","Planned",null,2,75,0,0,"NO"]
[null,"2017-10-20","10:00:00",30053830,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-10-20","12:08:00",50000167,"Short Rural","Planned",null,2,4,0,0,"NO"]
[null,"2017-10-20","13:30:00",50000034,"Short Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-10-20","18:45:00",20004751,"Urban","Other","Fuse Operator - No Trigger Found",50,55.699999999999996,1.2312439764096302E-2,2.21049187865284E-4,"NO"]
[null,"2017-10-21","06:21:00",25280514,"Short Rural","Asset failure","Distribution substation",1,240.8,5.9588473292832304E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-21","08:35:00",10020796,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-10-21","13:02:00",84119480,"Short Rural","Asset failure","Distribution substation",61,6.3833333333333293,9.6356969929432509E-4,1.5095086673018202E-4,"NO"]
[null,"2017-10-22","00:31:00",40001091,"Urban","Other","Service Fuse",2,237.833333333333,2.1029146072250701E-3,8.8419675146113493E-6,"NO"]
[null,"2017-10-22","12:07:00",20003983,"Short Rural","Asset failure","Distribution substation",1,214.98333333333301,5.3199869670836396E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-23","05:00:00",82561236,"Short Rural","Other","Fuse Operator - No Trigger Found",135,133.63333333333301,4.4643100184357999E-2,3.3407159030450002E-4,"NO"]
[null,"2017-10-23","07:05:00",40001143,"Urban","Planned",null,1,265,0,0,"NO"]
[null,"2017-10-23","09:30:00",50000034,"Short Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-10-23","11:20:00",60026803,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",12,50,1.48476262357556E-3,2.9695252471511097E-5,"NO"]
[null,"2017-10-23","12:17:00",60026671,"Short Rural","Other","Trip & Auto Reclose - No Trigger Found",253,1.2166666666666701,7.6172446930047096E-4,6.2607490627435895E-4,"NO"]
[null,"2017-10-23","12:43:00",60026733,"Long Rural","Asset failure","HV",1,1265.55,1.6551791786555102E-2,1.30787339785509E-5,"NO"]
[null,"2017-10-23","15:04:00",60026994,"Long Rural","Planned",null,1,54,0,0,"NO"]
[null,"2017-10-23","18:37:00",20001353,"Short Rural","Other","Service Fuse",1,125.283333333333,3.1002668448381802E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-24","06:21:00",82563099,"Urban","Vegetation","Grow-in - NSP responsibility",2,213.35,1.8864337692423301E-3,8.8419675146113493E-6,"NO"]
[null,"2017-10-24","08:46:00",40000961,"Long Rural","Planned",null,28,252,0,0,"NO"]
[null,"2017-10-24","10:00:00",30053830,"Short Rural","Planned",null,3,63,0,0,"NO"]
[null,"2017-10-24","11:35:00",10020796,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-10-24","11:40:00",30053824,"Urban","Planned",null,3,30,0,0,"NO"]
[null,"2017-10-24","14:30:00",20005577,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2017-10-24","16:26:00",40001121,"Short Rural","Third party","Vehicle impact",1,141.183333333333,3.4937289400857006E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-25","00:17:00",10020844,"Short Rural","Other","Fuse Operator - No Trigger Found",1,520.68333333333305,1.2884852534201102E-3,2.4746043726259304E-6,"NO"]
[null,"2017-10-25","08:30:00",10020836,"Short Rural","Planned",null,4,315,0,0,"NO"]
[null,"2017-10-25","09:00:00",10020770,"Short Rural","Planned",null,26,205,0,0,"NO"]
[null,"2017-10-25","10:00:00",30053824,"Urban","Planned",null,3,20,0,0,"NO"]
[null,"2017-10-25","11:30:00",40223076,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-25","12:50:00",30053824,"Urban","Planned",null,3,10,0,0,"NO"]
[null,"2017-10-25","15:35:00",10020796,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2017-10-26","08:05:00",40001029,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-10-26","08:33:00",40000961,"Long Rural","Planned",null,2,280,0,0,"NO"]
[null,"2017-10-26","09:04:00",50000214,"Urban","Planned",null,6,326,0,0,"NO"]
[null,"2017-10-26","11:00:00",30053824,"Urban","Planned",null,3,25,0,0,"NO"]
[null,"2017-10-26","11:40:00",30053824,"Urban","Planned",null,3,25,0,0,"NO"]
[null,"2017-10-26","13:30:00",82563086,"Short Rural","Other","Forced Corrective Maintenance",1,25,6.18651093156482E-5,2.4746043726259304E-6,"NO"]
[null,"2017-10-26","15:23:00",40216323,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",266,330.50513784461202,1.1498086145261099,3.4789432382945299E-3,"NO"]
[null,"2017-10-26","16:25:00",84000793,"Long Rural","Weather",null,1,509.96666666666704,6.6697183712616601E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-26","17:14:00",60026775,"Short Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",34,249.166666666667,2.0964023376762599E-2,8.4136548669281499E-5,"NO"]
[null,"2017-10-26","20:14:00",50000142,"Short Rural","Other","Service Fuse",1,85.183333333333294,2.1079504914151801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-27","06:03:00",60026807,"Short Rural","Weather",null,1,235.05,5.8165575778572408E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-27","08:30:00",20004796,"Short Rural","Planned",null,4,266.76666666666705,0,0,"NO"]
[null,"2017-10-27","09:00:00",40000961,"Long Rural","Planned",null,8,128.25,0,0,"NO"]
[null,"2017-10-27","09:50:00",82563099,"Urban","Planned",null,8,20,0,0,"NO"]
[null,"2017-10-27","10:45:00",50000113,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-10-27","13:00:00",50000159,"Long Rural","Planned",null,1,45,0,0,"NO"]
[null,"2017-10-27","14:22:00",50000159,"Long Rural","Asset failure","Distribution substation",3,147.81666666666698,5.7997645827883911E-3,3.9236201935652595E-5,"NO"]
[null,"2017-10-28","08:00:00",30053822,"Short Rural","Planned",null,2,17,0,0,"NO"]
[null,"2017-10-28","08:10:00",85161218,"Short Rural","Planned",null,8,434.5,0,0,"NO"]
[null,"2017-10-28","12:09:00",40001061,"Long Rural","Weather",null,1,148.36666666666699,1.94044816461767E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-29","08:30:00",60026678,"Short Rural","Planned",null,11,328,0,0,"NO"]
[null,"2017-10-29","19:26:00",82920985,"Urban","Other","Service Fuse",1,78.599999999999994,3.4748932332422604E-4,4.4209837573056797E-6,"NO"]
[null,"2017-10-30","07:21:00",82563612,"Long Rural","Other","Fuse Operator - No Trigger Found",1,141.56666666666698,1.8515127735635201E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-30","09:10:00",40000985,"Long Rural","Planned",null,2,107,0,0,"NO"]
[null,"2017-10-30","10:30:00",60026783,"Long Rural","Weather",null,1,98.383333333333297,1.2867294445897601E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-30","11:00:00",20005482,"Short Rural","Planned",null,6,20,0,0,"NO"]
[null,"2017-10-30","12:47:00",40000974,"Long Rural","Other","Trip & Auto Reclose - No Trigger Found",11,1.56666666666667,2.2539018223036002E-4,1.4386607376406E-4,"NO"]
[null,"2017-10-30","14:28:00",50000035,"Short Rural","Planned",null,5,17,0,0,"NO"]
[null,"2017-10-30","16:22:00",10020787,"Short Rural","Other","Forced Corrective Maintenance",19,114.8,5.3976070575716701E-3,4.7017483079892603E-5,"NO"]
[null,"2017-10-30","17:03:00",40001116,"Long Rural","Asset failure","Distribution substation",6,1214.9333333333302,9.5338739210044487E-2,7.8472403871305299E-5,"NO"]
[null,"2017-10-30","18:56:00",40001201,"Short Rural","Weather",null,1,222.45000000000002,5.504757426906371E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-30","20:22:00",84510820,"Short Rural","Other","Service Fuse",1,43.366666666666696,1.0731534295954401E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-31","00:17:00",40001111,"Long Rural","Asset failure","Distribution substation",28,651.83571428571406,0.23870520533612302,3.66204551399425E-4,"NO"]
[null,"2017-10-31","07:28:00",40001111,"Long Rural","Weather",null,1,160.96666666666698,2.1052402127474099E-3,1.30787339785509E-5,"NO"]
[null,"2017-10-31","08:45:00",10020847,"Short Rural","Planned",null,17,335,0,0,"NO"]
[null,"2017-10-31","09:09:00",40001135,"Short Rural","Planned",null,3,241,0,0,"NO"]
[null,"2017-10-31","11:40:00",82554035,"Short Rural","Planned",null,3,5,0,0,"NO"]
[null,"2017-10-31","12:10:00",84064137,"Urban","Other","Service Fuse",3,90.45,1.1996339425448998E-3,1.3262951271916999E-5,"NO"]
[null,"2017-10-31","14:40:00",20005482,"Short Rural","Planned",null,3,15,0,0,"NO"]
[null,"2017-10-31","15:37:00",20011420,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",47,20.383333333333301,2.3707122323818504E-3,1.1630640551341901E-4,"NO"]
[null,"2017-10-31","15:57:00",30053883,"Short Rural","Asset failure","LV",1,63.699999999999996,1.5763229853627201E-4,2.4746043726259304E-6,"NO"]
[null,"2017-10-31","17:50:00",82563086,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",295,2.4666666666666703,1.8006871151474702E-3,7.3000828992464807E-4,"NO"]
[null,"2017-10-31","18:17:00",30053840,"Short Rural","5 - STPIS Exclusion (3.3)(a)",null,753,34.9,0,0,"NO"]
[null,"2017-10-31","18:17:00",82563111,"Urban","5 - STPIS Exclusion (3.3)(a)",null,79,34.283333333333303,0,0,"NO"]
[null,"2017-10-31","20:17:00",30053862,"Short Rural","Weather",null,2,105.35000000000001,5.2139914131228303E-4,4.9492087452518498E-6,"NO"]
[null,"2017-11-01","08:00:00",20011700,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2017-11-01","08:30:00",10020802,"Urban","Planned",null,30,240,0,0,"NO"]
[null,"2017-11-01","09:00:00",50000177,"Short Rural","Planned",null,12,318,0,0,"NO"]
[null,"2017-11-01","10:56:00",60026666,"Long Rural","Other","Forced Corrective Maintenance",56,48,3.51556369343448E-2,7.3240910279884902E-4,"NO"]
[null,"2017-11-01","11:20:00",20005482,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-11-01","15:49:00",10020844,"Short Rural","Third party","Vehicle impact",1,175.23333333333301,4.3363317289648305E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-01","17:20:00",30053814,"Short Rural","Other","Service Fuse",1,89.3333333333333,2.21064657287916E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-02","06:14:00",30053779,"Long Rural","Animal","Animal impact",1,461.73333333333306,6.0388874356962193E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-02","08:30:00",25267731,"Short Rural","Planned",null,9,225,0,0,"NO"]
[null,"2017-11-02","09:00:00",60026676,"Long Rural","Planned",null,22,245,0,0,"NO"]
[null,"2017-11-02","09:42:00",82647141,"Urban","Other","Service Fuse",2,99.116666666666703,8.7638634682322806E-4,8.8419675146113493E-6,"NO"]
[null,"2017-11-02","12:15:00",10020808,"Urban","Other","Forced Corrective Maintenance",1,5,2.21049187865284E-5,4.4209837573056797E-6,"NO"]
[null,"2017-11-02","13:49:00",60026666,"Long Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-11-02","14:35:00",40000979,"Long Rural","Other","Fuse Operator - No Trigger Found",1,190.8,2.4954224431075101E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-03","06:57:00",20009615,"Short Rural","Other","Service Fuse",2,104.73333333333299,5.1834712925271091E-4,4.9492087452518498E-6,"NO"]
[null,"2017-11-03","08:44:00",40001040,"Short Rural","Planned",null,10,105.283333333333,0,0,"NO"]
[null,"2017-11-03","09:00:00",10020780,"Short Rural","Other","Service Fuse",1,86.616666666666703,2.1434198207561601E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-03","10:58:00",40001177,"Short Rural","Overloads",null,1,165.35,4.0917583301369699E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-03","13:15:00",60330968,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-11-03","15:12:00",40001177,"Short Rural","Other","Service Fuse",1,55.949999999999996,1.3845411464842101E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-04","08:39:00",20001108,"Urban","Planned",null,71,269,0,0,"NO"]
[null,"2017-11-04","16:25:00",20005314,"Short Rural","Other","Service Fuse",3,56.35,4.1833186919241301E-4,7.4238131178777803E-6,"NO"]
[null,"2017-11-05","11:30:00",83850831,"Short Rural","Other","Service Fuse",1,84.783333333333303,2.0980520739246803E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-05","18:18:00",60026819,"Long Rural","Asset failure","Subtransmission",2,988.41666666666708,2.58544772865987E-2,2.61574679571018E-5,"NO"]
[null,"2017-11-05","20:16:00",60026703,"Short Rural","Asset failure","Subtransmission",1,923.2,2.2845547568082604E-3,2.4746043726259304E-6,"NO"]
[null,"2017-11-06","05:43:00",60026712,"Long Rural","Weather",null,1,172.833333333333,2.2604411892928802E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-06","08:12:00",50000035,"Short Rural","Planned",null,5,18,0,0,"NO"]
[null,"2017-11-06","08:43:00",40000961,"Long Rural","Weather",null,1,184.51666666666699,2.41324439794228E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-06","10:15:00",50000178,"Urban","Planned",null,1,42.999999999999993,0,0,"NO"]
[null,"2017-11-06","11:38:00",50000094,"Long Rural","Other","Fuse Operator - No Trigger Found",2,27.133333333333301,7.0973929723602792E-4,2.61574679571018E-5,"NO"]
[null,"2017-11-06","13:38:00",82915259,"Short Rural","Planned",null,1,51.999999999999993,0,0,"NO"]
[null,"2017-11-06","16:08:00",60026821,"Long Rural","Weather",null,1,70.233333333333306,9.1856308309355705E-4,1.30787339785509E-5,"NO"]
[null,"2017-11-06","18:32:00",60026755,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",1718,127.63950329840901,2.8679658209085401,2.2469264975150401E-2,"NO"]
[null,"2017-11-06","19:23:00",60026891,"Long Rural","Asset failure","Distribution substation",271,194.49815498155002,0.68936698927543794,3.5443369081872901E-3,"NO"]
[null,"2017-11-06","22:16:00",50000159,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",615,102,0.82042898247449592,8.0434213968087909E-3,"NO"]
[null,"2017-11-07","05:29:00",60026667,"Long Rural","Weather",null,5,663.55000000000007,4.3391969657337194E-2,6.5393669892754389E-5,"YES"]
[null,"2017-11-07","07:57:00",60026755,"Long Rural","Weather",null,1,316.41666666666703,4.1383294097131398E-3,1.30787339785509E-5,"YES"]
[null,"2017-11-07","08:32:00",50000108,"Short Rural","Planned",null,5,297,0,0,"YES"]
[null,"2017-11-07","09:50:00",60026840,"Urban","Other","Service Fuse",2,92.183333333333294,8.1508203872192309E-4,8.8419675146113493E-6,"YES"]
[null,"2017-11-07","11:15:00",10020800,"Urban","Planned",null,1,15,0,0,"YES"]
[null,"2017-11-07","12:12:00",10020841,"Short Rural","Planned",null,1,6,0,0,"YES"]
[null,"2017-11-07","14:33:00",40001067,"Urban","Other","Forced Corrective Maintenance",2,151,1.3351370947063102E-3,8.8419675146113493E-6,"YES"]
[null,"2017-11-07","16:01:00",25273354,"Urban","Exclusion - Customer Installation Fault",null,1,44.883333333333304,0,0,"YES"]
[null,"2017-11-07","16:56:00",82915271,"Urban","Other","Trip & Manual Reclose - No Trigger Found",1086,1418.2333333333302,6.8092053723794592,4.801188360433961E-3,"YES"]
[null,"2017-11-07","18:12:00",40000979,"Long Rural","Weather",null,1,1061.6833333333302,1.38854738861278E-2,1.30787339785509E-5,"YES"]
[null,"2017-11-07","19:33:00",40001038,"Long Rural","Other","Fuse Operator - No Trigger Found",1,135.166666666667,1.7678088761007901E-3,1.30787339785509E-5,"YES"]
[null,"2017-11-07","21:51:00",40223073,"Long Rural","Asset failure","Distribution substation",19,973.81666666666706,0.24198949341703702,2.4849594559246701E-4,"YES"]
[null,"2017-11-08","06:46:00",50000233,"Short Rural","Other","Fuse Operator - No Trigger Found",1,643.96666666666715,1.59356272915868E-3,2.4746043726259304E-6,"NO"]
[null,"2017-11-08","08:05:00",50000211,"Short Rural","Other","Service Fuse",4,585.95000000000005,5.7999777285606506E-3,9.8984174905037098E-6,"NO"]
[null,"2017-11-08","08:45:00",20007111,"Short Rural","Planned",null,26,212.07692307692301,0,0,"NO"]
[null,"2017-11-08","10:03:00",40001101,"Urban","Planned",null,62,130,0,0,"NO"]
[null,"2017-11-08","12:45:00",20007445,"Urban","Planned",null,3,25,0,0,"NO"]
[null,"2017-11-08","12:55:00",50000155,"Urban","Other","Fuse Operator - No Trigger Found",1,50.533333333333303,2.2340704586918002E-4,4.4209837573056797E-6,"NO"]
[null,"2017-11-08","15:04:00",60027003,"Long Rural","Other","Forced Corrective Maintenance",1,86,1.1247711221553801E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-08","17:49:00",30053868,"Short Rural","Other","Forced Corrective Maintenance",15,3,1.1135719676816701E-4,3.7119065589388895E-5,"NO"]
[null,"2017-11-09","06:03:00",60026821,"Long Rural","Weather",null,1,185.916666666667,2.4315546255122499E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-09","08:00:00",20007358,"Urban","Planned",null,2,59,0,0,"NO"]
[null,"2017-11-09","09:03:00",40001046,"Short Rural","Other","Service Fuse",1,145.583333333333,3.60261153248124E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-09","09:32:00",50000035,"Short Rural","Other","Fuse Operator - No Trigger Found",2,218.70000000000002,1.0823919525865802E-3,4.9492087452518498E-6,"NO"]
[null,"2017-11-09","11:23:00",60026757,"Long Rural","Planned",null,1,107,0,0,"NO"]
[null,"2017-11-09","14:10:00",60026888,"Long Rural","Weather",null,1,110.583333333333,1.4462899991280801E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-10","02:53:00",10020828,"Long Rural","Asset failure","HV",668,194.96646706586802,1.7033429244049199,8.7365942976719898E-3,"NO"]
[null,"2017-11-10","07:00:00",20005133,"Long Rural","Planned",null,107,51.999999999999993,0,0,"NO"]
[null,"2017-11-10","08:30:00",20011656,"Urban","Planned",null,2,40,0,0,"NO"]
[null,"2017-11-10","10:00:00",40000961,"Long Rural","Planned",null,2,40,0,0,"NO"]
[null,"2017-11-10","12:17:00",40216323,"Long Rural","Other","Fuse Operator - No Trigger Found",1,181.683333333333,2.3761879850030501E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-10","15:31:00",50000124,"Short Rural","Overloads",null,1,83.949999999999989,2.07743037081947E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-10","18:18:00",60026764,"Short Rural","Other","Forced Corrective Maintenance",17,71,2.9868474777594899E-3,4.2068274334640702E-5,"NO"]
[null,"2017-11-11","08:44:00",40223076,"Long Rural","Planned",null,1,47,0,0,"NO"]
[null,"2017-11-11","13:10:00",20009306,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-11-12","09:00:00",25274647,"Urban","Planned",null,62,281.51612903225799,0,0,"NO"]
[null,"2017-11-12","09:35:00",40001111,"Long Rural","Asset failure","HV",22,370.18181818181802,0.106513209521318,2.8773214752811897E-4,"NO"]
[null,"2017-11-13","06:48:00",30053883,"Short Rural","Asset failure","LV",1,216.61666666666699,5.3604055051698605E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-13","09:20:00",50000167,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2017-11-13","11:00:00",20005482,"Short Rural","Planned",null,2,35,0,0,"NO"]
[null,"2017-11-13","17:05:00",83877404,"Urban","Other","Service Fuse",5,64.1666666666667,1.4183989554689001E-3,2.21049187865284E-5,"NO"]
[null,"2017-11-14","08:08:00",60026751,"Long Rural","Planned",null,13,313.21666666666704,0,0,"NO"]
[null,"2017-11-14","09:00:00",50000096,"Urban","Planned",null,1,18,0,0,"NO"]
[null,"2017-11-14","11:00:00",50000036,"Short Rural","Planned",null,1,80,0,0,"NO"]
[null,"2017-11-14","13:46:00",50000068,"Short Rural","Other","Fuse Operator - No Trigger Found",12,76.116666666666703,2.2603036339565205E-3,2.9695252471511097E-5,"NO"]
[null,"2017-11-14","13:51:00",82915259,"Short Rural","Other","Service Fuse",1,104.533333333333,2.5867864375183003E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-14","17:10:00",10020831,"Short Rural","Other","Service Fuse",1,82.966666666666697,2.05309676115531E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-15","08:05:00",20006666,"Short Rural","Other","Service Fuse",2,120.533333333333,5.9654462742769006E-4,4.9492087452518498E-6,"NO"]
[null,"2017-11-15","09:00:00",50000236,"Long Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-11-15","10:38:00",30053755,"Short Rural","Planned",null,1,88,0,0,"NO"]
[null,"2017-11-15","12:58:00",50000175,"Short Rural","Weather",null,1,118.95,2.9435419012385398E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-15","15:56:00",84666984,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2017-11-16","07:35:00",20003792,"Short Rural","Other","Service Fuse",1,105.183333333333,2.6028713659403702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-16","08:44:00",84255558,"Short Rural","Other","Forced Corrective Maintenance",14,464,1.6075030004578002E-2,3.4644461216762992E-5,"NO"]
[null,"2017-11-16","10:00:00",60026657,"Short Rural","Planned",null,1,139,0,0,"NO"]
[null,"2017-11-16","14:09:00",10020844,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2017-11-16","21:25:00",10020670,"Long Rural","Third party","Fire",16,1141.1500000000001,0.238796756473973,2.0925974365681402E-4,"NO"]
[null,"2017-11-17","08:30:00",10020776,"Short Rural","Planned",null,11,334,0,0,"NO"]
[null,"2017-11-17","09:26:00",20001649,"Short Rural","Other","Service Fuse",1,50.466666666666697,1.24885034005188E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-17","12:54:00",50000036,"Short Rural","Asset failure","Distribution substation",1,5942.5333333333301,1.4705418971142001E-2,2.4746043726259304E-6,"NO"]
[null,"2017-11-17","13:56:00",50000148,"Short Rural","Other","Forced Corrective Maintenance",4,35,3.4644461216762996E-4,9.8984174905037098E-6,"NO"]
[null,"2017-11-17","17:22:00",60322051,"Urban","Other","Trip & Manual Reclose - No Trigger Found",283,14.616666666666699,1.8287472995157501E-2,1.25113840331751E-3,"NO"]
[null,"2017-11-18","01:19:00",60026677,"Short Rural","Asset failure","LV",1,476.26666666666705,1.1785715758693099E-3,2.4746043726259304E-6,"NO"]
[null,"2017-11-18","08:00:00",20006948,"Short Rural","Planned",null,6,388.5,0,0,"NO"]
[null,"2017-11-18","15:51:00",20013260,"Short Rural","Overloads",null,1,78.399999999999991,1.94008982813873E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-19","07:00:00",40001215,"Urban","Planned",null,79,232.16455696202502,0,0,"NO"]
[null,"2017-11-19","13:39:00",50000185,"Short Rural","Other","Fuse Operator - No Trigger Found",16,125.75,4.9789039977233612E-3,3.9593669962014799E-5,"NO"]
[null,"2017-11-19","20:53:00",10020834,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",611,133.700409165303,0.202152782073966,1.5119832716744398E-3,"NO"]
[null,"2017-11-19","21:04:00",40001011,"Long Rural","Asset failure","HV",109,168.82599388379202,0.24067529863109302,1.4255820036620502E-3,"NO"]
[null,"2017-11-20","09:30:00",50000075,"Short Rural","Other","Forced Corrective Maintenance",1,10,2.4746043726259301E-5,2.4746043726259304E-6,"NO"]
[null,"2017-11-20","12:15:00",20007445,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2017-11-20","14:10:00",85206371,"Short Rural","Other","Forced Corrective Maintenance",1,30,7.4238131178777804E-5,2.4746043726259304E-6,"NO"]
[null,"2017-11-20","18:53:00",60026764,"Short Rural","Other","Forced Corrective Maintenance",7,101,1.74954529144653E-3,1.7322230608381499E-5,"NO"]
[null,"2017-11-21","06:20:00",40001066,"Long Rural","Asset failure","HV",35,1402.1023809523799,0.64182034179091507,4.5775568924928098E-4,"NO"]
[null,"2017-11-21","08:30:00",60026830,"Short Rural","Planned",null,34,118,0,0,"NO"]
[null,"2017-11-21","09:15:00",20008892,"Short Rural","Other","Forced Corrective Maintenance",1,23,5.6915900570396305E-5,2.4746043726259304E-6,"NO"]
[null,"2017-11-21","11:30:00",20005482,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2017-11-21","14:00:00",10131875,"Short Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2017-11-21","14:55:00",82912274,"Short Rural","Planned",null,4,10,0,0,"NO"]
[null,"2017-11-21","19:53:00",40000998,"Short Rural","Other","Service Fuse",27,40.999999999999993,2.7393870404969003E-3,6.6814318060900006E-5,"NO"]
[null,"2017-11-22","04:49:00",82914591,"Urban","Other","Service Fuse",1,100.25,4.4320362166989398E-4,4.4209837573056797E-6,"NO"]
[null,"2017-11-22","08:35:00",40000969,"Short Rural","Planned",null,41,393,0,0,"NO"]
[null,"2017-11-22","10:09:00",30053846,"Short Rural","Other","Service Fuse",3,119.25,8.8528971430692507E-4,7.4238131178777803E-6,"NO"]
[null,"2017-11-22","13:54:00",82907503,"Short Rural","Other","Service Fuse",1,51.5833333333333,1.2764834222128702E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-22","19:34:00",20010573,"Short Rural","Animal","Animal impact",1,772.26666666666711,1.9110544701665801E-3,2.4746043726259304E-6,"NO"]
[null,"2017-11-23","07:53:00",82915259,"Short Rural","Other","Fuse Operator - No Trigger Found",92,82.266666666666708,1.8729125681031702E-2,2.27663602281585E-4,"NO"]
[null,"2017-11-23","09:28:00",20006350,"Short Rural","Other","Service Fuse",1,282.41666666666703,6.9886951823577208E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-23","11:36:00",50000232,"Short Rural","Planned",null,6,51,0,0,"NO"]
[null,"2017-11-23","13:52:00",10020673,"Long Rural","Other","Forced Corrective Maintenance",3,7,2.7465341354956799E-4,3.9236201935652595E-5,"NO"]
[null,"2017-11-23","22:16:00",30053745,"Short Rural","Animal","Other",1,57.199999999999996,1.4154737011420299E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-24","08:30:00",10020847,"Short Rural","Planned",null,6,238,0,0,"NO"]
[null,"2017-11-24","08:50:00",30053832,"Short Rural","Other","Service Fuse",1,72.949999999999989,1.80522388983061E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-24","10:30:00",60026821,"Long Rural","Planned",null,1,81,0,0,"NO"]
[null,"2017-11-24","13:15:00",40001237,"Urban","Planned",null,1,45,0,0,"NO"]
[null,"2017-11-25","07:29:00",10020847,"Short Rural","Vegetation","Grow-in - NSP responsibility",1,624.78333333333308,1.54609156861047E-3,2.4746043726259304E-6,"NO"]
[null,"2017-11-25","09:59:00",25273020,"Urban","Overloads",null,1,133.5,5.9020133160030803E-4,4.4209837573056797E-6,"NO"]
[null,"2017-11-25","10:56:00",50000137,"Short Rural","Asset failure","HV",1,249.26666666666699,6.1683638328322303E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-26","09:36:00",82962855,"Short Rural","Other","Service Fuse",1,124.8,3.0883062570371595E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-27","00:59:00",40001116,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",35,310.05,0.14192715145173901,4.5775568924928098E-4,"NO"]
[null,"2017-11-27","08:30:00",82921002,"Urban","Planned",null,39,29,0,0,"NO"]
[null,"2017-11-27","10:00:00",40001115,"Short Rural","Planned",null,1,47.999999999999993,0,0,"NO"]
[null,"2017-11-27","12:50:00",40001106,"Short Rural","Asset failure","HV",1,92.366666666666703,2.28570957218215E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-27","13:15:00",20008892,"Short Rural","Asset failure","HV",8,68,1.3461847787085001E-3,1.9796834981007399E-5,"NO"]
[null,"2017-11-27","16:07:00",60026641,"Long Rural","Other","Forced Corrective Maintenance",18,70,1.6479204812974099E-2,2.3541721161391601E-4,"NO"]
[null,"2017-11-28","08:17:00",82552955,"Short Rural","Network business","Network error",1,42.55,1.05294416055233E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-28","09:00:00",82563117,"Short Rural","Planned",null,3,54,0,0,"NO"]
[null,"2017-11-28","11:21:00",50000044,"Long Rural","Overloads",null,1,275.566666666667,3.6040631266893402E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-28","12:45:00",50000118,"Long Rural","Asset failure","LV",1,232.25,3.03753596651844E-3,1.30787339785509E-5,"NO"]
[null,"2017-11-28","17:28:00",10020777,"Short Rural","Animal","Other",18,100.283333333333,4.4669083530270602E-3,4.4542878707266693E-5,"NO"]
[null,"2017-11-29","08:19:00",40001053,"Short Rural","Asset failure","Zone substation",795,6.4166666666666687,1.2623575555858E-2,1.96731047623761E-3,"NO"]
[null,"2017-11-29","08:35:00",85081026,"Short Rural","Planned",null,3,36,0,0,"NO"]
[null,"2017-11-29","09:39:00",30053832,"Short Rural","Asset failure","LV",1,76.883333333333297,1.9025583284872302E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-29","10:36:00",40001232,"Short Rural","Planned",null,2,38.999999999999993,0,0,"NO"]
[null,"2017-11-29","13:20:00",40001207,"Short Rural","Other","Fuse Operator - No Trigger Found",1,278.78333333333302,6.8987845568189803E-4,2.4746043726259304E-6,"NO"]
[null,"2017-11-29","15:50:00",50000090,"Urban","Asset failure","LV",2,168.11666666666699,1.4864821053314102E-3,8.8419675146113493E-6,"NO"]
[null,"2017-11-29","21:59:00",40001226,"Short Rural","Other","Fuse Operator - No Trigger Found",24,124.683333333333,7.4050061246458201E-3,5.9390504943022201E-5,"NO"]
[null,"2017-11-30","07:58:00",60026662,"Long Rural","Planned",null,4,352,0,0,"NO"]
[null,"2017-11-30","08:30:00",20003349,"Urban","Planned",null,12,360,0,0,"NO"]
[null,"2017-11-30","09:15:00",60026703,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-11-30","11:00:00",60026786,"Short Rural","Planned",null,24,150,0,0,"NO"]
[null,"2017-11-30","12:43:00",20001962,"Short Rural","Other","Fuse Operator - No Trigger Found",131,74.25,2.4069858081439199E-2,3.24173172813996E-4,"NO"]
[null,"2017-11-30","15:49:00",30053775,"Short Rural","Other","Service Fuse",1,45.533333333333303,1.12676985766901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-01","08:01:00",83897505,"Short Rural","Planned",null,32,114,0,0,"NO"]
[null,"2017-12-01","09:05:00",40000963,"Long Rural","Planned",null,45,224,0,0,"NO"]
[null,"2017-12-01","09:08:00",50000240,"Long Rural","Planned",null,2,173,0,0,"NO"]
[null,"2017-12-01","11:58:00",50000050,"Short Rural","Planned",null,2,81,0,0,"NO"]
[null,"2017-12-01","16:34:00",60026671,"Short Rural","Other","Service Fuse",1,147.88333333333301,3.6595274330516401E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-02","09:51:00",60026715,"Short Rural","Other","Service Fuse",2,152.333333333333,7.5392946552669897E-4,4.9492087452518498E-6,"NO"]
[null,"2017-12-02","15:23:00",20011487,"Short Rural","Asset failure","LV",48,225.8,2.6820752032268802E-2,1.18781009886044E-4,"NO"]
[null,"2017-12-02","16:12:00",60026666,"Long Rural","Weather",null,1,174.26666666666699,2.2791873746621297E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-02","23:34:00",60026709,"Urban","Other","Trip & Manual Reclose - No Trigger Found",1,26.8333333333333,1.18629730821036E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-03","00:40:00",60026758,"Short Rural","Weather",null,1,42.199999999999996,1.04428304524814E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-03","08:10:00",60026750,"Short Rural","Planned",null,5,334,0,0,"NO"]
[null,"2017-12-03","14:08:00",82912277,"Short Rural","Other","Service Fuse",1,57.566666666666698,1.4245472505083198E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-03","16:54:00",40001094,"Urban","Other","Service Fuse",1,130.71666666666698,5.7789626014247402E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-03","17:01:00",50000236,"Long Rural","Weather",null,2,33.033333333333303,8.6406835818292804E-4,2.61574679571018E-5,"NO"]
[null,"2017-12-04","07:14:00",40001011,"Long Rural","Animal","Animal impact",1,133.38333333333301,1.7444851338390402E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-04","09:00:00",30053830,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-12-04","10:00:00",40000966,"Long Rural","Planned",null,1,88,0,0,"NO"]
[null,"2017-12-04","12:38:00",40000960,"Short Rural","Weather",null,1,168,4.1573353460115599E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-04","16:18:00",25273354,"Urban","Other","Service Fuse",2,61.4,5.4289680539713696E-4,8.8419675146113493E-6,"NO"]
[null,"2017-12-04","22:41:00",84706956,"Short Rural","Third party","Fire",3,787.35,5.8451392583610696E-3,7.4238131178777803E-6,"NO"]
[null,"2017-12-05","08:30:00",60026830,"Short Rural","Planned",null,1,93,0,0,"NO"]
[null,"2017-12-05","09:01:00",20008373,"Short Rural","Planned",null,42,313.45238095238108,0,0,"NO"]
[null,"2017-12-05","12:33:00",30186258,"Urban","Planned",null,122,67,0,0,"NO"]
[null,"2017-12-05","17:13:00",50000093,"Long Rural","Animal","Animal impact",20,84.683333333333294,2.2151015781672299E-2,2.6157467957101799E-4,"NO"]
[null,"2017-12-05","17:53:00",20001246,"Short Rural","Animal","Animal impact",1,58.5,1.4476435579861699E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-06","08:30:00",25267836,"Short Rural","Planned",null,30,194,0,0,"NO"]
[null,"2017-12-06","09:00:00",25273274,"Short Rural","Planned",null,21,259,0,0,"NO"]
[null,"2017-12-06","09:20:00",50000214,"Urban","Planned",null,1,25,0,0,"NO"]
[null,"2017-12-06","12:46:00",30053819,"Short Rural","Planned",null,1,60.999999999999993,0,0,"NO"]
[null,"2017-12-06","16:10:00",40001210,"Long Rural","Other","Fuse Operator - No Trigger Found",1,74.716666666666711,9.7719940709739312E-4,1.30787339785509E-5,"NO"]
[null,"2017-12-06","19:48:00",20001263,"Short Rural","Other","Fuse Operator - No Trigger Found",2,38.6666666666667,1.9136940481640502E-4,4.9492087452518498E-6,"NO"]
[null,"2017-12-07","08:15:00",50000090,"Urban","Planned",null,2,90,0,0,"NO"]
[null,"2017-12-07","10:32:00",10020773,"Short Rural","Planned",null,2,95,0,0,"NO"]
[null,"2017-12-07","16:07:00",60026829,"Short Rural","Overloads",null,1,92.45,2.28777174249267E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-07","22:59:00",20006697,"Short Rural","Other","Trip & Auto Reclose - No Trigger Found",254,5.8500000000000005,3.67701463728486E-3,6.2854951064698504E-4,"NO"]
[null,"2017-12-08","07:50:00",30053878,"Short Rural","Other","Vibration",1,111.60000000000001,2.7616584798505298E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-08","09:00:00",30053825,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2017-12-08","09:30:00",84332230,"Short Rural","Planned",null,2,269,0,0,"NO"]
[null,"2017-12-08","12:54:00",30053868,"Short Rural","Animal","Animal impact",15,78,2.8952871159723297E-3,3.7119065589388895E-5,"NO"]
[null,"2017-12-08","16:11:00",10132684,"Long Rural","Asset failure","HV",174,189.56091954023,0.43138373005493102,2.2756997122678501E-3,"NO"]
[null,"2017-12-08","20:42:00",40000975,"Long Rural","Weather",null,3,203.25,7.9747580434214003E-3,3.9236201935652595E-5,"NO"]
[null,"2017-12-09","06:14:00",60026718,"Short Rural","Planned",null,24,175,0,0,"NO"]
[null,"2017-12-09","08:05:00",84653811,"Short Rural","Planned",null,10,194,0,0,"NO"]
[null,"2017-12-09","13:12:00",30053865,"Short Rural","Planned",null,2,4,0,0,"NO"]
[null,"2017-12-09","19:02:00",50000143,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",448,16,1.77379641429826E-2,1.1086227589364201E-3,"NO"]
[null,"2017-12-09","21:46:00",40001059,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",50,20.7,2.5612155256678299E-3,1.2373021863129599E-4,"NO"]
[null,"2017-12-10","01:21:00",60026771,"Long Rural","Animal","Animal impact",407,51.2181408681409,0.27263645479117599,5.3230447292702109E-3,"NO"]
[null,"2017-12-10","09:23:00",10134518,"Urban","Overloads",null,1,132.71666666666698,5.8673822765708498E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-10","13:09:00",82563612,"Long Rural","Asset failure","Distribution substation",1,1453.5333333333301,1.9010375795623004E-2,1.30787339785509E-5,"NO"]
[null,"2017-12-10","18:32:00",10020783,"Urban","Other","Service Fuse",1,346.18333333333305,1.5304708937166E-3,4.4209837573056797E-6,"NO"]
[null,"2017-12-11","08:26:00",60026783,"Long Rural","Animal","Animal impact",1,83.016666666666708,1.08575289911937E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-11","13:42:00",50000015,"Short Rural","Asset failure","LV",1,94.816666666666706,2.3463373793114801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-11","19:03:00",40001063,"Long Rural","Asset failure","Distribution substation",4,834.66666666666708,4.36655331763885E-2,5.2314935914203499E-5,"NO"]
[null,"2017-12-12","01:57:00",60026836,"Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,80.75,3.5699443840243297E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-12","08:30:00",60026678,"Short Rural","Planned",null,1,114.45,0,0,"NO"]
[null,"2017-12-12","09:35:00",30053745,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2017-12-12","11:06:00",82554035,"Short Rural","Other","Service Fuse",3,93.25,6.9227057324210302E-4,7.4238131178777803E-6,"NO"]
[null,"2017-12-12","16:00:00",82917286,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2017-12-12","19:49:00",30053808,"Short Rural","Animal","Animal impact",1,73.849999999999994,1.8274953291842503E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-13","07:26:00",50000206,"Urban","Other","Service Fuse",1,100.216666666667,4.4305625554465E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-13","09:04:00",30053785,"Short Rural","Planned",null,55,219,0,0,"NO"]
[null,"2017-12-13","11:45:00",10020785,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-12-13","14:02:00",30186550,"Urban","Other","Forced Corrective Maintenance",68,63.161764705882398,1.8988125237627902E-2,3.0062689549678601E-4,"NO"]
[null,"2017-12-14","08:00:00",10020782,"Short Rural","Planned",null,5,41,0,0,"NO"]
[null,"2017-12-14","08:30:00",82647120,"Short Rural","Planned",null,21,419,0,0,"NO"]
[null,"2017-12-14","10:10:00",60026667,"Long Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-12-14","14:08:00",60026666,"Long Rural","Overloads",null,2,211.51666666666699,5.5327404307263109E-3,2.61574679571018E-5,"NO"]
[null,"2017-12-14","15:15:00",30053746,"Short Rural","Other","Service Fuse",1,35.566666666666698,8.8013428853062097E-5,2.4746043726259304E-6,"NO"]
[null,"2017-12-14","21:45:00",20001148,"Urban","Asset failure","LV",1,146.80000000000001,6.4900041557247297E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-15","08:03:00",50000229,"Long Rural","Other","Forced Corrective Maintenance",2,31,8.1088150667015402E-4,2.61574679571018E-5,"NO"]
[null,"2017-12-15","09:00:00",60026711,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2017-12-15","10:55:00",60027003,"Long Rural","Planned",null,1,231,0,0,"NO"]
[null,"2017-12-16","04:13:00",10020824,"Short Rural","Animal","Animal impact",31,220.26666666666699,1.6897258550789201E-2,7.6712735551403687E-5,"NO"]
[null,"2017-12-16","12:26:00",25273358,"Urban","Other","Service Fuse",1,95.4,4.21761850446961E-4,4.4209837573056797E-6,"NO"]
[null,"2017-12-16","20:03:00",60026676,"Long Rural","Weather",null,1,774.80000000000007,1.0133403086581201E-2,1.30787339785509E-5,"NO"]
[null,"2017-12-17","08:30:00",60026801,"Short Rural","Planned",null,4,495,0,0,"NO"]
[null,"2017-12-17","16:40:00",30053778,"Long Rural","Exclusion - Customer Installation Fault",null,1,166.51666666666699,0,0,"NO"]
[null,"2017-12-18","00:42:00",40001096,"Urban","Animal","Other",31,102.933333333333,1.4107064437311901E-2,1.37050496476476E-4,"NO"]
[null,"2017-12-18","10:20:00",60026670,"Long Rural","Other","Forced Corrective Maintenance",17,35,7.7818467172377703E-3,2.2233847763536503E-4,"NO"]
[null,"2017-12-18","14:26:00",50000066,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2017-12-19","05:00:00",20008784,"Long Rural","Planned",null,36,32,0,0,"NO"]
[null,"2017-12-19","05:00:00",25268404,"Urban","Planned",null,159,32,0,0,"NO"]
[null,"2017-12-19","08:58:00",50000035,"Short Rural","Planned",null,19,236.25,0,0,"NO"]
[null,"2017-12-19","10:14:00",60026747,"Long Rural","Planned",null,4,283.33333333333303,0,0,"NO"]
[null,"2017-12-19","12:00:00",60026766,"Long Rural","Asset failure","LV",1,103.7,1.35626471357573E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-19","13:41:00",50000044,"Long Rural","Other","Fuse Operator - No Trigger Found",1,95.433333333333294,1.24814717935304E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-19","18:34:00",82912280,"Urban","Animal","Animal impact",79,117.7,4.1107633270555395E-2,3.4925771682714805E-4,"NO"]
[null,"2017-12-20","06:10:00",10020856,"Short Rural","Animal","Animal impact",1,67.683333333333294,1.6748947262056499E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-20","08:32:00",82912289,"Urban","Planned",null,23,140,0,0,"NO"]
[null,"2017-12-20","09:30:00",20010596,"Short Rural","Planned",null,14,328.92857142857105,0,0,"NO"]
[null,"2017-12-20","14:30:00",50000128,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2017-12-20","15:23:00",60026888,"Long Rural","Other","Service Fuse",1,114.566666666667,1.4983869561426501E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-21","00:39:00",20006383,"Long Rural","Animal","Animal impact",32,611,0.25571540674862697,4.1851948731362804E-4,"NO"]
[null,"2017-12-21","09:01:00",60026750,"Short Rural","Planned",null,21,259,0,0,"NO"]
[null,"2017-12-21","11:00:00",10020855,"Short Rural","Planned",null,8,142,0,0,"NO"]
[null,"2017-12-21","14:48:00",60026722,"Short Rural","Other","Forced Corrective Maintenance",2,21,1.0393338365028901E-4,4.9492087452518498E-6,"NO"]
[null,"2017-12-21","20:50:00",30053770,"Long Rural","Other","Service Fuse",1,61.4166666666667,8.0325224518266601E-4,1.30787339785509E-5,"NO"]
[null,"2017-12-22","08:24:00",82841186,"Short Rural","Planned",null,3,59,0,0,"NO"]
[null,"2017-12-22","10:47:00",60026745,"Short Rural","Weather",null,1,83.216666666666697,2.0592832720868801E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-22","21:11:00",40001100,"Short Rural","Other","Service Fuse",3,54.233333333333299,4.0261813142623804E-4,7.4238131178777803E-6,"NO"]
[null,"2017-12-23","12:10:00",40000985,"Long Rural","Overloads",null,2,126.333333333333,3.3045601185805202E-3,2.61574679571018E-5,"NO"]
[null,"2017-12-24","07:26:00",83022292,"Long Rural","Other","Fuse Operator - No Trigger Found",1,287.816666666667,3.76427761792658E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-24","17:47:00",60026747,"Long Rural","Other","Service Fuse",1,91.1,1.1914726654459801E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-24","19:53:00",60026670,"Long Rural","Overloads",null,1,126.466666666667,1.6540238904873999E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-25","14:15:00",60026662,"Long Rural","Other","Trip & Auto Reclose - No Trigger Found",16,1.6666666666666701,3.4876623942802301E-4,2.0925974365681402E-4,"NO"]
[null,"2017-12-25","17:25:00",84670339,"Short Rural","Other","Service Fuse",1,166.05,4.1090805607453502E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-25","17:59:00",60026662,"Long Rural","Other","Fuse Operator - No Trigger Found",1,1533.2833333333301,2.0053404830412399E-2,1.30787339785509E-5,"NO"]
[null,"2017-12-25","19:29:00",50000145,"Long Rural","Weather",null,2,285.63333333333304,7.4714447641468307E-3,2.61574679571018E-5,"NO"]
[null,"2017-12-26","06:06:00",60026821,"Long Rural","Weather",null,1,615.51666666666711,8.0501787426977105E-3,1.30787339785509E-5,"YES"]
[null,"2017-12-26","06:14:00",60026670,"Long Rural","Weather",null,1,375.73333333333306,4.91411631354085E-3,1.30787339785509E-5,"YES"]
[null,"2017-12-26","09:57:00",20010480,"Short Rural","Weather",null,105,133,3.4557850063721099E-2,2.5983345912572204E-4,"YES"]
[null,"2017-12-26","15:58:00",60026666,"Long Rural","Weather",null,1,1616.9,2.1147004969918899E-2,1.30787339785509E-5,"YES"]
[null,"2017-12-26","16:43:00",60026742,"Short Rural","Other","Fuse Operator - No Trigger Found",1,1918.2333333333302,4.7468685943834708E-3,2.4746043726259304E-6,"YES"]
[null,"2017-12-26","17:21:00",60026666,"Long Rural","Weather",null,2,1511.8333333333301,3.9545731973144996E-2,2.61574679571018E-5,"YES"]
[null,"2017-12-26","17:53:00",60026794,"Long Rural","Weather",null,1,146,1.9094951608684301E-3,1.30787339785509E-5,"YES"]
[null,"2017-12-26","18:17:00",60026985,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",90,14.5833333333333,3.2479182390715306E-3,2.2271439353633302E-4,"YES"]
[null,"2017-12-26","18:41:00",20005265,"Short Rural","Overloads",null,1,18.016666666666701,4.4584122113477098E-5,2.4746043726259304E-6,"YES"]
[null,"2017-12-26","19:27:00",60026888,"Long Rural","Overloads",null,1,896.6,1.1726392885168699E-2,1.30787339785509E-5,"YES"]
[null,"2017-12-26","20:17:00",50000040,"Long Rural","Asset failure","HV",335,365.18333333333305,1.6000054494724898,4.3813758828145409E-3,"YES"]
[null,"2017-12-26","22:11:00",50000233,"Short Rural","Weather",null,3,1050.7,7.8002004429541805E-3,7.4238131178777803E-6,"YES"]
[null,"2017-12-27","00:10:00",60026998,"Short Rural","Other","Fuse Operator - No Trigger Found",3,1241.55,9.2170351765011593E-3,7.4238131178777803E-6,"NO"]
[null,"2017-12-27","07:26:00",50000095,"Long Rural","Other","Fuse Operator - No Trigger Found",1,1695.3833333333303,2.2173467608335499E-2,1.30787339785509E-5,"NO"]
[null,"2017-12-27","08:29:00",50000130,"Long Rural","Weather",null,1,554.61666666666713,7.2536838434039607E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-27","09:53:00",50000125,"Long Rural","Weather",null,1,1374.7,1.7979335600313902E-2,1.30787339785509E-5,"NO"]
[null,"2017-12-27","10:33:00",50000094,"Long Rural","Overloads",null,4,1630.4333333333302,8.5296015345714501E-2,5.2314935914203499E-5,"NO"]
[null,"2017-12-27","13:27:00",50000241,"Long Rural","Weather",null,1,93.399999999999991,1.2215537535966499E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-27","15:31:00",25268404,"Urban","Other","Trip & Manual Reclose - No Trigger Found",158,31.866666666666699,2.2259358485783601E-2,6.9851543365429707E-4,"NO"]
[null,"2017-12-27","17:24:00",60026666,"Long Rural","Other","Fuse Operator - No Trigger Found",2,1126,2.9453308919696601E-2,2.61574679571018E-5,"NO"]
[null,"2017-12-27","19:00:00",40001116,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",397,142.9,0.74197358095736299,5.1922573894847002E-3,"NO"]
[null,"2017-12-28","04:45:00",40001065,"Short Rural","Animal","Animal impact",84,137.48333333333301,2.85782160577078E-2,2.0786676730057802E-4,"NO"]
[null,"2017-12-28","08:09:00",40000974,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",4,196.11666666666699,1.0259830848373902E-2,5.2314935914203499E-5,"NO"]
[null,"2017-12-28","09:40:00",60026666,"Long Rural","Other","Fuse Operator - No Trigger Found",1,235.683333333333,3.0824396198447998E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-28","11:33:00",60026666,"Long Rural","Other","Fuse Operator - No Trigger Found",1,234.75,3.0702328014648203E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-28","13:56:00",60026670,"Long Rural","Other","Service Fuse",1,2.8666666666666702,3.7492370738512501E-5,1.30787339785509E-5,"NO"]
[null,"2017-12-28","15:48:00",85068151,"Short Rural","Other","Forced Corrective Maintenance",2,18,8.90857574145334E-5,4.9492087452518498E-6,"NO"]
[null,"2017-12-28","19:28:00",50000211,"Short Rural","Other","Fuse Operator - No Trigger Found",1,111.033333333333,2.74763572173899E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-29","06:25:00",20008892,"Short Rural","Other","Fuse Operator - No Trigger Found",4,297.58333333333303,2.9456040715490602E-3,9.8984174905037098E-6,"NO"]
[null,"2017-12-29","09:19:00",30053774,"Short Rural","Other","Service Fuse",1,118.98333333333299,2.9443667693627496E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-29","15:05:00",50000093,"Long Rural","Other","Fuse Operator - No Trigger Found",4,117.783333333333,6.1618275350946005E-3,5.2314935914203499E-5,"NO"]
[null,"2017-12-29","20:13:00",50000049,"Short Rural","Other","Fuse Operator - No Trigger Found",51,90.366666666666703,1.1404709172121101E-2,1.2620482300392202E-4,"NO"]
[null,"2017-12-30","10:55:00",30053842,"Short Rural","Animal","Animal impact",1,94.066666666666706,2.3277778465167901E-4,2.4746043726259304E-6,"NO"]
[null,"2017-12-30","18:30:00",20005133,"Long Rural","Overloads",null,1,118.566666666667,1.5507018920568501E-3,1.30787339785509E-5,"NO"]
[null,"2017-12-30","19:41:00",30053878,"Short Rural","Other","Service Fuse",3,46.800000000000004,3.4743445391667999E-4,7.4238131178777803E-6,"NO"]
[null,"2017-12-31","03:42:00",60026682,"Long Rural","Weather",null,1,507.93333333333305,6.6431249455052802E-3,1.30787339785509E-5,"YES"]
[null,"2017-12-31","11:53:00",40001038,"Long Rural","Animal","Other",1,232.05,3.03492021972273E-3,1.30787339785509E-5,"YES"]
[null,"2017-12-31","13:48:00",10020828,"Long Rural","Asset failure","Distribution substation",1,281.18333333333305,3.6775220158688604E-3,1.30787339785509E-5,"YES"]
[null,"2017-12-31","16:00:00",60026701,"Long Rural","Asset failure","HV",32,376.01666666666705,0.15737030255471299,4.1851948731362804E-4,"YES"]
[null,"2017-12-31","16:58:00",60026892,"Long Rural","Asset failure","Distribution substation",1,1166.9333333333302,1.52620106373703E-2,1.30787339785509E-5,"YES"]
[null,"2017-12-31","17:49:00",50000028,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",112,102.60000000000001,2.8436173766718999E-2,2.7715568973410399E-4,"YES"]
[null,"2017-12-31","18:33:00",50000148,"Short Rural","Weather",null,1,1211.4666666666701,2.99790071062389E-3,2.4746043726259304E-6,"YES"]
[null,"2017-12-31","19:41:00",50000241,"Long Rural","Asset failure","Distribution substation",2,213.25,5.5780800418519499E-3,2.61574679571018E-5,"YES"]
[null,"2017-12-31","21:09:00",40000960,"Short Rural","Weather",null,20,211,1.04428304524814E-2,4.94920874525185E-5,"YES"]
[null,"2017-12-31","23:04:00",84119480,"Short Rural","Weather",null,1,953.5,2.3595352692988201E-3,2.4746043726259304E-6,"YES"]
[null,"2018-01-01","05:29:00",40000973,"Long Rural","Other","Fuse Operator - No Trigger Found",1,434.63333333333304,5.6844537448775007E-3,1.30787339785509E-5,"YES"]
[null,"2018-01-01","07:02:00",50000073,"Short Rural","Weather",null,1,149.63333333333301,3.7028330095725901E-4,2.4746043726259304E-6,"YES"]
[null,"2018-01-01","08:25:00",40000977,"Long Rural","Weather",null,1,254.183333333333,3.3243961984479905E-3,1.30787339785509E-5,"YES"]
[null,"2018-01-01","10:34:00",50000015,"Short Rural","Weather",null,1,1754.0333333333301,4.3405385563983004E-3,2.4746043726259304E-6,"YES"]
[null,"2018-01-01","14:10:00",40000970,"Short Rural","Overloads",null,4,72.3333333333333,7.1598553181310097E-4,9.8984174905037098E-6,"YES"]
[null,"2018-01-01","15:45:00",10020663,"Urban","Asset failure","LV",55,344.61666666666702,8.3794957720658703E-2,2.4315410665181201E-4,"YES"]
[null,"2018-01-01","16:48:00",25275177,"Urban","Other","Service Fuse",2,177.816666666667,1.5722491902231399E-3,8.8419675146113493E-6,"YES"]
[null,"2018-01-01","16:54:00",40000962,"Long Rural","Weather",null,1,1053.0166666666703,1.37721248583137E-2,1.30787339785509E-5,"YES"]
[null,"2018-01-01","17:34:00",10020808,"Urban","Other","Service Fuse",1,126.866666666667,5.6087547267684695E-4,4.4209837573056797E-6,"YES"]
[null,"2018-01-01","18:24:00",40000967,"Short Rural","Weather",null,2,1631.8500000000001,8.0763662909392395E-3,4.9492087452518498E-6,"YES"]
[null,"2018-01-01","18:51:00",50000053,"Long Rural","Weather",null,16,4.2166666666666694,8.8237858575289905E-4,2.0925974365681402E-4,"YES"]
[null,"2018-01-01","18:54:00",25272945,"Short Rural","Weather",null,20,6.7166666666666694,3.3242185405608297E-4,4.94920874525185E-5,"YES"]
[null,"2018-01-01","19:27:00",40001202,"Urban","Asset failure","LV",2,978.78333333333308,8.6543704371763504E-3,8.8419675146113493E-6,"YES"]
[null,"2018-01-01","19:42:00",40001111,"Long Rural","Asset failure","Subtransmission",437,289.33333333333303,1.6536576859359999,5.7154067486267302E-3,"YES"]
[null,"2018-01-01","20:18:00",40001201,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",37,81,7.4163893047599003E-3,9.1560361787159283E-5,"YES"]
[null,"2018-01-01","23:02:00",50000053,"Long Rural","Other","Fuse Operator - No Trigger Found",1,670.56666666666706,8.7701630482169314E-3,1.30787339785509E-5,"YES"]
[null,"2018-01-02","01:01:00",40001110,"Short Rural","Overloads",null,1,719.9,1.7814676878534002E-3,2.4746043726259304E-6,"YES"]
[null,"2018-01-02","06:19:00",40001115,"Short Rural","Asset failure","Distribution substation",3,438.75,3.2571980054688803E-3,7.4238131178777803E-6,"YES"]
[null,"2018-01-02","06:50:00",40000964,"Long Rural","Weather",null,4,564.53333333333308,2.9533525154765001E-2,5.2314935914203499E-5,"YES"]
[null,"2018-01-02","08:00:00",40001210,"Long Rural","Weather",null,1,38.6,5.0483913157206399E-4,1.30787339785509E-5,"YES"]
[null,"2018-01-02","08:34:00",10020780,"Short Rural","7 - STPIS Exclusion (3.3)(a)",null,665,80,0,0,"YES"]
[null,"2018-01-02","09:32:00",60026755,"Long Rural","Weather",null,1,122.23333333333299,1.5986572499782001E-3,1.30787339785509E-5,"YES"]
[null,"2018-01-02","10:51:00",60026771,"Long Rural","Asset failure","HV",1,232.11666666666699,3.0357921353213004E-3,1.30787339785509E-5,"YES"]
[null,"2018-01-02","11:38:00",40001177,"Short Rural","Weather",null,1,93.15,2.3050939731010501E-4,2.4746043726259304E-6,"YES"]
[null,"2018-01-02","14:03:00",10020836,"Short Rural","Other","Service Fuse",1,67.133333333333297,1.6612844021562101E-4,2.4746043726259304E-6,"YES"]
[null,"2018-01-02","14:15:00",84332614,"Short Rural","Other","Forced Corrective Maintenance",17,71,2.9868474777594899E-3,4.2068274334640702E-5,"YES"]
[null,"2018-01-02","15:52:00",40000974,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",686,14.1,0.12650536228093101,8.9720115092858984E-3,"YES"]
[null,"2018-01-02","16:27:00",50000233,"Short Rural","Weather",null,1,1381.2333333333302,3.4180060462833499E-3,2.4746043726259304E-6,"YES"]
[null,"2018-01-02","16:33:00",20007736,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",56,1132.6000000000001,0.82952654982997598,7.3240910279884902E-4,"YES"]
[null,"2018-01-02","17:04:00",40001112,"Short Rural","Weather",null,218,5.3666666666666689,2.8951221423474897E-3,5.3946375323245201E-4,"YES"]
[null,"2018-01-02","17:09:00",25268407,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",135,19.3,6.4475816928768505E-3,3.3407159030450002E-4,"YES"]
[null,"2018-01-02","17:32:00",20011126,"Long Rural","Weather",null,1,1147.6833333333302,1.5010245008283202E-2,1.30787339785509E-5,"YES"]
[null,"2018-01-02","17:55:00",50000025,"Long Rural","Asset failure","Distribution substation",2,905.11666666666713,2.3675560205772102E-2,2.61574679571018E-5,"YES"]
[null,"2018-01-02","18:29:00",40001227,"Short Rural","Weather",null,422,39.116666666666696,4.0848871786623102E-2,1.0442830452481401E-3,"YES"]
[null,"2018-01-02","18:46:00",85221946,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1714,11.0666666666667,4.6938955634467899E-2,4.24147189468084E-3,"YES"]
[null,"2018-01-02","18:47:00",50000133,"Long Rural","Weather",null,2,1070.6833333333302,2.8006364983869603E-2,2.61574679571018E-5,"YES"]
[null,"2018-01-02","20:26:00",40001208,"Long Rural","Weather",null,1,874.78333333333308,1.14410585055367E-2,1.30787339785509E-5,"YES"]
[null,"2018-01-02","21:11:00",30053770,"Long Rural","Other","Fuse Operator - No Trigger Found",1,99.8333333333333,1.3056936088586602E-3,1.30787339785509E-5,"YES"]
[null,"2018-01-03","06:40:00",82563612,"Long Rural","Animal","Animal impact",1,282.40000000000003,3.6934344755427703E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-03","07:29:00",40216323,"Long Rural","Other","Fuse Operator - No Trigger Found",1,361.51666666666705,4.7281803121457799E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-03","08:31:00",20013273,"Short Rural","Other","Service Fuse",1,260.11666666666702,6.4368584072621398E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-03","09:02:00",60026994,"Long Rural","Planned",null,25,68,0,0,"NO"]
[null,"2018-01-03","09:57:00",20005605,"Urban","Other","Service Fuse",1,111.283333333333,4.9198180912549995E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-03","11:34:00",40223076,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",3,186.4,7.3136280408056496E-3,3.9236201935652595E-5,"NO"]
[null,"2018-01-03","14:09:00",50000128,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",133,55.816666666666698,1.8370514264031999E-2,3.2912238155924801E-4,"NO"]
[null,"2018-01-03","15:00:00",50000053,"Long Rural","Other","Forced Corrective Maintenance",1,115,1.5040544075333501E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-03","15:29:00",84041077,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",109,125.833333333333,3.3941261140875104E-2,2.6973187661622595E-4,"NO"]
[null,"2018-01-03","17:34:00",60026832,"Short Rural","Asset failure","HV",1,2579.9666666666703,6.3843967945624702E-3,2.4746043726259304E-6,"NO"]
[null,"2018-01-03","18:33:00",50000184,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",285,18.933333333333298,1.3352965194689502E-2,7.0526224619838905E-4,"NO"]
[null,"2018-01-03","19:00:00",20010961,"Short Rural","Asset failure","Subtransmission",205,42.699999999999996,2.1661449375780999E-2,5.0729389638831494E-4,"NO"]
[null,"2018-01-03","20:40:00",50000180,"Short Rural","Weather",null,1,106.866666666667,2.6445272062129097E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-04","05:33:00",20004054,"Long Rural","Asset failure","HV",1,140.01666666666699,1.83124073589677E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-04","07:31:00",30053783,"Urban","Overloads",null,2,91.7,8.10808421089861E-4,8.8419675146113493E-6,"NO"]
[null,"2018-01-04","09:00:00",10020722,"Short Rural","Weather",null,1,60.633333333333304,1.50043511793552E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-04","09:48:00",10020670,"Long Rural","Other","Fuse Operator - No Trigger Found",1,139.31666666666698,1.82208562211178E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-04","12:22:00",40000977,"Long Rural","Weather",null,1,127.566666666667,1.66841049786381E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-04","14:10:00",82554035,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2018-01-04","16:24:00",10020828,"Long Rural","Other","Service Fuse",2,38.033333333333303,9.9485569796843717E-4,2.61574679571018E-5,"NO"]
[null,"2018-01-04","17:56:00",40001090,"Urban","Overloads",null,1,48.966666666666697,2.1648083798273503E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-04","19:24:00",50000016,"Short Rural","Weather",null,1,107.3,2.6552504918276199E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-04","21:05:00",40000974,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",3,1008,3.9550091551137805E-2,3.9236201935652595E-5,"NO"]
[null,"2018-01-05","05:56:00",40001062,"Long Rural","Asset failure","HV",23,729.21666666666715,0.21935630830935599,3.0081088150667E-4,"NO"]
[null,"2018-01-05","08:00:00",30053841,"Short Rural","Planned",null,12,120,0,0,"NO"]
[null,"2018-01-05","08:36:00",60026994,"Long Rural","Planned",null,7,69,0,0,"NO"]
[null,"2018-01-05","10:45:00",40001190,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2018-01-05","14:06:00",50000027,"Short Rural","Other","Fuse Operator - No Trigger Found",1,85.966666666666697,2.1273348923340899E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-05","15:43:00",60026987,"Short Rural","Other","Service Fuse",3,131.36666666666699,9.7524158325187796E-4,7.4238131178777803E-6,"NO"]
[null,"2018-01-05","18:53:00",40000961,"Long Rural","Overloads",null,1,53.716666666666697,7.0254599354782502E-4,1.30787339785509E-5,"NO"]
[null,"2018-01-05","23:16:00",20006383,"Long Rural","Asset failure","Distribution substation",26,846.43076923076899,0.28782631441276507,3.4004708344232299E-4,"NO"]
[null,"2018-01-06","08:45:00",83896573,"Short Rural","Other","Service Fuse",1,185.45000000000002,4.5891538090347798E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-06","09:52:00",84965685,"Short Rural","Other","Service Fuse",1,113.366666666667,2.8053764904335902E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-06","15:40:00",30053808,"Short Rural","Other","Fuse Operator - No Trigger Found",1,149.88333333333301,3.7090195205041597E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-07","08:00:00",60026688,"Short Rural","Planned",null,83,152,0,0,"NO"]
[null,"2018-01-07","18:21:00",40000977,"Long Rural","Other","Fuse Operator - No Trigger Found",1,135.35,1.77020664399686E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-08","06:07:00",50000150,"Short Rural","Asset failure","Distribution substation",1,156.70000000000002,3.8777050519048299E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-08","08:30:00",60026676,"Long Rural","Planned",null,1,73,0,0,"NO"]
[null,"2018-01-08","11:35:00",40001193,"Short Rural","Other","Fuse Operator - No Trigger Found",2,51.4,2.5438932950594498E-4,4.9492087452518498E-6,"NO"]
[null,"2018-01-08","14:28:00",60026735,"Short Rural","Weather",null,1,63.15,1.56271266131327E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-08","18:18:00",20009684,"Short Rural","Asset failure","HV",1,63.8333333333333,1.57962245785955E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-09","07:18:00",20011824,"Long Rural","Other","Service Fuse",1,460.63333333333304,6.0245008283198202E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-09","08:51:00",20008892,"Short Rural","Animal","Animal impact",1,40.216666666666697,9.9520339185772699E-5,2.4746043726259304E-6,"NO"]
[null,"2018-01-09","09:10:00",40223073,"Long Rural","Planned",null,3,10,0,0,"NO"]
[null,"2018-01-09","10:37:00",40000965,"Short Rural","Other","Service Fuse",3,60.050000000000004,4.4579997772856101E-4,7.4238131178777803E-6,"NO"]
[null,"2018-01-09","13:30:00",50000229,"Long Rural","Exclusion - Customer Installation Fault",null,1,23,0,0,"NO"]
[null,"2018-01-09","19:20:00",50000033,"Short Rural","Other","Service Fuse",1,50.699999999999996,1.2546244169213403E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-10","08:30:00",10020778,"Short Rural","Planned",null,38,293.15789473684202,0,0,"NO"]
[null,"2018-01-10","08:34:00",82921017,"Urban","Other","Service Fuse",3,154.26666666666699,2.0460312828810699E-3,1.3262951271916999E-5,"NO"]
[null,"2018-01-10","09:30:00",40001033,"Long Rural","Other","Forced Corrective Maintenance",7,68,6.2254773737902202E-3,9.1551137849856101E-5,"NO"]
[null,"2018-01-10","11:20:00",40001010,"Long Rural","Other","Forced Corrective Maintenance",1,98,1.2817159298979899E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-10","12:25:00",82552955,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-01-10","15:16:00",50000033,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2018-01-10","15:55:00",20009515,"Short Rural","Other","Service Fuse",3,191.53333333333299,1.42190767251086E-3,7.4238131178777803E-6,"NO"]
[null,"2018-01-11","05:04:00",30053815,"Urban","Planned",null,27,34,0,0,"NO"]
[null,"2018-01-11","08:38:00",10020855,"Short Rural","Planned",null,6,219,0,0,"NO"]
[null,"2018-01-11","09:35:00",60026990,"Long Rural","Weather",null,1,332.7,4.3512947946638802E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-11","10:00:00",20011865,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2018-01-11","12:20:00",82556069,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2018-01-11","13:02:00",82914591,"Urban","Other","Service Fuse",1,81.733333333333306,3.61341739097117E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-11","16:17:00",20007634,"Long Rural","Other","Service Fuse",1,1096.6000000000001,1.43421396808789E-2,1.30787339785509E-5,"NO"]
[null,"2018-01-12","06:05:00",50000016,"Short Rural","Weather",null,1,294.86666666666702,7.29678342674965E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-12","08:17:00",60026703,"Short Rural","Weather",null,1,42.699999999999996,1.05665606711127E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-12","09:02:00",50000016,"Short Rural","Weather",null,1,145.35,3.5968374556117797E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-12","10:00:00",40001067,"Urban","Planned",null,1,44,0,0,"NO"]
[null,"2018-01-12","14:03:00",25268413,"Long Rural","Weather",null,27,1382.99444444444,0.48837104368297102,3.5312581742087402E-4,"NO"]
[null,"2018-01-12","17:37:00",50000050,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",506,178.11666666666699,0.22302875077846901,1.2521498125487199E-3,"NO"]
[null,"2018-01-13","07:31:00",50000035,"Short Rural","Other","Forced Corrective Maintenance",1,9,2.2271439353633299E-5,2.4746043726259304E-6,"NO"]
[null,"2018-01-13","11:38:00",60027001,"Short Rural","Weather",null,1,78.816666666666706,1.9504006796913301E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-13","15:47:00",50000125,"Long Rural","Other","Fuse Operator - No Trigger Found",1,67.933333333333294,8.8848199494289011E-4,1.30787339785509E-5,"NO"]
[null,"2018-01-13","23:00:00",10020857,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",215,18.766666666666701,9.9846162094835104E-3,5.3203994011457396E-4,"NO"]
[null,"2018-01-14","10:13:00",40001004,"Urban","Overloads",null,1,49.5833333333333,2.1920711129974E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-14","13:12:00",40001004,"Urban","Overloads",null,3,47.133333333333304,6.2512710328302293E-4,1.3262951271916999E-5,"NO"]
[null,"2018-01-14","17:54:00",20002267,"Short Rural","Asset failure","LV",1,152.63333333333301,3.77707114075137E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-14","20:33:00",10020674,"Long Rural","Weather",null,61,1038.1647540983599,0.82825071933036909,7.9780277269160299E-4,"NO"]
[null,"2018-01-15","07:38:00",30053773,"Short Rural","Other","Fuse Operator - No Trigger Found",1,44.849999999999994,1.10986006112273E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-15","07:45:00",30053847,"Short Rural","Weather",null,2,180.61666666666699,8.9390958620490506E-4,4.9492087452518498E-6,"NO"]
[null,"2018-01-15","09:21:00",60026889,"Long Rural","Weather",null,1,448.11666666666702,5.8607986746882909E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-15","12:26:00",60026641,"Long Rural","Overloads",null,1,280.73333333333301,3.6716365855785204E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-15","15:27:00",60026705,"Short Rural","Weather",null,1,83.383333333333297,2.0634076127079202E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-15","16:48:00",20006599,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1,18.683333333333298,4.6233858361894396E-5,2.4746043726259304E-6,"NO"]
[null,"2018-01-15","18:50:00",20010596,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",41,8.65,8.7761844075178504E-4,1.0145877927766301E-4,"NO"]
[null,"2018-01-15","20:36:00",20004937,"Long Rural","Overloads",null,1,819.35,1.07160606853257E-2,1.30787339785509E-5,"NO"]
[null,"2018-01-15","23:57:00",20006212,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",240,28.1666666666667,1.6728325558951301E-2,5.93905049430222E-4,"NO"]
[null,"2018-01-16","03:39:00",30053776,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",308,70.066666666666706,5.3403282150266206E-2,7.6217814676878503E-4,"NO"]
[null,"2018-01-16","07:51:00",20004081,"Short Rural","Other","Service Fuse",1,301.48333333333306,7.46051974940506E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-16","08:42:00",50000177,"Short Rural","Planned",null,39,303.564102564103,0,0,"NO"]
[null,"2018-01-16","09:03:00",40001170,"Short Rural","Planned",null,1,177,0,0,"NO"]
[null,"2018-01-16","09:50:00",60026676,"Long Rural","Planned",null,1,125,0,0,"NO"]
[null,"2018-01-16","11:00:00",20002698,"Short Rural","Planned",null,1,47.999999999999993,0,0,"NO"]
[null,"2018-01-16","11:45:00",30053747,"Short Rural","Other","Fuse Operator - No Trigger Found",3,425.03333333333302,3.1553680355353203E-3,7.4238131178777803E-6,"NO"]
[null,"2018-01-16","13:31:00",20005919,"Urban","Asset failure","Distribution substation",9,68.400000000000006,2.7215576009973702E-3,3.9788853815751098E-5,"NO"]
[null,"2018-01-16","16:13:00",20004937,"Long Rural","Asset failure","HV",52,1154.0589743589699,0.78486877670241495,6.8009416688464598E-4,"NO"]
[null,"2018-01-16","18:26:00",20008784,"Long Rural","Weather",null,24,2044.0826388888902,0.64161631354084891,3.1388961548522103E-4,"NO"]
[null,"2018-01-17","07:30:00",30187348,"Short Rural","Planned",null,11,270,0,0,"NO"]
[null,"2018-01-17","08:35:00",83896573,"Short Rural","Planned",null,7,52,0,0,"NO"]
[null,"2018-01-17","09:20:00",40001060,"Short Rural","Planned",null,3,10,0,0,"NO"]
[null,"2018-01-17","11:20:00",40001236,"Urban","Planned",null,2,20,0,0,"NO"]
[null,"2018-01-17","13:41:00",30053776,"Short Rural","Other","Forced Corrective Maintenance",36,13,1.1581148463889301E-3,8.90857574145334E-5,"NO"]
[null,"2018-01-17","16:59:00",85068151,"Short Rural","Other","Forced Corrective Maintenance",1,71,1.7569691045644101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-18","07:20:00",10130408,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2018-01-18","08:30:00",50000229,"Long Rural","Planned",null,1563,318,0,0,"NO"]
[null,"2018-01-18","09:14:00",50000073,"Short Rural","Other","Service Fuse",1,287.98333333333301,7.1264481591005611E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-18","12:27:00",20006697,"Short Rural","Other","Service Fuse",1,146.6,3.6277700102696096E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-18","12:40:00",20005787,"Short Rural","Asset failure","HV",7,194.15,3.3631110726172705E-3,1.7322230608381499E-5,"NO"]
[null,"2018-01-18","15:43:00",60026733,"Long Rural","Weather",null,2,293.8,7.6850640857964898E-3,2.61574679571018E-5,"NO"]
[null,"2018-01-19","08:00:00",30053782,"Short Rural","Planned",null,9,128.05000000000001,0,0,"NO"]
[null,"2018-01-19","09:00:00",82563117,"Short Rural","Planned",null,5,240,0,0,"NO"]
[null,"2018-01-19","10:00:00",60026730,"Urban","Planned",null,8,105,0,0,"NO"]
[null,"2018-01-19","13:15:00",50000092,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2018-01-19","21:14:00",60327170,"Long Rural","Other","Service Fuse",1,83.55,1.09272822390793E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-20","00:22:00",40001184,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",134,40.316666666666698,1.33688851494867E-2,3.3159698593187399E-4,"NO"]
[null,"2018-01-20","09:00:00",50000073,"Short Rural","Other","Forced Corrective Maintenance",1,49,1.2125561425867E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-20","16:47:00",40000970,"Short Rural","Asset failure","LV",5,101.433333333333,1.2550368509834501E-3,1.2373021863129598E-5,"NO"]
[null,"2018-01-21","08:53:00",83864041,"Short Rural","Weather",null,1,117.666666666667,2.9117844784565098E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-21","12:11:00",50000074,"Short Rural","Asset failure","LV",1,108.15,2.6762846289949402E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-22","08:49:00",60026821,"Long Rural","Asset failure","LV",1,146.03333333333299,1.9099311186677101E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-22","10:50:00",50000050,"Short Rural","Other","Fuse Operator - No Trigger Found",1,286.88333333333304,7.0992275110016794E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-22","14:12:00",50000154,"Short Rural","Other","Service Fuse",1,107.083333333333,2.6498888490202602E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-22","21:46:00",30053817,"Urban","Asset failure","LV",2,141.48333333333301,1.2509910371922602E-3,8.8419675146113493E-6,"NO"]
[null,"2018-01-23","07:19:00",50000169,"Short Rural","Other","Service Fuse",4,93.15,9.2203758924042003E-4,9.8984174905037098E-6,"NO"]
[null,"2018-01-23","08:30:00",10020778,"Short Rural","Planned",null,50,233.12,0,0,"NO"]
[null,"2018-01-23","09:08:00",60026715,"Short Rural","Planned",null,5,124,0,0,"NO"]
[null,"2018-01-23","10:58:00",50000036,"Short Rural","Overloads",null,1,207.4,5.132329468826171E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-23","17:09:00",10020804,"Short Rural","Other","Service Fuse",2,67.383333333333297,3.3349418261755404E-4,4.9492087452518498E-6,"NO"]
[null,"2018-01-24","05:50:00",30053824,"Urban","Asset failure","LV",1,239.65,1.0594887574383099E-3,4.4209837573056797E-6,"NO"]
[null,"2018-01-24","08:30:00",50000125,"Long Rural","Planned",null,46,328,0,0,"NO"]
[null,"2018-01-24","09:00:00",50000095,"Long Rural","Planned",null,12,355.5,0,0,"NO"]
[null,"2018-01-24","10:12:00",40001004,"Urban","Other","Service Fuse",1,68.8,3.0416368250263002E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-24","11:33:00",60026781,"Urban","Planned",null,3,52,0,0,"NO"]
[null,"2018-01-24","14:33:00",60026755,"Long Rural","Other","Service Fuse",1,79.55,1.04041328799372E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-24","22:09:00",30053831,"Urban","Other","Fuse Operator - No Trigger Found",1,79.05,3.4947876601501402E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-25","01:07:00",10020804,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",5,464.90000000000003,5.7522178641689703E-3,1.2373021863129598E-5,"NO"]
[null,"2018-01-25","08:30:00",10020845,"Short Rural","Planned",null,23,150,0,0,"NO"]
[null,"2018-01-25","09:10:00",40001065,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2018-01-25","11:02:00",50000167,"Short Rural","Planned",null,2,4,0,0,"NO"]
[null,"2018-01-25","17:16:00",50000186,"Short Rural","Other","Forced Corrective Maintenance",69,54,9.2203758924041986E-3,1.70747701711189E-4,"NO"]
[null,"2018-01-25","20:49:00",82563086,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",148,24.933333333333298,9.131620082239349E-3,3.6624144714863702E-4,"NO"]
[null,"2018-01-26","09:05:00",10020662,"Short Rural","Other","Forced Corrective Maintenance",5,29,3.5881763403075904E-4,1.2373021863129598E-5,"NO"]
[null,"2018-01-26","16:11:00",60026735,"Short Rural","Other","Fuse Operator - No Trigger Found",5,268.066666666667,3.3167947274429501E-3,1.2373021863129598E-5,"NO"]
[null,"2018-01-26","18:15:00",60026994,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",4,85.100000000000009,4.4520010462987206E-3,5.2314935914203499E-5,"NO"]
[null,"2018-01-27","08:01:00",10020837,"Short Rural","Animal","Animal impact",1,44.816666666666698,1.10903519299852E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-27","17:59:00",50000025,"Long Rural","Animal","Animal impact",1,53.883333333333304,7.0472578254425001E-4,1.30787339785509E-5,"NO"]
[null,"2018-01-27","18:41:00",25280122,"Short Rural","Overloads",null,25,83.8333333333333,5.1863583309618398E-3,6.18651093156482E-5,"NO"]
[null,"2018-01-28","09:44:00",60026740,"Short Rural","Weather",null,1,68.933333333333294,1.7058272808634701E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-28","19:40:00",50000232,"Short Rural","Overloads",null,2,142.833333333333,7.0691198244680605E-4,4.9492087452518498E-6,"NO"]
[null,"2018-01-29","08:50:00",50000167,"Short Rural","Other","Forced Corrective Maintenance",2,103,5.0976850076094103E-4,4.9492087452518498E-6,"NO"]
[null,"2018-01-29","09:20:00",20002622,"Short Rural","Planned",null,3,60,0,0,"NO"]
[null,"2018-01-29","13:03:00",10020670,"Long Rural","Other","Forced Corrective Maintenance",2,45.999999999999993,1.20324352602668E-3,2.61574679571018E-5,"NO"]
[null,"2018-01-29","16:10:00",50000139,"Short Rural","Other","Service Fuse",1,90.6666666666667,2.2436412978475102E-4,2.4746043726259304E-6,"NO"]
[null,"2018-01-29","21:59:00",50000015,"Short Rural","Other","Forced Corrective Maintenance",26,99,6.3696316551391293E-3,6.4339713688274083E-5,"NO"]
[null,"2018-01-30","08:31:00",50000185,"Short Rural","Planned",null,3,101,0,0,"NO"]
[null,"2018-01-30","10:07:00",85081026,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-01-30","12:30:00",50000108,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-01-30","14:48:00",25275177,"Urban","Other","Fuse Operator - No Trigger Found",2,31.1666666666667,2.7557465420538697E-4,8.8419675146113493E-6,"NO"]
[null,"2018-01-30","17:10:00",40000967,"Short Rural","Asset failure","Distribution substation",12,208.96388888888902,6.2052354379843501E-3,2.9695252471511097E-5,"NO"]
[null,"2018-01-30","19:31:00",10020780,"Short Rural","Asset failure","LV",41,92.316666666666706,9.3663363069829194E-3,1.0145877927766301E-4,"NO"]
[null,"2018-01-31","08:30:00",10020777,"Short Rural","Planned",null,8,310,0,0,"NO"]
[null,"2018-01-31","08:40:00",60026675,"Long Rural","Overloads",null,1,295.11666666666702,3.85975237597001E-3,1.30787339785509E-5,"NO"]
[null,"2018-01-31","10:01:00",82563120,"Urban","Asset failure","LV",1,127.533333333333,5.6382279518171698E-4,4.4209837573056797E-6,"NO"]
[null,"2018-01-31","11:58:00",84332230,"Short Rural","Overloads",null,40,33.4166666666667,3.3077211780766502E-3,9.8984174905037095E-5,"NO"]
[null,"2018-01-31","13:40:00",60026790,"Short Rural","Other","Service Fuse",2,1069.7166666666701,5.2942510816083293E-3,4.9492087452518498E-6,"NO"]
[null,"2018-01-31","18:29:00",83877404,"Urban","Other","Fuse Operator - No Trigger Found",140,65.216666666666711,4.0365055365453296E-2,6.1893772602279501E-4,"NO"]
[null,"2018-02-01","06:31:00",50000124,"Short Rural","Other","Service Fuse",2,112.833333333333,5.5843572008925106E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-01","08:35:00",20013260,"Short Rural","2 or 3 - STPIS Exclusion (3.3)(a)",null,5,234.13333333333301,0,0,"NO"]
[null,"2018-02-01","09:17:00",30053832,"Short Rural","Asset failure","LV",96,262.01666666666705,6.22452085472835E-2,2.37562019772089E-4,"NO"]
[null,"2018-02-01","10:20:00",82564447,"Urban","Other","Fuse Operator - No Trigger Found",3,79.683333333333294,1.0568361671839199E-3,1.3262951271916999E-5,"NO"]
[null,"2018-02-01","12:35:00",50000229,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-02-01","14:11:00",60026783,"Long Rural","Other","Forced Corrective Maintenance",289,43.595155709342599,0.164778969395762,3.7797541198012004E-3,"NO"]
[null,"2018-02-01","17:06:00",40223073,"Long Rural","Asset failure","HV",14,981.98333333333312,0.17980338303252202,1.8310227569971198E-4,"NO"]
[null,"2018-02-02","03:23:00",20004307,"Long Rural","Animal","Animal impact",96,219.12239583333303,0.27512097828930204,1.2555584619408802E-3,"NO"]
[null,"2018-02-02","07:03:00",10020839,"Urban","Planned",null,2,7,0,0,"NO"]
[null,"2018-02-02","09:00:00",84332230,"Short Rural","Planned",null,4,390.25,0,0,"NO"]
[null,"2018-02-02","09:32:00",50000025,"Long Rural","Planned",null,1,183,0,0,"NO"]
[null,"2018-02-02","14:05:00",50000229,"Long Rural","Planned",null,1,25,0,0,"NO"]
[null,"2018-02-02","17:56:00",40001072,"Long Rural","Overloads",null,1,68.616666666666703,8.9741912982823301E-4,1.30787339785509E-5,"NO"]
[null,"2018-02-02","18:51:00",20001196,"Urban","Other","Service Fuse",2,33.966666666666697,3.0033216324629902E-4,8.8419675146113493E-6,"NO"]
[null,"2018-02-03","07:37:00",40216325,"Short Rural","Other","Fuse Operator - No Trigger Found",1,35.75,8.8467106321376906E-5,2.4746043726259304E-6,"NO"]
[null,"2018-02-03","11:35:00",10020827,"Short Rural","Other","Service Fuse",1,398.38333333333304,9.8584113864795932E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-03","14:32:00",40001045,"Short Rural","Weather",null,1,102.55,2.5377067841278895E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-03","18:31:00",10020673,"Long Rural","Weather",null,5,43.183333333333302,2.82391664486878E-3,6.5393669892754389E-5,"NO"]
[null,"2018-02-03","22:21:00",20007634,"Long Rural","Asset failure","HV",23,1247,0.37511116923881799,3.0081088150667E-4,"NO"]
[null,"2018-02-04","10:25:00",20004592,"Short Rural","Overloads",null,1,125.466666666667,3.10480361952133E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-04","10:39:00",20004796,"Short Rural","Other","Service Fuse",1,131.63333333333301,3.2574042224999298E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-05","08:20:00",10020778,"Short Rural","Animal","Animal impact",1,120.76666666666701,2.9884972140079106E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-05","10:38:00",60026641,"Long Rural","Planned",null,1,56,0,0,"NO"]
[null,"2018-02-05","12:55:00",50000196,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-02-05","14:56:00",60026990,"Long Rural","Asset failure","LV",1,201.05,2.6294794663876504E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-06","08:00:00",20001488,"Short Rural","Planned",null,41,292,0,0,"NO"]
[null,"2018-02-06","08:30:00",60026820,"Urban","Planned",null,11,180,0,0,"NO"]
[null,"2018-02-06","09:36:00",60027003,"Long Rural","Planned",null,1,295,0,0,"NO"]
[null,"2018-02-06","11:42:00",50000192,"Urban","Other","Service Fuse",1,112.7,4.9824486944835002E-4,4.4209837573056797E-6,"NO"]
[null,"2018-02-06","16:04:00",20008892,"Short Rural","Other","Fuse Operator - No Trigger Found",1,56.133333333333304,1.3890779211673501E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-06","20:55:00",60026667,"Long Rural","Overloads",null,1,57.933333333333302,7.5769465515738098E-4,1.30787339785509E-5,"NO"]
[null,"2018-02-07","06:21:00",10020777,"Short Rural","Other","Service Fuse",2,93.883333333333297,4.6464821436672805E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-07","09:34:00",50000160,"Long Rural","Asset failure","LV",3,670.45,2.6305911587758302E-2,3.9236201935652595E-5,"NO"]
[null,"2018-02-07","11:14:00",50000015,"Short Rural","Overloads",null,1,148.48333333333301,3.6743750592874001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-07","14:03:00",84579665,"Short Rural","Other","Service Fuse",1,83.75,2.0724811620742101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-07","15:41:00",40000977,"Long Rural","Other","Fuse Operator - No Trigger Found",1,96.1666666666667,1.2577382509373102E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-08","05:42:00",85068151,"Short Rural","Asset failure","HV",2,124.333333333333,6.1535162065964692E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-08","08:53:00",10020855,"Short Rural","Other","Service Fuse",2,79.650000000000006,3.9420447655931002E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-08","09:50:00",50000195,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2018-02-08","11:59:00",20008784,"Long Rural","Animal","Animal impact",1,268.33333333333303,3.5094602842444906E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-08","22:19:00",83896573,"Short Rural","Animal","Animal impact",47,200,2.32612811026837E-2,1.1630640551341901E-4,"NO"]
[null,"2018-02-09","08:30:00",40001236,"Urban","Planned",null,2,300,0,0,"NO"]
[null,"2018-02-09","09:00:00",60026751,"Long Rural","Planned",null,12,205,0,0,"NO"]
[null,"2018-02-09","10:35:00",50000151,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-02-09","14:14:00",40001246,"Short Rural","Planned",null,4,5,0,0,"NO"]
[null,"2018-02-09","17:22:00",60026694,"Short Rural","Overloads",null,2,97.9166666666667,4.8461002297257703E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-10","10:12:00",40001116,"Long Rural","Planned",null,4,108,0,0,"NO"]
[null,"2018-02-10","16:41:00",40000979,"Long Rural","Other","Fuse Operator - No Trigger Found",24,125.716666666667,3.94611561600837E-2,3.1388961548522103E-4,"NO"]
[null,"2018-02-10","17:19:00",50000074,"Short Rural","Asset failure","HV",305,1112.62508196721,0.83975860234345001,7.5475433365090807E-4,"NO"]
[null,"2018-02-11","08:30:00",10020809,"Urban","Planned",null,91,175,0,0,"NO"]
[null,"2018-02-11","17:48:00",50000075,"Short Rural","Other","Service Fuse",1,96.35,2.3842813130250801E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-11","19:33:00",10129324,"Short Rural","Overloads",null,1,56.816666666666698,1.4059877177136299E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-12","09:15:00",40001060,"Short Rural","Planned",null,9,225,0,0,"NO"]
[null,"2018-02-12","11:20:00",84375978,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-02-12","15:13:00",50000125,"Long Rural","Other","Fuse Operator - No Trigger Found",1,173.433333333333,2.2682884296800097E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-12","18:07:00",40001153,"Urban","Other","Service Fuse",1,271.73333333333301,1.2013286529852E-3,4.4209837573056797E-6,"NO"]
[null,"2018-02-12","18:31:00",50000125,"Long Rural","Other","Forced Corrective Maintenance",302,198.48333333333301,0.78396503618449698,3.9497776615223593E-3,"NO"]
[null,"2018-02-12","20:12:00",40001006,"Short Rural","Asset failure","LV",3,124.15,9.2166639858452597E-4,7.4238131178777803E-6,"NO"]
[null,"2018-02-13","08:30:00",40001038,"Long Rural","Planned",null,52,340,0,0,"NO"]
[null,"2018-02-13","08:35:00",60026824,"Short Rural","Planned",null,1,40,0,0,"NO"]
[null,"2018-02-13","09:28:00",10132684,"Long Rural","Animal","Animal impact",1,50.933333333333302,6.6614351730752506E-4,1.30787339785509E-5,"NO"]
[null,"2018-02-13","13:05:00",82649845,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2018-02-13","15:07:00",60026847,"Long Rural","Asset failure","HV",309,96.495307443365704,0.38996926497515,4.0413287993722197E-3,"NO"]
[null,"2018-02-13","16:11:00",60026832,"Short Rural","Other","Trip & Auto Reclose - No Trigger Found",47,1.8,2.0935152992415302E-4,1.1630640551341901E-4,"NO"]
[null,"2018-02-13","16:54:00",60026809,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1303,14.35,4.6270276289578201E-2,3.2244094975315803E-3,"NO"]
[null,"2018-02-13","17:26:00",50000094,"Long Rural","Other","Fuse Operator - No Trigger Found",2,726,1.8990321736855904E-2,2.61574679571018E-5,"NO"]
[null,"2018-02-13","17:44:00",60026747,"Long Rural","Weather",null,1,938.93333333333305,1.22800592902607E-2,1.30787339785509E-5,"NO"]
[null,"2018-02-13","18:58:00",50000095,"Long Rural","Other","Fuse Operator - No Trigger Found",1,269.63333333333304,3.5264626384166001E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-13","19:41:00",50000161,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",94,20.516666666666701,4.77243950623394E-3,2.3261281102683701E-4,"NO"]
[null,"2018-02-13","20:58:00",50000128,"Short Rural","Other","Fuse Operator - No Trigger Found",1,660.16666666666708,1.6336513199952198E-3,2.4746043726259304E-6,"NO"]
[null,"2018-02-14","04:25:00",85221077,"Short Rural","Weather",null,1,381.48333333333306,9.4402032475058098E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-14","05:27:00",50000130,"Long Rural","Other","Fuse Operator - No Trigger Found",1,212.13333333333301,2.7744354346499302E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-14","07:44:00",60026773,"Short Rural","Weather",null,2,332.68333333333305,1.6465192627328699E-3,4.9492087452518498E-6,"NO"]
[null,"2018-02-14","08:50:00",50000125,"Long Rural","Other","Fuse Operator - No Trigger Found",1,325.55,4.2577818467172393E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-14","09:30:00",40001246,"Short Rural","Planned",null,14,230,0,0,"NO"]
[null,"2018-02-14","11:01:00",50000126,"Short Rural","Planned",null,1,17,0,0,"NO"]
[null,"2018-02-14","11:44:00",20009035,"Short Rural","Asset failure","Distribution substation",1,44.9166666666667,1.1115097973711501E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-14","13:50:00",50000165,"Short Rural","Overloads",null,1,152.45000000000002,3.7725343660682201E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-14","15:32:00",10020669,"Long Rural","Asset failure","HV",11,1684.6333333333303,0.24236158339872699,1.4386607376406E-4,"NO"]
[null,"2018-02-14","18:04:00",50000159,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",616,14.5666666666667,0.11735635190513599,8.0565001307873422E-3,"NO"]
[null,"2018-02-14","18:17:00",50000143,"Short Rural","Other","Service Fuse",1,2323.1,5.74875341804729E-3,2.4746043726259304E-6,"NO"]
[null,"2018-02-14","19:57:00",50000229,"Long Rural","Other","Fuse Operator - No Trigger Found",1,1121.5,1.4667800156944799E-2,1.30787339785509E-5,"NO"]
[null,"2018-02-14","20:54:00",50000229,"Long Rural","Other","Fuse Operator - No Trigger Found",1,883.96666666666715,1.1561164879239701E-2,1.30787339785509E-5,"NO"]
[null,"2018-02-15","04:35:00",50000043,"Short Rural","Other","Service Fuse",1,200.96666666666698,4.9731299208539005E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-15","07:02:00",50000093,"Long Rural","Other","Fuse Operator - No Trigger Found",4,273.40000000000003,1.43029034789432E-2,5.2314935914203499E-5,"NO"]
[null,"2018-02-15","08:05:00",20001246,"Short Rural","Planned",null,4,153,0,0,"NO"]
[null,"2018-02-15","08:43:00",85081013,"Short Rural","Overloads",null,1,79.116666666666703,1.9578244928092101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-15","09:05:00",40001063,"Long Rural","Planned",null,7,231,0,0,"NO"]
[null,"2018-02-15","11:26:00",50000095,"Long Rural","Weather",null,1,207.53333333333299,2.7142732583485905E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-15","12:35:00",50000111,"Urban","Overloads",null,1,96.766666666666708,4.2780386158194602E-4,4.4209837573056797E-6,"NO"]
[null,"2018-02-15","14:03:00",50000229,"Long Rural","Asset failure","Distribution substation",4,203,1.06199319905833E-2,5.2314935914203499E-5,"NO"]
[null,"2018-02-15","16:39:00",60026830,"Short Rural","Other","Service Fuse",1,80.3,1.98710731121862E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-15","17:31:00",84332614,"Short Rural","Overloads",null,1,58.316666666666698,1.4431067833030201E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-15","20:05:00",10020856,"Short Rural","Animal","Other",1,89.0833333333333,2.2044600619476002E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-16","06:00:00",20009612,"Short Rural","Planned",null,1,575,0,0,"YES"]
[null,"2018-02-16","07:33:00",30053777,"Short Rural","Other","Service Fuse",1,172.9,4.2785909602702297E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-16","08:57:00",20007736,"Long Rural","Other","Fuse Operator - No Trigger Found",1,170.4,2.2286162699450699E-3,1.30787339785509E-5,"YES"]
[null,"2018-02-16","10:45:00",40000974,"Long Rural","Other","Fuse Operator - No Trigger Found",1,72.533333333333303,9.4864417124422399E-4,1.30787339785509E-5,"YES"]
[null,"2018-02-16","13:26:00",60026892,"Long Rural","Other","Fuse Operator - No Trigger Found",1,119.85000000000001,1.5674862673293202E-3,1.30787339785509E-5,"YES"]
[null,"2018-02-16","13:30:00",50000113,"Short Rural","Planned",null,1,11,0,0,"YES"]
[null,"2018-02-16","15:32:00",40001210,"Long Rural","Asset failure","Subtransmission",422,401.11666666666702,2.2138534309878799,5.5192257389484693E-3,"YES"]
[null,"2018-02-16","16:04:00",40001139,"Long Rural","Overloads",null,44,350.3,0.20158514255819998,5.7546429505623891E-4,"YES"]
[null,"2018-02-16","16:42:00",60026742,"Short Rural","Other","Fuse Operator - No Trigger Found",1,1784.1833333333302,4.4151478782329693E-3,2.4746043726259304E-6,"YES"]
[null,"2018-02-16","17:15:00",60026742,"Short Rural","Other","Fuse Operator - No Trigger Found",2,290.33333333333303,1.4369202723714502E-3,4.9492087452518498E-6,"YES"]
[null,"2018-02-16","17:32:00",10020722,"Short Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",1,106.083333333333,2.6251428052939999E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-16","17:52:00",40223076,"Long Rural","Weather",null,1,1180.7,1.5442061208475001E-2,1.30787339785509E-5,"YES"]
[null,"2018-02-16","18:19:00",40001033,"Long Rural","Asset failure","HV",59,1451.65,1.1201589066178399,7.7164530473450201E-4,"YES"]
[null,"2018-02-16","19:02:00",50000057,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",593,17.05,0.13223450170023501,7.7556892492806704E-3,"YES"]
[null,"2018-02-16","20:27:00",40001204,"Short Rural","Overloads",null,32,178.23333333333301,1.4113823552459602E-2,7.9187339924029597E-5,"YES"]
[null,"2018-02-16","21:27:00",40000961,"Long Rural","Other","Service Fuse",1,765.35,1.0009809050483902E-2,1.30787339785509E-5,"YES"]
[null,"2018-02-16","22:39:00",40001237,"Urban","Other","Forced Corrective Maintenance",1,7,3.0946886301139703E-5,4.4209837573056797E-6,"YES"]
[null,"2018-02-17","05:44:00",20001859,"Short Rural","Weather",null,1,99.0833333333333,2.4519204992101901E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-17","06:57:00",50000094,"Long Rural","Asset failure","Distribution substation",9,979.9,0.115342662830238,1.1770860580695802E-4,"NO"]
[null,"2018-02-17","07:05:00",50000118,"Long Rural","Other","Fuse Operator - No Trigger Found",1,142.06666666666698,1.8580521405527901E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-17","08:16:00",84965685,"Short Rural","Other","Service Fuse",1,234.083333333333,5.7926364022551898E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-17","08:56:00",84965685,"Short Rural","Other","Service Fuse",3,255.95000000000002,1.9001249675208202E-3,7.4238131178777803E-6,"NO"]
[null,"2018-02-17","10:04:00",50000125,"Long Rural","Weather",null,1,366.88333333333304,4.7983695178306701E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-17","12:14:00",50000149,"Short Rural","Asset failure","Distribution substation",1,134.19999999999999,3.3209190680639898E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-17","15:12:00",10020785,"Short Rural","Other","Service Fuse",1,125.25,3.0994419767139703E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-17","16:55:00",40000961,"Long Rural","Asset failure","LV",1,100.55,1.31506670154329E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-17","19:06:00",60026670,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",8,243.20000000000002,2.54459848286686E-2,1.0462987182840701E-4,"NO"]
[null,"2018-02-17","19:26:00",10020810,"Urban","5 - STPIS Exclusion (3.3)(a)",null,312,22.983333333333299,0,0,"NO"]
[null,"2018-02-17","19:26:00",10130408,"Short Rural","5 - STPIS Exclusion (3.3)(a)",null,289,24.883333333333301,0,0,"NO"]
[null,"2018-02-17","19:26:00",84382900,"Urban","5 - STPIS Exclusion (3.3)(a)",null,960,79.683333333333294,0,0,"NO"]
[null,"2018-02-17","22:05:00",10020836,"Short Rural","Asset failure","HV",310,399.93172043010804,0.30679856307972797,7.6712735551403709E-4,"NO"]
[null,"2018-02-18","00:36:00",84737242,"Short Rural","Overloads",null,1,54.5833333333333,1.35072155339165E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-18","09:44:00",40001033,"Long Rural","Weather",null,1,326.18333333333305,4.2660650449036506E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-18","09:58:00",50000125,"Long Rural","Weather",null,1,71.216666666666711,9.3142383817246504E-4,1.30787339785509E-5,"NO"]
[null,"2018-02-18","13:59:00",20013260,"Short Rural","Overloads",null,1,111.45,2.7579465732915996E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-18","17:37:00",20005336,"Urban","Overloads",null,3,82.433333333333294,1.0933092831816901E-3,1.3262951271916999E-5,"NO"]
[null,"2018-02-19","06:45:00",60026670,"Long Rural","Asset failure","HV",24,235.166666666667,7.3816374574941113E-2,3.1388961548522103E-4,"NO"]
[null,"2018-02-19","08:22:00",84666984,"Urban","Asset failure","LV",18,53.449999999999996,4.25342847290379E-3,7.9577707631502196E-5,"NO"]
[null,"2018-02-19","09:38:00",40001072,"Long Rural","Animal","Animal impact",1,87.35,1.14242741302642E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-19","11:08:00",50000208,"Short Rural","Planned",null,1,31.966666666666701,0,0,"NO"]
[null,"2018-02-19","11:57:00",50000208,"Short Rural","Planned",null,1,38.5833333333333,0,0,"NO"]
[null,"2018-02-19","14:11:00",50000153,"Short Rural","Third party","Fire",1,5.2333333333333298,1.29504295500757E-5,2.4746043726259304E-6,"NO"]
[null,"2018-02-19","16:46:00",60026641,"Long Rural","Other","Fuse Operator - No Trigger Found",1,213.63333333333301,2.7940535356177497E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-19","17:02:00",60026888,"Long Rural","Asset failure","HV",430,87.23100775193798,0.490574592379458,5.6238556107768801E-3,"NO"]
[null,"2018-02-19","17:49:00",60026751,"Long Rural","Weather",null,1,128.06666666666698,1.6749498648530802E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-19","19:32:00",50000040,"Long Rural","Overloads",null,1,203.066666666667,2.6558549132443998E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-19","20:40:00",60026670,"Long Rural","Weather",null,1,963.33333333333303,1.2599180399337299E-2,1.30787339785509E-5,"NO"]
[null,"2018-02-19","22:33:00",20003435,"Long Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",442,50.9166666666667,0.29433908797628405,5.7808004185194899E-3,"NO"]
[null,"2018-02-20","05:28:00",50000145,"Long Rural","Other","Fuse Operator - No Trigger Found",1,368.83333333333303,4.8238730490888495E-3,1.30787339785509E-5,"YES"]
[null,"2018-02-20","06:28:00",50000144,"Short Rural","Other","Fuse Operator - No Trigger Found",1,270.96666666666704,6.7053529816920503E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-20","06:51:00",10020772,"Long Rural","Animal","Animal impact",1,63.283333333333303,8.2766588194262798E-4,1.30787339785509E-5,"YES"]
[null,"2018-02-20","07:35:00",60026988,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",455,23.716666666666701,2.6703662002037401E-2,1.1259449895448001E-3,"YES"]
[null,"2018-02-20","08:37:00",20010627,"Short Rural","Other","Trip & Auto Reclose - No Trigger Found",2,1.63333333333333,8.0837076172446885E-6,4.9492087452518498E-6,"YES"]
[null,"2018-02-20","08:56:00",20007497,"Short Rural","Other","Fuse Operator - No Trigger Found",1,374.96666666666704,9.2789415292230195E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-20","09:20:00",10020674,"Long Rural","Weather",null,1,401.88333333333304,5.2561252070799499E-3,1.30787339785509E-5,"YES"]
[null,"2018-02-20","10:15:00",40000966,"Long Rural","Weather",null,1,13.8,1.80486528904002E-4,1.30787339785509E-5,"YES"]
[null,"2018-02-20","10:30:00",30053783,"Urban","Overloads",null,75,62.449999999999996,2.0706782673280501E-2,3.3157378179792598E-4,"YES"]
[null,"2018-02-20","11:20:00",82934570,"Short Rural","Weather",null,1,114.066666666667,2.8226987210419705E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-20","11:38:00",60026650,"Long Rural","Other","Service Fuse",1,1377.63333333333,1.8017699886651001E-2,1.30787339785509E-5,"YES"]
[null,"2018-02-20","12:44:00",60026694,"Short Rural","Other","Fuse Operator - No Trigger Found",4,395.40000000000003,3.9138342757451703E-3,9.8984174905037098E-6,"YES"]
[null,"2018-02-20","13:39:00",10020775,"Short Rural","Weather",null,1,48.0833333333333,1.18987226917097E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-20","14:10:00",40000966,"Long Rural","Other","Fuse Operator - No Trigger Found",1,1263.5,1.6524980381899E-2,1.30787339785509E-5,"YES"]
[null,"2018-02-20","15:35:00",20001148,"Urban","Weather",null,53,149.416666666667,3.5010138789416799E-2,2.34312139137201E-4,"YES"]
[null,"2018-02-20","17:18:00",40001062,"Long Rural","Asset failure","HV",38,1097.2333333333302,0.54531606940448207,4.9699189118493305E-4,"YES"]
[null,"2018-02-20","17:19:00",40001068,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",220,15,4.3159822129217901E-2,2.8773214752811898E-3,"YES"]
[null,"2018-02-20","18:03:00",50000125,"Long Rural","Weather",null,1,32.366666666666696,4.2331502310576303E-4,1.30787339785509E-5,"YES"]
[null,"2018-02-20","18:57:00",50000233,"Short Rural","Other","Fuse Operator - No Trigger Found",1,60.149999999999991,1.4884745301344898E-4,2.4746043726259304E-6,"YES"]
[null,"2018-02-20","19:49:00",10020772,"Long Rural","Asset failure","Distribution substation",1,54.216666666666697,7.0908536053709999E-4,1.30787339785509E-5,"YES"]
[null,"2018-02-20","20:24:00",84962745,"Long Rural","Overloads",null,1,190.6,2.4928066963118001E-3,1.30787339785509E-5,"YES"]
[null,"2018-02-20","20:59:00",30053863,"Short Rural","Weather",null,280,6.5833333333333295,4.5615207268737907E-3,6.9288922433525895E-4,"YES"]
[null,"2018-02-20","21:37:00",84928162,"Short Rural","Weather",null,2,1884.2083333333301,9.3253403612097493E-3,4.9492087452518498E-6,"YES"]
[null,"2018-02-20","22:26:00",84653782,"Short Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",2,1063.1500000000001,5.2617512775145099E-3,4.9492087452518498E-6,"YES"]
[null,"2018-02-20","23:15:00",20006518,"Short Rural","Weather",null,175,260.41666666666703,0.11277493885665001,4.3305576520953702E-4,"YES"]
[null,"2018-02-20","23:37:00",20009878,"Short Rural","5 - STPIS Exclusion (3.3)(a)",null,125,3.75,0,0,"YES"]
[null,"2018-02-21","06:40:00",30053752,"Long Rural","Weather",null,1,319.51666666666705,4.1788734850466492E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-21","07:58:00",20004081,"Short Rural","Weather",null,1,218.066666666667,5.3962872685729398E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-21","08:10:00",82563612,"Long Rural","Asset failure","LV",1,166.25,2.1743395239340801E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-21","09:16:00",50000030,"Short Rural","Planned",null,3,9,0,0,"NO"]
[null,"2018-02-21","10:11:00",60026667,"Long Rural","Weather",null,1,66.016666666666708,8.63414421484E-4,1.30787339785509E-5,"NO"]
[null,"2018-02-21","11:00:00",40000960,"Short Rural","Weather",null,1,122.183333333333,3.0235541092867799E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-21","12:39:00",40001118,"Long Rural","Other","Fuse Operator - No Trigger Found",1,175.666666666667,2.2974976022321E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-21","14:42:00",20010779,"Short Rural","Asset failure","Distribution substation",3,218,1.61839125969736E-3,7.4238131178777803E-6,"NO"]
[null,"2018-02-21","16:25:00",83879351,"Short Rural","Other","Service Fuse",1,138.85,3.4359881713910998E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-21","17:22:00",82563612,"Long Rural","Other","Fuse Operator - No Trigger Found",7,1307.6833333333302,0.119719897113959,9.1551137849856101E-5,"NO"]
[null,"2018-02-21","18:23:00",20010686,"Short Rural","Weather",null,1,935.3833333333331,2.3147036867480803E-3,2.4746043726259304E-6,"NO"]
[null,"2018-02-21","21:07:00",30053863,"Short Rural","Weather",null,1,175.816666666667,4.3507669211384801E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-22","00:58:00",10020670,"Long Rural","5 - STPIS Exclusion (3.3)(a)",null,169,23.9166666666667,0,0,"NO"]
[null,"2018-02-22","05:07:00",10020675,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",393,14.4333333333333,1.4036698382846002E-2,9.7251951844198902E-4,"NO"]
[null,"2018-02-22","07:30:00",60026763,"Urban","Asset failure","LV",3,99,1.31303217591979E-3,1.3262951271916999E-5,"NO"]
[null,"2018-02-22","08:21:00",30053783,"Urban","Other","Fuse Operator - No Trigger Found",70,40.65,1.2579909281413299E-2,3.0946886301139702E-4,"NO"]
[null,"2018-02-22","09:00:00",10020850,"Short Rural","Planned",null,19,200,0,0,"NO"]
[null,"2018-02-22","10:44:00",20007736,"Long Rural","Asset failure","HV",53,1881.2166666666703,1.3040084139855299,6.9317290086319604E-4,"NO"]
[null,"2018-02-22","14:08:00",60026666,"Long Rural","Asset failure","Distribution substation",43,33.426744186046506,1.87987182840701E-2,5.6238556107768799E-4,"NO"]
[null,"2018-02-22","15:33:00",30053778,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",9,1349.0333333333301,0.15879283285378001,1.1770860580695802E-4,"NO"]
[null,"2018-02-22","18:57:00",60026656,"Short Rural","Other","Service Fuse",1,101.26666666666701,2.5059493613458503E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-22","22:26:00",50000143,"Short Rural","Asset failure","LV",1,126.283333333333,3.1250128885644405E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-23","06:33:00",20004081,"Short Rural","Other","Service Fuse",1,213.86666666666699,5.2923538849226502E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-23","07:17:00",20013273,"Short Rural","Other","Fuse Operator - No Trigger Found",1,114.60000000000001,2.8358966110293097E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-23","08:35:00",82915259,"Short Rural","Planned",null,3,100,0,0,"NO"]
[null,"2018-02-23","09:27:00",20006666,"Short Rural","Other","Service Fuse",4,157.76666666666699,1.5616403327518001E-3,9.8984174905037098E-6,"NO"]
[null,"2018-02-23","10:25:00",50000229,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-02-23","13:08:00",82563612,"Long Rural","Other","Fuse Operator - No Trigger Found",1,85.683333333333294,1.1206295230621701E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-23","14:56:00",10020777,"Short Rural","Asset failure","LV",2,98.75,4.8873436359361995E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-23","19:14:00",10020782,"Short Rural","Asset failure","Distribution substation",658,103.655116514691,0.16878055620857599,1.62828967718786E-3,"NO"]
[null,"2018-02-24","01:15:00",40001118,"Long Rural","Animal","Animal impact",1,607.66666666666708,7.9475106809660818E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-24","08:30:00",40001246,"Short Rural","Planned",null,14,234,0,0,"NO"]
[null,"2018-02-24","09:53:00",40000962,"Long Rural","Other","Vibration",1,164.61666666666699,2.1529775917691202E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-24","13:37:00",82921011,"Urban","Other","Service Fuse",1,80.933333333333294,3.5780495209127299E-4,4.4209837573056797E-6,"NO"]
[null,"2018-02-24","15:16:00",40001068,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",220,4.8166666666666691,1.3859098439271102E-2,2.8773214752811898E-3,"NO"]
[null,"2018-02-24","16:22:00",81669225,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",101,27.466666666666701,6.8648824769140006E-3,2.4993504163521899E-4,"NO"]
[null,"2018-02-24","18:50:00",10020657,"Short Rural","Other","Service Fuse",1,55.016666666666701,1.3614448390063602E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-25","05:31:00",30053782,"Short Rural","Other","Forced Corrective Maintenance",5,70,8.6611153041907404E-4,1.2373021863129598E-5,"NO"]
[null,"2018-02-25","05:57:00",60026667,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",30,100.116666666667,3.9281977504577598E-2,3.9236201935652598E-4,"NO"]
[null,"2018-02-25","09:23:00",20007292,"Urban","Other","Service Fuse",1,244.05,1.0789410859704501E-3,4.4209837573056797E-6,"NO"]
[null,"2018-02-25","13:28:00",40001118,"Long Rural","Other","Service Fuse",1,120.60000000000001,1.5772953178132402E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-25","16:10:00",20007314,"Urban","Asset failure","Distribution substation",105,81.099999999999994,3.76468871853365E-2,4.6420329451709599E-4,"NO"]
[null,"2018-02-25","17:07:00",60026675,"Long Rural","Asset failure","HV",35,1072.8166666666702,0.49108793268811596,4.5775568924928098E-4,"NO"]
[null,"2018-02-25","20:23:00",50000180,"Short Rural","Other","Service Fuse",2,76.600000000000009,3.7910938988629201E-4,4.9492087452518498E-6,"NO"]
[null,"2018-02-25","21:14:00",20002652,"Short Rural","Other","Service Fuse",1,677.01666666666711,1.67534840367396E-3,2.4746043726259304E-6,"NO"]
[null,"2018-02-26","07:31:00",20009882,"Short Rural","Weather",null,1,95.6666666666667,2.3673715164788001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-26","09:11:00",10020778,"Short Rural","Asset failure","LV",1,288.90000000000003,7.1491320325163001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-26","12:37:00",83909007,"Short Rural","Weather",null,1,131.86666666666699,3.2631782993693901E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-26","13:46:00",60026701,"Long Rural","Other","Service Fuse",1,981.5,1.2836777399947702E-2,1.30787339785509E-5,"NO"]
[null,"2018-02-26","14:47:00",25268407,"Short Rural","Asset failure","LV",1,79.233333333333306,1.96071153124394E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-26","18:25:00",50000130,"Long Rural","Other","Service Fuse",1,80.816666666666706,1.05697968436655E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-26","22:19:00",40001045,"Short Rural","Asset failure","HV",8,1163,2.3023719082911599E-2,1.9796834981007399E-5,"NO"]
[null,"2018-02-27","06:20:00",60026731,"Short Rural","Weather",null,1,268.566666666667,6.6459624767490298E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-27","07:44:00",60026987,"Short Rural","Other","Fuse Operator - No Trigger Found",1,196.13333333333301,4.8535240428436503E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-27","09:03:00",30053878,"Short Rural","Weather",null,1,125.9,3.1155269051360402E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-27","09:58:00",40001038,"Long Rural","Asset failure","HV",25,180,5.88543029034789E-2,3.2696834946377201E-4,"NO"]
[null,"2018-02-27","11:19:00",83864041,"Short Rural","Other","Service Fuse",1,65.4166666666667,1.61880369375946E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-27","16:16:00",50000240,"Long Rural","Other","Service Fuse",1,51.4,6.7224692649751503E-4,1.30787339785509E-5,"NO"]
[null,"2018-02-27","19:27:00",83864041,"Short Rural","Other","Fuse Operator - No Trigger Found",44,207.316666666667,2.2573176113468901E-2,1.0888259239554101E-4,"NO"]
[null,"2018-02-28","08:02:00",40001208,"Long Rural","Planned",null,1,66,0,0,"NO"]
[null,"2018-02-28","08:43:00",40001118,"Long Rural","Weather",null,1,258.51666666666705,3.3810707123550403E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-28","10:45:00",50000230,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2018-02-28","13:55:00",50000125,"Long Rural","Asset failure","Distribution substation",1,81.45,1.0652628825529699E-3,1.30787339785509E-5,"NO"]
[null,"2018-02-28","14:58:00",82649838,"Short Rural","Network business","Network error",1,101.633333333333,2.51502291071215E-4,2.4746043726259304E-6,"NO"]
[null,"2018-02-28","20:16:00",30053745,"Short Rural","Other","Service Fuse",1,91.783333333333303,2.2712743800085001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-01","08:34:00",40000977,"Long Rural","Other","Forced Corrective Maintenance",1,110,1.4386607376405999E-3,1.30787339785509E-5,"NO"]
[null,"2018-03-01","08:42:00",60026774,"Short Rural","Weather",null,1,143.20000000000002,3.5436334616003299E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-01","10:13:00",10020679,"Short Rural","Weather",null,1,133.15,3.2949357221514201E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-01","13:54:00",40001139,"Long Rural","Planned",null,4,131,0,0,"NO"]
[null,"2018-03-01","15:27:00",50000050,"Short Rural","Other","Forced Corrective Maintenance",2,27,1.3362863612180001E-4,4.9492087452518498E-6,"NO"]
[null,"2018-03-02","01:16:00",82914276,"Short Rural","Other","Service Fuse",1,124.2,3.0734586308014001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-02","05:16:00",10020804,"Short Rural","Vegetation","Blow-in/Fall-in - NSP responsibility",243,141.193552812071,8.4903758511608002E-2,6.0132886254809993E-4,"NO"]
[null,"2018-03-02","08:50:00",40001034,"Short Rural","Asset failure","Distribution substation",1,187.28333333333299,4.6345215558662599E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-02","10:27:00",60026666,"Long Rural","Other","Fuse Operator - No Trigger Found",1,208.65,2.72887784462464E-3,1.30787339785509E-5,"NO"]
[null,"2018-03-02","12:20:00",40001101,"Urban","Other","Forced Corrective Maintenance",84,76,2.8223560306639403E-2,3.7136263561367701E-4,"NO"]
[null,"2018-03-02","18:34:00",82536638,"Short Rural","Other","Fuse Operator - No Trigger Found",1,65.5833333333333,1.6229280343805E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-03","08:37:00",20011981,"Urban","Planned",null,104,127.086538461538,0,0,"NO"]
[null,"2018-03-03","13:00:00",20001178,"Urban","Planned",null,7,145,0,0,"NO"]
[null,"2018-03-03","15:37:00",60026830,"Short Rural","Other","Fuse Operator - No Trigger Found",2,124.35000000000001,6.1543410747206802E-4,4.9492087452518498E-6,"NO"]
[null,"2018-03-03","18:52:00",30053830,"Short Rural","Asset failure","LV",1,103.033333333333,2.5496673719289101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-04","03:08:00",30053864,"Short Rural","Other","Fuse Operator - No Trigger Found",1,75.683333333333294,1.87286307601572E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-04","08:41:00",60026650,"Long Rural","Other","Fuse Operator - No Trigger Found",1,186.9,2.4444153805911603E-3,1.30787339785509E-5,"NO"]
[null,"2018-03-04","12:18:00",10020837,"Short Rural","Animal","Animal impact",1,103.383333333333,2.5583284872331E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-04","18:49:00",60026890,"Short Rural","Other","Fuse Operator - No Trigger Found",1,46.183333333333302,1.1428547860910701E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-04","20:55:00",85212266,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1,21.683333333333298,5.3657671479772194E-5,2.4746043726259304E-6,"NO"]
[null,"2018-03-05","10:11:00",50000150,"Short Rural","Other","Forced Corrective Maintenance",18,63,2.8062013585578001E-3,4.4542878707266693E-5,"NO"]
[null,"2018-03-05","13:38:00",50000093,"Long Rural","Asset failure","Distribution substation",1,106.683333333333,1.3952829366117398E-3,1.30787339785509E-5,"NO"]
[null,"2018-03-05","16:58:00",20006478,"Short Rural","Other","Fuse Operator - No Trigger Found",1,54.466666666666697,1.3478345149569199E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-06","07:24:00",20006478,"Short Rural","Weather",null,24,43.606249999999996,2.5897972061716601E-3,5.9390504943022201E-5,"NO"]
[null,"2018-03-06","07:30:00",20002622,"Short Rural","Planned",null,74,165,0,0,"NO"]
[null,"2018-03-06","09:20:00",30186258,"Urban","Planned",null,3,11,0,0,"NO"]
[null,"2018-03-06","12:26:00",50000148,"Short Rural","Other","Service Fuse",1,164.15,4.0620630776654602E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-06","14:00:00",84041077,"Short Rural","Planned",null,3,60,0,0,"NO"]
[null,"2018-03-06","20:00:00",10020798,"Short Rural","Vegetation","Grow-in - NSP responsibility",77,392.816666666667,7.4849069754972894E-2,1.9054453669219601E-4,"NO"]
[null,"2018-03-07","06:32:00",30053862,"Short Rural","Other","Fuse Operator - No Trigger Found",1,141.433333333333,3.4999154510172701E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-07","08:54:00",60026675,"Long Rural","Overloads",null,1,113.583333333333,1.4855262010637401E-3,1.30787339785509E-5,"NO"]
[null,"2018-03-07","11:00:00",40001120,"Short Rural","Planned",null,29,19,0,0,"NO"]
[null,"2018-03-07","19:10:00",10020679,"Short Rural","Other","Service Fuse",1,99.149999999999991,2.4535702354586098E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-08","07:40:00",60026822,"Urban","Other","Service Fuse",2,129.46666666666698,1.1447400608916801E-3,8.8419675146113493E-6,"NO"]
[null,"2018-03-08","08:30:00",60026691,"Short Rural","Planned",null,14,150,0,0,"NO"]
[null,"2018-03-08","10:14:00",40001130,"Urban","Other","Service Fuse",1,53.733333333333299,2.3755419389255802E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-08","12:59:00",40001065,"Short Rural","Planned",null,1,11,0,0,"NO"]
[null,"2018-03-08","14:15:00",40001115,"Short Rural","Other","Fuse Operator - No Trigger Found",17,126.633333333333,5.3272458065766705E-3,4.2068274334640702E-5,"NO"]
[null,"2018-03-08","19:03:00",10020829,"Short Rural","Other","Service Fuse",1,158.38333333333301,3.9193608921773602E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-09","06:55:00",10020804,"Short Rural","Other","Forced Corrective Maintenance",390,35,3.3778349686343905E-2,9.6509570532411109E-4,"NO"]
[null,"2018-03-09","08:30:00",10020831,"Short Rural","Planned",null,11,145,0,0,"NO"]
[null,"2018-03-09","10:31:00",20011656,"Urban","Planned",null,26,28,0,0,"NO"]
[null,"2018-03-09","14:50:00",30053830,"Short Rural","Other","Service Fuse",2,83.516666666666708,4.1334141704095099E-4,4.9492087452518498E-6,"NO"]
[null,"2018-03-09","17:54:00",20009956,"Short Rural","Other","Fuse Operator - No Trigger Found",5,74.600000000000009,9.2302743098947098E-4,1.2373021863129598E-5,"NO"]
[null,"2018-03-10","06:12:00",10020842,"Short Rural","Weather",null,1,147.4,3.64756684525062E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-10","10:52:00",30053746,"Short Rural","Other","Vibration",1,71.399999999999991,1.7668675220549099E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-10","15:14:00",20013273,"Short Rural","Asset failure","Distribution substation",1,138.05000000000001,3.41619133641009E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-10","20:02:00",60026840,"Urban","Asset failure","HV",80,87.866666666666703,3.1076568491353998E-2,3.5367870058445401E-4,"NO"]
[null,"2018-03-11","10:16:00",84965685,"Short Rural","Weather",null,1,171.083333333333,4.23363564750086E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-11","18:28:00",40001204,"Short Rural","Overloads",null,2,65.95,3.2640031674936E-4,4.9492087452518498E-6,"NO"]
[null,"2018-03-12","08:57:00",20001246,"Short Rural","Planned",null,6,111,0,0,"NO"]
[null,"2018-03-12","12:31:00",10131875,"Short Rural","Other","Service Fuse",1,296.2,7.3297781517179909E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-12","13:00:00",40001246,"Short Rural","Planned",null,1,110,0,0,"NO"]
[null,"2018-03-12","23:06:00",60330968,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1632,133.13333333333301,0.53766620061617598,4.03855433612551E-3,"NO"]
[null,"2018-03-13","08:30:00",60026755,"Long Rural","Planned",null,21,175,0,0,"NO"]
[null,"2018-03-13","09:28:00",50000173,"Short Rural","Planned",null,3,9,0,0,"NO"]
[null,"2018-03-13","11:39:00",20001263,"Short Rural","Other","Service Fuse",1,93,2.3013820665421101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-13","20:03:00",82915259,"Short Rural","Other","Vibration",1,57.566666666666698,1.4245472505083198E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-13","22:43:00",50000206,"Urban","Other","Fuse Operator - No Trigger Found",1,43.316666666666698,1.9150227975395801E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-14","08:30:00",30053784,"Long Rural","Planned",null,6,299,0,0,"NO"]
[null,"2018-03-14","10:54:00",50000148,"Short Rural","Asset failure","HV",24,305.73333333333306,1.815765704458E-2,5.9390504943022201E-5,"NO"]
[null,"2018-03-14","15:55:00",20002267,"Short Rural","7 - STPIS Exclusion (3.3)(a)",null,411,32.299999999999997,0,0,"NO"]
[null,"2018-03-15","09:00:00",10020850,"Short Rural","Planned",null,64,90,0,0,"NO"]
[null,"2018-03-15","10:00:00",30053864,"Short Rural","Planned",null,48,57,0,0,"NO"]
[null,"2018-03-15","13:30:00",30053781,"Long Rural","Planned",null,6,79,0,0,"NO"]
[null,"2018-03-15","18:42:00",20005482,"Short Rural","Overloads",null,3,60.5833333333333,4.4975934472476202E-4,7.4238131178777803E-6,"NO"]
[null,"2018-03-16","08:30:00",10020807,"Urban","Planned",null,65,160,0,0,"NO"]
[null,"2018-03-16","09:00:00",50000021,"Short Rural","Planned",null,49,258,0,0,"NO"]
[null,"2018-03-16","09:30:00",50000074,"Short Rural","Planned",null,1,60,0,0,"NO"]
[null,"2018-03-16","11:49:00",82962855,"Short Rural","Asset failure","Distribution substation",1,65.8333333333333,1.6291145453120701E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-16","13:58:00",25274647,"Urban","Other","Service Fuse",1,184.88333333333301,8.1736621366319795E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-17","08:53:00",20006948,"Short Rural","Asset failure","Distribution substation",1,48.55,1.2014204229098901E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-17","15:30:00",40001062,"Long Rural","Other","Fuse Operator - No Trigger Found",1,1187.63333333333,1.55327404307263E-2,1.30787339785509E-5,"NO"]
[null,"2018-03-18","04:18:00",82962940,"Short Rural","Asset failure","HV",36,147.65324074074098,1.31538007860993E-2,8.90857574145334E-5,"NO"]
[null,"2018-03-18","08:45:00",25273354,"Urban","Asset failure","LV",3,131.4,1.7427517971299001E-3,1.3262951271916999E-5,"NO"]
[null,"2018-03-18","18:45:00",40001215,"Urban","Other","Service Fuse",1,60.433333333333302,2.6717478506650601E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-19","07:38:00",40001204,"Short Rural","Other","Vibration",1,89.883333333333297,2.2242568969286001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-19","09:47:00",82563612,"Long Rural","Other","Service Fuse",1,59.816666666666698,7.8232627081698501E-4,1.30787339785509E-5,"NO"]
[null,"2018-03-19","14:38:00",40001200,"Short Rural","Planned",null,23,103,0,0,"NO"]
[null,"2018-03-19","18:24:00",30053832,"Short Rural","Third party","Fire",1,127.883333333333,3.1646065585264597E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-19","19:12:00",60026713,"Short Rural","Overloads",null,1,177.38333333333301,4.38953572297629E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-20","08:02:00",50000154,"Short Rural","Planned",null,2,108,0,0,"NO"]
[null,"2018-03-20","09:10:00",50000180,"Short Rural","Planned",null,3,341,0,0,"NO"]
[null,"2018-03-20","11:30:00",60026673,"Short Rural","Planned",null,1,63.999999999999993,0,0,"NO"]
[null,"2018-03-20","13:00:00",40001072,"Long Rural","Planned",null,1,28,0,0,"NO"]
[null,"2018-03-20","18:54:00",50000195,"Urban","Other","Service Fuse",1,79.983333333333306,3.5360501752183202E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-21","08:00:00",50000229,"Long Rural","Planned",null,1,60,0,0,"NO"]
[null,"2018-03-21","08:30:00",83022301,"Short Rural","Planned",null,1,227,0,0,"NO"]
[null,"2018-03-21","09:31:00",60026740,"Short Rural","Planned",null,83,291,0,0,"NO"]
[null,"2018-03-21","14:00:00",10020657,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-03-21","21:12:00",50000053,"Long Rural","Animal","Other",2,95.9,2.5085011770860604E-3,2.61574679571018E-5,"NO"]
[null,"2018-03-21","21:15:00",40001210,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",153,17.350000000000001,3.4718153282762204E-2,2.00104629871828E-3,"NO"]
[null,"2018-03-22","09:00:00",84375978,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2018-03-22","10:26:00",60026657,"Short Rural","Animal","Animal impact",1,133.98333333333301,3.3155574252566398E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-22","11:53:00",50000130,"Long Rural","Animal","Animal impact",1,170.1,2.2246926497515003E-3,1.30787339785509E-5,"NO"]
[null,"2018-03-22","16:00:00",10020836,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2018-03-23","06:45:00",20004592,"Short Rural","Planned",null,22,5,0,0,"NO"]
[null,"2018-03-23","08:27:00",30053769,"Short Rural","Other","Fuse Operator - No Trigger Found",1,140.13333333333301,3.4677455941731298E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-23","09:30:00",10020827,"Short Rural","Asset failure","LV",1,312.15000000000003,7.7244775491518299E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-23","14:10:00",10020786,"Urban","Asset failure","LV",1,76.516666666666708,3.3827894049650599E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-24","06:59:00",84255558,"Short Rural","Animal","Animal impact",708,112.468079096045,0.19704631222083399,1.75201989581916E-3,"NO"]
[null,"2018-03-24","10:03:00",25268197,"Short Rural","Overloads",null,1,55.8333333333333,1.3816541080494802E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-24","13:58:00",50000054,"Short Rural","Third party","Vehicle impact",1,200.4,4.9591071627423601E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-24","18:54:00",20010376,"Urban","Overloads",null,1,160.933333333333,7.11483652675727E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-25","11:52:00",10020657,"Short Rural","Other","Service Fuse",1,226.78333333333299,5.6119902830535E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-25","16:32:00",40001066,"Long Rural","Asset failure","HV",55,163.333333333333,0.117490626907315,7.1933036882029799E-4,"NO"]
[null,"2018-03-26","05:54:00",40001005,"Long Rural","Animal","Animal impact",9,186.26666666666699,2.1925189641642698E-2,1.1770860580695802E-4,"NO"]
[null,"2018-03-26","08:47:00",20005577,"Urban","Other","Service Fuse",1,58.8333333333333,2.6010121105481701E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-26","10:01:00",10020744,"Long Rural","Planned",null,4,90.75,0,0,"NO"]
[null,"2018-03-26","13:15:00",50000194,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2018-03-26","22:23:00",82563751,"Short Rural","5 - STPIS Exclusion (3.3)(a)",null,2,59.483333333333299,0,0,"NO"]
[null,"2018-03-27","08:30:00",40000961,"Long Rural","Planned",null,26,296.07692307692304,0,0,"NO"]
[null,"2018-03-27","09:30:00",40001116,"Long Rural","Planned",null,1,122,0,0,"NO"]
[null,"2018-03-27","10:15:00",82554035,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2018-03-27","13:33:00",40001066,"Long Rural","Planned",null,1,94,0,0,"NO"]
[null,"2018-03-27","15:07:00",10020661,"Urban","Other","Fuse Operator - No Trigger Found",76,95.966666666666697,3.2244297667783701E-2,3.3599476555523102E-4,"NO"]
[null,"2018-03-27","23:00:00",50000137,"Short Rural","Other","Forced Corrective Maintenance",1,100,2.4746043726259296E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-28","09:03:00",40001170,"Short Rural","Planned",null,61,308,0,0,"NO"]
[null,"2018-03-28","12:00:00",50000196,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-03-28","13:50:00",50000125,"Long Rural","Vegetation","Grow-in - NSP responsibility",1,47.016666666666701,6.1491847589153397E-4,1.30787339785509E-5,"NO"]
[null,"2018-03-28","15:25:00",25273354,"Urban","Planned",null,1,10,0,0,"NO"]
[null,"2018-03-29","08:33:00",60026703,"Short Rural","Planned",null,43,106,0,0,"NO"]
[null,"2018-03-29","10:23:00",30053773,"Short Rural","Other","Service Fuse",1,210.48333333333301,5.2086297703154711E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-29","10:58:00",10020857,"Short Rural","Animal","Other",1,132.11666666666699,3.2693648103009504E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-29","16:54:00",84965685,"Short Rural","Planned",null,3,11,0,0,"NO"]
[null,"2018-03-30","10:22:00",25273354,"Urban","Overloads",null,1,115.75,5.11728869908132E-4,4.4209837573056797E-6,"NO"]
[null,"2018-03-30","16:35:00",10020787,"Short Rural","Other","Service Fuse",1,127.616666666667,3.1580076135327896E-4,2.4746043726259304E-6,"NO"]
[null,"2018-03-31","13:47:00",20004903,"Short Rural","Overloads",null,1,111.333333333333,2.7550595348568602E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-01","11:31:00",20012874,"Short Rural","Overloads",null,3,44.483333333333299,3.3023595352692995E-4,7.4238131178777803E-6,"NO"]
[null,"2018-04-02","13:11:00",85206371,"Short Rural","Asset failure","LV",1,92.1666666666667,2.2807603634369001E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-03","08:49:00",20005265,"Short Rural","Planned",null,4,36,0,0,"NO"]
[null,"2018-04-03","10:00:00",10020847,"Short Rural","Planned",null,7,232,0,0,"NO"]
[null,"2018-04-03","13:45:00",50000192,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2018-04-03","17:36:00",30053749,"Urban","Weather",null,1,74.5,3.2936328991927299E-4,4.4209837573056797E-6,"NO"]
[null,"2018-04-04","07:44:00",83832366,"Short Rural","Asset failure","HV",958,27.0982776617954,6.4241100704024889E-2,2.3706709889756402E-3,"NO"]
[null,"2018-04-04","09:03:00",30053812,"Urban","Other","Forced Corrective Maintenance",570,5,1.25998037083212E-2,2.5199607416642403E-3,"NO"]
[null,"2018-04-04","10:40:00",50000124,"Short Rural","Planned",null,2,15,0,0,"NO"]
[null,"2018-04-04","12:49:00",60026819,"Long Rural","Other","Fuse Operator - No Trigger Found",1,69.4166666666667,9.0788211701107308E-4,1.30787339785509E-5,"NO"]
[null,"2018-04-04","16:11:00",60026818,"Urban","Planned",null,2,38.999999999999993,0,0,"NO"]
[null,"2018-04-05","08:35:00",83864041,"Short Rural","Planned",null,5,155,0,0,"NO"]
[null,"2018-04-05","09:30:00",40000974,"Long Rural","Planned",null,15,163,0,0,"NO"]
[null,"2018-04-05","14:38:00",84965669,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2018-04-05","19:57:00",40223073,"Long Rural","Overloads",null,1,75.366666666666703,9.8570058418345112E-4,1.30787339785509E-5,"NO"]
[null,"2018-04-06","08:49:00",10020828,"Long Rural","Planned",null,1,253,0,0,"NO"]
[null,"2018-04-06","11:15:00",50000034,"Short Rural","Planned",null,3,5,0,0,"NO"]
[null,"2018-04-06","13:02:00",40001227,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-04-06","18:27:00",30053817,"Urban","Other","Service Fuse",1,153.26666666666699,6.7758944386971706E-4,4.4209837573056797E-6,"NO"]
[null,"2018-04-07","09:05:00",50000067,"Short Rural","Planned",null,23,171,0,0,"NO"]
[null,"2018-04-08","05:27:00",60026819,"Long Rural","Asset failure","LV",1,187.76666666666699,2.4557502833725698E-3,1.30787339785509E-5,"NO"]
[null,"2018-04-08","09:51:00",50000109,"Short Rural","Planned",null,2,52,0,0,"NO"]
[null,"2018-04-09","08:30:00",10020778,"Short Rural","Planned",null,5,380,0,0,"NO"]
[null,"2018-04-09","10:25:00",20001263,"Short Rural","Other","Forced Corrective Maintenance",5,10,1.2373021863129599E-4,1.2373021863129598E-5,"NO"]
[null,"2018-04-09","13:01:00",50000052,"Short Rural","Planned",null,1,16,0,0,"NO"]
[null,"2018-04-09","17:07:00",40000961,"Long Rural","Other","Fuse Operator - No Trigger Found",1,46.9,6.1339262359403604E-4,1.30787339785509E-5,"NO"]
[null,"2018-04-10","08:21:00",25267731,"Short Rural","Other","Service Fuse",1,64.8333333333333,1.6043685015858101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-10","08:48:00",60026670,"Long Rural","Planned",null,1,77,0,0,"NO"]
[null,"2018-04-10","10:40:00",82554089,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2018-04-10","12:50:00",40001175,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2018-04-10","18:46:00",20007229,"Short Rural","Overloads",null,1,258.5,6.3968523032380199E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-10","19:02:00",40001200,"Short Rural","Overloads",null,2,54.75,2.7096917880253899E-4,4.9492087452518498E-6,"NO"]
[null,"2018-04-11","09:00:00",30053843,"Short Rural","Planned",null,91,298,0,0,"NO"]
[null,"2018-04-11","09:42:00",10020847,"Short Rural","Planned",null,1,412,0,0,"NO"]
[null,"2018-04-11","12:55:00",40223073,"Long Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-04-11","16:33:00",40001106,"Short Rural","Other","Service Fuse",1,72.699999999999989,1.79903737889905E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-12","08:34:00",60026992,"Long Rural","Planned",null,1,62,0,0,"NO"]
[null,"2018-04-12","10:00:00",60026666,"Long Rural","Planned",null,24,253,0,0,"NO"]
[null,"2018-04-12","10:48:00",50000044,"Long Rural","Planned",null,1,75,0,0,"NO"]
[null,"2018-04-12","13:01:00",40001175,"Urban","Planned",null,1,4,0,0,"NO"]
[null,"2018-04-13","08:00:00",40001066,"Long Rural","Planned",null,3,51,0,0,"NO"]
[null,"2018-04-13","08:15:00",50000094,"Long Rural","Planned",null,2,49.999999999999993,0,0,"NO"]
[null,"2018-04-13","08:50:00",50000211,"Short Rural","Planned",null,3,7,0,0,"NO"]
[null,"2018-04-13","12:00:00",50000109,"Short Rural","Planned",null,1,4,0,0,"NO"]
[null,"2018-04-13","19:00:00",10020773,"Short Rural","Vegetation","Grow-in - NSP responsibility",1,146.65,3.62900731245592E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-14","04:01:00",60026688,"Short Rural","Other","Service Fuse",3,195.53333333333299,1.45160292498237E-3,7.4238131178777803E-6,"NO"]
[null,"2018-04-14","08:30:00",40001003,"Short Rural","Planned",null,5,156,0,0,"NO"]
[null,"2018-04-14","12:27:00",30053784,"Long Rural","Other","Fuse Operator - No Trigger Found",2,102.716666666667,2.6868079169936401E-3,2.61574679571018E-5,"NO"]
[null,"2018-04-14","16:22:00",84119480,"Short Rural","Planned",null,1,31.0833333333333,0,0,"NO"]
[null,"2018-04-15","07:57:00",60026690,"Urban","Vegetation","Grow-in - NSP responsibility",3,216.45000000000002,2.8707658028064402E-3,1.3262951271916999E-5,"NO"]
[null,"2018-04-15","10:14:00",25280514,"Short Rural","Asset failure","LV",66,194,3.1684834387102401E-2,1.6332388859331099E-4,"NO"]
[null,"2018-04-15","16:26:00",10129324,"Short Rural","Other","Trip & Manual Reclose - No Trigger Found",1108,133.71666666666698,0.36663259961313699,2.7418616448695301E-3,"NO"]
[null,"2018-04-16","04:32:00",40001142,"Urban","Other","Service Fuse",1,174.01666666666699,7.6932485683380903E-4,4.4209837573056797E-6,"NO"]
[null,"2018-04-16","06:02:00",84928162,"Short Rural","Animal","Animal impact",157,238.11666666666699,9.2511393490965599E-2,3.8851288650227001E-4,"NO"]
[null,"2018-04-16","09:35:00",10020765,"Short Rural","Animal","Animal impact",63,118.616666666667,1.8492347285977699E-2,1.55900075475433E-4,"NO"]
[null,"2018-04-16","13:36:00",50000159,"Long Rural","Overloads",null,1,112.85000000000001,1.4759351294794699E-3,1.30787339785509E-5,"NO"]
[null,"2018-04-16","16:17:00",30053833,"Short Rural","Asset failure","LV",1,162.70000000000002,4.0261813142623804E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-17","08:00:00",10020770,"Short Rural","Planned",null,6,16,0,0,"YES"]
[null,"2018-04-17","09:07:00",60026675,"Long Rural","Planned",null,1,103,0,0,"YES"]
[null,"2018-04-17","09:10:00",60026847,"Long Rural","Planned",null,2,254,0,0,"YES"]
[null,"2018-04-17","10:40:00",10132684,"Long Rural","Animal","Animal nesting/burrowing, etc and other",1,140.6,1.83886999738425E-3,1.30787339785509E-5,"YES"]
[null,"2018-04-17","15:55:00",50000208,"Short Rural","Other","Service Fuse",1,80.75,1.99824303089544E-4,2.4746043726259304E-6,"YES"]
[null,"2018-04-17","18:42:00",50000035,"Short Rural","Asset failure","Subtransmission",1080,200,0.53451454448719993,2.6725727224360001E-3,"YES"]
[null,"2018-04-17","18:42:00",82915259,"Short Rural","Asset failure","Subtransmission",2801,198,1.37241063584959,6.9313668477252195E-3,"YES"]
[null,"2018-04-18","07:30:00",50000170,"Short Rural","Other","Forced Corrective Maintenance",1,74,1.8312072357431903E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-18","08:54:00",82915259,"Short Rural","Other","Service Fuse",2,75.8333333333333,3.7531499651493201E-4,4.9492087452518498E-6,"NO"]
[null,"2018-04-18","10:20:00",40001094,"Urban","Planned",null,2,10,0,0,"NO"]
[null,"2018-04-18","14:18:00",20008373,"Short Rural","Other","Forced Corrective Maintenance",5,76.0833333333333,9.4138074675311303E-4,1.2373021863129598E-5,"NO"]
[null,"2018-04-18","20:58:00",20003088,"Short Rural","Other","Service Fuse",1,54.5833333333333,1.35072155339165E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-19","09:00:00",60026676,"Long Rural","Planned",null,7,196,0,0,"NO"]
[null,"2018-04-19","11:00:00",50000168,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2018-04-19","15:43:00",40000982,"Short Rural","Overloads",null,1,62.283333333333303,1.5412660900838499E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-20","07:15:00",60026745,"Short Rural","Animal","Animal impact",1,117.35000000000001,2.90394823127652E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-20","09:00:00",20007634,"Long Rural","Planned",null,2,362,0,0,"NO"]
[null,"2018-04-20","09:18:00",60026677,"Short Rural","Other","Service Fuse",1,135.88333333333301,3.3625749083365298E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-20","13:44:00",60026667,"Long Rural","Other","Forced Corrective Maintenance",1,87,1.13784985613393E-3,1.30787339785509E-5,"NO"]
[null,"2018-04-20","20:28:00",40001135,"Short Rural","Asset failure","LV",2,113.116666666667,5.5983799590040499E-4,4.9492087452518498E-6,"NO"]
[null,"2018-04-21","06:08:00",20002744,"Urban","Planned",null,1,420,0,0,"NO"]
[null,"2018-04-21","10:00:00",40001132,"Urban","Planned",null,6,63,0,0,"NO"]
[null,"2018-04-22","06:24:00",40001062,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",659,3.9666666666666703,3.4188246577731299E-2,8.618885691865032E-3,"NO"]
[null,"2018-04-22","08:31:00",50000185,"Short Rural","Planned",null,3,324,0,0,"NO"]
[null,"2018-04-22","17:16:00",85093128,"Short Rural","Other","Service Fuse",1,171.1,4.2340480815629601E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-23","07:16:00",82563123,"Urban","Animal","Animal impact",8,91.25,3.2273181428331401E-3,3.5367870058445404E-5,"NO"]
[null,"2018-04-23","09:45:00",40001061,"Long Rural","Planned",null,1,51,0,0,"NO"]
[null,"2018-04-23","12:43:00",30187535,"Short Rural","Other","Service Fuse",1,150.36666666666699,3.7209801083051803E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-23","18:02:00",20001108,"Urban","Overloads",null,1,99.133333333333297,4.3826685647423602E-4,4.4209837573056797E-6,"NO"]
[null,"2018-04-24","08:30:00",60026703,"Short Rural","Planned",null,2,8,0,0,"NO"]
[null,"2018-04-24","09:04:00",30053882,"Short Rural","Animal","Animal impact",1,93.600000000000009,2.3162296927778703E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-24","11:06:00",40001117,"Short Rural","Other","Fuse Operator - No Trigger Found",1,263.10000000000002,6.5106841043788104E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-24","14:53:00",20006799,"Short Rural","Other","Fuse Operator - No Trigger Found",1,79.883333333333297,1.9767964596660101E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-25","11:49:00",30053866,"Short Rural","Other","Service Fuse",2,80.3,3.9742146224372394E-4,4.9492087452518498E-6,"NO"]
[null,"2018-04-26","08:38:00",82647125,"Urban","Planned",null,61,32,0,0,"NO"]
[null,"2018-04-26","09:30:00",40001111,"Long Rural","Planned",null,1,259,0,0,"NO"]
[null,"2018-04-26","13:18:00",10020855,"Short Rural","Overloads",null,1,112.316666666667,2.7793931445210194E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-27","08:00:00",10020797,"Short Rural","Planned",null,1,47.999999999999993,0,0,"NO"]
[null,"2018-04-27","08:30:00",50000148,"Short Rural","Planned",null,4,29,0,0,"NO"]
[null,"2018-04-27","10:32:00",50000185,"Short Rural","Planned",null,58,148,0,0,"NO"]
[null,"2018-04-27","15:48:00",10020671,"Long Rural","Asset failure","LV",1,156.36666666666699,2.0450780364460698E-3,1.30787339785509E-5,"NO"]
[null,"2018-04-28","03:24:00",30053872,"Short Rural","Asset failure","Subtransmission",1520,64.233333333333306,0.241607173053208,3.7613986463914104E-3,"NO"]
[null,"2018-04-28","19:38:00",40001038,"Long Rural","Other","Trip & Manual Reclose - No Trigger Found",631,16.850000000000001,0.139057677216845,8.2526811404656005E-3,"NO"]
[null,"2018-04-29","14:14:00",50000165,"Short Rural","Other","Service Fuse",1,72.183333333333294,1.78625192297381E-4,2.4746043726259304E-6,"NO"]
[null,"2018-04-30","09:01:00",40001005,"Long Rural","Planned",null,2,196,0,0,"NO"]
[null,"2018-04-30","13:45:00",50000165,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-05-01","07:09:00",25267731,"Short Rural","Other","Service Fuse",1,64.933333333333294,1.6068431059584301E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-01","08:44:00",20006212,"Short Rural","Overloads",null,1,1397.9333333333302,3.4593319393062E-3,2.4746043726259304E-6,"NO"]
[null,"2018-05-01","09:20:00",20007634,"Long Rural","Planned",null,5,200,0,0,"NO"]
[null,"2018-05-01","11:57:00",50000093,"Long Rural","Other","Service Fuse",1,106.416666666667,1.3917952742174601E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-01","14:30:00",60026716,"Long Rural","Planned",null,1,40,0,0,"NO"]
[null,"2018-05-02","09:00:00",60026716,"Long Rural","Planned",null,2,373,0,0,"NO"]
[null,"2018-05-02","11:00:00",20004054,"Long Rural","Planned",null,2,20,0,0,"NO"]
[null,"2018-05-02","11:03:00",50000167,"Short Rural","Planned",null,2,4,0,0,"NO"]
[null,"2018-05-02","14:54:00",10020776,"Short Rural","Asset failure","Distribution substation",10,65.099999999999994,1.6109674465794798E-3,2.4746043726259301E-5,"NO"]
[null,"2018-05-03","08:13:00",20002149,"Short Rural","Other","Forced Corrective Maintenance",2,180,8.9085757414533403E-4,4.9492087452518498E-6,"NO"]
[null,"2018-05-03","08:31:00",40001118,"Long Rural","Planned",null,2,94,0,0,"NO"]
[null,"2018-05-03","10:00:00",50000127,"Long Rural","Planned",null,3,120,0,0,"NO"]
[null,"2018-05-03","13:00:00",60026754,"Short Rural","Planned",null,1,14,0,0,"NO"]
[null,"2018-05-03","14:30:00",10130452,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2018-05-04","06:22:00",40223076,"Long Rural","Other","Fuse Operator - No Trigger Found",2,153.61666666666699,4.0182230360101103E-3,2.61574679571018E-5,"NO"]
[null,"2018-05-04","10:00:00",30053867,"Short Rural","Planned",null,1,23,0,0,"NO"]
[null,"2018-05-04","11:00:00",30053817,"Urban","Planned",null,4,180,0,0,"NO"]
[null,"2018-05-05","02:43:00",10020838,"Urban","Asset failure","HV",945,125.86349206349202,0.5258362290776939,4.1778296506538607E-3,"NO"]
[null,"2018-05-05","09:28:00",10020755,"Long Rural","Network business","Switching and protection error",1,116.73333333333299,1.52672421309617E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-06","11:39:00",85018905,"Short Rural","Other","Service Fuse",2,269.85000000000002,1.3355439799062102E-3,4.9492087452518498E-6,"NO"]
[null,"2018-05-06","20:39:00",10020827,"Short Rural","Other","Forced Corrective Maintenance",1,33210.15,8.2181982405562903E-2,2.4746043726259304E-6,"NO"]
[null,"2018-05-07","12:46:00",40000965,"Short Rural","Asset failure","LV",1,1204.55,2.98078469704656E-3,2.4746043726259304E-6,"NO"]
[null,"2018-05-08","00:53:00",60026809,"Short Rural","Other","Fuse Operator - No Trigger Found",5,756.73333333333301,9.3630780778923006E-3,1.2373021863129598E-5,"NO"]
[null,"2018-05-08","08:30:00",83029792,"Short Rural","Asset failure","LV",1,176,4.35530369582163E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-08","09:35:00",50000127,"Long Rural","Asset failure","LV",2,144.70000000000002,3.7849856133926199E-3,2.61574679571018E-5,"NO"]
[null,"2018-05-08","18:36:00",20003949,"Long Rural","Overloads",null,36,24.594444444444399,1.15799110646089E-2,4.7083442322783201E-4,"NO"]
[null,"2018-05-09","08:28:00",50000142,"Short Rural","Other","Service Fuse",1,144.80000000000001,3.5832271315623405E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-09","09:26:00",50000034,"Short Rural","Planned",null,74,202,0,0,"NO"]
[null,"2018-05-09","13:00:00",30053807,"Short Rural","Other","Service Fuse",1,98.133333333333297,2.4284117576702402E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-09","15:31:00",50000020,"Short Rural","Asset failure","LV",1,103.583333333333,2.5632776959783597E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-10","08:37:00",10020804,"Short Rural","Animal","Animal impact",1,267.3,6.6146174880290999E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-10","09:08:00",50000036,"Short Rural","Planned",null,4,113,0,0,"NO"]
[null,"2018-05-10","12:14:00",40000974,"Long Rural","Overloads",null,1,80.116666666666703,1.0478245705815702E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-10","17:34:00",40001175,"Urban","Overloads",null,1,53.550000000000004,2.3674368020371901E-4,4.4209837573056797E-6,"NO"]
[null,"2018-05-11","08:35:00",60026816,"Long Rural","Planned",null,5,230,0,0,"NO"]
[null,"2018-05-11","08:43:00",20012178,"Short Rural","Planned",null,37,115,0,0,"NO"]
[null,"2018-05-11","13:39:00",10020764,"Short Rural","Other","Service Fuse",1,57.649999999999991,1.4266094208188502E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-11","14:40:00",84255558,"Short Rural","Planned",null,1,49.999999999999993,0,0,"NO"]
[null,"2018-05-12","11:53:00",40001011,"Long Rural","Planned",null,1,54.999999999999993,0,0,"NO"]
[null,"2018-05-12","16:30:00",81669226,"Short Rural","Planned",null,43,6.7441860465116301,0,0,"NO"]
[null,"2018-05-13","10:56:00",60026997,"Long Rural","Animal","Animal impact",1,91.6,1.19801203243526E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-13","19:05:00",20005336,"Urban","Asset failure","LV",1,818.56666666666706,3.6188699376051799E-3,4.4209837573056797E-6,"NO"]
[null,"2018-05-14","08:45:00",82773016,"Urban","Planned",null,2,30,0,0,"NO"]
[null,"2018-05-14","10:55:00",40001011,"Long Rural","Planned",null,1,70,0,0,"NO"]
[null,"2018-05-14","15:38:00",20006697,"Short Rural","Asset failure","Distribution substation",1,132.4,3.2763761893567298E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-15","08:19:00",50000133,"Long Rural","Planned",null,1,28,0,0,"NO"]
[null,"2018-05-15","08:36:00",20007497,"Short Rural","Planned",null,26,520,0,0,"NO"]
[null,"2018-05-15","10:30:00",82773016,"Urban","Planned",null,1,45,0,0,"NO"]
[null,"2018-05-15","13:00:00",60026650,"Long Rural","Planned",null,1,47,0,0,"NO"]
[null,"2018-05-15","15:03:00",82554035,"Short Rural","Third party","Vehicle impact",2,25.9,1.2818450650202301E-4,4.9492087452518498E-6,"NO"]
[null,"2018-05-16","08:16:00",20011420,"Short Rural","Planned",null,21,213,0,0,"NO"]
[null,"2018-05-16","09:00:00",50000050,"Short Rural","Planned",null,14,149.357142857143,0,0,"NO"]
[null,"2018-05-16","09:46:00",40001038,"Long Rural","Planned",null,2,33.999999999999993,0,0,"NO"]
[null,"2018-05-16","13:05:00",60026847,"Long Rural","Planned",null,2,32,0,0,"NO"]
[null,"2018-05-16","19:23:00",40001100,"Short Rural","Other","Fuse Operator - No Trigger Found",1,236.55,5.8536766434466299E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-17","08:48:00",50000241,"Long Rural","Planned",null,1,25,0,0,"NO"]
[null,"2018-05-17","10:00:00",50000032,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2018-05-17","11:56:00",50000030,"Short Rural","Planned",null,1,12,0,0,"NO"]
[null,"2018-05-17","15:48:00",40200483,"Long Rural","Other","Fuse Operator - No Trigger Found",1,97.5,1.2751765629087099E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-17","20:17:00",84375978,"Short Rural","Other","Service Fuse",1,123.683333333333,3.0606731748761702E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-18","08:30:00",30053817,"Urban","Planned",null,28,269,0,0,"NO"]
[null,"2018-05-18","09:20:00",82912277,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2018-05-18","12:30:00",82912277,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2018-05-18","16:18:00",20011515,"Short Rural","Animal","Animal impact",1,77.433333333333294,1.9161686525366801E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-19","08:31:00",10020780,"Short Rural","Planned",null,16,340,0,0,"NO"]
[null,"2018-05-20","07:03:00",20005605,"Urban","Planned",null,52,142,0,0,"NO"]
[null,"2018-05-20","09:00:00",60327522,"Urban","Planned",null,2,240,0,0,"NO"]
[null,"2018-05-20","18:58:00",10020797,"Short Rural","Animal","Animal impact",59,74.5,1.0877123519877302E-2,1.4600165798493001E-4,"NO"]
[null,"2018-05-21","08:15:00",10020655,"Short Rural","Planned",null,2,38.999999999999993,0,0,"NO"]
[null,"2018-05-21","10:00:00",60026756,"Short Rural","Planned",null,1,45,0,0,"NO"]
[null,"2018-05-21","12:35:00",20002494,"Short Rural","Other","Forced Corrective Maintenance",2,126,6.2360030190173298E-4,4.9492087452518498E-6,"NO"]
[null,"2018-05-21","19:36:00",20001962,"Short Rural","Other","Service Fuse",1,94.783333333333303,2.3455125111872702E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-22","08:31:00",20009882,"Short Rural","Planned",null,18,392.444444444444,0,0,"NO"]
[null,"2018-05-22","11:21:00",10020655,"Short Rural","Planned",null,1,32,0,0,"NO"]
[null,"2018-05-22","12:05:00",10020671,"Long Rural","Other","Forced Corrective Maintenance",149,181,0.35272037666753903,1.9487313628040802E-3,"NO"]
[null,"2018-05-22","14:16:00",60026670,"Long Rural","Planned",null,1,33,0,0,"NO"]
[null,"2018-05-23","08:30:00",60026692,"Short Rural","Planned",null,1,238,0,0,"NO"]
[null,"2018-05-23","09:24:00",60026994,"Long Rural","Planned",null,1,86,0,0,"NO"]
[null,"2018-05-23","11:16:00",50000235,"Short Rural","Planned",null,3,46,0,0,"NO"]
[null,"2018-05-23","12:42:00",82920982,"Short Rural","Other","Service Fuse",1,13.633333333333299,3.3737106280133503E-5,2.4746043726259304E-6,"NO"]
[null,"2018-05-23","19:39:00",40000974,"Long Rural","Other","Fuse Operator - No Trigger Found",1,123.9,1.62045513994245E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-24","08:26:00",30053878,"Short Rural","Other","Service Fuse",1,59.099999999999994,1.4624911842219199E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-24","09:00:00",60026667,"Long Rural","Planned",null,1,54.999999999999993,0,0,"NO"]
[null,"2018-05-24","10:58:00",60026756,"Short Rural","Planned",null,1,30,0,0,"NO"]
[null,"2018-05-24","19:07:00",10020836,"Short Rural","Other","Service Fuse",1,39.483333333333299,9.7705629312513695E-5,2.4746043726259304E-6,"NO"]
[null,"2018-05-25","08:55:00",30053840,"Short Rural","Planned",null,5,318.61,0,0,"NO"]
[null,"2018-05-25","09:17:00",10020836,"Short Rural","Overloads",null,1,37.383333333333304,9.2508960129999204E-5,2.4746043726259304E-6,"NO"]
[null,"2018-05-25","12:49:00",82915271,"Urban","Asset failure","LV",7,137.85,4.2660282766121098E-3,3.0946886301139703E-5,"NO"]
[null,"2018-05-26","07:22:00",60026990,"Long Rural","Other","Fuse Operator - No Trigger Found",1,142.916666666667,1.8691690644345603E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-26","10:25:00",40001116,"Long Rural","Other","Fuse Operator - No Trigger Found",1,92.216666666666697,1.20607725172203E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-27","06:40:00",40000977,"Long Rural","Other","Fuse Operator - No Trigger Found",1,155.13333333333301,2.0289475978725303E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-28","08:00:00",10020764,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2018-05-28","08:40:00",10020764,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2018-05-28","13:00:00",40001208,"Long Rural","Planned",null,2,10,0,0,"NO"]
[null,"2018-05-29","08:00:00",83877381,"Urban","Planned",null,57,350,0,0,"NO"]
[null,"2018-05-29","08:31:00",20006136,"Short Rural","Planned",null,53,288,0,0,"NO"]
[null,"2018-05-29","11:00:00",60026644,"Long Rural","Other","Forced Corrective Maintenance",1,82,1.0724561862411701E-3,1.30787339785509E-5,"NO"]
[null,"2018-05-29","13:20:00",40001208,"Long Rural","Planned",null,1,10,0,0,"NO"]
[null,"2018-05-30","07:30:00",82906978,"Urban","Planned",null,84,5,0,0,"NO"]
[null,"2018-05-30","09:00:00",60026824,"Short Rural","Planned",null,5,298.3,0,0,"NO"]
[null,"2018-05-30","09:38:00",50000035,"Short Rural","Planned",null,1,8,0,0,"NO"]
[null,"2018-05-30","12:28:00",10020772,"Long Rural","Other","Forced Corrective Maintenance",9,260.33333333333303,3.0643473711744699E-2,1.1770860580695802E-4,"NO"]
[null,"2018-05-30","16:09:00",20009956,"Short Rural","Other","Fuse Operator - No Trigger Found",1,74.983333333333306,1.8555408454073402E-4,2.4746043726259304E-6,"NO"]
[null,"2018-05-31","09:01:00",50000066,"Short Rural","Planned",null,2,179,0,0,"NO"]
[null,"2018-05-31","11:31:00",30053833,"Short Rural","Other","Forced Corrective Maintenance",10,10,2.4746043726259296E-4,2.4746043726259301E-5,"NO"]
[null,"2018-05-31","20:18:00",30053770,"Long Rural","Other","Service Fuse",1,134.46666666666698,1.7586537623158101E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-01","06:15:00",50000142,"Short Rural","Other","Service Fuse",1,147.31666666666698,3.6455046749400905E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-01","08:22:00",60026742,"Short Rural","Other","Vibration",4,170.333333333333,1.6860304458824601E-3,9.8984174905037098E-6,"NO"]
[null,"2018-06-01","09:00:00",60026816,"Long Rural","Planned",null,1,270,0,0,"NO"]
[null,"2018-06-01","11:30:00",30187133,"Urban","Planned",null,1,90,0,0,"NO"]
[null,"2018-06-01","14:18:00",10020780,"Short Rural","Third party","Vehicle impact",279,124.427538829152,8.5906591933614607E-2,6.9041461996263308E-4,"NO"]
[null,"2018-06-02","09:00:00",40001120,"Short Rural","Planned",null,241,68,0,0,"NO"]
[null,"2018-06-02","20:17:00",60026671,"Short Rural","Overloads",null,1,131,3.24173172813996E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-03","11:48:00",83022298,"Short Rural","Overloads",null,1,103.55,2.5624528278541498E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-03","12:30:00",10020828,"Long Rural","Planned",null,2,53,0,0,"NO"]
[null,"2018-06-04","09:09:00",20008686,"Long Rural","Planned",null,49,366.8,0,0,"NO"]
[null,"2018-06-04","10:12:00",82563751,"Short Rural","Planned",null,2,117,0,0,"NO"]
[null,"2018-06-04","23:28:00",20006697,"Short Rural","Asset failure","HV",255,92.193921568627502,5.8176587768030592E-2,6.3102411501961102E-4,"NO"]
[null,"2018-06-05","08:03:00",82563612,"Long Rural","Planned",null,7,196,0,0,"NO"]
[null,"2018-06-05","08:58:00",20006136,"Short Rural","Planned",null,2,27,0,0,"NO"]
[null,"2018-06-05","10:00:00",50000145,"Long Rural","Planned",null,5,43,0,0,"NO"]
[null,"2018-06-05","11:05:00",60026716,"Long Rural","Planned",null,1,35,0,0,"NO"]
[null,"2018-06-05","14:30:00",40001227,"Short Rural","Planned",null,1,10,0,0,"NO"]
[null,"2018-06-06","08:05:00",50000154,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-06-06","08:50:00",60026652,"Short Rural","Planned",null,18,380,0,0,"NO"]
[null,"2018-06-06","09:15:00",60026666,"Long Rural","Overloads",null,1,542.08333333333303,7.0897637108727901E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-06","10:30:00",50000195,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2018-06-06","13:31:00",10020842,"Short Rural","Exclusion - Customer Installation Fault",null,1,24,0,0,"NO"]
[null,"2018-06-06","16:30:00",50000168,"Short Rural","Planned",null,1,20,0,0,"NO"]
[null,"2018-06-07","08:30:00",10020673,"Long Rural","Planned",null,14,224,0,0,"NO"]
[null,"2018-06-07","09:07:00",10020806,"Long Rural","Other","Service Fuse",1,12.6666666666667,1.6566396372831102E-4,1.30787339785509E-5,"NO"]
[null,"2018-06-07","10:30:00",50000139,"Short Rural","Planned",null,19,45,0,0,"NO"]
[null,"2018-06-07","15:57:00",50000145,"Long Rural","Asset failure","LV",33,98.283333333333303,4.2418911849333003E-2,4.3159822129217897E-4,"NO"]
[null,"2018-06-08","08:30:00",40001207,"Short Rural","Planned",null,6,428,0,0,"NO"]
[null,"2018-06-08","09:15:00",20005265,"Short Rural","Planned",null,11,129,0,0,"NO"]
[null,"2018-06-08","12:25:00",60026891,"Long Rural","Planned",null,1,20,0,0,"NO"]
[null,"2018-06-08","12:52:00",25267735,"Short Rural","Other","Service Fuse",1,43.3,1.0715036933470301E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-09","10:04:00",60026715,"Short Rural","Other","Generation failure - Isolated",109,14,3.77624627262716E-3,2.6973187661622595E-4,"NO"]
[null,"2018-06-09","15:10:00",40001210,"Long Rural","Other","Forced Corrective Maintenance",583,31,0.23637195919435,7.6249019094951605E-3,"NO"]
[null,"2018-06-10","08:55:00",10130408,"Short Rural","Planned",null,3,218,0,0,"NO"]
[null,"2018-06-10","19:44:00",20005412,"Urban","Other","Service Fuse",2,98.683333333333294,8.7255482756689706E-4,8.8419675146113493E-6,"NO"]
[null,"2018-06-11","09:41:00",40001030,"Short Rural","Other","Fuse Operator - No Trigger Found",1,85.016666666666708,2.1038261507941403E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-11","09:50:00",82915231,"Urban","Planned",null,1,20,0,0,"NO"]
[null,"2018-06-11","13:59:00",60026990,"Long Rural","Other","Fuse Operator - No Trigger Found",1,67.316666666666706,8.8041677565611602E-4,1.30787339785509E-5,"NO"]
[null,"2018-06-12","08:27:00",10020831,"Short Rural","Planned",null,2,254,0,0,"NO"]
[null,"2018-06-12","09:10:00",30053771,"Short Rural","Other","Service Fuse",1,95.533333333333303,2.3640720439819702E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-12","10:30:00",50000086,"Short Rural","Planned",null,1,100,0,0,"NO"]
[null,"2018-06-12","13:27:00",40001210,"Long Rural","Other","Forced Corrective Maintenance",2,78,2.0402825006539402E-3,2.61574679571018E-5,"NO"]
[null,"2018-06-12","21:16:00",20004592,"Short Rural","Other","Service Fuse",1,61.466666666666697,1.52105682104074E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-13","08:01:00",40001117,"Short Rural","Planned",null,22,29,0,0,"NO"]
[null,"2018-06-13","09:00:00",40000961,"Long Rural","Planned",null,3,74,0,0,"NO"]
[null,"2018-06-13","10:48:00",50000016,"Short Rural","Planned",null,1,19,0,0,"NO"]
[null,"2018-06-13","16:38:00",50000166,"Urban","Other","Service Fuse",1,176.95000000000002,7.8229307585523896E-4,4.4209837573056797E-6,"NO"]
[null,"2018-06-13","19:19:00",10129324,"Short Rural","Overloads",null,1,98.75,2.4436718179681003E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-14","08:30:00",20012587,"Short Rural","Planned",null,2,5,0,0,"NO"]
[null,"2018-06-14","09:04:00",84928162,"Short Rural","Planned",null,21,218.57142857142901,0,0,"NO"]
[null,"2018-06-14","12:03:00",10020673,"Long Rural","Other","Service Fuse",2,165.13333333333301,4.3194698753160708E-3,2.61574679571018E-5,"NO"]
[null,"2018-06-14","19:03:00",50000208,"Short Rural","Other","Service Fuse",1,88.816666666666706,2.1978611169539301E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-15","08:00:00",50000092,"Short Rural","Planned",null,1,5,0,0,"NO"]
[null,"2018-06-15","08:35:00",60026750,"Short Rural","Planned",null,1,95,0,0,"NO"]
[null,"2018-06-15","10:00:00",40000975,"Long Rural","Other","Forced Corrective Maintenance",1,318,4.1590374051791801E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-15","12:30:00",50000208,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-06-16","10:51:00",40001177,"Short Rural","Third party","Vehicle impact",1,76.366666666666703,1.8897728725620003E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-17","08:01:00",10020783,"Urban","Planned",null,42,213,0,0,"NO"]
[null,"2018-06-17","14:09:00",60026821,"Long Rural","Asset failure","Distribution substation",1,187.28333333333299,2.4494288952829403E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-17","19:14:00",50000086,"Short Rural","Other","Service Fuse",21,21.933333333333298,1.1398027740315E-3,5.1966691825144498E-5,"NO"]
[null,"2018-06-18","09:30:00",40223073,"Long Rural","Planned",null,6,127,0,0,"NO"]
[null,"2018-06-18","10:45:00",50000193,"Short Rural","Planned",null,4,15,0,0,"NO"]
[null,"2018-06-18","16:18:00",82556069,"Short Rural","Asset failure","LV",1,106.26666666666701,2.6296795799771497E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-19","09:00:00",40001003,"Short Rural","Planned",null,56,304,0,0,"NO"]
[null,"2018-06-19","09:00:00",50000058,"Short Rural","Planned",null,7,319,0,0,"NO"]
[null,"2018-06-19","10:25:00",20011464,"Short Rural","Planned",null,1,332,0,0,"NO"]
[null,"2018-06-19","12:48:00",60026836,"Urban","Other","Service Fuse",1,74.599999999999994,3.2980538829500299E-4,4.4209837573056797E-6,"NO"]
[null,"2018-06-19","21:39:00",60027002,"Long Rural","Animal","Animal impact",1,142.4,1.8624117185456401E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-20","08:08:00",10020825,"Short Rural","Asset failure","Distribution substation",1,3.4166666666666701,8.4548982731385798E-6,2.4746043726259304E-6,"NO"]
[null,"2018-06-20","08:40:00",60026786,"Short Rural","Planned",null,1,25,0,0,"NO"]
[null,"2018-06-20","10:00:00",50000159,"Long Rural","Planned",null,1,180,0,0,"NO"]
[null,"2018-06-20","13:30:00",82889011,"Short Rural","Planned",null,1,15,0,0,"NO"]
[null,"2018-06-20","19:31:00",82554035,"Short Rural","Asset failure","LV",2,49.4166666666667,2.44573398827862E-4,4.9492087452518498E-6,"NO"]
[null,"2018-06-21","08:30:00",50000165,"Short Rural","Planned",null,1,90,0,0,"NO"]
[null,"2018-06-21","10:01:00",60026650,"Long Rural","Planned",null,12,163,0,0,"NO"]
[null,"2018-06-21","10:09:00",50000167,"Short Rural","Planned",null,1,6,0,0,"NO"]
[null,"2018-06-21","14:30:00",25275177,"Urban","Planned",null,3,5,0,0,"NO"]
[null,"2018-06-22","08:51:00",40000961,"Long Rural","Planned",null,27,166.666666666667,0,0,"NO"]
[null,"2018-06-22","11:17:00",60026697,"Short Rural","Other","Forced Corrective Maintenance",621,5.4166666666666687,8.3239504584204597E-3,1.5367293154007E-3,"NO"]
[null,"2018-06-22","17:09:00",30053765,"Long Rural","Overloads",null,1,95.633333333333297,1.25076292614875E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-23","08:31:00",30053773,"Short Rural","Animal","Animal impact",1,75.649999999999991,1.8720382078915102E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-23","16:27:00",60026833,"Short Rural","Other","Service Fuse",1,110.816666666667,2.7422740789316303E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-24","08:00:00",60026759,"Urban","Planned",null,3,705,0,0,"NO"]
[null,"2018-06-24","16:27:00",60026650,"Long Rural","Animal","Animal impact",1,52.683333333333302,6.8903130176998899E-4,1.30787339785509E-5,"NO"]
[null,"2018-06-25","10:10:00",50000130,"Long Rural","Planned",null,1,140,0,0,"NO"]
[null,"2018-06-25","14:45:00",10020655,"Short Rural","Planned",null,1,28,0,0,"NO"]
[null,"2018-06-26","07:08:00",40001098,"Short Rural","Other","Forced Corrective Maintenance",1,65,1.6084928422068501E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-26","08:30:00",50000148,"Short Rural","Planned",null,1,74,0,0,"NO"]
[null,"2018-06-26","09:04:00",10020817,"Short Rural","Other","Service Fuse",1,125.816666666667,3.1134647348255199E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-26","13:50:00",50000194,"Urban","Planned",null,1,5,0,0,"NO"]
[null,"2018-06-26","19:02:00",30053846,"Short Rural","Asset failure","LV",1,140.6,3.4792937479120504E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-27","00:36:00",40000973,"Long Rural","Other","Service Fuse",1,480.08333333333303,6.2788822042026309E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-27","07:28:00",20002494,"Short Rural","Third party","Vehicle impact",2,424.58333333333303,2.1013515464215204E-3,4.9492087452518498E-6,"NO"]
[null,"2018-06-27","08:07:00",50000178,"Urban","Other","Service Fuse",1,57.899999999999991,2.5597495954799896E-4,4.4209837573056797E-6,"NO"]
[null,"2018-06-27","09:04:00",50000054,"Short Rural","Planned",null,28,251,0,0,"NO"]
[null,"2018-06-27","11:51:00",40000962,"Long Rural","Overloads",null,1,191.26666666666699,2.5015258522975E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-27","14:49:00",10020660,"Short Rural","Asset failure","LV",1,7.55,1.8683263013325698E-5,2.4746043726259304E-6,"NO"]
[null,"2018-06-27","17:38:00",50000167,"Short Rural","Other","Vibration",1,52.133333333333304,1.29009374626232E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-27","21:08:00",25275177,"Urban","Other","Service Fuse",1,98.55,4.35687949282474E-4,4.4209837573056797E-6,"NO"]
[null,"2018-06-28","08:31:00",30053843,"Short Rural","Planned",null,4,163,0,0,"NO"]
[null,"2018-06-28","09:04:00",60026734,"Long Rural","Planned",null,1,47,0,0,"NO"]
[null,"2018-06-28","11:00:00",25273020,"Urban","Planned",null,1,15,0,0,"NO"]
[null,"2018-06-28","13:40:00",30053783,"Urban","Planned",null,1,30,0,0,"NO"]
[null,"2018-06-28","16:16:00",60026771,"Long Rural","Other","Service Fuse",1,138.55000000000001,1.8120585927282201E-3,1.30787339785509E-5,"NO"]
[null,"2018-06-29","08:30:00",10020827,"Short Rural","Planned",null,3,350,0,0,"NO"]
[null,"2018-06-29","11:00:00",50000125,"Long Rural","Planned",null,1,58,0,0,"NO"]
[null,"2018-06-29","14:04:00",60026809,"Short Rural","Other","Service Fuse",1,125.066666666667,3.0949052020308297E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-30","00:25:00",10020850,"Short Rural","Other","Service Fuse",1,109.48333333333299,2.7092793539632899E-4,2.4746043726259304E-6,"NO"]
[null,"2018-06-30","08:30:00",20009306,"Short Rural","Planned",null,307,360.89576547231303,0,0,"NO"]
[null,"2018-06-30","12:36:00",82554035,"Short Rural","Other","Service Fuse",1,66.466666666666711,1.6447870396720302E-4,2.4746043726259304E-6,"NO"]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]

{"sheet":"Amendments","index":25,"n_rows":3,"n_cols":4,"rows_kept":3,"cut":false,"hidden":false,"merged":[[1,1,1,3]]}
[null,"This sheet may be used to identify amendments made to data resubmitted to the AER."]
[null,"NSP data amendments"]
[null,"Worksheet","Table","Comments"]