## BOP
BOP ID | Tab ID | Tab Name | Table and Rule Allocation | Estimated / Actual | Data Source | Why Estimated – Provide justification | Methodology | Assumptions | Additional Comments | Consistency Information
EBR1 | 3.1 | Revenue | TABLE 3.1.1 - REVENUE GROUPING BY CHARGEABLE QUANTITY Revenue from Fixed Customer Charges [Standard Control Services] Revenue from Fixed Customer Charges [Alternative Control Services] Revenue from Energy Delivery charges where time of use is not a determinant [Standard Control Services] Revenue from Energy Delivery charges where time of use is not a determinant [Alternative Control Services] Revenue from On-Peak Energy Delivery charges [Standard Control Services] Revenue from On-Peak Energy Delivery charges [Alternative Control Services] Revenue from Shoulder period Energy Delivery Charges [Standard Control Services] Revenue from Shoulder period Energy Delivery Charges [Alternative Control Services] Revenue from Off-Peak Energy Delivery charges [Standard Control Services] Revenue from Off-Peak Energy Delivery charges [Alternative Control Services] Revenue from controlled load customer charges [Standard Control Services] Revenue from controlled load customer charges [Alternative Control Services] Revenue from unmetered supplies [Standard Control Services] Revenue from unmetered supplies [Alternative Control Services] Revenue from Contracted Maximum Demand charges [Standard Control Services] Revenue from Contracted Maximum Demand charges [Alternative Control Services] Revenue from Measured Maximum Demand charges [Standard Control Services] Revenue from Measured Maximum Demand charges [Alternative Control Services] Revenue from metering charges [Standard Control Services] Revenue from metering charges [Alternative Control Services] Revenue from connection charges [Standard Control Services] Revenue from connection charges [Alternative Control Services] Revenue from public lighting charges [Standard Control Services] Revenue from public lighting charges [Alternative Control Services] | Actual | ORACLE VELOCITY |  | Data is based on the billing data from Velocity and equates to the actual reads for the period and as per AER requirements only DUoS is recorded. Adjustments including unreads and recoveries for Transmission & Jurisdictional recoveries is excluded. This is recorded against other sources which is done so the consolidated result equals the aged trial balance for that financial year.
EBR2 | 3.1 | Revenue | TABLE 3.1.1 - REVENUE GROUPING BY CHARGEABLE QUANTITY Revenue from other Sources [Standard Control Services] Revenue from other Sources [Alternative Control Services] | Actual | ORACLE VELOCITY
EBR3 | 3.1 | Revenue | TABLE 3.1.2 - REVENUE GROUPING BY CUSTOMER TYPE OR CLASS Revenue from residential Customers [Standard Control Services] Revenue from residential Customers [Alternative Control Services] Revenue from Non residential customers not on demand tariffs [Standard Control Services] Revenue from Non residential customers not on demand tariffs [Alternative Control Services] Revenue from Non-residential low voltage demand tariff customers [Standard Control Services] Revenue from Non-residential low voltage demand tariff customers [Alternative Control Services] Revenue from Non-residential high voltage demand tariff customers [Standard Control Services] Revenue from Non-residential high voltage demand tariff customers [Alternative Control Services] Revenue from unmetered supplies [Standard Control Services] Revenue from unmetered supplies [Alternative Control Services] | Actual | ORACLE VELOCITY |  | Data is based on the billing data from Velocity and equates to the actual reads for the period and as per AER requirements only DUoS is recorded. Adjustments including unreads and recoveries for Transmission & Jurisdictional recoveries is excluded. This is recorded against other sources which is done so the consolidated result equals the aged trial balance for that financial year.
EBR4 | 3.1 | Revenue | TABLE 3.1.2 - REVENUE GROUPING BY CUSTOMER TYPE OR CLASS Revenue from Other Customers [Standard Control Services] Revenue from Other Customers [Alternative Control Services] | Actual | ORACLE
EBR5 | 3.1 | Revenue | TABLE 3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES EBSS [Standard Control Services] EBSS [Alternative Control Services] | Actual | It is not applicable to Evoenergy for 2014-19 regulatory period
EBR6 | 3.1 | Revenue | TABLE 3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES STPIS [Standard Control Services] STPIS [Alternative Control Services] | Actual |  |  | To calculate STPIS revenue, the Evoenergy Electricity Distribution Final Decision PTRM revenue is multiplied by the approved S-factor (0.975) for the year 2019-20. For the S-factor, refer to AER final S-factor model for Evoenergy ('S-factor sheet row 30).
EBR7 | 3.1 | Revenue | TABLE 3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES F-Factor [Standard Control Services] F-Factor [Alternative Control Services] | Actual | It is not applicable to Evoenergy for 2014-19 regulatory period
EBR8 | 3.1 | Revenue | TABLE 3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES S-Factor True up [Standard Control Services] S-Factor True up [Alternative Control Services] | Actual |  |  | To calculate STPIS revenue, the Evoenergy Electricity Distribution Final Decision PTRM revenue is multiplied by the approved S-factor (0.975) for the year 2019-20. For the S-factor, refer to AER final S-factor model for Evoenergy ('S-factor sheet row 30).
EBR9 | 3.1 | Revenue | TABLE 3.1.3 - REVENUE (penalties) ALLOWED (deducted) THROUGH INCENTIVE SCHEMES Other [Standard Control Services] Other [Alternative Control Services] | Actual | It is not applicable to Evoenergy for 2014-19 regulatory period
EBO1 | 3.2 | Operating Expenditure | TABLE 3.2.1 - CURRENT OPEX CATEGORIES AND COST ALLOCATIONS TABLE 3.2.2 - OPEX CONSISTENCY - CURRENT COST ALLOCATION APPROACH | Actual | ORACLE |  | Total Expenditure at an activity level from ORACLE, then adjusted to reverse the accounting treatment for depreciation on corporate assets.
EBO2 | 3.2 | Operating Expenditure | TABLE 3.2.4 - OPEX FOR HIGH VOLTAGE CUSTOMERS | Estimated | VELOCITY Spreadsheet Calculation |  | VELOCITY: Total High Voltage (HV) customers from VELOCITY report is filtered by tariff code '122'. This network charge is appropriate for large customers taking supply at HV where the customer owns and is fully responsible for their own low voltage network and where the customer owns and is responsible for their HV assets (including transformers and switch gear - see Evoenergy Schedule of Electricity Network Charges for full tariff code description). HV customer data includes maximum kVA per connection customer, and connection dates where these occurred since 2005. Assumptions: As no data is held on private customer HV assets, the following assumptions were made to develop an asset base for estimating costs: 1. Customers with a demand over 5000kVA and/or a connection voltage of 66kV or above have a zone substation to reduce voltages to distribution level, typically 11kV, excluding generators. 2. Customers with a demand less than 5000kVA and connection voltage of less than 66kV have no zone substation to reduce voltages for connection to distribution substations. 3. The number of zone substations as per assumption 1 above is one per connection. 4. The number of distribution substations is one per 500kVA of demand or part thereof. 5. No allowance has been made for overhead or underground circuits or switch gear as there is no basis on which to determine this. Formula: Average estimated annual opex per sub (based on normal maintenance activities for a zone sub) then total cost per year summed to give total estimated annual OPEX per sub. The average of the total estimated annual opex for all zone subs (used for this query) Formula: Total estimated annual opex x CPI index base x number of HV customers (total subs) = expenditure
EBP1 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS TABLE 3.2.3 - PROVISIONS Opening balance (the carrying amount at the beginning of the period) [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Closing balance (carrying amount at the end of the period) [Value ($0's)] | Actual | ORACLE |  | Taken directly from Evoenergy's balance sheet.
EBP2 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] TABLE 3.2.3 - PROVISIONS | Actual | N/A |  | Evoenergy does not have any capital provisions
EBP3 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS Opening balance (the carrying amount at the beginning of the period) [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Closing balance (carrying amount at the end of the period) [Value ($0's)] TABLE 3.2.3 - PROVISIONS | Actual | ORACLE |  | Taken directly from Evoenergy's balance sheet.
EBP4 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS TABLE 3.2.3 - PROVISIONS Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] | Actual | N/A |  | Evoenergy does not have any capital provisions
EBP5 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS TABLE 3.2.3 - PROVISIONS Opening balance (the carrying amount at the beginning of the period) [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] | Actual | ORACLE |  | Taken directly from Evoenergy's balance sheet.
EBP6 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] TABLE 3.2.3 - PROVISIONS | Actual | N/A |  | Evoenergy does not have any capital provisions
EBP7 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS Opening balance (the carrying amount at the beginning of the period) [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Closing balance (carrying amount at the end of the period) [Value ($0's)] TABLE 3.2.3 - PROVISIONS | Actual | ORACLE |  | Taken directly from Evoenergy's balance sheet.
EBP8 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS TABLE 3.2.3 - PROVISIONS Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] | Actual | N/A |  | Evoenergy does not have any capital provisions
EBP9 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS TABLE 3.2.3 - PROVISIONS Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Opening balance (the carrying amount at the beginning of the period) [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Opex component [Value ($0's)] Closing balance (carrying amount at the end of the period) [Value ($0's)] | Actual | ORACLE |  | Taken directly from Evoenergy's balance sheet.
EBP10 | 3.2.3 | Provisions | TABLE 3.2.3 - PROVISIONS Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] Capex component [Value ($0's)] TABLE 3.2.3 - PROVISIONS | Actual | N/A |  | Evoenergy does not have any capital provisions
3.3BOP1 | 3.3 | Assets (RAB) | TABLE 3.3.1 - REGULATORY ASSET BASE VALUES | Estimated | ORACLE Calculated data | Estimated due to use of modelling assumptions as per AER guidelines. | Values are a combination of regulatory asset base values (which are effected by past determinations), actual capex during the current reg period, and forecast depreciation and inflation rates. The value of the RAB from the AER's 2009, 2015 and 2019 distribution determinations, with dual function assets separated, are rolled forward using historical capex and forecast depreciation/inflation. Data is sourced directly from the RFM in the majority of cases. The 2009 opening RAB is sourced from the 2015 distribution determination RFMs. Of the categories in the RFMs, the 'opening distribution assets' category is proportionally split across the categories in the RIN using the same proportions as in the modelling underlying the economic benchmarking RIN submitted in 2014 - i.e.: based on actual data (asset register) as at 2009 June 30. Capex figures have been updated for actual outcome in 2019/20 sourced from ORACLE. The calculation of the asset categories in the RAB takes the capital project expenditure for 2019/20 then calculates percentages for each asset type based on the capitalisation of projects for the period starting 2014 from the fixed asset register (FAR). It would then be sense checked if the allocation represents what is being installed. Adjustments will be made as needed to reconcile the allocation to what is being installed. Every project for 2019/20 is allocated to a project type in Oracle and based on this we assume a calculated proportion to each asset category based on the project type. | See above. |  | See above
3.3BOP2 | 3.3 | Assets (RAB) | TABLE 3.3.2 - ASSET VALUE ROLL FORWARD | Estimated | Calculated data |  | For the 2009-14 regulatory period, numbers are sourced directly from or as simple additions of relevant values in the 2015 distribution determination RFMs. Of the categories in the RFMs, the 'opening distribution assets' category is proportionally split across the categories in the RIN using the same proportions as in the modelling underlying the economic benchmarking RIN submitted in 2014 - i.e.: based on actual data (asset register) as at 2009 June 30. For the 2014-19 and current regulatory periods, capex figures have been updated for actual outcomes sourced from ORACLE Financials, rolled forward using the RFM roll forward. | See above. |  | See above.
3.3BOP3 | 3.3 | Assets (RAB) | TABLE 3.3.3 - TOTAL DISAGGREGATED RAB ASSET VALUES | Estimated | Calculated data |  | Average of opening and closing RAB values in this category
3.3BOP4 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED SERVICE LIFE OF NEW ASSETS) Overhead network assets less than 33kV (wires and poles) [Service Life (Years)] Overhead network assets less than 33kV (wires and poles) [Service Life (Years)] Overhead network assets less than 33kV (wires and poles) [Service Life (Years)] Underground network assets less than 33kV (cables) [Service Life (Years)] Underground network assets less than 33kV (cables) [Service Life (Years)] Underground network assets less than 33kV (cables) [Service Life (Years)] Distribution substations including transformers [Service Life (Years)] Distribution substations including transformers [Service Life (Years)] Distribution substations including transformers [Service Life (Years)] Overhead network assets 33kV and above (wires and towers / poles etc) [Service Life (Years)] Overhead network assets 33kV and above (wires and towers / poles etc) [Service Life (Years)] Overhead network assets 33kV and above (wires and towers / poles etc) [Service Life (Years)] Underground network assets 33kV and above(cables, ducts etc) [Service Life (Years)] Underground network assets 33kV and above(cables, ducts etc) [Service Life (Years)] Underground network assets 33kV and above(cables, ducts etc) [Service Life (Years)] Zone substations and transformers [Service Life (Years)] Zone substations and transformers [Service Life (Years)] Zone substations and transformers [Service Life (Years)] | Actual | RIVA CA RIN 5.2 |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to the estimated service life of new assets to each category to data calculated using the assets' standard design life. This approach is consistent with legislation and is based on the specified manufacturer standard design life for each asset. This data is considered to be estimated as it is based on the assets' standard design life derived from specified manufacturer standard designs.
3.3BOP5 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED SERVICE LIFE OF NEW ASSETS) Meters [Service Life (Years)] Meters [Service Life (Years)] Meters [Service Life (Years)] | Estimated | VELOCITY Evoenergy Metering Asset Management Plan (MAMP) |  | Evoenergy applies a standard 20 year design life for electronic meters based on our experience with other electronic devices operating within the network therefore where the age exceeds the expected life, the age of this meter is set to 20 years. Evoenergy perform asset testing and inspections in accordance with the MAMP that feeds into condition based assessments to identify assets for replacement. The replacement strategy is outlined in section 1.14 of the MAMP.
3.3BOP6 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED SERVICE LIFE OF NEW ASSETS) "Other" assets with long lives [Service Life (Years)] "Other" assets with long lives [Service Life (Years)] "Other" assets with long lives [Service Life (Years)] | Estimated |  |  | Evoenergy has applied a weighted standard life methodology based on standard lives as per the RFM/PTRM, with 2018/19 CAPEX as the weight (refer to below). This data is considered to be estimated as it is derived from the average age of an asset with a long life, applying a weighted average used in the RFM. The RAB asset categories included in 'Other (long term)' assets are based on greater than 10 years. They are: 'Buildings', 'IT & Communication Systems (Networks)'; and 'Equity raising costs'. Land has been excluded as it does not depreciate and so has no real age. The average age of new assets is calculated as the weighted standard life used in the RFM/PTRM using the capex in 2018/19 as the weight.
3.3BOP7 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED SERVICE LIFE OF NEW ASSETS) "Other" assets with short lives [Service Life (Years)] "Other" assets with short lives [Service Life (Years)] "Other" assets with short lives [Service Life (Years)] | Estimated |  |  | Evoenergy has applied a weighted standard life methodology based on standard lives as per the RFM/PTRM, with 2018/19 CAPEX as the weight (refer to below). This data is considered to be estimated as it is derived from the average age of an asset with a long life, applying a weighted average used in the RFM. The RAB asset categories for 'Other (short term)' assets are based on less than 10 years. They are: IT & Communication Systems (Networks); Motor Vehicles; Other Non-System Assets (Networks); IT Systems (Corporate); Telecommunications (Corporate); Other Non-System Assets (Corporate). The average age of new assets is calculated as the weighted standard life used in the RFM/PTRM using the capex in 2018/19 as the weight.
3.3BOP8 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED RESIDUAL SERVICE LIFE) Overhead network assets less than 33kV (wires and poles) [Service Life (Years)] Overhead network assets less than 33kV (wires and poles) [Service Life (Years)] Overhead network assets less than 33kV (wires and poles) [Service Life (Years)] Underground network assets less than 33kV (cables) [Service Life (Years)] Underground network assets less than 33kV (cables) [Service Life (Years)] Underground network assets less than 33kV (cables) [Service Life (Years)] Distribution substations including transformers [Service Life (Years)] Distribution substations including transformers [Service Life (Years)] Distribution substations including transformers [Service Life (Years)] Overhead network assets 33kV and above (wires and towers / poles etc) [Service Life (Years)] Overhead network assets 33kV and above (wires and towers / poles etc) [Service Life (Years)] Overhead network assets 33kV and above (wires and towers / poles etc) [Service Life (Years)] Underground network assets 33kV and above (cables, ducts etc) [Service Life (Years)] Underground network assets 33kV and above (cables, ducts etc) [Service Life (Years)] Underground network assets 33kV and above (cables, ducts etc) [Service Life (Years)] Zone substations and transformers [Service Life (Years)] Zone substations and transformers [Service Life (Years)] Zone substations and transformers [Service Life (Years)] | Actual | RIVA CA RIN 5.2 and 2.8 |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to the estimated residual service life of assets to each category (e.g. overhead less than 33kV, distribution substations including transformers) to data calculated for provision in table 3.3.4, using the methodology described below and data shown in CA RIN 5.2 and CA RIN 2.8. This data is considered to be estimated as it is based on the expected asset life shown in EB RIN 3.3.4.1 and the estimated replacement cost of the asset. Methodology for Overhead assets only: On the basis of replacement costs, average lives and expected lives. 1) n is number of asset in category j ; 2) RCi,j is the replacement cost of asset I in category j; 3) TRCj is the sum of the replacement costs all assets in category j; 4) ELi,j is the expected life of asset I in category j. * Data source for n and ELi,j: CA RIN: 5.2 Asset Age Profile and data source for RCi,j and TRCj: RIVA Estimated residual service life = Expected life when new - Sum over all assets in category of (age of each asset * estimated replacement cost of the asset /sum of replacement costs of all assets in the category). Methodology for UG cables, Distribution Substation and Zone Substation: Estimated residual service life = Expected Life when new* - Average serviced life** * Expected Life when new for UG cables, Distribution Substation and Zone Substation category are sourced from EB RIN 3.3.4.1 ** Average serviced life for UG cables, Distribution Substation and Zone Substation category are sourced from CA RIN 2.8 Maintenance, please refer to CA RIN 2.8 for methodology, definitions and calculations.
3.3BOP9 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED RESIDUAL SERVICE LIFE) Meters [Service Life (Years)] Meters [Service Life (Years)] Meters [Service Life (Years)] | Actual | VELOCITY Evoenergy Metering Asset Management Plan (MAMP) |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to the estimated residual service life of metering assets to data calculated for provision in EB RIN 3.3.4. Evoenergy apply a standard 20 year design life for electronic meters based on our experience with other electronic devices operating within the network, therefore where the age exceeds the expected life, the age of this meter is set to 20 years. Evoenergy perform asset testing and inspections in accordance with the MAMP that feed into condition based assessments to identify assets for replacement. The replacement strategy is outlined in section 1.14 of the MAMP. This data is considered to be actual as it is derived from the assets' standard design life derived from specified manufacturer standard designs. Sum over all assets in category of ((expected total lifetime of each asset when new - age of each asset) * estimated replacement cost of the asset )) /(sum of replacement costs of all assets in the category)
3.3BOP10 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED RESIDUAL SERVICE LIFE) "Other" assets with long lives [Service Life (Years)] "Other" assets with long lives [Service Life (Years)] "Other" assets with long lives [Service Life (Years)] | Estimated |  |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to the estimated residual service life of metering assets to data calculated for provision in EB RIN 3.3.4. Evoenergy has applied a weighted standard life methodology in the 2019-24 RFM with 2019/20 CAPEX as the weight. Evoenergy considers this reasonable as it is consistent with legislation and based on the latest RFM model approved by the AER. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered to be estimated as it is derived from the average age of an asset with a short life, applying a weighted average used in the RFM/PTRM. The RAB asset categories included in 'Other (long term)' assets are based on greater than 10 years: 'Buildings', 'IT & Communication Systems (Networks)' and 'Equity raising costs'. Land has been excluded as it does not depreciate and so has no real age. The average age of new assets is calculated as the weighted standard life used in the PTRM using the capex in 2019/20 as the weight.
3.3BOP11 | 3.3 | Assets (RAB) | TABLE 3.3.4 - ASSET LIVES (ESTIMATED RESIDUAL SERVICE LIFE) "Other" assets with short lives [Service Life (Years)] "Other" assets with short lives [Service Life (Years)] "Other" assets with short lives [Service Life (Years)] | Estimated |  |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to the estimated residual service life of metering assets to data calculated for provision in EB RIN 3.3.4. Evoenergy has applied a weighted standard life methodology in the 2019-24 RFM with 2019/20 CAPEX as the weight. Evoenergy considers this reasonable as it is consistent with legislation and based on the latest RFM model approved by the AER. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered to be estimated as it is derived from the average age of an asset with a short life, applying a weighted average used in the RFM/PTRM. The RAB asset categories for 'Other (short term)' assets are based on less than 10 years: Motor Vehicles; Other Non-System Assets (Networks); IT Systems (Corporate); Telecommunications (Corporate); Other Non-System Assets (Corporate). The average age of new assets is calculated as the weighted standard life used in the PTRM using the capex in 2019/20 as the weight. The residual life estimate for asset type i is calculated as tres;i = t0;i where t0;i is the estimated service life for a new asset of type i, and ti is the average age of a type i asset. The estimated lives for new assets t0;i are given in table "EB RIN 3.3.4 - Asset lives (estimated service life of new assets)". In agreement with Evoenergy's methodology from previous years, the average age of a type i asset is â¢ given in table "CA RIN 2.8.1 - Descriptor metrics for routine and nonroutine maintenance" for underground assets (DRAB1502, DRAB1505, DRAB1506) and distribution substations including transformers (DRAB1503), and â¢ calculated from asset age profile data in table "CA RIN 5.2.1 - Asset age profile" for LV and HV overhead assets (DRAB1501, DRAB1504).
EOD1 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Total energy delivered [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy delivery by chargeable quantity where time of use is not a determinant to data calculated for provision in EB RIN 3.4.1.1, using a straight data extract from VELOCITY (energy supplied from TNSP and embedded generation from metered data for reporting FY) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation and previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered to be actual as it is actual metering data from VELOCITY. VELOCITY: Energy supplied from TNSP's & Embedded Generation from metered data. A calculated line loss is formulated based on five year analysis of billed/delivered energy. The calculated total energy delivered is allocated to different groupings firstly based on groups that are read monthly & the remainder allocated to the group "Energy Delivery where time of use is not a determinant".
EOD2 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy Delivery where time of use is not a determinant [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy delivery by chargeable quantity where time of use is not a determinant to data calculated for provision in EB RIN 3.4.1.1, using a straight data extract from VELOCITY (energy supplied from TNSP and embedded generation from metered data for reporting FY) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation and previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered to be actual as it is actual metering data from VELOCITY. VELOCITY: Energy supplied from TNSP's & Embedded Generation from metered data. A calculated line loss is formulated based on five year analysis of billed/delivered energy. The calculated total energy delivered is allocated to different groupings firstly based on groups that are read monthly & the remainder allocated to the group "Energy Delivery where time of use is not a determinant".
EOD3 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy Delivery at On-peak times [Standard Control Services] Energy Delivery at Shoulder times [Standard Control Services] Energy Delivery at Off-peak times [Standard Control Services] Controlled load energy deliveries [Standard Control Services] Energy Delivery to unmetered supplies [Standard Control Services] | Actual |  |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy delivery (grouped by chargeable quantity) received into DNSP system to data calculated for provision in EB RIN 3.4.1.1, using a straight data extract from VELOCITY (grouped by on-peak/shoulder/off-peak times published by Evoenergy in Electricity Network Schedule of Charges) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation, based on times and charges approved by the AER, and aligns with previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered to be actual as it is actual metering data from VELOCITY. VELOCITY: Billed meter data is entered into TM1 and grouped by Network Tariff. Interval metered data is grouped into on-peak, shoulder & Off-peak. Unmetered & controlled load come straight from billed data. The remainder is entered as energy delivered where time of use is not a determinant.
EOD4 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy into DNSP network at On-peak times [Standard Control Services] Energy into DNSP network at Shoulder times [Standard Control Services] Energy into DNSP network at Off-peak times [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy received into DNSP system to data calculated for provision in EB RIN 3.4.1.2, using a straight data extract from VELOCITY (grouped by on-peak/shoulder/off-peak times published by Evoenergy in Electricity Network Schedule of Charges) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation, based on times and charges approved by the AER, and aligns with previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered 'Actual' as it is actual metering data from VELOCITY. VELOCITY: The monthly report is to show the highest clocked half hour kW demand and kWh energy for each TNI for each month in the reporting period. It also reports the monthly consumption broken down by period.
EOD5 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy received from TNSP and other DNSPs not included in the above categories [Standard Control Services] | Actual
EOD6 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy into DNSP network at On-peak times from non-residential embedded generation [Standard Control Services] Energy into DNSP network at Shoulder times from non-residential embedded generation [Standard Control Services] Energy into DNSP network at Off-peak times from non-residential embedded generation [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy received into DNSP system from non-residential embedded generation to data calculated for provision in EB RIN 3.4.1.3, using a straight data extract from VELOCITY (grouped by on-peak/shoulder/off-peak times published by Evoenergy in Electricity Network Schedule of Charges) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation, based on times and charges approved by the AER, and aligns with previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered 'Actual' as it is actual metering data from VELOCITY. VELOCITY: Metering data for large generators which have time of use meters. Data grouped based on time of generation using times from TNSPs.
EOD7 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy received from embedded generation not included in above categories from non-residential embedded generation [Standard Control Services] | Actual |  |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy received into DNSP system from non-residential embedded generation to data calculated for provision in EB RIN 3.4.1.3, using a straight data extract from VELOCITY (not grouped by on-peak/shoulder/off-peak times published by Evoenergy in Electricity Network Schedule of Charges) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation, based on times and charges approved by the AER, and aligns with previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology. This data is considered 'Actual' as it is actual metering data from VELOCITY. VELOCITY: Data collected from metered photovoltaic sites which are non-residential. Meters are not read as time of use.
EOD8 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy into DNSP network at On-peak times from residential embedded generation [Standard Control Services] Energy into DNSP network at Shoulder times from residential embedded generation [Standard Control Services] Energy into DNSP network at Off-peak times from residential embedded generation [Standard Control Services] | Actual
EOD9 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Energy received from embedded generation not included in above categories from residential embedded generation [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy received into DNSP system from residential embedded generation to data calculated for provision in EB RIN 3.4.1.3, using a straight data extract from VELOCITY (not grouped by on-peak times published by Evoenergy in Electricity Network Schedule of Charges) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation , based on times and charges approved by the AER, and aligns with previous years methodologies. Evoenergy also considers this reliable as there exists sufficient and appropriate supporting documentation to present in support of the methodology, and the information itself was prepared by competent, capable and objective Evoenergy staff (role: Planning and Analysis Manager). This data is considered 'Actual' as it is actual metering data from VELOCITY. VELOCITY: Data collected from metered photovoltaic sites which are residential. Meters are not read as time of use.
EOD10 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Residential customers energy deliveries [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy delivery for residential customers by customer class or type to data calculated for provision in table 3.4.1.4, using a straight data extract from VELOCITY (energy supplied from TNSP and embedded generation from metered data for reporting FY) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation and previous years methodologies. This data is considered 'Actual' as it is actual metering data from VELOCITY. VELOCITY: Energy supplied from TNSP's & Embedded Generation from metered data. A calculated line loss is formulated based on five year analysis of billed/delivered energy. The calculated total energy delivered is allocated to different groupings firstly based on groups that are read monthly & the remainder allocated to the group "Energy Delivery where time of use is not a determinant".
EOD11 | 3.4 | Operational Data | TABLE 3.4.1 - ENERGY DELIVERY Non residential customers not on demand tariffs energy deliveries [Standard Control Services] Non-residential low voltage demand tariff customers energy deliveries [Standard Control Services] Non-residential high voltage demand tariff customers energy deliveries [Standard Control Services] Other Customer Class Energy Deliveries [Standard Control Services] | Actual | VELOCITY |  | Evoenergy has applied the requirements, definitions and calculation methodology relating to energy delivery (grouped by chargeable quantity) received into DNSP system for non-residential customers to data calculated for provision in EB RIN 3.4.1.4, using a straight data extract from VELOCITY (grouped by on-peak/shoulder/off-peak times published by Evoenergy in Electricity Network Schedule of Charges) to derive the numbers. Evoenergy considers this reasonable as it is consistent with legislation , based on times and charges approved by the AER, and aligns with previous years methodologies. This data is considered 'Actual' as it is actual metering data from VELOCITY. VELOCITY: Billed meter data is entered into TM1 and grouped by Network Tariff. Network Tariffs are then grouped into each customer type or class. The remainder is entered as residential customers.
EOD12 | 3.4 | Operational Data | TABLE 3.4.2 - CUSTOMER NUMBERS Residential customer numbers [Standard Control Services] Non residential customers not on demand tariff customer numbers [Standard Control Services] Low voltage demand tariff customer numbers [Standard Control Services] High voltage demand tariff customer numbers [Standard Control Services] Unmetered Customer Numbers [Standard Control Services] Other Customer Numbers [Standard Control Services] | Actual | ArcFM GIS VELOCITY SQL Report: Customer Count by Feeder |  | The SQL report provides the customers connected to each feeder. This report also has the feeder network type classification (Urban, Short Rural). The number of customers for each network type is totalled providing the ratio of customers for each network type. This ratio is then applied against the authoritative total number of customers (from Velocity) to give the customers by network type.
EOD13 | 3.4 | Operational Data | TABLE 3.4.2 - CUSTOMER NUMBERS Customers on CBD network [Standard Control Services] Customers on Urban network [Standard Control Services] Customers on Short rural network [Standard Control Services] Customers on Long rural network [Standard Control Services] | Actual | ArcFM GIS VELOCITY ADMS SQL Report: Customer Count by Feeder |  | The authoritative total number of network customers is extracted from Velocity. To determine the number of customers by network type, distribution feeder classifications are determined from feeder lengths (SQL Report: Customer Count by Feeder) and the feeder maximum demand (ADMS). Feeder classifications are applied according to the definition in AER Distribution Reliability Measures Guideline 2018. The number of customers connected to each distribution feeder is extracted (SQL Report: Customer Count by Feeder). The number of customers for each network type is calculated by applying the ratio of customers by network type from SQL Report: Customer Count by Feeder, to the authoritative total number of network customers from Velocity.
EOD14 | 3.4 | Operational Data | TABLE 3.4.3 - SYSTEM DEMAND Non-coincident Summated Raw System Annual Maximum Demand [Standard Control Services] Coincident Raw System Annual Maximum Demand [Standard Control Services] Non-coincident Summated Raw System Annual Maximum Demand [Standard Control Services] Coincident Raw System Annual Maximum Demand [Standard Control Services] Non-coincident Summated Raw System Annual Maximum Demand [Standard Control Services] Coincident Raw System Annual Maximum Demand [Standard Control Services] Non-coincident Summated Raw System Annual Maximum Demand [Standard Control Services] Coincident Raw System Annual Maximum Demand [Standard Control Services] Average power factor conversion for 11 kV lines [Standard Control Services] Average power factor conversion for 66 kV lines [Standard Control Services] | Actual | Raw data for tables - EB RIN Table 3.4.3.1-4 - CA RIN Table 5.3.1 - CA RIN Table 5.4.1 are directly extracted as Excel sheets for every financial year via the SQL Server Reporting Services (SSRS) from the Velocity database, through Electricity Networks > Velocity Reports > Meter Data Management Reports > Zone Sub 15 Minute Data Report Data give - active (real) energy consumption (in kWh), - reactive energy consumption (in kVARh), - active (real) energy generation (in kWh), and - reactive energy generation (in kVARh) measured over 15 minute intervals for all zone substations and bulk supply points ("Canberra Bulk Supply", "Queanbeyan Bulk Supply", "Williamsdale Bulk Supply"). Note that "Williamsdale Bulk Supply" does not measure reactive consumption. |  | Raw data processing Raw data processing involves the following steps: 1. Duplicate data for "QueanbeyanBulkSupply" and change name of second (duplicated) set to "XXXX-Fyshwick"; this is because "Queanbeyan Bulk Supply" supplies only Fyshwick ZSS, and we can take "Queanbeyan Bulk Supply" data to be "Fyshwick" data on the zone substation level. Note however that Queanbeyan bulk supply data is measured at 66 kV and data at the zone substation level is measured at 11 kV. This needs to be taken into account when estimating power factors at different voltages. 2. Group data from zone substations (ZSS), bulk supply points by adding a `name_group` column 3. Rename all ZSSs by stripping leading "\\w{4}-". 4. Remove unnecessary variables. 5. Replace all `NA` values with zero's; this is justified because we are only interested in MD. 6. Convert real and reactive energies to powers (assuming constant power over the time interval). 7. Rename variables: Load: E Stream (kWh) -> real_power B Stream (kVARh) -> reactive power Generation: B Stream (kWh) -> gen_real_power K Stream (kVARh) -> gen_reactive power 8. Reshape power data from long to wide. 9. Calculate apparent power from real and reactive power. 10. Infer apparent power for "Williamsdale Bulk Supply" (which does not measure reactive energy) by using the power factor from "Canberra Bulk Supply" for the same time period. Following raw data processing, outliers are removed from the apparent power data for every asset (i.e. every zone substation and bulk supply point). This is done using the seasonal hybrid extreme Studentised deviate (S-H-ESD) method developed by Vallis et al. from Twitter. Definitions We define maximum demand (MD) as the maximum apparent power in MVA; all other quantities (active power in MW, time & date of MD) are taken at the time & date of the maximum apparent power. Evoenergy does not maintain any subtransmission substations, so any MD characteristics pertaining to "Subtransmission substations" are left blank in CA RIN Table 5.4.1. Evoenergy's transmission connection points are at the zone substations. Any MD characteristic that is based on "transmission connection point" data is derived using zone substation data (EB RIN 3.4.3.2, EB RIN 3.4.3.4, CA RIN 5.3.1). Power factor estimation Average overall network power factor conversion between MVA and MW: In alignment with previous year's methodologies, this is the average power factor for the 132 kV lines, and is considered an estimate because no reactive power/energy readings are available at the Williamsdale bulk supply point. The only 132 kV bulk supply point with reactive energy data (and revenue metering) is Canberra bulk supply. For the power factor calculation, daily data from Canberra bulk supply are used. Average power factor conversion for low voltage distribution lines: Evoenergy only measures current and voltage to the feeder point. As a result, power factors of LV distribution lines can not be estimated robustly and the field is reported as NA. Average power factor conversion for 11 kV lines: This is the average power factor calculated from daily real and apparent power data from all zone substations except Fyshwick; Fyshwick was excluded because data for Fyshwick was derived from the 66 kV data from Queanbeyan bulk supply. Average power factor conversion for 22 kV lines: Evoenergy has two 22 kV distribution feeders (Cotter and Tidbinbilla) supplied through Woden zone substation. Since Evoenergy only measures current and voltage to the feeder point, Woden zone substation real and reactive data are used to provide an estimate of the average power factor at Woden zone substation. Average power factor conversion for 66 kV lines: This is the average power factor calculated from daily real and apparent power data measured at Queanbeyan bulk supply. Average power factor conversion for 132 kV lines: This is the average power factor calculated from daily real and apparent power data measured at Canberra bulk supply. Weather correction Weather correction was carried out from the bottom-up at the level of every asset (zone substation, bulk supply point); the methodology is in alignment with the weather correction methodology described in section 5.3 of the 2013 Connection Point Forecasting report from Acil Allen Consulting to the AER. 1. First, for each season of the current financial year, we fit a linear model to the daily MD as a function of a temperature variable (HDD in winter, SDD in summer), day of the week and holiday. The HDD and CDD are defined relative to a base-line temperature of 18.5 degree Celsius. 2. We then simulate weather data based on historic data from the last 25 years recorded at 2 weather stations Tuggeranong and Canberra Airport from the Bureau of Meteorology: For every financial year and season we repeatedly (K = 100) draw N = 1000 weather bootstrap samples. 3. For every k = 1,...,K we calculate a maximum seasonal & annual bootstrap MD from all K MDs obtained through the regression model from step 1. We account for variability in both seasonal MDs during the current financial year and historic weather variability. 4. The weather-corrected MDs with a 10%, 50% and 90% probability of exceedance (PoE) are then given by the 90%, 50% and 10% quantiles, respectively, of the distribution of all bootstrap samples. We obtain seasonal MD 10%, 50% and 90% PoE scaling factors based on the seasonal maximum demand for every asset, and use the same scaling factor to calculate weather-corrected MD's in MVA and MW (i.e. the maximum apparent power and active power at the point of time where maximum apparent power has occurred). |  |  | Methodology and data provided are in alignment with definitions & requirements laid out by the AER Category Analysis and Economic Benchmarking RIN guidelines.
EOD15 | 3.4 | Operational Data | TABLE 3.4.3 - SYSTEM DEMAND Non-coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Non-coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 10% POE [Standard Control Services] Coincident Weather Adjusted System Annual Maximum Demand 50% POE [Standard Control Services] Average overall network power factor conversion between MVA and MW [Standard Control Services] Average power factor conversion for low voltage distribution lines [Standard Control Services] Average power factor conversion for SWER lines [Standard Control Services] Average power factor conversion for 22 kV lines [Standard Control Services] Average power factor conversion for 33 kV lines [Standard Control Services] Average power factor conversion for 132 kV lines [Standard Control Services] | Estimated | Raw data for tables - EB RIN Table 3.4.3.1-4 - CA RIN Table 5.3.1 - CA RIN Table 5.4.1 are directly extracted as Excel sheets for every financial year via the SQL Server Reporting Services (SSRS) from the Velocity database, through Electricity Networks > Velocity Reports > Meter Data Management Reports > Zone Sub 15 Minute Data Report Data give - active (real) energy consumption (in kWh), - reactive energy consumption (in kVARh), - active (real) energy generation (in kWh), and - reactive energy generation (in kVARh) measured over 15 minute intervals for all zone substations and bulk supply points ("Canberra Bulk Supply", "Queanbeyan Bulk Supply", "Williamsdale Bulk Supply"). Note that "Williamsdale Bulk Supply" does not measure reactive consumption. |  | Raw data processing Raw data processing involves the following steps: 1. Duplicate data for "QueanbeyanBulkSupply" and change name of second (duplicated) set to "XXXX-Fyshwick"; this is because "Queanbeyan Bulk Supply" supplies only Fyshwick ZSS, and we can take "Queanbeyan Bulk Supply" data to be "Fyshwick" data on the zone substation level. Note however that Queanbeyan bulk supply data is measured at 66 kV and data at the zone substation level is measured at 11 kV. This needs to be taken into account when estimating power factors at different voltages. 2. Group data from zone substations (ZSS), bulk supply points by adding a `name_group` column 3. Rename all ZSSs by stripping leading "\\w{4}-". 4. Remove unnecessary variables. 5. Replace all `NA` values with zero's; this is justified because we are only interested in MD. 6. Convert real and reactive energies to powers (assuming constant power over the time interval). 7. Rename variables: Load: E Stream (kWh) -> real_power B Stream (kVARh) -> reactive power Generation: B Stream (kWh) -> gen_real_power K Stream (kVARh) -> gen_reactive power 8. Reshape power data from long to wide. 9. Calculate apparent power from real and reactive power. 10. Infer apparent power for "Williamsdale Bulk Supply" (which does not measure reactive energy) by using the power factor from "Canberra Bulk Supply" for the same time period. Following raw data processing, outliers are removed from the apparent power data for every asset (i.e. every zone substation and bulk supply point). This is done using the seasonal hybrid extreme Studentised deviate (S-H-ESD) method developed by Vallis et al. from Twitter. Definitions We define maximum demand (MD) as the maximum apparent power in MVA; all other quantities (active power in MW, time & date of MD) are taken at the time & date of the maximum apparent power. Evoenergy does not maintain any subtransmission substations, so any MD characteristics pertaining to "Subtransmission substations" are left blank in CA RIN Table 5.4.1. Evoenergy's transmission connection points are at the zone substations. Any MD characteristic that is based on "transmission connection point" data is derived using zone substation data (EB RIN 3.4.3.2, EB RIN 3.4.3.4, CA RIN 5.3.1). Power factor estimation Average overall network power factor conversion between MVA and MW: In alignment with previous year's methodologies, this is the average power factor for the 132 kV lines, and is considered an estimate because no reactive power/energy readings are available at the Williamsdale bulk supply point. The only 132 kV bulk supply point with reactive energy data (and revenue metering) is Canberra bulk supply. For the power factor calculation, daily data from Canberra bulk supply are used. Average power factor conversion for low voltage distribution lines: Evoenergy only measures current and voltage to the feeder point. As a result, power factors of LV distribution lines can not be estimated robustly and the field is reported as NA. Average power factor conversion for 11 kV lines: This is the average power factor calculated from daily real and apparent power data from all zone substations except Fyshwick; Fyshwick was excluded because data for Fyshwick was derived from the 66 kV data from Queanbeyan bulk supply. Average power factor conversion for 22 kV lines: Evoenergy has two 22 kV distribution feeders (Cotter and Tidbinbilla) supplied through Woden zone substation. Since Evoenergy only measures current and voltage to the feeder point, Woden zone substation real and reactive data are used to provide an estimate of the average power factor at Woden zone substation. Average power factor conversion for 66 kV lines: This is the average power factor calculated from daily real and apparent power data measured at Queanbeyan bulk supply. Average power factor conversion for 132 kV lines: This is the average power factor calculated from daily real and apparent power data measured at Canberra bulk supply. Weather correction Weather correction was carried out from the bottom-up at the level of every asset (zone substation, bulk supply point); the methodology is in alignment with the weather correction methodology described in section 5.3 of the 2013 Connection Point Forecasting report from Acil Allen Consulting to the AER. 1. First, for each season of the current financial year, we fit a linear model to the daily MD as a function of a temperature variable (HDD in winter, SDD in summer), day of the week and holiday. The HDD and CDD are defined relative to a base-line temperature of 18.5 degree Celsius. 2. We then simulate weather data based on historic data from the last 25 years recorded at 2 weather stations Tuggeranong and Canberra Airport from the Bureau of Meteorology: For every financial year and season we repeatedly (K = 100) draw N = 1000 weather bootstrap samples. 3. For every k = 1,...,K we calculate a maximum seasonal & annual bootstrap MD from all K MDs obtained through the regression model from step 1. We account for variability in both seasonal MDs during the current financial year and historic weather variability. 4. The weather-corrected MDs with a 10%, 50% and 90% probability of exceedance (PoE) are then given by the 90%, 50% and 10% quantiles, respectively, of the distribution of all bootstrap samples. We obtain seasonal MD 10%, 50% and 90% PoE scaling factors based on the seasonal maximum demand for every asset, and use the same scaling factor to calculate weather-corrected MD's in MVA and MW (i.e. the maximum apparent power and active power at the point of time where maximum apparent power has occurred). |  |  | Methodology and data provided are in alignment with definitions & requirements laid out by the AER Category Analysis and Economic Benchmarking RIN guidelines.
EOD16 | 3.4 | Operational Data | TABLE 3.4.3 - SYSTEM DEMAND Summated Chargeable Contracted Maximum Demand [Standard Control Services] Summated Chargeable Measured Maximum Demand [Standard Control Services] | Actual |  |  | Evoenergy does not use MW measure to charge customers.
EOD17 | 3.4 | Operational Data | TABLE 3.4.3 - SYSTEM DEMAND Summated Chargeable Contracted Maximum Demand [Standard Control Services] | Actual |  |  | Evoenergy does not have customers who are charged on a contracted maximum.
EOD18 | 3.4 | Operational Data | TABLE 3.4.3 - SYSTEM DEMAND Summated Chargeable Measured Maximum Demand [Standard Control Services] | Actual | VELOCITY |  | A report is generated from VELOCITY of all billing records for reporting FY, filtered by demand tariff type and summed by measured maximum demand.
EPA1 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead low voltage distribution [Volume in KM's (0's)] (DPA0101) | Actual | ArcFM (GIS) |  | From ArcFM feature class - Overhead LV Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Sum by line length. Summarised in the RIN SQL report "Overhead Conductors Attributes"
EPA2 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 2.2 kV [Volume in KM's (0's)] (DPA0102) | Actual | Evoenergy does not have 2.2 kV lines
EPA3 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 6.6kv [Volume in KM's (0's)] (DPA0103) | Actual | Evoenergy does not have 6.6 kV lines
EPA4 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 7.6 kV [Volume in KM's (0's)] (DPA0104) | Actual | Evoenergy does not have 7.6 kV lines
EPA5 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 11 kV [Volume in KM's (0's)] (DPA0105) | Actual | ArcFM (GIS) |  | From ArcFM feature class - Overhead HV Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 11kV; Sum by line length. Summarised in the RIN SQL report "Overhead Conductors Attributes"
EPA6 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 11 kV [Volume in KM's (0's)] (DPA0105) | Actual | Evoenergy does not have SWER lines
EPA7 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 22 kV [Volume in KM's (0's)] (DPA0107) | Actual | ArcFM (GIS) |  | From ArcFM feature class - Overhead HV Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 11kV; Sum by line length. Summarised in the RIN SQL report "Overhead Conductors Attributes"
EPA8 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 33 kV [Volume in KM's (0's)] (DPA0108) | Actual | Evoenergy does not have 33 kV lines
EPA9 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 44 kV [Volume in KM's (0's)] (DPA0109) | Actual | Evoenergy does not have 44 kV lines
EPA10 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 66 kV [Volume in KM's (0's)] (DPA0110) | Actual | ArcFM (GIS) |  | From ArcFM feature class - Overhead Transmission Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 66kV; Sum by line length. Summarised in the RIN SQL report "Overhead Conductors Attributes"
EPA11 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 110kV [Volume in KM's (0's)] (DPA0111) | Actual | Evoenergy does not have 110 kV lines
EPA12 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 132 kV [Volume in KM's (0's)] (DPA0112) | Actual | ArcFM (GIS) |  | From ArcFM feature class - Overhead Transmission Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 132kV; Sum by line length. Summarised in the RIN SQL report "Overhead Conductors Attributes"
EPA13 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 220kV [Volume in KM's (0's)] (DPA0113) | Actual | Evoenergy does not have 220 kV lines
EPA14 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Other [Volume in KM's (0's)] (DPA0114) | Actual | Evoenergy does not have other voltage lines
EPA15 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground low voltage distribution [Volume in KM's (0's)] (DPA0201) | Actual | ArcFM (GIS) |  | From ArcFM feature class - UG LV Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Sum by line length. Summarised in the RIN SQL report "Underground Cables Attributes"
EPA16 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 5 kV [Volume in KM's (0's)] (DPA0202) | Actual | Evoenergy does not have 5 kV lines
EPA17 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 6.6 Kv [Volume in KM's (0's)] (DPA0203) | Actual | Evoenergy does not have 6.6 kV lines
EPA18 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 7.6 kV [Volume in KM's (0's)] (DPA0204) | Actual | Evoenergy does not have 7.6 kV lines
EPA19 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 11 kV [Volume in KM's (0's)] (DPA0205) | Actual | ArcFM (GIS) |  | From ArcFM feature class - UG HV Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 11kV; Sum by line length. Summarised in the RIN SQL report "Underground Cables Attributes"
EPA20 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground SWER [Volume in KM's (0's)] (DPA0206) | Actual | Evoenergy does not have SWER lines
EPA21 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 22 kV [Volume in KM's (0's)] (DPA0207) | Actual | ArcFM (GIS) |  | From ArcFM feature class - UG Transmission Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 132kV; Sum by line length. Summarised in the RIN SQL report "Underground Cables Attributes"
EPA22 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 33 kV [Volume in KM's (0's)] (DPA0208) | Actual | Evoenergy does not have 33 kV lines
EPA23 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 66 kV [Volume in KM's (0's)] (DPA0209) | Actual | Evoenergy does not have 66 kV lines
EPA24 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 110 kV [Volume in KM's (0's)] (DPA0210) | Actual | Evoenergy does not have 110 kV lines
EPA25 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 132 kV [Volume in KM's (0's)] (DPA0211) | Actual | ArcFM (GIS) |  | From ArcFM feature class - UG Transmission Electric Line. Filter using Lifecycle = Inservice; Owner = AAD; Operating Voltage = 132kV; Sum by line length. Summarised in the RIN SQL report "Underground Cables Attributes"
EPA26 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Other [Volume in KM's (0's)] (DPA0212) | Actual | Evoenergy does not have other voltage lines
EPA27 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead low voltage distribution [Volume in MVA (0's)] (DPA0301) | Actual | ArcFM GIS database |  | From ArcFM database - Overhead LV Electric Line. The MVA = I(A) Ã â3 Ã VL-L(V) for each conductor type. The sum of the MVA x length for each cable types divided by the total length is the weighted average.
EPA28 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 6.6 kV [Volume in MVA (0's)] (DPA0302) | Actual | Evoenergy does not have 6.6 kV lines
EPA29 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 7.6 kV [Volume in MVA (0's)] (DPA0303) | Actual | Evoenergy does not have 7.6 kV lines
EPA30 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 11 kV [Volume in MVA (0's)] (DPA0304) | Actual | ArcFM GIS database |  | From ArcFM database - Overhead HV Electric Line. Using the Electrical Data Manual for continuous current rating; The MVA = I(A) Ã â3 Ã VL-L(V). The sum of the MVA x length for each cable types divided by the total length is the weighted average
EPA31 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead SWER [Volume in MVA (0's)] (DPA0305) | Actual | Evoenergy does not have SWER lines
EPA32 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 22 kV [Volume in MVA (0's)] (DPA0306) | Actual | ArcFM GIS database |  | From ArcFM database - Overhead HV Electric Line. Using the Electrical Data Manual for continuous current rating; The MVA = I(A) Ã â3 Ã VL-L(V). The sum of the MVA x length for each cable types divided by the total length is the weighted average
EPA33 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 33 kV [Volume in MVA (0's)] (DPA0307) | Actual | Evoenergy does not have 33 kV lines
EPA34 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 44 kV [Volume in MVA (0's)] (DPA0308) | Actual | Evoenergy does not have 44 kV lines
EPA35 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 66 kV [Volume in MVA (0's)] (DPA0309) | Actual | ArcFM GIS database |  | From ArcFM database - Overhead Transmission Line Using the Electrical Data Manual for continuous current rating; The MVA = I(A) Ã â3 Ã VL-L(V). The sum of the MVA x length for each cable types divided by the Total Length is the Weighted average. 3 phase kVA to amps calculation formula.
EPA36 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 110 kV [Volume in MVA (0's)] (DPA0310) | Actual | Evoenergy does not have 110 kV lines
EPA37 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 132 kV [Volume in MVA (0's)] (DPA0311) | Actual | ArcFM GIS database |  | From ArcFM database - Overhead Transmission Line Using the Electrical Data Manual for continuous current rating; The MVA = I(A) Ã â3 Ã VL-L(V). The sum of the MVA x length for each cable types divided by the Total Length is the Weighted average. 3 phase kVA to amps calculation formula.
EPA38 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Overhead 220 kV [Volume in MVA (0's)] (DPA0312) | Actual | Evoenergy does not have 220 kV lines
EPA39 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Other [Volume in MVA (0's)] (DPA0313) | Actual | Evoenergy does not have other voltage lines
EPA40 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground low voltage distribution [Volume in MVA (0's)] (DPA0401) | Actual | ArcFM GIS |  | From ArcFM database - Underground LV Electric Line. The MVA = I(A) Ã â3 Ã VL-L(V) for each cable types. The sum of the MVA x length for each cable types divided by the total length is the weighted average.
EPA41 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 5 kV [Volume in MVA (0's)] (DPA0402) | Actual | Evoenergy does not have 5 kV lines
EPA42 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 6.6 kV [Volume in MVA (0's)] (DPA0403) | Actual | Evoenergy does not have 6.6 kV lines
EPA43 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 7.6 kV [Volume in MVA (0's)] (DPA0404) | Actual | Evoenergy does not have 7.6 kV lines
EPA44 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 11 kV [Volume in MVA (0's)] (DPA0405) | Actual | ArcFM GIS |  | From ArcFM database - Underground HV Electric Line. The MVA = I(A) Ã â3 Ã VL-L(V) for each cable types. The sum of the MVA x length for each cable types divided by the total length is the weighted average. 3 phase kVA to amps calculation formula.
EPA45 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground SWER [Volume in MVA (0's)] (DPA0406) | Actual | Evoenergy does not have SWER lines
EPA46 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 12.7 kV [Volume in MVA (0's)] (DPA0407) | Actual | Evoenergy does not have 12.7 kV lines
EPA47 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 22 kV [Volume in MVA (0's)] (DPA0408) | Actual | ArcFM GIS |  | From ArcFM database - Underground HV Electric Line. The MVA = I(A) Ã â3 Ã VL-L(V) for each cable types. The sum of the MVA x length for each cable types divided by the total length is the weighted average. 3 phase kVA to amps calculation formula.
EPA48 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 33 kV [Volume in MVA (0's)] (DPA0409) | Actual | Evoenergy does not have 33 kV lines
EPA49 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 66 kV [Volume in MVA (0's)] (DPA0410) | Actual | Evoenergy does not have 66 kV lines
EPA50 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 110 kV [Volume in MVA (0's)] (DPA0411) | Actual | Evoenergy does not have 110 kV lines |  | Evoenergy does not have 110 kV lines
EPA51 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Underground 132 kV [Volume in MVA (0's)] (DPA0412) | Actual | vArcFM GIS |  | From ArcFM database - Underground HV Electric Line. The MVA = I(A) Ã â3 Ã VL-L(V) for each cable types. The sum of the MVA x length for each cable types divided by the total length is the weighted average. 3 phase kVA to amps calculation formula.
EPA52 | 3.5 | Physical Assets | TABLE 3.5.1 - NETWORK CAPACITIES Other [Volume in MVA (0's)] (DPA0413) | Actual | Evoenergy does not have other voltage lines
EPA53 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Distribution transformer capacity owned by utility [Volume in MVA's (0's)] (DPA0501) | Actual | ORACLE SQL Query |  | From SQL Server Reporting Services - Transformers (Distribution) MVA. Sum of Transformers (Distribution) MVA and Cold spare capacity (DPA0503)
EPA54 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Distribution transformer capacity owned by High Voltage Customers [Volume in MVA's (0's)] (DPA0502) | Actual | HV customer account manager records |  | This is the distribution transformer capacity in substations which supply Tariff 122 customers.
EPA55 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Cold spare capacity included in DPA0501 [Volume in MVA's (0's)] (DPA0503) | Actual | ORACLE |  | From Oracle Database; Stock at warehouse as at end of FY. Note - The AER definitions of transformers, mentions that auxiliary transformers are to be removed to be removed
EPA56 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Total installed capacity for first step transformation where there are two steps to reach distribution voltage [Volume in MVA's (0's)] (DPA0601) | Actual | Evoenergy does not have power transformers with two steps to reach distribution voltage |  | N/A
EPA57 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Total installed capacity for second step transformation where there are two steps to reach distribution voltage [Volume in MVA's (0's)] (DPA0602) | Actual | Evoenergy does not have power transformers with two steps to reach distribution voltage |  | N/A
EPA58 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Total zone substation transformer capacity where there is only a single step transformation to reach distribution voltage [Volume in MVA's (0's)] (DPA0603) | Actual |  |  | From SQL RIN Report "Transformers (Power) Attributes" From ArcFM GIS Database for the zone power transformers, considering rated capacity of the transformer summated to get this data. Same query used where data is reported under RIN CA 5.2 Asset Age Profile.
EPA59 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Total zone substation transformer capacity [Volume in MVA's (0's)] (DPA0604) | Actual |  |  | From SQL RIN Report "Transformers (Power) Attributes" From ArcFM GIS Database for the zone power transformers, considering rated capacity of the transformer summated to get this data. Same query used where data is reported under RIN CA 5.2 Asset Age Profile.
EPA60 | 3.5 | Physical Assets | TABLE 3.5.2 - TRANSFORMER CAPACITIES Cold spare capacity of zone substation transformers included in DPA0604 [Volume in MVA's (0's)] (DPA0605) | Actual | Evoenergy does not have cold spare capacity. |  | N/A
EQS1 | 3.6 | Quality of Service | TABLE 3.6.1 - RELIABILITY Whole of network unplanned SAIDI [(0's)] Whole of network unplanned SAIDI excluding excluded outages [(0's)] Whole of network unplanned SAIFI [(0's)] Whole of network unplanned SAIFI excluding excluded outages [(0's)] | Actual | ArcFM GIS ADMS VELOCITY |  | Outage Data: ADMS Report - Premise Outages Extract ADMS Report - Incident Summary Customer Data: Velocity ArcFM Report - Customer Count by Feeder Evoenergy confirms reliability calculations are made in accordance with the AER's Distribution Reliability Measures Guideline and AER Electricity distribution network service providers Service target performance incentive scheme Version 2.0. SAIDI is the sum of the duration of each unplanned sustained interruption (in minutes) divided by the total number of distribution customers. SAIDI excludes momentary interruptions (three minutes or less). The number of distribution customer used to derive SAIDI reflect the relevant network type and the average of the number of customer at the beginning of the reporting period and the number of customers at the end of the reporting period. SAIFI is the total number of each unplanned sustained interruption divided by the total number of distribution customers. SAIFI excluded momentary interruption (three minutes or less)). SAIFI is expressed per 1 interruption. The number of distribution customer used to derive SAIFI reflect the relevant network type and the average of the number of customer at the beginning of the reporting period and the number of customers at the end of the reporting period. Whole Network - Total Distribution customers (from Velocity) Network Classification (Urban): Total Urban Customers (from ArcFM - Customer Count by Feeder) Network Classification (Short Rural): Total Short Rural Customers (from ArcFM - Customer Count by Feeder) Note: The underlying data extracted from ArcFM for feeder classifications (e.g. rural, urban) is actual and allowed Evoenergy to determine the network classification ratio of distribution customers.
EQS2 | 3.6 | Quality of Service | TABLE 3.6.1 - RELIABILITY Whole of network unplanned SAIDI [(0's)] Whole of network unplanned SAIDI excluding excluded outages [(0's)] Whole of network unplanned SAIFI [(0's)] Whole of network unplanned SAIFI excluding excluded outages [(0's)] | Actual | ArcFM GIS ADMS VELOCITY |  | Outage Data: ADMS Report - Premise Outages Extract ADMS Report - Incident Summary Customer Data: Velocity ArcFM Report - Customer Count by Feeder MED Data: Evoenergy monthly reliability forecast report Evoenergy confirms reliability calculations are made in accordance with the AER's Distribution Reliability Measures Guideline and AER Electricity distribution network service providers Service target performance incentive scheme Version 2.0. SAIDI is the sum of the duration of each unplanned sustained interruption (in minutes) divided by the total number of distribution customers. SAIDI excludes momentary interruptions (three minutes or less). The number of distribution customer used to derive SAIDI reflect the relevant network type and the average of the number of customer at the beginning of the reporting period and the number of customers at the end of the reporting period. SAIFI is the total number of each unplanned sustained interruption divided by the total number of distribution customers. SAIFI excluded momentary interruption (three minutes or less)). SAIFI is expressed per 1 interruption. The number of distribution customer used to derive SAIFI reflect the relevant network type and the average of the number of customer at the beginning of the reporting period and the number of customers at the end of the reporting period. Whole Network - Total Distribution customers (from Velocity) Network Classification (Urban): Total Urban Customers (from ArcFM - Customer Count by Feeder) Network Classification (Short Rural): Total Short Rural Customers (from ArcFM - Customer Count by Feeder) Note: The underlying data extracted from ArcFM for feeder classifications (e.g. rural, urban) is actual and allowed Evoenergy to determine the network classification ratio of distribution customers. MED exclusions: Major Event Day's are excluded from the calculation by excluding all outage incidents which occurred on the day(s) deemed to be an MED. An MED is deemed by the unplanned SAIDI for any one day exceeds the MED threshold. MEDs are calculated in an internal report, Evoenergy monthly reliability forecast report. Days determined as an MED in this report are used in RIN.
EQS3 | 3.6 | Quality of Service | TABLE 3.6.2 - ENERGY NOT SUPPLIED | Actual | ADMS |  | Outage Data: ADMS Report - Premise Outages Extract ADMS Report - Incident Summary Energy not supplied The energy not supplied is calculated for each customer for each outage. This is calculated in ADMS from customer consumption profiles and outage start and end times. The total energy not supplied is calculated summing the energy not supplied to each customer for each incident. Incidents are classified as planned or unplanned based on the incident cause.
EQS4 | 3.6 | Quality of Service | TABLE 3.6.3 - SYSTEM LOSSES | Actual | Calculated data |  | Evoenergy has applied the requirements and definitions relating to system losses to data provided in EB RIN 3.6.3, calculated from dependent variables in EB RIN 3.4. These have been applied by Evoenergy in accordance with requirements of the Economic Benchmarking RIN (stated above). As such all methodologies, definitions and application to calculations used to derive system losses are linked to table 3.4 as required. Formula: DQS03 = 1- (DOPED01 / Sum of all values in Tables 3.4.1.2 and 3.4.1.3)
EQS5 | 3.6 | Quality of Service | TABLE 3.6.4 - CAPACITY UTILISATION | Actual | EB RIN 3.4.3.3 and 5.4 |  | Network Classification (Urban): Total Urban Customers (from ArcFM - Customer Count by Feeder)
EOE1 | 3.7 | Operating Environment | TABLE 3.7.1 - DENSITY FACTORS Customer Density [(0's)] | Actual | Calculated data |  | Evoenergy has applied the requirements and definitions (as per Economic Benchmarking RIN issued by the AER to Evoenergy 19th December 2013) relating to customer density to data provided in EB RIN 3.7.1, calculated from dependent variables in EB RIN 3.4 and EB RIN 3.7. These have been applied by Evoenergy in accordance with requirements of the Economic Benchmarking RIN (stated above). As such all methodologies, definitions and application to calculations used to derive customer density are linked to EB RIN 3.4 and EB RIN 3.7 as required. Formula: Customer numbers in EB RIN 3.4 - Operational data (cell D65 - DOPCN02) divided by route line length in EB RIN 3.7.3 - Operating Environment (cell D35 - DOEF0301) - refer 'EB RIN 3.7.1 - workings'
EOE2 | 3.7 | Operating Environment | TABLE 3.7.1 - DENSITY FACTORS Energy Density [(0's)] | Actual | Calculated data |  | Evoenergy has applied the requirements and definitions (as per Economic Benchmarking RIN issued by the AER to Evoenergy 19th December 2013) relating to energy density to data provided in EB RIN 3.7.1, calculated from dependent variables in EB RIN 3.4. These have been applied by Evoenergy in accordance with requirements of the Economic Benchmarking RIN (stated above). As such all methodologies, definitions and application to calculations used to derive energy density are linked to EB RIN 3.4 as required. Formula: Total energy delivered in EB RIN 3.4 - Operational data (cell D12 - DOPED01) *1000 divided by customer numbers (cell D65 - DOPCN02) - refer 'EB RIN 3.7.1 - workings'
EOE3 | 3.7 | Operating Environment | TABLE 3.7.1 - DENSITY FACTORS Demand Density [(0's)] | Actual | Calculated data |  | Evoenergy has applied the requirements and definitions (as per Economic Benchmarking RIN issued by the AER to Evoenergy 19th December 2013) relating to demand density to data provided in EB RIN 3.7.1, calculated from dependent variables in EB RIN 3.4. These have been applied by Evoenergy in accordance with requirements of the Economic Benchmarking RIN (stated above). As such all methodologies, definitions and application to calculations used to derive demand density are linked to EB RIN 3.4 as required. Formula: Raw system annual maximum demand in EB RIN 3.4 - Operational data (cell D102 - DOPSD0201) * 1000 divided by customer numbers (cell D65 - DOPCN02) - refer 'EB RIN 3.7.1 - workings'
EOE4 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Rural Proportion [(0's)] | Estimated | ArcFM GIS CA RIN 2.7.1 EB RIN 3.7.3 |  | Based on rural line length divided by the sum of urban and rural line length. Transmission line is included in the rural line length.
EOE5 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Urban and CBD Vegetation Maintenance Spans [(0's)] | Actual | LIDAR CA RIN 2.7.1 EB RIN 3.7.3 |  | Evoenergy inspects different regional sectors each year in a three year cycle. The count of spans is identified by helicopter using LiDAR or through ground inspections with a vegetation defect. An assumption is made that everything detected in the aerial inspection at the start of the year is cleared by the end of the year. |  | Inspected Urban HV and Multi voltage networks.
EOE6 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Rural Vegetation Maintenance Spans [(0's)] | Actual | LIDAR CA RIN 2.7.1 EB RIN 3.7.3 |  | Rural vegetation includes lines in the bushfire management zone & transmission lines. The results of the rural vegetation program indicate either less favourable conditions for tree growth or active cutting last year by lessees.
EOE7 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Total Vegetation Maintenance Spans [(0's)] | Actual | Calculated data |  | Sum of the rural and urban.
EOE8 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Total Number of Spans [(0's)] | Actual | ArcFM GIS |  | Total number of poles minus 1.
EOE9 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Average Urban and CBD Vegetation Maintenance Span Cycle [(0's)] | Actual | Evoenergy policies & plans CA RIN 2.7.1 |  | Inspection in accordance with Vegetation Management Policy
EOE10 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Average Rural Vegetation Maintenance Span Cycle [(0's)] | Actual | Evoenergy policies & plans CA RIN 2.7.1 |  | Inspection in accordance with Vegetation Management Policy
EOE11 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Average Number of Trees per Urban and CBD Vegetation Maintenance Span [(0's)] | Actual | LIDAR CA RIN 2.7.1 |  | Using LiDAR data (All vegetation classified as urban vegetation). Number of urban defects (including actionable and advisory only) / the number of urban maintenance span.
EOE12 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Average Number of Trees per Rural Vegetation Maintenance Span [(0's)] | Actual | LIDAR CA RIN 2.7.1 |  | Using LiDAR data (All vegetation classified as rural + transmission vegetation). Number of rural + transmission defects (including actionable and advisory only)/ the number of rural + transmission maintenance span
EOE13 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Average Number of Defects per Urban and CBD Vegetation Maintenance Span [(0's)] | Actual | LIDAR CA RIN 2.7.1 |  | Using LiDAR data (All vegetation classified as urban vegetation). Number of urban actionable defects / the number of urban maintenance span.
EOE14 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Average Number of Defects per Rural Vegetation Maintenance Span [(0's)] | Actual | LIDAR CA RIN 2.7.1 |  | Using LiDAR data (All vegetation classified as rural + transmission vegetation). Number of rural + transmission actionable defects / the number of rural + transmission maintenance span.
EOE15 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Tropical Proportion [(0's)] | Actual | N/A
EOE16 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Standard Vehicle Access [(0's)] | Actual | ArcFM GIS CA RIN 2.7.1 |  | 10% of all rural lines + all of 66kV and 132kV lines
EOE17 | 3.7 | Operating Environment | TABLE 3.7.2 - TERRAIN FACTORS Bushfire risk [(0's)] | Actual | ArcFM GIS CA RIN 2.7.1 |  | According to Utilities technical regulator (ACT) the defination of bushfire spans are different, due to this for bushfire risk we have calculated this based on total span (Urban and rural) - (minus) 1. (Only overhead spans included in calculations)
EOE18 | 3.7 | Operating Environment | TABLE 3.7.3 - SERVICE AREA FACTORS | Estimated | ArcFM GIS |  | Query run using the following rules to merge adjacent circuits into the one route, 1. EHV voltage = 132kv overhead circuits within 10m of each other 2. EHV voltage = 66kv overheard circuits are within 8m of each other 3. HV voltage = 22kv circuits are within 6m of each other 4. HV voltage = 11kv circuits are within 4m of each other 5. LV circuits within 2m of each other. Overhead and underground included as this section request operational data. Sub-transmission & service lines excluded as per definition. |  | Overhead HV Electric Line (AAD) - 986691.8 Overhead LV Electric Line (AAD) - 1209482 Overhead Transmission Line (AAD) - 213237.8 Underground Transmission Line (AAD) - 6108.41 Underground HV Electric Line (AAD) - 1633282 Underground LV Electric Line (AAD)- 1572885 Total - 5621686