## Cover
Amendments made on 6 August 2014.
Click here for details.
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | JEN
DNSP - Australian business number: |  | 82 064 651 083
Reporting year: |  | 2014
Business address | Address |  | 321 Ferntree Gully Road
| Suburb |  | Mt Waverley
|  | State | VIC | Postcode | 3149
Postal address | Address |  | Locked Bag 7000
| Suburb |  | Mt Waverley
|  | State | VIC | Postcode | 3149
Contact name/s | Matthew Serpell
Contact phone/s | (03) 8544 9814
Contact email address/s | matthew.serpell@jemena.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet
Definitions
1. Service Target Performance Incentive Scheme | 2. Quality of service and customer service
1a. STPIS - Reliability | 3. General Information (deleted)
1b. STPIS - Customer service | 4. Network performance
1c. STPIS - Daily performance | 4a. Network performance - feeder reliability
1d. STPIS - MED threshold (deleted) | 4b. Network performance - outages (deleted)
1e. STPIS - Exclusions | 4c. Network performance - planned outages
1f. STPIS - GSL

## Definitions
JEN
Definitions
2014
Appendix C – non- financial templates | Definition
STPIS
Customer numbers at the start of period | The number of Distribution Customers, measured on the first day of the Relevant Regulatory Year.
Customer numbers at the end of period | The number of Distribution Customers, measured on the last day of the Relevant Regulatory Year.
Distribution Customer/Customer | A Distribution Customer (with active accounts) with an active National Metering Identifier (NMI).
Duration of interruption (unplanned) (mins) | The duration of an unplanned interruption experienced by a customer.
Effect on unplanned MAIFI | Unplanned MAIFI for the event on the identified feeder.
Exclusion category/ Excluded event/Event category | The exclusions allowed under clauses 3.3 and 5.4 of the service target performance incentive scheme that applies to the DNSP.
Feeder classification | The following classification of the Feeder as: CBD: network is predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban: the network is not a CBD network, with actual maximum demand over the reporting period per total feeder (network) route length greater than 0.3 MVA/km; Rural Short: not a CBD or urban network with a network route length less than 200 km; Rural Long: not a CBD or urban network with a total network route length greater than 200 km; or as otherwise agreed with by the AER.
Feeder ID/name | The unique code or feeder identifier that the DNSP uses internally.
Interruption | Any planned or unplanned, monetary on sustained, loss of electricity supply to a customer associated with an outage of any part of the electricity supply network, including generation facilities and transmission networks, of more than 0.5 seconds (as recorded by equipment such as SCADA or, where such equipment does not exist, at the time of the first customer call relating to the network outage), including outages affecting a single premises; and not including subsequent interruptions caused by network switching during fault finding. An interruption ends when supply is again generally available to the customer.
MAIFI Momentary Average Interruption Frequency Index | As per the ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30: The total number of momentary interruptions divided by the total number of distribution customers. The number of Distribution Customers used to derive MAIFI should reflect the relevant network type: • Whole network – total Distribution Customers • Network classification (CBD/Urban/Rural short/Rural long) – CBD/Urban/Rural short/Rural long Customers respectively • Individual Feeder – Customers on that feeder.
MED - Major Event Day | As per the STPIS, Appendix D.
Network categorisation | The following classification of the network as: - CBD: network is predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. - Urban: the network is not a CBD network, with actual maximum demand over the reporting period per total feeder (network) route length greater than 0.3 MVA/km; - Rural Short: not a CBD or urban network with a network route length less than 200 km; - Rural Long: not a CBD or urban network with a total network route length greater than 200 km. or as otherwise agreed with by the AER
New connections - number | Total number of connections to customers' premises (excluding re-energisations).
New connections - number not provided on or before the agreed date | The number of connections to customers' premises (excluding re-energisations) made after the date agreed to with the customer
Number of calls answered within 30 seconds | The number of calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: (a) calls to payment lines and automated interactive services (b) calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned). Note: being placed in an automated queuing system (automated or otherwise) does not constitute a response.
Number of calls received | the total number of calls to the fault line to be reported, including any answered by an automated response service and terminated without being answered by an operator. Excludes missed calls where the fault line is overloaded.
Outage ID/Event ID | The unique identifier for an outage used by the DNSP.
SAIDI System Average Interruption Duration Index | As per the STPIS: the sum of the duration of each sustained interruption (in minutes) divided by the total number of distribution customers as defined in the service target performance incentive scheme
SAIFI System Average Interruption Frequency Index | As per the STPIS: the total number of sustained interruptions divided by the total number of distribution customers as defined in the service target performance incentive scheme
Streetlight repair - Faulty streetlights not repaired within 5 business days of fault report or agreed date | The number of streetlights reported as not working within the reporting period that were not repaired within 5 days of the fault report, or were not repaired by the agreed date
Streetlight repair - number of streetlight faults | The number of streetlights reported by customers as not working in the reporting period
Streetlight repair - number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | The number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business as not working in the reporting period
Streetlight repair - number of streetlights | The total number of street lights
Telephone answering excluded events | The events listed in section 3.3 of the STPIS, November 2009.
Total unplanned minutes off supply | The sum of the duration of each unplanned interruption experienced by customers on a feeder, including single premise outages but not including momentary interruptions.
STPIS - GSL
AER GSL scheme | The Guaranteed service level component, in chapter 6 of the AER, Electricity distribution network service providers Service target performance incentive scheme, November 2009.
All other terms | As per the AER GSL Scheme, or the Victorian jurisdictional GSL scheme.
Victorian jurisdictional GSL scheme | As per the Victorian Electricity Distribution Code and the Public Lighting Code.
Customer service
Call centre - number of overload events | The number of times that the call centre queuing system is inadequate to queue all incoming calls
Calls abandoned | The number of calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator
Calls abandoned - percentage | (calls abandoned/calls to call centre fault line)* 100
Calls to fault line - average waiting time before call answered | The average time in seconds from when calls enter the system (including that time when a call may be ringing unanswered) and the caller speaks to a human operator or is connected to an interactive service that provides the information requested
Complaint | A written or verbal expression of dissatisfaction about an action, a proposed action, or a failure to act by a distributor, its employees or contractors. This includes failure by a distributor to observe its published practices or procedures
Complaint - administrative process or customer service | The number of complaints relating to the administrative process or customer service of Jemena, excluding those reported under 'connection and augmentation'
Complaint - connection or augmentation | The number of complaints about: (a) the quality and timeliness of a new connection; and (b) the cost, timeliness and quality of augmentation works
Complaint - other | The number of complaints that are not under the categories of 'connection & augmentation', 'reliability of supply', 'quality of supply' and 'administrative process or customer service'
Complaint - reliability of supply | The number of complaints relating to the reliability of supply
Complaint - technical quality of supply | The number of complaints relating to the technical quality of supply
Complaints - technical quality of supply - number | The total number of complaints made to the DNSP where the complaint raised issues about voltage variations.
Complaints by category - Low voltage supply | The proportion of complaints made to the DNSP where the complainant raised issues about low voltage supply
Complaints by category - Noise from appliances | The proportion of complaints made to the DNSP where the complainant raised issues about noise from appliances
Complaints by category - Other | The proportion of complaints made to the DNSP where the complainant raised issues about any matter that is not low voltage supply, voltage dips, volctage swell, voltage spike, TV or radio interference or noise from appliances.
Complaints by category - TV or radio interference | The proportion of complaints made to the DNSP where the complainant raised issues about TV or radio interference
Complaints by category - Voltage dips | The proportion of complaints made to the DNSP where the complainant raised issues about voltage dips
Complaints by category - Voltage spike (impulsive transient) | The proportion of complaints made to the DNSP where the complainant raised issues about voltage spikes (impulsive transient)
Complaints by category - Voltage swell | The proportion of complaints made to the DNSP where the complainant raised issues about voltage swell
Complaints by Likely Cause - Customer internal problem | The proportion of complaints where the event that gave rise to the complaint was likely to be a customer internal problem
Complaints by Likely Cause - Environmental | The proportion of complaints where the event that gave rise to the complaint was likely to be environmental
Complaints by Likely Cause - Network equipment faulty | The proportion of complaints where the event that gave rise to the complaint was likely to be faulty network equipment
Complaints by Likely Cause - Network interference by another customer | The proportion of complaints where the event that gave rise to the complaint was likely to be network interference by another customer
Complaints by Likely Cause - Network interference by NSP equipment | The proportion of complaints where the event that gave rise to the complaint was likely to be network interference by NSP equipment
Complaints by Likely Cause - Network limitation | The proportion of complaints where the event that gave rise to the complaint was likely to be a network limitation
Complaints by Likely Cause - No problem identified | The proportion of complaints where the event that gave rise to the complaint was not able to be identified
Complaints by Likely Cause - Other | The proportion of complaints where the event that gave rise to the complaint was likely to be a cause other than faulty network equipment, network interference by NSP equipment, network interference by another customer, a network limitation, a customer internal problem, environmental, or not able to be identified.
Customers receiving over-voltage - due to high voltage injection | The estimated number of customers affected by over-voltage events due to high voltage injection, based on customer’s with confirmed damage (including estimated damage) as investigated by the DNSP
Customers receiving over-voltage - due to lightning | The estimated number of customers affected by over-voltage events due to lightning, based on customer with confirmed damage (including estimated damage) and investigated by the DNSP
Customers receiving over-voltage - due to voltage regulation or other cause | The estimated number of customers affected by over-voltage events due to voltage regulations or other causes (including events due to unknown causes), based on confirmed damage (including estimated damage) and investigated by the DNSP
New connections - number | Total number of connections to customers' premises (excluding re-energisations).
New connections - number not provided on or before the agreed date | The number of connections to customers' premises (excluding re-energisations) made after the date agreed to with the customer
Number of calls answered in 30 seconds | The number of calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: (a) calls to payment lines and automated interactive services (b) calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned). Note: being placed in an automated queuing system (automated or otherwise) does not constitute a response.
Number of calls received | The number of calls to the fault line excluding: (a) calls to payment lines and automated interactive services; (b) calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned).
Over voltage events - due to high voltage injection | The number of over-voltage events, due to high voltage injection, in the distribution or transmission system leading to at least one customer complaint
Over voltage events - due to lightning | The number of over-voltage events, due to lightning, in the distribution or transmission system leading to at least one customer complaint
Over voltage events - due to voltage regulation or other cause | The number of over-voltage events, due to voltage regulation or other cause, in the distribution or transmission system leading to at least one customer complaint, including events due to an unknown cause
Streetlights - average monthly number "out" | The total number of street lights reported by customers as not working over the year, divided by twelve
Streetlights - average number of days to repair | The average number of days to repair street lights that were reported as not working
Telephone answering excluded events | The events listed in section 3.3 of the STPIS, November 2009.
Voltage variations - % feeders monitored | The percentage of feeders required to be monitored (i.e. one feeder supplied from each zone substation) that have recorders installed at the end of each Relevant Regulatory Year
Voltage variations - % zone subs monitored | The percentage of zone substations with recorders installed at the end of each Relevant Regulatory Year
Voltage variations - 10 seconds (zone sub) Min<0.7 | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside the standard nominal voltage range or set point voltage, and with a duration greater than or equal to 0.01 seconds (0.5 cycles) and less than 10 seconds, and where the minimum voltage variation during that excursion is less than 70% of the nominal voltage or set point voltage
Voltage variations - 10 seconds (zone sub) Min<0.8 | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside the standard nominal voltage range or set point voltage, and with a duration greater than or equal to 0.01 seconds (0.5 cycles) and less than 10 seconds, and where the minimum voltage during that excursion is less than 80% of the nominal voltage or set point voltage
Voltage variations - 10 seconds (zone sub) Min<0.9 | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside of the standard nominal voltage range or set point voltage and with a duration greater than or equal to 0.01 seconds (0.5 cycles) and less than 10 seconds, and where the minimum voltage variation during that excursion is less than 90% of the nominal voltage or set point voltage
Voltage variations - one minute (zone sub) | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside of the standard nominal voltage range or set point voltage, and with a duration greater than or equal to 10 seconds and less than 1 minute
Voltage variations - steady state (feeder) | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location on a feeder, outside the standard nominal voltage range or set point voltage under steady state (greater than or equal to 1 minute) conditions
Voltage variations - steady state (zone sub) | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside of the standard nominal voltage range or set point voltage under steady state (greater than or equal to 1 minute) conditions
Network performance (outages, feeders, WSC, reliability)
Description of feeder service area | A description of the location of the Feeder
Duration of interruption | The duration of an interruption from the time as recorded by equipment such as SCADA or, where such equipment does not exist, the time of notification of an unplanned interruption by a customer or the commencement of a planned interruption to restoration of supply.
Energy not supplied (planned) (MWh) | Total energy not supplied (measured in MWh) minus Energy not supplied - Unplanned.
Energy not supplied (unplanned) (MWh) | The estimate of energy not supplied (due to unplanned outage) to be based on average Customer demand (multiplied by number of customers interrupted and the duration of the interruption). Average Customer demand to be determined from (in order of preference): (a) average consumption of the Customers interrupted based on their billing history (b) Feeder demand at the time of the interruption divided by the number of Customers on the Feeder (c) average consumption of Customers on the Feeder based on their billing history (d) average feeder demand derived from Feeder maximum demand and estimated load factor, divided by the number of customers on the Feeder.
Feeder classification | The following classification of the Feeder as: CBD: network is predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban: the network is not a CBD network, with actual maximum demand over the reporting period per total feeder (network) route length greater than 0.3 MVA/km; Rural Short: not a CBD or urban network with a network route length less than 200 km; Rural Long: not a CBD or urban network with a total network route length greater than 200 km.or as otherwise agreed with by the AER.
Feeder ID/name | The unique code or feeder identifier that the DNSP uses internally.
Length of high voltage distribution lines (overhead) | The route length (measured in kilometres) of overhead lines in service (the total length of Feeders including all spurs), where each SWER line, single-phase line, and three-phase line counts as one line. A double circuit line counts as two lines.
Length of high voltage distribution lines (underground) | The route length (measured in kilometres) of underground lines in service (the total length of Feeders including all spurs), where each SWER line, single-phase line, and three-phase line counts as one line. A double circuit line counts as two lines.
Low Reliability Feeder (SAIDI) | A Yes or No answer describing whether the annual reported SAIDI for a feeder is above or below the reporting threshold: CBD Feeder - 70, where the number of interuptions is greater than 1; Urban - 270; Short rural - 600; Long rural - 850. An answer of Yes is required if the reported SAIDI exceeds the threshold, and an answer of No is required if the reported SAIDI is less than or equal to the threshold. This definition includes both planned and unplanned SAIDI.
Maximum demand (MVA) | The recorded maximum demand for the Feeder.
Momentary Interruptions | the sum of Momentary Interruptions Due to Feeder Outages and Momentary Interruptions Due to Feeder Section Outages
Momentary interruptions due to feeder outages | the number of interruptions caused by momentary feeder outages
Number of distribution customers | The average of the number of Distribution Customers at the beginning of each Relevant Regulatory Year and the number of Distribution Customers at the end of the Relevant Regulatory Year.
Outage | An event causing an interuption
Planned interruptions (SAIFI) | The total number of planned sustained Customer interruptions divided by the total number of Distribution Customers. Planned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions. The number of Distribution Customers used to derive SAIFI should reflect the relevant network type: o Whole network - total Distribution Customers o Network classification (CBD/Urban/Rural short/Rural long) - CBD/Urban/Rural short/Rural long Customers respectively o Individual Feeder - Customers on that Feeder. Note: The number of Distribution Customers used to derive SAIDI and SAIFI is defined in the STPIS as: the average of the number of Customers at the beginning of the reporting period and the number of Customers at the end of the reporting period.
Planned outage | The number of planned events causing interruptions and does not include single premise outages.
Planned SAIDI | The sum of the duration of each planned sustained customer interruption (in minutes) divided by the total number of Distribution Customers. Planned SAIDI excludes momentary interruptions (one minute or less). The number of Distribution Customers used to derive SAIDI should reflect the relevant network type: • Whole network – total Distribution Customers • Network classification (CBD/Urban/Rural short/Rural long) – CBD/Urban/Rural short/Rural long Customers respectively • Individual Feeder – Customers on that feeder. Note: The number of Distribution Customers used to derive SAIDI and SAIFI is defined in the STPIS as: the average of the number of customers at the beginning of the reporting period and the number of customers at the end of the reporting period.
Total number of momentary feeder outages | The number of feeder outages of less than or equal to 1 minute (where each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one outage), but greater than 0.5 seconds, in duration, including any outage of an entire feeder (including due to a sub-transmission fault) that results in an interruption, and does not include an outage of a feeder section. Each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one momentary outage if the sequence is completed in no more than one minute. Re-closes that are followed by lockout are to be excluded from the momentary outage indicator.
Total number of momentary feeder section outages | The number of feeder section outages of less than or equal to 1 minute (where each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one outage), but greater than 0.5 seconds, in duration, including outages of a feeder section that result in an interruption but does not include feeder outages;Each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one momentary outage if the sequence is completed in no more than one minute. Re-closes that are followed by lockout are to be excluded from the momentary outage indicator.
Total unplanned customer minutes off supply (Mins) | The sum of the duration of each unplanned interruption experienced by Customers on a Feeder, including single premise outages but not including momentary interruptions.
Unplanned interruptions (SAIFI) | The total number of unplanned sustained Customer interruptions divided by the total number of Distribution Customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions. The number of Distribution Customers used to derive SAIFI should reflect the relevant network type: o Whole network - total Distribution Customers o Network classification (CBD/Urban/Rural short/Rural long) - CBD/Urban/Rural short/Rural long Customers respectively o Individual Feeder - Customers on that Feeder. Note: The number of Distribution Customers used to derive SAIDI and SAIFI is defined in the STPIS as: the average of the number of Customers at the beginning of the reporting period and the number of Customers at the end of the reporting period.
Unplanned outage | The number of unplanned events causing interruptions on the DNSP's network, including deliberate interruptions in response to an emergency event but does not include: (a) momentary outages and single premise outages (b) subsequent outages caused by network switching during fault finding.
Contents

## 1a. STPIS Reliability
JEN
STPIS Data Reporting
2014
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI (System Average Interruption Duration Index)
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
Total |  | 62.1661 | 110.3942 |  | 64.2611
Total (after removing excluded events and MED) |  | 57.0027 | 94.2668 |  | 58.6214
Table 2: SAIFI (System Average Interruption Frequency Index)
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
Total |  | 1.0232 | 0.96682 |  | 1.0208
Total (after removing excluded events and MED) |  | 0.96908 | 0.66679 |  | 0.95595
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
Total |  | 0.78803 | 1.544 |  | 0.82087
Total (after removing excluded events and MED) |  | 0.76 | 1.544 |  | 0.79405
Table 4: Distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period |  | 305483 | 12811 |  | 318294
Customer numbers at the end of period |  | 303711 | 14853 |  | 318564
Average distribution customer numbers | 0 | 304597 | 13832 | 0 | 318429
Contents
Contents

## 1b. STPIS Customer Service
JEN
STPIS Data Reporting - AER Definitions
2014
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
| Total - after removing excluded events | Total
Number of calls received | 65407 | 66947
Number of calls answered in 30 seconds | 48138 | 48468
Percentage of calls answered within 30 seconds | 73.6% | 72.4%
Table 2: New connections
Note: This is for newly energised properties only
Total
Number of new connections | 8268
Number of new connections not provided on or before the agreed date | 7
Percentage of new connections not provided on or before the agreed date | 0.08466%
Table 3: Streetlight repair
Total
Total number of streetlights | 70725
Total number of streetlight faults | 3716
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | 1320
Faulty streetlights not repaired within 2 business days of fault report or agreed date | 20
Percentage of faulty streetlights not repaired within 2 business days of fault report or agreed date | 0.5382%
Contents

## 1c. STPIS Daily Performance
JEN |  |  |  | 2014-01-01
STPIS Data Reporting |  |  |  | 2015-01-01
2014
Daily Performance Data
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1 Daily Performance Data (unplanned)
*Customer service information must be reported as per the definitions in the STPIS, that is excluding: • calls to payment lines and automated interactive services • calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned).
Customer service*
| CBD |  | Urban |  | Short rural |  | Long rural |  | Network
Date | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | Number of calls received | Number of calls answered in 30 seconds
2014-01-01 |  |  | 0.0072949 | 0.0072949 | 0 | 0 |  |  | 0.006978 | 0.006978 | 139 | 102
2014-01-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 121 | 108
2014-01-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 102 | 101
2014-01-04 |  |  | 0.0057913 | 0.0057913 | 0 | 0 |  |  | 0.0055397 | 0.0055397 | 130 | 78
2014-01-05 |  |  | 0.018441 | 0.018441 | 0 | 0 |  |  | 0.01764 | 0.01764 | 234 | 99
2014-01-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 162 | 143
2014-01-07 |  |  | 0.0096948 | 0.0096948 | 0 | 0 |  |  | 0.0092737 | 0.0092737 | 282 | 156
2014-01-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 135 | 126
2014-01-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 123 | 123
2014-01-10 |  |  | 0.019869 | 0.019869 | 0 | 0 |  |  | 0.019006 | 0.019006 | 229 | 184
2014-01-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 107 | 98
2014-01-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 43 | 41
2014-01-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 256 | 216
2014-01-14 |  |  | 0.0050887 | 0.0050887 | 0 | 0 |  |  | 0.0048676 | 0.0048676 | 1086 | 380
2014-01-15 |  |  | 0 | 0 | 0.13346 | 0.13346 |  |  | 0.0057972 | 0.0057972 | 950 | 810
2014-01-16 |  |  | 0.0097375 | 0.0097375 | 0 | 0 |  |  | 0.0093145 | 0.0093145 | 1429 | 766
2014-01-17 |  |  | 0.0053185 | 0.0053185 | 0 | 0 |  |  | 0.0050875 | 0.0050875 | 488 | 422
2014-01-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 114 | 107
2014-01-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 69 | 67
2014-01-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 209 | 187
2014-01-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 355 | 289
2014-01-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 214 | 204
2014-01-23 |  |  | 0.01089 | 0.01089 | 0 | 0 |  |  | 0.010417 | 0.010417 | 243 | 237
2014-01-24 |  |  | 0.0035621 | 0.0035621 | 0 | 0 |  |  | 0.0034074 | 0.0034074 | 258 | 218
2014-01-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 208 | 108
2014-01-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 22 | 22
2014-01-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 125 | 101
2014-01-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 779 | 463
2014-01-29 |  |  | 0.011609 | 0.011609 | 0 | 0 |  |  | 0.011105 | 0.011105 | 616 | 454
2014-01-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 253 | 216
2014-01-31 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 216 | 200
2014-02-01 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 90 | 89
2014-02-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 500 | 187
2014-02-03 |  |  | 0.013828 | 0.013828 | 0 | 0 |  |  | 0.013227 | 0.013227 | 623 | 341
2014-02-04 |  |  | 0.00051215 | 0.00051215 | 0 | 0 |  |  | 0.00048991 | 0.00048991 | 517 | 367
2014-02-05 |  |  | 0.0042285 | 0.0042285 | 0 | 0 |  |  | 0.0040449 | 0.0040449 | 208 | 202
2014-02-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 303 | 269
2014-02-07 |  |  | 0 | 0 | 0.13324 | 0.13324 |  |  | 0.0057878 | 0.0057878 | 215 | 174
2014-02-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 216 | 192
2014-02-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 427 | 314
2014-02-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 429 | 373
2014-02-11 |  |  | 0.0077151 | 0.0077151 | 0 | 0 |  |  | 0.00738 | 0.00738 | 202 | 197
2014-02-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 202 | 184
2014-02-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 182 | 167
2014-02-14 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 185 | 174
2014-02-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 202 | 181
2014-02-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 803 | 361
2014-02-17 |  |  | 0.0099049 | 0.0099049 | 0 | 0 |  |  | 0.0094746 | 0.0094746 | 187 | 173
2014-02-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 176 | 158
2014-02-19 |  |  | 0.0099049 | 0.0099049 | 0 | 0 |  |  | 0.0094746 | 0.0094746 | 202 | 194
2014-02-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 155 | 140
2014-02-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 140 | 137
2014-02-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 69 | 61
2014-02-23 |  |  | 0.0040151 | 0.0040151 | 0 | 0 |  |  | 0.0038407 | 0.0038407 | 42 | 39
2014-02-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 167 | 152
2014-02-25 |  |  | 0.00061721 | 0.00061721 | 0 | 0 |  |  | 0.0005904 | 0.0005904 | 212 | 149
2014-02-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 150 | 149
2014-02-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 164 | 160
2014-02-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 155 | 153
2014-03-01 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 81 | 71
2014-03-02 |  |  | 0.0020683 | 0.0020683 | 0 | 0 |  |  | 0.0019785 | 0.0019785 | 66 | 44
2014-03-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 178 | 159
2014-03-04 |  |  | 0.0060112 | 0.0060112 | 0 | 0 |  |  | 0.0057501 | 0.0057501 | 221 | 201
2014-03-05 |  |  | 0.0024656 | 0.0024656 | 0.18999 | 0.18999 |  |  | 0.010611 | 0.010611 | 259 | 252
2014-03-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 177 | 174
2014-03-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 350 | 148
2014-03-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 126 | 110
2014-03-09 |  |  | 0 | 0 | 0.044318 | 0.044318 |  |  | 0.0019251 | 0.0019251 | 64 | 48
2014-03-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 49 | 47
2014-03-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 195 | 175
2014-03-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 251 | 198
2014-03-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 128 | 108
2014-03-14 |  |  | 0.002761 | 0.002761 | 0 | 0 |  |  | 0.0026411 | 0.0026411 | 176 | 136
2014-03-15 |  |  | 0.0010342 | 0.0010342 | 0 | 0 |  |  | 0.00098923 | 0.00098923 | 218 | 165
2014-03-16 |  |  | 0.0068385 | 0.0068385 | 0 | 0 |  |  | 0.0065415 | 0.0065415 | 47 | 44
2014-03-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 181 | 136
2014-03-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 170 | 126
2014-03-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 157 | 139
2014-03-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 185 | 162
2014-03-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 178 | 159
2014-03-22 |  |  | 0.0025115 | 0.0025115 | 0 | 0 |  |  | 0.0024024 | 0.0024024 | 100 | 76
2014-03-23 |  |  | 0.010581 | 0.010581 | 0 | 0 |  |  | 0.010122 | 0.010122 | 48 | 46
2014-03-24 |  |  | 0.0044945 | 0.0044945 | 0 | 0 |  |  | 0.0042992 | 0.0042992 | 160 | 134
2014-03-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 196 | 147
2014-03-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 313 | 239
2014-03-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 225 | 164
2014-03-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 313 | 159
2014-03-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 78 | 70
2014-03-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 72 | 65
2014-03-31 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 226 | 145
2014-04-01 |  |  | 5.5811e-05 | 5.5811e-05 | 0 | 0 |  |  | 5.3387e-05 | 5.3387e-05 | 494 | 163
2014-04-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 202 | 138
2014-04-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 161 | 130
2014-04-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 125 | 101
2014-04-05 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 46 | 44
2014-04-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 62 | 47
2014-04-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 141 | 116
2014-04-08 |  |  | 0.0028398 | 0.0028398 | 0 | 0 |  |  | 0.0027165 | 0.0027165 | 304 | 148
2014-04-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 274 | 169
2014-04-10 |  |  | 0.0049705 | 0.0049705 | 0 | 0 |  |  | 0.0047546 | 0.0047546 | 274 | 247
2014-04-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 319 | 237
2014-04-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 147 | 103
2014-04-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 56 | 52
2014-04-14 |  |  | 0.0040053 | 0.0040053 | 0 | 0 |  |  | 0.0038313 | 0.0038313 | 156 | 107
2014-04-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 147 | 122
2014-04-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 163 | 140
2014-04-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 154 | 126
2014-04-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 66 | 58
2014-04-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 58 | 50
2014-04-20 |  |  | 0.0050953 | 0.0050953 | 0.040847 | 0.040847 |  |  | 0.0066483 | 0.0066483 | 35 | 34
2014-04-21 |  |  | 0 | 0 | 0.044173 | 0.044173 |  |  | 0.0019188 | 0.0019188 | 129 | 75
2014-04-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 207 | 153
2014-04-23 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 152 | 113
2014-04-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 218 | 181
2014-04-25 |  |  | 0.0050723 | 0.0050723 | 0 | 0 |  |  | 0.0048519 | 0.0048519 | 56 | 56
2014-04-26 |  |  | 0.0041793 | 0.0041793 | 0 | 0 |  |  | 0.0039978 | 0.0039978 | 57 | 54
2014-04-27 |  |  | 0.00078793 | 0.00078793 | 0 | 0 |  |  | 0.0007537 | 0.0007537 | 42 | 39
2014-04-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 223 | 147
2014-04-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 222 | 145
2014-04-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 167 | 150
2014-05-01 |  |  | 0.0050427 | 0.0050427 | 0 | 0 |  |  | 0.0048237 | 0.0048237 | 200 | 187
2014-05-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 170 | 152
2014-05-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 93 | 83
2014-05-04 |  |  | 0.015112 | 0.015112 | 0.13389 | 0.13389 |  |  | 0.020271 | 0.020271 | 133 | 114
2014-05-05 |  |  | 0.012801 | 0.012801 | 0 | 0 |  |  | 0.012244 | 0.012244 | 190 | 132
2014-05-06 |  |  | 0.0069173 | 0.0069173 | 0 | 0 |  |  | 0.0066169 | 0.0066169 | 146 | 130
2014-05-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 157 | 148
2014-05-08 |  |  | 0.0035949 | 0.0035949 | 0 | 0 |  |  | 0.0034388 | 0.0034388 | 178 | 150
2014-05-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 114 | 108
2014-05-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 183 | 102
2014-05-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 163 | 115
2014-05-12 |  |  | 0 | 0 | 0.022556 | 0.022556 |  |  | 0.00097981 | 0.00097981 | 196 | 177
2014-05-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 154 | 144
2014-05-14 |  |  | 0.0001937 | 0.0001937 | 0 | 0 |  |  | 0.00018528 | 0.00018528 | 184 | 153
2014-05-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 374 | 177
2014-05-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 157 | 141
2014-05-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 97 | 92
2014-05-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 31 | 31
2014-05-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 157
2014-05-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 132 | 120
2014-05-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 166 | 136
2014-05-22 |  |  | 0 | 0 | 0.044173 | 0.044173 |  |  | 0.0019188 | 0.0019188 | 127 | 120
2014-05-23 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 107 | 98
2014-05-24 |  |  | 0.011563 | 0.011563 | 0.036437 | 0.036437 |  |  | 0.012643 | 0.012643 | 115 | 85
2014-05-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 47 | 46
2014-05-26 |  |  | 0.0083783 | 0.0083783 | 0 | 0 |  |  | 0.0080143 | 0.0080143 | 159 | 127
2014-05-27 |  |  | 0.012623 | 0.012623 | 0 | 0 |  |  | 0.012075 | 0.012075 | 226 | 164
2014-05-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 265 | 232
2014-05-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 170 | 143
2014-05-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 112 | 109
2014-05-31 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 87 | 80
2014-06-01 |  |  | 0.0081879 | 0.0081879 | 0 | 0 |  |  | 0.0078322 | 0.0078322 | 171 | 83
2014-06-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 203 | 178
2014-06-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 259 | 205
2014-06-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 188 | 145
2014-06-05 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 193 | 164
2014-06-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 134 | 125
2014-06-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 157 | 141
2014-06-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 57 | 51
2014-06-09 |  |  | 0.0011162 | 0.0011162 | 0 | 0 |  |  | 0.0010677 | 0.0010677 | 130 | 43
2014-06-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 289 | 224
2014-06-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 187 | 155
2014-06-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 178 | 155
2014-06-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 206 | 175
2014-06-14 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 144 | 108
2014-06-15 |  |  | 0.0081682 | 0.0081682 | 0 | 0 |  |  | 0.0078134 | 0.0078134 | 73 | 67
2014-06-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 197 | 147
2014-06-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 154 | 149
2014-06-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 176 | 149
2014-06-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 159
2014-06-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 134 | 120
2014-06-21 |  |  | 0.0044945 | 0.0044945 | 0 | 0 |  |  | 0.0042992 | 0.0042992 | 62 | 61
2014-06-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 39 | 37
2014-06-23 |  |  | 0.010289 | 0.010289 | 0 | 0 |  |  | 0.0098421 | 0.0098421 | 534 | 191
2014-06-24 |  |  | 0.028037 | 0.028037 | 0 | 0 |  |  | 0.026819 | 0.026819 | 1540 | 330
2014-06-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 320 | 242
2014-06-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 194 | 155
2014-06-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 236 | 186
2014-06-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 128 | 96
2014-06-29 |  |  | 0.011704 | 0.011704 | 0 | 0 |  |  | 0.011196 | 0.011196 | 172 | 118
2014-06-30 |  |  | 0 | 0 | 0.013158 | 0.013158 |  |  | 0.00057156 | 0.00057156 | 249 | 180
2014-07-01 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 157 | 153
2014-07-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 185 | 163
2014-07-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 406 | 136
2014-07-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 160 | 145
2014-07-05 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 72 | 67
2014-07-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 50 | 45
2014-07-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 187 | 143
2014-07-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 167 | 146
2014-07-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 221 | 170
2014-07-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 232 | 175
2014-07-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 211 | 178
2014-07-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 106 | 76
2014-07-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 96 | 59
2014-07-14 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 320 | 182
2014-07-15 |  |  | 0.0073868 | 0.0073868 | 0 | 0 |  |  | 0.0070659 | 0.0070659 | 149 | 122
2014-07-16 |  |  | 0.0042712 | 0.0042712 | 0 | 0 |  |  | 0.0040857 | 0.0040857 | 237 | 177
2014-07-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 177 | 127
2014-07-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 139 | 123
2014-07-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 76 | 69
2014-07-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 39 | 38
2014-07-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 231 | 150
2014-07-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 189 | 164
2014-07-23 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 211 | 173
2014-07-24 |  |  | 0 | 0 | 0.044173 | 0.044173 |  |  | 0.0019188 | 0.0019188 | 166 | 148
2014-07-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 165 | 129
2014-07-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 92 | 84
2014-07-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 65 | 63
2014-07-28 |  |  | 0.0075116 | 0.0075116 | 0 | 0 |  |  | 0.0071853 | 0.0071853 | 160 | 130
2014-07-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 174 | 153
2014-07-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 154 | 135
2014-07-31 |  |  | 0.00097178 | 0.00097178 | 0.018291 | 0.018291 |  |  | 0.0017241 | 0.0017241 | 431 | 233
2014-08-01 |  |  | 0.0084768 | 0.0084768 | 0 | 0 |  |  | 0.0081086 | 0.0081086 | 202 | 126
2014-08-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 160 | 103
2014-08-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 100 | 78
2014-08-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 5 | 4
2014-08-05 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 127 | 113
2014-08-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 189 | 147
2014-08-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 224 | 187
2014-08-08 |  |  | 0.0011622 | 0.0011622 | 0 | 0 |  |  | 0.0011117 | 0.0011117 | 171 | 151
2014-08-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 101 | 83
2014-08-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 50 | 45
2014-08-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 156 | 142
2014-08-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 152 | 146
2014-08-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 203 | 174
2014-08-14 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 184 | 173
2014-08-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 145 | 128
2014-08-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 114 | 95
2014-08-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 97 | 78
2014-08-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 223 | 181
2014-08-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 102 | 98
2014-08-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 129 | 115
2014-08-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 187 | 124
2014-08-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 139 | 123
2014-08-23 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 92 | 68
2014-08-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 43 | 37
2014-08-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 128 | 108
2014-08-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 129 | 109
2014-08-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 279 | 231
2014-08-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 229 | 185
2014-08-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 117 | 107
2014-08-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 69 | 55
2014-08-31 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 31 | 31
2014-09-01 |  |  | 9.8491e-06 | 9.8491e-06 | 0 | 0 |  |  | 9.4213e-06 | 9.4213e-06 | 201 | 156
2014-09-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 162 | 148
2014-09-03 |  |  | 0.0057683 | 0.0057683 | 0 | 0 |  |  | 0.0055177 | 0.0055177 | 355 | 139
2014-09-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 131 | 125
2014-09-05 |  |  | 0.014866 | 0.014866 | 0 | 0 |  |  | 0.01422 | 0.01422 | 192 | 137
2014-09-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 84 | 78
2014-09-07 |  |  | 0.0058635 | 0.0058635 | 0 | 0 |  |  | 0.0056088 | 0.0056088 | 42 | 38
2014-09-08 |  |  | 0.0088248 | 0.0088248 | 0 | 0 |  |  | 0.0084414 | 0.0084414 | 165 | 141
2014-09-09 |  |  | 0.01068 | 0.01068 | 0 | 0 |  |  | 0.010216 | 0.010216 | 617 | 370
2014-09-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 159 | 157
2014-09-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 89 | 84
2014-09-12 |  |  | 0 | 0 | 0.21053 | 0.21053 |  |  | 0.0091449 | 0.0091449 | 143 | 126
2014-09-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 73 | 64
2014-09-14 |  |  | 0.0015496 | 0.0015496 | 0 | 0 |  |  | 0.0014823 | 0.0014823 | 50 | 48
2014-09-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 163 | 122
2014-09-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 137
2014-09-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 170 | 158
2014-09-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 124 | 98
2014-09-19 |  |  | 0.024396 | 0.024396 | 0 | 0 |  |  | 0.023336 | 0.023336 | 235 | 154
2014-09-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 64 | 60
2014-09-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 38 | 35
2014-09-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 180 | 123
2014-09-23 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 123 | 115
2014-09-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 133 | 121
2014-09-25 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 162 | 142
2014-09-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 135 | 122
2014-09-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 81 | 75
2014-09-28 |  |  | 0.012068 | 0.012068 | 0 | 0 |  |  | 0.011544 | 0.011544 | 202 | 119
2014-09-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 179 | 132
2014-09-30 |  |  | 2.6264e-05 | 2.6264e-05 | 0 | 0 |  |  | 2.5123e-05 | 2.5123e-05 | 466 | 229
2014-10-01 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 244 | 192
2014-10-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 135 | 121
2014-10-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 129 | 102
2014-10-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 75 | 61
2014-10-05 |  |  | 0.0038773 | 0.0038773 | 0 | 0 |  |  | 0.0037088 | 0.0037088 | 72 | 62
2014-10-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 133 | 125
2014-10-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 138 | 130
2014-10-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 122 | 103
2014-10-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 154 | 127
2014-10-10 |  |  | 0.0041662 | 0.0041662 | 0 | 0 |  |  | 0.0039852 | 0.0039852 | 159 | 113
2014-10-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 84 | 77
2014-10-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 50 | 46
2014-10-13 |  |  | 0.011543 | 0.011543 | 0 | 0 |  |  | 0.011042 | 0.011042 | 269 | 157
2014-10-14 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 211 | 158
2014-10-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 102 | 85
2014-10-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 130 | 111
2014-10-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 111 | 98
2014-10-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 68 | 58
2014-10-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 37 | 31
2014-10-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 152 | 101
2014-10-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 132 | 104
2014-10-22 |  |  | 0.017961 | 0.017961 | 0 | 0 |  |  | 0.017181 | 0.017181 | 162 | 100
2014-10-23 |  |  | 0.008677 | 0.008677 | 0 | 0 |  |  | 0.0083001 | 0.0083001 | 150 | 100
2014-10-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 102 | 99
2014-10-25 |  |  | 0.0093304 | 0.0093304 | 0 | 0 |  |  | 0.0089251 | 0.0089251 | 76 | 64
2014-10-26 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 32 | 31
2014-10-27 |  |  | 0.09528 | 0.09528 | 0.34912 | 0.34912 |  |  | 0.10631 | 0.10631 | 780 | 177
2014-10-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 185 | 111
2014-10-29 |  |  | 0.00696 | 0.00696 | 0 | 0 |  |  | 0.0066577 | 0.0066577 | 117 | 66
2014-10-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 126 | 83
2014-10-31 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 145 | 81
2014-11-01 |  |  | 0.016625 | 0.016625 | 0 | 0 |  |  | 0.015903 | 0.015903 | 88 | 64
2014-11-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 35 | 30
2014-11-03 |  |  | 0.0092023 | 0.0092023 | 0 | 0 |  |  | 0.0088026 | 0.0088026 | 117 | 90
2014-11-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 85 | 76
2014-11-05 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 156 | 92
2014-11-06 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 125 | 80
2014-11-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 117 | 100
2014-11-08 |  |  | 0.012988 | 0.012988 | 0 | 0 |  |  | 0.012423 | 0.012423 | 138 | 97
2014-11-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 82 | 61
2014-11-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 156 | 97
2014-11-11 |  |  | 0 | 0 | 0.050463 | 0.050463 |  |  | 0.002192 | 0.002192 | 221 | 175
2014-11-12 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 123 | 83
2014-11-13 |  |  | 0.019065 | 0.019065 | 0 | 0 |  |  | 0.018236 | 0.018236 | 129 | 96
2014-11-14 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 209 | 141
2014-11-15 |  |  | 0.0055286 | 0.0055286 | 0 | 0 |  |  | 0.0052885 | 0.0052885 | 130 | 82
2014-11-16 |  |  | 0.003631 | 0.003631 | 0 | 0 |  |  | 0.0034733 | 0.0034733 | 154 | 108
2014-11-17 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 225 | 111
2014-11-18 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 149 | 118
2014-11-19 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 172 | 102
2014-11-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 164 | 95
2014-11-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 138 | 101
2014-11-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 96 | 81
2014-11-23 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 43 | 41
2014-11-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 240 | 131
2014-11-25 |  |  | 2.9547e-05 | 2.9547e-05 | 0 | 0 |  |  | 2.8264e-05 | 2.8264e-05 | 236 | 150
2014-11-26 |  |  | 0.012787 | 0.012787 | 0 | 0 |  |  | 0.012232 | 0.012232 | 175 | 126
2014-11-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 141 | 109
2014-11-28 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 104 | 78
2014-11-29 |  |  | 0 | 0 | 0.012073 | 0.012073 |  |  | 0.00052445 | 0.00052445 | 133 | 119
2014-11-30 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 162 | 82
2014-12-01 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 222 | 151
2014-12-02 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 126 | 93
2014-12-03 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 168 | 71
2014-12-04 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 141 | 110
2014-12-05 |  |  | 0.0059554 | 0.0059554 | 0 | 0 |  |  | 0.0056967 | 0.0056967 | 145 | 107
2014-12-06 |  |  | 0.010883 | 0.010883 | 0 | 0 |  |  | 0.01041 | 0.01041 | 156 | 112
2014-12-07 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 119 | 102
2014-12-08 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 178 | 114
2014-12-09 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 151 | 100
2014-12-10 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 216 | 122
2014-12-11 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 113
2014-12-12 |  |  | 5.9094e-05 | 5.9094e-05 | 0 | 0 |  |  | 5.6528e-05 | 5.6528e-05 | 161 | 111
2014-12-13 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 137 | 93
2014-12-14 |  |  | 0.0039692 | 0.0039692 | 0 | 0 |  |  | 0.0037968 | 0.0037968 | 56 | 49
2014-12-15 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 183 | 112
2014-12-16 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 510 | 210
2014-12-17 |  |  | 0.0022522 | 0.0022522 | 0 | 0 |  |  | 0.0021543 | 0.0021543 | 227 | 165
2014-12-18 |  |  | 0.0025246 | 0.0025246 | 0 | 0 |  |  | 0.002415 | 0.002415 | 131 | 111
2014-12-19 |  |  | 0 | 0 | 0.023062 | 0.023062 |  |  | 0.0010018 | 0.0010018 | 121 | 107
2014-12-20 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 65 | 52
2014-12-21 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 70 | 62
2014-12-22 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 101 | 86
2014-12-23 |  |  | 0.0039692 | 0.0039692 | 0 | 0 |  |  | 0.0037968 | 0.0037968 | 167 | 110
2014-12-24 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 129 | 93
2014-12-25 |  |  | 3.283e-06 | 3.283e-06 | 0 | 0 |  |  | 3.1404e-06 | 3.1404e-06 | 48 | 36
2014-12-26 |  |  | 0.0056895 | 0.0056895 | 0 | 0 |  |  | 0.0054423 | 0.0054423 | 52 | 49
2014-12-27 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 265 | 47
2014-12-28 |  |  | 0.006937 | 0.006937 | 0 | 0 |  |  | 0.0066357 | 0.0066357 | 168 | 76
2014-12-29 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 193 | 152
2014-12-30 |  |  | 0.0045897 | 0.0045897 | 0 | 0 |  |  | 0.0043903 | 0.0043903 | 133 | 107
2014-12-31 |  |  | 0.017702 | 0.017702 | 0 | 0 |  |  | 0.016933 | 0.016933 | 63 | 54
Formulas:
Date = [Date, row above]+1
Contents
Contents

## 1e. STPIS Exclusions
JEN
STPIS Data Reporting
2014
Exclusions
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of interruptions (unplanned) | Duration of interruption (unplanned) (mins) | Total unplanned minutes off supply | Event category (use exclusion categories listed in section 3.3(a) of the AER's STPIS) | Effect on unplanned MAIFI (by feeder classification) | Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning
Weather
Equipment failure
Operational error
Vegetation
Animals
Third party impacts
Transmission failure
Load shedding
Inter-distributor connection failure
Other
Contents

## 1f. STPIS - GSL
JEN
STPIS Data Reporting
2014
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1 Guaranteed service levels - jurisdictional GSL scheme
Appointments (excluding AMI)
Customer arranged appointments Central - number | 2840
Appointments not met within 15 minutes of agreed time - number | 42
Appointments - GSL payments - number | 42
Appointments - GSL payments - ($) | 840
Appointments (AMI only)
Customer arranged appointments Central - number | 6272
Appointments not met within 15 minutes of agreed time - number | 291
Appointments - GSL payments - number | 291
Appointments - GSL payments - ($) | 5820
Connections
Connections made | 8268
Connections not made on agreed date | 7
Connections - GSL payments - 1-4 day delay - number | 4
Connections - GSL payments - 1-4 day delay - ($) | 450
Connections - GSL payments - 5+ day delay - number | 3
Connections - GSL payments - 5+ day delay - ($) | 750
Reliability of supply
Low reliability payments - 20 hours - number | 250
Low reliability payments - 20 hours - ($) | 25000
Low reliability payments - 30 hours - number | 234
Low reliability payments - 30 hours - ($) | 35100
Low reliability payments - 60 hours - number | 68
Low reliability payments - 60 hours - ($) | 20400
Low reliability payments - 10 events - number | 0
Low reliability payments - 10 events - ($) | 0
Low reliability payments - 15 events - number | 0
Low reliability payments - 15 events - ($) | 0
Low reliability payments - 30 events - number | 0
Low reliability payments - 30 events - ($) | 0
Low reliability payments - 24 momentary events - number | 0
Low reliability payments - 24 momentary events - ($) | 0
Low reliability payments - 36 momentary events - number | 0
Low reliability payments - 36 momentary events - ($) | 0
Street lights
Street lights | 70725
Street lights "out" during period | 3716
Street lights not repaired by "fix by" date | 159
Street lights not repaired in 2 business days | 1958
Street lights – number of business days to repair | 3.4176
Street lights - GSL payments - number | 20
Street lights - GSL payments - ($) | 200
Planned interruptions
Planned interruptions - 4 business days notice not given | 26
Total GSL payments made ($) | 82740
Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 2 must be completed. Do not complete table 2 if the AER's GSL scheme did not apply during the regulatory year.
Table 2: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Customer Service
JEN
Customer Service
2014
Table 1 Quality of supply
Over voltage events - due to high voltage injection | 12
Customers receiving over-voltage - due to high voltage injection | 259
Over voltage events - due to lightning | 4
Customers receiving over-voltage - due to lightning | 47
Over voltage events - due to voltage regulation or other cause | 39
Customers receiving over-voltage - due to voltage regulation or other cause | 3546
Voltage variations - steady state (zone sub) | 148
Voltage variations - one minute (zone sub) | 39
Voltage variations - 10 seconds (zone sub) Min<0.7 | 152
Voltage variations - 10 seconds (zone sub) Min<0.8 | 239
Voltage variations - 10 seconds (zone sub) Min<0.9 | 760
Voltage variations - steady state (feeder) | 1622
Voltage variations - % zone subs monitored | 1
Voltage variations - % feeders monitored | 96%
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number | 143
Complaints by category (%)
Low voltage supply | 20.28%
Voltage dips | 6.993%
Voltage swell | 0.6993%
Voltage spike (impulsive transient) | 0.6993%
TV or radio interference | 0%
Noise from appliances | 0%
Other | 71.33%
Complaints by Likely Cause (%)
Network equipment faulty | 18.18%
Network interference by NSP equipment | 0%
Network interference by another customer | 0%
Network limitation | 46.85%
Customer internal problem | 4.196%
No problem identified | 0%
Environmental | 0%
Other | 30.77%
Table 3 Customer service
Timely provision of services
Connections made | 8268
Connections not made on agreed date | 7
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 309.6667
Streetlights - not repaired by "fix by" date | 20
Streetlights - average number of days to repair | 3.4176
Total streetlights | 70725
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 115621 | Calls to call centre fault line is equal to 115,621
Calls to fault line answered within 30 seconds | 48468 | The equation originally in cell H53 linked to Number of calls received in 1b. STPIS Customer Service Cell D11
Calls to fault line - average waiting time before call answered | 38.2976
Calls abandoned - percentage | 25.72%
Call centre - number of overload events | 0
Customer complaints (number)
Complaint - reliability of supply | 48
Complaint - technical quality of supply | 143
Complaint - administrative process or customer service | 339
Complaint - connection or augmentation | 48
Complaint - other | 308
Complaint - AMI | 270
Total complaints | 886
Contents

## 4a. Network perf - Feeders
JEN
Annual Feeder Reliability
2014
Table 1 Annual Feeder Reliability Data
[19 empty] | Total number of momentary feeder and feeder section outages | Total momentary interruptions (MAIFI) (including excluded events and MEDs) | Total momentary interruptions (MAIFI) (after removing excluded events and MEDs)
Feeder ID / name | Description of the service area for the feeder | Feeder classification | Number of distribution customers(1) | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply (including excluded events and MEDs) | Planned customer minutes off-supply (after removing excluded events and MED) | Planned interruptions (SAIFI) (including excluded events and MEDs) | Planned interruptions (SAIFI) (after removing excluded events and MEDs) | Total number of momentary feeder outages | Momentary interruptions due to feeder outages (MAIFI) (including excluded events and MEDs) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events and MEDs) | Low Reliability Feeder (SAIDI)
AW 01 | Airport West | Urban | 729 | 4.678 | 4.316 | 8.7639 | 0.8039 | 0.20619 | 3 | 10660 | 10660 | 72 | 72 | 6 | 9114 | 9114 | 59 | 59 | 0 | 0 | 0 | N
AW 02 | Airport West | Urban | 3732 | 16.309 | 3.419 | 12.9554 | 1.7183 | 0.48408 | 6 | 90313 | 90313 | 4622 | 4622 | 8 | 84810 | 84810 | 295 | 295 | 0 | 0 | 0 | N
AW 03 | Airport West | Urban | 267 | 6.096 | 4.488 | 13.0697 | 0 | 1.9869 | 0 | 0 | 0 | 0 | 0 | 4 | 19533 | 19533 | 46 | 46 | 1 | 258 | 258 | N
AW 04 | Airport West | Urban | 1963 | 11.464 | 10.756 | 14.7081 | 0.7569 | 0.54979 | 6 | 15842 | 15842 | 99 | 99 | 4 | 38357 | 38357 | 111 | 111 | 0 | 0 | 0 | N
AW 05 | Airport West | Urban | 544 | 4.898 | 0.875 | 7.4684 | 3.2604 | 0.34119 | 5 | 38682 | 38682 | 609 | 609 | 6 | 13493 | 13493 | 50 | 50 | 0 | 0 | 0 | N
AW 06 | Airport West | Urban | 4965 | 16.717 | 1.646 | 13.1078 | 0.97845 | 0.63246 | 12 | 95463 | 95463 | 3976 | 3976 | 14 | 205687 | 205687 | 888 | 888 | 1 | 3317 | 3317 | N
AW 07 | Airport West | Urban | 4615 | 15.682 | 5.713 | 12.079 | 2.6558 | 0.21836 | 5 | 272948 | 173555 | 4931 | 4819 | 9 | 74805 | 74805 | 288 | 288 | 1 | 4603 | 4603 | N
AW 08 | Airport West | Urban | 2361 | 14.684 | 8.54 | 10.8977 | 11.4401 | 0.87553 | 13 | 431820 | 431820 | 7354 | 7354 | 8 | 110160 | 110160 | 385 | 385 | 2 | 4714 | 4714 | N
AW 09 | Airport West | Urban | 2453 | 9.488 | 7.261 | 8.4591 | 5.796 | 0.50852 | 7 | 326813 | 326813 | 5265 | 5265 | 7 | 95579 | 95579 | 402 | 402 | 1 | 2195 | 2195 | N
AW 11 | Airport West | Urban | 472 | 5.997 | 3.32 | 8.2686 | 0.23744 | 1.7541 | 1 | 2364 | 2364 | 95 | 95 | 3 | 58213 | 58213 | 114 | 114 | 1 | 472 | 472 | N
AW 12 | Airport West | Urban | 1792 | 5.699 | 6.954 | 8.0018 | 0.39604 | 0.12253 | 3 | 10835 | 10835 | 2238 | 2238 | 4 | 11174 | 11174 | 106 | 106 | 0 | 0 | 0 | N
AW 14 | Airport West | Urban | 1254 | 8.881 | 4.713 | 9.0688 | 0.028743 | 0.35845 | 0 | 515 | 515 | 4 | 4 | 6 | 21408 | 21408 | 121 | 121 | 0 | 0 | 0 | N
BD 01 | Broadmeadows | Urban | 1690 | 11.211 | 5.444 | 9.6784 | 1.0816 | 0.088406 | 4 | 32155 | 32155 | 1745 | 1745 | 5 | 8761 | 8761 | 49 | 49 | 2 | 3382 | 3382 | N
BD 02 | Broadmeadows | Urban | 1 | 0.665 | 0.073 | 8.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
BD 03 | Broadmeadows | Urban | 370 | 4.012 | 6.328 | 10.7453 | 0.15303 | 0.032658 | 1 | 731 | 731 | 5 | 5 | 2 | 520 | 520 | 3 | 3 | 0 | 0 | 0 | N
BD 04 | Broadmeadows | Urban | 1022 | 8.198 | 4.434 | 10.7453 | 6.2492 | 0.70124 | 4 | 142540 | 142540 | 2116 | 2116 | 10 | 53316 | 53316 | 250 | 250 | 5 | 4436 | 4436 | N
BD 06 | Broadmeadows | Urban | 1 | 0.749 | 0.08 | 7.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | N
BD 07 | Broadmeadows | Urban | 3323 | 19.162 | 1.84 | 12.5362 | 2.0488 | 0.034165 | 10 | 149774 | 137557 | 2744 | 2691 | 2 | 8325 | 8325 | 17 | 17 | 0 | 0 | 0 | N
BD 08 | Broadmeadows | Urban | 788 | 9.506 | 1.496 | 7.697 | 6.6638 | 0.068949 | 11 | 114122 | 114122 | 1959 | 1959 | 1 | 3936 | 3936 | 12 | 12 | 3 | 1395 | 1395 | N
BD 09 | Broadmeadows | Urban | 687 | 5.171 | 1.292 | 5.2584 | 5.9342 | 0.27672 | 8 | 121997 | 121997 | 862 | 862 | 2 | 18963 | 18963 | 28 | 28 | 2 | 722 | 722 | N
BD 10 | Broadmeadows | Urban | 1150 | 6.613 | 4.311 | 11.6979 | 0.068047 | 0.045774 | 0 | 1164 | 1164 | 8 | 8 | 2 | 2610 | 2610 | 6 | 6 | 0 | 0 | 0 | N
BD 11 | Broadmeadows | Urban | 2819 | 10.073 | 1.72 | 7.316 | 0.79728 | 0.54172 | 7 | 47193 | 36348 | 391 | 328 | 16 | 106886 | 106886 | 544 | 544 | 0 | 0 | 0 | N
BD 13 | Broadmeadows | Urban | 486 | 8.78 | 2.509 | 11.3931 | 9.6131 | 0.60892 | 15 | 78905 | 75801 | 1206 | 1179 | 2 | 16660 | 16660 | 42 | 42 | 1 | 513 | 513 | N
BD 14 | Broadmeadows | Urban | 576 | 6.671 | 3.053 | 11.0883 | 0.0088747 | 0.8682 | 0 | 198 | 198 | 2 | 2 | 8 | 64567 | 64567 | 170 | 170 | 0 | 0 | 0 | N
BD 15 | Broadmeadows | Urban | 808 | 8.639 | 1.596 | 10.7072 | 4.7295 | 0 | 4 | 47920 | 47920 | 899 | 899 | 0 | 0 | 0 | 0 | 0 | 1 | 296 | 296 | N
BD 16 | Broadmeadows | Urban | 1448 | 9.04 | 2.4 | 7.8113 | 2.5805 | 0.24222 | 6 | 67440 | 67440 | 1536 | 1536 | 3 | 21101 | 21101 | 90 | 90 | 0 | 0 | 0 | N
BY 11 | Braybrook | Urban | 4043 | 16.114 | 2.437 | 9.9832 | 1.8572 | 0.39723 | 7 | 138678 | 138678 | 2851 | 2851 | 11 | 98872 | 98872 | 308 | 308 | 1 | 4043 | 4043 | N
BY 12 | Braybrook | Urban | 1255 | 4.676 | 0.696 | 2.934 | 0.84504 | 0.014026 | 3 | 49344 | 49344 | 1351 | 1351 | 1 | 2730 | 2730 | 7 | 7 | 1 | 1269 | 1269 | N
BY 13 | Braybrook | Urban | 744 | 2.98 | 1.753 | 13.9461 | 4.5076 | 0.051634 | 2 | 43527 | 43527 | 1198 | 1198 | 1 | 1662 | 1662 | 6 | 6 | 1 | 751 | 751 | N
BY 14 | Braybrook | Urban | 2929 | 12.214 | 3.324 | 7.5827 | 1.5575 | 0.20142 | 5 | 115902 | 115902 | 2975 | 2975 | 12 | 49962 | 49962 | 252 | 252 | 1 | 1936 | 1936 | N
BY 15 | Braybrook | Urban | 1017 | 6.14 | 2.211 | 7.9637 | 2.6897 | 0 | 10 | 47902 | 35251 | 1182 | 1139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
CN 01 | Coburg North | Urban | 104 | 1.866 | 0.31 | 7.5065 | 3.5232 | 0.75767 | 2 | 5022 | 5022 | 17 | 17 | 1 | 3600 | 3600 | 12 | 12 | 0 | 0 | 0 | N
CN 02 | Coburg North | Urban | 460 | 4.854 | 0.932 | 8.3448 | 1.3273 | 0 | 2 | 16026 | 16026 | 507 | 507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
CN 03 | Coburg North | Urban | 1341 | 4.826 | 0.952 | 2.4006 | 1.2767 | 0.16368 | 3 | 152947 | 152947 | 2664 | 2664 | 7 | 65360 | 65360 | 232 | 232 | 0 | 0 | 0 | N
CN 04 | Coburg North | Urban | 1409 | 7.356 | 5.782 | 11.0502 | 4.1377 | 0.16122 | 4 | 61555 | 61555 | 183 | 183 | 2 | 7995 | 7995 | 28 | 28 | 0 | 0 | 0 | N
CN 05 | Coburg North | Urban | 3976 | 13.032 | 1.579 | 8.421 | 15.6259 | 0.34845 | 12 | 1357811 | 1357811 | 16253 | 16253 | 11 | 100930 | 100930 | 344 | 344 | 0 | 0 | 0 | Y
CN 06 | Coburg North | Urban | 2098 | 9.869 | 1.333 | 7.6208 | 1.1138 | 0.062078 | 4 | 47255 | 9814 | 221 | 85 | 3 | 8779 | 8779 | 41 | 41 | 1 | 2113 | 2113 | N
CN 07 | Coburg North | Urban | 5430 | 16.075 | 1.382 | 9.2974 | 2.8846 | 0.82242 | 14 | 301325 | 301240 | 8276 | 8275 | 18 | 286362 | 286362 | 1054 | 1054 | 6 | 18742 | 18742 | N
CN 08 | Coburg North | Urban | 2847 | 11.631 | 2.292 | 6.4777 | 2.7778 | 0.28897 | 10 | 188119 | 188119 | 3921 | 3921 | 7 | 65233 | 65233 | 226 | 226 | 0 | 0 | 0 | N
CN 09 | Coburg North | Urban | 47 | 2.432 | 0.542 | 4.5725 | 2.1 | 1.6277 | 2 | 2921 | 2921 | 50 | 50 | 3 | 7547 | 7547 | 16 | 16 | 0 | 0 | 0 | N
CN 10 | Coburg North | Urban | 1902 | 6.247 | 1.067 | 7.4303 | 4.0833 | 0.0066334 | 6 | 132963 | 132963 | 2090 | 2090 | 1 | 720 | 720 | 4 | 4 | 0 | 0 | 0 | N
CN 11 | Coburg North | Urban | 3224 | 11.857 | 1.438 | 8.3448 | 6.0859 | 0.47851 | 15 | 482342 | 482342 | 9558 | 9558 | 8 | 126414 | 126414 | 376 | 376 | 0 | 0 | 0 | N
COO11 | Coolaroo | Rural-short | 1731 | 132.531 | 25.584 | 9.2974 | 25.9519 | 4.4068 | 24 | 719942 | 719942 | 1288 | 1288 | 35 | 407505 | 407505 | 1165 | 1165 | 4 | 1749 | 1749 | Y
COO12 | Coolaroo | Urban | 1 | 0.269 | 0.549 | 4.5344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
COO13 | Coolaroo | Urban | 3923 | 6.229 | 11.297 | 11.3169 | 2.7295 | 0.09702 | 9 | 220415 | 169565 | 4966 | 4800 | 5 | 26115 | 26115 | 118 | 118 | 1 | 17 | 17 | N
COO14 | Coolaroo | Urban | 2931 | 1.382 | 13.884 | 6.8587 | 0.060567 | 0 | 3 | 5298 | 5298 | 53 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
COO21 | Coolaroo | Urban | 1928 | 16.845 | 10.862 | 7.8079 | 0.027664 | 0.099241 | 1 | 1586 | 1586 | 10 | 10 | 6 | 18965 | 18965 | 72 | 72 | 0 | 0 | 0 | N
COO22 | Coolaroo | Urban | 3500 | 0.713 | 19.266 | 10.0595 | 3.3833 | 0 | 3 | 194687 | 194687 | 3601 | 3601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
CS 02 | Coburg South | Urban | 5563 | 14.955 | 1.041 | 11.1645 | 1.1804 | 0.33138 | 9 | 130313 | 130313 | 2228 | 2228 | 14 | 121941 | 121941 | 440 | 440 | 1 | 4212 | 4212 | N
CS 03 | Coburg South | Urban | 3976 | 10.861 | 2.427 | 9.2593 | 4.0214 | 0.063217 | 18 | 287706 | 287706 | 10166 | 10166 | 5 | 15076 | 15076 | 57 | 57 | 0 | 0 | 0 | N
CS 05 | Coburg South | Urban | 4730 | 12.113 | 0.711 | 9.2593 | 1.3565 | 0.27273 | 6 | 135006 | 47925 | 552 | 437 | 8 | 90477 | 90477 | 348 | 348 | 0 | 0 | 0 | N
CS 08 | Coburg South | Urban | 2913 | 8.417 | 2.305 | 8.6496 | 4.9806 | 0.29895 | 3 | 237346 | 101101 | 6623 | 3584 | 9 | 47487 | 47487 | 146 | 146 | 0 | 0 | 0 | N
CS 09 | Coburg South | Urban | 1981 | 4.034 | 1.828 | 4.9795 | 3.0075 | 0.091885 | 4 | 253730 | 253730 | 1272 | 1272 | 6 | 25840 | 25840 | 96 | 96 | 0 | 0 | 0 | N
CS 12 | Coburg South | Urban | 1914 | 9.01 | 1.026 | 7.4095 | 1.2525 | 0.071464 | 12 | 44089 | 44089 | 416 | 416 | 2 | 8385 | 8385 | 32 | 32 | 0 | 0 | 0 | N
CS 13 | Coburg South | Urban | 1714 | 5.576 | 2.515 | 3.4294 | 0.16868 | 0.027472 | 2 | 12671 | 12671 | 96 | 96 | 2 | 6879 | 6879 | 30 | 30 | 0 | 0 | 0 | N
EP 02 | East Preston | Urban | 58 | 0.776 | 0.26 | 2.8235 | 0.017999 | 1.6041 | 1 | 96 | 96 | 2 | 2 | 2 | 28520 | 28520 | 59 | 59 | 0 | 0 | 0 | Y
EP 03 | East Preston | Urban | 91 | 1.035 | 0.458 | 1.7947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 04 | East Preston | Urban | 5 | 1.126 | 0.367 | 1.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 07 | East Preston | Urban | 45 | 1.915 | 0.719 | 2.2177 | 0 | 0.040464 | 0 | 0 | 0 | 0 | 0 | 1 | 485 | 485 | 5 | 5 | 0 | 0 | 0 | N
EP 09 | East Preston | Urban | 237 | 2.549 | 0.661 | 2.8235 | 0.76718 | 0.014002 | 10 | 10109 | 9185 | 56 | 50 | 1 | 615 | 615 | 3 | 3 | 0 | 0 | 0 | N
EP 11 | East Preston | Urban | 433 | 3.85 | 0.554 | 1.8176 | 0.042249 | 0.0062189 | 1 | 2140 | 2140 | 25 | 25 | 1 | 1050 | 1050 | 5 | 5 | 0 | 0 | 0 | N
EP 16 | East Preston | Urban | 57 | 1.952 | 0.151 | 2.7778 | 0.41024 | 0 | 2 | 1363 | 1363 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 17 | East Preston | Urban | 132 | 1.038 | 0.357 | 2.995 | 0.50812 | 2.6369 | 1 | 3648 | 3648 | 132 | 132 | 2 | 63105 | 63105 | 130 | 130 | 0 | 0 | 0 | Y
EP 18 | East Preston | Urban | 18 | 1.271 | 0.331 | 1.5661 | 0.3249 | 0 | 1 | 800 | 800 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 20 | East Preston | Urban | 358 | 2.497 | 0.164 | 3.0293 | 0.67884 | 0.61763 | 2 | 14435 | 14435 | 80 | 80 | 4 | 43778 | 43778 | 118 | 118 | 1 | 354 | 354 | N
EP 27 | East Preston | Urban | 26 | 0.053 | 1.49 | 2.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 34 | East Preston | Urban | 1433 | 5.226 | 0.754 | 3.1779 | 0.12167 | 0.14664 | 4 | 13951 | 13792 | 148 | 147 | 6 | 56048 | 56048 | 212 | 212 | 0 | 0 | 0 | N
EP 35 | East Preston | Urban | 30 | 1.882 | 0.397 | 2.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 36 | East Preston | Urban | 963 | 5.215 | 0.268 | 2.2634 | 0.50753 | 0.1583 | 4 | 42953 | 42953 | 272 | 272 | 2 | 44656 | 44656 | 137 | 137 | 0 | 0 | 0 | N
EP 37 | East Preston | Urban | 843 | 3.675 | 0.326 | 3.4179 | 0.22514 | 0.28585 | 3 | 9725 | 9725 | 107 | 107 | 5 | 41157 | 41157 | 180 | 180 | 0 | 0 | 0 | N
EP 41 | East Preston | Urban | 56 | 1.404 | 0.536 | 3.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
EP 42 | East Preston | Urban | 292 | 2.66 | 0.54 | 3.0636 | 0.036206 | 0 | 0 | 565 | 565 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ES 11 | Essendon | Urban | 1141 | 4.334 | 0.559 | 5.2012 | 0.043738 | 0.027503 | 1 | 1979 | 1979 | 32 | 32 | 1 | 4148 | 4148 | 17 | 17 | 0 | 0 | 0 | N
ES 12 | Essendon | Urban | 1232 | 3.919 | 0.334 | 2.2672 | 0.15958 | 0.0085052 | 4 | 15423 | 14815 | 115 | 104 | 1 | 2740 | 2740 | 137 | 137 | 0 | 0 | 0 | N
ES 13 | Essendon | Urban | 2647 | 7.485 | 1.14 | 7.3541 | 0.18826 | 0.2027 | 2 | 17177 | 17177 | 257 | 257 | 7 | 61648 | 61648 | 190 | 190 | 1 | 2643 | 2643 | N
ES 15 | Essendon | Urban | 2020 | 5.729 | 1.98 | 5.5441 | 0.50349 | 0.23332 | 3 | 34503 | 34503 | 233 | 233 | 4 | 53296 | 53296 | 129 | 129 | 0 | 0 | 0 | N
ES 16 | Essendon | Urban | 1310 | 3.799 | 0.47 | 3.0102 | 1.6188 | 0.0624 | 2 | 127794 | 127794 | 1984 | 1984 | 2 | 16420 | 16420 | 44 | 44 | 2 | 2423 | 2423 | N
ES 21 | Essendon | Urban | 1553 | 3.425 | 0.573 | 4.9916 | 0.29527 | 0.12149 | 7 | 20398 | 20398 | 187 | 187 | 6 | 27976 | 27976 | 127 | 127 | 0 | 0 | 0 | N
ES 23 | Essendon | Urban | 479 | 1.104 | 0.444 | 1.2263 | 0.0017013 | 0 | 0 | 102 | 102 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ES 24 | Essendon | Urban | 1838 | 4.24 | 1.038 | 5.868 | 0.1621 | 0.10248 | 3 | 8801 | 8801 | 77 | 77 | 2 | 18546 | 18546 | 51 | 51 | 1 | 1831 | 1831 | N
ES 25 | Essendon | Urban | 1058 | 3.86 | 2.009 | 4.9345 | 0.94691 | 0.015695 | 4 | 53214 | 53214 | 1111 | 1111 | 1 | 2940 | 2940 | 6 | 6 | 1 | 865 | 865 | N
ES 26 | Essendon | Urban | 1268 | 2.74 | 1.84 | 5.144 | 0.19708 | 0.18514 | 2 | 10422 | 10422 | 82 | 82 | 1 | 32635 | 32635 | 107 | 107 | 1 | 1281 | 1281 | N
FE 02 | Footscray | Urban | 72 | 0.748 | 1.822 | 1.2678 | 0.071973 | 0 | 0 | 668 | 668 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
FE 05 | Footscray | Urban | 3099 | 8.42 | 0.853 | 8.802 | 4.0858 | 0.37782 | 7 | 312982 | 300735 | 3391 | 3354 | 6 | 96474 | 96474 | 381 | 381 | 3 | 8193 | 8193 | N
FE 06 | Footscray | Urban | 4062 | 9.046 | 7.238 | 10.8596 | 1.6516 | 0.077767 | 9 | 84575 | 66824 | 570 | 524 | 3 | 13274 | 13274 | 47 | 47 | 2 | 5307 | 5307 | N
FE 08 | Footscray | Urban | 2233 | 3.843 | 5.146 | 8.2686 | 2.3319 | 0.64354 | 7 | 84036 | 45384 | 347 | 209 | 6 | 77306 | 77306 | 317 | 317 | 2 | 18 | 18 | N
FE 09 | Footscray | Urban | 4045 | 7.404 | 1.148 | 6.8206 | 5.0415 | 0.064393 | 13 | 501090 | 501090 | 13618 | 13618 | 6 | 21334 | 21334 | 96 | 96 | 2 | 4408 | 4408 | N
FF 87 | Fairfield | Urban | 974 | 2.632 | 0.238 | 1.9776 | 0.064209 | 0.019472 | 2 | 4501 | 4501 | 32 | 32 | 1 | 4550 | 4550 | 13 | 13 | 0 | 0 | 0 | N
FF 88 | Fairfield | Urban | 1269 | 3.949 | 0.454 | 2.1605 | 0.074244 | 0.079571 | 0 | 7401 | 7401 | 19 | 19 | 3 | 26440 | 26440 | 98 | 98 | 0 | 0 | 0 | N
FF 89 | Fairfield | Urban | 371 | 3.912 | 0.836 | 2.2862 | 1.3367 | 0 | 2 | 37408 | 37408 | 388 | 388 | 0 | 0 | 0 | 0 | 0 | 4 | 1468 | 1468 | N
FF 90 | Fairfield | Urban | 1039 | 3.427 | 0.394 | 2.7206 | 0.51465 | 0 | 2 | 35757 | 35757 | 1095 | 1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
FF 95 | Fairfield | Urban | 1645 | 4.795 | 0.065 | 3.2465 | 1.777 | 0.3965 | 7 | 178599 | 178599 | 1345 | 1345 | 4 | 132835 | 130435 | 362 | 347 | 0 | 0 | 0 | N
FF 96 | Fairfield | Urban | 1038 | 3.691 | 0.386 | 2.4463 | 0.063445 | 0.036741 | 2 | 5452 | 5452 | 50 | 50 | 2 | 10524 | 10524 | 42 | 42 | 0 | 0 | 0 | N
FT 01 | Flemington | Urban | 3556 | 6.718 | 2.639 | 6.6491 | 1.5 | 0.10936 | 9 | 135773 | 132331 | 3963 | 3951 | 4 | 32994 | 32994 | 115 | 115 | 1 | 3565 | 3565 | N
FT 02 | Flemington | Urban | 290 | 1.59 | 5.677 | 3.9438 | 0.019271 | 0.23845 | 0 | 294 | 294 | 2 | 2 | 3 | 12126 | 12126 | 37 | 37 | 0 | 0 | 0 | N
FT 04 | Flemington | Urban | 1520 | 3.494 | 2.86 | 4.02 | 0.094162 | 0.55311 | 2 | 4645 | 4645 | 42 | 42 | 7 | 90950 | 90950 | 251 | 251 | 0 | 0 | 0 | N
FT 05 | Flemington | Urban | 2392 | 4.668 | 2.037 | 4.4772 | 2.7969 | 0.019151 | 10 | 244481 | 244481 | 2805 | 2805 | 2 | 5580 | 5580 | 20 | 20 | 0 | 0 | 0 | N
FT 06 | Flemington | Urban | 245 | 0.674 | 1.26 | 2.1719 | 0.53146 | 0 | 2 | 10009 | 9469 | 249 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
FT 09 | Flemington | Urban | 1795 | 3.113 | 3.121 | 5.6394 | 0.58416 | 0.22295 | 3 | 27595 | 19688 | 197 | 171 | 3 | 35107 | 35107 | 88 | 88 | 1 | 1786 | 1786 | N
FT 10 | Flemington | Urban | 2075 | 4.15 | 1.891 | 4.02 | 0.04771 | 0.015156 | 0 | 3312 | 3312 | 21 | 21 | 1 | 3507 | 3507 | 7 | 7 | 2 | 5298 | 5298 | N
FT 13 | Flemington | Urban | 1272 | 2.359 | 5.599 | 5.8109 | 2.2166 | 0.023036 | 3 | 92372 | 92372 | 1859 | 1859 | 2 | 3200 | 3200 | 10 | 10 | 1 | 769 | 769 | N
FT 14 | Flemington | Urban | 1592 | 1.883 | 1.712 | 4.6487 | 0.57941 | 0.5881 | 4 | 25123 | 25123 | 157 | 157 | 3 | 84998 | 84998 | 219 | 219 | 2 | 3132 | 3132 | N
FT 15 | Flemington | Urban | 87 | 0.127 | 0.943 | 3.4294 | 0.017987 | 0 | 0 | 58 | 58 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
FW 04 | Footscray West | Urban | 1535 | 5.782 | 1.455 | 7.7351 | 5.5421 | 0.73092 | 7 | 140173 | 139744 | 3384 | 3383 | 5 | 61622 | 61622 | 167 | 167 | 1 | 9 | 9 | N
FW 05 | Footscray West | Urban | 1642 | 7.483 | 1.135 | 4.5344 | 0.064328 | 0.094012 | 1 | 4007 | 4007 | 36 | 36 | 1 | 19520 | 19520 | 61 | 61 | 1 | 1620 | 1620 | N
FW 06 | Footscray West | Urban | 968 | 5.618 | 2.651 | 4.8011 | 0.84938 | 0.66878 | 1 | 25435 | 915 | 981 | 8 | 4 | 66756 | 66756 | 182 | 182 | 0 | 0 | 0 | N
FW 08 | Footscray West | Urban | 2899 | 7.81 | 1.237 | 8.3067 | 2.5509 | 0.17138 | 9 | 167880 | 57143 | 3241 | 397 | 3 | 37595 | 37595 | 98 | 98 | 5 | 14204 | 8516 | N
FW 09 | Footscray West | Urban | 1369 | 9.061 | 3.665 | 8.5353 | 3.449 | 1.022 | 7 | 79575 | 74475 | 1070 | 1059 | 10 | 78599 | 78599 | 236 | 236 | 1 | 1311 | 1311 | N
FW 13 | Footscray West | Urban | 457 | 5.14 | 0.644 | 11.3169 | 8.7075 | 0 | 4 | 43103 | 43103 | 494 | 494 | 0 | 0 | 0 | 0 | 0 | 1 | 156 | 156 | N
FW 16 | Footscray West | Urban | 2536 | 9.193 | 0.351 | 4.763 | 2.8936 | 0.32803 | 9 | 202602 | 132752 | 2975 | 2845 | 4 | 76559 | 76559 | 217 | 217 | 3 | 7431 | 7431 | N
FW 17 | Footscray West | Urban | 2291 | 8.579 | 0.305 | 4.0009 | 2.2003 | 0.10681 | 10 | 213979 | 174953 | 2878 | 2794 | 2 | 34623 | 34623 | 107 | 107 | 0 | 0 | 0 | N
HB 14 | Heidelberg | Urban | 1708 | 5.305 | 2.002 | 5.2202 | 5.6387 | 0.0012611 | 6 | 321939 | 321939 | 4506 | 4506 | 1 | 240 | 240 | 2 | 2 | 1 | 1712 | 1712 | N
HB 15 | Heidelberg | Urban | 2389 | 9.397 | 1.287 | 6.1347 | 0.772 | 0.013404 | 6 | 58054 | 58054 | 1335 | 1335 | 1 | 3360 | 3360 | 14 | 14 | 3 | 3286 | 3286 | N
HB 22 | Heidelberg | Urban | 1121 | 5.005 | 0.904 | 3.9819 | 4.0775 | 0.027258 | 8 | 194091 | 194091 | 3159 | 3159 | 2 | 4325 | 4325 | 26 | 26 | 1 | 1116 | 1116 | N
HB 23 | Heidelberg | Urban | 1470 | 5.48 | 0.512 | 3.9247 | 3.6598 | 0.22267 | 5 | 305748 | 77246 | 3062 | 1526 | 4 | 62007 | 62007 | 200 | 200 | 0 | 0 | 0 | N
HB 24 | Heidelberg | Urban | 875 | 6.455 | 0.346 | 3.7342 | 0.60304 | 0.19928 | 4 | 28440 | 4941 | 97 | 34 | 4 | 31328 | 31328 | 120 | 120 | 0 | 0 | 0 | N
HB 31 | Heidelberg | Urban | 737 | 1.51 | 0.528 | 3.8485 | 0.10428 | 0 | 1 | 3278 | 3278 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
HB 32 | Heidelberg | Urban | 523 | 2.167 | 0.578 | 3.0483 | 0.80196 | 0.77651 | 1 | 22856 | 22856 | 80 | 80 | 4 | 73769 | 73769 | 224 | 224 | 0 | 0 | 0 | N
KLO13 | Kalkallo | Rural-short | 15 | 0.32 | 0.939 | 0.27019 | 0 | 0.1417 | 0 | 0 | 0 | 0 | 0 | 4 | 4505 | 4505 | 11 | 11 | 1 | 2 | 2 | N
KLO22 | Kalkallo | Rural-short | 1899 | 12.242 | 17.308 | 2.4768 | 0.054671 | 0.17114 | 2 | 7298 | 7298 | 36 | 36 | 4 | 76152 | 76152 | 194 | 194 | 4 | 7439 | 7439 | N
NH 02 | North Heidelberg | Urban | 4231 | 16.305 | 4.108 | 9.6784 | 2.6331 | 0.15022 | 13 | 240915 | 239763 | 3129 | 3128 | 6 | 45815 | 45815 | 167 | 167 | 3 | 5433 | 5433 | N
NH 03 | North Heidelberg | Urban | 1311 | 9.16 | 0.78 | 7.8113 | 3.391 | 0.39335 | 10 | 105063 | 98273 | 787 | 724 | 3 | 40624 | 40624 | 104 | 104 | 2 | 2205 | 2205 | N
NH 05 | North Heidelberg | Urban | 4533 | 16.175 | 1.134 | 7.2398 | 4.889 | 0.022752 | 15 | 546665 | 546665 | 10682 | 10682 | 3 | 8480 | 8480 | 38 | 38 | 5 | 6968 | 6968 | N
NH 08 | North Heidelberg | Urban | 2592 | 11.243 | 1.334 | 5.7537 | 1.0328 | 0.13569 | 7 | 108569 | 108569 | 397 | 397 | 7 | 47546 | 47546 | 170 | 170 | 4 | 6690 | 6690 | N
NH 09 | North Heidelberg | Urban | 638 | 6.512 | 1.254 | 9.4117 | 9.652 | 2.7295 | 9 | 109303 | 105177 | 1538 | 1507 | 8 | 103032 | 103032 | 202 | 202 | 0 | 0 | 0 | Y
NH 12 | North Heidelberg | Urban | 17 | 0 | 4.028 | 4.4582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
NH 13 | North Heidelberg | Urban | 593 | 2.563 | 2.662 | 7.5065 | 4.5289 | 0 | 1 | 45113 | 45113 | 789 | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
NH 16 | North Heidelberg | Urban | 2555 | 7.169 | 4.486 | 8.1924 | 10.4472 | 0.44411 | 10 | 530867 | 529298 | 3519 | 3506 | 9 | 75224 | 75224 | 317 | 317 | 3 | 5133 | 5133 | N
NH 17 | North Heidelberg | Urban | 2022 | 6.403 | 2.026 | 7.1636 | 3.273 | 0.67366 | 7 | 139353 | 139353 | 4317 | 4317 | 8 | 95608 | 95608 | 352 | 352 | 6 | 8523 | 8523 | N
NH 20 | North Heidelberg | Urban | 1993 | 8.128 | 2.563 | 3.6199 | 0.68025 | 0.071316 | 5 | 61294 | 54467 | 475 | 261 | 2 | 21420 | 21420 | 36 | 36 | 1 | 1940 | 1940 | N
NS 07 | North Essendon | Urban | 1064 | 3.714 | 1.68 | 4.5534 | 0.0045953 | 0.22891 | 0 | 172 | 172 | 2 | 2 | 1 | 28560 | 28560 | 112 | 112 | 0 | 0 | 0 | N
NS 08 | North Essendon | Urban | 1159 | 2.945 | 0.263 | 2.934 | 0.21158 | 0.043204 | 1 | 15867 | 15867 | 70 | 70 | 1 | 10800 | 10800 | 30 | 30 | 0 | 0 | 0 | N
NS 09 | North Essendon | Urban | 1032 | 3.659 | 1.147 | 4.5915 | 0.080677 | 0.1043 | 1 | 3200 | 3200 | 38 | 38 | 3 | 13790 | 13790 | 64 | 64 | 0 | 0 | 0 | N
NS 11 | North Essendon | Urban | 0 | 0 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
NS 12 | North Essendon | Urban | 1229 | 3.676 | 1.17 | 3.0674 | 1.0004 | 0.18505 | 5 | 95063 | 95063 | 1356 | 1356 | 4 | 58617 | 58617 | 162 | 162 | 0 | 0 | 0 | N
NS 14 | North Essendon | Urban | 1419 | 5.613 | 1.263 | 5.125 | 1.2528 | 0 | 7 | 76115 | 76115 | 1654 | 1654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
NS 15 | North Essendon | Urban | 1547 | 4.401 | 1.145 | 4.5153 | 2.9801 | 0.010214 | 3 | 183818 | 183818 | 3138 | 3138 | 1 | 2100 | 2100 | 12 | 12 | 1 | 1552 | 1552 | N
NS 16 | North Essendon | Urban | 701 | 3.189 | 0.422 | 1.9243 | 0.72238 | 0 | 5 | 58195 | 58195 | 1396 | 1396 | 0 | 0 | 0 | 0 | 0 | 2 | 887 | 887 | N
NS 17 | North Essendon | Urban | 809 | 3.575 | 0.513 | 2.6482 | 0.018047 | 0.0073889 | 0 | 1231 | 990 | 10 | 9 | 1 | 1680 | 1680 | 8 | 8 | 0 | 0 | 0 | N
NS 18 | North Essendon | Urban | 1727 | 3.447 | 2.638 | 9.6403 | 0.23731 | 0.064706 | 2 | 6233 | 6233 | 58 | 58 | 1 | 5665 | 5665 | 11 | 11 | 0 | 0 | 0 | N
NT 03 | Newport | Urban | 2988 | 10.626 | 3.348 | 9.7546 | 2.1377 | 0.3258 | 5 | 135420 | 135420 | 3662 | 3662 | 5 | 68796 | 68796 | 208 | 208 | 5 | 12264 | 12264 | N
NT 04 | Newport | Urban | 1568 | 3.376 | 1.946 | 8.1543 | 9.862 | 0.30754 | 3 | 226263 | 226263 | 314 | 314 | 1 | 23520 | 23520 | 56 | 56 | 2 | 3059 | 3059 | N
NT 08 | Newport | Urban | 0 | 0 | 0.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
NT 10 | Newport | Urban | 64 | 1.9 | 0.841 | 1.6766 | 0 | 0.12149 | 0 | 0 | 0 | 0 | 0 | 2 | 1832 | 1832 | 8 | 8 | 0 | 0 | 0 | N
NT 11 | Newport | Urban | 3506 | 10.156 | 2.731 | 10.7159 | 10.0692 | 1.7541 | 12 | 733847 | 476516 | 9704 | 6053 | 10 | 426123 | 426123 | 973 | 973 | 4 | 6591 | 6591 | Y
NT 15 | Newport | Urban | 1195 | 5.349 | 2.937 | 5.487 | 0.069986 | 0.18896 | 1 | 3355 | 3355 | 39 | 39 | 3 | 30194 | 30194 | 131 | 131 | 0 | 0 | 0 | N
NT 16 | Newport | Urban | 216 | 2.912 | 1.609 | 5.487 | 0.07721 | 0.74155 | 1 | 1272 | 1272 | 6 | 6 | 3 | 40722 | 40722 | 107 | 107 | 0 | 0 | 0 | N
NT 17 | Newport | Urban | 2793 | 8.677 | 2.89 | 3.0407 | 0.20443 | 0.19066 | 5 | 32097 | 32097 | 356 | 356 | 4 | 99785 | 99785 | 265 | 265 | 2 | 4163 | 4163 | N
P 56 | Preston | Urban | 2 | 2.049 | 0.255 | 1.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
P 57 | Preston | Urban | 101 | 1.784 | 0.282 | 0.30864 | 0.044972 | 0 | 1 | 3183 | 3183 | 99 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
P 58 | Preston | Urban | 0 | 0.127 | 0.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
P 59 | Preston | Urban | 815 | 2.783 | 1.607 | 1.1546 | 0.37745 | 0.037378 | 1 | 52597 | 52597 | 812 | 812 | 5 | 17362 | 17362 | 88 | 88 | 0 | 0 | 0 | N
P 61 | Preston | Urban | 81 | 0.331 | 0.153 | 0.29721 | 0 | 0.18833 | 0 | 0 | 0 | 0 | 0 | 1 | 49770 | 49770 | 79 | 79 | 0 | 0 | 0 | Y
P 62 | Preston | Urban | 660 | 1.822 | 0.81 | 2.995 | 0.025551 | 0.0075455 | 0 | 960 | 960 | 4 | 4 | 1 | 945 | 945 | 3 | 3 | 0 | 0 | 0 | N
P 63 | Preston | Urban | 846 | 2.83 | 0.18 | 2.4691 | 0.86909 | 0.20555 | 2 | 57039 | 57039 | 923 | 923 | 3 | 44967 | 44967 | 149 | 149 | 0 | 0 | 0 | N
P 65 | Preston | Urban | 255 | 0.32 | 0.2 | 0.98308 | 0.42053 | 0.68884 | 3 | 15278 | 15278 | 173 | 173 | 4 | 83419 | 83419 | 251 | 251 | 0 | 0 | 0 | Y
P 66 | Preston | Urban | 733 | 2.132 | 0.657 | 3.2922 | 0.045761 | 0.23733 | 0 | 1952 | 1952 | 8 | 8 | 2 | 33745 | 33745 | 127 | 127 | 0 | 0 | 0 | N
PV 12 | Pascoe Vale | Urban | 466 | 2.614 | 1.647 | 1.3946 | 0.022243 | 0 | 0 | 1034 | 1034 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
PV 13 | Pascoe Vale | Urban | 3147 | 10.049 | 0.527 | 5.6203 | 0.61654 | 0.075813 | 8 | 71513 | 71466 | 1439 | 1438 | 2 | 29312 | 29312 | 80 | 80 | 1 | 3134 | 3134 | N
PV 14 | Pascoe Vale | Urban | 2765 | 10.059 | 0.934 | 6.0776 | 0.051649 | 0.0047917 | 1 | 5384 | 5384 | 41 | 41 | 1 | 1665 | 1665 | 9 | 9 | 0 | 0 | 0 | N
PV 15 | Pascoe Vale | Urban | 1741 | 5.392 | 0.372 | 3.9057 | 0.97096 | 0.47798 | 3 | 97792 | 96710 | 1783 | 1780 | 9 | 160468 | 160468 | 612 | 612 | 0 | 0 | 0 | N
PV 21 | Pascoe Vale | Urban | 1249 | 5.598 | 0.181 | 2.8006 | 0.16168 | 0.0061045 | 3 | 13547 | 13547 | 478 | 478 | 1 | 1705 | 1705 | 11 | 11 | 0 | 0 | 0 | N
PV 22 | Pascoe Vale | Urban | 2549 | 9.884 | 0.428 | 6.1728 | 0.6872 | 0.10851 | 5 | 73176 | 73176 | 1983 | 1983 | 5 | 38515 | 38515 | 193 | 193 | 4 | 4309 | 4309 | N
PV 23 | Pascoe Vale | Urban | 2398 | 8.015 | 0.185 | 5.3727 | 1.0568 | 0.16162 | 4 | 109708 | 108850 | 2503 | 2502 | 1 | 55930 | 55930 | 119 | 119 | 0 | 0 | 0 | N
PV 24 | Pascoe Vale | Urban | 1678 | 6.928 | 0.535 | 5.0869 | 6.0737 | 0.17071 | 5 | 411362 | 411362 | 5274 | 5274 | 1 | 38540 | 38540 | 82 | 82 | 1 | 1684 | 1684 | N
PV 31 | Pascoe Vale | Urban | 1984 | 5.815 | 1.471 | 4.8964 | 0.54053 | 0 | 4 | 35376 | 35376 | 169 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
SA 02 | St Alban | Rural-short | 63 | 13.591 | 0 | 0.22862 | 0.03908 | 0.14646 | 4 | 2563 | 2563 | 122 | 122 | 6 | 32019 | 32019 | 88 | 88 | 0 | 0 | 0 | N
SA 06 | St Alban | Urban | 146 | 4.366 | 1.203 | 0.45725 | 0.036016 | 0 | 2 | 2737 | 1138 | 9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
SA 10 | St Alban | Urban | 43 | 1.262 | 0.816 | 0.038104 | 0.0098369 | 0 | 2 | 2642 | 2642 | 86 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
SA 12 | St Alban | Urban | 1842 | 1.085 | 6.188 | 3.8104 | 0.57111 | 0 | 4 | 65708 | 65708 | 3935 | 3935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
SBY11 | Sunbury | Rural-short | 2974 | 62.273 | 10.736 | 6.6301 | 3.2352 | 1.5746 | 24 | 217468 | 214677 | 4892 | 4887 | 29 | 352807 | 352807 | 1621 | 1621 | 5 | 1680 | 1680 | N
SBY13 | Sunbury | Urban | 0 | 0 | 0.283 | 4.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
SBY14 | Sunbury | Rural-short | 4101 | 90.845 | 23.177 | 12.6886 | 4.3592 | 1.088 | 12 | 264553 | 44271 | 4419 | 274 | 24 | 220097 | 220097 | 765 | 765 | 0 | 0 | 0 | N
SBY31 | Sunbury | Urban | 2117 | 6.307 | 7.967 | 7.697 | 0.46947 | 0.0029237 | 7 | 20136 | 20136 | 108 | 108 | 2 | 418 | 418 | 4 | 4 | 0 | 0 | 0 | N
SBY32 | Sunbury | Rural-short | 2915 | 116.619 | 10.233 | 6.4396 | 3.7185 | 0.44721 | 16 | 295176 | 295176 | 779 | 779 | 64 | 118332 | 118332 | 522 | 522 | 5 | 7676 | 7676 | N
SBY33 | Sunbury | Urban | 3004 | 14.103 | 4.584 | 7.5446 | 3.3474 | 0.58768 | 6 | 284137 | 284137 | 3418 | 3418 | 10 | 166281 | 166281 | 734 | 734 | 1 | 2740 | 2740 | N
SHM11 | Sydenham | Rural-short | 1062 | 64.326 | 3.128 | 2.4768 | 0.43577 | 1.5472 | 15 | 19972 | 19972 | 1837 | 1837 | 17 | 236364 | 236364 | 972 | 972 | 2 | 2810 | 2810 | N
SHM12 | Sydenham | Urban | 2841 | 4.711 | 14.954 | 8.3829 | 1.4371 | 0.15333 | 6 | 102823 | 102823 | 328 | 328 | 2 | 36570 | 36570 | 90 | 90 | 0 | 0 | 0 | N
SHM14 | Sydenham | Urban | 3895 | 18.868 | 22.925 | 11.0502 | 4.8654 | 1.3185 | 5 | 354107 | 354107 | 3676 | 3676 | 8 | 319861 | 319861 | 865 | 865 | 0 | 0 | 0 | N
SHM21 | Sydenham | Urban | 4900 | 3.885 | 20.493 | 11.0121 | 2.4565 | 0 | 7 | 228826 | 228826 | 5135 | 5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
SHM24 | Sydenham | Urban | 1 | 0 | 0.807 | 7.3541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ST 11 | Somerton | Urban | 177 | 6.981 | 4.202 | 7.8113 | 10.3285 | 1.9176 | 3 | 33493 | 33493 | 354 | 354 | 4 | 20728 | 20728 | 98 | 98 | 0 | 0 | 0 | Y
ST 12 | Somerton | Urban | 241 | 9.54 | 3.136 | 7.6485 | 11.1029 | 0.38312 | 9 | 39454 | 13190 | 497 | 257 | 3 | 4538 | 4538 | 33 | 33 | 1 | 240 | 240 | N
ST 13 | Somerton | Urban | 193 | 4.786 | 4.262 | 6.3634 | 3.4181 | 0 | 4 | 17212 | 17212 | 205 | 205 | 0 | 0 | 0 | 0 | 0 | 1 | 190 | 190 | N
ST 14 | Somerton | Urban | 88 | 0 | 4.985 | 7.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ST 21 | Somerton | Urban | 3 | 0 | 1.41 | 0.38104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ST 22 | Somerton | Urban | 4328 | 6.83 | 16.249 | 12.6886 | 0.12571 | 0.12225 | 3 | 7083 | 7083 | 58 | 58 | 4 | 22960 | 22960 | 162 | 162 | 0 | 0 | 0 | N
ST 23 | Somerton | Urban | 149 | 7.213 | 3.511 | 10.6691 | 1.0119 | 0 | 4 | 2091 | 2091 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ST 24 | Somerton | Urban | 1 | 0 | 3.765 | 4.6106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ST 31 | Somerton | Urban | 1 | 0 | 0.617 | 6.592 | 1.481 | 0 | 1 | 86 | 86 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
ST 32 | Somerton | Urban | 5801 | 9.194 | 32.822 | 12.1933 | 4.0166 | 0.21695 | 8 | 362808 | 362808 | 5798 | 5798 | 11 | 65321 | 64841 | 255 | 254 | 2 | 11602 | 11602 | N
ST 33 | Somerton | Urban | 3093 | 11.043 | 5.805 | 9.145 | 7.4203 | 0 | 8 | 414339 | 358212 | 9893 | 9787 | 0 | 0 | 0 | 0 | 0 | 2 | 2690 | 2690 | N
ST 34 | Somerton | Urban | 302 | 6.855 | 7.294 | 7.9637 | 5.0116 | 0.80758 | 3 | 38592 | 38592 | 632 | 632 | 5 | 20729 | 20729 | 55 | 55 | 1 | 340 | 340 | N
TH 11 | Tottenham | Urban | 127 | 3.129 | 0.839 | 3.6961 | 0 | 1.9336 | 0 | 0 | 0 | 0 | 0 | 4 | 25910 | 25910 | 79 | 79 | 2 | 254 | 254 | N
TH 12 | Tottenham | Urban | 24 | 3.437 | 0.653 | 5.2202 | 0.28154 | 0 | 0 | 238 | 238 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
TH 13 | Tottenham | Urban | 54 | 3.227 | 0.502 | 3.3913 | 1.2102 | 0 | 2 | 4134 | 4134 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
TH 14 | Tottenham | Urban | 0 | 0 | 0.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
TH 21 | Tottenham | Urban | 153 | 5.482 | 0.802 | 19.2425 | 3.2136 | 0.3755 | 1 | 14732 | 14732 | 82 | 82 | 2 | 5738 | 5738 | 28 | 28 | 1 | 70 | 70 | N
TH 22 | Tottenham | Urban | 889 | 10.321 | 3.686 | 5.9823 | 1.1594 | 0.46072 | 11 | 37718 | 37718 | 987 | 987 | 5 | 49960 | 49960 | 202 | 202 | 0 | 0 | 0 | N
TH 23 | Tottenham | Urban | 2 | 0 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
TH 24 | Tottenham | Urban | 0 | 0 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
TT 03 | Thomastown | Urban | 2851 | 13.378 | 4.318 | 12.1933 | 1.8593 | 2.2584 | 7 | 67777 | 67777 | 329 | 329 | 25 | 274407 | 274407 | 1235 | 1235 | 1 | 2852 | 0 | N
TT 08 | Thomastown | Urban | 2785 | 14.915 | 1.963 | 7.5065 | 1.9556 | 0.25226 | 16 | 91168 | 79572 | 678 | 596 | 2 | 39200 | 39200 | 109 | 109 | 1 | 1273 | 1273 | N
TT 10 | Thomastown | Urban | 4140 | 14.608 | 1.554 | 8.8782 | 2.6278 | 0.20588 | 7 | 248086 | 246914 | 2970 | 2969 | 6 | 64789 | 64789 | 226 | 226 | 2 | 8262 | 8262 | N
TT 11 | Thomastown | Urban | 4774 | 11.886 | 0.146 | 10.0976 | 3.5437 | 0.32489 | 15 | 539356 | 538776 | 6550 | 6549 | 22 | 164831 | 164831 | 798 | 798 | 0 | 0 | 0 | N
WT 04 | Watsonia | Urban | 145 | 3.02 | 1.644 | 2.1338 | 0.0054603 | 0 | 0 | 52 | 52 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
YVE10 | Yarraville | Urban | 1 | 0 | 0.634 | 12.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
YVE11 | Yarraville | Urban | 1 | 0.005 | 0.835 | 5.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
YVE12 | Yarraville | Urban | 852 | 8.006 | 1.381 | 3.1245 | 4.3127 | 0.045652 | 6 | 159216 | 72019 | 1932 | 1086 | 4 | 5618 | 5618 | 27 | 27 | 1 | 841 | 841 | N
YVE14 | Yarraville | Urban | 247 | 1.668 | 0.842 | 4.6106 | 11.2557 | 1.0786 | 3 | 72746 | 72746 | 1047 | 1047 | 2 | 23237 | 23237 | 62 | 62 | 0 | 0 | 0 | Y
YVE15 | Yarraville | Urban | 557 | 6.288 | 5.218 | 4.0771 | 0.43489 | 0 | 1 | 8572 | 8572 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 1 | 569 | 569 | N
YVE21 | Yarraville | Urban | 689 | 4.77 | 2.783 | 6.1728 | 1.4635 | 0.58912 | 5 | 25176 | 25176 | 767 | 767 | 9 | 33781 | 33781 | 107 | 107 | 0 | 0 | 0 | N
YVE22 | Yarraville | Urban | 2485 | 7.87 | 13.613 | 6.0966 | 6.5489 | 0.024095 | 7 | 430121 | 430121 | 8692 | 8692 | 3 | 5275 | 3385 | 35 | 28 | 0 | 0 | 0 | N
YVE23 | Yarraville | Urban | 180 | 2.128 | 5.785 | 1.6004 | 0.31634 | 0 | 1 | 5510 | 5510 | 181 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
YVE24 | Yarraville | Urban | 777 | 3.347 | 1.538 | 3.5056 | 2.7545 | 0.097613 | 3 | 81779 | 7387 | 1630 | 62 | 3 | 9660 | 9660 | 35 | 35 | 0 | 0 | 0 | N
YVE25 | Yarraville | Urban | 2 | 0.663 | 1.455 | 3.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N
Note
(1) The sum of the number of distribution customers for each feeder category may not equal the average distribution customer numbers shown on sheet 1a, due to rounding.
Contents
Contents

## 4c. Network perf - reliability
JEN
Reliability - planned outages
2014
The information in templates 4a & c is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
SAIDI |  | 23.3182 | 104.669 |  | 26.852
SAIFI |  | 0.07981 | 0.38592 |  | 0.093107
Contents

## Amendments
Amendments - RIN rationalisation
Information no longer required from Annual Reporting RIN |  | Reasoning
(workbook/worksheet/table/row-column-cell)
Non-financial information templates
1c. STPIS Daily performance (customer service data and MAIFI data retained) | All SAIDI, SAIFI and MED information – columns C-F, I-L, O-R, U-X, AA-AD, AI | Information in Category analysis RIN Worksheet 6.3
1d. STPIS MED threshold | Entire worksheet | Information derived from Category analysis RIN Worksheet 6.3
1e. STPIS Exclusions | SAIDI and SAIFI data – col K,L (MAIFI data retained) | Information in Category analysis RIN Worksheet 6.3
3. General information | Entire worksheet | · Information in Benchmarking RIN Worksheet 5; table 5.1.1; table 5.2; table 7.3
· Information in Category analysis RIN Worksheet 5.2
· Redundant Information
4b Network perf – causes and WSC | Entire worksheet | Information in or derived from Category analysis RIN Worksheet 6.3