## Cover
Amendments made on 6 August 2014.
Click here for details.
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | Powercor Australia Ltd
DNSP - Australian business number: |  | ACN 064 651 109
Reporting year: |  | 2014
Business address | Address |  | 40 Market Street
| Suburb |  | Melbourne
|  | State | VIC | Postcode | 3000
Postal address | Address |  | Locked Bag 14090
| Suburb |  | Melbourne
|  | State | VIC | Postcode | 8001
Contact name/s | Hannah Williams
Contact phone/s | 03 9683 4088
Contact email address/s | hwilliams@powercor.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet
Definitions
1. Service Target Performance Incentive Scheme | 2. Quality of service and customer service
1a. STPIS - Reliability | 3. General Information (deleted)
1b. STPIS - Customer service | 4. Network performance
1c. STPIS - Daily performance | 4a. Network performance - feeder reliability
1d. STPIS - MED threshold (deleted) | 4b. Network performance - outages (deleted)
1e. STPIS - Exclusions | 4c. Network performance - planned outages
1f. STPIS - GSL

## Definitions
Powercor Australia Ltd
Definitions
2014
Appendix C – non- financial templates | Definition
STPIS
Customer numbers at the start of period | The number of Distribution Customers, measured on the first day of the Relevant Regulatory Year.
Customer numbers at the end of period | The number of Distribution Customers, measured on the last day of the Relevant Regulatory Year.
Distribution Customer/Customer | A Distribution Customer (with active accounts) with an active National Metering Identifier (NMI).
Duration of interruption (unplanned) (mins) | The duration of an unplanned interruption experienced by a customer.
Effect on unplanned MAIFI | Unplanned MAIFI for the event on the identified feeder.
Exclusion category/ Excluded event/Event category | The exclusions allowed under clauses 3.3 and 5.4 of the service target performance incentive scheme that applies to the DNSP.
Feeder classification | The following classification of the Feeder as: CBD: network is predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban: the network is not a CBD network, with actual maximum demand over the reporting period per total feeder (network) route length greater than 0.3 MVA/km; Rural Short: not a CBD or urban network with a network route length less than 200 km; Rural Long: not a CBD or urban network with a total network route length greater than 200 km; or as otherwise agreed with by the AER.
Feeder ID/name | The unique code or feeder identifier that the DNSP uses internally.
Interruption | Any planned or unplanned, monetary on sustained, loss of electricity supply to a customer associated with an outage of any part of the electricity supply network, including generation facilities and transmission networks, of more than 0.5 seconds (as recorded by equipment such as SCADA or, where such equipment does not exist, at the time of the first customer call relating to the network outage), including outages affecting a single premises; and not including subsequent interruptions caused by network switching during fault finding. An interruption ends when supply is again generally available to the customer.
MAIFI Momentary Average Interruption Frequency Index | As per the ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30: The total number of momentary interruptions divided by the total number of distribution customers. The number of Distribution Customers used to derive MAIFI should reflect the relevant network type: • Whole network – total Distribution Customers • Network classification (CBD/Urban/Rural short/Rural long) – CBD/Urban/Rural short/Rural long Customers respectively • Individual Feeder – Customers on that feeder.
MED - Major Event Day | As per the STPIS, Appendix D.
Network categorisation | The following classification of the network as: - CBD: network is predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. - Urban: the network is not a CBD network, with actual maximum demand over the reporting period per total feeder (network) route length greater than 0.3 MVA/km; - Rural Short: not a CBD or urban network with a network route length less than 200 km; - Rural Long: not a CBD or urban network with a total network route length greater than 200 km. or as otherwise agreed with by the AER
New connections - number | Total number of connections to customers' premises (excluding re-energisations).
New connections - number not provided on or before the agreed date | The number of connections to customers' premises (excluding re-energisations) made after the date agreed to with the customer
Number of calls answered in 30 seconds | The number of calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: (a) calls to payment lines and automated interactive services (b) calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned). Note: being placed in an automated queuing system (automated or otherwise) does not constitute a response.
Number of calls received | The number of calls to the fault line excluding: (a) calls to payment lines and automated interactive services; (b) calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned).
Outage ID/Event ID | The unique identifier for an outage used by the DNSP.
SAIDI System Average Interruption Duration Index | As per the STPIS: the sum of the duration of each sustained interruption (in minutes) divided by the total number of distribution customers as defined in the service target performance incentive scheme
SAIFI System Average Interruption Frequency Index | As per the STPIS: the total number of sustained interruptions divided by the total number of distribution customers as defined in the service target performance incentive scheme
Streetlight repair - Faulty streetlights not repaired within 5 business days of fault report or agreed date | The number of streetlights reported as not working within the reporting period that were not repaired within 5 days of the fault report, or were not repaired by the agreed date
Streetlight repair - number of streetlight faults | The number of streetlights reported by customers as not working in the reporting period
Streetlight repair - number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | The number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business as not working in the reporting period
Streetlight repair - number of streetlights | The total number of street lights
Telephone answering excluded events | The events listed in section 3.3 of the STPIS, November 2009.
Total unplanned minutes off supply | The sum of the duration of each unplanned interruption experienced by customers on a feeder, including single premise outages but not including momentary interruptions.
STPIS - GSL
AER GSL scheme | The Guaranteed service level component, in chapter 6 of the AER, Electricity distribution network service providers Service target performance incentive scheme, November 2009.
All other terms | As per the AER GSL Scheme, or the Victorian jurisdictional GSL scheme.
Victorian jurisdictional GSL scheme | As per the Victorian Electricity Distribution Code and the Public Lighting Code.
Customer service
Call centre - number of overload events | The number of times that the call centre queuing system is inadequate to queue all incoming calls
Calls abandoned | The number of calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator
Calls abandoned - percentage | (calls abandoned/calls to call centre fault line)* 100
Calls to fault line - average waiting time before call answered | The average time in seconds from when calls enter the system (including that time when a call may be ringing unanswered) and the caller speaks to a human operator or is connected to an interactive service that provides the information requested
Complaint | A written or verbal expression of dissatisfaction about an action, a proposed action, or a failure to act by a distributor, its employees or contractors. This includes failure by a distributor to observe its published practices or procedures
Complaint - administrative process or customer service | The number of complaints relating to the administrative process or customer service of Powercor, excluding those reported under 'connection and augmentation'
Complaint - connection or augmentation | The number of complaints about: (a) the quality and timeliness of a new connection; and (b) the cost, timeliness and quality of augmentation works
Complaint - other | The number of complaints that are not under the categories of 'connection & augmentation', 'reliability of supply', 'quality of supply' and 'administrative process or customer service'
Complaint - reliability of supply | The number of complaints relating to the reliability of supply
Complaint - technical quality of supply | The number of complaints relating to the technical quality of supply
Complaints - technical quality of supply - number | The total number of complaints made to the DNSP where the complaint raised issues about voltage variations.
Complaints by category - Low voltage supply | The proportion of complaints made to the DNSP where the complainant raised issues about low voltage supply
Complaints by category - Noise from appliances | The proportion of complaints made to the DNSP where the complainant raised issues about noise from appliances
Complaints by category - Other | The proportion of complaints made to the DNSP where the complainant raised issues about any matter that is not low voltage supply, voltage dips, volctage swell, voltage spike, TV or radio interference or noise from appliances.
Complaints by category - TV or radio interference | The proportion of complaints made to the DNSP where the complainant raised issues about TV or radio interference
Complaints by category - Voltage dips | The proportion of complaints made to the DNSP where the complainant raised issues about voltage dips
Complaints by category - Voltage spike (impulsive transient) | The proportion of complaints made to the DNSP where the complainant raised issues about voltage spikes (impulsive transient)
Complaints by category - Voltage swell | The proportion of complaints made to the DNSP where the complainant raised issues about voltage swell
Complaints by Likely Cause - Customer internal problem | The proportion of complaints where the event that gave rise to the complaint was likely to be a customer internal problem
Complaints by Likely Cause - Environmental | The proportion of complaints where the event that gave rise to the complaint was likely to be environmental
Complaints by Likely Cause - Network equipment faulty | The proportion of complaints where the event that gave rise to the complaint was likely to be faulty network equipment
Complaints by Likely Cause - Network interference by another customer | The proportion of complaints where the event that gave rise to the complaint was likely to be network interference by another customer
Complaints by Likely Cause - Network interference by NSP equipment | The proportion of complaints where the event that gave rise to the complaint was likely to be network interference by NSP equipment
Complaints by Likely Cause - Network limitation | The proportion of complaints where the event that gave rise to the complaint was likely to be a network limitation
Complaints by Likely Cause - No problem identified | The proportion of complaints where the event that gave rise to the complaint was not able to be identified
Complaints by Likely Cause - Other | The proportion of complaints where the event that gave rise to the complaint was likely to be a cause other than faulty network equipment, network interference by NSP equipment, network interference by another customer, a network limitation, a customer internal problem, environmental, or not able to be identified.
Customers receiving over-voltage - due to high voltage injection | The estimated number of customers affected by over-voltage events due to high voltage injection, based on customer’s with confirmed damage (including estimated damage) as investigated by the DNSP
Customers receiving over-voltage - due to lightning | The estimated number of customers affected by over-voltage events due to lightning, based on customer with confirmed damage (including estimated damage) and investigated by the DNSP
Customers receiving over-voltage - due to voltage regulation or other cause | The estimated number of customers affected by over-voltage events due to voltage regulations or other causes (including events due to unknown causes), based on confirmed damage (including estimated damage) and investigated by the DNSP
New connections - number | Total number of connections to customers' premises (excluding re-energisations).
New connections - number not provided on or before the agreed date | The number of connections to customers' premises (excluding re-energisations) made after the date agreed to with the customer
Over voltage events - due to high voltage injection | The number of over-voltage events, due to high voltage injection, in the distribution or transmission system leading to at least one customer complaint
Over voltage events - due to lightning | The number of over-voltage events, due to lightning, in the distribution or transmission system leading to at least one customer complaint
Over voltage events - due to voltage regulation or other cause | The number of over-voltage events, due to voltage regulation or other cause, in the distribution or transmission system leading to at least one customer complaint, including events due to an unknown cause
Streetlights - average monthly number "out" | The total number of street lights reported by customers as not working over the year, divided by twelve
Streetlights - average number of days to repair | The average number of days to repair street lights that were reported as not working
Number of calls | The total number of calls to the fault line to be reported, including any answered by an automated response service and terminated without being answered by an operator. Excludes missed calls where the fault line is overloaded.
Number of calls answered within 30 seconds | The number of calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: (a) calls to payment lines and automated interactive services (b) calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned). Note: being placed in an automated queuing system (automated or otherwise) does not constitute a response.
Telephone answering excluded events | The events listed in section 3.3 of the STPIS, November 2009.
Voltage variations - % feeders monitored | The percentage of feeders required to be monitored (i.e. one feeder supplied from each zone substation) that have recorders installed at the end of each Relevant Regulatory Year
Voltage variations - % zone subs monitored | The percentage of zone substations with recorders installed at the end of each Relevant Regulatory Year
Voltage variations - 10 seconds (zone sub) Min<0.7 | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside the standard nominal voltage range or set point voltage, and with a duration greater than or equal to 0.01 seconds (0.5 cycles) and less than 10 seconds, and where the minimum voltage variation during that excursion is less than 70% of the nominal voltage or set point voltage
Voltage variations - 10 seconds (zone sub) Min<0.8 | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside the standard nominal voltage range or set point voltage, and with a duration greater than or equal to 0.01 seconds (0.5 cycles) and less than 10 seconds, and where the minimum voltage during that excursion is less than 80% of the nominal voltage or set point voltage
Voltage variations - 10 seconds (zone sub) Min<0.9 | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside of the standard nominal voltage range or set point voltage and with a duration greater than or equal to 0.01 seconds (0.5 cycles) and less than 10 seconds, and where the minimum voltage variation during that excursion is less than 90% of the nominal voltage or set point voltage
Voltage variations - one minute (zone sub) | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside of the standard nominal voltage range or set point voltage, and with a duration greater than or equal to 10 seconds and less than 1 minute
Voltage variations - steady state (feeder) | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location on a feeder, outside the standard nominal voltage range or set point voltage under steady state (greater than or equal to 1 minute) conditions
Voltage variations - steady state (zone sub) | The aggregate number, in the Relevant Regulatory Year, of variations at each monitored location in a zone substation, outside of the standard nominal voltage range or set point voltage under steady state (greater than or equal to 1 minute) conditions
Network performance (outages, feeders, WSC, reliability)
Description of feeder service area | A description of the location of the Feeder
Duration of interruption | The duration of an interruption from the time as recorded by equipment such as SCADA or, where such equipment does not exist, the time of notification of an unplanned interruption by a customer or the commencement of a planned interruption to restoration of supply.
Energy not supplied (planned) (MWh) | Total energy not supplied (measured in MWh) minus Energy not supplied - Unplanned.
Energy not supplied (unplanned) (MWh) | The estimate of energy not supplied (due to unplanned outage) to be based on average Customer demand (multiplied by number of customers interrupted and the duration of the interruption). Average Customer demand to be determined from (in order of preference): (a) average consumption of the Customers interrupted based on their billing history (b) Feeder demand at the time of the interruption divided by the number of Customers on the Feeder (c) average consumption of Customers on the Feeder based on their billing history (d) average feeder demand derived from Feeder maximum demand and estimated load factor, divided by the number of customers on the Feeder.
Feeder classification | The following classification of the Feeder as: CBD: network is predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban: the network is not a CBD network, with actual maximum demand over the reporting period per total feeder (network) route length greater than 0.3 MVA/km; Rural Short: not a CBD or urban network with a network route length less than 200 km; Rural Long: not a CBD or urban network with a total network route length greater than 200 km.or as otherwise agreed with by the AER.
Feeder ID/name | The unique code or feeder identifier that the DNSP uses internally.
Length of high voltage distribution lines (overhead) | The route length (measured in kilometres) of overhead lines in service (the total length of Feeders including all spurs), where each SWER line, single-phase line, and three-phase line counts as one line. A double circuit line counts as two lines.
Length of high voltage distribution lines (underground) | The route length (measured in kilometres) of underground lines in service (the total length of Feeders including all spurs), where each SWER line, single-phase line, and three-phase line counts as one line. A double circuit line counts as two lines.
Low Reliability Feeder (SAIDI) | A Yes or No answer describing whether the annual reported SAIDI for a feeder is above or below the reporting threshold: CBD Feeder - 70, where the number of interuptions is greater than 1; Urban - 270; Short rural - 600; Long rural - 850. An answer of Yes is required if the reported SAIDI exceeds the threshold, and an answer of No is required if the reported SAIDI is less than or equal to the threshold. This definition includes both planned and unplanned SAIDI.
Maximum demand (MVA) | The recorded maximum demand for the Feeder.
Momentary Interruptions | the sum of Momentary Interruptions Due to Feeder Outages and Momentary Interruptions Due to Feeder Section Outages
Momentary interruptions due to feeder outages | the number of interruptions caused by momentary feeder outages
Number of distribution customers | The average of the number of Distribution Customers at the beginning of each Relevant Regulatory Year and the number of Distribution Customers at the end of the Relevant Regulatory Year.
Outage | An event causing an interuption
Planned interruptions (SAIFI) | The total number of planned sustained Customer interruptions divided by the total number of Distribution Customers. Planned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions. The number of Distribution Customers used to derive SAIFI should reflect the relevant network type: o Whole network - total Distribution Customers o Network classification (CBD/Urban/Rural short/Rural long) - CBD/Urban/Rural short/Rural long Customers respectively o Individual Feeder - Customers on that Feeder. Note: The number of Distribution Customers used to derive SAIDI and SAIFI is defined in the STPIS as: the average of the number of Customers at the beginning of the reporting period and the number of Customers at the end of the reporting period.
Planned outage | The number of planned events causing interruptions and does not include single premise outages.
Planned SAIDI | The sum of the duration of each planned sustained customer interruption (in minutes) divided by the total number of Distribution Customers. Planned SAIDI excludes momentary interruptions (one minute or less). The number of Distribution Customers used to derive SAIDI should reflect the relevant network type: • Whole network – total Distribution Customers • Network classification (CBD/Urban/Rural short/Rural long) – CBD/Urban/Rural short/Rural long Customers respectively • Individual Feeder – Customers on that feeder. Note: The number of Distribution Customers used to derive SAIDI and SAIFI is defined in the STPIS as: the average of the number of customers at the beginning of the reporting period and the number of customers at the end of the reporting period.
Total number of momentary feeder outages | The number of feeder outages of less than or equal to 1 minute (where each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one outage), but greater than 0.5 seconds, in duration, including any outage of an entire feeder (including due to a sub-transmission fault) that results in an interruption, and does not include an outage of a feeder section. Each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one momentary outage if the sequence is completed in no more than one minute. Re-closes that are followed by lockout are to be excluded from the momentary outage indicator.
Total number of momentary feeder section outages | The number of feeder section outages of less than or equal to 1 minute (where each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one outage), but greater than 0.5 seconds, in duration, including outages of a feeder section that result in an interruption but does not include feeder outages;Each sequence of auto-reclose attempts resulting in a successful auto re-close is counted as one momentary outage if the sequence is completed in no more than one minute. Re-closes that are followed by lockout are to be excluded from the momentary outage indicator.
Total unplanned customer minutes off supply (Mins) | The sum of the duration of each unplanned interruption experienced by Customers on a Feeder, including single premise outages but not including momentary interruptions.
Unplanned interruptions (SAIFI) | The total number of unplanned sustained Customer interruptions divided by the total number of Distribution Customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions. The number of Distribution Customers used to derive SAIFI should reflect the relevant network type: o Whole network - total Distribution Customers o Network classification (CBD/Urban/Rural short/Rural long) - CBD/Urban/Rural short/Rural long Customers respectively o Individual Feeder - Customers on that Feeder. Note: The number of Distribution Customers used to derive SAIDI and SAIFI is defined in the STPIS as: the average of the number of Customers at the beginning of the reporting period and the number of Customers at the end of the reporting period.
Unplanned outage | The number of unplanned events causing interruptions on the DNSP's network, including deliberate interruptions in response to an emergency event but does not include: (a) momentary outages and single premise outages (b) subsequent outages caused by network switching during fault finding.
Contents

## 1a. STPIS Reliability
Powercor Australia Ltd
STPIS Data Reporting
2014
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI (System Average Interruption Duration Index)
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
Total | 0 | 109.9701 | 142.1483 | 394.6753 | 197.4531
Total (after removing excluded events and MED) | 0 | 79.6058 | 130.6298 | 338.0304 | 166.227
Table 2: SAIFI (System Average Interruption Frequency Index)
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
Total | 0 | 1.248 | 1.5759 | 2.7938 | 1.7737
Total (after removing excluded events and MED) | 0 | 1.0686 | 1.5177 | 2.4905 | 1.6008
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
Total | 0 | 1.1398 | 2.9796 | 5.3671 | 2.8891
Total (after removing excluded events and MED) | 0 | 1.0446 | 2.8754 | 5.2446 | 2.7836
Table 4: Distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period | 0 | 303133 | 244058 | 203057 | 750248
Customer numbers at the end of period | 0 | 300632 | 255732 | 204906 | 761270
Average distribution customer numbers | 0 | 301882.5 | 249895 | 203981.5 | 755759
Contents
Contents

## 1b. STPIS Customer Service
Powercor Australia Ltd
STPIS Data Reporting - AER Definitions
2014
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
| Total - after removing excluded events | Total
Number of calls received | 90625 | 94756
Number of calls answered within 30 seconds | 69126 | 70168
Percentage of calls answered within 30 seconds | 76.28% | 74.05%
Table 2: New connections
Note: This is for newly energised properties only
Total
Number of new connections | 14638
Number of new connections not provided on or before the agreed date | 5
Percentage of new connections not provided on or before the agreed date | 0.03416%
Table 3: Streetlight repair
Total
Total number of streetlights | 159229
Total number of streetlight faults | 6047
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | 1676
Faulty streetlights not repaired within 5 business days of fault report or agreed date | 59
Percentage of faulty streetlights not repaired within 5 business days of fault report or agreed date | 0.9757%
Contents

## 1c. STPIS Daily Performance
Powercor Australia Ltd |  |  |  | 2014-01-01
STPIS Data Reporting |  |  |  | 2015-01-01
2014
Daily Performance Data
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1 Daily Performance Data (unplanned)
*Customer service information must be reported as per the definitions in the STPIS, that is excluding: • calls to payment lines and automated interactive services • calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned).
Customer service*
| CBD |  | Urban |  | Short rural |  | Long rural |  | Network
Date | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | MAIFI All events | MAIFI (after removing excluded events) | Number of calls received | Number of calls answered in 30 seconds
2014-01-01 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0095388 | 0.0095388 | 0.0025746 | 0.0025746 | 196 | 170
2014-01-02 | n/a | n/a | 0 | 0 | 0.0051375 | 0.0051375 | 0.038704 | 0.038704 | 0.012145 | 0.012145 | 192 | 192
2014-01-03 | n/a | n/a | 0.026736 | 0.026736 | 0 | 0 | 0.0058135 | 0.0058135 | 0.012248 | 0.012248 | 131 | 128
2014-01-04 | n/a | n/a | 0 | 0 | 0.014064 | 0.014064 | 0 | 0 | 0.0046504 | 0.0046504 | 128 | 115
2014-01-05 | n/a | n/a | 0.0009539 | 0.0009539 | 0.0088546 | 0.0088546 | 0.012274 | 0.012274 | 0.0066217 | 0.0066217 | 425 | 243
2014-01-06 | n/a | n/a | 0 | 0 | 0.0026728 | 0.0026728 | 0 | 0 | 0.00088377 | 0.00088377 | 214 | 198
2014-01-07 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0095388 | 0.0095388 | 0.0025746 | 0.0025746 | 188 | 181
2014-01-08 | n/a | n/a | 0 | 0 | 0.0014684 | 0.0014684 | 0.0067988 | 0.0067988 | 0.0023206 | 0.0023206 | 230 | 216
2014-01-09 | n/a | n/a | 0 | 0 | 0.00088426 | 0.00088426 | 0.005088 | 0.005088 | 0.0016657 | 0.0016657 | 190 | 183
2014-01-10 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 188
2014-01-11 | n/a | n/a | 0.0038686 | 0.0038686 | 0 | 0 | 0.019636 | 0.019636 | 0.0068452 | 0.0068452 | 111 | 104
2014-01-12 | n/a | n/a | 0 | 0 | 0.022455 | 0.022455 | 0 | 0 | 0.0074247 | 0.0074247 | 113 | 100
2014-01-13 | n/a | n/a | 0.013527 | 0.013527 | 0.013564 | 0.013564 | 0.017534 | 0.017534 | 0.014621 | 0.014621 | 355 | 221
2014-01-14 | n/a | n/a | 0 | 0 | 0.014168 | 0.014168 | 0.056174 | 0.056174 | 0.019846 | 0.019846 | 1484 | 305
2014-01-15 | n/a | n/a | 0.031532 | 0.031532 | 0.078011 | 0.078011 | 0.076722 | 0.076722 | 0.059097 | 0.059097 | 1760 | 959
2014-01-16 | n/a | n/a | 0.014511 | 0.014511 | 0.0011083 | 0.0011083 | 0.014191 | 0.014191 | 0.0099927 | 0.0099927 | 1480 | 855
2014-01-17 | n/a | n/a | 0 | 0 | 0.032626 | 0.032626 | 0.003745 | 0.003745 | 0.011799 | 0.011799 | 609 | 383
2014-01-18 | n/a | n/a | 0 | 0 | 0.0029369 | 0.0029369 | 0.0026715 | 0.0026715 | 0.0016921 | 0.0016921 | 273 | 128
2014-01-19 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0073281 | 0.0073281 | 0.0019779 | 0.0019779 | 193 | 163
2014-01-20 | n/a | n/a | 0 | 0 | 0.0048734 | 0.0048734 | 0.0065439 | 0.0065439 | 0.0033776 | 0.0033776 | 346 | 279
2014-01-21 | n/a | n/a | 0 | 0 | 0.0051255 | 0.0051255 | 0.011529 | 0.011529 | 0.0048065 | 0.0048065 | 257 | 238
2014-01-22 | n/a | n/a | 0 | 0 | 0 | 0 | 0.021931 | 0.021931 | 0.0059191 | 0.0059191 | 222 | 220
2014-01-23 | n/a | n/a | 0 | 0 | 0.018337 | 0.018337 | 0.017887 | 0.017887 | 0.010891 | 0.010891 | 204 | 193
2014-01-24 | n/a | n/a | 0.023029 | 0.023029 | 0.032698 | 0.032698 | 0.03641 | 0.03641 | 0.029838 | 0.029838 | 495 | 451
2014-01-25 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0044508 | 0.0044508 | 0.0012013 | 0.0012013 | 189 | 183
2014-01-26 | n/a | n/a | 0.0077438 | 0.0077438 | 0.0038451 | 0.0038451 | 0.0076173 | 0.0076173 | 0.0064206 | 0.0064206 | 69 | 69
2014-01-27 | n/a | n/a | 0.011265 | 0.011265 | 0 | 0 | 0.015166 | 0.015166 | 0.0085929 | 0.0085929 | 189 | 161
2014-01-28 | n/a | n/a | 0 | 0 | 0.011627 | 0.011627 | 0.0037646 | 0.0037646 | 0.0048607 | 0.0048607 | 812 | 412
2014-01-29 | n/a | n/a | 0 | 0 | 0 | 0 | 0.011818 | 0.011818 | 0.0031898 | 0.0031898 | 311 | 270
2014-01-30 | n/a | n/a | 0 | 0 | 0.016393 | 0.016393 | 0.00018627 | 0.00018627 | 0.0054706 | 0.0054706 | 276 | 261
2014-01-31 | n/a | n/a | 0 | 0 | 0 | 0 | 0.018004 | 0.018004 | 0.0048594 | 0.0048594 | 396 | 352
2014-02-01 | n/a | n/a | 0 | 0 | 0.012988 | 0.012988 | 0.015338 | 0.015338 | 0.0084342 | 0.0084342 | 201 | 154
2014-02-02 | n/a | n/a | 0.013298 | 0.013298 | 0 | 0 | 0 | 0 | 0.0053119 | 0.0053119 | 296 | 97
2014-02-03 | n/a | n/a | 0.0077869 | 0.0077869 | 0.032658 | 0.032658 | 0.080904 | 0.080904 | 0.035745 | 0.035745 | 777 | 471
2014-02-04 | n/a | n/a | 0.017518 | 0.017518 | 0 | 0 | 0.0099065 | 0.0099065 | 0.0096712 | 0.0096712 | 911 | 390
2014-02-05 | n/a | n/a | 0 | 0 | 0 | 0 | 0.02772 | 0.02772 | 0.0074816 | 0.0074816 | 247 | 166
2014-02-06 | n/a | n/a | 0.0090157 | 0.0090157 | 0.0054416 | 0.0054416 | 0 | 0 | 0.0054005 | 0.0054005 | 290 | 215
2014-02-07 | n/a | n/a | 0.0090157 | 0.0090157 | 0.0054456 | 0.0054456 | 0 | 0 | 0.0054018 | 0.0054018 | 370 | 284
2014-02-08 | n/a | n/a | 0 | 0 | 0.023747 | 0.023747 | 0.020833 | 0.020833 | 0.013475 | 0.013475 | 354 | 200
2014-02-09 | n/a | n/a | 0 | 0 | 0.028857 | 0.028857 | 0.044738 | 0.044738 | 0.021617 | 0.021617 | 344 | 277
2014-02-10 | n/a | n/a | 0 | 0 | 0 | 0 | 0.013098 | 0.013098 | 0.0035351 | 0.0035351 | 522 | 447
2014-02-11 | n/a | n/a | 0 | 0 | 0 | 0 | 0.013867 | 0.013867 | 0.0037428 | 0.0037428 | 499 | 356
2014-02-12 | n/a | n/a | 0 | 0 | 0.029033 | 0.029033 | 0.0097594 | 0.0097594 | 0.012234 | 0.012234 | 430 | 303
2014-02-13 | n/a | n/a | 0.014474 | 0.014474 | 0.0036171 | 0.0036171 | 0.032798 | 0.032798 | 0.01583 | 0.01583 | 393 | 239
2014-02-14 | n/a | n/a | 0 | 0 | 0.022467 | 0.022467 | 0.022342 | 0.022342 | 0.013459 | 0.013459 | 334 | 219
2014-02-15 | n/a | n/a | 0.0017124 | 0.0017124 | 0.0026928 | 0.0026928 | 0.05915 | 0.05915 | 0.017539 | 0.017539 | 786 | 358
2014-02-16 | n/a | n/a | 0.029293 | 0.029293 | 0.0019366 | 0.0019366 | 0.0055341 | 0.0055341 | 0.013835 | 0.013835 | 1853 | 683
2014-02-17 | n/a | n/a | 0.0047066 | 0.0047066 | 0 | 0 | 0.0053233 | 0.0053233 | 0.0033168 | 0.0033168 | 466 | 376
2014-02-18 | n/a | n/a | 0 | 0 | 0.045666 | 0.045666 | 0.05215 | 0.05215 | 0.029175 | 0.029175 | 227 | 224
2014-02-19 | n/a | n/a | 0 | 0 | 0.056333 | 0.056333 | 0.045792 | 0.045792 | 0.030986 | 0.030986 | 538 | 291
2014-02-20 | n/a | n/a | 0.0020436 | 0.0020436 | 0.0012324 | 0.0012324 | 0.0065292 | 0.0065292 | 0.002986 | 0.002986 | 666 | 520
2014-02-21 | n/a | n/a | 0 | 0 | 0.015913 | 0.015913 | 0.00014705 | 0.00014705 | 0.0053013 | 0.0053013 | 226 | 213
2014-02-22 | n/a | n/a | 0.0095423 | 0.0095423 | 0.0087506 | 0.0087506 | 0.0032303 | 0.0032303 | 0.0075769 | 0.0075769 | 122 | 106
2014-02-23 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 85
2014-02-24 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00023038 | 0.00023038 | 6.2181e-05 | 6.2181e-05 | 252 | 243
2014-02-25 | n/a | n/a | 0 | 0 | 0.0016885 | 0.0016885 | 0.041518 | 0.041518 | 0.011764 | 0.011764 | 375 | 297
2014-02-26 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 225
2014-02-27 | n/a | n/a | 0 | 0 | 0.029881 | 0.029881 | 0.0067742 | 0.0067742 | 0.011709 | 0.011709 | 230 | 227
2014-02-28 | n/a | n/a | 0.0037792 | 0.0037792 | 0.030033 | 0.030033 | 0.034165 | 0.034165 | 0.020661 | 0.020661 | 244 | 238
2014-03-01 | n/a | n/a | 0 | 0 | 0.0077823 | 0.0077823 | 0.0029558 | 0.0029558 | 0.003371 | 0.003371 | 242 | 210
2014-03-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0052743 | 0.0052743 | 0.0014236 | 0.0014236 | 104 | 88
2014-03-03 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 218
2014-03-04 | n/a | n/a | 0.00020867 | 0.00020867 | 0.014436 | 0.014436 | 0.082399 | 0.082399 | 0.027097 | 0.027097 | 294 | 269
2014-03-05 | n/a | n/a | 0 | 0 | 0 | 0 | 8.8232e-05 | 8.8232e-05 | 2.3814e-05 | 2.3814e-05 | 282 | 269
2014-03-06 | n/a | n/a | 0.0086911 | 0.0086911 | 0.0028929 | 0.0028929 | 0.026381 | 0.026381 | 0.011549 | 0.011549 | 203 | 190
2014-03-07 | n/a | n/a | 0 | 0 | 0.013024 | 0.013024 | 0.001147 | 0.001147 | 0.004616 | 0.004616 | 372 | 300
2014-03-08 | n/a | n/a | 0 | 0 | 0 | 0 | 0.011509 | 0.011509 | 0.0031064 | 0.0031064 | 358 | 261
2014-03-09 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0038038 | 0.0038038 | 0.0010267 | 0.0010267 | 130 | 120
2014-03-10 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0060929 | 0.0060929 | 0.0016445 | 0.0016445 | 118 | 115
2014-03-11 | n/a | n/a | 0 | 0 | 0.03509 | 0.03509 | 0.024009 | 0.024009 | 0.018083 | 0.018083 | 284 | 240
2014-03-12 | n/a | n/a | 0.0049086 | 0.0049086 | 0.01422 | 0.01422 | 0.012617 | 0.012617 | 0.010068 | 0.010068 | 332 | 299
2014-03-13 | n/a | n/a | 0 | 0 | 0.02568 | 0.02568 | 0.0032499 | 0.0032499 | 0.0093682 | 0.0093682 | 210 | 186
2014-03-14 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0097006 | 0.0097006 | 0.0026182 | 0.0026182 | 163 | 156
2014-03-15 | n/a | n/a | 0.042054 | 0.042054 | 0.064747 | 0.064747 | 0.19785 | 0.19785 | 0.091609 | 0.091609 | 1049 | 460
2014-03-16 | n/a | n/a | 0 | 0 | 0.0049575 | 0.0049575 | 0 | 0 | 0.0016392 | 0.0016392 | 277 | 225
2014-03-17 | n/a | n/a | 0.0052663 | 0.0052663 | 0.0087346 | 0.0087346 | 0 | 0 | 0.0049917 | 0.0049917 | 348 | 285
2014-03-18 | n/a | n/a | 5.2994e-05 | 5.2994e-05 | 0 | 0 | 0.0070242 | 0.0070242 | 0.001917 | 0.001917 | 185 | 182
2014-03-19 | n/a | n/a | 0 | 0 | 0.0086666 | 0.0086666 | 0 | 0 | 0.0028656 | 0.0028656 | 167 | 162
2014-03-20 | n/a | n/a | 0 | 0 | 0.0013884 | 0.0013884 | 0.024798 | 0.024798 | 0.0071522 | 0.0071522 | 286 | 253
2014-03-21 | n/a | n/a | 0.0013149 | 0.0013149 | 0.0086626 | 0.0086626 | 0.025499 | 0.025499 | 0.010272 | 0.010272 | 318 | 285
2014-03-22 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 84
2014-03-23 | n/a | n/a | 0 | 0 | 0.00052816 | 0.00052816 | 0.020573 | 0.020573 | 0.0057273 | 0.0057273 | 128 | 106
2014-03-24 | n/a | n/a | 0.0027425 | 0.0027425 | 0 | 0 | 0.019754 | 0.019754 | 0.0064272 | 0.0064272 | 171 | 162
2014-03-25 | n/a | n/a | 0.0027524 | 0.0027524 | 0.050263 | 0.050263 | 0.024558 | 0.024558 | 0.024347 | 0.024347 | 200 | 172
2014-03-26 | n/a | n/a | 0.0083102 | 0.0083102 | 0.0081624 | 0.0081624 | 0.020685 | 0.020685 | 0.011601 | 0.011601 | 385 | 250
2014-03-27 | n/a | n/a | 0.032558 | 0.032558 | 0.012092 | 0.012092 | 0.0071958 | 0.0071958 | 0.018945 | 0.018945 | 366 | 295
2014-03-28 | n/a | n/a | 0 | 0 | 0.0011283 | 0.0011283 | 0.0038038 | 0.0038038 | 0.0013997 | 0.0013997 | 231 | 213
2014-03-29 | n/a | n/a | 0 | 0 | 0.023651 | 0.023651 | 0.041337 | 0.041337 | 0.018977 | 0.018977 | 128 | 126
2014-03-30 | n/a | n/a | 0 | 0 | 0.014692 | 0.014692 | 0.033778 | 0.033778 | 0.013975 | 0.013975 | 117 | 113
2014-03-31 | n/a | n/a | 0 | 0 | 0 | 0 | 0.020117 | 0.020117 | 0.0054296 | 0.0054296 | 233 | 212
2014-04-01 | n/a | n/a | 0 | 0 | 0.011199 | 0.011199 | 0.013098 | 0.013098 | 0.0072382 | 0.0072382 | 229 | 206
2014-04-02 | n/a | n/a | 0 | 0 | 0.0080304 | 0.0080304 | 0.0010539 | 0.0010539 | 0.0029397 | 0.0029397 | 206 | 196
2014-04-03 | n/a | n/a | 0 | 0 | 0 | 0 | 0.032195 | 0.032195 | 0.0086895 | 0.0086895 | 161 | 154
2014-04-04 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0033773 | 0.0033773 | 0.00091155 | 0.00091155 | 183 | 164
2014-04-05 | n/a | n/a | 0 | 0 | 0 | 0 | 0.021705 | 0.021705 | 0.0058583 | 0.0058583 | 95 | 95
2014-04-06 | n/a | n/a | 0.0058426 | 0.0058426 | 0 | 0 | 0.0024019 | 0.0024019 | 0.0029821 | 0.0029821 | 88 | 79
2014-04-07 | n/a | n/a | 0.01244 | 0.01244 | 0 | 0 | 0.016798 | 0.016798 | 0.0095032 | 0.0095032 | 206 | 196
2014-04-08 | n/a | n/a | 0.0037262 | 0.0037262 | 0 | 0 | 0.024391 | 0.024391 | 0.0080717 | 0.0080717 | 353 | 269
2014-04-09 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0090242 | 0.0090242 | 0.0024357 | 0.0024357 | 270 | 213
2014-04-10 | n/a | n/a | 0.00020867 | 0.00020867 | 0.025776 | 0.025776 | 0.00025489 | 0.00025489 | 0.008675 | 0.008675 | 373 | 307
2014-04-11 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 213
2014-04-12 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0013627 | 0.0013627 | 0.0003678 | 0.0003678 | 124 | 110
2014-04-13 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0037989 | 0.0037989 | 0.0010253 | 0.0010253 | 103 | 91
2014-04-14 | n/a | n/a | 0 | 0 | 0 | 0 | 0.010054 | 0.010054 | 0.0027135 | 0.0027135 | 151 | 123
2014-04-15 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0019999 | 0.0019999 | 0.00053979 | 0.00053979 | 177 | 160
2014-04-16 | n/a | n/a | 0 | 0 | 0 | 0 | 0.017014 | 0.017014 | 0.0045922 | 0.0045922 | 232 | 183
2014-04-17 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0031714 | 0.0031714 | 0.00085599 | 0.00085599 | 164 | 145
2014-04-18 | n/a | n/a | 0 | 0 | 0.028504 | 0.028504 | 0.00030881 | 0.00030881 | 0.0095085 | 0.0095085 | 121 | 116
2014-04-19 | n/a | n/a | 0.014938 | 0.014938 | 0 | 0 | 0.023926 | 0.023926 | 0.012424 | 0.012424 | 136 | 126
2014-04-20 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0026617 | 0.0026617 | 0.00071839 | 0.00071839 | 68 | 66
2014-04-21 | n/a | n/a | 0.012146 | 0.012146 | 0.0096309 | 0.0096309 | 0 | 0 | 0.008036 | 0.008036 | 202 | 101
2014-04-22 | n/a | n/a | 0.00023185 | 0.00023185 | 0.027112 | 0.027112 | 0.020362 | 0.020362 | 0.014553 | 0.014553 | 331 | 272
2014-04-23 | n/a | n/a | 0 | 0 | 0.0077783 | 0.0077783 | 0.00050978 | 0.00050978 | 0.0027095 | 0.0027095 | 237 | 178
2014-04-24 | n/a | n/a | 0 | 0 | 0.00085225 | 0.00085225 | 0.026337 | 0.026337 | 0.0073903 | 0.0073903 | 443 | 309
2014-04-25 | n/a | n/a | 0 | 0 | 0.0026048 | 0.0026048 | 0 | 0 | 0.00086128 | 0.00086128 | 93 | 91
2014-04-26 | n/a | n/a | 0.0075484 | 0.0075484 | 0.0026928 | 0.0026928 | 0.033111 | 0.033111 | 0.012842 | 0.012842 | 123 | 116
2014-04-27 | n/a | n/a | 0 | 0 | 0.012244 | 0.012244 | 0.010318 | 0.010318 | 0.0068333 | 0.0068333 | 69 | 68
2014-04-28 | n/a | n/a | 0 | 0 | 0.012116 | 0.012116 | 0 | 0 | 0.0040061 | 0.0040061 | 222 | 215
2014-04-29 | n/a | n/a | 0 | 0 | 0.0026928 | 0.0026928 | 0 | 0 | 0.00089038 | 0.00089038 | 328 | 242
2014-04-30 | n/a | n/a | 0.0032327 | 0.0032327 | 0.010111 | 0.010111 | 0 | 0 | 0.0046345 | 0.0046345 | 299 | 228
2014-05-01 | n/a | n/a | 0 | 0 | 0.0003481 | 0.0003481 | 0 | 0 | 0.0001151 | 0.0001151 | 256 | 196
2014-05-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0063282 | 0.0063282 | 0.001708 | 0.001708 | 256 | 178
2014-05-03 | n/a | n/a | 0 | 0 | 0 | 0 | 0.033616 | 0.033616 | 0.0090732 | 0.0090732 | 146 | 136
2014-05-04 | n/a | n/a | 0 | 0 | 0.003237 | 0.003237 | 0 | 0 | 0.0010703 | 0.0010703 | 121 | 103
2014-05-05 | n/a | n/a | 0 | 0 | 0.0082264 | 0.0082264 | 0 | 0 | 0.0027201 | 0.0027201 | 337 | 288
2014-05-06 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 157
2014-05-07 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 200
2014-05-08 | n/a | n/a | 0 | 0 | 0.027136 | 0.027136 | 0.042582 | 0.042582 | 0.020466 | 0.020466 | 268 | 177
2014-05-09 | n/a | n/a | 0 | 0 | 0.00050815 | 0.00050815 | 0.00374 | 0.00374 | 0.0011775 | 0.0011775 | 213 | 145
2014-05-10 | n/a | n/a | 0 | 0 | 0.018541 | 0.018541 | 0.0067791 | 0.0067791 | 0.0079605 | 0.0079605 | 106 | 67
2014-05-11 | n/a | n/a | 0 | 0 | 0.018425 | 0.018425 | 0.0063282 | 0.0063282 | 0.0078005 | 0.0078005 | 78 | 69
2014-05-12 | n/a | n/a | 0 | 0 | 0.014892 | 0.014892 | 0.0040047 | 0.0040047 | 0.0060051 | 0.0060051 | 231 | 172
2014-05-13 | n/a | n/a | 0 | 0 | 0.00050815 | 0.00050815 | 0.0019068 | 0.0019068 | 0.00068267 | 0.00068267 | 197 | 183
2014-05-14 | n/a | n/a | 0 | 0 | 0.0096188 | 0.0096188 | 0 | 0 | 0.0031805 | 0.0031805 | 173 | 155
2014-05-15 | n/a | n/a | 0 | 0 | 0 | 0 | 0.01047 | 0.01047 | 0.0028259 | 0.0028259 | 185 | 111
2014-05-16 | n/a | n/a | 0.022648 | 0.022648 | 0 | 0 | 0 | 0 | 0.0090467 | 0.0090467 | 164 | 133
2014-05-17 | n/a | n/a | 0 | 0 | 0.015601 | 0.015601 | 0.013941 | 0.013941 | 0.008921 | 0.008921 | 116 | 104
2014-05-18 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0042547 | 0.0042547 | 0.0011484 | 0.0011484 | 80 | 69
2014-05-19 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 160
2014-05-20 | n/a | n/a | 0 | 0 | 0.00012404 | 0.00012404 | 0.0075046 | 0.0075046 | 0.0020665 | 0.0020665 | 253 | 215
2014-05-21 | n/a | n/a | 0.00011261 | 0.00011261 | 0.0051055 | 0.0051055 | 0.0035979 | 0.0035979 | 0.0027042 | 0.0027042 | 202 | 160
2014-05-22 | n/a | n/a | 0 | 0 | 0.0038852 | 0.0038852 | 0.006637 | 0.006637 | 0.003076 | 0.003076 | 208 | 187
2014-05-23 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00014705 | 0.00014705 | 3.969e-05 | 3.969e-05 | 295 | 215
2014-05-24 | n/a | n/a | 0.012026 | 0.012026 | 0 | 0 | 0 | 0 | 0.0048038 | 0.0048038 | 96 | 86
2014-05-25 | n/a | n/a | 0 | 0 | 0.0049215 | 0.0049215 | 0.016896 | 0.016896 | 0.0061877 | 0.0061877 | 92 | 75
2014-05-26 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 192
2014-05-27 | n/a | n/a | 0.0063494 | 0.0063494 | 0.068288 | 0.068288 | 0.070782 | 0.070782 | 0.04422 | 0.04422 | 574 | 312
2014-05-28 | n/a | n/a | 0.019578 | 0.019578 | 0 | 0 | 0.0028332 | 0.0028332 | 0.008585 | 0.008585 | 283 | 222
2014-05-29 | n/a | n/a | 0 | 0 | 8.4025e-05 | 8.4025e-05 | 0.00024509 | 0.00024509 | 9.3934e-05 | 9.3934e-05 | 203 | 148
2014-05-30 | n/a | n/a | 0 | 0 | 0.0061618 | 0.0061618 | 0.00012254 | 0.00012254 | 0.0020705 | 0.0020705 | 193 | 136
2014-05-31 | n/a | n/a | 0.0025007 | 0.0025007 | 0.012008 | 0.012008 | 0.0096124 | 0.0096124 | 0.0075636 | 0.0075636 | 160 | 114
2014-06-01 | n/a | n/a | 0 | 0 | 0.0011283 | 0.0011283 | 0.0086859 | 0.0086859 | 0.0027175 | 0.0027175 | 137 | 117
2014-06-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0.011799 | 0.011799 | 0.0031845 | 0.0031845 | 234 | 162
2014-06-03 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0037891 | 0.0037891 | 0.0010227 | 0.0010227 | 311 | 191
2014-06-04 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00010294 | 0.00010294 | 2.7783e-05 | 2.7783e-05 | 280 | 219
2014-06-05 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0043234 | 0.0043234 | 0.0011669 | 0.0011669 | 192 | 152
2014-06-06 | n/a | n/a | 0 | 0 | 0 | 0 | 0.020411 | 0.020411 | 0.005509 | 0.005509 | 173 | 138
2014-06-07 | n/a | n/a | 0 | 0 | 0.0097749 | 0.0097749 | 0.016205 | 0.016205 | 0.007606 | 0.007606 | 132 | 113
2014-06-08 | n/a | n/a | 0 | 0 | 0.0006882 | 0.0006882 | 0.012475 | 0.012475 | 0.0035946 | 0.0035946 | 89 | 78
2014-06-09 | n/a | n/a | 0 | 0 | 0.012128 | 0.012128 | 0 | 0 | 0.00401 | 0.00401 | 96 | 93
2014-06-10 | n/a | n/a | 0 | 0 | 0.00015205 | 0.00015205 | 0 | 0 | 5.0274e-05 | 5.0274e-05 | 187 | 158
2014-06-11 | n/a | n/a | 0.013043 | 0.013043 | 0 | 0 | 0.018024 | 0.018024 | 0.010075 | 0.010075 | 195 | 166
2014-06-12 | n/a | n/a | 0.0061374 | 0.0061374 | 0 | 0 | 0.012196 | 0.012196 | 0.0057432 | 0.0057432 | 241 | 181
2014-06-13 | n/a | n/a | 0 | 0 | 0.0013644 | 0.0013644 | 0 | 0 | 0.00045115 | 0.00045115 | 266 | 211
2014-06-14 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 136
2014-06-15 | n/a | n/a | 0 | 0 | 0.0014564 | 0.0014564 | 0.0031322 | 0.0031322 | 0.001327 | 0.001327 | 79 | 74
2014-06-16 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0099555 | 0.0099555 | 0.002687 | 0.002687 | 170 | 148
2014-06-17 | n/a | n/a | 0.0079293 | 0.0079293 | 0.00010403 | 0.00010403 | 0.011911 | 0.011911 | 0.0064166 | 0.0064166 | 180 | 140
2014-06-18 | n/a | n/a | 3.6434e-05 | 3.6434e-05 | 0 | 0 | 0.032964 | 0.032964 | 0.0089118 | 0.0089118 | 165 | 139
2014-06-19 | n/a | n/a | 0 | 0 | 0.00076023 | 0.00076023 | 0 | 0 | 0.00025137 | 0.00025137 | 300 | 190
2014-06-20 | n/a | n/a | 0 | 0 | 0.00050815 | 0.00050815 | 0.0055194 | 0.0055194 | 0.0016577 | 0.0016577 | 276 | 142
2014-06-21 | n/a | n/a | 0 | 0 | 0.0022007 | 0.0022007 | 0.0027989 | 0.0027989 | 0.0014831 | 0.0014831 | 92 | 61
2014-06-22 | n/a | n/a | 0 | 0 | 0 | 0 | 0.021695 | 0.021695 | 0.0058556 | 0.0058556 | 151 | 98
2014-06-23 | n/a | n/a | 0 | 0 | 0.0012484 | 0.0012484 | 0.01099 | 0.01099 | 0.003379 | 0.003379 | 391 | 96
2014-06-24 | n/a | n/a | 0.065945 | 0.065945 | 0.1023 | 0.1023 | 0.11704 | 0.11704 | 0.091757 | 0.091757 | 2278 | 359
2014-06-25 | n/a | n/a | 0.00036102 | 0.00036102 | 0.0031889 | 0.0031889 | 0.016176 | 0.016176 | 0.0055646 | 0.0055646 | 529 | 254
2014-06-26 | n/a | n/a | 0 | 0 | 0.015697 | 0.015697 | 0.0044508 | 0.0044508 | 0.0063915 | 0.0063915 | 315 | 228
2014-06-27 | n/a | n/a | 0 | 0 | 0.0082064 | 0.0082064 | 0.00024999 | 0.00024999 | 0.002781 | 0.002781 | 338 | 113
2014-06-28 | n/a | n/a | 0 | 0 | 0.0042653 | 0.0042653 | 0.014269 | 0.014269 | 0.0052616 | 0.0052616 | 173 | 121
2014-06-29 | n/a | n/a | 0 | 0 | 0.014116 | 0.014116 | 0.0013529 | 0.0013529 | 0.0050327 | 0.0050327 | 185 | 145
2014-06-30 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0040538 | 0.0040538 | 0.0010941 | 0.0010941 | 285 | 158
2014-07-01 | n/a | n/a | 0 | 0 | 0.0029609 | 0.0029609 | 0.0050145 | 0.0050145 | 0.0023325 | 0.0023325 | 302 | 133
2014-07-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 143
2014-07-03 | n/a | n/a | 0 | 0 | 0.00084825 | 0.00084825 | 0 | 0 | 0.00028048 | 0.00028048 | 199 | 157
2014-07-04 | n/a | n/a | 0 | 0 | 0.0040092 | 0.0040092 | 0.010779 | 0.010779 | 0.004235 | 0.004235 | 239 | 177
2014-07-05 | n/a | n/a | 0 | 0 | 0.0026008 | 0.0026008 | 0 | 0 | 0.00085996 | 0.00085996 | 140 | 114
2014-07-06 | n/a | n/a | 0.0080253 | 0.0080253 | 0.024999 | 0.024999 | 0 | 0 | 0.011472 | 0.011472 | 99 | 71
2014-07-07 | n/a | n/a | 0.00020867 | 0.00020867 | 0.011647 | 0.011647 | 0.012323 | 0.012323 | 0.0072607 | 0.0072607 | 238 | 208
2014-07-08 | n/a | n/a | 0 | 0 | 0.027448 | 0.027448 | 0.024911 | 0.024911 | 0.015799 | 0.015799 | 225 | 182
2014-07-09 | n/a | n/a | 0 | 0 | 0.0026128 | 0.0026128 | 0.0029411 | 0.0029411 | 0.0016577 | 0.0016577 | 257 | 193
2014-07-10 | n/a | n/a | 0 | 0 | 0.00070421 | 0.00070421 | 0.01047 | 0.01047 | 0.0030588 | 0.0030588 | 287 | 217
2014-07-11 | n/a | n/a | 0 | 0 | 0.013968 | 0.013968 | 0.006936 | 0.006936 | 0.0064907 | 0.0064907 | 251 | 164
2014-07-12 | n/a | n/a | 1.6561e-05 | 1.6561e-05 | 0.0011603 | 0.0011603 | 0.0026519 | 0.0026519 | 0.001106 | 0.001106 | 153 | 91
2014-07-13 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0021029 | 0.0021029 | 0.00056757 | 0.00056757 | 150 | 117
2014-07-14 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0011715 | 0.0011715 | 0.0003162 | 0.0003162 | 433 | 214
2014-07-15 | n/a | n/a | 0 | 0 | 0.0070941 | 0.0070941 | 0 | 0 | 0.0023457 | 0.0023457 | 182 | 145
2014-07-16 | n/a | n/a | 0 | 0 | 0.013776 | 0.013776 | 0.0040293 | 0.0040293 | 0.0056426 | 0.0056426 | 240 | 170
2014-07-17 | n/a | n/a | 0.020376 | 0.020376 | 0.029789 | 0.029789 | 0.022386 | 0.022386 | 0.024031 | 0.024031 | 241 | 160
2014-07-18 | n/a | n/a | 0 | 0 | 0.0011203 | 0.0011203 | 0.007387 | 0.007387 | 0.0023642 | 0.0023642 | 210 | 175
2014-07-19 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00030881 | 0.00030881 | 8.335e-05 | 8.335e-05 | 113 | 99
2014-07-20 | n/a | n/a | 0.00061275 | 0.00061275 | 0 | 0 | 0.0092594 | 0.0092594 | 0.0027439 | 0.0027439 | 99 | 86
2014-07-21 | n/a | n/a | 0 | 0 | 0.0082304 | 0.0082304 | 0.01224 | 0.01224 | 0.006025 | 0.006025 | 273 | 183
2014-07-22 | n/a | n/a | 0.0070516 | 0.0070516 | 0 | 0 | 0.0095339 | 0.0095339 | 0.0053899 | 0.0053899 | 242 | 206
2014-07-23 | n/a | n/a | 0 | 0 | 0.014936 | 0.014936 | 0.0092889 | 0.0092889 | 0.0074459 | 0.0074459 | 200 | 169
2014-07-24 | n/a | n/a | 0 | 0 | 0.0013644 | 0.0013644 | 0.032979 | 0.032979 | 0.0093523 | 0.0093523 | 219 | 172
2014-07-25 | n/a | n/a | 0 | 0 | 0.003357 | 0.003357 | 0.0015343 | 0.0015343 | 0.0015241 | 0.0015241 | 172 | 160
2014-07-26 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 72
2014-07-27 | n/a | n/a | 0 | 0 | 0.0026808 | 0.0026808 | 0.010544 | 0.010544 | 0.0037322 | 0.0037322 | 118 | 77
2014-07-28 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 285
2014-07-29 | n/a | n/a | 0.0037427 | 0.0037427 | 0 | 0 | 0.0013088 | 0.0013088 | 0.0018482 | 0.0018482 | 205 | 170
2014-07-30 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0011519 | 0.0011519 | 0.00031091 | 0.00031091 | 194 | 182
2014-07-31 | n/a | n/a | 0.006197 | 0.006197 | 0.039832 | 0.039832 | 0.038709 | 0.038709 | 0.026094 | 0.026094 | 748 | 465
2014-08-01 | n/a | n/a | 0 | 0 | 0.0086025 | 0.0086025 | 0.0057204 | 0.0057204 | 0.0043884 | 0.0043884 | 388 | 178
2014-08-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 122
2014-08-03 | n/a | n/a | 0 | 0 | 0 | 0 | 0.011573 | 0.011573 | 0.0031236 | 0.0031236 | 106 | 99
2014-08-04 | n/a | n/a | 0 | 0 | 0.0014604 | 0.0014604 | 0 | 0 | 0.0004829 | 0.0004829 | 285 | 199
2014-08-05 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0048282 | 0.0048282 | 0.0013032 | 0.0013032 | 243 | 215
2014-08-06 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0035979 | 0.0035979 | 0.00097109 | 0.00097109 | 204 | 185
2014-08-07 | n/a | n/a | 0.0017919 | 0.0017919 | 0.0075702 | 0.0075702 | 0 | 0 | 0.0032189 | 0.0032189 | 284 | 242
2014-08-08 | n/a | n/a | 0 | 0 | 0 | 0 | 0.016352 | 0.016352 | 0.0044136 | 0.0044136 | 219 | 182
2014-08-09 | n/a | n/a | 0.0067502 | 0.0067502 | 0 | 0 | 0.0037842 | 0.0037842 | 0.0037177 | 0.0037177 | 98 | 85
2014-08-10 | n/a | n/a | 0 | 0 | 0.0014764 | 0.0014764 | 0.016558 | 0.016558 | 0.0049573 | 0.0049573 | 179 | 139
2014-08-11 | n/a | n/a | 0.0096218 | 0.0096218 | 0.0040492 | 0.0040492 | 0.0042596 | 0.0042596 | 0.0063319 | 0.0063319 | 334 | 270
2014-08-12 | n/a | n/a | 0 | 0 | 0.0028328 | 0.0028328 | 0.035891 | 0.035891 | 0.010624 | 0.010624 | 309 | 240
2014-08-13 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0070487 | 0.0070487 | 0.0019025 | 0.0019025 | 273 | 255
2014-08-14 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0015195 | 0.0015195 | 0.00041013 | 0.00041013 | 160 | 148
2014-08-15 | n/a | n/a | 0.016004 | 0.016004 | 0.016421 | 0.016421 | 0.00022058 | 0.00022058 | 0.011882 | 0.011882 | 192 | 173
2014-08-16 | n/a | n/a | 0 | 0 | 0.0011844 | 0.0011844 | 0.00033822 | 0.00033822 | 0.0004829 | 0.0004829 | 115 | 107
2014-08-17 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0034803 | 0.0034803 | 0.00093934 | 0.00093934 | 91 | 76
2014-08-18 | n/a | n/a | 0 | 0 | 0 | 0 | 0.001745 | 0.001745 | 0.00047099 | 0.00047099 | 216 | 197
2014-08-19 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0028479 | 0.0028479 | 0.00076867 | 0.00076867 | 185 | 162
2014-08-20 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0042596 | 0.0042596 | 0.0011497 | 0.0011497 | 206 | 186
2014-08-21 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00014705 | 0.00014705 | 3.969e-05 | 3.969e-05 | 125 | 109
2014-08-22 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0024607 | 0.0024607 | 0.00066415 | 0.00066415 | 123 | 91
2014-08-23 | n/a | n/a | 0 | 0 | 0.013908 | 0.013908 | 0.029156 | 0.029156 | 0.012468 | 0.012468 | 153 | 128
2014-08-24 | n/a | n/a | 0.0068164 | 0.0068164 | 0 | 0 | 0.0037253 | 0.0037253 | 0.0037282 | 0.0037282 | 94 | 80
2014-08-25 | n/a | n/a | 0.026355 | 0.026355 | 0.016553 | 0.016553 | 0.026641 | 0.026641 | 0.023191 | 0.023191 | 192 | 183
2014-08-26 | n/a | n/a | 0 | 0 | 0 | 0 | 0.020636 | 0.020636 | 0.0055699 | 0.0055699 | 191 | 178
2014-08-27 | n/a | n/a | 0 | 0 | 0.010823 | 0.010823 | 0.0057253 | 0.0057253 | 0.005124 | 0.005124 | 300 | 240
2014-08-28 | n/a | n/a | 0 | 0 | 0 | 0 | 0.030945 | 0.030945 | 0.0083522 | 0.0083522 | 195 | 174
2014-08-29 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0011323 | 0.0011323 | 0.00030561 | 0.00030561 | 151 | 135
2014-08-30 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 101
2014-08-31 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 75
2014-09-01 | n/a | n/a | 0 | 0 | 0.012336 | 0.012336 | 0.0072791 | 0.0072791 | 0.0060435 | 0.0060435 | 225 | 176
2014-09-02 | n/a | n/a | 0 | 0 | 0.00064419 | 0.00064419 | 0.00040685 | 0.00040685 | 0.00032281 | 0.00032281 | 160 | 151
2014-09-03 | n/a | n/a | 0.00053657 | 0.00053657 | 0.0022607 | 0.0022607 | 0.00092153 | 0.00092153 | 0.0012106 | 0.0012106 | 164 | 139
2014-09-04 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0030146 | 0.0030146 | 0.00081365 | 0.00081365 | 182 | 174
2014-09-05 | n/a | n/a | 0.0075418 | 0.0075418 | 0.0086546 | 0.0086546 | 0 | 0 | 0.0058742 | 0.0058742 | 136 | 122
2014-09-06 | n/a | n/a | 0.01254 | 0.01254 | 0 | 0 | 0.014196 | 0.014196 | 0.0088403 | 0.0088403 | 84 | 84
2014-09-07 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 92
2014-09-08 | n/a | n/a | 0 | 0 | 0 | 0 | 0.020024 | 0.020024 | 0.0054045 | 0.0054045 | 291 | 248
2014-09-09 | n/a | n/a | 0.0023682 | 0.0023682 | 0.071241 | 0.071241 | 0.055782 | 0.055782 | 0.039558 | 0.039558 | 308 | 202
2014-09-10 | n/a | n/a | 0 | 0 | 0.0036051 | 0.0036051 | 0.011377 | 0.011377 | 0.0042627 | 0.0042627 | 195 | 176
2014-09-11 | n/a | n/a | 0.013997 | 0.013997 | 0 | 0 | 6.8625e-05 | 6.8625e-05 | 0.0056096 | 0.0056096 | 164 | 157
2014-09-12 | n/a | n/a | 0 | 0 | 0.00016405 | 0.00016405 | 0.0029509 | 0.0029509 | 0.00085069 | 0.00085069 | 195 | 145
2014-09-13 | n/a | n/a | 0 | 0 | 8.0024e-06 | 8.0024e-06 | 0.027136 | 0.027136 | 0.0073268 | 0.0073268 | 160 | 131
2014-09-14 | n/a | n/a | 0 | 0 | 0 | 0 | 0.015416 | 0.015416 | 0.0041609 | 0.0041609 | 55 | 52
2014-09-15 | n/a | n/a | 0 | 0 | 0.0082464 | 0.0082464 | 0.0059458 | 0.0059458 | 0.0043315 | 0.0043315 | 200 | 189
2014-09-16 | n/a | n/a | 0.011364 | 0.011364 | 0.016605 | 0.016605 | 0.00048037 | 0.00048037 | 0.010159 | 0.010159 | 176 | 145
2014-09-17 | n/a | n/a | 0 | 0 | 0.0043853 | 0.0043853 | 0.010259 | 0.010259 | 0.0042191 | 0.0042191 | 174 | 172
2014-09-18 | n/a | n/a | 0 | 0 | 0.00015605 | 0.00015605 | 0 | 0 | 5.1597e-05 | 5.1597e-05 | 170 | 160
2014-09-19 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00040685 | 0.00040685 | 0.00010981 | 0.00010981 | 152 | 136
2014-09-20 | n/a | n/a | 0 | 0 | 0.0092427 | 0.0092427 | 0.0028479 | 0.0028479 | 0.0038248 | 0.0038248 | 80 | 70
2014-09-21 | n/a | n/a | 0.014044 | 0.014044 | 0 | 0 | 0.0032646 | 0.0032646 | 0.0064907 | 0.0064907 | 47 | 44
2014-09-22 | n/a | n/a | 0 | 0 | 0 | 0 | 0.004044 | 0.004044 | 0.0010915 | 0.0010915 | 451 | 219
2014-09-23 | n/a | n/a | 0 | 0 | 0.011047 | 0.011047 | 0.00074997 | 0.00074997 | 0.0038552 | 0.0038552 | 190 | 169
2014-09-24 | n/a | n/a | 0 | 0 | 0.0050095 | 0.0050095 | 0.0027891 | 0.0027891 | 0.0024092 | 0.0024092 | 233 | 216
2014-09-25 | n/a | n/a | 0.0054187 | 0.0054187 | 0.017621 | 0.017621 | 0.0002892 | 0.0002892 | 0.008069 | 0.008069 | 233 | 198
2014-09-26 | n/a | n/a | 0 | 0 | 0.0022607 | 0.0022607 | 0.00010294 | 0.00010294 | 0.00077528 | 0.00077528 | 181 | 146
2014-09-27 | n/a | n/a | 0 | 0 | 0.014148 | 0.014148 | 0.039513 | 0.039513 | 0.015343 | 0.015343 | 112 | 88
2014-09-28 | n/a | n/a | 0.018618 | 0.018618 | 0.15392 | 0.15392 | 0.11415 | 0.11415 | 0.089142 | 0.089142 | 312 | 145
2014-09-29 | n/a | n/a | 0 | 0 | 0.0012244 | 0.0012244 | 0.0046714 | 0.0046714 | 0.0016657 | 0.0016657 | 184 | 182
2014-09-30 | n/a | n/a | 0.013735 | 0.013735 | 0.0069261 | 0.0069261 | 0.035744 | 0.035744 | 0.017424 | 0.017424 | 543 | 339
2014-10-01 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0066272 | 0.0066272 | 0.0017887 | 0.0017887 | 285 | 249
2014-10-02 | n/a | n/a | 0.0095787 | 0.0095787 | 0 | 0 | 0.01373 | 0.01373 | 0.0075319 | 0.0075319 | 203 | 188
2014-10-03 | n/a | n/a | 0.0095787 | 0.0095787 | 0 | 0 | 0.0032156 | 0.0032156 | 0.004694 | 0.004694 | 203 | 180
2014-10-04 | n/a | n/a | 0 | 0 | 0.0042293 | 0.0042293 | 0.0036126 | 0.0036126 | 0.0023735 | 0.0023735 | 111 | 93
2014-10-05 | n/a | n/a | 0 | 0 | 0.022107 | 0.022107 | 0.0021813 | 0.0021813 | 0.0078984 | 0.0078984 | 99 | 91
2014-10-06 | n/a | n/a | 0.003915 | 0.003915 | 0.039672 | 0.039672 | 0.029185 | 0.029185 | 0.022559 | 0.022559 | 307 | 193
2014-10-07 | n/a | n/a | 0.0093502 | 0.0093502 | 0.0029729 | 0.0029729 | 0.0018529 | 0.0018529 | 0.0052179 | 0.0052179 | 238 | 211
2014-10-08 | n/a | n/a | 0 | 0 | 0 | 0 | 0.053135 | 0.053135 | 0.014341 | 0.014341 | 225 | 200
2014-10-09 | n/a | n/a | 1.6561e-05 | 1.6561e-05 | 0.0039052 | 0.0039052 | 0.0041175 | 0.0041175 | 0.0024092 | 0.0024092 | 210 | 174
2014-10-10 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0014803 | 0.0014803 | 0.00039955 | 0.00039955 | 157 | 122
2014-10-11 | n/a | n/a | 0.012315 | 0.012315 | 0.0011643 | 0.0011643 | 0.0045586 | 0.0045586 | 0.0065343 | 0.0065343 | 89 | 89
2014-10-12 | n/a | n/a | 0 | 0 | 0.00051215 | 0.00051215 | 0.002245 | 0.002245 | 0.00077528 | 0.00077528 | 133 | 122
2014-10-13 | n/a | n/a | 0.011215 | 0.011215 | 0.015997 | 0.015997 | 0.019386 | 0.019386 | 0.015002 | 0.015002 | 362 | 275
2014-10-14 | n/a | n/a | 0.0048159 | 0.0048159 | 0 | 0 | 0.019911 | 0.019911 | 0.0072977 | 0.0072977 | 294 | 219
2014-10-15 | n/a | n/a | 0 | 0 | 0.018565 | 0.018565 | 0.021043 | 0.021043 | 0.011818 | 0.011818 | 227 | 199
2014-10-16 | n/a | n/a | 0.0027292 | 0.0027292 | 0.010667 | 0.010667 | 0.031474 | 0.031474 | 0.013112 | 0.013112 | 221 | 187
2014-10-17 | n/a | n/a | 0.02454 | 0.02454 | 0.0086666 | 0.0086666 | 0.055517 | 0.055517 | 0.027652 | 0.027652 | 178 | 164
2014-10-18 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0066419 | 0.0066419 | 0.0017927 | 0.0017927 | 117 | 113
2014-10-19 | n/a | n/a | 0.0096549 | 0.0096549 | 0.013716 | 0.013716 | 0.022131 | 0.022131 | 0.014365 | 0.014365 | 105 | 95
2014-10-20 | n/a | n/a | 0 | 0 | 0.026856 | 0.026856 | 0.00030881 | 0.00030881 | 0.0089634 | 0.0089634 | 176 | 149
2014-10-21 | n/a | n/a | 0.019976 | 0.019976 | 0.0072742 | 0.0072742 | 0.019597 | 0.019597 | 0.015674 | 0.015674 | 224 | 175
2014-10-22 | n/a | n/a | 0 | 0 | 0.0061458 | 0.0061458 | 0.0069311 | 0.0069311 | 0.0039029 | 0.0039029 | 329 | 247
2014-10-23 | n/a | n/a | 0 | 0 | 0.00041612 | 0.00041612 | 0.0013333 | 0.0013333 | 0.00049745 | 0.00049745 | 207 | 179
2014-10-24 | n/a | n/a | 0.0035705 | 0.0035705 | 0.0013924 | 0.0013924 | 0.028254 | 0.028254 | 0.0095124 | 0.0095124 | 214 | 194
2014-10-25 | n/a | n/a | 0 | 0 | 0.0060338 | 0.0060338 | 0.035254 | 0.035254 | 0.01151 | 0.01151 | 184 | 153
2014-10-26 | n/a | n/a | 0 | 0 | 0.0053936 | 0.0053936 | 0.10654 | 0.10654 | 0.030538 | 0.030538 | 172 | 106
2014-10-27 | n/a | n/a | 0.021675 | 0.021675 | 0.045682 | 0.045682 | 0.20691 | 0.20691 | 0.079608 | 0.079608 | 944 | 434
2014-10-28 | n/a | n/a | 0 | 0 | 0 | 0 | 0.029881 | 0.029881 | 0.0080651 | 0.0080651 | 243 | 222
2014-10-29 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0066517 | 0.0066517 | 0.0017953 | 0.0017953 | 185 | 177
2014-10-30 | n/a | n/a | 0.0052862 | 0.0052862 | 0.0011203 | 0.0011203 | 0.0008186 | 0.0008186 | 0.0027029 | 0.0027029 | 174 | 165
2014-10-31 | n/a | n/a | 0 | 0 | 0.0052816 | 0.0052816 | 0.015406 | 0.015406 | 0.0059046 | 0.0059046 | 303 | 241
2014-11-01 | n/a | n/a | 0 | 0 | 0.0139 | 0.0139 | 0.0052253 | 0.0052253 | 0.0060065 | 0.0060065 | 244 | 236
2014-11-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0055292 | 0.0055292 | 0.0014924 | 0.0014924 | 83 | 82
2014-11-03 | n/a | n/a | 0 | 0 | 0.0023167 | 0.0023167 | 0.014514 | 0.014514 | 0.0046835 | 0.0046835 | 186 | 168
2014-11-04 | n/a | n/a | 0.0094264 | 0.0094264 | 0 | 0 | 0.037043 | 0.037043 | 0.013763 | 0.013763 | 171 | 160
2014-11-05 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0038773 | 0.0038773 | 0.0010465 | 0.0010465 | 201 | 184
2014-11-06 | n/a | n/a | 0 | 0 | 0.0048654 | 0.0048654 | 0.0037499 | 0.0037499 | 0.0026209 | 0.0026209 | 179 | 171
2014-11-07 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 187
2014-11-08 | n/a | n/a | 0.0056306 | 0.0056306 | 0.071985 | 0.071985 | 0 | 0 | 0.026051 | 0.026051 | 447 | 297
2014-11-09 | n/a | n/a | 0.017203 | 0.017203 | 0.0011203 | 0.0011203 | 0.0021225 | 0.0021225 | 0.007815 | 0.007815 | 147 | 95
2014-11-10 | n/a | n/a | 0 | 0 | 0 | 0 | 0.023421 | 0.023421 | 0.0063213 | 0.0063213 | 200 | 174
2014-11-11 | n/a | n/a | 0.0089859 | 0.0089859 | 0 | 0 | 0.015661 | 0.015661 | 0.0078163 | 0.0078163 | 178 | 149
2014-11-12 | n/a | n/a | 0.013616 | 0.013616 | 0.019718 | 0.019718 | 0.011274 | 0.011274 | 0.015002 | 0.015002 | 193 | 175
2014-11-13 | n/a | n/a | 0 | 0 | 0.0037051 | 0.0037051 | 0.014382 | 0.014382 | 0.0051068 | 0.0051068 | 208 | 190
2014-11-14 | n/a | n/a | 0.0021396 | 0.0021396 | 0.00050815 | 0.00050815 | 0.019818 | 0.019818 | 0.0063716 | 0.0063716 | 254 | 215
2014-11-15 | n/a | n/a | 0 | 0 | 0.0036931 | 0.0036931 | 0.07511 | 0.07511 | 0.021494 | 0.021494 | 325 | 198
2014-11-16 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0039214 | 0.0039214 | 0.0010584 | 0.0010584 | 358 | 260
2014-11-17 | n/a | n/a | 0 | 0 | 0.019698 | 0.019698 | 0.025126 | 0.025126 | 0.013295 | 0.013295 | 274 | 237
2014-11-18 | n/a | n/a | 0 | 0 | 0.0082744 | 0.0082744 | 0.0049018 | 0.0049018 | 0.004059 | 0.004059 | 206 | 177
2014-11-19 | n/a | n/a | 0.0079624 | 0.0079624 | 0.0055256 | 0.0055256 | 0.0094359 | 0.0094359 | 0.0075544 | 0.0075544 | 329 | 248
2014-11-20 | n/a | n/a | 0 | 0 | 0.0013924 | 0.0013924 | 0.016333 | 0.016333 | 0.0048687 | 0.0048687 | 204 | 185
2014-11-21 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0066566 | 0.0066566 | 0.0017966 | 0.0017966 | 226 | 206
2014-11-22 | n/a | n/a | 0.0096284 | 0.0096284 | 0.024375 | 0.024375 | 0.046224 | 0.046224 | 0.024382 | 0.024382 | 177 | 76
2014-11-23 | n/a | n/a | 0.009582 | 0.009582 | 0.003305 | 0.003305 | 0.030484 | 0.030484 | 0.013148 | 0.013148 | 166 | 102
2014-11-24 | n/a | n/a | 0.0050312 | 0.0050312 | 0.045453 | 0.045453 | 0.084129 | 0.084129 | 0.039746 | 0.039746 | 943 | 737
2014-11-25 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0087448 | 0.0087448 | 0.0023602 | 0.0023602 | 265 | 239
2014-11-26 | n/a | n/a | 0 | 0 | 0.0086666 | 0.0086666 | 0 | 0 | 0.0028656 | 0.0028656 | 171 | 161
2014-11-27 | n/a | n/a | 0.012583 | 0.012583 | 0.01957 | 0.01957 | 0.011289 | 0.011289 | 0.014544 | 0.014544 | 167 | 155
2014-11-28 | n/a | n/a | 0 | 0 | 0.011864 | 0.011864 | 0.014495 | 0.014495 | 0.0078349 | 0.0078349 | 215 | 185
2014-11-29 | n/a | n/a | 0 | 0 | 0.00070421 | 0.00070421 | 0.025269 | 0.025269 | 0.007053 | 0.007053 | 245 | 176
2014-11-30 | n/a | n/a | 0.001666 | 0.001666 | 0.0012484 | 0.0012484 | 0.01172 | 0.01172 | 0.0042416 | 0.0042416 | 145 | 124
2014-12-01 | n/a | n/a | 0.0072668 | 0.0072668 | 0 | 0 | 0.015112 | 0.015112 | 0.0069815 | 0.0069815 | 247 | 232
2014-12-02 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0016421 | 0.0016421 | 0.00044321 | 0.00044321 | 172 | 165
2014-12-03 | n/a | n/a | 0.012669 | 0.012669 | 0.016769 | 0.016769 | 0.25841 | 0.25841 | 0.08035 | 0.08035 | 857 | 695
2014-12-04 | n/a | n/a | 0 | 0 | 0.015849 | 0.015849 | 0.01994 | 0.01994 | 0.010622 | 0.010622 | 720 | 506
2014-12-05 | n/a | n/a | 0 | 0 | 0.0053936 | 0.0053936 | 0.0047253 | 0.0047253 | 0.0030588 | 0.0030588 | 207 | 197
2014-12-06 | n/a | n/a | 0 | 0 | 0.03361 | 0.03361 | 0.041454 | 0.041454 | 0.022302 | 0.022302 | 417 | 304
2014-12-07 | n/a | n/a | 0.0068263 | 0.0068263 | 0 | 0 | 0.0021568 | 0.0021568 | 0.0033088 | 0.0033088 | 177 | 164
2014-12-08 | n/a | n/a | 0 | 0 | 0.0069581 | 0.0069581 | 0.00021568 | 0.00021568 | 0.0023589 | 0.0023589 | 235 | 229
2014-12-09 | n/a | n/a | 0 | 0 | 0.0014804 | 0.0014804 | 0.023823 | 0.023823 | 0.0069193 | 0.0069193 | 294 | 275
2014-12-10 | n/a | n/a | 0.010172 | 0.010172 | 0.0042693 | 0.0042693 | 0.00044116 | 0.00044116 | 0.0055937 | 0.0055937 | 235 | 216
2014-12-11 | n/a | n/a | 0 | 0 | 0.0055176 | 0.0055176 | 0.0044606 | 0.0044606 | 0.0030284 | 0.0030284 | 256 | 238
2014-12-12 | n/a | n/a | 0 | 0 | 0 | 0 | 0.008431 | 0.008431 | 0.0022756 | 0.0022756 | 230 | 206
2014-12-13 | n/a | n/a | 0 | 0 | 0.00053216 | 0.00053216 | 0.0073576 | 0.0073576 | 0.0021618 | 0.0021618 | 169 | 141
2014-12-14 | n/a | n/a | 0 | 0 | 0.0017405 | 0.0017405 | 0.012196 | 0.012196 | 0.0038672 | 0.0038672 | 88 | 82
2014-12-15 | n/a | n/a | 0.0083632 | 0.0083632 | 0.065435 | 0.065435 | 0.057096 | 0.057096 | 0.040387 | 0.040387 | 345 | 311
2014-12-16 | n/a | n/a | 0.0027126 | 0.0027126 | 0.024075 | 0.024075 | 0.036999 | 0.036999 | 0.01903 | 0.01903 | 652 | 569
2014-12-17 | n/a | n/a | 0 | 0 | 0.0015405 | 0.0015405 | 0.0002696 | 0.0002696 | 0.00058212 | 0.00058212 | 305 | 284
2014-12-18 | n/a | n/a | 0.0071675 | 0.0071675 | 0.028769 | 0.028769 | 0 | 0 | 0.012375 | 0.012375 | 235 | 224
2014-12-19 | n/a | n/a | 0.014514 | 0.014514 | 0 | 0 | 0.0099163 | 0.0099163 | 0.0084739 | 0.0084739 | 162 | 157
2014-12-20 | n/a | n/a | 0 | 0 | 0 | 0 | 0.024362 | 0.024362 | 0.0065754 | 0.0065754 | 107 | 105
2014-12-21 | n/a | n/a | 0 | 0 | 0.017617 | 0.017617 | 0.014872 | 0.014872 | 0.0098392 | 0.0098392 | 116 | 111
2014-12-22 | n/a | n/a | 0 | 0 | 0.010263 | 0.010263 | 0.038709 | 0.038709 | 0.013841 | 0.013841 | 297 | 267
2014-12-23 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0094996 | 0.0094996 | 0.002564 | 0.002564 | 157 | 149
2014-12-24 | n/a | n/a | 0 | 0 | 0 | 0 | 0.00013235 | 0.00013235 | 3.5721e-05 | 3.5721e-05 | 111 | 104
2014-12-25 | n/a | n/a | 0.0086712 | 0.0086712 | 0.0045854 | 0.0045854 | 0.030224 | 0.030224 | 0.013137 | 0.013137 | 72 | 69
2014-12-26 | n/a | n/a | 0.0065216 | 0.0065216 | 0 | 0 | 0.029406 | 0.029406 | 0.010542 | 0.010542 | 96 | 87
2014-12-27 | n/a | n/a | 0.0083632 | 0.0083632 | 0.0017445 | 0.0017445 | 0.0010833 | 0.0010833 | 0.0042098 | 0.0042098 | 81 | 81
2014-12-28 | n/a | n/a | 0 | 0 | 0 | 0 | 0.0056811 | 0.0056811 | 0.0015334 | 0.0015334 | 63 | 62
2014-12-29 | n/a | n/a | 0 | 0 | 0.023039 | 0.023039 | 0.024342 | 0.024342 | 0.014188 | 0.014188 | 360 | 325
2014-12-30 | n/a | n/a | 0 | 0 | 0.012792 | 0.012792 | 0.00017156 | 0.00017156 | 0.004276 | 0.004276 | 150 | 144
2014-12-31 | n/a | n/a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 127
Formulas:
Date = [Date, row above]+1
Contents
Contents

## 1e. STPIS Exclusions
Powercor Australia Ltd
STPIS Data Reporting
2014
Exclusions
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of interruptions (unplanned) | Duration of interruption (unplanned) (mins) | Total unplanned minutes off supply | Event category (use exclusion categories listed in section 3.3(a) of the AER's STPIS) | Effect on unplanned MAIFI (by feeder classification) | Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning
2014-02-16 | 469260-1 | BAN005 | Urban | Other | 1672 | 0 | 0 | 3.3 b) | 0.0055379 | Threshold exceeded due to Weather related Pole Fires across
2014-02-16 | 470345-1 | SA004 | Urban | Equipment failure | 3662 | 0 | 0 | 3.3 b) | 0.012129 | Threshold exceeded due to Weather related Pole Fires across
2014-02-16 | 477331-1 | BMH006 | Rural Long | Other | 363 | 0 | 0 | 3.3 b) | 0.0017793 | Threshold exceeded due to Weather related Pole Fires across
2014-02-16 | 470576-1 | FNS032 | Rural Short | Other | 117 | 0 | 0 | 3.3 b) | 0.00046814 | Threshold exceeded due to Weather related Pole Fires across
2014-02-16 | 470577-1 | MNA034 | Rural Long | Other | 766 | 0 | 0 | 3.3 b) | 0.0037548 | Threshold exceeded due to Weather related Pole Fires across
2014-02-16 | 475909-1 | SA005 | Urban | Other | 3510 | 0 | 0 | 3.3 b) | 0.011626 | Threshold exceeded due to Weather related Pole Fires across
2014-02-16 | 478344-1 | SHL004 | Rural Short | Other | 367 | 0 | 0 | 3.3 b) | 0.0014684 | Threshold exceeded due to Weather related Pole Fires across
2014-06-24 | 520064-1 | AL007 | Urban | Other | 1899 | 0 | 0 | 3.3 b) | 0.0062898 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519191-1 | ART031 | Rural Short | Other | 1286 | 0 | 0 | 3.3 b) | 0.0051455 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520120-1 | BLT016 | Urban | Other | 556 | 0 | 0 | 3.3 b) | 0.0018416 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519926-1 | BLT016 | Urban | Other | 556 | 0 | 0 | 3.3 b) | 0.0018416 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520155-1 | BLT030 | Urban | Other | 2678 | 0 | 0 | 3.3 b) | 0.0088699 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520330-1 | CLC005 | Rural Short | Weather | 2165 | 0 | 0 | 3.3 b) | 0.0086626 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519133-1 | CLC006 | Rural Long | Weather | 2686 | 0 | 0 | 3.3 b) | 0.013166 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519064-1 | CLC006 | Rural Long | Weather | 2686 | 0 | 0 | 3.3 b) | 0.013166 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520513-1 | MLN011 | Rural Short | Other | 4103 | 0 | 0 | 3.3 b) | 0.016417 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520242-1 | SA004 | Urban | Other | 3674 | 0 | 0 | 3.3 b) | 0.012169 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520334-1 | SU003 | Urban | Other | 5165 | 0 | 0 | 3.3 b) | 0.017107 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521315-1 | TRG003 | Rural Long | Other | 1664 | 0 | 0 | 3.3 b) | 0.0081565 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519978-1 | WBE013 | Urban | Weather | 5375 | 0 | 0 | 3.3 b) | 0.017803 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520136-1 | WBE023 | Rural Short | Other | 3205 | 0 | 0 | 3.3 b) | 0.012824 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520061-1 | WBE023 | Rural Short | Other | 3205 | 0 | 0 | 3.3 b) | 0.012824 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519335-1 | WBE023 | Rural Short | Other | 3204 | 0 | 0 | 3.3 b) | 0.01282 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521037-1 | BAN006 | Rural Long | Other | 68 | 0 | 0 | 3.3 b) | 0.00033332 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521516-1 | CLC006 | Rural Long | Other | 51 | 0 | 0 | 3.3 b) | 0.00024999 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519185-1 | CLC006 | Rural Long | Other | 377 | 0 | 0 | 3.3 b) | 0.001848 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518995-1 | CLC006 | Rural Long | Other | 100 | 0 | 0 | 3.3 b) | 0.00049018 | Threshold exceeded due to storm activity on the network
2014-06-24 | F-1727-b | CLC007 | Rural Long | Vegetation | 1564 | 0 | 0 | 3.3 b) | 0.0076664 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521508-1 | CLC007 | Rural Long | Other | 1348 | 0 | 0 | 3.3 b) | 0.0066076 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521505-1 | CLC007 | Rural Long | Other | 1348 | 0 | 0 | 3.3 b) | 0.0066076 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519050-1 | CLC007 | Rural Long | Other | 2502 | 0 | 0 | 3.3 b) | 0.012264 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518949-1 | CLC007 | Rural Long | Other | 2502 | 0 | 0 | 3.3 b) | 0.012264 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521515-1 | GL012 | Rural Long | Other | 423 | 0 | 0 | 3.3 b) | 0.0020734 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521514-1 | GL012 | Rural Long | Other | 423 | 0 | 0 | 3.3 b) | 0.0020734 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521513-1 | GL012 | Rural Long | Other | 423 | 0 | 0 | 3.3 b) | 0.0020734 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519249-1 | GL012 | Rural Long | Other | 2555 | 0 | 0 | 3.3 b) | 0.012524 | Threshold exceeded due to storm activity on the network
2014-06-24 | 519337-1 | GLE031 | Rural Short | Other | 1358 | 0 | 0 | 3.3 b) | 0.0054336 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518836-1 | KRT012 | Rural Long | Other | 543 | 0 | 0 | 3.3 b) | 0.0026617 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518889-1 | KRT022 | Rural Short | Other | 2185 | 0 | 0 | 3.3 b) | 0.0087426 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518857-1 | KRT022 | Rural Short | Other | 2185 | 0 | 0 | 3.3 b) | 0.0087426 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518835-1 | KRT022 | Rural Short | Other | 2185 | 0 | 0 | 3.3 b) | 0.0087426 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521511-1 | LV004 | Urban | Other | 7 | 0 | 0 | 3.3 b) | 2.3185e-05 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521481-1 | MRO007 | Rural Long | Other | 44 | 0 | 0 | 3.3 b) | 0.00021568 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521475-1 | MRO007 | Rural Long | Other | 44 | 0 | 0 | 3.3 b) | 0.00021568 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521418-1 | MRO007 | Rural Long | Other | 46 | 0 | 0 | 3.3 b) | 0.00022548 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520787-1 | MRO007 | Rural Long | Other | 58 | 0 | 0 | 3.3 b) | 0.0002843 | Threshold exceeded due to storm activity on the network
2014-06-24 | 518996-1 | TRG004 | Rural Short | Other | 487 | 0 | 0 | 3.3 b) | 0.0019486 | Threshold exceeded due to storm activity on the network
2014-06-24 | 521474-1 | TRG005 | Rural Long | Other | 1038 | 0 | 0 | 3.3 b) | 0.005088 | Threshold exceeded due to storm activity on the network
2014-06-24 | 520947-1 | WBL012 | Rural Long | Other | 1384 | 0 | 0 | 3.3 b) | 0.006784 | Threshold exceeded due to storm activity on the network
Weather
Equipment failure
Operational error
Vegetation
Animals
Third party impacts
Transmission failure
Load shedding
Inter-distributor connection failure
Other
Contents

## 1f. STPIS GSL
Powercor Australia Ltd
STPIS Data Reporting
2014
Exclusions
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 4 Guaranteed service levels - jurisdictional GSL scheme
Appointments
Customer arranged appointments Central - number | 8452
Appointments not met within 15 minutes of agreed time - number | 609
Appointments - GSL payments - number | 4
Appointments - GSL payments - ($) | 160
Connections
Connections made | 78770
Connections not made on agreed date | 57
Connections - GSL payments - 1-4 day delay - number | 48
Connections - GSL payments - 1-4 day delay - ($) | 8000
Connections - GSL payments - 5+ day delay - number | 9
Connections - GSL payments - 5+ day delay - ($) | 4500
Reliability of supply
Low reliability payments - 20 hours - number | 8885
Low reliability payments - 20 hours - ($) | 888500
Low reliability payments - 30 hours - number | 4585
Low reliability payments - 30 hours - ($) | 687750
Low reliability payments - 60 hours - number | 410
Low reliability payments - 60 hours - ($) | 123000
Low reliability payments - 10 events - number | 2707
Low reliability payments - 10 events - ($) | 270700
Low reliability payments - 15 events - number | 13
Low reliability payments - 15 events - ($) | 1950
Low reliability payments - 30 events - number | 0
Low reliability payments - 30 events - ($) | 0
Low reliability payments - 24 momentary events - number | 1430
Low reliability payments - 24 momentary events - ($) | 35750
Low reliability payments - 36 momentary events - number | 127
Low reliability payments - 36 momentary events - ($) | 4445
Street lights
Street lights | 159229
Street lights "out" during period | 6047
Street lights not repaired by "fix by" date | 109
Street lights not repaired in 2 business days | 127
Street lights – number of business days to repair | 2.15
Street lights - GSL payments - number | 105
Street lights - GSL payments - ($) | 4200
Planned interruptions
Planned interruptions - 4 business days notice not given | 186
Total GSL payments made ($) | 2028955
Did the AER's GSL Scheme apply at any time during the regulatory year? |  | no
If the AER's GSL scheme applied at any time during the regulatory year, table 2 must be completed. Do not complete table 2 if the AER's GSL scheme did not apply during the regulatory year.
Table 2: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) |  | 0
Contents

## 2. Customer Service
Powercor Australia Ltd
Customer Service
2014
The information is required to assess the outturn level of service provided to the DNSPs customers, and will inform the AER’s review of future regulatory proposals. The information may be used in performance reports.
Table 1 Quality of supply
Over voltage events - due to high voltage injection | 0
Customers receiving over-voltage - due to high voltage injection | 213
Over voltage events - due to lightning | 0
Customers receiving over-voltage - due to lightning | 145
Over voltage events - due to voltage regulation or other cause | 9
Customers receiving over-voltage - due to voltage regulation or other cause | 1026
Voltage variations - steady state (zone sub) | 983
Voltage variations - one minute (zone sub) | 38
Voltage variations - 10 seconds (zone sub) Min<0.7 | 454
Voltage variations - 10 seconds (zone sub) Min<0.8 | 211
Voltage variations - 10 seconds (zone sub) Min<0.9 | 604
Voltage variations - steady state (feeder) | 48414
Voltage variations - % zone subs monitored | 100%
Voltage variations - % feeders monitored | 98%
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number | 9
Complaints by category (%)
Low voltage supply | 3
Voltage dips | 2
Voltage swell | 3
Voltage spike (impulsive transient) | 0
TV or radio interference | 1
Noise from appliances | 0
Other | 0
Complaints by Likely Cause (%)
Network equipment faulty | 0
Network interference by NSP equipment | 1
Network interference by another customer | 1
Network limitation | 1
Customer internal problem | 2
No problem identified | 1
Environmental | 0
Other | 3
Table 3 Customer service
Timely provision of services
Connections made | 78770
Connections not made on agreed date | 57
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 504
Streetlights - not repaired by "fix by" date | 43
Streetlights - average number of days to repair | 0.45
Total streetlights | 159229
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 312348
Calls to fault line answered within 30 seconds | 70168
Calls to fault line - average waiting time before call answered | 16.593
Calls abandoned - percentage | 1.21%
Call centre - number of overload events | 0
Customer complaints (number)
Complaint - reliability of supply | 24
Complaint - technical quality of supply | 9
Complaint - administrative process or customer service | 165
Complaint - connection or augmentation | 43
Complaint - other | 13
Total complaints | 254
Contents

## 4a. Network perf - Feeders
Powercor Australia Ltd
Network performance - feeders
2014
Table 1 Annual Feeder Reliability Data
Feeder ID / name | Description of the service area for the feeder | Feeder classification | Number of distribution customers(1) | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply (including excluded events and MEDs) | Planned customer minutes off-supply (after removing excluded events and MED) | Planned interruptions (SAIFI) (including excluded events and MEDs) | Planned interruptions (SAIFI) (after removing excluded events and MEDs) | Total number of momentary feeder outages | Momentary interruptions due to feeder outages (MAIFI) (including excluded events and MEDs) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events and MEDs) | Low Reliability Feeder (SAIDI)
AC024 | Sunshine CSC | Rural Short | 2 | 1.656 | 0.072 | 0.176 | 0 | 0.302 | 0 | 0 | 0 | 0 | 0 | 1 | 616 | 616 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | No
AC025 | Sunshine CSC | Rural Short | 2 | 0.784 | 1.172 | 0.157 | 0 | 0.248 | 0 | 0 | 0 | 0 | 0 | 1 | 618 | 618 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | No
AC026 | Sunshine CSC | Rural Short | 0 | 0.322 | 0.147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AC031 | Sunshine CSC | Urban | 11 | 3.579 | 1.232 | 1.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.4553e-05 | 1.4553e-05 | No
AC032 | Sunshine CSC | Rural Short | 0 | 0.352 | 0.251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AC033 | Sunshine CSC | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL002 | Sunshine CSC | Urban | 273 | 6.571 | 1.221 | 2.55 | 0.641 | 0 | 3 | 9427 | 8634 | 5.5566e-05 | 5.4243e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL004 | Sunshine CSC | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL005 | Sunshine CSC | Rural Short | 0 | 0 | 0.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL006 | Sunshine CSC | Urban | 2237 | 9.886 | 0.207 | 4.86 | 2.672 | 0.229 | 7 | 237884 | 237884 | 0.0035523 | 0.0035523 | 2 | 20430 | 20430 | 7.9381e-05 | 7.9381e-05 | 0 | 0 | 0 | No
AL007 | Sunshine CSC | Urban | 1898 | 7.979 | 1.113 | 4.502 | 0.356 | 0 | 3 | 29860 | 29860 | 0.00025402 | 0.00025402 | 0 | 0 | 0 | 0 | 0 | 2 | 0.0050221 | 0.0025097 | No
AL011 | Sunshine CSC | Urban | 119 | 3.649 | 0.999 | 4.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL012 | Sunshine CSC | Urban | 2 | 1.245 | 0.138 | 0.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL013 | Sunshine CSC | Urban | 2 | 0 | 0.846 | 2.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
AL014 | Sunshine CSC | Urban | 2183 | 12.183 | 1.472 | 6.274 | 0.412 | 0.162 | 4 | 24998 | 24998 | 0.00028842 | 0.00028842 | 1 | 9805 | 9805 | 4.8951e-05 | 4.8951e-05 | 1 | 0.0029027 | 0.0029027 | No
ART023 | Horsham CSC | Rural Long | 1012 | 219.914 | 1.308 | 4.661 | 1.366 | 0.902 | 13 | 34562 | 34562 | 0.0027598 | 0.0027598 | 15 | 22810 | 22810 | 0.0001323 | 0.0001323 | 1 | 0.0013362 | 0.0013362 | No
ART031 | Horsham CSC | Rural Short | 1282 | 92.553 | 0.565 | 4.741 | 3.776 | 2.616 | 14 | 158826 | 68326 | 0.004063 | 0.0036872 | 12 | 110049 | 110049 | 0.00044188 | 0.00044188 | 1 | 0.0017014 | 0 | No
ART033 | Horsham CSC | Rural Long | 1929 | 916.134 | 0.978 | 3.984 | 12.189 | 1.044 | 67 | 1128900 | 1128900 | 0.010304 | 0.010304 | 14 | 96706 | 96706 | 0.00052391 | 0.00052391 | 0 | 0 | 0 | No
ART034 | Horsham CSC | Rural Short | 2300 | 25.696 | 1.025 | 6.175 | 1.01 | 11.28 | 7 | 59498 | 59458 | 0.0062697 | 0.0062684 | 7 | 664205 | 664205 | 0.0020864 | 0.0020864 | 0 | 0 | 0 | No
BAN001 | Ballarat CSC | Urban | 2685 | 11.817 | 5.425 | 9.122 | 0.586 | 4.426 | 1 | 24027 | 24027 | 0.0002302 | 0.0002302 | 10 | 181614 | 181614 | 0.00084011 | 0.00084011 | 3 | 0.010805 | 0.010805 | No
BAN002 | Ballarat CSC | Urban | 976 | 16.851 | 1.906 | 8.688 | 1.379 | 0 | 5 | 16739 | 16739 | 0.00027122 | 0.00027122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
BAN003 | Ballarat CSC | Urban | 498 | 8.79 | 1.695 | 12.242 | 0.026 | 0 | 0 | 103 | 103 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 1 | 0.00065886 | 0.00065886 | No
BAN004 | Ballarat CSC | Urban | 1186 | 11.245 | 3.659 | 7.661 | 9.694 | 0.073 | 3 | 175215 | 175215 | 0.00048025 | 0.00048025 | 1 | 1325 | 1325 | 6.615e-06 | 6.615e-06 | 0 | 0 | 0 | No
BAN005 | Ballarat CSC | Urban | 1672 | 8.336 | 1.285 | 8.569 | 16.177 | 0 | 7 | 467742 | 251635 | 0.0029768 | 0.0026315 | 1 | 1 | 1 | 1.323e-06 | 1.323e-06 | 1 | 0.0022121 | 0 | YES
BAN006 | Ballarat CSC | Rural Long | 4858 | 412.437 | 4.847 | 9.557 | 39.1 | 0.557 | 48 | 2759995 | 2223234 | 0.020254 | 0.016284 | 11 | 39316 | 39316 | 0.00031488 | 0.00031488 | 2 | 0.01287 | 0.01287 | No
BAN007 | Ballarat CSC | Rural Short | 4441 | 32.767 | 3.308 | 8.175 | 1.821 | 0.076 | 14 | 128750 | 128452 | 0.0069392 | 0.0069379 | 3 | 5361 | 5361 | 0.0058953 | 0.0058953 | 0 | 0 | 0 | No
BAN008 | Ballarat CSC | Rural Long | 3466 | 245.251 | 4.604 | 8.412 | 20.618 | 0.899 | 64 | 1185938 | 766487 | 0.022454 | 0.017891 | 11 | 51685 | 51685 | 0.00035986 | 0.00035986 | 4 | 0.018354 | 0.018354 | No
BAN009 | Ballarat CSC | Rural Long | 3086 | 356.632 | 5.223 | 9.596 | 18.946 | 12.867 | 67 | 810147 | 669648 | 0.0091976 | 0.0085863 | 58 | 550199 | 550199 | 0.0026037 | 0.0026037 | 2 | 0.0081616 | 0.0081616 | No
BAN011 | Ballarat CSC | Rural Long | 3712 | 567.485 | 26.652 | 10.544 | 17.081 | 0.395 | 116 | 1356892 | 1163144 | 0.0113 | 0.010486 | 19 | 31403 | 31403 | 0.00078719 | 0.00078719 | 1 | 0.0049123 | 0.0049123 | No
BAN013 | Ballarat CSC | Urban | 504 | 4.907 | 1.67 | 8.688 | 1.393 | 0.703 | 2 | 12682 | 12682 | 0.00012436 | 0.00012436 | 2 | 6402 | 6402 | 4.2336e-05 | 4.2336e-05 | 1 | 0.00066547 | 0.00066547 | No
BAN015 | Ballarat CSC | Rural Short | 4743 | 48.493 | 5.928 | 8.056 | 8.112 | 0.001 | 24 | 728209 | 160094 | 0.003289 | 0.0019488 | 1 | 104 | 104 | 1.5876e-05 | 1.5876e-05 | 0 | 0 | 0 | No
BAS011 | Ballarat CSC | Rural Long | 3522 | 985.098 | 9.188 | 11.613 | 25.293 | 17.384 | 73 | 1163556 | 1163277 | 0.014123 | 0.014122 | 107 | 799725 | 799725 | 0.0064166 | 0.0064166 | 1 | 0.0046279 | 0.0046279 | No
BAS012 | Ballarat CSC | Urban | 2279 | 8.036 | 3.225 | 9.041 | 2.545 | 0.115 | 3 | 101356 | 101356 | 0.003203 | 0.003203 | 1 | 4590 | 4590 | 3.5721e-05 | 3.5721e-05 | 0 | 0 | 0 | No
BAS013 | Ballarat CSC | Rural Short | 3431 | 23.509 | 4.906 | 6.791 | 3.627 | 0.061 | 7 | 252089 | 12129 | 0.0047853 | 0.00025005 | 2 | 4230 | 4230 | 6.4827e-05 | 6.4827e-05 | 6 | 0.027208 | 0.027208 | No
BAS014 | Ballarat CSC | Urban | 2619 | 12.174 | 2.162 | 8.037 | 4.699 | 0.336 | 15 | 196190 | 196190 | 0.0044506 | 0.0044506 | 4 | 14038 | 14038 | 0.00016405 | 0.00016405 | 2 | 0.0069352 | 0.0069352 | No
BAS021 | Ballarat CSC | Rural Long | 5249 | 548.279 | 11.423 | 10.729 | 7.564 | 9.788 | 84 | 607390 | 558086 | 0.0066362 | 0.006529 | 106 | 785926 | 785926 | 0.0038963 | 0.0038963 | 0 | 0 | 0 | No
BAS022 | Ballarat CSC | Rural Long | 6552 | 558.92 | 12.642 | 13.341 | 15.949 | 2.215 | 126 | 1200704 | 1186534 | 0.011476 | 0.011379 | 26 | 166712 | 166712 | 0.00095124 | 0.00095124 | 3 | 0.026103 | 0.026103 | No
BAS023 | Ballarat CSC | Rural Short | 3724 | 110.38 | 3.246 | 9.122 | 26.03 | 1.407 | 31 | 1721126 | 1700771 | 0.022137 | 0.022047 | 4 | 93054 | 93054 | 0.00041939 | 0.00041939 | 2 | 0.0098379 | 0.0098379 | No
BAS024 | Ballarat CSC | Urban | 3762 | 18.033 | 12.9 | 11.292 | 6.402 | 3.281 | 9 | 303356 | 303356 | 0.0051544 | 0.0051544 | 11 | 155441 | 155441 | 0.00067341 | 0.00067341 | 0 | 0 | 0 | No
BAS034 | Ballarat CSC | Urban | 4091 | 31.324 | 5.22 | 12.055 | 37.196 | 2.936 | 36 | 1768522 | 787542 | 0.0081034 | 0.0026791 | 9 | 139573 | 139573 | 0.00075147 | 0.00075147 | 4 | 0.016289 | 0.016289 | YES
BBD013 | Mildura CSC | Rural Short | 33 | 40.982 | 0.303 | 3.712 | 1.334 | 0.7 | 7 | 2264 | 1814 | 0.00012701 | 0.00010319 | 1 | 1188 | 1188 | 1.1907e-05 | 1.1907e-05 | 5 | 6.615e-05 | 6.615e-05 | No
BBD014 | Mildura CSC | Rural Short | 66 | 117.018 | 1.155 | 9.201 | 27.479 | 5.37 | 8 | 46104 | 41012 | 0.00060594 | 0.00042865 | 3 | 9010 | 9010 | 9.1288e-05 | 9.1288e-05 | 4 | 0.00034927 | 0.00034927 | YES
BBD021 | Mildura CSC | Rural Short | 213 | 81.777 | 0.482 | 9.083 | 5.933 | 4.317 | 14 | 38458 | 17272 | 0.0015281 | 0.00096183 | 3 | 27983 | 27983 | 0.00028974 | 0.00028974 | 3 | 0.00084937 | 0.00084937 | No
BBD022 | Mildura CSC | Urban | 5 | 4.267 | 0.357 | 5.41 | 1.453 | 2.905 | 5 | 320 | 80 | 3.3075e-05 | 1.9845e-05 | 1 | 640 | 640 | 6.615e-06 | 6.615e-06 | 3 | 1.9845e-05 | 1.9845e-05 | No
BET001 | Bendigo CSC | Rural Long | 4366 | 365.899 | 9.743 | 12.389 | 4.362 | 0.456 | 29 | 613743 | 125891 | 0.0070887 | 0.0009605 | 23 | 64122 | 64122 | 0.00042469 | 0.00042469 | 3 | 0.017507 | 0.017507 | No
BET002 | Bendigo CSC | Urban | 3405 | 16.989 | 2.568 | 8.366 | 8.477 | 5.116 | 6 | 636096 | 636096 | 0.013746 | 0.013746 | 22 | 383908 | 383908 | 0.0013825 | 0.0013825 | 3 | 0.013538 | 0.013538 | YES
BET003 | Bendigo CSC | Rural Short | 327 | 10.994 | 0.631 | 3.067 | 2.247 | 0.157 | 4 | 36881 | 4706 | 0.00054111 | 0.00011113 | 3 | 2583 | 2583 | 6.615e-06 | 6.615e-06 | 0 | 0 | 0 | No
BET004 | Bendigo CSC | Rural Short | 3038 | 188.222 | 4.629 | 9.561 | 1.088 | 0.317 | 22 | 106568 | 106568 | 0.0012436 | 0.0012436 | 10 | 31012 | 31012 | 0.00017199 | 0.00017199 | 2 | 0.0080042 | 0.0080042 | No
BET005 | Bendigo CSC | Rural Long | 2799 | 323.466 | 6.501 | 12.15 | 10.042 | 1.396 | 32 | 431173 | 110673 | 0.0067447 | 0.0025045 | 14 | 59928 | 59928 | 0.00045115 | 0.00045115 | 0 | 0 | 0 | No
BET006 | Bendigo CSC | Rural Short | 3264 | 58.638 | 3.059 | 10.198 | 0.544 | 0.569 | 10 | 25519 | 25519 | 0.00037177 | 0.00037177 | 10 | 26683 | 26683 | 0.00012039 | 0.00012039 | 3 | 0.012895 | 0.012895 | No
BET007 | Bendigo CSC | Rural Short | 3043 | 134.199 | 3.12 | 6.533 | 18.485 | 1.318 | 19 | 1508651 | 1506875 | 0.0084104 | 0.0083522 | 9 | 107539 | 107539 | 0.00043527 | 0.00043527 | 0 | 0 | 0 | No
BET008 | Bendigo CSC | Urban | 944 | 6.671 | 4.861 | 9.72 | 0.013 | 0.808 | 0 | 376 | 376 | 6.615e-06 | 6.615e-06 | 3 | 23565 | 23565 | 6.7473e-05 | 6.7473e-05 | 1 | 0.0025005 | 0.0025005 | No
BGO011 | Bendigo CSC | Urban | 568 | 0.983 | 4 | 5.179 | 0.008 | 0 | 0 | 195 | 195 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
BGO012 | Bendigo CSC | Urban | 2200 | 11.337 | 1.548 | 6.215 | 5.464 | 1.111 | 5 | 315344 | 118095 | 0.0041503 | 0.00098035 | 10 | 64130 | 64130 | 0.00049216 | 0.00049216 | 2 | 0.0063478 | 0.0063478 | No
BGO013 | Bendigo CSC | Rural Short | 3694 | 173.421 | 11.449 | 10.318 | 1.506 | 0.46 | 26 | 107052 | 107052 | 0.00083217 | 0.00083217 | 9 | 32657 | 32657 | 0.00068532 | 0.00068532 | 3 | 0.014369 | 0.014369 | No
BGO021 | Bendigo CSC | Urban | 1519 | 0.001 | 0.359 | 0.239 | 1.262 | 0.737 | 20 | 51558 | 51442 | 0.00095786 | 0.00095654 | 7 | 30130 | 30130 | 0.00011907 | 0.00011907 | 0 | 0 | 0 | No
BGO022 | Bendigo CSC | Urban | 4373 | 18.675 | 2.547 | 9.641 | 5.757 | 0.229 | 9 | 494285 | 494024 | 0.0061255 | 0.0061229 | 4 | 19698 | 19698 | 0.00020374 | 0.00020374 | 7 | 0.040488 | 0.040488 | No
BGO023 | Bendigo CSC | Rural Long | 2655 | 541.935 | 4.08 | 10.398 | 20.15 | 0.968 | 58 | 646469 | 641957 | 0.0082344 | 0.00811 | 18 | 31046 | 31046 | 0.00025005 | 0.00025005 | 1 | 0.0035245 | 0.0035245 | No
BGO024 | Bendigo CSC | Urban | 578 | 0 | 5.929 | 10.318 | 0.211 | 1.515 | 4 | 2528 | 2528 | 3.0429e-05 | 3.0429e-05 | 5 | 18155 | 18155 | 8.335e-05 | 8.335e-05 | 0 | 0 | 0 | No
BLT016 | Sunshine CSC | Urban | 559 | 10.149 | 7.223 | 10.781 | 23.081 | 4.693 | 9 | 166694 | 166694 | 0.0029807 | 0.0029807 | 5 | 33895 | 33895 | 0.00012833 | 0.00012833 | 2 | 0.0014712 | 0 | YES
BLT017 | Sunshine CSC | Urban | 985 | 10.663 | 3.22 | 8.135 | 29.721 | 0.368 | 15 | 541380 | 251642 | 0.0056545 | 0.0042971 | 5 | 6704 | 6704 | 1.323e-05 | 1.323e-05 | 0 | 0 | 0 | YES
BLT019 | Sunshine CSC | Urban | 0 | 3.78 | 0.045 | 12.519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
BLT020 | Sunshine CSC | Urban | 69 | 6.884 | 0.913 | 8.372 | 17.406 | 15.572 | 4 | 17649 | 3978 | 0.00019713 | 0.00010055 | 3 | 15790 | 15790 | 5.6889e-05 | 5.6889e-05 | 2 | 0.00018654 | 0.00018654 | YES
BLT021 | Sunshine CSC | Rural Short | 522 | 10.286 | 0.986 | 0.316 | 0.005 | 0 | 1 | 972 | 972 | 1.1907e-05 | 1.1907e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
BLT022 | Sunshine CSC | Urban | 1255 | 12.568 | 4.927 | 6.082 | 8.591 | 0.086 | 9 | 255581 | 255581 | 0.0018165 | 0.0018165 | 1 | 2568 | 2568 | 1.0584e-05 | 1.0584e-05 | 0 | 0 | 0 | No
BLT023 | Sunshine CSC | Urban | 2 | 3.505 | 0.847 | 13.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
BLT030 | Sunshine CSC | Urban | 2411 | 10.148 | 0.147 | 6.792 | 0.947 | 0.046 | 12 | 64214 | 38329 | 0.0005464 | 0.00032546 | 2 | 3105 | 3105 | 2.1168e-05 | 2.1168e-05 | 2 | 0.006406 | 0.002863 | No
BLT031 | Sunshine CSC | Urban | 1299 | 3.072 | 1.673 | 7.069 | 9.32 | 1.011 | 8 | 274553 | 181801 | 0.0024529 | 0.0021367 | 2 | 29790 | 29790 | 0.00027783 | 0.00027783 | 1 | 0.0019607 | 0.0019607 | No
BMH003 | Sunshine CSC | Rural Long | 2705 | 320.14 | 3.664 | 6.028 | 30.339 | 8.561 | 66 | 1837496 | 1542284 | 0.021199 | 0.018179 | 55 | 518482 | 518482 | 0.0050804 | 0.0050804 | 17 | 0.060701 | 0.060701 | YES
BMH004 | Sunshine CSC | Rural Short | 3078 | 23.795 | 8.48 | 6.51 | 4.967 | 0.811 | 16 | 435238 | 435238 | 0.0057524 | 0.0057524 | 4 | 71065 | 71065 | 0.00039558 | 0.00039558 | 17 | 0.069244 | 0.069244 | No
BMH005 | Sunshine CSC | Rural Short | 3705 | 63.384 | 8.69 | 10.769 | 11.239 | 4.462 | 18 | 616118 | 615519 | 0.010069 | 0.010055 | 19 | 244615 | 244615 | 0.0015757 | 0.0015757 | 21 | 0.10347 | 0.10347 | No
BMH006 | Sunshine CSC | Rural Long | 1475 | 227.051 | 18.265 | 7.916 | 17.188 | 8.064 | 36 | 390892 | 184721 | 0.0044175 | 0.0034504 | 22 | 183399 | 183399 | 0.00090494 | 0.00090494 | 17 | 0.033164 | 0.033164 | No
CDN001 | Warrnambool CSC | Rural Long | 1751 | 289.65 | 0.016 | 8.135 | 26.748 | 0.054 | 67 | 806716 | 494291 | 0.0069127 | 0.0054534 | 3 | 1614 | 1614 | 7.9381e-06 | 7.9381e-06 | 2 | 0.0046424 | 0.0046424 | No
CDN002 | Warrnambool CSC | Rural Long | 518 | 203.688 | 0.102 | 2.409 | 1.676 | 3.209 | 46 | 66315 | 27229 | 0.00045776 | 0.00041278 | 7 | 127017 | 127017 | 0.00069193 | 0.00069193 | 1 | 0.00068532 | 0.00068532 | No
CDN003 | Warrnambool CSC | Urban | 1641 | 16.01 | 0.084 | 5.094 | 2.148 | 0 | 4 | 111929 | 88004 | 0.0022279 | 0.0021949 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0021644 | 0.0021644 | No
CDN004 | Warrnambool CSC | Rural Long | 795 | 382.798 | 0.165 | 2.211 | 0.656 | 0.033 | 25 | 54575 | 47267 | 0.00035854 | 0.0003506 | 6 | 2712 | 2712 | 2.3814e-05 | 2.3814e-05 | 1 | 0.0010465 | 0.0010465 | No
CDN006 | Warrnambool CSC | Rural Long | 1004 | 433.377 | 0.251 | 3.12 | 9.461 | 0.062 | 41 | 495044 | 495044 | 0.0040497 | 0.0040497 | 7 | 3252 | 3252 | 2.9106e-05 | 2.9106e-05 | 0 | 0 | 0 | No
CHA003 | Bendigo CSC | Rural Short | 1199 | 69.562 | 1.016 | 4.757 | 0.565 | 1.072 | 16 | 22570 | 22570 | 0.00027122 | 0.00027122 | 10 | 42809 | 42809 | 0.00025402 | 0.00025402 | 3 | 0.0050512 | 0.0050512 | No
CHA005 | Bendigo CSC | Rural Long | 1281 | 302.879 | 0.159 | 5.419 | 8.768 | 3.153 | 56 | 262365 | 262126 | 0.0034795 | 0.0034782 | 18 | 94356 | 94356 | 0.00049613 | 0.00049613 | 1 | 0.0016035 | 0.0016035 | No
CHA006 | Bendigo CSC | Rural Long | 1881 | 894.312 | 0.012 | 7.993 | 44.924 | 4.305 | 91 | 1863333 | 1788378 | 0.0098524 | 0.0084236 | 33 | 178572 | 178572 | 0.00080968 | 0.00080968 | 4 | 0.010006 | 0.010006 | YES
CHM011 | Horsham CSC | Rural Long | 1562 | 810.505 | 0.107 | 3.949 | 11.859 | 6.002 | 45 | 908131 | 908131 | 0.0081299 | 0.0081299 | 57 | 459604 | 459604 | 0.0024026 | 0.0024026 | 2 | 0.0041093 | 0.0041093 | YES
CHM012 | Horsham CSC | Rural Long | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
CLC001 | Ballarat CSC | Urban | 1654 | 7.884 | 0.962 | 8.569 | 13.183 | 6.917 | 11 | 524555 | 524555 | 0.0097664 | 0.0097664 | 9 | 275222 | 275222 | 0.00092346 | 0.00092346 | 2 | 0.0043818 | 0.0043818 | YES
CLC002 | Ballarat CSC | Urban | 2862 | 15.39 | 0.868 | 7.78 | 7.063 | 0.896 | 8 | 334653 | 334064 | 0.0078137 | 0.0078124 | 5 | 42478 | 42478 | 0.00021433 | 0.00021433 | 1 | 0.0037865 | 0.0037865 | No
CLC003 | Ballarat CSC | Rural Long | 1565 | 529.081 | 0.397 | 9.912 | 34.402 | 6.389 | 57 | 640951 | 639616 | 0.0078018 | 0.0077978 | 19 | 119033 | 119033 | 0.0026315 | 0.0026315 | 1 | 0.0020612 | 0.0020612 | No
CLC004 | Ballarat CSC | Rural Long | 2119 | 219.145 | 1.723 | 6.674 | 13.543 | 8.488 | 55 | 536581 | 532353 | 0.010521 | 0.010502 | 56 | 336290 | 336290 | 0.0016458 | 0.0016458 | 2 | 0.0056625 | 0.0056625 | No
CLC005 | Ballarat CSC | Rural Short | 1800 | 69.852 | 15.745 | 10.978 | 5.559 | 6.429 | 9 | 279918 | 278105 | 0.0049494 | 0.0049401 | 7 | 323711 | 323711 | 0.0015426 | 0.0015426 | 14 | 0.036249 | 0.033385 | No
CLC006 | Ballarat CSC | Rural Long | 2695 | 509.204 | 14.776 | 7.938 | 40.998 | 2.576 | 68 | 2196282 | 1056095 | 0.017228 | 0.013712 | 18 | 138000 | 138000 | 0.00059535 | 0.00059535 | 4 | 0.01421 | 0.0071032 | YES
CLC007 | Ballarat CSC | Rural Long | 3415 | 356.547 | 8.981 | 10.031 | 36.196 | 10.078 | 48 | 3086040 | 1102481 | 0.012002 | 0.0089793 | 58 | 859192 | 859192 | 0.0036687 | 0.0036687 | 2 | 0.0090626 | 0.0090626 | YES
CME014 | Shepparton CSC | Rural Short | 3403 | 91.793 | 8.275 | 9.999 | 25.363 | 2.635 | 45 | 2276535 | 2276535 | 0.049822 | 0.049822 | 50 | 236479 | 236479 | 0.001454 | 0.001454 | 1 | 0.0045048 | 0.0045048 | YES
CME015 | Shepparton CSC | Rural Short | 904 | 61.749 | 3.151 | 8.127 | 27.602 | 11.603 | 23 | 482251 | 482251 | 0.0085361 | 0.0085361 | 25 | 202724 | 202724 | 0.00085731 | 0.00085731 | 7 | 0.0083852 | 0.0083852 | YES
CME016 | Shepparton CSC | Rural Long | 1930 | 285.566 | 9.163 | 6.852 | 14.971 | 1.755 | 49 | 870002 | 870002 | 0.016466 | 0.016466 | 15 | 101968 | 101968 | 0.00044056 | 0.00044056 | 11 | 0.027942 | 0.027942 | No
CME021 | Shepparton CSC | Rural Short | 1729 | 25.025 | 3.333 | 7.33 | 14.593 | 5.335 | 16 | 587493 | 587493 | 0.011969 | 0.011969 | 18 | 214785 | 214785 | 0.0011457 | 0.0011457 | 4 | 0.0091737 | 0.0091737 | No
CME022 | Shepparton CSC | Urban | 714 | 16.681 | 0.246 | 12.071 | 37.075 | 2.675 | 7 | 232503 | 232503 | 0.0047747 | 0.0047747 | 2 | 16778 | 16778 | 7.9381e-05 | 7.9381e-05 | 3 | 0.0028405 | 0.0028405 | YES
CMN001 | Bendigo CSC | Rural Long | 3975 | 234.702 | 4.948 | 8.087 | 37.504 | 9.463 | 59 | 2858232 | 2514381 | 0.038596 | 0.032758 | 39 | 721201 | 721201 | 0.0039915 | 0.0039915 | 1 | 0.0046464 | 0.0046464 | YES
CMN002 | Bendigo CSC | Rural Short | 430 | 60.385 | 0.991 | 1.315 | 0.12 | 0.107 | 5 | 6133 | 6133 | 5.4243e-05 | 5.4243e-05 | 2 | 5489 | 5489 | 3.3075e-05 | 3.3075e-05 | 1 | 0.00057551 | 0.00057551 | No
CMN003 | Bendigo CSC | Rural Long | 2860 | 255.767 | 3.136 | 6.573 | 3.493 | 0.438 | 33 | 196824 | 196754 | 0.0022094 | 0.0022081 | 11 | 24660 | 24660 | 0.00012569 | 0.00012569 | 1 | 0.0037997 | 0.0037997 | No
CMN004 | Bendigo CSC | Rural Long | 1634 | 228.303 | 0.406 | 4.462 | 2.518 | 0.048 | 21 | 170402 | 128057 | 0.0027161 | 0.0024066 | 4 | 3276 | 3276 | 2.1168e-05 | 2.1168e-05 | 0 | 0 | 0 | No
CMN005 | Bendigo CSC | Urban | 985 | 18.812 | 0.812 | 7.41 | 3.019 | 0.237 | 4 | 66889 | 66889 | 0.001454 | 0.001454 | 1 | 5250 | 5250 | 1.9845e-05 | 1.9845e-05 | 2 | 0.0025878 | 0.0025878 | No
COB011 | Warrnambool CSC | Rural Long | 735 | 258.586 | 0 | 4.976 | 32.849 | 9.957 | 46 | 812633 | 168506 | 0.0041238 | 0.0020798 | 31 | 246324 | 246324 | 0.0010518 | 0.0010518 | 2 | 0.0019461 | 0.0019461 | YES
COB012 | Warrnambool CSC | Urban | 35 | 11.579 | 0.722 | 5.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4.4982e-05 | 4.4982e-05 | No
COB021 | Warrnambool CSC | Rural Short | 2 | 34.587 | 0.149 | 6.279 | 26.25 | 0 | 1 | 848 | 848 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | 0 | 0 | 2 | 5.292e-06 | 5.292e-06 | No
CRO013 | Geelong CSC | Rural Long | 4581 | 213.092 | 2.56 | 10.741 | 1.894 | 1.928 | 42 | 166175 | 147496 | 0.0040233 | 0.0037865 | 39 | 169162 | 169162 | 0.00095654 | 0.00095654 | 1 | 0.0060858 | 0.0060858 | No
CRO014 | Geelong CSC | Urban | 2 | 1.036 | 0.008 | 2.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
CRO021 | Geelong CSC | Urban | 541 | 4.389 | 0.466 | 2.211 | 0.251 | 0.405 | 2 | 8762 | 8079 | 5.6889e-05 | 5.5566e-05 | 2 | 14175 | 14175 | 6.4827e-05 | 6.4827e-05 | 0 | 0 | 0 | No
CRO022 | Geelong CSC | Urban | 3984 | 19.212 | 2.81 | 9.399 | 4.428 | 0.387 | 15 | 328287 | 327979 | 0.0041939 | 0.0041926 | 7 | 28712 | 28712 | 0.00038896 | 0.00038896 | 0 | 0 | 0 | No
CRO023 | Geelong CSC | Urban | 290 | 4.052 | 0.35 | 1.698 | 0.083 | 0.241 | 4 | 4863 | 4863 | 8.9965e-05 | 8.9965e-05 | 2 | 14034 | 14034 | 0.00015876 | 0.00015876 | 1 | 0.00038103 | 0.00038103 | No
CRO024 | Geelong CSC | Rural Short | 0 | 0.378 | 0.376 | 0.158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
CRO031 | Geelong CSC | Urban | 1 | 0.905 | 0 | 6.121 | 0 | 7.981 | 0 | 0 | 0 | 0 | 0 | 1 | 169 | 169 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | No
CRO032 | Geelong CSC | Rural Short | 4 | 2.03 | 0.176 | 0.118 | 0.006 | 0.007 | 1 | 156 | 156 | 5.292e-06 | 5.292e-06 | 1 | 180 | 180 | 3.969e-06 | 3.969e-06 | 0 | 0 | 0 | No
CRO033 | Geelong CSC | Urban | 19 | 1.978 | 0.289 | 2.488 | 7.791 | 0 | 4 | 6801 | 6801 | 3.1752e-05 | 3.1752e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES
CRO034 | Geelong CSC | Urban | 1073 | 6.391 | 0.276 | 4.383 | 3.2 | 0.203 | 2 | 127006 | 127006 | 0.00024608 | 0.00024608 | 2 | 8065 | 8065 | 3.3075e-05 | 3.3075e-05 | 1 | 0.0014262 | 0.0014262 | No
CTN001 | Bendigo CSC | Rural Long | 1653 | 852.891 | 1.149 | 6.454 | 23.041 | 5.561 | 39 | 952601 | 914641 | 0.0096341 | 0.0083257 | 51 | 229921 | 229921 | 0.0052616 | 0.0052616 | 7 | 0.015303 | 0.015303 | No
CTN002 | Bendigo CSC | Rural Long | 1158 | 516.081 | 0.893 | 2.47 | 15.448 | 2.573 | 34 | 1228544 | 1228544 | 0.008503 | 0.008503 | 31 | 204641 | 204641 | 0.0042998 | 0.0042998 | 7 | 0.010726 | 0.010726 | YES
CTN003 | Bendigo CSC | Rural Long | 1239 | 776.078 | 1.045 | 3.067 | 9.442 | 0.67 | 33 | 665650 | 665650 | 0.0046094 | 0.0046094 | 10 | 47212 | 47212 | 0.0033975 | 0.0033975 | 7 | 0.011477 | 0.011477 | No
CTN004 | Bendigo CSC | Rural Long | 1213 | 229.006 | 0.244 | 3.506 | 10.238 | 3.865 | 14 | 462645 | 462645 | 0.0032506 | 0.0032506 | 27 | 174668 | 174668 | 0.0039809 | 0.0039809 | 7 | 0.011231 | 0.011231 | No
CTN005 | Bendigo CSC | Rural Short | 660 | 8.032 | 0.503 | 1.793 | 3.812 | 0.209 | 4 | 253330 | 253330 | 0.0018244 | 0.0018244 | 2 | 13894 | 13894 | 0.0017503 | 0.0017503 | 8 | 0.0070133 | 0.0070133 | No
CTN006 | Bendigo CSC | Rural Long | 2047 | 988.09 | 0.708 | 5.936 | 34.281 | 6.066 | 43 | 1687749 | 1687749 | 0.012332 | 0.012332 | 57 | 298647 | 298647 | 0.005128 | 0.005128 | 9 | 0.022896 | 0.022896 | YES
DDL011 | Geelong CSC | Rural Short | 4151 | 36.052 | 6.26 | 9.043 | 2.024 | 0.623 | 22 | 189759 | 185643 | 0.0062671 | 0.0062592 | 5 | 58392 | 58392 | 0.00030958 | 0.00030958 | 0 | 0 | 0 | No
DDL012 | Geelong CSC | Rural Short | 3923 | 53.348 | 7.327 | 8.846 | 10.171 | 0.396 | 36 | 999232 | 625105 | 0.016449 | 0.014701 | 11 | 38941 | 38941 | 0.00037441 | 0.00037441 | 2 | 0.010379 | 0.010379 | No
DDL013 | Geelong CSC | Rural Short | 4229 | 68.039 | 5.18 | 7.503 | 1.836 | 0.059 | 21 | 196963 | 196963 | 0.0063055 | 0.0063055 | 2 | 6330 | 6330 | 0.00012833 | 0.00012833 | 6 | 0.033741 | 0.033741 | No
DDL014 | Geelong CSC | Rural Short | 2526 | 46.871 | 3.859 | 9.201 | 4.124 | 0.458 | 22 | 399694 | 399694 | 0.004309 | 0.004309 | 11 | 44385 | 44385 | 0.00032546 | 0.00032546 | 4 | 0.013148 | 0.013148 | No
DDL021 | Geelong CSC | Rural Short | 3334 | 65.367 | 3.555 | 8.372 | 1.566 | 3.032 | 22 | 138519 | 138519 | 0.00082953 | 0.00082953 | 12 | 268079 | 268079 | 0.0010306 | 0.0010306 | 2 | 0.0088165 | 0.0088165 | No
DDL022 | Geelong CSC | Urban | 3632 | 17.152 | 1.945 | 7.74 | 1.708 | 0.011 | 14 | 186934 | 186065 | 0.0015268 | 0.0015254 | 1 | 1245 | 1245 | 2.1168e-05 | 2.1168e-05 | 2 | 0.0095839 | 0.0095839 | No
DDL023 | Geelong CSC | Rural Short | 2786 | 43.998 | 3.176 | 7.069 | 2.288 | 2.027 | 20 | 180807 | 180807 | 0.0042429 | 0.0042429 | 8 | 160171 | 160171 | 0.0005345 | 0.0005345 | 2 | 0.0073427 | 0.0073427 | No
DDL024 | Geelong CSC | Rural Short | 2909 | 59.185 | 6.704 | 6.674 | 2.586 | 2.888 | 22 | 70298 | 69595 | 0.00050407 | 0.00050274 | 2 | 78521 | 78521 | 0.00035854 | 0.00035854 | 1 | 0.0038076 | 0.0038076 | No
DLF001 | # | Urban | 1176 | 0 | 0 | 4.134 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 1 | 480 | 480 | 5.292e-06 | 5.292e-06 | 0 | 0 | 0 | No
DLF004 | # | Urban | 0 | 0 | 2.302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
ECA001 | Shepparton CSC | Urban | 2184 | 23.329 | 2.284 | 7.888 | 0.323 | 0.313 | 8 | 14249 | 14249 | 0.00019316 | 0.00019316 | 2 | 13800 | 13800 | 0.00012304 | 0.00012304 | 0 | 0 | 0 | No
ECA003 | Shepparton CSC | Rural Short | 2441 | 61.025 | 3.225 | 9.561 | 0.318 | 0.028 | 17 | 13385 | 13385 | 0.00015612 | 0.00015612 | 1 | 1200 | 1200 | 5.292e-06 | 5.292e-06 | 2 | 0.0064669 | 0.0064669 | No
ECA005 | Shepparton CSC | Rural Short | 825 | 150.173 | 2.64 | 8.685 | 3.641 | 1.447 | 31 | 49166 | 49166 | 0.00056889 | 0.00056889 | 4 | 19535 | 19535 | 8.7319e-05 | 8.7319e-05 | 0 | 0 | 0 | No
ECA007 | Shepparton CSC | Rural Short | 2 | 25.968 | 0.981 | 6.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5.292e-06 | 5.292e-06 | No
ECA010 | Shepparton CSC | Rural Short | 1759 | 88.427 | 4.308 | 6.732 | 1.694 | 0.309 | 16 | 69857 | 69857 | 0.00072104 | 0.00072104 | 3 | 12762 | 12762 | 0.00010716 | 0.00010716 | 1 | 0.0023457 | 0.0023457 | No
ECA012 | Shepparton CSC | Rural Long | 1862 | 286.387 | 5.997 | 6.015 | 6.801 | 2.715 | 64 | 311877 | 311877 | 0.003539 | 0.003539 | 71 | 124486 | 124486 | 0.00077925 | 0.00077925 | 7 | 0.01731 | 0.01731 | No
EHK021 | Bendigo CSC | Urban | 279 | 10.024 | 4.175 | 9.402 | 12.205 | 2.218 | 3 | 85902 | 85902 | 0.00038235 | 0.00038235 | 3 | 15608 | 15608 | 5.292e-05 | 5.292e-05 | 0 | 0 | 0 | YES
EHK022 | Bendigo CSC | Urban | 801 | 10.386 | 3.184 | 4.462 | 0.452 | 0.391 | 4 | 10151 | 10151 | 0.00020771 | 0.00020771 | 3 | 8790 | 8790 | 3.4398e-05 | 3.4398e-05 | 0 | 0 | 0 | No
EHK023 | Bendigo CSC | Rural Long | 2583 | 296.835 | 4.159 | 8.047 | 3.607 | 1.193 | 43 | 171401 | 171401 | 0.0025018 | 0.0025018 | 17 | 56694 | 56694 | 0.00032943 | 0.00032943 | 1 | 0.0033697 | 0.0033697 | No
EHK024 | Bendigo CSC | Rural Long | 2734 | 865.757 | 2.215 | 9.202 | 33.62 | 4.028 | 86 | 1481459 | 1481459 | 0.014933 | 0.014933 | 46 | 177492 | 177492 | 0.00154 | 0.00154 | 0 | 0 | 0 | No
EHK031 | Bendigo CSC | Rural Short | 4966 | 70.382 | 6.768 | 10.836 | 2.311 | 3.727 | 14 | 221792 | 221792 | 0.006881 | 0.006881 | 28 | 357734 | 357734 | 0.0019078 | 0.0019078 | 1 | 0.006541 | 0.006541 | No
EHK032 | Bendigo CSC | Rural Short | 1301 | 21.605 | 0.765 | 3.984 | 0.089 | 0.085 | 3 | 5115 | 5115 | 8.5996e-05 | 8.5996e-05 | 3 | 4880 | 4880 | 4.4982e-05 | 4.4982e-05 | 1 | 0.0017318 | 0.0017318 | No
EHK033 | Bendigo CSC | Rural Short | 3512 | 44.675 | 7.293 | 12.549 | 0.774 | 1.614 | 11 | 30988 | 29692 | 0.00061917 | 0.00060858 | 6 | 64626 | 64626 | 0.00032414 | 0.00032414 | 1 | 0.0046358 | 0.0046358 | No
EHK034 | Bendigo CSC | Urban | 831 | 3.468 | 2.34 | 6.454 | 0.443 | 0.616 | 1 | 10168 | 10168 | 0.00010981 | 0.00010981 | 3 | 14145 | 14145 | 5.292e-05 | 5.292e-05 | 1 | 0.0010994 | 0.0010994 | No
ETSA001 | Warrnambool CSC | Rural Long | 308 | 29.642 | 0 | 0.711 | 0.929 | 0.003 | 12 | 113256 | 113256 | 0.0009142 | 0.0009142 | 1 | 424 | 424 | 1.0584e-05 | 1.0584e-05 | 0 | 0 | 0 | No
ETSA003 | Mildura CSC | Rural Short | 48 | 26.209 | 0 | 0 | 7.426 | 2.032 | 5 | 25436 | 25436 | 0.00028445 | 0.00028445 | 1 | 6960 | 6960 | 6.3504e-05 | 6.3504e-05 | 0 | 0 | 0 | YES
FNS011 | Geelong CSC | Rural Short | 2042 | 59.065 | 2.548 | 9.241 | 2.782 | 1.346 | 20 | 84515 | 84515 | 0.0030032 | 0.0030032 | 10 | 40890 | 40890 | 0.00023153 | 0.00023153 | 0 | 0 | 0 | No
FNS012 | Geelong CSC | Rural Short | 3355 | 32.998 | 6.389 | 8.214 | 5.671 | 1.344 | 9 | 299557 | 299189 | 0.006066 | 0.0060647 | 5 | 70976 | 70976 | 0.0003969 | 0.0003969 | 0 | 0 | 0 | No
FNS013 | Geelong CSC | Urban | 3 | 0.08 | 0 | 3.278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
FNS021 | Geelong CSC | Rural Short | 3156 | 67.664 | 5.246 | 13.466 | 11.963 | 0.269 | 21 | 731058 | 706491 | 0.016006 | 0.015825 | 5 | 16465 | 16465 | 0.00024608 | 0.00024608 | 0 | 0 | 0 | No
FNS022 | Geelong CSC | Rural Short | 1593 | 150.038 | 8.153 | 9.636 | 17.398 | 0.746 | 30 | 594776 | 594776 | 0.0074525 | 0.0074525 | 17 | 25520 | 25520 | 0.00022359 | 0.00022359 | 0 | 0 | 0 | No
FNS023 | Geelong CSC | Urban | 0 | 0.067 | 0 | 11.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
FNS032 | Geelong CSC | Rural Short | 230 | 41.356 | 2.553 | 4.147 | 2.419 | 34.627 | 12 | 30460 | 27632 | 0.00041013 | 0.00040087 | 12 | 435968 | 435968 | 0.0012674 | 0.0012674 | 0 | 0 | 0 | YES
GB011 | Geelong CSC | Urban | 6 | 0.608 | 1.483 | 5.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
GB012 | Geelong CSC | Rural Short | 17 | 3.276 | 0.602 | 0.869 | 0 | 0.079 | 0 | 0 | 0 | 0 | 0 | 1 | 600 | 600 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | No
GB014 | Geelong CSC | Urban | 463 | 2.514 | 1.597 | 3.238 | 0.035 | 0.501 | 1 | 976 | 976 | 6.615e-06 | 6.615e-06 | 4 | 13833 | 13833 | 6.615e-05 | 6.615e-05 | 0 | 0 | 0 | No
GB031 | Geelong CSC | Urban | 564 | 10.577 | 1.106 | 7.661 | 0.042 | 4.068 | 1 | 580 | 580 | 9.2611e-06 | 9.2611e-06 | 13 | 55915 | 55915 | 0.000213 | 0.000213 | 0 | 0 | 0 | No
GB032 | Geelong CSC | Urban | 3 | 1.198 | 0.197 | 5.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
GCY012 | Geelong CSC | Urban | 542 | 0.67 | 2.701 | 5.371 | 0.778 | 0 | 1 | 14461 | 151 | 4.2336e-05 | 2.646e-06 | 0 | 0 | 0 | 0 | 0 | 1 | 0.00071575 | 0.00071575 | No
GCY013 | Geelong CSC | Urban | 450 | 0.201 | 2.859 | 7.424 | 0.013 | 0 | 0 | 148 | 148 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
GCY014 | Geelong CSC | Urban | 2445 | 11.275 | 1.132 | 8.727 | 1.104 | 0.258 | 9 | 52124 | 43924 | 0.00049613 | 0.00046305 | 3 | 12177 | 12177 | 4.7628e-05 | 4.7628e-05 | 1 | 0.0044996 | 0.0044996 | No
GCY021 | Geelong CSC | Urban | 277 | 0 | 2.037 | 3.08 | 1.602 | 0.261 | 1 | 31506 | 31506 | 0.00039293 | 0.00039293 | 3 | 5127 | 5127 | 7.1442e-05 | 7.1442e-05 | 0 | 0 | 0 | No
GCY022 | Geelong CSC | Urban | 608 | 1.376 | 2.011 | 7.977 | 0.021 | 0 | 0 | 326 | 326 | 5.292e-06 | 5.292e-06 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0008163 | 0.0008163 | No
GCY023 | Geelong CSC | Urban | 3769 | 14.945 | 2.333 | 11.689 | 4.088 | 0.932 | 9 | 231499 | 230955 | 0.0033975 | 0.0033962 | 3 | 52804 | 52804 | 0.00019316 | 0.00019316 | 3 | 0.015004 | 0.015004 | No
GCY024 | Geelong CSC | Urban | 2190 | 8.195 | 1.432 | 5.41 | 2.568 | 2.936 | 10 | 185757 | 185757 | 0.0026315 | 0.0026315 | 18 | 212417 | 212417 | 0.00091817 | 0.00091817 | 0 | 0 | 0 | No
GL011 | Geelong CSC | Urban | 1322 | 5.107 | 1.009 | 5.45 | 0.123 | 0.164 | 1 | 5548 | 5548 | 8.4673e-05 | 8.4673e-05 | 1 | 7425 | 7425 | 4.3659e-05 | 4.3659e-05 | 2 | 0.0029834 | 0.0029834 | No
GL012 | Geelong CSC | Rural Long | 3673 | 236.462 | 13.281 | 11.808 | 25.982 | 3.304 | 52 | 1375525 | 905476 | 0.011805 | 0.0083998 | 37 | 174926 | 174926 | 0.0027386 | 0.0027386 | 4 | 0.019354 | 0.019354 | No
GL013 | Geelong CSC | Urban | 2051 | 7.766 | 1.121 | 4.739 | 0.313 | 0.227 | 4 | 34073 | 34073 | 0.00024079 | 0.00024079 | 3 | 24740 | 24740 | 0.00014553 | 0.00014553 | 2 | 0.0054495 | 0.0054495 | No
GL014 | Geelong CSC | Urban | 2272 | 11.299 | 0.3 | 3.831 | 0.876 | 1.621 | 8 | 106397 | 97117 | 0.0022253 | 0.0022015 | 7 | 196830 | 196830 | 0.001069 | 0.001069 | 2 | 0.0060276 | 0.0060276 | No
GL015 | Geelong CSC | Rural Long | 4091 | 367.811 | 8.369 | 12.677 | 8.922 | 10.606 | 75 | 543127 | 534892 | 0.0072276 | 0.0071906 | 110 | 645661 | 645661 | 0.0029609 | 0.0029609 | 2 | 0.0108 | 0.0108 | No
GL021 | Geelong CSC | Urban | 3955 | 15.221 | 7.94 | 8.925 | 6.176 | 2.018 | 8 | 545189 | 545189 | 0.004399 | 0.004399 | 14 | 178181 | 178181 | 0.0011894 | 0.0011894 | 0 | 0 | 0 | No
GL022 | Geelong CSC | Urban | 4798 | 13.248 | 1.006 | 11.215 | 9.385 | 1.498 | 11 | 857297 | 857297 | 0.0057948 | 0.0057948 | 23 | 136860 | 136860 | 0.00094198 | 0.00094198 | 0 | 0 | 0 | No
GL023 | Geelong CSC | Urban | 1229 | 5.717 | 2.149 | 5.055 | 2.406 | 0 | 2 | 104379 | 104379 | 0.0016895 | 0.0016895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
GL024 | Geelong CSC | Urban | 1469 | 5.84 | 1.571 | 6.832 | 1.294 | 0.254 | 7 | 58822 | 58822 | 0.00067606 | 0.00067606 | 2 | 11545 | 11545 | 0.00019581 | 0.00019581 | 0 | 0 | 0 | No
GLE011 | Geelong CSC | Urban | 250 | 5.442 | 0.442 | 3.673 | 0.067 | 0.144 | 3 | 893 | 893 | 7.9381e-06 | 7.9381e-06 | 2 | 1932 | 1932 | 7.9381e-06 | 7.9381e-06 | 0 | 0 | 0 | No
GLE012 | Geelong CSC | Urban | 2881 | 15.552 | 2.163 | 7.977 | 2.141 | 0.625 | 10 | 102556 | 102556 | 0.00068003 | 0.00068003 | 3 | 29945 | 29945 | 0.00018125 | 0.00018125 | 5 | 0.019116 | 0.019116 | No
GLE013 | Geelong CSC | Rural Short | 4114 | 42.164 | 3.507 | 8.214 | 5.985 | 1.475 | 20 | 624874 | 592606 | 0.011654 | 0.01157 | 21 | 153980 | 153980 | 0.00087848 | 0.00087848 | 4 | 0.021689 | 0.021689 | No
GLE021 | Geelong CSC | Urban | 575 | 3.85 | 0.853 | 6.871 | 3.25 | 9.886 | 3 | 43299 | 43299 | 0.00081762 | 0.00081762 | 4 | 131691 | 131691 | 0.00065754 | 0.00065754 | 0 | 0 | 0 | YES
GLE023 | Geelong CSC | Urban | 1 | 2.416 | 0.528 | 2.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
GLE024 | Geelong CSC | Rural Short | 4588 | 41.504 | 7.381 | 9.991 | 0.907 | 0.598 | 10 | 68985 | 68518 | 0.00045379 | 0.00045247 | 6 | 45487 | 45487 | 0.00030297 | 0.00030297 | 1 | 0.0060925 | 0.0060925 | No
GLE031 | Geelong CSC | Rural Short | 3369 | 30.183 | 5.121 | 9.754 | 6.841 | 1.362 | 9 | 375785 | 10183 | 0.0018641 | 8.0704e-05 | 10 | 74827 | 74827 | 0.00053185 | 0.00053185 | 1 | 0.0044294 | 0.0044294 | No
GLE032 | Geelong CSC | Urban | 2628 | 11.8 | 0.949 | 4.857 | 2.069 | 0.085 | 5 | 187778 | 187731 | 0.0049481 | 0.0049467 | 1 | 7685 | 7685 | 3.8367e-05 | 3.8367e-05 | 0 | 0 | 0 | No
GLE033 | Geelong CSC | Urban | 548 | 6.753 | 0.943 | 7.148 | 0.701 | 0 | 4 | 17707 | 17707 | 0.00054111 | 0.00054111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
GSB011 | Bendigo CSC | Rural Short | 2497 | 83.811 | 8.022 | 9.625 | 9.938 | 3.364 | 39 | 560365 | 560365 | 0.0059377 | 0.0059377 | 20 | 189698 | 189698 | 0.00092611 | 0.00092611 | 5 | 0.019923 | 0.019923 | No
GSB012 | Bendigo CSC | Rural Short | 1933 | 187.397 | 2.728 | 5.479 | 5.671 | 0.772 | 58 | 274530 | 259090 | 0.0059403 | 0.005722 | 23 | 37358 | 37358 | 0.00027915 | 0.00027915 | 4 | 0.010263 | 0.010263 | No
GSB013 | Bendigo CSC | Rural Short | 1750 | 45.65 | 7.607 | 3.572 | 7.523 | 1.092 | 21 | 333919 | 331918 | 0.003678 | 0.003674 | 7 | 48471 | 48471 | 0.00018125 | 0.00018125 | 6 | 0.010941 | 0.010941 | No
GSB014 | Bendigo CSC | Rural Short | 1935 | 84.642 | 7.494 | 5.721 | 9.537 | 0.064 | 41 | 708058 | 704166 | 0.0065145 | 0.0064655 | 2 | 4740 | 4740 | 5.6889e-05 | 5.6889e-05 | 3 | 0.0077039 | 0.0077039 | No
HSM001 | Horsham CSC | Rural Long | 1164 | 495.912 | 1.215 | 3.067 | 8.566 | 0.415 | 31 | 570167 | 569297 | 0.0013085 | 0.0013005 | 21 | 27605 | 27605 | 0.00046041 | 0.00046041 | 1 | 0.0015479 | 0.0015479 | No
HSM002 | Horsham CSC | Rural Long | 1387 | 679.292 | 2.404 | 2.988 | 8.297 | 0.174 | 53 | 733625 | 536698 | 0.0055434 | 0.0048025 | 8 | 15421 | 15421 | 0.00015876 | 0.00015876 | 1 | 0.0018377 | 0.0018377 | No
HSM003 | Horsham CSC | Rural Long | 1720 | 1003.046 | 0.376 | 6.055 | 9.489 | 0.072 | 40 | 569550 | 569550 | 0.0043276 | 0.0043276 | 3 | 4292 | 4292 | 3.7044e-05 | 3.7044e-05 | 0 | 0 | 0 | No
HSM004 | Horsham CSC | Rural Long | 2046 | 1084.667 | 0.327 | 4.82 | 4.615 | 6.237 | 61 | 377637 | 377637 | 0.0035787 | 0.0035787 | 98 | 510435 | 510435 | 0.0023378 | 0.0023378 | 0 | 0 | 0 | No
HSM005 | Horsham CSC | Rural Long | 1687 | 419.965 | 0.523 | 5.577 | 14.689 | 1.252 | 37 | 864533 | 864533 | 0.0053383 | 0.0053383 | 10 | 73681 | 73681 | 0.00041807 | 0.00041807 | 2 | 0.0044718 | 0.0044718 | No
HSM006 | Horsham CSC | Rural Long | 3004 | 287.543 | 5.138 | 9.999 | 4.814 | 6.309 | 16 | 257159 | 257159 | 0.0018893 | 0.0018893 | 29 | 336976 | 336976 | 0.001458 | 0.001458 | 2 | 0.0079645 | 0.0079645 | No
HSM009 | Horsham CSC | Urban | 3008 | 17.97 | 3.405 | 7.33 | 3.062 | 1.31 | 4 | 211128 | 211128 | 0.0042442 | 0.0042442 | 7 | 90336 | 90336 | 0.00061917 | 0.00061917 | 0 | 0 | 0 | No
HSM010 | Horsham CSC | Urban | 2945 | 20.729 | 2.141 | 11.274 | 10.012 | 0.614 | 14 | 444333 | 444333 | 0.011964 | 0.011964 | 6 | 27257 | 27257 | 0.00016538 | 0.00016538 | 0 | 0 | 0 | No
HTN001 | Warrnambool CSC | Rural Long | 801 | 302.479 | 0.073 | 5.213 | 43.414 | 9.881 | 47 | 703218 | 151945 | 0.0051253 | 0.0035959 | 15 | 160047 | 160047 | 0.0007475 | 0.0007475 | 1 | 0.0010558 | 0.0010558 | YES
HTN002 | Warrnambool CSC | Rural Long | 1919 | 1181.635 | 6.699 | 4.699 | 12.324 | 5.396 | 74 | 959314 | 701004 | 0.0088814 | 0.005943 | 30 | 420067 | 420067 | 0.002003 | 0.002003 | 0 | 0 | 0 | No
HTN003 | Warrnambool CSC | Rural Long | 1848 | 525.009 | 0.65 | 4.304 | 3.483 | 2.604 | 54 | 267050 | 267050 | 0.0062671 | 0.0062671 | 12 | 199638 | 199638 | 0.00075544 | 0.00075544 | 0 | 0 | 0 | No
HTN004 | Warrnambool CSC | Rural Long | 3310 | 370.217 | 1.251 | 9.122 | 15.443 | 16.982 | 32 | 876534 | 550725 | 0.0062036 | 0.0025666 | 29 | 963890 | 963890 | 0.0045406 | 0.0045406 | 5 | 0.021883 | 0.021883 | No
HTN005 | Warrnambool CSC | Rural Long | 2995 | 442.943 | 2.732 | 8.372 | 10.921 | 0.379 | 45 | 597501 | 340642 | 0.0096805 | 0.005472 | 8 | 20753 | 20753 | 0.00016273 | 0.00016273 | 1 | 0.0039637 | 0.0039637 | No
HTN006 | Warrnambool CSC | Rural Long | 2431 | 578.673 | 0.228 | 7.464 | 15.205 | 0.636 | 72 | 1039166 | 359240 | 0.011235 | 0.0083548 | 15 | 43448 | 43448 | 0.00029106 | 0.00029106 | 2 | 0.0064431 | 0.0064431 | No
HYT011 | Warrnambool CSC | Rural Short | 177 | 107.928 | 1.316 | 2.29 | 0 | 0 | 3 | 2231 | 481 | 0.00023682 | 5.292e-06 | 3 | 4803 | 4803 | 0.00025666 | 0.00025666 | 3 | 0.00069723 | 0.00069723 | No
KGT002 | Mildura CSC | Rural Short | 2168 | 55.383 | 0.646 | 7.239 | 1.481 | 5.967 | 17 | 67846 | 67496 | 0.0036568 | 0.0036541 | 13 | 273433 | 273433 | 0.0011523 | 0.0011523 | 1 | 0.0028855 | 0.0028855 | No
KGT003 | Mildura CSC | Rural Long | 1263 | 451.794 | 0.24 | 4.413 | 7.53 | 3.631 | 49 | 319733 | 319733 | 0.0048277 | 0.0048277 | 9 | 154182 | 154182 | 0.00065621 | 0.00065621 | 2 | 0.0033525 | 0.0033525 | No
KGT004 | Mildura CSC | Rural Long | 895 | 547.033 | 0.183 | 3.755 | 4.131 | 3.742 | 51 | 173305 | 173305 | 0.0015519 | 0.0015519 | 17 | 156982 | 156982 | 0.00073162 | 0.00073162 | 4 | 0.0047364 | 0.0047364 | No
KRT012 | Warrnambool CSC | Rural Long | 1020 | 298.663 | 0.193 | 4.344 | 12.096 | 6.501 | 40 | 586686 | 426405 | 0.0057247 | 0.0049944 | 30 | 315319 | 315319 | 0.0015201 | 0.0015201 | 1 | 0.0013521 | 0.0013521 | YES
KRT013 | Warrnambool CSC | Rural Long | 2404 | 580.427 | 2.196 | 8.056 | 4.935 | 15.978 | 86 | 190724 | 189774 | 0.0034398 | 0.0034345 | 35 | 617488 | 617488 | 0.0031091 | 0.0031091 | 0 | 0 | 0 | No
KRT022 | Warrnambool CSC | Rural Short | 2711 | 87.265 | 0.521 | 8.648 | 19.256 | 6.285 | 71 | 894662 | 890792 | 0.015735 | 0.015675 | 24 | 292020 | 292020 | 0.0016114 | 0.0016114 | 1 | 0.0035787 | 0.0035787 | No
KRT023 | Warrnambool CSC | Rural Short | 2877 | 27.203 | 2.054 | 7.7007 | 18.098 | 3.546 | 23 | 577751 | 565174 | 0.0096659 | 0.0096394 | 10 | 113189 | 113189 | 0.00054376 | 0.00054376 | 4 | 0.022601 | 0.022601 | No
KRT031 | Warrnambool CSC | Urban | 161 | 25.154 | 0.637 | 8.688 | 8.576 | 12.283 | 7 | 15127 | 15127 | 0.00015479 | 0.00015479 | 10 | 21667 | 21667 | 0.0003678 | 0.0003678 | 2 | 0.00042865 | 0.00042865 | No
KYM001 | Shepparton CSC | Rural Long | 1692 | 452.908 | 0.791 | 6.653 | 6.961 | 3.565 | 65 | 334279 | 334184 | 0.0075888 | 0.0075875 | 39 | 171185 | 171185 | 0.0019514 | 0.0019514 | 5 | 0.0092439 | 0.0092439 | No
KYM002 | Shepparton CSC | Rural Short | 1063 | 43.206 | 0.938 | 4.98 | 0.143 | 3.221 | 3 | 5053 | 5053 | 8.0704e-05 | 8.0704e-05 | 8 | 113644 | 113644 | 0.00055169 | 0.00055169 | 1 | 0.0014117 | 0.0014117 | No
KYM003 | Shepparton CSC | Rural Long | 1162 | 230.683 | 1.817 | 6.254 | 6.529 | 7.565 | 35 | 231794 | 225892 | 0.002482 | 0.0024436 | 53 | 268569 | 268569 | 0.0012529 | 0.0012529 | 4 | 0.0061282 | 0.0061282 | No
KYM004 | Shepparton CSC | Rural Long | 1530 | 293.662 | 0.881 | 6.095 | 27.511 | 2.006 | 71 | 1128857 | 1128857 | 0.006062 | 0.006062 | 9 | 82323 | 82323 | 0.00038632 | 0.00038632 | 4 | 0.0080704 | 0.0080704 | No
KYM005 | Shepparton CSC | Urban | 1931 | 12.572 | 1.966 | 6.294 | 0.607 | 3.899 | 8 | 40355 | 40355 | 0.00029238 | 0.00029238 | 18 | 259150 | 259150 | 0.0014474 | 0.0014474 | 2 | 0.0050962 | 0.0050962 | No
KYM006 | Shepparton CSC | Rural Short | 477 | 105.675 | 0.345 | 7.171 | 11.231 | 17.951 | 25 | 90190 | 90190 | 0.0016233 | 0.0016233 | 25 | 144156 | 144156 | 0.00056228 | 0.00056228 | 2 | 0.0012542 | 0.0012542 | No
LV001 | Sunshine CSC | Urban | 3517 | 13.582 | 10.983 | 10.544 | 0.247 | 0.897 | 7 | 14284 | 14284 | 0.00012172 | 0.00012172 | 3 | 51960 | 51960 | 0.00029371 | 0.00029371 | 3 | 0.013599 | 0.013599 | No
LV002 | Sunshine CSC | Rural Short | 6441 | 83.49 | 38.376 | 12.835 | 9.845 | 0.504 | 24 | 1499830 | 1499830 | 0.018218 | 0.018218 | 15 | 76797 | 76797 | 0.00035854 | 0.00035854 | 1 | 0.0088351 | 0.0088351 | No
LV003 | Sunshine CSC | Rural Short | 3327 | 20.84 | 11.988 | 3.396 | 0.001 | 0.505 | 0 | 82 | 82 | 1.323e-06 | 1.323e-06 | 2 | 54695 | 54695 | 0.00025137 | 0.00025137 | 0 | 0 | 0 | No
LV004 | Sunshine CSC | Urban | 5369 | 16.139 | 22.153 | 13.387 | 14.766 | 0.011 | 10 | 1008193 | 221134 | 0.01628 | 0.0019726 | 1 | 738 | 738 | 3.969e-06 | 3.969e-06 | 0 | 0 | 0 | No
LV005 | Sunshine CSC | Urban | 2373 | 6.941 | 15.485 | 9.794 | 3.577 | 0.296 | 2 | 133632 | 130882 | 0.0031474 | 0.0031448 | 2 | 11073 | 11073 | 3.3075e-05 | 3.3075e-05 | 1 | 0.0031289 | 0.0031289 | No
LV006 | Sunshine CSC | Urban | 3717 | 20.199 | 15.607 | 11.215 | 27.422 | 0.01 | 6 | 1046200 | 320820 | 0.010634 | 0.0076126 | 2 | 390 | 390 | 2.5137e-05 | 2.5137e-05 | 1 | 0.0032056 | 0.0032056 | YES
LV007 | Sunshine CSC | Urban | 3808 | 2.903 | 13.816 | 13.506 | 3.351 | 6.589 | 5 | 153511 | 152542 | 0.0044943 | 0.0044929 | 5 | 301827 | 301827 | 0.001286 | 0.001286 | 1 | 0.0071562 | 0.0071562 | No
LV008 | Sunshine CSC | Urban | 4144 | 8.41 | 20.743 | 13.466 | 6.561 | 0.841 | 6 | 344522 | 323618 | 0.0061414 | 0.0060898 | 4 | 44157 | 44157 | 0.00024476 | 0.00024476 | 0 | 0 | 0 | No
LV009 | Sunshine CSC | Urban | 4123 | 15.227 | 4.721 | 9.399 | 16.532 | 0.334 | 8 | 1641328 | 769751 | 0.016061 | 0.010597 | 1 | 33184 | 33184 | 0.00017993 | 0.00017993 | 1 | 0.0054865 | 0.0054865 | YES
LV010 | Sunshine CSC | Urban | 3281 | 1.07 | 19.975 | 10.268 | 0.649 | 0 | 2 | 35565 | 35565 | 0.0048726 | 0.0048726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
LVN001 | Sunshine CSC | Urban | 1 | 0 | 2.089 | 14.491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
LVN021 | Sunshine CSC | Urban | 21 | 4.874 | 0.621 | 6.235 | 0.91 | 5.769 | 3 | 745 | 745 | 6.615e-06 | 6.615e-06 | 3 | 4721 | 4721 | 1.9845e-05 | 1.9845e-05 | 1 | 3.0429e-05 | 3.0429e-05 | No
LVN022 | Sunshine CSC | Urban | 4557 | 28.014 | 5.621 | 15.121 | 33.287 | 0.396 | 26 | 1393247 | 1375495 | 0.019566 | 0.019258 | 4 | 16575 | 16575 | 8.4673e-05 | 8.4673e-05 | 0 | 0 | 0 | YES
LVN023 | Sunshine CSC | Urban | 135 | 5.055 | 1.903 | 11.652 | 0.521 | 0.343 | 1 | 636 | 636 | 7.9381e-06 | 7.9381e-06 | 2 | 419 | 419 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | No
LVN024 | Sunshine CSC | Urban | 369 | 10.762 | 20.107 | 17.909 | 0.339 | 9.586 | 0 | 856 | 856 | 3.969e-06 | 3.969e-06 | 5 | 24213 | 24213 | 5.1597e-05 | 5.1597e-05 | 1 | 0.00047099 | 0.00047099 | No
LVN031 | Sunshine CSC | Urban | 57 | 6.528 | 2.025 | 11.535 | 0.759 | 0 | 2 | 320 | 320 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
LVN032 | Sunshine CSC | Urban | 200 | 8.307 | 1 | 13.601 | 18.251 | 2.95 | 10 | 26570 | 26570 | 0.00011113 | 0.00011113 | 3 | 4294 | 4294 | 3.0429e-05 | 3.0429e-05 | 1 | 0.0002646 | 0.0002646 | No
LVN033 | Sunshine CSC | Urban | 128 | 5.033 | 0.43 | 7.833 | 1.003 | 1.945 | 3 | 1640 | 1640 | 1.0584e-05 | 1.0584e-05 | 2 | 3181 | 3181 | 1.1907e-05 | 1.1907e-05 | 0 | 0 | 0 | No
LVN034 | Sunshine CSC | Urban | 105 | 6.765 | 2.644 | 13.796 | 2.966 | 1.55 | 4 | 2611 | 2611 | 4.2336e-05 | 4.2336e-05 | 5 | 1365 | 1365 | 1.4553e-05 | 1.4553e-05 | 1 | 0.00014421 | 0.00014421 | No
MBN012 | Mildura CSC | Urban | 1949 | 12.889 | 3.344 | 4.94 | 0.115 | 0.708 | 5 | 6293 | 6293 | 9.1288e-05 | 9.1288e-05 | 6 | 38647 | 38647 | 0.00020639 | 0.00020639 | 1 | 0.003711 | 0.003711 | No
MBN013 | Mildura CSC | Rural Short | 448 | 39.352 | 0.448 | 2.948 | 7.358 | 0.167 | 18 | 253647 | 253647 | 0.0013032 | 0.0013032 | 2 | 5756 | 5756 | 3.1752e-05 | 3.1752e-05 | 1 | 0.00059138 | 0.00059138 | No
MBN014 | Mildura CSC | Rural Short | 809 | 87.158 | 0.704 | 4.342 | 3.694 | 1.199 | 19 | 118745 | 118745 | 0.0011735 | 0.0011735 | 7 | 38558 | 38558 | 0.00024079 | 0.00024079 | 4 | 0.0042826 | 0.0042826 | No
MBN021 | Mildura CSC | Rural Short | 1299 | 117.979 | 2.965 | 7.011 | 2.777 | 7.056 | 25 | 79368 | 79368 | 0.0020057 | 0.0020057 | 16 | 201656 | 201656 | 0.0012516 | 0.0012516 | 3 | 0.0051439 | 0.0051439 | No
MBN022 | Mildura CSC | Rural Short | 2177 | 49.954 | 3.405 | 6.892 | 2 | 1.865 | 15 | 106205 | 106205 | 0.0044308 | 0.0044308 | 17 | 99052 | 99052 | 0.0004313 | 0.0004313 | 2 | 0.0058503 | 0.0058503 | No
MBN023 | Mildura CSC | Rural Short | 1385 | 27.411 | 6.112 | 6.693 | 0.053 | 0.632 | 4 | 3687 | 3687 | 9.5257e-05 | 9.5257e-05 | 9 | 44188 | 44188 | 0.00047628 | 0.00047628 | 1 | 0.0036528 | 0.0036528 | No
MDA022 | Mildura CSC | Urban | 1769 | 7.61 | 3.005 | 10.915 | 1.408 | 0.677 | 8 | 40050 | 40050 | 0.0013336 | 0.0013336 | 3 | 19253 | 19253 | 7.6734e-05 | 7.6734e-05 | 0 | 0 | 0 | No
MDA023 | Mildura CSC | Rural Short | 2055 | 74.523 | 6.443 | 10.119 | 0.646 | 1.843 | 16 | 23023 | 23023 | 0.00029768 | 0.00029768 | 7 | 65705 | 65705 | 0.00053053 | 0.00053053 | 0 | 0 | 0 | No
MDA024 | Mildura CSC | Urban | 1184 | 29.885 | 2.281 | 9.88 | 3.466 | 6.326 | 6 | 74731 | 74731 | 0.00077528 | 0.00077528 | 10 | 136382 | 136382 | 0.00062711 | 0.00062711 | 1 | 0.0015453 | 0.0015453 | No
MDA031 | Mildura CSC | Urban | 1797 | 9.659 | 3.417 | 7.171 | 0.352 | 1.821 | 8 | 15668 | 15668 | 0.00012965 | 0.00012965 | 7 | 81036 | 81036 | 0.00034398 | 0.00034398 | 0 | 0 | 0 | No
MDA032 | Mildura CSC | Urban | 2027 | 11.073 | 2.21 | 7.967 | 2.094 | 0.083 | 13 | 77103 | 77103 | 0.0058609 | 0.0058609 | 2 | 3066 | 3066 | 2.9106e-05 | 2.9106e-05 | 1 | 0.0026963 | 0.0026963 | No
MDA033 | Mildura CSC | Urban | 1612 | 10.821 | 3.777 | 6.095 | 0.032 | 3.123 | 2 | 1324 | 1324 | 1.323e-05 | 1.323e-05 | 6 | 130224 | 130224 | 0.00069061 | 0.00069061 | 1 | 0.0021327 | 0.0021327 | No
MDA034 | Mildura CSC | Urban | 2505 | 7.838 | 7.401 | 11.194 | 2.41 | 0.026 | 9 | 89355 | 89355 | 0.0013521 | 0.0013521 | 2 | 968 | 968 | 6.615e-06 | 6.615e-06 | 1 | 0.0033194 | 0.0033194 | No
MLN011 | Sunshine CSC | Rural Short | 4088 | 70.628 | 6.822 | 8.922 | 9.487 | 6.081 | 23 | 748190 | 517497 | 0.0058556 | 0.0051028 | 19 | 479581 | 479581 | 0.0019369 | 0.0019369 | 2 | 0.010902 | 0.0054733 | No
MLN012 | Sunshine CSC | Rural Short | 3201 | 105.295 | 9.942 | 5.651 | 0.497 | 0.71 | 14 | 30615 | 30615 | 0.00016405 | 0.00016405 | 6 | 43775 | 43775 | 0.00022359 | 0.00022359 | 0 | 0 | 0 | No
MLN013 | Sunshine CSC | Rural Short | 3488 | 16.584 | 19.095 | 9.992 | 0.491 | 0.272 | 7 | 25879 | 25879 | 0.00010981 | 0.00010981 | 1 | 14341 | 14341 | 9.3934e-05 | 9.3934e-05 | 0 | 0 | 0 | No
MLN014 | Sunshine CSC | Rural Short | 4513 | 19.2 | 12.113 | 8.379 | 0.369 | 1.739 | 14 | 28267 | 28267 | 0.00021697 | 0.00021697 | 9 | 133217 | 133217 | 0.00084143 | 0.00084143 | 0 | 0 | 0 | No
MLN021 | Sunshine CSC | Rural Short | 891 | 80.48 | 4.248 | 5.274 | 6.894 | 0.021 | 16 | 148972 | 148972 | 0.0031474 | 0.0031474 | 1 | 450 | 450 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | No
MLN022 | Sunshine CSC | Rural Short | 4431 | 25.914 | 18.723 | 7.716 | 10.771 | 0.934 | 13 | 984307 | 984307 | 0.0066137 | 0.0066137 | 12 | 85341 | 85341 | 0.00076734 | 0.00076734 | 0 | 0 | 0 | No
MLN024 | Sunshine CSC | Urban | 1436 | 4.793 | 7.045 | 7.251 | 0.403 | 8.306 | 2 | 10348 | 10348 | 2.5137e-05 | 2.5137e-05 | 8 | 213384 | 213384 | 0.0010042 | 0.0010042 | 0 | 0 | 0 | No
MNA013 | Shepparton CSC | Urban | 643 | 34.642 | 1.397 | 11.632 | 0.406 | 2.744 | 5 | 2209 | 2209 | 4.2336e-05 | 4.2336e-05 | 2 | 14930 | 14930 | 9.7903e-05 | 9.7903e-05 | 1 | 0.00085466 | 0.00085466 | No
MNA014 | Shepparton CSC | Rural Long | 1562 | 229.929 | 2.785 | 9.003 | 31.13 | 3.63 | 44 | 781789 | 781789 | 0.0096977 | 0.0096977 | 9 | 91162 | 91162 | 0.00056492 | 0.00056492 | 2 | 0.004145 | 0.004145 | No
MNA021 | Shepparton CSC | Rural Short | 2525 | 151.452 | 2.097 | 11.513 | 21.932 | 5.326 | 34 | 867525 | 867525 | 0.0096064 | 0.0096064 | 17 | 210661 | 210661 | 0.00088245 | 0.00088245 | 7 | 0.023419 | 0.023419 | No
MNA022 | Shepparton CSC | Urban | 585 | 3.896 | 2.201 | 3.745 | 0.178 | 0.278 | 1 | 4094 | 4094 | 6.0858e-05 | 6.0858e-05 | 2 | 6411 | 6411 | 7.5411e-05 | 7.5411e-05 | 0 | 0 | 0 | No
MNA024 | Shepparton CSC | Rural Short | 1839 | 32.342 | 6.699 | 7.529 | 3.63 | 3.532 | 6 | 134672 | 134672 | 0.0025746 | 0.0025746 | 3 | 131054 | 131054 | 0.00046305 | 0.00046305 | 0 | 0 | 0 | No
MNA034 | Shepparton CSC | Rural Long | 2274 | 325.161 | 4.015 | 9.362 | 22.121 | 10.317 | 85 | 1067057 | 1064913 | 0.0149 | 0.014889 | 46 | 497660 | 497660 | 0.0022504 | 0.0022504 | 3 | 0.0090481 | 0.0090481 | No
MRO002 | Bendigo CSC | Urban | 2 | 0.776 | 0 | 1.115 | 5.397 | 0 | 2 | 1458 | 1458 | 5.292e-06 | 5.292e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES
MRO004 | Bendigo CSC | Rural Short | 1773 | 16.252 | 0.348 | 4.302 | 0.031 | 0 | 1 | 2442 | 93 | 0.00011642 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
MRO005 | Bendigo CSC | Rural Long | 1999 | 547.642 | 2.193 | 5.498 | 14.437 | 0.756 | 36 | 830095 | 830095 | 0.0091618 | 0.0091618 | 21 | 43491 | 43491 | 0.0016511 | 0.0016511 | 1 | 0.0026473 | 0.0026473 | No
MRO006 | Bendigo CSC | Urban | 1045 | 5.495 | 0.532 | 4.621 | 0.065 | 1.041 | 1 | 2128 | 2128 | 0.00013362 | 0.00013362 | 2 | 34300 | 34300 | 0.00012172 | 0.00012172 | 0 | 0 | 0 | No
MRO007 | Bendigo CSC | Rural Long | 2676 | 723.62 | 4.751 | 5.617 | 16.621 | 10.867 | 63 | 1202950 | 1088982 | 0.016628 | 0.015815 | 51 | 786475 | 786475 | 0.0028167 | 0.0028167 | 4 | 0.014138 | 0.014138 | No
MRO008 | Bendigo CSC | Rural Long | 2759 | 297.331 | 0.618 | 6.732 | 5.679 | 0.516 | 31 | 382972 | 382972 | 0.0041966 | 0.0041966 | 29 | 34789 | 34789 | 0.00030561 | 0.00030561 | 0 | 0 | 0 | No
NHL015 | Horsham CSC | Rural Long | 1625 | 1047.957 | 0.412 | 3.904 | 10.332 | 0.272 | 49 | 892747 | 892747 | 0.0085797 | 0.0085797 | 9 | 23469 | 23469 | 0.00016273 | 0.00016273 | 6 | 0.012853 | 0.012853 | No
NHL016 | Horsham CSC | Rural Long | 1390 | 290.495 | 0.489 | 4.024 | 8.356 | 0.072 | 28 | 487586 | 487586 | 0.006107 | 0.006107 | 5 | 4213 | 4213 | 3.5721e-05 | 3.5721e-05 | 4 | 0.0073744 | 0.0073744 | No
NHL031 | Horsham CSC | Rural Long | 1395 | 911.4 | 0.441 | 5.378 | 3.233 | 0.748 | 54 | 915140 | 915140 | 0.0048594 | 0.0048594 | 18 | 211606 | 211606 | 0.00095124 | 0.00095124 | 5 | 0.0092492 | 0.0092492 | No
NKA001 | Shepparton CSC | Rural Long | 1118 | 381.102 | 0.367 | 3.952 | 7.27 | 0.63 | 42 | 328617 | 328617 | 0.0040206 | 0.0040206 | 9 | 28483 | 28483 | 0.0001151 | 0.0001151 | 1 | 0.0015162 | 0.0015162 | No
NKA002 | Shepparton CSC | Rural Long | 1631 | 284.367 | 1.134 | 5.027 | 50.036 | 2.438 | 53 | 2654543 | 2654543 | 0.015462 | 0.015462 | 10 | 129358 | 129358 | 0.00064827 | 0.00064827 | 5 | 0.010794 | 0.010794 | YES
NKA003 | Shepparton CSC | Rural Short | 579 | 118.784 | 0.389 | 5.139 | 2.695 | 2.019 | 16 | 37933 | 37933 | 0.00095786 | 0.00095786 | 5 | 28413 | 28413 | 0.00016802 | 0.00016802 | 2 | 0.001712 | 0.001712 | No
NKA004 | Shepparton CSC | Rural Short | 2403 | 71.408 | 2.137 | 8.167 | 35.718 | 0.433 | 25 | 1396784 | 1396784 | 0.013311 | 0.013311 | 5 | 16933 | 16933 | 9.5257e-05 | 9.5257e-05 | 5 | 0.015917 | 0.015917 | No
NKA005 | Shepparton CSC | Rural Long | 890 | 215.082 | 0.832 | 5.298 | 10.997 | 0.647 | 50 | 313526 | 313526 | 0.0040616 | 0.0040616 | 9 | 18434 | 18434 | 8.335e-05 | 8.335e-05 | 2 | 0.0021777 | 0.0021777 | No
NKA006 | Shepparton CSC | Rural Long | 1383 | 412.424 | 2.671 | 7.131 | 55.276 | 6.467 | 74 | 1554897 | 1547032 | 0.01463 | 0.014441 | 33 | 181928 | 181928 | 0.00080174 | 0.00080174 | 12 | 0.021974 | 0.021974 | YES
OYN001 | Mildura CSC | Rural Long | 949 | 885.133 | 0.056 | 2.271 | 20.991 | 1.056 | 48 | 1819542 | 1725294 | 0.010114 | 0.0063359 | 3 | 91567 | 91567 | 0.00066812 | 0.00066812 | 2 | 0.0025111 | 0.0025111 | YES
OYN003 | Mildura CSC | Rural Long | 375 | 410.128 | 0.263 | 0.916 | 1.327 | 0.376 | 20 | 152651 | 115803 | 0.0035523 | 0.0020599 | 23 | 43255 | 43255 | 0.0002646 | 0.0002646 | 4 | 0.0019991 | 0.0019991 | No
OYN005 | Mildura CSC | Rural Long | 1356 | 1027.311 | 1.035 | 3.546 | 25.761 | 3.53 | 47 | 2048344 | 1902778 | 0.012779 | 0.0069775 | 14 | 280665 | 280665 | 0.0018363 | 0.0018363 | 4 | 0.0072091 | 0.0072091 | YES
OYN007 | Mildura CSC | Rural Short | 644 | 9.48 | 0 | 2.51 | 2.833 | 0 | 8 | 139700 | 77684 | 0.0045842 | 0.0020202 | 0 | 0 | 0 | 0 | 0 | 3 | 0.0025653 | 0.0025653 | No
PLD001 | Warrnambool CSC | Rural Long | 1843 | 310.661 | 1.215 | 5.805 | 16.661 | 12.477 | 48 | 943160 | 943160 | 0.0052629 | 0.0052629 | 38 | 706330 | 706330 | 0.0036819 | 0.0036819 | 1 | 0.0024343 | 0.0024343 | YES
PLD002 | Warrnambool CSC | Urban | 17 | 3.525 | 0.3 | 1.738 | 0.021 | 0 | 0 | 59 | 59 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 1 | 2.1168e-05 | 2.1168e-05 | No
PLD003 | Warrnambool CSC | Rural Long | 1107 | 451.234 | 1.118 | 1.58 | 1.646 | 4.559 | 50 | 176714 | 176714 | 0.0023126 | 0.0023126 | 32 | 489501 | 489501 | 0.0019157 | 0.0019157 | 0 | 0 | 0 | No
PLD004 | Warrnambool CSC | Rural Short | 2812 | 26.952 | 1.283 | 6.674 | 2.408 | 1.607 | 14 | 129464 | 129365 | 0.0057061 | 0.0057048 | 4 | 86422 | 86422 | 0.00042998 | 0.00042998 | 0 | 0 | 0 | No
PLD005 | Warrnambool CSC | Urban | 162 | 7.561 | 3.585 | 5.726 | 0.15 | 0 | 4 | 662 | 662 | 9.2611e-06 | 9.2611e-06 | 0 | 0 | 0 | 0 | 0 | 1 | 0.000213 | 0.000213 | No
PLD006 | Warrnambool CSC | Rural Short | 3241 | 137.277 | 1.319 | 5.331 | 6.06 | 2.191 | 57 | 578115 | 575572 | 0.0055461 | 0.005509 | 21 | 209029 | 209029 | 0.0010875 | 0.0010875 | 1 | 0.004309 | 0.004309 | No
RCT011 | Mildura CSC | Rural Short | 993 | 43.637 | 0.831 | 4.265 | 5.292 | 3.308 | 9 | 245185 | 245185 | 0.0015559 | 0.0015559 | 6 | 153287 | 153287 | 0.00051862 | 0.00051862 | 2 | 0.002642 | 0.002642 | No
RCT012 | Mildura CSC | Urban | 1 | 0.237 | 0.001 | 1.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
RCT013 | Mildura CSC | Rural Short | 639 | 135.697 | 0.416 | 11.215 | 7.64 | 0.477 | 18 | 93062 | 93062 | 0.0009949 | 0.0009949 | 5 | 5816 | 5816 | 4.4982e-05 | 4.4982e-05 | 4 | 0.0033895 | 0.0033895 | No
RCT014 | Mildura CSC | Rural Short | 365 | 77.12 | 1.457 | 12.479 | 2.535 | 0.267 | 9 | 13608 | 13608 | 8.9965e-05 | 8.9965e-05 | 3 | 1434 | 1434 | 1.0584e-05 | 1.0584e-05 | 1 | 0.0004829 | 0.0004829 | No
RCT015 | Mildura CSC | Rural Short | 437 | 8.626 | 0.087 | 2.33 | 12.905 | 0.123 | 9 | 207580 | 207580 | 0.0016696 | 0.0016696 | 2 | 1986 | 1986 | 1.0584e-05 | 1.0584e-05 | 3 | 0.0033829 | 0.0033829 | No
RCT021 | Mildura CSC | Rural Short | 898 | 66.603 | 0.254 | 6.634 | 7.366 | 3.234 | 19 | 221584 | 221584 | 0.0038791 | 0.0038791 | 15 | 97285 | 97285 | 0.00057815 | 0.00057815 | 1 | 0.0011867 | 0.0011867 | No
RCT022 | Mildura CSC | Rural Short | 422 | 182.025 | 0.487 | 5.812 | 6.386 | 5.505 | 9 | 104302 | 104302 | 0.00066018 | 0.00066018 | 7 | 89909 | 89909 | 0.00046041 | 0.00046041 | 1 | 0.0011153 | 0.0011153 | No
RCT023 | Mildura CSC | Rural Long | 2424 | 564.689 | 5.686 | 8.412 | 13.924 | 1.097 | 46 | 719166 | 719166 | 0.0046305 | 0.0046305 | 9 | 56650 | 56650 | 0.00047496 | 0.00047496 | 4 | 0.012845 | 0.012845 | No
RVL001 | Mildura CSC | Rural Short | 619 | 92.284 | 0.499 | 7.211 | 4.797 | 0.808 | 13 | 74973 | 74973 | 0.0014712 | 0.0014712 | 7 | 12634 | 12634 | 0.00010319 | 0.00010319 | 5 | 0.0040669 | 0.0040669 | No
RVL004 | Mildura CSC | Rural Short | 1255 | 41.489 | 0.773 | 10.278 | 0.486 | 3.106 | 14 | 9547 | 9547 | 0.00014024 | 0.00014024 | 3 | 61081 | 61081 | 0.00017331 | 0.00017331 | 6 | 0.0099847 | 0.0099847 | No
RVL006 | Mildura CSC | Urban | 63 | 10.053 | 0.018 | 5.179 | 0.637 | 0.157 | 6 | 2599 | 2599 | 4.8951e-05 | 4.8951e-05 | 1 | 640 | 640 | 2.646e-06 | 2.646e-06 | 5 | 0.00041542 | 0.00041542 | No
RVL008 | Mildura CSC | Rural Short | 153 | 52.23 | 0.317 | 7.569 | 2.58 | 2.242 | 12 | 12687 | 12687 | 0.00019977 | 0.00019977 | 5 | 11023 | 11023 | 6.7473e-05 | 6.7473e-05 | 6 | 0.0013521 | 0.0013521 | No
SA001 | Sunshine CSC | Rural Short | 1067 | 9.092 | 0.88 | 0.79 | 1.443 | 0.003 | 3 | 160209 | 160209 | 0.0026129 | 0.0026129 | 1 | 340 | 340 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | No
SA002 | Sunshine CSC | Rural Short | 3472 | 32.606 | 3.243 | 10.07 | 1.564 | 0 | 14 | 111763 | 99945 | 0.007737 | 0.0077078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SA003 | Sunshine CSC | Urban | 2988 | 3.928 | 11.402 | 8.767 | 4.235 | 0.097 | 9 | 277486 | 277486 | 0.0099398 | 0.0099398 | 1 | 6360 | 6360 | 5.292e-05 | 5.292e-05 | 0 | 0 | 0 | No
SA004 | Sunshine CSC | Urban | 3100 | 9.766 | 0.378 | 7.464 | 5.438 | 0.517 | 15 | 407904 | 375683 | 0.0089462 | 0.0088179 | 3 | 38749 | 38749 | 0.00012039 | 0.00012039 | 3 | 0.014557 | 0.0048515 | No
SA005 | Sunshine CSC | Urban | 3502 | 5.884 | 7.092 | 9.083 | 4.313 | 0.51 | 7 | 271879 | 20867 | 0.0048422 | 0.00013495 | 5 | 32136 | 32136 | 0.00023153 | 0.00023153 | 0 | 0 | 0 | No
SA006 | Sunshine CSC | Urban | 1252 | 6.562 | 6.357 | 3.949 | 0.449 | 0 | 4 | 28169 | 28169 | 0.00026725 | 0.00026725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SA007 | Sunshine CSC | Urban | 7331 | 12.791 | 16.097 | 17.139 | 23.817 | 3.201 | 16 | 1766975 | 694433 | 0.021763 | 0.011298 | 5 | 237446 | 237446 | 0.0011166 | 0.0011166 | 3 | 0.031349 | 0.031349 | YES
SA008 | Sunshine CSC | Rural Short | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SA009 | Sunshine CSC | Urban | 4302 | 11.752 | 16.247 | 11.571 | 11.351 | 1.167 | 9 | 828328 | 293796 | 0.015928 | 0.011986 | 3 | 85195 | 85195 | 0.00052788 | 0.00052788 | 0 | 0 | 0 | No
SA010 | Sunshine CSC | Urban | 2535 | 4.44 | 11.063 | 8.175 | 8.674 | 0.04 | 18 | 495742 | 494607 | 0.012845 | 0.012842 | 1 | 2310 | 2310 | 4.3659e-05 | 4.3659e-05 | 0 | 0 | 0 | No
SA011 | Sunshine CSC | Urban | 4207 | 5.923 | 18.317 | 10.702 | 12.148 | 0 | 8 | 1075012 | 1075012 | 0.022801 | 0.022801 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0056096 | 0.0056096 | No
SA012 | Sunshine CSC | Urban | 269 | 8.521 | 4.241 | 9.596 | 12.641 | 0.028 | 5 | 64656 | 64656 | 0.0011325 | 0.0011325 | 1 | 145 | 145 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | No
SHL001 | Mildura CSC | Rural Long | 363 | 419.945 | 0.042 | 1.269 | 6.928 | 4.352 | 25 | 257292 | 257292 | 0.0018945 | 0.0018945 | 16 | 161619 | 161619 | 0.00063108 | 0.00063108 | 2 | 0.00095918 | 0.00095918 | YES
SHL002 | Mildura CSC | Rural Long | 1302 | 453.029 | 0.79 | 10.035 | 4.646 | 6.821 | 27 | 109310 | 109310 | 0.0008335 | 0.0008335 | 26 | 160507 | 160507 | 0.0026923 | 0.0026923 | 1 | 0.0017212 | 0.0017212 | No
SHL004 | Mildura CSC | Rural Short | 1398 | 178.636 | 2.224 | 8.131 | 11.299 | 7.175 | 42 | 333476 | 332716 | 0.0066349 | 0.0066243 | 53 | 211773 | 211773 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | No
SHL005 | Mildura CSC | Rural Long | 1684 | 236.905 | 0.85 | 5.989 | 4.721 | 4.202 | 34 | 223222 | 223222 | 0.0019104 | 0.0019104 | 32 | 198686 | 198686 | 0.00088377 | 0.00088377 | 0 | 0 | 0 | No
SHL007 | Mildura CSC | Urban | 1986 | 15.936 | 1.509 | 9.757 | 0.307 | 0.364 | 5 | 9950 | 9950 | 0.0001323 | 0.0001323 | 3 | 11830 | 11830 | 5.9535e-05 | 5.9535e-05 | 2 | 0.0052709 | 0.0052709 | No
SHL008 | Mildura CSC | Urban | 2524 | 19.614 | 1.565 | 9.995 | 2.951 | 4.801 | 11 | 116357 | 116357 | 0.0042985 | 0.0042985 | 21 | 189291 | 189291 | 0.0013283 | 0.0013283 | 3 | 0.01003 | 0.01003 | No
SHN011 | Shepparton CSC | Rural Long | 1462 | 319.838 | 5.454 | 7.051 | 44.658 | 4.812 | 62 | 1262877 | 1253239 | 0.0094397 | 0.009306 | 18 | 136082 | 136082 | 0.00061388 | 0.00061388 | 2 | 0.0038817 | 0.0038817 | YES
SHN012 | Shepparton CSC | Urban | 2572 | 10.55 | 0.403 | 7.25 | 0.408 | 0.398 | 8 | 27750 | 27750 | 0.00038764 | 0.00038764 | 1 | 27033 | 27033 | 0.00012965 | 0.00012965 | 0 | 0 | 0 | No
SHN014 | Shepparton CSC | Urban | 352 | 11.447 | 0.907 | 5.816 | 4.768 | 0 | 1 | 45777 | 45777 | 0.00047496 | 0.00047496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SHN021 | Shepparton CSC | Rural Short | 1986 | 31.55 | 5.399 | 5.737 | 3.713 | 0.093 | 21 | 234321 | 234321 | 0.0030403 | 0.0030403 | 2 | 5890 | 5890 | 6.8796e-05 | 6.8796e-05 | 1 | 0.0026592 | 0.0026592 | No
SHN022 | Shepparton CSC | Urban | 1967 | 8.155 | 2.728 | 7.928 | 0.244 | 0 | 7 | 11291 | 10409 | 0.000213 | 0.00018522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SHN023 | Shepparton CSC | Urban | 822 | 6.021 | 2.136 | 4.422 | 0.64 | 0.338 | 2 | 21004 | 21004 | 6.3504e-05 | 6.3504e-05 | 2 | 11090 | 11090 | 7.5411e-05 | 7.5411e-05 | 4 | 0.0043739 | 0.0043739 | No
SHN024 | Shepparton CSC | Rural Short | 1094 | 151.208 | 1.189 | 5.976 | 6.968 | 0.31 | 19 | 174911 | 174911 | 0.0016035 | 0.0016035 | 10 | 7792 | 7792 | 5.1597e-05 | 5.1597e-05 | 1 | 0.00145 | 0.00145 | No
SHP011 | Shepparton CSC | Rural Short | 787 | 134.401 | 0.431 | 7.29 | 8.775 | 6.214 | 29 | 108046 | 108046 | 0.00145 | 0.00145 | 8 | 76519 | 76519 | 0.00035721 | 0.00035721 | 0 | 0 | 0 | No
SHP012 | Shepparton CSC | Rural Long | 2270 | 371.55 | 0.699 | 8.525 | 21.621 | 10.976 | 65 | 954097 | 954089 | 0.0089713 | 0.00897 | 71 | 484373 | 484373 | 0.0025905 | 0.0025905 | 6 | 0.017973 | 0.017973 | No
SHP014 | Shepparton CSC | Rural Long | 1691 | 301.016 | 0.188 | 6.215 | 6.473 | 0.584 | 43 | 286789 | 286789 | 0.0036105 | 0.0036105 | 11 | 25858 | 25858 | 0.00011642 | 0.00011642 | 0 | 0 | 0 | No
SHP021 | Shepparton CSC | Rural Long | 684 | 350.687 | 3.563 | 5.498 | 12.92 | 2.566 | 41 | 154425 | 154425 | 0.0033036 | 0.0033036 | 17 | 30670 | 30670 | 0.00027651 | 0.00027651 | 2 | 0.0018112 | 0.0018112 | No
SSE011 | Sunshine CSC | Urban | 1090 | 8.781 | 2.286 | 13.523 | 6.789 | 1.082 | 4 | 70813 | 70813 | 0.0015122 | 0.0015122 | 3 | 11291 | 11291 | 6.0858e-05 | 6.0858e-05 | 0 | 0 | 0 | No
SSE012 | Sunshine CSC | Urban | 3224 | 10.96 | 3.735 | 7.249 | 6.141 | 2.473 | 7 | 415964 | 366543 | 0.0089025 | 0.0088059 | 3 | 167548 | 167548 | 0.00050407 | 0.00050407 | 0 | 0 | 0 | No
SSE013 | Sunshine CSC | Urban | 1966 | 6.358 | 3.177 | 10.288 | 7.24 | 0 | 8 | 217452 | 216855 | 0.0031818 | 0.0031157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SSE014 | Sunshine CSC | Urban | 3698 | 15.862 | 3.722 | 10.951 | 13.097 | 1.021 | 18 | 517844 | 450644 | 0.0063835 | 0.0058861 | 3 | 40364 | 40364 | 0.00014553 | 0.00014553 | 1 | 0.0049269 | 0.0049269 | No
SSE031 | Sunshine CSC | Urban | 4752 | 22.819 | 9.324 | 9.938 | 15.115 | 0.158 | 12 | 1077207 | 1076640 | 0.013401 | 0.013398 | 1 | 11250 | 11250 | 5.9535e-05 | 5.9535e-05 | 1 | 0.0053119 | 0.0053119 | No
SSE032 | Sunshine CSC | Urban | 2669 | 16.885 | 3.485 | 10.055 | 2.11 | 0.879 | 8 | 87005 | 86747 | 0.0037587 | 0.0037573 | 5 | 36237 | 36237 | 0.00018787 | 0.00018787 | 0 | 0 | 0 | No
SSE033 | Sunshine CSC | Urban | 1314 | 9.472 | 1.821 | 5.534 | 11.326 | 0 | 4 | 229916 | 5773 | 0.0018112 | 6.3504e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SSE034 | Sunshine CSC | Urban | 2366 | 12.546 | 1.008 | 10.561 | 14.313 | 0.903 | 21 | 417234 | 416356 | 0.0051465 | 0.0051452 | 5 | 26322 | 26322 | 0.00014553 | 0.00014553 | 1 | 0.0031104 | 0.0031104 | No
STL004 | Horsham CSC | Urban | 1588 | 15.172 | 0.123 | 5.059 | 17.968 | 1.646 | 8 | 718033 | 718033 | 0.0097532 | 0.0097532 | 12 | 65761 | 65761 | 0.000385 | 0.000385 | 2 | 0.0042151 | 0.0042151 | YES
STL005 | Horsham CSC | Rural Long | 2589 | 314.723 | 0.774 | 7.33 | 42.418 | 1.975 | 33 | 2579429 | 2579429 | 0.018875 | 0.018875 | 12 | 120123 | 120123 | 0.00050274 | 0.00050274 | 0 | 0 | 0 | YES
STL006 | Horsham CSC | Rural Long | 1648 | 929.534 | 3.555 | 4.661 | 13.679 | 4.684 | 51 | 759007 | 759007 | 0.0078904 | 0.0078904 | 60 | 259879 | 259879 | 0.0013627 | 0.0013627 | 0 | 0 | 0 | No
STL007 | Horsham CSC | Rural Long | 823 | 353.693 | 1 | 6.175 | 32.251 | 0.133 | 24 | 414985 | 414985 | 0.0036978 | 0.0036978 | 1 | 1710 | 1710 | 2.5137e-05 | 2.5137e-05 | 2 | 0.0021684 | 0.0021684 | No
STN011 | Shepparton CSC | Rural Long | 1040 | 289.913 | 0.961 | 5.976 | 6.401 | 0.089 | 34 | 182680 | 182680 | 0.00090758 | 0.00090758 | 5 | 2531 | 2531 | 2.5137e-05 | 2.5137e-05 | 3 | 0.0041291 | 0.0041291 | No
STN012 | Shepparton CSC | Urban | 3013 | 16.127 | 10.989 | 9.481 | 5.253 | 0.426 | 11 | 302704 | 302704 | 0.0064364 | 0.0064364 | 4 | 24561 | 24561 | 0.00020771 | 0.00020771 | 0 | 0 | 0 | No
STN013 | Shepparton CSC | Urban | 3 | 0.183 | 0.967 | 6.254 | 0 | 4.151 | 0 | 0 | 0 | 0 | 0 | 1 | 324 | 324 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | No
STN014 | Shepparton CSC | Urban | 632 | 4.373 | 2.015 | 8.645 | 6.131 | 0 | 3 | 88958 | 88958 | 0.0009486 | 0.0009486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
STN021 | Shepparton CSC | Rural Short | 1814 | 122.12 | 3.972 | 5.577 | 7.528 | 0.131 | 22 | 420043 | 419958 | 0.0038288 | 0.0038275 | 3 | 7315 | 7315 | 4.2336e-05 | 4.2336e-05 | 2 | 0.0048052 | 0.0048052 | No
STN022 | Shepparton CSC | Urban | 2858 | 13.614 | 0.843 | 8.127 | 3.337 | 0.353 | 8 | 222020 | 222020 | 0.0012066 | 0.0012066 | 3 | 23471 | 23471 | 0.00015612 | 0.00015612 | 1 | 0.0037653 | 0.0037653 | No
STN023 | Shepparton CSC | Urban | 308 | 1.338 | 2.885 | 5.577 | 0.007 | 0.72 | 0 | 75 | 75 | 1.323e-06 | 1.323e-06 | 3 | 8028 | 8028 | 0.00045644 | 0.00045644 | 2 | 0.00081894 | 0.00081894 | No
STN024 | Shepparton CSC | Rural Long | 1223 | 218.974 | 2.22 | 9.402 | 4.114 | 5.897 | 20 | 86605 | 86605 | 0.00060858 | 0.00060858 | 10 | 124132 | 124132 | 0.00048158 | 0.00048158 | 2 | 0.0032189 | 0.0032189 | No
SU001 | Sunshine CSC | Urban | 86 | 7.465 | 4.17 | 9.318 | 5.224 | 13.652 | 1 | 4702 | 159 | 1.0584e-05 | 1.323e-06 | 5 | 12287 | 12287 | 2.5137e-05 | 2.5137e-05 | 0 | 0 | 0 | No
SU002 | Sunshine CSC | Urban | 1520 | 0 | 0 | 11.284 | 22.877 | 0.012 | 5 | 532233 | 22016 | 0.0045578 | 0.00055169 | 1 | 275 | 275 | 7.2765e-05 | 7.2765e-05 | 0 | 0 | 0 | YES
SU003 | Sunshine CSC | Urban | 5022 | 8.389 | 15.009 | 13.722 | 2.594 | 0.168 | 17 | 462185 | 397097 | 0.015002 | 0.014703 | 2 | 29880 | 29880 | 0.00019184 | 0.00019184 | 2 | 0.013705 | 0.0068717 | No
SU004 | Sunshine CSC | Urban | 2765 | 14.825 | 3.035 | 9.043 | 25.763 | 3.68 | 19 | 835810 | 230791 | 0.0098763 | 0.00752 | 6 | 119380 | 119380 | 0.00047496 | 0.00047496 | 1 | 0.0031818 | 0.0031818 | YES
SU005 | Sunshine CSC | Urban | 2211 | 0 | 0 | 15.177 | 30.278 | 2.012 | 8 | 607250 | 607250 | 0.013798 | 0.013798 | 5 | 40361 | 40361 | 0.00024873 | 0.00024873 | 0 | 0 | 0 | YES
SU008 | Sunshine CSC | Urban | 6562 | 19.329 | 22.733 | 17.654 | 3.304 | 2.058 | 17 | 154869 | 154869 | 0.0061335 | 0.0061335 | 4 | 96465 | 96465 | 0.00034266 | 0.00034266 | 0 | 0 | 0 | No
SU009 | Sunshine CSC | Urban | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU010 | Sunshine CSC | Rural Short | 0 | 0 | 3.464 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU011 | Sunshine CSC | Rural Short | 0 | 0.32 | 0.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU012 | Sunshine CSC | Urban | 1507 | 10.1 | 12.383 | 11.284 | 0 | 0 | 0 | 179 | 179 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU013 | Sunshine CSC | Urban | 1263 | 4.936 | 19.52 | 11.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU015 | Sunshine CSC | Urban | 2495 | 8.135 | 31.136 | 15.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU027 | Sunshine CSC | Urban | 284 | 0.313 | 8.542 | 4.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
SU097 | Sunshine CSC | Rural Short | 1237 | 0 | 0 | 11.874 | 0.412 | 0.056 | 2 | 13568 | 13568 | 7.5411e-05 | 7.5411e-05 | 2 | 1851 | 1851 | 2.646e-06 | 2.646e-06 | 0 | 0 | 0 | No
TRG001 | Warrnambool CSC | Rural Short | 439 | 117.486 | 0 | 2.211 | 0.51 | 0.187 | 17 | 18133 | 18133 | 0.00023285 | 0.00023285 | 1 | 6650 | 6650 | 3.0429e-05 | 3.0429e-05 | 0 | 0 | 0 | No
TRG002 | Warrnambool CSC | Rural Long | 2005 | 722.111 | 2.432 | 7.227 | 7.889 | 0.654 | 57 | 385766 | 276712 | 0.0041238 | 0.0036634 | 11 | 31957 | 31957 | 0.00034927 | 0.00034927 | 3 | 0.0079658 | 0.0079658 | No
TRG003 | Warrnambool CSC | Rural Long | 1666 | 346.45 | 1.285 | 7.819 | 12.712 | 0.397 | 81 | 412056 | 237393 | 0.0047827 | 0.002945 | 12 | 12873 | 12873 | 0.00019845 | 0.00019845 | 4 | 0.0087914 | 0.0065899 | No
TRG004 | Warrnambool CSC | Rural Short | 1566 | 158.121 | 0 | 5.884 | 8.955 | 4.304 | 21 | 422181 | 408187 | 0.0038156 | 0.0037679 | 9 | 202910 | 202910 | 0.00084408 | 0.00084408 | 0 | 0 | 0 | No
TRG005 | Warrnambool CSC | Rural Long | 1076 | 239.258 | 0.802 | 5.726 | 12.079 | 10.332 | 50 | 347354 | 347077 | 0.0032705 | 0.0032692 | 21 | 297105 | 297105 | 0.0012383 | 0.0012383 | 1 | 0.0014222 | 0.0014222 | No
WBE011 | Sunshine CSC | Urban | 2912 | 11.956 | 2.213 | 7.369 | 0.735 | 0.016 | 5 | 45932 | 31037 | 0.00039293 | 0.00037177 | 2 | 980 | 980 | 5.292e-06 | 5.292e-06 | 0 | 0 | 0 | No
WBE012 | Sunshine CSC | Urban | 4072 | 3.84 | 18.926 | 9.26 | 2.875 | 0 | 6 | 307119 | 307119 | 0.0055394 | 0.0055394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
WBE013 | Sunshine CSC | Urban | 5370 | 9.585 | 25.719 | 11.27 | 2.044 | 0.769 | 6 | 157246 | 98726 | 0.00037441 | 0.00025799 | 6 | 59139 | 59139 | 0.000385 | 0.000385 | 1 | 0.0071112 | 0 | No
WBE014 | Sunshine CSC | Rural Short | 3503 | 10.865 | 13.874 | 7.306 | 0.021 | 0 | 2 | 1846 | 1846 | 0.00014288 | 0.00014288 | 0 | 0 | 0 | 0 | 0 | 1 | 0.0047139 | 0.0047139 | No
WBE021 | Sunshine CSC | Urban | 2151 | 5.217 | 3.878 | 10.521 | 0.007 | 0.399 | 0 | 295 | 295 | 2.646e-06 | 2.646e-06 | 2 | 16700 | 16700 | 0.00014421 | 0.00014421 | 0 | 0 | 0 | No
WBE022 | Sunshine CSC | Urban | 1447 | 9.064 | 3.183 | 7.566 | 0.991 | 0.013 | 4 | 33793 | 33793 | 0.00024343 | 0.00024343 | 1 | 440 | 440 | 2.646e-06 | 2.646e-06 | 2 | 0.00385 | 0.00385 | No
WBE023 | Sunshine CSC | Rural Short | 3221 | 43.571 | 11.962 | 7.369 | 0.208 | 0.072 | 5 | 24378 | 24378 | 0.00016405 | 0.00016405 | 4 | 8477 | 8477 | 0.00010055 | 0.00010055 | 4 | 0.016933 | 0.0042138 | No
WBE024 | Sunshine CSC | Urban | 3039 | 15.157 | 3.2 | 15.959 | 31.094 | 0.282 | 12 | 893745 | 325571 | 0.012279 | 0.0082648 | 4 | 8119 | 8119 | 0.00015347 | 0.00015347 | 1 | 0.004063 | 0.004063 | YES
WBE031 | Sunshine CSC | Urban | 3966 | 16.455 | 3.644 | 8.748 | 1.221 | 0 | 6 | 857836 | 122709 | 0.0094238 | 0.0048845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
WBE032 | Sunshine CSC | Rural Short | 4927 | 40.96 | 17.604 | 9.93 | 0.453 | 0.101 | 12 | 455686 | 455686 | 0.0063637 | 0.0063637 | 6 | 101675 | 101675 | 0.0003625 | 0.0003625 | 1 | 0.0061388 | 0.0061388 | No
WBE033 | Sunshine CSC | Urban | 3154 | 26.047 | 3.372 | 9.457 | 0.76 | 3.793 | 3 | 51586 | 27369 | 0.00027254 | 0.00021168 | 7 | 257603 | 257603 | 0.0010174 | 0.0010174 | 0 | 0 | 0 | No
WBE034 | Sunshine CSC | Rural Short | 2351 | 56.246 | 6.669 | 10.521 | 18.041 | 0.063 | 18 | 609613 | 52813 | 0.0024568 | 0.00060197 | 2 | 2136 | 2136 | 3.3075e-05 | 3.3075e-05 | 0 | 0 | 0 | No
WBL002 | Warrnambool CSC | Rural Short | 1848 | 158.806 | 1.396 | 14.454 | 13.5 | 9.247 | 42 | 203016 | 183303 | 0.0059363 | 0.005722 | 12 | 139055 | 139055 | 0.00065489 | 0.00065489 | 0 | 0 | 0 | No
WBL003 | Warrnambool CSC | Urban | 1773 | 12.859 | 6.911 | 7.227 | 1.382 | 3.757 | 2 | 55023 | 55023 | 0.0023378 | 0.0023378 | 8 | 149590 | 149590 | 0.00078322 | 0.00078322 | 1 | 0.0023338 | 0.0023338 | No
WBL004 | Warrnambool CSC | Urban | 1963 | 19.357 | 3.56 | 9.754 | 11.066 | 0.149 | 23 | 283138 | 271158 | 0.0061216 | 0.0059853 | 4 | 3805 | 3805 | 3.1752e-05 | 3.1752e-05 | 2 | 0.0051915 | 0.0051915 | No
WBL005 | Warrnambool CSC | Rural Short | 2045 | 157.853 | 3.826 | 5.884 | 13.638 | 1.93 | 34 | 887635 | 887215 | 0.0083548 | 0.008327 | 10 | 125640 | 125640 | 0.00056625 | 0.00056625 | 2 | 0.0054495 | 0.0054495 | No
WBL006 | Warrnambool CSC | Rural Short | 1388 | 14.024 | 0.708 | 4.226 | 0 | 0 | 0 | 89 | 89 | 1.323e-06 | 1.323e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
WBL008 | Warrnambool CSC | Urban | 2282 | 10.877 | 1.087 | 5.805 | 2.499 | 0.135 | 6 | 157564 | 133358 | 0.004055 | 0.0039346 | 2 | 8490 | 8490 | 0.00031355 | 0.00031355 | 2 | 0.0060488 | 0.0060488 | No
WBL010 | Warrnambool CSC | Urban | 1112 | 5.617 | 1.172 | 9.399 | 1.681 | 1.211 | 2 | 35179 | 35179 | 0.0014791 | 0.0014791 | 5 | 25335 | 25335 | 0.00018654 | 0.00018654 | 0 | 0 | 0 | No
WBL012 | Warrnambool CSC | Rural Long | 2558 | 263.242 | 1.002 | 10.939 | 13.224 | 12.761 | 85 | 505468 | 498808 | 0.010794 | 0.010719 | 37 | 487768 | 487768 | 0.0021327 | 0.0021327 | 0 | 0 | 0 | No
WIN011 | Ballarat CSC | Rural Long | 1495 | 312.613 | 9.13 | 3.87 | 8.007 | 23.176 | 27 | 133416 | 64736 | 0.0025362 | 0.0024634 | 52 | 386163 | 386163 | 0.0016868 | 0.0016868 | 5 | 0.0098921 | 0.0098921 | No
WIN012 | Ballarat CSC | Rural Long | 999 | 209.031 | 7.948 | 3.554 | 12.205 | 3.42 | 35 | 287218 | 287218 | 0.0044969 | 0.0044969 | 13 | 80482 | 80482 | 0.00048554 | 0.00048554 | 4 | 0.0053 | 0.0053 | No
WIN013 | Ballarat CSC | Rural Short | 756 | 134.055 | 4.643 | 2.054 | 17.243 | 5.675 | 13 | 246229 | 246229 | 0.0011563 | 0.0011563 | 7 | 81044 | 81044 | 0.00042469 | 0.00042469 | 4 | 0.00401 | 0.00401 | No
WMN014 | Mildura CSC | Rural Short | 139 | 62.118 | 1.407 | 9.399 | 10.182 | 36.455 | 12 | 27238 | 12334 | 0.0006615 | 0.00011378 | 5 | 97523 | 97523 | 0.00075808 | 0.00075808 | 4 | 0.00073692 | 0.00073692 | YES
WMN021 | Mildura CSC | Rural Short | 83 | 111.976 | 0.785 | 10.031 | 14.962 | 58.207 | 4 | 24315 | 20580 | 0.00022227 | 0.00011246 | 18 | 94595 | 94595 | 0.00061917 | 0.00061917 | 3 | 0.00032678 | 0.00032678 | YES
WND011 | Bendigo CSC | Rural Short | 291 | 92.511 | 2.609 | 1.134 | 0.42 | 0.218 | 12 | 22923 | 22923 | 0.00013627 | 0.00013627 | 6 | 11923 | 11923 | 7.2765e-05 | 7.2765e-05 | 7 | 0.0027069 | 0.0027069 | No
WND012 | Bendigo CSC | Rural Long | 2920 | 271.982 | 8.374 | 5.455 | 21.632 | 1.561 | 57 | 1373635 | 1373359 | 0.012561 | 0.012559 | 15 | 99113 | 99113 | 0.00042469 | 0.00042469 | 12 | 0.038874 | 0.038874 | No
WND013 | Bendigo CSC | Rural Long | 3134 | 560.57 | 10.371 | 9.094 | 18.624 | 0.855 | 66 | 1051043 | 1000346 | 0.0026447 | 0.00256 | 14 | 48237 | 48237 | 0.00037573 | 0.00037573 | 4 | 0.018051 | 0.018051 | No
WND014 | Bendigo CSC | Rural Short | 2185 | 35.022 | 2.623 | 4.855 | 3.429 | 0.774 | 12 | 205137 | 204982 | 0.0031395 | 0.0031382 | 5 | 46276 | 46276 | 0.00018258 | 0.00018258 | 6 | 0.017396 | 0.017396 | No
WND021 | Bendigo CSC | Rural Short | 683 | 22.316 | 3.215 | 1.501 | 0.369 | 0.019 | 14 | 29088 | 28963 | 0.00027519 | 0.00027386 | 1 | 1512 | 1512 | 1.5876e-05 | 1.5876e-05 | 3 | 0.0027056 | 0.0027056 | No
WND022 | Bendigo CSC | Rural Short | 132 | 12.789 | 0.278 | 0.794 | 0.027 | 0 | 4 | 2934 | 2934 | 4.1013e-05 | 4.1013e-05 | 0 | 0 | 0 | 0 | 0 | 4 | 0.00069987 | 0.00069987 | No
WND023 | Bendigo CSC | Rural Long | 1777 | 365.004 | 5.764 | 4.565 | 1.459 | 0.421 | 26 | 67799 | 67799 | 0.00073559 | 0.00073559 | 6 | 19545 | 19545 | 7.9381e-05 | 7.9381e-05 | 5 | 0.0097969 | 0.0097969 | No
WND024 | Bendigo CSC | Rural Long | 2317 | 332.788 | 6.182 | 4.889 | 21.939 | 1.304 | 47 | 1477833 | 976704 | 0.0097823 | 0.0067222 | 25 | 87866 | 87866 | 0.00049216 | 0.00049216 | 6 | 0.018396 | 0.018396 | No
WPD011 | Geelong CSC | Rural Short | 393 | 1.368 | 2.619 | 0.829 | 0.002 | 0.028 | 1 | 404 | 404 | 2.646e-06 | 2.646e-06 | 2 | 6810 | 6810 | 3.5721e-05 | 3.5721e-05 | 0 | 0 | 0 | No
WPD012 | Geelong CSC | Urban | 3518 | 12.636 | 8.683 | 12.44 | 0.181 | 0.681 | 10 | 9574 | 9369 | 0.00010716 | 0.00010584 | 4 | 36097 | 36097 | 0.00016538 | 0.00016538 | 0 | 0 | 0 | No
WPD013 | Geelong CSC | Rural Short | 3675 | 138.881 | 6.868 | 10.307 | 14.044 | 5.624 | 45 | 739884 | 739133 | 0.019719 | 0.019714 | 23 | 296263 | 296263 | 0.001114 | 0.001114 | 4 | 0.021984 | 0.021984 | No
WPD014 | Geelong CSC | Rural Short | 3945 | 179.865 | 5.931 | 9.478 | 5.052 | 2.978 | 43 | 524378 | 522972 | 0.0057961 | 0.0057921 | 11 | 309083 | 309083 | 0.0014791 | 0.0014791 | 1 | 0.0047443 | 0.0047443 | No
WPD021 | Geelong CSC | Rural Short | 2524 | 89.872 | 6.799 | 8.53 | 7.169 | 0.044 | 38 | 548228 | 545894 | 0.0089171 | 0.0088972 | 5 | 3380 | 3380 | 2.9106e-05 | 2.9106e-05 | 1 | 0.003338 | 0.003338 | No
WPD022 | Geelong CSC | Rural Short | 4628 | 60.008 | 24.879 | 10.939 | 12.232 | 0.977 | 40 | 916999 | 887613 | 0.012197 | 0.01212 | 8 | 73233 | 73233 | 0.00073162 | 0.00073162 | 1 | 0.0059721 | 0.0059721 | No
WPD024 | Geelong CSC | Rural Short | 2465 | 77.478 | 12.399 | 9.162 | 8.685 | 1.142 | 24 | 384485 | 288372 | 0.005767 | 0.0049639 | 11 | 50565 | 50565 | 0.00037838 | 0.00037838 | 2 | 0.0063491 | 0.0063491 | No
WPD031 | Geelong CSC | Urban | 3468 | 8.596 | 6.829 | 7.78 | 1.608 | 0.081 | 17 | 169553 | 169553 | 0.0014064 | 0.0014064 | 4 | 8590 | 8590 | 0.00027386 | 0.00027386 | 0 | 0 | 0 | No
WPD032 | Geelong CSC | Rural Short | 3931 | 33.114 | 9.317 | 10.347 | 9.813 | 0.237 | 14 | 558234 | 558234 | 0.0093008 | 0.0093008 | 3 | 13493 | 13493 | 0.00014685 | 0.00014685 | 4 | 0.020741 | 0.020741 | No
WPD033 | Geelong CSC | Urban | 2868 | 10.629 | 6.141 | 10.505 | 1.34 | 0.649 | 14 | 67019 | 59981 | 0.00057815 | 0.00049084 | 4 | 32450 | 32450 | 0.00038235 | 0.00038235 | 3 | 0.011546 | 0.011546 | No
Note
(1) The sum of the number of distribution customers for each feeder category may not equal the average distribution customer numbers shown on sheet 1a, due to rounding.
Contents
Contents

## 4c. Network perf - reliability
Powercor Australia Ltd
Reliability - planned outages
2014
The information in templates 4a & c is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
| CBD | Urban | Rural short | Rural long | Whole network
SAIDI | 0 | 20.6739 | 40.5127 | 101.1778 | 48.962
SAIFI | 0 | 0.082671 | 0.17643 | 0.49271 | 0.22434
Contents

## Amendments
Amendments - RIN rationalisation
Information no longer required from Annual Reporting RIN |  | Reasoning
(workbook/worksheet/table/row-column-cell)
Non-financial information templates
1c. STPIS Daily performance (customer service data and MAIFI data retained) | All SAIDI, SAIFI and MED information – columns C-F, I-L, O-R, U-X, AA-AD, AI | Information in Category analysis RIN Worksheet 6.3
1d. STPIS MED threshold | Entire worksheet | Information derived from Category analysis RIN Worksheet 6.3
1e. STPIS Exclusions | SAIDI and SAIFI data – col K,L (MAIFI data retained) | Information in Category analysis RIN Worksheet 6.3
3. General information | Entire worksheet | · Information in Benchmarking RIN Worksheet 5; table 5.1.1; table 5.2; table 7.3
· Information in Category analysis RIN Worksheet 5.2
· Redundant Information
4b Network perf – causes and WSC | Entire worksheet | Information in or derived from Category analysis RIN Worksheet 6.3