## General Instructions
SA Power Networks 2013-14 Economic Benchmarking RIN
General Instructions template:
a) Those cells/variables in the data templates not relevant to SA Power Networks have been left blank (i.e. zero values have not been entered).
b) The "actual" and "estimate" templates have been left blank where the information is contained in the other template. That is, for variables based on estimated information, the cells will be left blank in the actual template (and vice versa).

## 3.1 Revenue
Table / Variable Code | Description | Actual / Estimate |  | Reason for Estimate (if applicable) | If estimate, reason it is best estimate | Data Source(s) | Methodologies and Assumptions
|  | SCS | ACS
3.1. Revenue worksheet
Table 3.1.1 Revenue grouping by chargeable quantity
DREV0101 | Revenue from Fixed Customer Charges | Actual |  |  |  | Sales Model (internal) | Data is based on an as-billed basis. Actual data is extracted from the Sales Model. Includes revenue from all supply charges
DREV0102 | Revenue from Energy Delivery charges where time of use is not a determinant | Actual |  |  |  | Sales Model (internal) | Data is based on an as-billed basis. Actual data is extracted from the Sales Model. Includes revenue from Residential (excl Controlled Load) tariffs & Business Single Rates tariffs
DREV0103 | Revenue from On–Peak Energy Delivery charges | Estimate |  | SAPN does not separately record actual SCS information in this category. ACS is not applicable in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft WAPC Pricing Return 2014 | Data is based on an as-billed basis. Actual data is extracted from the Sales Model for peak and off-peak energy deliveries. The split between peak and off-peak energy deliveries is estimated using WAPC quantities in the Draft WAPC Pricing Return 2014. Includes revenue from Business Two Rates; Contracted Low and High Voltage Demand Peak Rates
DREV0104 | Revenue from Shoulder period Energy Delivery Charges |  |  | SAPN does not have any 'shoulder' charges. |  | Nil | Nil
DREV0105 | Revenue from Off–Peak Energy Delivery charges | Estimate |  | SAPN does not separately record actual SCS information in this category. ACS is not applicable in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft WAPC Pricing Return 2014 | Data is based on an as-billed basis. Actual data is extracted from the Sales Model for peak and off-peak energy deliveries. The split between peak and off-peak energy deliveries is estimated using WAPC quantities in the Draft WAPC Pricing Return 2014. An estimate is made on the split between peak and off-peak sales, based on WAPC quantities.
DREV0106 | Revenue from controlled load customer charges | Actual |  |  |  | Sales Model (internal) Draft WAPC Pricing Return 2014 | Data is based on an as-billed basis. Actual data is extracted from the Sales Model. Includes revenue from Controlled Load Rates (primarily Residential).
DREV0107 | Revenue from unmetered supplies | Actual |  |  |  | Sales Model (internal) Draft WAPC Pricing Return 2014 | Actual data is extracted from the Sales Model. Includes revenue from 12 and 24 hour Unmetered rates (incl Public Lighting NUOS)
DREV0108 | Revenue from Contracted Maximum Demand charges | Actual |  |  |  | Sales Model (internal) Draft WAPC Pricing Return 2014 | Data is based on an as-billed basis. Actual data is extracted from the Sales Model. Includes revenue from Contracted Low and High Voltage Demand Rates
DREV0109 | Revenue from Measured Maximum Demand charges |  |  | SAPN does not have any Measured Maximum Demand charges. |  | Nil | Nil
DREV0110 | Revenue from metering charges |  | Estimate | SAPN does not separately record actual ACS information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on an as-billed basis. SCS: Nil. ACS: Actual data is extracted from the Sales Model. Adjustment is made to this number in order to reconcile to Regulatory Accounts.
DREV0111 | Revenue from connection charges |  |  |  |  | Nil | Connection charges revenue is Negotiated Services Revenue for SAPN
DREV0112 | Revenue from public lighting charges |  |  |  |  | Nil | Public Lighting revenue is Negotiated Services Revenue for SAPN
DREV0113 | Revenue from other Sources | Actual | Actual |  |  | Sales Model and Regulatory Accounts | Includes Incentive Schemes for EBSS; STPIS/Service Incentive & Profit Share (2006-2010); Revenue adjustments relating to billing timing; over/under revenue recoveries and other. SCS: Has been detailed in Working Table 2 below (for SCS). ACS: Reconciliation between the Regulatory Accounts and Sales Model.
DREV01 | Total revenue by chargeable quantity | Actual | Actual | Actual |  | Regulatory Accounts | As reported to AER.
Table 3.1.2 Revenue grouping by Customer type or class
DREV0201 | Revenue from residential Customers | Estimate | Estimate | SAPN has not separately recorded revenue in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft WAPC Pricing Return 2014 Draft WAPC (Meters) Pricing Return 2014 | Data is based on a tariff-applied basis. Actual data is extracted from Sales Model (internal) for SCS and ACS. SCS: Draft WAPC Pricing Return 2014 is used to determine the proportion of controlled load that should be allocated to residential customers. ACS: Draft WAPC (Meters) Pricing Return 2014 is used to adjust the Sales Model data, if necessary. Includes revenue from Supply, Controlled Load, Peak and Non-Peak charges
DREV0202 | Revenue from non-residential customers not on demand tariffs | Estimate | Estimate | SAPN has not separately recorded revenue in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft WAPC Pricing Return 2014 Draft WAPC (Meters) Pricing Return 2014 | Data is based on a tariff-applied basis. Actual data is extracted from Sales Model (internal) for SCS and ACS. SCS: Draft WAPC Pricing Return 2014 is used to determine the proportion of controlled load that should be allocated to non-residential customers. ACS: Draft WAPC (Meters) Pricing Return 2014 is used to adjust the Sales Model data, if necessary Includes revenue from Business 1 & 2 Rates, Supply, Peak and Non-Peak charges
DREV0203 | Revenue from non-residential low voltage demand tariff customers | Actual | Estimate | SAPN has not separately recorded revenue in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft WAPC Pricing Return 2014 Draft WAPC (Meters) Pricing Return 2014 | Data is based on a tariff-applied basis. SCS: Actual data is extracted from the Sales Model. ACS: Actual data is extracted from Draft WAPC (Meters) Pricing Return 2014 file, then adjusted based on the split between LV and HV in the previous year. Includes revenue from all LV Demand Rates (kVA & kW) including Supply, Contracted Demand, Peak and Non-Peak charges
DREV0204 | Revenue from non-residential high voltage demand tariff customers | Actual | Estimate | SAPN has not separately recorded revenue in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft WAPC Pricing Return 2014 Draft WAPC (Meters) Pricing Return 2014 | Data is based on a tariff-applied basis. SCS: Actual data is extracted from the Sales Model. ACS: Actual data extracted from Draft WAPC (Meters) Pricing Return 2014 file, then adjusted using the split between LV and HV in the previous year. Includes revenue from all HV Demand Rates (kVA, kW & Sub)) including Supply, Contracted Demand, Peak and Non-Peak charges
DREV0205 | Revenue from unmetered supplies | Actual |  | SAPN has not separately recorded revenue in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | SCS: Actual data is extracted from the Sales Model (same number as DREV0107). Includes revenue from 12 and 24 hour Unmetered rates (incl Public Lighting NUOS) ACS: Nil
DREV0206 | Revenue from Other Customers | Actual | Actual |  |  | Sales Model and Regulatory Accounts | Includes Incentive Schemes for EBSS; STPIS/Service Incentive & Profit Share (2006-2010); Revenue adjustments relating to billing timing; over/under revenue recoveries and other. SCS: Has been detailed in Working Table 2 below (for SCS). ACS: Reconciliation between the Regulatory Accounts and Sales Model.
DREV02 | Total revenue by customer class | Actual | Actual |  |  | Regulatory Accounts | As reported to the AER.
Table 3.1.3 Revenue (penalties) allowed (deducted) through incentive schemes
DREV0301 | EBSS | Actual |  |  |  | EDPD 2010-2015 AER Reset | Actual data extracted from the 2010-2015 EDPD Decision from the AER. Includes incentives/penalties receovered from customers within the tariffs for the applicable years as opposed to when earned/incurred from an accounting perspective.
DREV0302 | STPIS | Actual |  |  |  | Sales Model (internal) | Actual data extracted from the Sales Model. Includes incentives/penalties receovered from customers within the tariffs for the applicable years as opposed to when earned/incurred from an accounting perspective.
DREV0303 | F-Factor |  |  |  |  | N/A | SAPN does not have an F-factor
DREV0304 | S-Factor True up |  |  |  |  | N/A | SAPN does not have a S-Factor True up
DREV0305 | Other |  |  |  |  | Nil | Nil
DREV03 | Total revenue of incentive schemes | Estimate | Estimate | Sum of estimates | Relying on opinion of experienced manager using what reliable data is available. | Sum of DREV0301-DREV0303
Working Table 2: DREV0113 and DREV0206
Standard Control
[8 empty] | $'000 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
[8 empty] | Q Factor | -19615 | -10494 | -4367 | -6781 | 780 | 0 | 0 | 0 | 0
[8 empty] | K Factor | 0 | -12646 | -4330 | -3224 | -2738 | 0 | 0 | 0 | 0
[8 empty] | EDPD | 0 | 0 | 0 | 0 | 0 | 37375 | 8115 | 0 | 0
[8 empty] | S-Factor | 0 | 0 | 0 | 0 | 0 | -4200 | 17700 | 5880 | -19830
[8 empty] | EBSS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Service Incentive | 600 | -1800 | 1200 | 2200 | -1800 | 0 | 0 | 0 | 0
[8 empty] | Pass Through (excl PV) | 0 | 0 | 0 | 0 | 3171 | 363 | 0 | 0 | 0
[8 empty] | Interest | -45 | 0 | -2970 | -1497 | 1891 | 1494 | 5645 | 4802 | 1375.9
[8 empty] | Profit Share (P Factor) | -2000 | 0 | -800 | 80 | 96 | 0 | 0 | 0 | 0
[8 empty] | EPO Transition Factor | -1631 | 1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | DM Accrual | 0 | 0 | 0 | 0 | -6800 | 0 | 0 | 0 | 0
[8 empty] | Billing Timing | 13387 | 1681 | 1744 | 2404 | -257 | -6321 | 2266 | 14753 | -7261
[8 empty] | Total | -9304 | -22196 | -9523 | -6818 | -5657 | 28711 | 33726 | 25435 | -11193

## 3.2 Opex
Table / Variable Code | Description | Actual / Estimate |  | Reason for Estimate (if applicable) | Data Source(s) | Methodologies and Assumptions
|  | Standard Control Services | Alternative Control Services
3.2 Opex worksheet
Table 3.2.1 Opex categories
Table 3.2.1.1 Current opex categories and cost allocations
DOPEX0101 | Distribution licence fee | Actual | Actual |  | Refer data sources for DOPEX0101A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0102 | Network operating costs | Actual | Actual |  | Refer data sources for DOPEX0102A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0103 | Inspections | Actual | Actual |  | Refer data sources for DOPEX0103A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0104 | Maintenance & repair | Actual | Actual |  | Refer data sources for DOPEX0104A below. | Directly attributed to service segments dependent upon current asset classifications and in accordance with current Cost Allocation Method.
DOPEX0105 | Substation property maintenance | Actual | Actual |  | Refer data sources for DOPEX0105A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0106 | Vegetation management | Actual | Actual |  | Refer data sources for DOPEX0106A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0107 | Emergency response | Actual | Actual |  | Refer data sources for DOPEX0107A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0108 | Demand management | Actual | Actual |  | Refer data sources for DOPEX0108A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0109 | Guaranteed service level payments | Actual | Actual |  | Refer data sources for DOPEX0109A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0110 | Network insurance | Actual | Actual |  | Refer data sources for DOPEX0110A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0111 | Call centre | Actual | Actual |  | Refer data sources for DOPEX0111A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0112 | Full retail contestability | Actual | Actual |  | Refer data sources for DOPEX0112A below. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0113 | Meter reading | Actual | Actual |  | Refer data sources for DOPEX0113A below. | Directly attributed to service segments dependent upon current Meter asset classifications and in accordance with current Cost Allocation Method.
DOPEX0114 | Other customer services | Actual | Actual |  | Refer data sources for DOPEX0114A below. | Costs are allocated across service segments in accordance with the current Cost Allocation Method for the Customer Relations group.
DOPEX0115 | Corporate costs and other operating | Actual | Actual |  | Refer data sources for DOPEX0115A below. | Costs are allocated across service segments as detailed in the current Cost Allocation Method.
DOPEX01 | Total opex | Actual | Actual |  | Refer data sources for DOPEX01A below. | Represents the respective totals of Standard Control Services opex and Alternative Control Services opex as reported in the 2013-14 Annual RIN.
Table 3.2.1.2A Historical opex categories and cost allocations
(per AER Cost Allocation Method 2011-2014)
DOPEX0101A | Distribution licence fee | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0102A | Network operating costs | Actual | Actual |  | Sub-total of Network operating cost lines (excluding Distribution licence fee) from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0103A | Inspections | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0104A | Maintenance & repair | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to service segments dependent upon current asset classifications and in accordance with current Cost Allocation Method.
DOPEX0105A | Substation property maintenance | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0106A | Vegetation management | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0107A | Emergency response | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0108A | Demand management | Actual | Actual |  | Total of Demand Management and Demand Management Innovation Fund reporting lines from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0109A | Guaranteed service level payments | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0110A | Network insurance | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0111A | Call centre | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0112A | Full retail contestability | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to Standard Control Services as per current Cost Allocation Method.
DOPEX0113A | Meter reading | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Directly attributed to service segments dependent upon current Meter asset classifications and in accordance with current Cost Allocation Method.
DOPEX0114A | Other customer services | Actual | Actual |  | Specified reporting line from 2013-14 Annual RIN. | Costs are allocated across service segments in accordance with the current Cost Allocation Method for the Customer Relations group.
DOPEX0115A | Corporate costs and other operating | Actual | Actual |  | Allocated and other cost lines from 2013-14 Annual RIN. | Costs are allocated across service segments as detailed in the current Cost Allocation Method.
DOPEX01A | Total opex | Actual | Actual |  | Total Operating and Maintenance expenditure reported in 2013-14 Annual RIN | Represents the respective totals of Standard Control Services opex and Alternative Control Services opex as reported in the 2013-14 Annual RIN.
Table 3.2.1.2B Historical opex categories and cost allocations
(per ESCOSA Cost Allocation Method 2006-2010)
DOPEX0101B | Distribution licence fee | Actual | Actual |  | Not applicable for 2013-14. | The Historical cost allocation approach which operated during the period 2005-06 to 2009-10 was replaced by the current Cost Allocation Method commencing from the 2010-11 regulatory year.
DOPEX0102B | Network operating costs | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0103B | Inspections | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0104B | Maintenance & repair | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0105B | Substation property maintenance | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0106B | Vegetation management | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0107B | Emergency response | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0108B | Demand management | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0109B | Guaranteed service level payments | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0110B | Network insurance | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0111B | Call centre | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0112B | Full retail contestability | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0113B | Meter reading | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0114B | Other customer services | Actual | Actual |  | Not applicable for 2013-14.
DOPEX0115B | Corporate costs and other operating | Actual | Actual |  | Not applicable for 2013-14.
DOPEX01B | Total opex | Actual | Actual |  | Not applicable for 2013-14.
Table 3.2.2 Opex consistency
Table 3.2.2.1 Opex consistency - current cost allocation
DOPEX0201 | Opex for network services | Actual | Actual |  | Total Standard Control Services from Table 3.2.1.1 excluding Connection Services reported against DOPEX0203. | Assumes that all direct and allocated indirect Standard Control Services costs reported in Table 3.2.1.1 necessarily support the delivery of Network Services, other than those classified as Connection Services.
DOPEX0202 | Opex for metering | Actual | Actual |  | Total Alternative Control Services from Table 3.2.1.1 excluding Connection Services reported against DOPEX0203. | Assumes that all direct and allocated indirect Alternative Control Services costs reported in Table 3.2.1.1 necessarily support the delivery of Metering Services, other than those classified as Connection Services.
DOPEX0203 | Opex for connection services | Actual | Actual |  | Reported as part of Other Customer Services line in the 2013-14 Annual RIN. | Costs associated with the dedicated Connection Services group were extracted and excluded from Other Customer Services costs and allocated across service segments in accordance with the current Cost Allocation Method.
DOPEX0204 | Opex for public lighting | Actual | Actual |  | Not applicable to SA Power Networks. | SA Power Networks' Public Lighting works are classified under Negotiated Services, hence a nil value is reported for both Standard and Alternative Control Services.
DOPEX0205 | Opex for amounts payable for easement levy or similar direct charges on DNSP | Actual | Actual |  | Not applicable to SA Power Networks. | SA Power Networks are not subject to any easement levy or similar direct charges.
DOPEX0206 | Opex for transmission connection point planning | Actual | Actual |  | Not applicable to SA Power Networks. | SA Power Networks capitalises all costs associated with transmission connection points.
Table 3.2.2.2 Opex consistency - historical cost allocation
DOPEX0201A | Opex for network services | Actual | Actual |  | Total Standard Control Services from Table 3.2.1.2A excluding Connection Services reported against DOPEX0203A. | Assumes that all direct and allocated indirect Standard Control Services costs reported in Table 3.2.1.2A necessarily support the delivery of Network Services, other than those classified as Connection Services.
DOPEX0202A | Opex for metering | Actual | Actual |  | Total Alternative Control Services from Table 3.2.1.2A excluding Connection Services reported against DOPEX0203A. | Assumes that all direct and allocated indirect Alternative Control Services costs reported in Table 3.2.1.2A necessarily support the delivery of Metering Services, other than those classified as Connection Services.
DOPEX0203A | Opex for connection services | Actual | Actual |  | Reported as part of Other Customer Services line in the 2013-14 Annual RIN. | Costs associated with the dedicated Connection Services group were extracted and excluded from Other Customer Services costs and allocated across service segments in accordance with the current Cost Allocation Method.
DOPEX0204A | Opex for public lighting | Actual | Actual |  | Not applicable to SA Power Networks. | SA Power Networks' Public Lighting works are classified under Negotiated Services, hence a nil value is reported for both Standard and Alternative Control Services.
DOPEX0205A | Opex for amounts payable for easement levy or similar direct charges on DNSP | Actual | Actual |  | Not applicable to SA Power Networks. | SA Power Networks are not subject to any easement levy or similar direct charges.
DOPEX0206A | Opex for transmission connection point planning | Actual | Actual |  | Not applicable to SA Power Networks. | SA Power Networks capitalises all costs associated with transmission connection points.
Table 3.4 Opex for high voltage customers
DOPEX0401 | Opex for high voltage customers | Estimate | Not requested | For commercial reasons, SA Power Networks is unable to obtain actual cost information from it's high voltage customers, hence an estimate of end user costs is necessary. | There is no reasonable data source for this information. Hence, it has been necessary for SA Power Networks to calculate a best estimate of costs as described in the Methodologies and Assumptions column. | SA Power Networks were required to estimate the additional Opex that would have been incurred had it been responsible for operating and maintaining the electricity Distribution Transformers that are owned by its high voltage customers. This was achieved by undertaking the following processes: (1) Using historical costs reported in Table 3.2.1.2A of the RIN as the basis, SA Power Networks identified the relevant Standard Control Services opex categories that were considered to represent the type of costs its high voltage customers might incur in maintaining their Distribution Transformer assets, these categories were: Network operating costs; Maintenance & repair; and Network insurance; (2) In order to approximate the amount of this opex relating to Distribution Transformers, the total of the relevant Standard Control Services opex categories for the year were then multiplied by a percentage amount, representing the percentage of SA Power Networks' closing RAB values for Standard Control Services at 30 June 2014 attributable to Distribution Transformers; and (3) In order to determine the share of these calculated values relating to high voltage customers for the 2013-14 regulatory year, the values were multiplied by the ratio of high voltage customer observed peak demand MVA (reported each year against Variable Code DPA0502 in Table 3.5.2.1 of the RIN) as a portion of SA Power Networks' total network observed peak demand MVA (reported each year against Variable Code DOPSD0201 in Table 3.4.3.3 of the RIN).

## 3.2.3 Provisions
Basis of Preparation
Benchmarking RIN Response 2013-14
Table / Variable Code | Description | Standard Control Services |  | Reason for Estimate (if applicable) | Data Source(s) | Methodologies and Assumptions
|  | Component | Actual / Estimated
3.2.3 Provisions worksheet
Table 3.2.3 Provisions
DOPEX03A | Annual Leave
DOPEX0301A | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward Standard Control Services balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the provision for annual leave are allocated across service segments in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Annual Leave provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302A | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Derived values representing the Standard Control Services component of the Annual Leave P&L expense +/- any offsetting movements in the provision as a result of values reported against DOPEX0311A.
DOPEX0303A | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304A | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305A | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306A | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307A | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308A | Unused amounts reversed during the period | Opex | Actual |  | Not applicable to SA Power Networks. Any unused amounts provided for annual leave are paid out to employees upon departure from the business.
DOPEX0309A | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310A | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311A | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Standard Control Services component of movements in the provision as a result of changes arising from the passage of time and the effect of any change in the discount rate.
DOPEX0312A | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313A | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314A | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The Standard Control Services component of the specific General Ledger accounts that represent the total provision for annual leave. The Annual Leave provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.
DOPEX03B | Long Service Leave
DOPEX0301B | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward Standard Control Services balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the provision for long service leave are allocated across service segments in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Long Service Leave provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302B | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Derived values representing the Standard Control Services component of the Long Service Leave P&L expense +/- any offsetting movements in the provision as a result of values reported against DOPEX0308B and DOPEX0311B.
DOPEX0303B | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304B | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305B | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306B | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307B | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308B | Unused amounts reversed during the period | Opex | Actual |  | Unused amounts provided for long service leave not paid out due to employees departing the business prior to reaching legislated period of service (7 years). Note the unused amount reflects the gross accrual for each individual employee and accordingly does not consider the adjustments required by AASB119 for probability, wage increases and on-costs. These AASB119 adjustments are reflected in the annual assessment of SA Power Networks' long service leave liability, as calculated by an independent Actuary, and are included in the amounts reported against Variable Code DOPEX0311B.
DOPEX0309B | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310B | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311B | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Standard Control Services component of movements in the provision as a result of changes arising from the passage of time and the effect of any change in the discount rate.
DOPEX0312B | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313B | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314B | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The Standard Control Services component of the specific General Ledger accounts that represent the total provision for long service leave. The Long Service Leave provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.
DOPEX03C | Workers' Compensation
DOPEX0301C | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward Standard Control Services balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the provision for workers compensation are allocated across service segments in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Workers Compensation provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302C | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Derived values representing the Standard Control Services component of the Workers' Compensation P&L expense +/- any offsetting movements in the provision as a result of values reported against DOPEX0308C.
DOPEX0303C | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304C | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305C | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306C | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307C | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308C | Unused amounts reversed during the period | Opex | Actual |  | Unused amounts provided for individual workers' compensation claims not paid out and written back from the provision upon finalisation of claims. Note, many workers' compensation claims are uncertain by their nature, in that individual claims may be opened and closed several times during the life of the claim, and thus the individual provision for each claim can be adjusted up or down on multiple occasions. Individual claims can also have a material impact on the unused value reported as the result of changing outlooks following the establishment of the provision amount, e.g. improved medical prognosis and successful claims management. Consequently, the unused amounts reported as a proportion of the total provision value are typically higher than for other provisions.
DOPEX0309C | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310C | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311C | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Not applicable to SA Power Networks. As workers' compensation claims are normally settled within a defined period (e.g. within a year), there is generally no impacts on the provision associated with either changes in the discount rate or the passage of time.
DOPEX0312C | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313C | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314C | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The Standard Control Services component of the specific General Ledger accounts that represent the total provision for workers compensation. The Workers compensation provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.
DOPEX03D | Self Insurance
DOPEX0301D | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the provision for self insurance are directly attributed to Standard Control Services in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Self Insurance provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302D | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Derived values representing the Self Insurance P&L expense +/- any offsetting movements in the provision as a result of values reported against DOPEX0308D.
DOPEX0303D | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304D | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305D | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306D | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307D | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308D | Unused amounts reversed during the period | Opex | Actual |  | Unused amounts provided for individual self insurance claims not paid out and written back from the provision based upon the date of finalisation for the claims. Note, SA Power Networks records all insurance claims in its Figtree system, which tracks provisions for individual claims outside of our SAP accounting system. Typically, a high volume of claims are received from customers for which no payments are actually incurred. It was not therefore possible to determine exactly if and when these individual claims hit the provision. Consequently, in determining unused amounts of the provision, only claims where costs were actually incurred by SA Power Networks are included in this calculation. To not exclude those claims with nil payments would result in the reporting of erroneously-high unused provision values.
DOPEX0309D | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310D | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311D | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Not applicable to SA Power Networks. The amount of the self insurance provision is assessed and adjusted by SA Power Networks on a monthly basis via the P&L expense account. SA Power Networks has not made any adjustments to the provision for either changes to the discount rate or the passage of time.
DOPEX0312D | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313D | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314D | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The balance of the specific General Ledger accounts that represent the total provision for self insurance. The Self Insurance provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.
DOPEX03E | Income Protection Scheme
DOPEX0301E | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward Standard Control Services balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the provision for income protection are allocated across service segments in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Income Protection Scheme provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302E | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Values represent the Standard Control Services component of any increments to the total Income Protection provision by way of journal.
DOPEX0303E | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304E | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305E | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306E | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307E | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308E | Unused amounts reversed during the period | Opex | Actual |  | Values represent the Standard Control Services component of any decrements to the total Income Protection provision by way of journal.
DOPEX0309E | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310E | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311E | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Not applicable to SA Power Networks. The amount of the income protection scheme provision is assessed and adjusted by SA Power Networks on a monthly basis via the P&L expense account. SA Power Networks has not made any adjustments to the provision for either changes to the discount rate or the passage of time.
DOPEX0312E | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313E | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314E | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The Standard Control Services component of the specific General Ledger accounts that represent the total provision for income protection. The Income Protection Scheme provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.
DOPEX03F | Environmental - Demolition and Site Restoration
DOPEX0301F | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the environmental provision are directly attributed to Standard Control Services in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Environmental provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302F | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Values represent the increments to the total Environmental provision by way of journal.
DOPEX0303F | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304F | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305F | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306F | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307F | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308F | Unused amounts reversed during the period | Opex | Actual |  | Values represent the decrements to the total Environmental provision by way of journal.
DOPEX0309F | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310F | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311F | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Not applicable to SA Power Networks. The total amount of the environmental provision is assessed by SA Power Networks on a monthly basis, and adjusted periodically via the P&L expense account as required. SA Power Networks has not made any adjustments to the provision for either changes to the discount rate or the passage of time.
DOPEX0312F | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313F | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314F | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The balance of the specific General Ledger accounts that represent SA Power Networks' total environmental provision (being provisions for demolition and site restoration). The Environmental provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.
DOPEX03G | Employee Bonuses
DOPEX0301G | Opening balance (the carrying amount at the beginning of the period) | Total | Actual |  | Carried forward Standard Control Services balance as reported in the historical Economic Benchmarking RIN at 30 June 2013. | The balances and movements of the provision for employee bonuses are allocated across service segments in accordance with SA Power Networks' current Cost Allocation Method. SA Power Networks' Employee Bonus provision is accounted for wholly against the operating accounts. Therefore, there are nil balances and movements reported against the Capex and Other components of the provision.
DOPEX0302G | Additional provisions made in the period, including increases to existing provisions | Opex | Actual |  | Dervived values representing the Standard Control Services component of the Employee Bonuses P&L expense +/- any offsetting movements in the provision as a result of values reported against DOPEX0308G.
DOPEX0303G | Additional provisions made in the period, including increases to existing provisions | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0304G | Additional provisions made in the period, including increases to existing provisions | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0305G | Amounts used (that is, incurred and charged against the provision) during the period | Opex | Actual |  | Balancing item, reflecting payments from the provision +/- any other movements in the provision not captured within the other categories.
DOPEX0306G | Amounts used (that is, incurred and charged against the provision) during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0307G | Amounts used (that is, incurred and charged against the provision) during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0308G | Unused amounts reversed during the period | Opex | Actual |  | Unused amounts provided for employee bonuses, where applicable, not paid out and written back from the provision. For 2013-14, consistent with the approach adopted for each year of the historical Economic Benchmarking RIN, the audited closing provision balance at 31 December 2013 (being SA Power Networks' financial year end) was compared to the employee bonuses actually paid early in 2014. As the provision balance exceeded the bonuses paid for the year, the difference is the amount reported as unused.
DOPEX0309G | Unused amounts reversed during the period | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0310G | Unused amounts reversed during the period | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0311G | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Opex | Actual |  | Not applicable to SA Power Networks. The amount of the employee bonuses provision is assessed and adjusted by SA Power Networks on a monthly basis via the P&L expense account. SA Power Networks has not made any adjustments to the provision for either changes to the discount rate or the passage of time.
DOPEX0312G | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Capex | Actual |  | Not applicable to SA Power Networks.
DOPEX0313G | The increase during the period in the discounted amount arising from the passage of time and the effect of any change in the discount rate | Other | Actual |  | Not applicable to SA Power Networks.
DOPEX0314G | Closing balance (the carrying amount at the end of the period) | Total | Actual |  | The Standard Control Services component of the specific General Ledger account that represents the total provision for employee bonuses. The Employee Bonus provision forms part of the total Provisions liability reported in SA Power Networks' financial accounts at 30 June 2014.

## 3.3 Assets (RAB)
Table / Variable Code | Description | Actual / Estimate |  |  | Reason for Estimate (if applicable) | Data Source(s) | Methodologies and Assumptions
|  | Network Services | Standard Control Services | Alternative Control Services
3.3 Assets (RAB) worksheet
Table 3.3.1 Regulatory Asset Base Values
For total asset base:
DRAB0101 | Opening value | Estimate | Actual | Actual | It was necessary to estimate the original Network Services RAB opening balance at 1 July 2005 (as reported in the historical Economic Benchmarking RIN) owing to the fact that SA Power Networks does not separately record the value of the Connection Services component of its RAB. SA Power Networks has subsequently rolled forward each year of the Network Services RAB with its movements having been based on this original opening balance. | Carried forward 30 June 2013 balances as reported in the historical Economic Benchmarking RIN.
DRAB0102 | Inflation addition | Estimate | Actual | Actual | While actual CPI rates were applied, the inflation addition to the Network Services opening RAB value is an estimate by virtue of the opening value reported against DRAB0101 being an estimate. | Australian Bureau of Statistics - Consumer Price Index, Australia | The opening values as per DRAB0101 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0103 | Straight line depreciation | Estimate | Actual | Actual | It was necessary to estimate the straight line depreciation values in the Network Services RAB roll forward owing to the fact that SA Power Networks does not separately track the value or age of the Connection Services component of its RAB. | "AER, Electricity Distribution Network Service Providers Roll Forward Model, Version: 01, 26 June 2008" to be used by the AER to roll forward SA Power Networks' RAB values for the period 1 July 2010 to 30 June 2015. | The outputs from the model as described in the Data Source were used to determine the total straight line depreciation values for Standard Control Services and Alternative Control Services. Total Network Services depreciation was estimated as the Network Services opening RAB value divided by the Standard Control Services opening RAB value multiplied by the Standard Control Services straight line depreciation charge for each applicable asset category.
DRAB0104 | Regulatory depreciation | Estimate | Actual | Actual | Regulatory depreciation values in the Network Services RAB roll forward are estimates by virtue of the other estimates which have been made to roll forward the Network Services RAB. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0102 less the straight line depreciation as per DRAB0103.
DRAB0105 | Actual additions (recognised in RAB) | Actual | Actual | Actual |  | Actual capital additions and Capital Contributions as reported in 2013-14 Annual RIN. Rate of return (nominal WACC) additions to RAB are as per the "AER, Electricity Distribution Network Service Providers Roll Forward Model, Version: 01, 26 June 2008". | Represents the net of Capital Additions, Capital Contributions and Rate of return (nominal WACC) additions.
DRAB0106 | Disposals | Actual | Actual | Actual |  | Actual Disposals as reported in 2013-14 Annual RIN.
DRAB0107 | Closing value for asset value | Estimate | Actual | Actual | The closing balance of the Network Services RAB is an estimate owing to the fact that SA Power Networks does not separately record the value of the Connection Services component of its RAB and has had to make a number of assumptions in building the Network Services RAB roll forward (as described against DRAB0101 and DRAB0103). | Refer Data Source provided for DRAB0103. | The 30 June 2014 closing RAB balances for Standard Control Services and Alternative Control Services were obtained by entering 2013-14 data into "AER, Electricity Distribution Network Service Providers Roll Forward Model, Version: 01, 26 June 2008" to be used by the AER to roll forward SA Power Networks' RAB values for the period 1 July 2010 to 30 June 2015, adjusted where necessary to reflect the impacts of replacing forecast values with actual values. The closing Network Services RAB balance at 30 June 2014 was obtained by rolling forward the opening balance with a combination of actual and estimated 2013-14 asset movements as described against the Variable Codes DRAB0101 to DRAB0107.
Table 3.3.2 Asset value roll forward
For overhead network assets less than 33kV:
DRAB0201 | Opening value | Estimate | Estimate | Actual | As reported and described in the historical Economic Benchmarking RIN, the derivation of the 30 June 2013 balance for Standard Control Services required the allocation of RAB balances and movements in accordance with the AER's RAB allocation approach of using total estimated depreciated replacement cost, and also included allocations of Work in Progress across applicable asset categories. Further estimation was required to establish the 30 June 2013 balance for Network Services (as described against DRAB0101) as SA Power Networks does not separately record the value of the Connection Services component of its RAB. | Carried forward 30 June 2013 balances as reported in the historical Economic Benchmarking RIN. | Comprised of the following SA Power Networks' asset classes: Distribution Lines (overhead % estimated using depreciated replacement cost calculation), Low Voltage Services (overhead % estimated using depreciated replacement cost calculation), Capital Contributions (overhead % estimated using depreciated replacement cost calculation) and share of Work in Progress (% estimated based on pro rata closing asset values). For Network Services, balances exclude estimated values associated with Connection Services assets. SA Power Networks used the best available data source in each instance to determine the splits across multiple asset categories using the depreciated replacement cost calculation. It was necessary to use physical asset data, replacement unit cost data and estimated service and residual life data from various information sources. The majority of the data used was derived from the Asset Installation template contained in the 2012-13 Annual RIN submitted by SA Power Networks to the AER in November 2013. These data sources were deemed the best available to provide the necessary information to complete the calculations at a detailed asset level which best reflects SA Power Networks' regulated asset base.
DRAB0202 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB0201 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0201 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0203 | Straight line depreciation | Estimate | Estimate | Actual | While total straight line depreciation represents actual data for Standard Control Services, values at the category level are estimates due to the assumptions and allocations required to establish the asset roll forward. SA Power Networks does not separately track the value or age of the Connection Services component of its RAB, therefore for Network Services it was also necessary to estimate depreciation values for the category (as described against DRAB0103). | Refer Data Source provided for DRAB0103. | The outputs from the model as described in the Data Source were used to determine the total straight line depreciation values for the asset classes comprising this category. These were then allocated across asset categories in accordance with the depreciated replacement cost methodology. For Network Services, depreciation values exclude estimated values associated with Connection Services assets.
DRAB0204 | Regulatory depreciation | Estimate | Estimate | Actual | While total regulatory depreciation represents actual data for Standard Control Services, values at the category level are estimates due to the assumptions and allocations required to establish the asset roll forward. Regulatory depreciation values in the Network Services RAB roll forward are estimates by virtue of the other estimates which were needed to be made to roll forward the Network Services RAB. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0202 less the straight line depreciation as per DRAB0203.
DRAB0205 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | While total actual additions represents actual data for Network Services and Standard Control Services, values at the category level are estimates due to the requirement to allocate additions in accordance with the AER's RAB allocation approach of using total estimated depreciated replacement cost. Includes an allocation of the Work in Progress asset category based on pro rata closing asset values at 30 June 2014 across applicable asset categories. | Refer Data Source provided for DRAB0105. | Represents the net of Capital Additions, Capital Contributions and Rate of return (nominal WACC) additions. For Network Services, additions exclude values associated with Connection Services assets.
DRAB0206 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0207 | Closing value for overhead distribution asset value | Estimate | Estimate | Actual | The closing balance of the Standard Control Services RAB is an estimate owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB0201, DRAB0203 and DRAB0205). Further estimation was required to establish closing values for Network Services as SA Power Networks does not separately record the value of the Connection Services component of its RAB (as described against DRAB0101 and DRAB0103). | Closing balances as per the output of "AER, Electricity Distribution Network Service Providers Roll Forward Model, Version: 01, 26 June 2008". | Refer Methodologies and Assumptions provided for DRAB0201.
For underground network assets less than 33kV:
DRAB0301 | Opening value | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0201. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Distribution Lines (underground % estimated using depreciated replacement cost calculation), Low Voltage Services (underground % estimated using depreciated replacement cost calculation), Capital Contributions (underground % estimated using depreciated replacement cost calculation) and share of Work in Progress (% estimated based on pro rata closing asset values). For Network Services, balances exclude estimated values associated with Connection Services assets. Refer Methodologies and Assumptions provided for DRAB0201 for detail on how the depreciated replacement cost calculations were undertaken.
DRAB0302 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB0301 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0301 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0303 | Straight line depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0203. | Refer Data Source provided for DRAB0103. | Refer Methodologies and Assumptions provided for DRAB0203.
DRAB0304 | Regulatory depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0204. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0302 less the straight line depreciation as per DRAB0303.
DRAB0305 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0205. | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0205.
DRAB0306 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0307 | Closing value for underground distribution asset value | Estimate | Estimate | Actual | The closing balance of the Standard Control Services RAB is an estimate owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB0301, DRAB0303 and DRAB0305). Further estimation was required to establish closing values for Network Services as SA Power Networks does not separately record the value of the Connection Services component of its RAB (as described against DRAB0101 and DRAB0103). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0301.
For distribution substations and transformers:
DRAB0401 | Opening value | Estimate | Estimate | Actual | As reported and described in the historical Economic Benchmarking RIN, the derivation of the 30 June 2013 balances for Network Services and Standard Control Services required the allocation of RAB balances and movements in accordance with the AER's RAB allocation approach of using total estimated depreciated replacement cost, and also included allocations of Work in Progress across applicable asset categories. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Substations (Distribution Substation % estimated using depreciated replacement cost calculation), Transformers (Distribution Transformer % estimated using depreciated replacement cost calculation) and share of Work in Progress (% estimated based on pro rata closing asset values). Refer Methodologies and Assumptions provided for DRAB0201 for detail on how the depreciated replacement cost calculations were undertaken.
DRAB0402 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB0401 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0401 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0403 | Straight line depreciation | Estimate | Estimate | Actual | While total straight line depreciation represents actual data for Standard Control Services, values at the category level are estimates due to the assumptions and allocations required to establish the asset roll forward. | Refer Data Source provided for DRAB0103. | The outputs from the model as described in the Data Source were used to determine the total straight line depreciation values for the asset classes comprising this category. These were then allocated across asset categories in accordance with the depreciated replacement cost methodology.
DRAB0404 | Regulatory depreciation | Estimate | Estimate | Actual | While total regulatory depreciation represents actual data for Standard Control Services, values at the category level are estimates due to the assumptions and allocations required to establish the asset roll forward. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0402 less the straight line depreciation as per DRAB0403.
DRAB0405 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0205. | Refer Data Source provided for DRAB0105. | Represents the total of Capital Additions and Rate of return (nominal WACC) additions.
DRAB0406 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0407 | Closing value for distribution substations and transformers asset value | Estimate | Estimate | Actual | The closing balances of the Network Services and Standard Control Services RAB are estimates owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB0401, DRAB0403 and DRAB0405). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0401.
For overhead network assets 33kV and above:
DRAB0501 | Opening value | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0401. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Sub-transmission Lines (overhead % estimated using depreciated replacement cost calculation) and share of Work in Progress (% estimated based on pro rata closing asset values). Refer Methodologies and Assumptions provided for DRAB0201 for detail on how the depreciated replacement cost calculations were undertaken.
DRAB0502 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB0501 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0501 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0503 | Straight line depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0403. | Refer Data Source provided for DRAB0103. | Refer Methodologies and Assumptions provided for DRAB0403.
DRAB0504 | Regulatory depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0404. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0502 less the straight line depreciation as per DRAB0503.
DRAB0505 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0205. | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB0506 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0507 | Closing value for overhead asset 33kV and above value | Estimate | Estimate | Actual | The closing balances of the Network Services and Standard Control Services RAB are estimates owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB0501, DRAB0503 and DRAB0505). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0501.
For underground network assets 33kV and above:
DRAB0601 | Opening value | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0401. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Sub-transmission Lines (underground % estimated using depreciated replacement cost calculation) and share of Work in Progress (% estimated based on pro rata closing asset values). Refer Methodologies and Assumptions provided for DRAB0201 for detail on how the depreciated replacement cost calculations were undertaken.
DRAB0602 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB0601 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0601 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0603 | Straight line depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0403. | Refer Data Source provided for DRAB0103. | Refer Methodologies and Assumptions provided for DRAB0403.
DRAB0604 | Regulatory depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0404. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0602 less the straight line depreciation as per DRAB0603.
DRAB0605 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0205. | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB0606 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0607 | Closing value for underground asset 33kV and above value | Estimate | Estimate | Actual | The closing balances of the Network Services and Standard Control Services RAB are estimates owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB0601, DRAB0603 and DRAB0605). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0601.
For zone substations and transformers:
DRAB0701 | Opening value | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0401. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Substations (Zone Substation % estimated using depreciated replacement cost calculation), Substation Land (for the period since 1 July 2009), Transformers (Zone Transformer % estimated using depreciated replacement cost calculation) and share of Work in Progress (% estimated based on pro rata closing asset values). Prior to 1 July 2009, Substation Land asset balances and movements were not separately identifiable, but were contained within the "Other asset items with long lives" category of the RAB worksheet reported in the historical Economic Benchmarking RIN .
DRAB0702 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB0701 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0701 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0703 | Straight line depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0403. | Refer Data Source provided for DRAB0103. | Refer Methodologies and Assumptions provided for DRAB0403.
DRAB0704 | Regulatory depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0404. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0702 less the straight line depreciation as per DRAB0703.
DRAB0705 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0205. | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB0706 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0707 | Closing value for zone substations and transformers asset value | Estimate | Estimate | Actual | The closing balances of the Network Services and Standard Control Services RAB are estimates owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB0701, DRAB0703 and DRAB0705). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0701.
For easements:
DRAB0801 | Opening value | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0201. | Comprised solely of SA Power Networks' Easement asset category, thus no estimations or allocations were required for this category. Prior to 1 July 2009, Easements asset balances and movements were not separately identifiable, but were contained within the "Other asset items with long lives" category of the RAB worksheet reported in the historical Economic Benchmarking RIN.
DRAB0802 | Inflation addition | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0801 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0805 | Actual additions (recognised in RAB) | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB0806 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0807 | Closing value for easements asset value | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0801.
For meters:
DRAB0901 | Opening value | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0201. | Comprised solely of SA Power Networks' Meters asset category. Thus no estimations or allocations were required for this category.
DRAB0902 | Inflation addition | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0102. | The opening values as per DRAB0901 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB0903 | Straight line depreciation | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0103. | The output from the model as described in the Data Source represents the total straight line depreciation value for the Meters asset category.
DRAB0904 | Regulatory depreciation | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB0902 less the straight line depreciation as per DRAB0903.
DRAB0905 | Actual additions (recognised in RAB) | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB0906 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB0907 | Closing value for meters asset value | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB0901.
For "other" asset items with long lives:
DRAB1001 | Opening value | Estimate | Estimate | Actual | As reported and described in the historical Economic Benchmarking RIN, the derivation of the 30 June 2013 balances for Network Services and Standard Control Services included best estimate allocations of Work in Progress across applicable asset categories. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Communications, Land, Substation Land (for the period until 30 June 2009), Easements (for the period until 30 June 2009), Buildings, Heavy Vehicles, Plant & Tools / Office Furniture, Equity Raising Costs and share of Work in Progress (% estimated based on pro rata closing asset values). Prior to 1 July 2009, Land, Substation Land and Easements asset balances and movements were not separately identifiable, but were contained within this category of the RAB worksheet reported in the historical Economic Benchmarking RIN. For the period since 1 July 2009, Substation Land asset movements have been separately included against the "Zone substations and transformers" category and Easements asset movements have been separately reported against the "Easements" category in the RAB worksheet.
DRAB1002 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB1001 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB1001 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB1003 | Straight line depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0403. | Refer Data Source provided for DRAB0103. | Refer Methodologies and Assumptions provided for DRAB0403.
DRAB1004 | Regulatory depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0404. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB1002 less the straight line depreciation as per DRAB1003.
DRAB1005 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | While total actual additions represents actual data for Network Services and Standard Control Services, values at the category level are estimates due to the allocation of the Work in Progress asset category based on pro rata closing asset values at 30 June 2014 across applicable asset categories. | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB1006 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB1007 | Closing value for "other" asset (long life) value | Estimate | Estimate | Actual | The closing balances of the Network Services and Standard Control Services RAB are estimates owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB1001, DRAB1003 and DRAB1005). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB1001.
For "other" asset items with short lives:
DRAB1101 | Opening value | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1001. | Refer Data Source provided for DRAB0201. | Comprised of the following SA Power Networks' asset classes: Light Vehicles, IT / Office Equipment and share of Work in Progress (% estimated based on pro rata closing asset values).
DRAB1102 | Inflation addition | Estimate | Estimate | Actual | While actual CPI rates were applied, the inflation additions to the Network Services and Standard Control Services opening RAB values are estimates by virtue of the opening values reported against DRAB1101 being estimates. | Refer Data Source provided for DRAB0102. | The opening values as per DRAB1101 multiplied by the March 2014 on March 2013 movement in the ABS's "Weighted average of eight capital cities index".
DRAB1103 | Straight line depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0403. | Refer Data Source provided for DRAB0103. | Refer Methodologies and Assumptions provided for DRAB0403.
DRAB1104 | Regulatory depreciation | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB0404. | Refer Data Source provided for DRAB0103. | Regulatory depreciation, as confirmed by the outputs from the model as described in the Data Source, represents the inflation addition as per DRAB1102 less the straight line depreciation as per DRAB1103.
DRAB1105 | Actual additions (recognised in RAB) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1005. | Refer Data Source provided for DRAB0105. | Refer Methodologies and Assumptions provided for DRAB0405.
DRAB1106 | Disposals | Actual | Actual | Actual |  | Refer Data Source provided for DRAB0106.
DRAB1107 | Closing value for "other" asset (short life) value | Estimate | Estimate | Actual | The closing balances of the Network Services and Standard Control Services RAB are estimates owing to the fact that SA Power Networks has had to make a number of allocation estimates and assumptions in building the RAB roll forward (as described against DRAB1101, DRAB1103 and DRAB1105). | Refer Data Source provided for DRAB0207. | Refer Methodologies and Assumptions provided for DRAB1101.
Table 3.3.3 Total disaggregated RAB asset values
DRAB1201 | Overhead distribution assets less than 33kV (wires and poles) | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB0201 to DRAB0207. | Refer Data Sources provided for DRAB0201 to DRAB0207. | Refer to Methodologies and Assumptions provided for DRAB0201 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0201) and the closing value at 30 June 2014 (as per DRAB0207).
DRAB1202 | Underground distribution assets less than 33kV (cables, ducts etc) | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB0301 to DRAB0307. | Refer Data Sources provided for DRAB0301 to DRAB0307. | Refer to Methodologies and Assumptions provided for DRAB0301 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0301) and the closing value at 30 June 2014 (as per DRAB0307).
DRAB1203 | Distribution substations including transformers | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB0401 to DRAB0407. | Refer Data Sources provided for DRAB0401 to DRAB0407. | Refer to Methodologies and Assumptions provided for DRAB0401 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0401) and the closing value at 30 June 2014 (as per DRAB0407).
DRAB1204 | Overhead assets 33kV and above (wires and towers / poles etc) | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB0501 to DRAB0507. | Refer Data Sources provided for DRAB0501 to DRAB0507. | Refer to Methodologies and Assumptions provided for DRAB0501 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0501) and the closing value at 30 June 2014 (as per DRAB0507).
DRAB1205 | Underground assets 33kV and above (cables, ducts etc) | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB0601 to DRAB0607. | Refer Data Sources provided for DRAB0601 to DRAB0607. | Refer to Methodologies and Assumptions provided for DRAB0601 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0601) and the closing value at 30 June 2014 (as per DRAB0607).
DRAB1206 | Zone substations and transformers | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB0701 to DRAB0707. | Refer Data Sources provided for DRAB0701 to DRAB0707. | Refer to Methodologies and Assumptions provided for DRAB0701 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0701) and the closing value at 30 June 2014 (as per DRAB0707).
DRAB1207 | Easements | Actual | Actual | Actual |  | Refer Data Sources provided for DRAB0801 to DRAB0807. | Refer to Methodologies and Assumptions provided for DRAB0801 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0801) and the closing value at 30 June 2014 (as per DRAB0807).
DRAB1208 | Meters | Actual | Actual | Actual |  | Refer Data Sources provided for DRAB0901 to DRAB0907. | Refer to Methodologies and Assumptions provided for DRAB0901 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB0901) and the closing value at 30 June 2014 (as per DRAB0907).
DRAB1209 | Other assets with long lives (please specify) | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB1001 to DRAB1007. | Refer Data Sources provided for DRAB1001 to DRAB1007. | Refer to Methodologies and Assumptions provided for DRAB1001 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB1001) and the closing value at 30 June 2014 (as per DRAB1007).
DRAB1210 | Other assets with short lives (please specify) | Estimate | Estimate | Actual | Refer Reasons for Estimates provided for DRAB1101 to DRAB1107. | Refer Data Sources provided for DRAB1101 to DRAB1107. | Refer to Methodologies and Assumptions provided for DRAB1101 for a listing of SA Power Networks' asset classes included in this category. As stipulated in the AER's Instructions and Definitions document, values in this table should represent the average of the opening and closing values for each asset class: in this case the opening value at 1 July 2013 (as per DRAB1101) and the closing value at 30 June 2014 (as per DRAB1107).
Capital Contributions
DRAB13 | Value of Capital Contributions or Contributed Assets | Actual | Actual | Actual |  | Capital Contributions as reported in 2013-14 Annual RIN.
Table 3.3.4 Asset Lives
Table 3.3.4.1 Asset Lives - estimated service life of new assets
DRAB1401 | Overhead network assets less than 33kV (wires and poles) | Estimate | Estimate | Actual | Given that assets do not have a literal defined life span, estimated services lives (where > 0) provided, must by their nature be estimates rather than actuals. | Standard life values from: "AER, Electricity Distribution Network Service Providers Roll Forward Model, Version: 01, 26 June 2008" to be used by the AER to roll forward SA Power Networks' RAB values for the period 1 July 2010 to 30 June 2015. | Determined as the weighted average of estimated service lives for the SA Power Networks' depreciable asset classes comprising this asset category. Wherever the asset category did not apply to one or more of Network Services, Standard Control Services and Alternative Control Services, a nil value was reported in the "Actual" RAB worksheet.
DRAB1402 | Underground network assets less than 33kV (cables, ducts etc) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1403 | Distribution substations including transformers | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1404 | Overhead network assets 33kV and above (wires and towers / poles etc) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1405 | Underground network assets 33kV and above (cables, ducts etc) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1406 | Zone substations and transformers | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1407 | Meters | Actual | Actual | Estimate | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1408 | "Other" assets with long lives | Estimate | Estimate | Estimate | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
DRAB1409 | "Other" assets with short lives | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1401. | Refer Data Source provided for DRAB1401. | Refer to Methodologies and Assumptions provided for DRAB1401.
Table 3.3.4.2 Asset Lives - estimated residual service life
DRAB1501 | Overhead network assets less than 33kV (wires and poles) | Estimate | Estimate | Actual | Given that assets do not have a literal defined life span, estimated residual services lives (where > 0) provided, must by their nature be estimates rather than actuals. | Template 3.3: Assets (RAB) worksheet from the AER's 2013-14 Economic Benchmarking RIN; and "AER, Electricity Distribution Network Service Providers Roll Forward Model, Version: 01, 26 June 2008" to be used by the AER to roll forward SA Power Networks' RAB values for the period 1 July 2010 to 30 June 2015. | Estimated residual lives for each year were determined by dividing the closing RAB values at 30 June 2014 for SA Power Networks' depreciable asset classes comprising this asset category contained in Table 3.3.2 by the 2014-15 straight line depreciation charge as per the calculated outputs of the AER's Roll Forward Model (e.g. if the closing RAB value for depreciable assets in 2013-14 was $3,000,000 and the straight line depreciation for 2014-15 was $500,000, the estimated residual life in 2013-14 would be ($3,000,000/$500,000 = 6 years). Wherever the asset category did not apply to one or more of Network Services, Standard Control Services and Alternative Control Services, a nil value was reported in the "Actual" RAB worksheet.
DRAB1502 | Underground network assets less than 33kV (cables, ducts etc) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1503 | Distribution substations including transformers | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1504 | Overhead network assets 33kV and above (wires and towers / poles etc) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1505 | Underground network assets 33kV and above (cables, ducts etc) | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1506 | Zone substations and transformers | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1507 | Meters | Actual | Actual | Estimate | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1508 | "Other" assets with long lives | Estimate | Estimate | Estimate | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.
DRAB1509 | "Other" assets with short lives | Estimate | Estimate | Actual | Refer Reason for Estimate provided for DRAB1501. | Refer Data Sources provided for DRAB1501. | Refer to Methodologies and Assumptions provided for DRAB1501.

## 3.4 Operational Data
Table / Variable Code | Description | Actual / Estimate | Reason for Estimate (if applicable) | If estimate, reason it is best estimate | Data Source(s) | Methodologies and Assumptions | Further Assumptions
3.4 Operational data worksheet
Table 3.4.1 Energy delivery
DOPED01 | Total energy delivered | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data extracted from Sales Model.
Table 3.4.1.1 Energy grouping - delivery by chargeable quantity
DOPED0201 | Energy Delivery where time of use is not a determinant | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data extracted from Sales Model. Includes Residential (excl Controlled load) & Business Single tariff volumes
DOPED0202 | Energy Delivery at On-peak times | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft 2014 WAPC Pricing Return | Data is based on a tariff-applied basis Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Draft 2014 WAPC Pricing Return. Includes Business 2 rates, Contracted LV and HV Demand peak volumes
DOPED0203 | Energy Delivery at Shoulder times |  | SAPN does not have any shoulder period charges |  | Nil | Nil
DOPED0204 | Energy Delivery at Off-peak times | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft 2014 WAPC Pricing Return | Data is based on a tariff-applied basis Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Draft 2014 WAPC Pricing Return. Includes all off- peak volumes
DOPED0205 | Controlled load energy deliveries | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data is extracted from the Sales Model. Includes Controlled Load volumes (primarily Residential)
DOPED0206 | Energy Delivery to unmetered supplies | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data is extracted from the Sales Model. Includes 12 & 24 Hour Unmetered volumes
Table 3.4.1.2 Energy - received from TNSP and other DNSPs by time of receipt
DOPED0301 | Energy into DNSP network at On-peak times | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Purchases and Customer Segment Data (internal) | Total energy from ElectraNet is agreed with ElectraNet each 6 months as part of our financial accounts audit (by Deloitte). Based on work day/time of day. Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Purchases and Customer Segment Data file.
DOPED0302 | Energy into DNSP network at Shoulder times |  | SAPN does not have any shoulder period charges |  | Nil | Nil
DOPED0303 | Energy into DNSP network at Off-peak times | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Purchases and Customer Segment Data (internal) | Total energy from ElectraNet is agreed with ElectraNet each 6 months as part of our financial accounts audit (by Deloitte). Based on work day/time of day. Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Purchases and Customer Segment Data file.
DOPED0304 | Energy received from TNSP and other DNSPs not included in the above categories |  | SAPN has no other energy received |  | Nil | Nil
Table 3.4.1.3 Energy - received into DNSP system from embedded generation by time of receipt
DOPED0401 | Energy into DNSP network at On-peak times from non-residential embedded generation | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Purchases and Customer Segment Data (internal) | Summation of individual generators export. Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Purchases and Customer Segment Data file.
DOPED0402 | Energy into DNSP network at Shoulder times from non-residential embedded generation |  | SAPN does not have any shoulder periods |  | Nil | Nil
DOPED0403 | Energy into DNSP network at Off-peak times from non-residential embedded generation | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Purchases and Customer Segment Data (internal) | Summation of individual generators export. Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Purchases and Customer Segment Data file.
DOPED0404 | Energy received from embedded generation not included in above categories from non-residential embedded generation |  | SAPN has no other energy received |  | Nil | Nil
DOPED0405 | Energy into DNSP network at On-peak times from residential embedded generation | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Purchases and Customer Segment Data (internal) | Based on approved PV capacity installed with daily output profiles determined by panel efficiency and sample data, that is an estimate of the gross output of PV. An estimate (non TOU) for residential in-house has also been made. The nett of these two numbers reflects the actual nett PV exported via meters as per pricing proposal WAPC data. Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Purchases and Customer Segment Data file.
DOPED0406 | Energy into DNSP network at Shoulder times from residential embedded generation |  | SAPN does not have any shoulder periods |  | Nil | Nil
DOPED0407 | Energy into DNSP network at Off-peak times from residential embedded generation | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Purchases and Customer Segment Data (internal) | Based on approved PV capacity installed with daily output profiles determined by panel efficiency and sample data, that is an estimate of the gross output of PV. An estimate (non TOU) for residential in-house has also been made. The nett of these two numbers reflects the actual nett PV exported via meters as per pricing proposal WAPC data. Actual data is extracted from the Sales Model for all energy received. The split between peak and off-peak energy received is based on quantities in the Purchases and Customer Segment Data file.
DOPED0408 | Energy received from embedded generation not included in above categories from residential embedded generation |  | SAPN has no other energy received |  | Nil | Nil
Table 3.4.1.4 Energy grouping - customer type or class
DOPED0501 | Residential customers energy deliveries | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft 2014 WAPC Pricing Return | Data is based on a tariff-applied basis Actual data is extracted from Sales Model (internal). Draft WAPC Pricing Return 2014 is used to determine the proportion of controlled load energy deliveries that should be allocated to residential customers. Includes all residential including contracted demand, peak and non-peak volumes.
DOPED0502 | Non-residential customers not on demand tariffs energy deliveries | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) Draft 2014 WAPC Pricing Return | Data is based on a tariff-applied basis Actual data is extracted from Sales Model (internal). Draft WAPC Pricing Return 2014 is used to determine the proportion of controlled load energy deliveries that should be allocated to residential customers. Includes all business including 1 & 2 rate; peak & non-peak volumes
DOPED0503 | Non-residential low voltage demand tariff customers energy deliveries | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data is extracted from Sales Model (internal). Includes all LV Demand Rates (kVA & kW) including contracted demand, peak and non-peak volumes
DOPED0504 | Non-residential high voltage demand tariff customers energy deliveries | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data is extracted from Sales Model (internal). Includes all HV Demand Rates (kVA & kW) including contracted demand, peak and non-peak volumes
DOPED0505 | Other Customer Class Energy Deliveries | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based on a tariff-applied basis Actual data is extracted from Sales Model (internal). Includes all 12 & 24 hour unmetered volumes
3.4.2 Customer numbers
Table 3.4.2.1 Distribution customer numbers by customer type or class
DOPCN0101 | Residential customer numbers | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Draft 2014 WAPC Pricing Return Total from DOPCN02 | Average by category estimated based on total supply charge days/no. of days in year, from the Draft 2014 WAPC Pricing Return. The category averages are then apportioned to reconcile with total customer numbers as reported in 3.4.2.2 (DOPCNO2).
DOPCN0102 | Non-residential customers not on demand tariff customer numbers | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Draft 2014 WAPC Pricing Return Total from DOPCN02 | Average by category estimated based on total supply charge days/no. of days in year, from the Draft 2014 WAPC Pricing Return. The category averages are then apportioned to reconcile with total customer numbers as reported in 3.4.2.2 (DOPCNO2).
DOPCN0103 | Low voltage demand tariff customer numbers | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Draft 2014 WAPC Pricing Return Total from DOPCN02 | Average by category estimated based on total supply charge days/no. of days in year, from the Draft 2014 WAPC Pricing Return. The category averages are then apportioned to reconcile with total customer numbers as reported in 3.4.2.2 (DOPCNO2).
DOPCN0104 | High voltage demand tariff customer numbers | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Draft 2014 WAPC Pricing Return Total from DOPCN02 | Average by category estimated based on total supply charge days/no. of days in year, from the Draft 2014 WAPC Pricing Return. The category averages are then apportioned to reconcile with total customer numbers as reported in 3.4.2.2 (DOPCNO2).
DOPCN0105 | Unmetered Customer Numbers | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Draft 2014 WAPC Pricing Return Total from DOPCN02 | Average by category estimated based on total supply charge days/no. of days in year, from the Draft 2014 WAPC Pricing Return. The category averages are then apportioned to reconcile with total customer numbers as reported in 3.4.2.2 (DOPCNO2).
DOPCN0106 | Other Customer Numbers |  | SAPN has no other Other customers |  | Nil | Nil
DOPCN01 | Total customer numbers |  | Sum of estimates in rows above |  | Rows above | Sum of DOPCNO101-DOPCN0106
Table 3.4.2.2 Distribution customer numbers by location on the network
DOPCN0201 | Customers on CBD network | Actual |  |  | CIS/OV, GIS, OMS, SCADA (where available) and load recorders for feeder demand readings. | Calculations are in accordance with our procedures: o Obtain all feeder lengths as at 30 June o Obtain the maximum demand for the period ending 30 June o If the feeder name begins with CBD and the transformer is situated within the CBD boundary defined by the Distribution Code and the feeder plans, assign the feeder to the SCONRRR category ‘CBD’ o Based on the feeder length and maximum demand, determine the load per km for all other feeders. Use the actual maximum demand over the reporting period where available, otherwise, use the forecast peak o If the demand per km > 0.3 MVA and the feeder is not a ‘CBD’ feeder, assign the feeder to the SCONRRR category ‘Urban’ o If the demand per km ≤ 0.3 MVA but the feeder is situated in the general metropolitan area or a regional metropolitan area as defined in the Distribution Code, generally assign the feeder to the SCONRRR category ‘Urban’ o If the feeder is not ‘CBD’ or ‘Urban’ and the feeder route length is ≤ 200km, assign the feeder to the SCONRRR category ‘Rural Short’ o If the feeder is not ‘CBD’ or ‘Urban’ and the feeder route length is > 200km, assign the feeder to the SCONRRR category ‘Rural Long’ o NMI’s are linked to transformers, which are linked to feeders (via CIS/OV, GIS and OMS), which are then mapped to the feeder categories as calculated above and then summated to obtain the customers per feeder category
DOPCN0202 | Customers on Urban network | Actual
DOPCN0203 | Customers on Short rural network | Actual
DOPCN0204 | Customers on Long rural network | Actual
DOPCN02 | Total customer numbers | Actual |  |  | Rows above | The total customer numbers are the summation of the numbers from DOPCN0201-0204
Table 3.4.2.4 Unmetered Supply
DOPCN0301 | Number of unmetered connections reported in customer numbers in the economic benchmarking RIN | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Same as DOPCN0105.
DOPCN0302 | Unmetered connections nor reported in customer numbers in the economic benchmarking RIN | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. | Nil | Nil
DOPCN0303 | Total unmetered connections | Estimate | SAPN does not separately record actual information in this category | Relying on opinion of experienced manager using what reliable data is available. |  | Sum of DOPCN0301 and DOPCN0303
3.4.3 System demand
Table 3.4.3.1 Annual system maximum demand characteristics at the zone substation level – MW measure
DOPSD0101 | Non-coincident Summated Raw System Annual Maximum Demand | Estimate | Not all of SA Power Networks’ substations are presently SCADA enabled and those that currently are have not all been monitored since 2005/06. Under the new NER definition of a “Zone Sub”, many of SA Power Networks’ smaller sites are not SCADA enabled. Most of these sites consist of 1 or 2 transformers with a capacity of less than 1.5MVA and together represent less than 10-15% of the total load supplied by SA Power Networks and an even smaller percentage of the load supplied by any given Transmission Connection Point. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | The following steps were undertaken to derive the non-coincident and coincident actual, 10 and 50 PoE, MW and MVA demand values at the zone substation level: For each zone substation, the actual non-coincident readings and reconciled non-coincident, 10 and 50 PoE MW values were summated to arrive at the values submitted within fields DOPSD0101, DOPSD0102 and DOPSD0103 respectively. This summation excluded those substations categorised within variable DPA0602 in Table 6.2.2 as “Stage 2” transformations to avoid double counting of loads at both a Stage 1 and Stage 2 level as well as those loads supplied by unregulated zone substation transformer assets. Similarly, the reconciled coincident, zone substation actual, 10 and 50 PoE MW values were summated to arrive at the values submitted within fields, DOPSD0104, DOPSD0105 and DOPSD0106 respectively. All non-coincident and coincident MVAr values measured and at the 10 and 50 PoE level were separately summated. Again, this summation excluded those substations categorised within DPA0602 of Table 6.2.2 as “Stage 2” transformations to avoid double counting of loads at both a Stage 1 and Stage 2 level. The resultant MW and MVAr totals were then converted to the non-coincident and coincident MVA value using the formula; MVA=√(〖MW〗^2+ 〖MVAr〗^2 ) The calculated non-coincident and coincident actual MVA values and at 10 and 50 PoE were then entered within DOPSD0201, DOPSD0202, DOPSD0203, DOPSD0204, DOPSD0205 and DOPSD0206 respectively. | The following assumptions were made in preparing the data provided: 1. “Coincident” refers to the time of system peak (ie SA Power Networks load only and therfore excludes the influence of and ElectraNet direct connected customers). 2. For non-continuously metered zone substations, weather corrected forecasts were not produced. Instead, SA Power Networks employed the methodology as described in Section 2.5. 3. For non-continuously metered zone substations, the time of day peak has been assumed to be when the overall system’s demand peaks (ie: coincident and non-coincident peaks are at the same time). 4. For reconciliation purposes, sub-transmission substations (ie connection points) were reconciled to the trend of the State demand (flat) as per AEMO’s National Electricity Forecasting Report (Chapter 5, Section 5.4). Zone substations were then reconciled to the corresponding reconciled sub-transmission substation trend value. 5. Where actual demand data is only available in Amps, the MW and MVA values have been determined assuming nominal voltage and the PF of the upstream sub-transmission substation. 6. Model Parameters: • PV – no future time of day shift allowed for (ie: peak assumed to remain constant at same time as 2013/14 measured peak); • Future PV growth extracted from Energia created summary graphs (2014/15 = 14%, 2015/16 = 12%, 2016/17 = 13.5%, 2017/18 = 9%, 2018/19 = 8.2%, 2019/20 = 8.5%); • PF – for all continuously metered sites, an average over the last 1, 2 or 3 years was applied; • Coincidence Factor – all continuously metered site’s the coincidence factor was held constant at the 2013/14 measured value. • Major customers, spot loads and transfers – no adjustment factor between 10 PoE and 50 PoE forecasts. Refer SAPN, "2013/14 Economic Benchmarking RIN Basis of Preparation ", 9 October 2014 document P7 for additional comments
DOPSD0102 | Non-coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0101 | Refer assumptions for DOPSD0101
DOPSD0103 | Non-coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0101 | Refer assumptions for DOPSD0101
DOPSD0104 | Coincident Raw System Annual Maximum Demand | Estimate | Not all of SA Power Networks’ substations are presently SCADA enabled and those that currently are have not all been monitored since 2005/06. Under the new NER definition of a “Zone Sub”, many of SA Power Networks’ smaller sites are not SCADA enabled. Most of these sites consist of 1 or 2 transformers with a capacity of less than 1.5MVA and together represent less than 10-15% of the total load supplied by SA Power Networks and an even smaller percentage of the load supplied by any given Transmission Connection Point. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0101 | Refer assumptions for DOPSD0101
DOPSD0105 | Coincident Weather Adjusted System Annual Maximum Demand 10% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0101 | Refer assumptions for DOPSD0101
DOPSD0106 | Coincident Weather Adjusted System Annual Maximum Demand 50% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0101 | Refer assumptions for DOPSD0101
Table 3.4.3.2 Annual system maximum demand characteristics at the transmission connection point – MW measure
DOPSD0107 | Non-coincident Summated Raw System Annual Maximum Demand | Estimate | SA Power Networks operates a meshed 66kV sub-transmission network within metropolitan Adelaide. At the time of segregation of the South Australian transmission and distribution networks, not all metropolitan 66kV buses were allocated to SA Power Networks. Several of these buses contain direct connection of generation sources and TNSP owned 66kV lines. Therefore, for these regions it is not simply a matter of summating the output of the TNSP’s connection point transformers to determine the load supplied by the TNSP to SA Power Networks. In order to determine the load in some regions, SA Power Networks has created pre-defined summations within its SCADA system (SubsLoad) to calculate the total demand delivered by the TNSP in each area. These values have been used within the values contained within the RIN. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | The following steps were undertaken to derive the non-coincident and coincident actual, 10 and 50 PoE, MW and MVA demand values at the connection point level: The actual and reconciled non-coincident, connection point substation 10 and 50 PoE MW values for 2013/14 were summated to arrive at the values submitted within field DOPSD107, DOPSD108 and DOPSD0109 respectively. Similarly, the reconciled coincident, connection point actual, 10 and 50 PoE MW values for each 2014/14 were summated to arrive at the values submitted within field DOPSD0110, DOPSD0111 and DOPSD0112 respectively. All corresponding non-coincident and coincident MVAr forecast values for a given year were separately summated. The resultant MW and MVAr totals were then converted to the non-coincident and coincident MVA value using the formula; MVA=√(〖MW〗^2+ 〖MVAr〗^2 ) The calculated non-coincident and coincident MVA values were then entered within DOPSD0207, DOPSD0208, DOPSD0209, DOPSD0210, DOPSD0211 and DOPSD0212 respectively. | The following assumptions were made in preparing the data provided: 1. For reconciliation purposes, sub-transmission substations (ie connection points) were reconciled to the trend of the State demand (flat) as per AEMO’s National Electricity Forecasting Report (Chapter 5, Section 5.4). Zone substations were then reconciled to the corresponding reconciled sub-transmission substation trend value. 2. Model Parameters: • PV – no future time of day shift allowed for (ie: peak assumed to remain constant at same time as 2013/14 measured peak); • Future PV growth extracted from Energia created summary graphs (2014/15 = 14%, 2015/16 = 12%, 2016/17 = 13.5%, 2017/18 = 9%, 2018/19 = 8.2%, 2019/20 = 8.5%); • PF – for all continuously metered sites, an average over the last 1, 2 or 3 years was applied; • Coincidence Factor – all continuously metered site’s the coincidence factor was held constant at the 2013/14 measured value. • Major customers, spot loads and transfers – no adjustment factor between 10 PoE and 50 PoE forecasts Refer SAPN, "2013/14 Economic Benchmarking RIN Basis of Preparation ", 9 October 2014 document P10 for additional comments
DOPSD0108 | Non-coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0107 | Refer assumptions for DOPSD0107
DOPSD0109 | Non-coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE | n/a | PoE values are calculated not actually measured |  | Load forecast model, SCADA | Refer methodology for DOPSD0107 | Refer assumptions for DOPSD0107
DOPSD0110 | Coincident Raw System Annual Maximum Demand | Estimate | SA Power Networks operates a meshed 66kV sub-transmission network within metropolitan Adelaide. At the time of segregation of the South Australian transmission and distribution networks, not all metropolitan 66kV buses were allocated to SA Power Networks. Several of these buses contain direct connection of generation sources and TNSP owned 66kV lines. Therefore, for these regions it is not simply a matter of summating the output of the TNSP’s connection point transformers to determine the load supplied by the TNSP to SA Power Networks. In order to determine the load in some regions, SA Power Networks has created pre-defined summations within its SCADA system (SubsLoad) to calculate the total demand delivered by the TNSP in each area. These values have been used within the values contained within the RIN. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0107. This number includes all embedded generation at the time of the coincident peak. | Refer assumptions for DOPSD0107
DOPSD0111 | Coincident Weather Adjusted System Annual Maximum Demand 10% POE | n/a | PoE values are calculated not actually measured |  | Load forecast model, SCADA | Refer methodology for DOPSD0107 | Refer assumptions for DOPSD0107
DOPSD0112 | Coincident Weather Adjusted System Annual Maximum Demand 50% POE | n/a | PoE values are calculated not actually measured |  | Load forecast model, SCADA | Refer methodology for DOPSD0107 | Refer assumptions for DOPSD0107
Table 3.4.3.3 Annual system maximum demand characteristics at the zone substation level – MVA measure
DOPSD0201 | Non–coincident Summated Raw System Annual Maximum Demand | Estimate | Not all of SA Power Networks’ substations are presently SCADA enabled. Under the new NER definition of a “Zone Sub”, many of SA Power Networks’ smaller sites are not SCADA enabled. Most of these sites consist of 1 or 2 transformers with a capacity of less than 1.5MVA and together represent less than 10-15% of the total load supplied by SA Power Networks and an even smaller percentage of the load supplied by any given Transmission Connection Point. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | The following steps were undertaken to derive the non-coincident and coincident actual, 10 and 50 PoE, MW and MVA demand values at the zone substation level: For each zone substation, the actual non-coincident readings and reconciled non-coincident, 10 and 50 PoE MW values were summated to arrive at the values submitted within fields DOPSD0101, DOPSD0102 and DOPSD0103 respectively. This summation excluded those substations categorised within variable DPA0602 in Table 6.2.2 as “Stage 2” transformations to avoid double counting of loads at both a Stage 1 and Stage 2 level as well as those loads supplied by unregulated zone substation transformer assets. Similarly, the reconciled coincident, zone substation actual, 10 and 50 PoE MW values were summated to arrive at the values submitted within fields, DOPSD0104, DOPSD0105 and DOPSD0106 respectively. All non-coincident and coincident MVAr values measured and at the 10 and 50 PoE level were separately summated. Again, this summation excluded those substations categorised within DPA0602 of Table 6.2.2 as “Stage 2” transformations to avoid double counting of loads at both a Stage 1 and Stage 2 level. The resultant MW and MVAr totals were then converted to the non-coincident and coincident MVA value using the formula; MVA=√(〖MW〗^2+ 〖MVAr〗^2 ) The calculated non-coincident and coincident actual MVA values and at 10 and 50 PoE were then entered within DOPSD0201, DOPSD0202, DOPSD0203, DOPSD0204, DOPSD0205 and DOPSD0206 respectively. | The following assumptions were made in preparing the data provided: 1. “Coincident” refers to the time of system peak (ie SA Power Networks load only and therfore excludes the influence of and ElectraNet direct connected customers). 2. For non-continuously metered zone substations, weather corrected forecasts were not produced. Instead, SA Power Networks employed the methodology as described in Section 2.5. 3. For non-continuously metered zone substations, the time of day peak has been assumed to be when the overall system’s demand peaks (ie: coincident and non-coincident peaks are at the same time). 4. For reconciliation purposes, sub-transmission substations (ie connection points) were reconciled to the trend of the State demand (flat) as per AEMO’s National Electricity Forecasting Report (Chapter 5, Section 5.4). Zone substations were then reconciled to the corresponding reconciled sub-transmission substation trend value. 5. Where actual demand data is only available in Amps, the MW and MVA values have been determined assuming nominal voltage and the PF of the upstream sub-transmission substation. 6. Model Parameters: • PV – no future time of day shift allowed for (ie: peak assumed to remain constant at same time as 2013/14 measured peak); • Future PV growth extracted from Energia created summary graphs (2014/15 = 14%, 2015/16 = 12%, 2016/17 = 13.5%, 2017/18 = 9%, 2018/19 = 8.2%, 2019/20 = 8.5%); • PF – for all continuously metered sites, an average over the last 1, 2 or 3 years was applied; • Coincidence Factor – all continuously metered site’s the coincidence factor was held constant at the 2013/14 measured value. • Major customers, spot loads and transfers – no adjustment factor between 10 PoE and 50 PoE forecasts. Refer SAPN, "2013/14 Economic Benchmarking RIN Basis of Preparation ", 9 October 2014 document P7 for additional comments
DOPSD0202 | Non–coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0201 | Refer assumptions for DOPSD0201
DOPSD0203 | Non–coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0201 | Refer assumptions for DOPSD0201
DOPSD0204 | Coincident Raw System Annual Maximum Demand | Estimate | Not all of SA Power Networks’ substations are presently SCADA enabled. Under the new NER definition of a “Zone Sub”, many of SA Power Networks’ smaller sites are not SCADA enabled. Most of these sites consist of 1 or 2 transformers with a capacity of less than 1.5MVA and together represent less than 10-15% of the total load supplied by SA Power Networks and an even smaller percentage of the load supplied by any given Transmission Connection Point. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0201 | Refer assumptions for DOPSD0201
DOPSD0205 | Coincident Weather Adjusted System Annual Maximum Demand 10% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0201 | Refer assumptions for DOPSD0201
DOPSD0206 | Coincident Weather Adjusted System Annual Maximum Demand 50% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0201 | Refer assumptions for DOPSD0201
Table 3.4.3.4 Annual system maximum demand characteristics at the transmission connection point – MVA measure
DOPSD0207 | Non–coincident Summated Raw System Annual Maximum Demand | Estimate | SA Power Networks operates a meshed 66kV sub-transmission network within metropolitan Adelaide. At the time of segregation of the South Australian transmission and distribution networks, not all metropolitan 66kV buses were allocated to SA Power Networks. Several of these buses contain direct connection of generation sources and TNSP owned 66kV lines. Therefore, for these regions it is not simply a matter of summating the output of the TNSP’s connection point transformers to determine the load supplied by the TNSP to SA Power Networks. In order to determine the load in some regions, SA Power Networks has created pre-defined summations within its SCADA system (SubsLoad) to calculate the total demand delivered by the TNSP in each area. These values have been used within the values contained within the RIN. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | The following steps were undertaken to derive the non-coincident and coincident actual, 10 and 50 PoE, MW and MVA demand values at the connection point level: The actual and reconciled non-coincident, connection point substation 10 and 50 PoE MW values for 2013/14 were summated to arrive at the values submitted within field DOPSD107, DOPSD108 and DOPSD0109 respectively. Similarly, the reconciled coincident, connection point actual, 10 and 50 PoE MW values for each 2014/14 were summated to arrive at the values submitted within field DOPSD0110, DOPSD0111 and DOPSD0112 respectively. All corresponding non-coincident and coincident MVAr forecast values for a given year were separately summated. The resultant MW and MVAr totals were then converted to the non-coincident and coincident MVA value using the formula; MVA=√(〖MW〗^2+ 〖MVAr〗^2 ) The calculated non-coincident and coincident MVA values were then entered within DOPSD0207, DOPSD0208, DOPSD0209, DOPSD0210, DOPSD0211 and DOPSD0212 respectively. | The following assumptions were made in preparing the data provided: 1. For reconciliation purposes, sub-transmission substations (ie connection points) were reconciled to the trend of the State demand (flat) as per AEMO’s National Electricity Forecasting Report (Chapter 5, Section 5.4). Zone substations were then reconciled to the corresponding reconciled sub-transmission substation trend value. 2. Model Parameters: • PV – no future time of day shift allowed for (ie: peak assumed to remain constant at same time as 2013/14 measured peak); • Future PV growth extracted from Energia created summary graphs (2014/15 = 14%, 2015/16 = 12%, 2016/17 = 13.5%, 2017/18 = 9%, 2018/19 = 8.2%, 2019/20 = 8.5%); • PF – for all continuously metered sites, an average over the last 1, 2 or 3 years was applied; • Coincidence Factor – all continuously metered site’s the coincidence factor was held constant at the 2013/14 measured value. • Major customers, spot loads and transfers – no adjustment factor between 10 PoE and 50 PoE forecasts Refer SAPN, "2013/14 Economic Benchmarking RIN Basis of Preparation ", 9 October 2014 document P10 for additional comments
DOPSD0208 | Non–coincident Summated Weather Adjusted System Annual Maximum Demand 10% POE | Estimate | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0207 | Refer assumptions for DOPSD0207
DOPSD0209 | Non–coincident Summated Weather Adjusted System Annual Maximum Demand 50% POE | n/a | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0207 | Refer assumptions for DOPSD0207
DOPSD0210 | Coincident Raw System Annual Maximum Demand | Estimate | SA Power Networks operates a meshed 66kV sub-transmission network within metropolitan Adelaide. At the time of segregation of the South Australian transmission and distribution networks, not all metropolitan 66kV buses were allocated to SA Power Networks. Several of these buses contain direct connection of generation sources and TNSP owned 66kV lines. Therefore, for these regions it is not simply a matter of summating the output of the TNSP’s connection point transformers to determine the load supplied by the TNSP to SA Power Networks. In order to determine the load in some regions, SA Power Networks has created pre-defined summations within its SCADA system (SubsLoad) to calculate the total demand delivered by the TNSP in each area. These values have been used within the values contained within the RIN. | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0207 | Refer assumptions for DOPSD0207
DOPSD0211 | Coincident Weather Adjusted System Annual Maximum Demand 10% POE | n/a | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0207 | Refer assumptions for DOPSD0207
DOPSD0212 | Coincident Weather Adjusted System Annual Maximum Demand 50% POE | n/a | PoE values are calculated not actually measured | Relying on opinion of experienced manager using what reliable data is available. | Load forecast model, SCADA | Refer methodology for DOPSD0207 | Refer assumptions for DOPSD0207
Table 3.4.3.5 Power factor conversion between MVA and MW
DOPSD0301 | Average overall network power factor conversion between MVA and MW | Estimate | Actual values for non-SCADA substations need to be estimated. | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0301 - Average overall network power factor 1. Given this is intended to represent the average PF of the entire network, the non-coincident, actual connection point values in DOPSD0107 have been divided by those contained in DOPSD0207 to arrive at the values entered within DOPSD0301 of the RIN. | SA Power Networks does not individually SCADA monitor its distribution transformers, it has been assumed that the value for these parameters will be equivalent to that of the combined 11 and 7.6kV networks from which the vast majority of SA Power Networks’ distribution transformers are supplied, with the MVAr values corrected for the removal of any 11 or 7.6kV capacitor banks. Similarly, SA Power Networks does not individually SCADA monitor its SWER systems, it has been assumed that the value for these parameters will be equivalent to the “corrected” values of the 33kV networks from which the vast majority of SA Power Networks’ SWER systems are supplied with the MVAr values corrected for the removal of any 33kV capacitor banks. The following assumptions have been made in preparing the data submitted: DOPSD0301 - Average overall network power factor 1. The non coincident actual, MW and MVA values at the connection point level have been used as these represent the average PF seen by the TNSP’s network at the time of each connection point’s peak. The PF submitted includes the effect of any capacitor banks which may or may not have been on at the time the demand readings were recorded.
DOPSD0302 | Average power factor conversion for low voltage distribution lines | Estimate | Given that SA Power Networks does not individually SCADA monitor its distribution transformers, it has been assumed that the value for these parameters will be equivalent to that of the combined 11kV and 7.6kV networks from which the vast majority of SA Power Networks’ distribution transformers are supplied with the MVAr values corrected for the removal of any 11kV or 7.6kV capacitor banks. | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0302 - Average power factor conversion for low voltage 1. Given this value is intended to represent the average PF of the entire LV network and the majority of SA Power Networks’ distribution transformers are supplied by the 11 and 7.6kV networks, the non-coincident actual MW and MVAr values for all 11 and 7.6kV zone substations have been summated according to each substation’s secondary voltage (eg 11and 7.6kV) to provide a summated value of the MW and MVAr supplied by the 11kV and 7.6kV networks. 2. The final MVAr value was then adjusted to remove the effect of any 11kV or 7.6kV capacitor banks in each year as these reduce the MVArs measured at the 11 and 7.6kV terminals of the zone substation’s transformers. 3. The summated MW and “adjusted” MVAr values at 11 and 7.6kV were then converted to MVA using Pythagoras’ Theorem. The MW sum was then divided by the result of the MVA calculation to arrive at the average LV PF value per annum entered within DOPSD0302 of the RIN. | SA Power Networks does not individually SCADA monitor its distribution transformers, it has been assumed that the value for these parameters will be equivalent to that of the combined 11 and 7.6kV networks from which the vast majority of SA Power Networks’ distribution transformers are supplied, with the MVAr values corrected for the removal of any 11 or 7.6kV capacitor banks. Similarly, SA Power Networks does not individually SCADA monitor its SWER systems, it has been assumed that the value for these parameters will be equivalent to the “corrected” values of the 33kV networks from which the vast majority of SA Power Networks’ SWER systems are supplied with the MVAr values corrected for the removal of any 33kV capacitor banks. The following assumptions have been made in preparing the data submitted: DOPSD0302 - Average power factor conversion for low voltage 2. Given the lack of metering at LV level, all distribution transformers have been assumed to be connected to the 11 & 7.6kV networks. Whilst there are distribution transformers directly connected to the 33kV and SWER networks (largely supplied from the 33kV sub-transmission network), it is not anticipated that these customer’s PF values will vary greatly (if at all) from the vast majority of those customers supplied by the LV networks primarily supplied by both the 11 and 7.6kV networks.
DOPSD0303 | Average power factor conversion for 3.3 kV lines | Estimate | Refer 'Basis of Preparation - Network Planning Variables' attached | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0303 - Average power factor conversion for 3.3kV 1. SA Power Networks separately summated the MW and MVAr values for all zone substations with a secondary voltage of 3.3kV. These summated values were then converted to MVA using Pythagoras’ Theorem with the summated MW value being divided by the calculated MVA value. The result was then entered into within DOPSD0303 of the RIN. | All customers supplied at 6.6kV and 3.3kV are supplied from dedicated zone substation transformers with all secondary cable / overhead connection assets being owned by the customer (eg cables). As such, SA Power Networks does not operate any 6.6 or 3.3kV feeders, hence the reason these voltages are not contained within Tables 3.5.1.1, 3.5.1.2, 3.5.1.3 or 3.5.1.4.
DOPSD0304 | Average power factor conversion for 6.6 kV lines | Estimate | Refer 'Basis of Preparation - Network Planning Variables' attached | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0304 - Average power factor conversion for 6.6kV 1. SA Power Networks separately summated the MW and MVAr values for all zone substations with a secondary voltage of 6.6kV. These summated values were then converted to MVA using Pythagoras’ Theorem with the summated MW value being divided by the calculated MVA value. The result was then entered into within DOPSD0304 of the RIN. | All customers supplied at 6.6kV and 3.3kV are supplied from dedicated zone substation transformers with all secondary cable / overhead connection assets being owned by the customer (eg cables). As such, SA Power Networks does not operate any 6.6 or 3.3kV feeders, hence the reason these voltages are not contained within Tables 3.5.1.1, 3.5.1.2, 3.5.1.3 or 3.5.1.4.
DOPSD0305 | Average power factor conversion for 7.6 kV lines | Estimate | Refer 'Basis of Preparation - Network Planning Variables' attached | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0305 - Average power factor conversion for 7.6kV 1. SA Power Networks summated the MW and MVAr values for all zone substations with a secondary voltage of 7.6kV. These summated values were then converted to MVA using Pythagoras’ Theorem with the summated MW value being divided by the calculated MVA value. The result was then entered into within DOPSD0305 of the RIN. DOPSD0306 - Average power factor conversion for 11kV 1. SA Power Networks summated the MW and MVAr values for all zone substations with a secondary voltage of 11kV. These summated values were then converted to MVA using Pythagoras’ Theorem with the summated MW value being divided by the calculated MVA value. The result was then entered into within DOPSD0306 of the RIN. DOPSD0307 - Average power factor conversion for SWER 1 This section are intended to represent the average PF of the SWER network, the MW and MVAr values used to generate the values contained in DOPSD0102 and DOPSD0202 have been added according to each substation’s secondary voltage (ie 33kV) to provide a summated value of the MW and MVAr supplied by the 33kV network. 2 The final MVAr value has then been adjusted to remove the effect of any 33kV capacitor banks as these reduce the MVArs seen at the 33kV terminals of the zone substation transformers. 3 The summated MW and adjusted MVAr values at 33kV have then been converted to MVA using Pythagoras’ Theorem. The MW sum was then divided by the result of this MVA calculation to arrive at the average SWER PF value entered within DOPSD0307 of the RIN. DOPSD0308 - Average power factor conversion for 22kV 1 Not applicable. Voltage not operated by SA Power Networks. DOPSD0309 - Average power factor conversion for 33kV 1 In order to determine the PF of the 33kV network, SA Power Networks separately summated the MW and MVAr values for all zone substations and connection points with a secondary voltage of 33kV. 2 These summated values were then converted to MVA using Pythagoras’ Theorem. 3 The summated MW value was then divided by the calculated MVA value. The result was then entered into DOPSD0309 of the RIN. DOPSD0310 - Average power factor conversion for 44kV 1 Not applicable. Voltage not operated by SA Power Networks. DOPSD0311 - Average power factor conversion for 66kV 1 In order to determine the PF of the 66kV network, SA Power Networks separately summated the MW and MVAr values for all zone substations and connection points with a secondary voltage of 66kV. 2 These summated values were then converted to MVA using Pythagoras’ Theorem. 3 The summated MW value was then divided by the calculated MVA value. The result was then entered into DOPSD0311 of the RIN. DOPSD0312 - Average power factor conversion for 110kV 1 Not applicable. Voltage not operated by SA Power Networks. DOPSD0313 - Average power factor conversion for 132kV 1 Not applicable. Voltage not operated by SA Power Networks DOPSD0314 - Average power factor conversion for 220kV 1 Not applicable. Voltage not operated by SA Power Networks | SA Power Networks does not individually SCADA monitor its distribution transformers, it has been assumed that the value for these parameters will be equivalent to that of the combined 11 and 7.6kV networks from which the vast majority of SA Power Networks’ distribution transformers are supplied, with the MVAr values corrected for the removal of any 11 or 7.6kV capacitor banks. Similarly, SA Power Networks does not individually SCADA monitor its SWER systems, it has been assumed that the value for these parameters will be equivalent to the “corrected” values of the 33kV networks from which the vast majority of SA Power Networks’ SWER systems are supplied with the MVAr values corrected for the removal of any 33kV capacitor banks. The following assumptions have been made in preparing the data submitted: DOPSD0305 and DOPSD0306 - Average power factor conversion for 7.6 kV and 11kV 3. Calculated values at 11 and 7.6kVdo not represent customer’s PF levels as they are compensated for by SA Power Networks owned capacitor banks installed across the network. They therefore represent PF values as effectively seen by the upstream network and substation’s transformers.
DOPSD0306 | Average power factor conversion for 11 kV lines | Estimate | Both DOPSD0101 and DOPSD0201 on which this value has been derived are estimated. | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0306 - Average power factor conversion for 11kV 1. SA Power Networks summated the MW and MVAr values for all zone substations with a secondary voltage of 11kV. These summated values were then converted to MVA using Pythagoras’ Theorem with the summated MW value being divided by the calculated MVA value. The result was then entered into within DOPSD0306 of the RIN. | SA Power Networks does not individually SCADA monitor its distribution transformers, it has been assumed that the value for these parameters will be equivalent to that of the combined 11 and 7.6kV networks from which the vast majority of SA Power Networks’ distribution transformers are supplied, with the MVAr values corrected for the removal of any 11 or 7.6kV capacitor banks. Similarly, SA Power Networks does not individually SCADA monitor its SWER systems, it has been assumed that the value for these parameters will be equivalent to the “corrected” values of the 33kV networks from which the vast majority of SA Power Networks’ SWER systems are supplied with the MVAr values corrected for the removal of any 33kV capacitor banks. The following assumptions have been made in preparing the data submitted: DOPSD0305 and DOPSD0306 - Average power factor conversion for 7.6 kV and 11kV 3. Calculated values at 11 and 7.6kVdo not represent customer’s PF levels as they are compensated for by SA Power Networks owned capacitor banks installed across the network. They therefore represent PF values as effectively seen by the upstream network and substation’s transformers.
DOPSD0307 | Average power factor conversion for SWER lines | Estimate | Given that SA Power Networks does not individually SCADA monitor its SWER systems, it has been assumed that the value for these parameters will be equivalent to the “corrected” values of the 33kV networks from which the vast majority of SA Power Networks’ SWER systems are supplied with the MVAr values corrected for the removal of any 33kV capacitor banks. | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0307 - Average power factor conversion for SWER 1 This section are intended to represent the average PF of the SWER network, the MW and MVAr values used to generate the values contained in DOPSD0102 and DOPSD0202 have been added according to each substation’s secondary voltage (ie 33kV) to provide a summated value of the MW and MVAr supplied by the 33kV network. 2 The final MVAr value has then been adjusted to remove the effect of any 33kV capacitor banks as these reduce the MVArs seen at the 33kV terminals of the zone substation transformers. 3 The summated MW and adjusted MVAr values at 33kV have then been converted to MVA using Pythagoras’ Theorem. The MW sum was then divided by the result of this MVA calculation to arrive at the average SWER PF value entered within DOPSD0307 of the RIN. | SA Power Networks does not individually SCADA monitor its distribution transformers, it has been assumed that the value for these parameters will be equivalent to that of the combined 11 and 7.6kV networks from which the vast majority of SA Power Networks’ distribution transformers are supplied, with the MVAr values corrected for the removal of any 11 or 7.6kV capacitor banks. Similarly, SA Power Networks does not individually SCADA monitor its SWER systems, it has been assumed that the value for these parameters will be equivalent to the “corrected” values of the 33kV networks from which the vast majority of SA Power Networks’ SWER systems are supplied with the MVAr values corrected for the removal of any 33kV capacitor banks. The following assumptions have been made in preparing the data submitted: DOPSD0307 - Average power factor conversion for SWER 4. Given the lack of metering at SWER level, all SWER systems have been assumed to be connected to the 33kV network. Whilst there are a few SWER systems supplied from 11kV feeders (ie 11/19kV), it is not anticipated that the customer’s connected to these systems will have different PF values (if at all) to those supplied primarily by the 33kV network.
DOPSD0308 | Average power factor conversion for 22 kV lines |  | SAPN does not have any 22kV |  | Nil | Nil | Nil
DOPSD0309 | Average power factor conversion for 33 kV lines | Estimate | Both DOPSD0101 and DOPSD0201 on which this value has been derived are estimated. | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0309 - Average power factor conversion for 33kV 1 In order to determine the PF of the 33kV network, SA Power Networks separately summated the MW and MVAr values for all zone substations and connection points with a secondary voltage of 33kV. 2 These summated values were then converted to MVA using Pythagoras’ Theorem. 3 The summated MW value was then divided by the calculated MVA value. The result was then entered into DOPSD0309 of the RIN. | DOPSD0309 & DOPSD0311- Average power factor conversion for 33 kV and 66kV 1. Calculated values do not represent customer’s PF levels as they are compensated for by SA Power Networks’ and ElectraNet’s capacitor banks installed across the network. They therefore represent PF values as effectively seen by the upstream transmission network and substation’s transformers.
DOPSD0310 | Average power factor conversion for 44 kV lines |  | SAPN does not have any 44kV |  | Nil | Nil | Nil
DOPSD0311 | Average power factor conversion for 66 kV lines | Estimate | Refer 'Basis of Preparation - Network Planning Variables' attached | Relying on opinion of experienced manager using what reliable data is available. | SCADA | DOPSD0311 - Average power factor conversion for 66kV 1 In order to determine the PF of the 66kV network, SA Power Networks separately summated the MW and MVAr values for all zone substations and connection points with a secondary voltage of 66kV. 2 These summated values were then converted to MVA using Pythagoras’ Theorem. 3 The summated MW value was then divided by the calculated MVA value. The result was then entered into DOPSD0311 of the RIN. | DOPSD0309 & DOPSD0311- Average power factor conversion for 33 kV and 66kV 1. Calculated values do not represent customer’s PF levels as they are compensated for by SA Power Networks’ and ElectraNet’s capacitor banks installed across the network. They therefore represent PF values as effectively seen by the upstream transmission network and substation’s transformers.
DOPSD0312 | Average power factor conversion for 110 kV lines |  | SAPN does not have any 110kV |  | Nil | Nil | Nil
DOPSD0313 | Average power factor conversion for 132 kV lines |  | SAPN does not have any 132kV |  | Nil | Nil | Nil
DOPSD0314 | Average power factor conversion for 220 kV lines |  | SAPN does not have any 220kV |  | Nil | Nil | Nil
Table 3.4.3.6 Demand supplied (for customers charged on this basis) – MW measure
DOPSD0401 | Summated Chargeable Contracted Maximum Demand | Actual |  |  | Nil | Nil
DOPSD0402 | Summated Chargeable Measured Maximum Demand |  |  |  | Nil | Nil
Table 3.4.3.7 Demand supplied (for customers charged on this basis) – MVA measure
DOPSD0403 | Summated Chargeable Contracted Maximum Demand | Estimate | SAPN has not separately recorded MVA in this category -based on Sales Model |  | Sales Model (internal) | Based on the maximum demand tariff kVA quantities billed relating to LV Demand, HV Demand, Zone substation, Substation. Billing is on agreed demand not on measured demand. Actual data is extracted from the Sales Model.
DOPSD0404 | Summated Chargeable Measured Maximum Demand | N/A | Actual (0) - SAPN only has contracted maximum demand tariffs |  | Nil | Nil

## 3.5 Physical Assets
Table / Variable Code | Description | Actual / Estimate | Reason for Estimate (if applicable) | If estimate, reason it is best estimate | Data Source(s) | Methodology | Assumptions
3.5. Physical Assets worksheet
Table 3.5.1 Network Capacities Variables
Circuit length
Table 3.5.1.1 Overhead network length of circuit at each voltage
DPA0101 | Overhead low voltage distribution | Actual |  |  | Geographic Information System (GIS) | Snapshot has been taken of GIS circuit length data by voltage. LV excludes service lines <10m in length) GIS extract is in tabs: HVOH LVOH(Serv>10m) HVOH is filtered by voltages and lengths per voltage summated.
DPA0102 | Overhead 2.2kV
DPA0103 | Overhead 6.6kV
DPA0104 | Overhead 7.6 kV
DPA0105 | Overhead 11 kV
DPA0106 | Overhead SWER
DPA0107 | Overhead 22 kV
DPA0108 | Overhead 33 kV
DPA0109 | Overhead 44kV
DPA0110 | Overhead 66 kV
DPA0111 | Overhead 110kV
DPA0112 | Overhead 132 kV
DPA0113 | Overhead 220kV
DPA0114 | Other
DPA01 | Total overhead circuit km
Table 3.5.1.2 Underground network circuit length at each voltage
DPA0201 | Underground low voltage distribution | Actual |  |  | Geographic Information System (GIS) | Snapshot has been taken of GIS circuit length data by voltage. LV excludes service lines <10m in length) GIS extract is in tabs: . HVUG . LVUG(Serv?10m) HVUG is filtered by voltages and lengths per voltage summated.
DPA0202 | Underground 5kV
DPA0203 | Underground 6.6kV
DPA0204 | Underground 7.6 kV
DPA0205 | Underground 11 kV
DPA0206 | Underground SWER
DPA0207 | Underground 22 kV
DPA0208 | Underground 33 kV
DPA0209 | Underground 66 kV
DPA0210 | Underground 110kV
DPA0211 | Underground 132 kV
DPA0212 | Other
DPA02 | Total underground circuit km
Circuit Capacity MVA
Table 3.5.1.3 Estimated overhead network weighted average MVA capacity by voltage class
DPA0301 | Overhead low voltage distribution | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | The following steps were undertaken to compile the data submitted: For 33kV and 66kV (ie DPA0307 and 309 respectively), 1. The 66kV and 33kV line spreadsheets held, maintained and used by Network Planning Department for planning purposes were updated to reflect any augmentation of the 66kV and 33kV sub-transmission networks completed during the course of 2013/14 financial year. Those augmentations of the 33kV and 66kV sub-transmission network (both new lines and upgrades) in progress, but not completed were not considered as per the instructions in the RIN Notice. 2. For each line segment, the length of the overhead section(s) was multiplied by the lowest rating of those overhead sections of conductor within the overall line to arrive at a MVA.km value for that line. 3. These MVA.km values were then summated (according to operating voltage) as was the total length of overhead conductor at each voltage. 4. The weighted average MVA per km value was then determined by dividing the MVA.km value by the total route length of the relevant voltage’s overhead circuits. For 7.6kV and 11kV (ie DPA0303 and 304 respectively), 1. An extract from SA Power Networks’ GIS system was obtained. 2. The MVA capacity of each conductor for which sufficient details were available was determined and multiplied by the length of the conductor segment. These resulting MVA.km values were then summated according to their nominal voltage. 3. Similarly, the route length of each conductor used in the MVA.km calculation was summated to arrive at the respective voltage’s total conductor length in km. 4. The total MVA.km value was then divided by the total route length for each voltage to arrive at the final MVA per km value. For SWER and LV (ie DPA0301 and 305 respectively), as stated within the assumptions section: 1. the capacity of SA Power Networks’ SWER systems has been limited to a maximum of 0.2 MVA per km for the reasons stated in Section 5.4. 2. For the low voltage network, an extract from SA Power Networks’ GIS system was obtained. 3. The MVA capacity of each conductor for which sufficient details were available was determined and multiplied by the length of the conductor segment. These resulting MVA.km values were then summated according to their nominal voltage. 4. Similarly, the route length of each conductor used in the MVA.km calculation was summated to arrive at the respective voltage’s total length in km. 5. The total MVA.km value was then divided by the total route length for each voltage to arrive at the final MVA per km value. | In compiling the data contained within this table, the following assumptions were made: 1. This analysis was based on a system snapshot taken from SA Power Networks’ GIS on the 10 July 2014. This analysis considered all overhead conductors for which adequate records existed to enable determination of a conductor rating irrespective of whether the conductor formed part of the feeder backbone or a spur. 2. For all 66kV and 33kV lines containing multiple conductor sizes or design temperatures, the conductor with the lowest rating was used to determine the MVA.km value for that line. 3. For all 11kV, 7.6kV and LV conductors, a design temperature of 75oC was assumed to determine the conductor rating. For 66kV and 33kV conductors, the actual design temperature was known and used. 4. Irrespective of the capacity of the overhead conductors used to construct SA Power Networks’ SWER networks, their capacity is limited to the largest SWER Isolating TF to prevent both overloading of the TF and also to ensure adequate protection co-ordination with upstream protection devices. 5. All MVA capacity values are based on the asset’s “normal” rating according to SA Power Networks’ QMS Procedure 638. The following variable codes within Table 3.1.5.3 were not submitted either due to these voltages not being operated by SA Power Networks or where operated by SA Power Networks at these voltages, they directly supply HV customers from the ZSS and therefore SA Power Networks does not operate any overhead assets at this voltage: 1. DPA0302 – 6.6kV (no overhead assets owned by SA Power Networks); 2. DPA0306 – 22kV (not operated by SA Power Networks); 3. DPA0308 – 44kV (not operated by SA Power Networks); 4. DPA0310 – 110kV (not operated by SA Power Networks); 5. DPA0311 – 132kV (not operated by SA Power Networks); 6. DPA0312 – 220kV (not operated by SA Power Networks); 7. DPA0313 – Other (no overhead assets owned by SA Power Networks).
DPA0302 | Overhead 6.6kV |  | SAPN does not have any 6.6kV |  | Nil | Nil | Nil
DPA0303 | Overhead 7.6kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0301 | Refer assumptions under DPA0301
DPA0304 | Overhead 11 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0301 | Refer assumptions under DPA0301
DPA0305 | Overhead SWER | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0301 | Refer assumptions under DPA0301
DPA0306 | Overhead 22 kV |  | SAPN does not have any 22kV |  | Nil | Nil | Nil
DPA0307 | Overhead 33 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0301 | Refer assumptions under DPA0301
DPA0308 | Overhead 44kV |  | SAPN does not have any 44kV |  | Nil | Nil | Nil
DPA0309 | Overhead 66 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0301 | Refer assumptions under DPA0301
DPA0310 | Overhead 110kV |  | SAPN does not have any 110kV |  | Nil | Nil | Nil
DPA0311 | Overhead 132 kV |  |  |  | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0301 | Refer assumptions under DPA0301
DPA0312 | Overhead 220kV |  | SAPN does not have any 220kV |  | Nil | Nil | Nil
Table 3.5.1.4 Estimated underground network weighted average MVA capacity by voltage class
DPA0401 | Underground low voltage distribution | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | The following steps were undertaken to compile the data submitted: For 33kV and 66kV (ie DPA0409 and 410 respectively), 1. The 66kV and 33kV line spreadsheets held, maintained and used by Network Planning Department for planning purposes were updated to reflect any augmentation of the 66kV and 33kV sub-transmission networks completed during the course of 2013/14 financial year. Those augmentations of the 33kV and 66kV sub-transmission network (both new lines and upgrades) in progress, but not completed were not considered as per the instructions in the RIN Notice. 2. For each line segment, the length of the underground section(s) was multiplied by the lowest rating of those cable sections within the overall line to arrive at a MVA.km value for that line. 3. These MVA.km values were then summated (according to operating voltage) as was the total length of overhead conductor at each voltage. 4. The weighted average MVA per km value was then determined by dividing the MVA.km value by the total route length of the relevant voltage’s underground circuits. For 7.6kV and 11kV (ie DPA0304 and 305 respectively), 1. An extract from SA Power Networks’ GIS system was obtained. 2. The MVA capacity of each cable for which sufficient details were available was determined and multiplied by the length of the cable segment. These resulting MVA.km values were then summated according to their nominal voltage. 3. Similarly, the route length of each cable used in the MVA.km calculation was summated to arrive at the respective voltage’s total cable length in km. 4. The total MVA.km value was then divided by the total route length for each voltage to arrive at the final MVA per km value. For SWER and LV (ie DPA0406 and 401 respectively), as stated within the assumptions section: 1. the capacity of SA Power Networks’ SWER systems has been limited to 0.2 MVA per km. 2. For the low voltage network, an extract from SA Power Networks’ GIS system was obtained. 3. The MVA capacity of each cable for which sufficient details were available was determined and multiplied by the length of the cable segment. These resulting MVA.km values were then summated according to their nominal voltage. 4. Similarly, the route length of each cable used in the MVA.km calculation was summated to arrive at the respective voltage’s total cable length in km. 5. The total MVA.km value was then divided by the total route length for each voltage to arrive at the final MVA per km value. | In compiling the data contained within this table, the following assumptions were made: 1. This analysis was based on a system snapshot taken from SA Power Networks’ GIS system on the 10 July 2014. This analysis considered all overhead conductors for which adequate records existed to enable determination of a conductor rating irrespective of whether the conductor formed part of the feeder backbone or a spur. 2. For all 66kV and 33kV lines containing multiple cable sizes or installation configurations, the cable with the lowest rating was used to determine the MVA.km value for that line. 3. For all 11kV, 7.6kV and LV cables, ratings have been determined assuming a standard installation configuration. For 66kV and 33kV cables, the actual configuration was known and used. 4. Irrespective of the capacity of the underground cables used to construct SA Power Networks’ SWER networks, their capacity is limited to the largest SWER Isolating TF to prevent both overloading of the TF and also to ensure adequate protection co-ordination with upstream protection devices. 1. All MVA capacity values are based on the asset’s “normal” rating according to SA Power Networks’ QMS Procedure 638 The following variable codes within Table 3.1.5.4 were not submitted either due to these voltages not being operated by SA Power Networks or where operated by SA Power Networks at these voltages, they directly supply HV customers from the ZSS and therefore SA Power Networks does not operate any underground assets at this voltage: 1. DPA0402 – 5kV (not operated by SA Power Networks); 2. DPA0403 – 6.6kV (no underground assets owned by SA Power Networks); 3. DPA0407 – 12.7kV (not operated by SA Power Networks); 4. DPA0408 – 22kV (not operated by SA Power Networks); 5. DPA0411 – 110kV (not operated by SA Power Networks); 6. DPA0412 – 132kV (not operated by SA Power Networks); 7. DPA0413 – Other (no underground assets owned by SA Power Networks).
DPA0402 | Underground 5kV |  | SAPN does not have any 5kV |  | Nil | Nil | Nil
DPA0403 | Underground 6.6kV |  | SAPN does not have any 6.6kV |  | Nil | Nil | Nil
DPA0404 | Underground 7.6 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0401 | Refer assumptions under DPA0401
DPA0405 | Underground 11 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0401 | Refer assumptions under DPA0401
DPA0406 | Underground SWER | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0401 | Refer assumptions under DPA0401
DPA0407 | Underround 12.7kV |  | SAPN does not have any 12.7kV |  | Nil | Nil | Nil
DPA0408 | Underground 22 kV |  | SAPN does not have any 22kV |  | Nil | Nil | Nil
DPA0409 | Underground 33 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0401 | Refer assumptions under DPA0401
DPA0410 | Underground 66 kV | Estimate | Not all asset infomration available within SAPN records. | Relying on opinion of experienced manager using what reliable data is available. | Geographic Information System (GIS), Network Planning sub-transmission line records, QMS Procedure 638 | Refer methodology under DPA0401 | Refer assumptions under DPA0401
DPA0411 | Underground 110kV |  | SAPN does not have any 110kV |  | Nil | Nil | Nil
DPA0412 | Underground 132 kV |  | SAPN does not have any 132kV |  | Nil | Nil | Nil
3.5.2 Transformer Capacities Variables
Table 3.5.2.1 Distribution transformer total installed capacity
DPA0501 | Distribution transformer capacity owned by utility | Estimate | Based on internal records however records may not be complete. | Unknown MVA can be best estimated based on known MVA. | Distribution and sub-transmission transformer MVA from SAP and internal records | Refer to internal records. For 2005/06-2007/08, the total figure has been grossed up for a small number of transformers (less than 2%) with no MVA recorded. Transformation to 7.6, 11 and 19kV have been excluded. From 2008/09, no grossing up required. Summated all transformers with Secondary voltage of "LV" and "3.3kV". | A small number of transformers (less than 2%) with no MVA recorded have proportionally the same MVA as other distribution transformers. All transformers listed with secondaries of 7.6kV, 11kV or 19kV have another transformation to LV or 3.3kV before supplying the customer.
DPA0502 | Distribution transformer capacity owned by High Voltage Customers | Estimate | SAPN does not separately record information in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Data is based HV demand tariff kW and kVA quantities billed relating to HV Demand, Zone substation, Substation. Data is extracted from the Sales Model. | Customers would require transformers at their property to at least equal to the agreed HV demand.
DPA0503 | Cold spare capacity included in DPA0501 | Actual |  |  | SA Power Networks internal stock records | SA Power Networks only collects this data for stock reconciliation at the end of the financial year and hence the data is a snapshot of transformer capacity in hand at 30th of June each year, as a result this data is accurate for this day each year it does not reflect an average for the year. For transformers the peak stock holding is typically around the 1st of November as summer emergency spare numbers are required to be in place by this date, after summer is over the spares are consumed without replacement until re-ordering occurs for the following November. There are no other stock holding records for other times of the years. Actual data is based on actual stockholding in warehouses as at 30th June each year, the type, capacity and number of transformers were entered into a spreadsheet and then the capacity of the transformer was multiplied by the number of transformers held in stock. All of the capacity figures were summed to calculate the total spare capacity. | Nil
Table 3.5.2.2 Zone substation transformer capacity
DPA0601 | Total installed capacity for first step transformation where there are two steps to reach distribution voltage | Estimate | Limited records available. Available data only valid as at date of original preparation. No ability to easily re-verify data collected at the time of original report's preparation | Relying on opinion of experienced manager using what reliable data is available. | Network Planning Asset Utilisation Spreadsheets | 1. Starting with the installed TF nameplate capacities submitted within the 2012/13 Economic Benchmarking (EB) RIN, those capacity driven augmentations involving the upgrading or addition of further TFs at existing zone substation sites, or the installation of TFs at new zone substation sites, were added to the baseline TF installed capacity portfolio based on the installed TF capacity held within SAP and registered on the SSDs as stated within the assumptions section above. 2. An audit of SA Power Networks’ TF stores was undertaken to verify those TFs registered in SAP as held in stock. These were segmented for internal use into “system spares” and “project”. 3. Each TF according to its ZSS, was assigned a "classification code" (S1, S2, P or C) to indicate whether they were "Stage 1", "Stage2", "Primary" or "Cold Standby" TFs respectively, based on their position and function within the network. Those TF units held in stores were classified as cold standby units. 4. A summation of the capacity of those TFs within each classification in each forecast year was then performed using the “SUMIF” function within MS Excel, to arrive at the forecast summated TF capacity according to the classifications specified within the RIN. | 1. The figures provided are based on those TF nameplate capacities recorded in SAP and manually cross checked against those values specified on SA Power Networks’ SSDs. 2. In order to maintain consistency and comparability with previous Economic Benchmarking RIN submissions, all TF capacities (at each voltage reporting level), are based on the highest in service nameplate rating for the given TF according to its operating voltage (ie dual ratio transformers will have differing ratings depending on the secondary voltage they are set to operate at). In the case of cold standby units, if the TF has forced cooling, the nameplate rating reported is the ONAF rather than ONAN nameplate rating. Nameplate ratings have historically been provided rather than normal rating as those normal ratings applied by SA Power Networks are subject to change due to re-calculation of rating due to changes in rating parameters (eg consideration of impact of PV on demand profile curve) or to reflect unbalanced sharing of transformers. The highest nameplate value according to the TF’s operating voltage has been used where fans exist and according to operating voltage 3. All TFs owned by SA Power Networks but which are deemed unregulated assets have been excluded from the reported values. 4. Those TFs reported as being "cold standby" include TFs which are: i) installed, but de-energised (ie traditional cold standby); ii) installed, energised, but not on load (ie hot standby); iii) mobile units for use by SA Power Networks under contingent conditions or during ZSS augmentation; iv) not installed and held as system spares; and v) not installed, but held in stores awaiting future installation (either as part of a planned network upgrade or new customer installation).
DPA0602 | Total installed capacity for second step transformation where there are two steps to reach distribution voltage | Estimate | Limited records available. Available data only valid as at date of original preparation. No ability to easily re-verify data collected at the time of original report's preparation | Relying on opinion of experienced manager using what reliable data is available. | Network Planning Asset Utilisation Spreadsheets | Refer methodology under DPA0601 | Refer assumptions under DPA0601
DPA0603 | Total zone substation transformer capacity where there is only a single step transformation to reach distribution voltage | Estimate | Limited records available. Available data only valid as at date of original preparation. No ability to easily re-verify data collected at the time of original report's preparation | Relying on opinion of experienced manager using what reliable data is available. | Network Planning Asset Utilisation Spreadsheets | Refer methodology under DPA0601 | Refer assumptions under DPA0601
DPA0604 | Total zone substation transformer capacity | Estimate | Sum of estimates | Relying on opinion of experienced manager using what reliable data is available. | Sum of DPA0601, DPA0602, DPA0603 and DPA0605 | Refer methodology under DPA0601 | Refer assumptions under DPA0601
DPA0605 | Cold spare capacity of zone substation transformers included in DPA0604 | Estimate | SA Power Networks does not have a single data collection for Cold Spare Capacity. Part A below contains an outline of how estimates of Spare Capacity were determined and Part B contains the outline for Cold Capacity. SA Power Networks does not purchase all of its transformers (TFs) on stock. Over the last ten years or so, units for projects and insurance spares were purchased non stock. To determine Part A:Spare Capacity, a combination of stock units from the Logistic Stock List and non stock units from Purchase History and the SAP Asset Register Spares were used. Part B: Cold Capacity sourced data from ESCOSA GL12 demand management spreadsheets.. | Relying on opinion of experienced manager using what reliable data is available. | Logistic Stock List, Non Stock Transformers via Purchase History, Network Planning Asset Utilisation Spreadsheets | Refer methodology under DPA0601 | Refer assumptions under DPA0601
Table 3.5.2.3 Distribution - other transformer capacity
3.5.3 Public lighting
DPA0701 | Public lighting luminaires | Actual |  |  | Geographic Information System (GIS) | Luminaires are accumulative and taken from the GIS lighting summary at 30 June each year. Energy only luminaires have not been included as we have no maintenance obligations for these. | SA Power Networks has counted luminaires as the number of lamps. However, some lamps contain more than one luminaire.
DPA0702 | Public lighting poles | Estimate | SA Power Networks' Column numbers from GIS known at 2012/13 and 2006/07 only. | Relying on opinion of experienced manager using what reliable data is available. | GIS Lighting Summary data at 30 June 2014 | Estimates calculated based on numerous assumptions.
DPA0703 | Public lighting columns |  |  |  |  | SAPN is not required to complete this row as we did not report this previously.

## 3.6 Quality of services
Table / Variable Code | Description | Actual / Estimate | Reason for Estimate (if applicable) | If estimate, reason it is best estimate | Data Source(s) | Methodologies and Assumptions
3.6 Quality of services worksheet
Table 3.6.1 Reliability
Table 3.6.1.1 Inclusive of MEDs
DQS0101 | Whole of network unplanned SAIDI | Estimate | SA Power Networks cannot provide actual data with current metering technology (as it mainly has Type 6 metering and meters are only read every 3 months). | Most efficient and cost effective way with current systems. | CIS/OV (i.e. customer meter readings), GIS and OMS | Calculations are in accordance with our procedures: o Unplanned SAIDI = Total Unplanned Customer Minutes / Total Customers (i.e.DOPCN02) o Unplanned SAIFI = Total Unplanned Customers Interrupted / Total Customers (i.e.DOPCN02) - the required inclusions / exclusions are obtained by applying the appropriate filters to the cause of interruptions e.g. to obtain the figures for ‘excluding excluded outages’ the causes of Planned, ElectraNet, Generation and Emergency Disconnections would be excluded - MEDs are identified by calculating the daily unplanned SAIDI excluding excluded outages for each day and identifying those days that exceed Tmed – these are then included / excluded as required Where an interruption affects a phase(s), the number of customers affected is estimated as follows: 1/3rd if only one LV phase is affected, 2/3rds if two LV phases are affected and 2/3rds if only one HV phase is affected.
DQS0102 | Whole of network unplanned SAIDI excluding excluded outages
DQS0103 | Whole of network unplanned SAIFI
DQS0104 | Whole of network unplanned SAIFI excluding excluded outages
Table 3.6.1.2 Exclusive of MEDs
DQS0105 | Whole of network unplanned SAIDI
DQS0106 | Whole of network unplanned SAIDI excluding excluded outages
DQS0107 | Whole of network unplanned SAIFI
DQS0108 | Whole of network unplanned SAIFI excluding excluded outages
Table 3.6.2 Energy not supplied
DQS0201 | Energy Not Supplied (planned) | Estimate | SA Power Networks cannot provide actual data with current metering technology (as it mainly has Type 6 metering and meters are only read every 3 months). | Most efficient and cost effective way with current systems. | CIS/OV (i.e. customer meter readings), GIS and OMS | The consumption by NMI (KWh) for a 12 month period is extracted from CIS/OV and is allocated to a feeder and then allocated to a feeder category. These figures are subsequently converted to GWh/minute and then multiplied by the corresponding feeder category SAIDI (unplanned / planned) and summated to obtain the whole of network figures. The consumption data is based on actual meter readings taken as close to 30 June as possible. Note that method (3) on pg. 38 of the 'Instructions and definitions' was used.
DQS0202 | Energy Not Supplied (unplanned)
DQS02 | Energy Not Supplied - Total
Table 3.6.3 System losses
DQS03 | System losses | Estimate | SA Power Networks does not separately measure or record information in this category. | Relying on opinion of experienced manager using what reliable data is available. | Sales Model (internal) | Calculated by dividing Total Deliveries (DOPED01) by Total Purchases (extracted from Sales Model). Data provided is based on SAPN methodology and represents actuals as reported to AER.
Table 3.6.4 Capacity utilisation
DQS04 | Overall utilisation | Estimate | The other RIN data (specified in Data Source) on which this value has been derived are estimated. | Relying on opinion of experienced manager using what reliable data is available. | DPA0604 & DOPSD0201. | Methodology The values submitted were calculated according to the following process: 1. The utilisation values were calculated based on the value held in DOPSD0201 (Non–coincident Actual Maximum Demand in MVA) divided by the value held in DPA0604 which represent the summation of DPA0601 (ie first step transformation capacity), DPA0602 (ie second step transformation capacity), DPA0603 (ie single step transformation capacity) and DPA0605 (ie cold standby capacity). 2. The resultant values were then converted to percent. Assumptions The following assumptions were made in deriving the values submitted: 1. The value provided within DOPSD0201 excludes the loads seen by the second step transformations to avoid double counting of the loads seen by the first and second step transformations. As an exercise, SA Power Networks re-calculated the utilisation values which would have been seen had the installed capacity of these loads had been excluded and found that the utilisation value would have increased by 1.3%.

## 3.7 Operating environment
Table / Variable Code | Description | Actual / Estimate | Reason for Estimate (if applicable) | If estimate, reason it is best estimate | Data Source(s) | Methodologies and Assumptions
3.7 Operating environment factors worksheet
Table 3.7.1 Density factors
DOEF0101 | Customer density | Estimate | The other RIN data (specified in Data Source) on which these values has been derived are estimated. | Only available approach. | DOPCN02, DOEF0301 | Density factors calculated from other RIN variables as defined
DOEF0102 | Energy density | Estimate |  |  | DOPED01, DOPCN02
DOEF0103 | Demand density | Estimate |  |  | DOPCN02, DOPSD0201
Table 3.7.2 Terrain factors
DOEF0201 | Rural proportion | Estimate | Estimate of route line length in Table 3.7.3 is based on circuit length data | Circuit length data is only reasonable basis for historical estimate of rural proportion. | GIS circuit length data. | Snapshot has been taken of GIS circuit length data by region. Assumed that rural proportion for line length is the same as rural proportion for circuit length.
DOEF0202 | Urban and CBD vegetation maintenance spans | Estimate | Assumes two defects per span in NBFRA, and number of spans in BFRAs | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors | Prorata estimate based on number of spans for each feeder category for which SA Power Networks is responsible for. Assumes two defects per span in NBFRA. The step change in volumes is subject to SA Power Networks' pass-through, approved by the AER.
DOEF0203 | Rural vegetation maintenance spans | Estimate | Assumes two defects per span in NBFRA, and number of spans in BFRAs | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors | Prorata estimate based on number of spans for each feeder category for which SA Power Networks is responsible for. Assumes two defects per span in NBFRA. The step change in volumes is subject to SA Power Networks' pass-through, approved by the AER.
DOEF0204 | Total vegetation maintenance spans | Estimate | Assumes two defects per span in NBFRA, and number of spans in BFRAs | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors | Number of spans for which SA Power Networks is responsible for recorded by contractors. Assumes two defects per span in NBFRA.
DOEF0205 | Total number of spans | Estimate | Number of poles or spans not recorded. | Relying on opinion of experienced manager using what reliable data is available. | Based on route length and average span length per base voltage level. | Based on average span length per base voltage level. Route length used to prorate estimated pole numbers before 2013.
DOEF0206 | Average urban and CBD vegetation maintenance span cycle | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Local Network Records | Prorata estimate based on number of spans for each feeder category
DOEF0207 | Average rural vegetation maintenance span cycle | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Local Network Records | Prorata estimate based on number of spans for each feeder category
DOEF0208 | Average number of trees per urban and CBD vegetation maintenance span | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors estimate | Expert opinion
DOEF0209 | Average number of trees per rural vegetation maintenance span | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors estimate | Assumes 1 defect per Span as do not collect information
DOEF0210 | Average number of defects per urban and CBD vegetation maintenance span | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors estimate Expert opinion | Assumes 2 defects per Span as do not collect information
DOEF0211 | Average number of defects per rural vegetation maintenance span | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Vegetation clearance contractors estimate | Expert opinion
DOEF0212 | Tropical proportion | Actual |  |  | http://www.bom.gov.au/jsp/ncc/climate_averages/climate-classifications/index.jsp?maptype=kpngrp | Refer to map
DOEF0213 | Standard vehicle access | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | Internal expert opinion | Approximate estimate of 7% of route line length
DOEF0214 | Bushfire risk | Estimate | Number of spans estimated per feeder type based on average span length | Relying on opinion of experienced manager using what reliable data is available. | Based on route length and average span length per base voltage level. | Based on average span length per base voltage level The circuit length of each feeder was determined. Each feeder is classified into bushfire risk areas and non-bushfire risk areas. An average span length per voltage was used to convert circuit kms to route kms.
Table 3.7.3 Service area factors
DOEF0301 | Route Line length | Estimate | SAPN does not separately record information in this category | Relying on opinion of experienced manager using what reliable data is available. | GIS and average span length per base voltage level. | Route line length for 2014 based on estimate of percentage of route for each voltage that runs parallel to other voltages. Conductor on the same route was estimated by voltage starting with LV and working up to 132kV. Estimate of route line length for earlier years has been pro-rated by historical GIS circuit length data.

## 3.7.4 Weather stations
Table / Variable Code | Description | Actual / Estimate | Reason for Estimate (if applicable) | If estimate, reason it is best estimate | Data Source(s) | Methodologies and Assumptions
Table 3.7.4 Weather stations
N/A | Weather Stations | Actual |  |  | Weather stations in SA Power Networks service area collected from Bureau of Meteorology website (BoM) | Feeders are assigned to the nearest AWS providing 30 minute intervals on wind and temperature data which is necessary for managing the safety of the network. A "no" categorisation in terms of materiality is applied when the we do not use the weather station's observations because it doesn't provide half-hourly data. Note: Woomera and Yunta weather stations were removed as these are not in our regulated service area.