{"text_format":"1","workbook":"xlsx","n_sheets":26,"sheets":["AER only","Instructions","Contents","Business & other details","2.1 Expenditure summary","2.2 Repex","2.3(a) Augex","2.3(b) Augex","2.5 Connections","2.6 Non-network","2.7 Vegetation management","2.8 Maintenance","2.9 Emergency Response","2.10 Overheads","2.10(A) Overheads","2.11 Labour","2.12 Input tables","4.1 Public lighting","4.2 Metering","4.3 Fee-based services","4.4 Quoted services","5.2 Asset Age Profile","5.3 MD - Network level","5.4 MD & utilisation-Spatial","6.3 Sustained interruptionss","Amendments"],"not_rendered":{"charts":0,"images":7,"macros":1,"external_links":2,"defined_names":752,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"AER only","index":0,"n_rows":147,"n_cols":40,"rows_kept":147,"cut":false,"hidden":true,"merged":[[52,34,54,34],[0,1,0,11],[4,28,4,38],[5,28,5,31],[5,34,5,38],[50,22,50,26],[50,28,50,31],[51,1,51,5],[51,14,51,21],[51,22,51,26],[51,28,51,31],[52,2,52,3],[55,34,59,34],[63,34,64,34],[69,14,69,15],[69,22,69,25],[107,1,107,8]]}
[null,"Data in these columns used for data validation and database purposes."]
[null,"Date last modified:","2017-01-16","added (Albury and Victora) for AGN"]
[null,null,"2016-10-17","updated TransGrid's correct legal name, corrected TasNetworks (T) to June financial year"]
[null,null,"2017-02-01","inserted Power and Water, added NRs (dms_FeederCat_1 and dms_FeederCat_2)"]
[null,null,"2017-03-03","inserted AEMO as a business",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"FOR ELECTRICITY BUSINESSES ONLY"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Feeder Types",null,null,null,"TasNetworks (D)","MAIFI flag","Feeder Names"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","long rural","EXTRA"]
[null,"dms_TradingName_List","dms_TradingNameFull_List","dms_ABN_List","dms_JurisdictionList","dms_Sector_List","dms_Segment_List","dms_FormControl_List","dms_RPT_List","dms_RPTMonth_List","dms_CRCPlength_List","dms_FRCPlength_List","dms_663_List","dms_DeterminationRef_List","dms_Addr1_List","dms_Addr2_List","dms_Suburb_List","dms_State_List","dms_PostCode_List","dms_PAddr1_List","dms_PAddr2_List","dms_PSuburb_List","dms_PState_List","dms_PPostCode_List","dms_ContactName1_List","dms_ContactPh1_List","dms_ContactEmail_List","Column1","dms_CBD_flag","dms_Urban_flag","dms_ShortRural_flag","dms_LongRural_flag","dms_FeederType_5_flag","dms_MAIFI_flag_List","dms_FeederName_1","dms_FeederName_2","dms_FeederName_3","dms_FeederName_4","dms_FeederName_5"]
[null,"ActewAGL Distribution","ActewAGL Distribution",76670568688,"ACT","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","40 Bunda Street",null,"CANBERRA","ACT","2600","GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au",null,"NO","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"ActewAGL Distribution"]
[null,"ActewAGL Distribution (Tx Assets)","ActewAGL Distribution (Tx Assets)",76670568688,"ACT","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","40 Bunda Street",null,"CANBERRA","ACT","2600","GPO BOX 366",null,"CANBERRA","ACT",2601,"Robert Walker","02 6248 3847","robert.walker@actewagle.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"ActewAGL Distribution (Tx Assets)"]
[null,"ActewAGL Gas","ActewAGL Gas",76670568688,"ACT","Gas","Distribution","Weighted average price cap","Financial","June",5,5,"x",null,"40 Bunda Street",null,"CANBERRA","ACT","2600","GPO BOX 366",null,"CANBERRA","ACT",2601,"Philip Deamer","02 6248 3438","GasAAReview@actewagl.com.au",null,null,null,null,null,null,null,null,null,null,null,null,"ActewAGL Gas"]
[null,"AEMO","Australian Energy Market Operator Ltd",94072010327,"Vic","Electricity","Transmission","-","Financial","March",5,5,"x","-","Level 22","530 Collins Street","MELBOURNE","VIC","3000","GPO Box 2008",null,"MELBOURNE","VIC","3001",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AEMO"]
[null,"AGN (Albury and Victoria)","Australian Gas Networks Limited (reporting data for Albury and Victoria)",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 6","400 King William Street","ADELAIDE","SA","5000","PO Box 6468","Halifax Street","ADELAIDE","SA","5000","Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"AGN (Albury)"]
[null,"AGN (Albury)","Australian Gas Networks Limited (reporting data for Albury)",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 6","400 King William Street","ADELAIDE","SA","5000","PO Box 6468","Halifax Street","ADELAIDE","SA","5000","Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural"]
[null,"AGN (SA)","Australian Gas Networks Limited (reporting data for SA)",19078551685,"SA","Gas","Distribution","Weighted average price cap","Financial","June",5,5,5,"distribution determination","Level 6","400 King William Street","ADELAIDE","SA","5000","PO Box 6468","Halifax Street","ADELAIDE","SA","5000","Craig de Laine","08 8418 1129 ","craig.delaine@agn.com.au",null,null,null,null,null,null,null,null,null,null,null,null,"AGN (SA)"]
[null,"AGN (Victoria)","Australian Gas Networks Limited (reporting data for Victoria)",19078551685,"Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AGN (Victoria)"]
[null,"Amadeus","APT Pipelines (NT) Pty Ltd",39009737393,"NT","Gas","Transmission","Weighted average price cap","Financial","June",5,5,"x","n/a","Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","Alexandra Curran","02 9275 0020","alexandra.curran@apa.com.au",null,null,null,null,null,null,null,null,null,null,null,null,"Amadeus"]
[null,"APA GasNet","APA GasNet Australia (Operations) Pty Ltd","065083009","Vic","Gas","Transmission","Weighted average price cap","Calendar","December",5,5,"x",null,"Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","PO Box R41",null,"ROYAL EXCHANGE","NSW","1225",null,"02 9693 0000",null,null,null,null,null,null,null,null,null,null,null,null,null,"APA GasNet"]
[null,"Ausgrid","Ausgrid",78508211731,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","570 George St",null,"SYDNEY","NSW",2000,"GPO Box 4009",null,"SYDNEY","NSW","2001","John Thomson","(02) 9269 2312","john.thomson@ausgrid.com.au",null,"YES","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Ausgrid"]
[null,"Ausgrid (Tx Assets)","Ausgrid (Tx Assets)",67505337385,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination",null,null,null,"NSW",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Ausgrid (Tx Assets)"]
[null,"AusNet (D)","AusNet Electricity Services Pty Ltd",91064651118,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 32","2 Southbank Boulevard","SOUTHBANK","Vic","3006","Locked Bag 14051",null,"MELBOURNE CITY MAIL CENTRE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,null,"YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"AusNet (D)"]
[null,"AusNet (Gas)","AusNet Gas Services","086015036","Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"X",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"AusNet (Gas)"]
[null,"AusNet (T)","Ausnet Services (Transmission) Ltd",48116124362,"Vic","Electricity","Transmission","Revenue cap","Financial","March",5,5,2,"transmission determination","Level 32","2 Southbank Boulevard","SOUTHBANK","Vic","3006","Locked Bag 14051",null,"MELBOURNE CITY MAIL CENTRE","Vic","8001","Clare Thompson","03 9695 6670","clare.e.thompson@ausnetservices.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"AusNet (T)"]
[null,"Australian Distribution Co.","Australian Distribution Co.",11222333444,"-","Electricity","Distribution","Revenue cap","Financial","June",5,5,2,"distribution determination","123 Straight Street",null,"SYDNEY","NSW","2000","PO Box 123",null,"SYDNEY","NSW",2000,"Bob Smith","02 1234 5678","bob@auselec.net.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Australian Distribution Co."]
[null,"Australian Distribution Co. (Vic)","Australian Distribution Co. (Victoria)",11222333444,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"distribution determination","123 Straight Street",null,"MELBOURNE","Vic","3000","PO Box 123",null,"MELBOURNE","VIC","3000","Bob Smith","02 1234 5678","bob@auselec.net.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Australian Distribution Co. (Vic)"]
[null,"Australian Transmission Co.","Australian Transmission Co.",11222333444,"-","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","123 Straight Street",null,"SYDNEY","NSW","2000","PO Box 123",null,"SYDNEY","NSW",2000,"Bob Smith","02 1234 5678","bob@auselec.net.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Australian Transmission Co."]
[null,"CitiPower","CitiPower",76064651056,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","40 Market Street",null,"MELBOURNE","Vic","3000","Locked Bag 14090",null,"MELBOURNE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,"YES","YES","NO","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"CitiPower"]
[null,"Directlink","Directlink",16779340889,"Qld","Electricity","Transmission","Revenue cap","Financial","June",9,5,5,"transmission determination","Level 19, HSBC Building","580 George Street","SYDNEY","NSW","2000","PO Box R41",null,"ROYAL EXCHANGE","NSW","1225","Scott Young","02 9275 0031","scott.young@apa.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Directlink"]
[null,"ElectraNet","ElectraNet",41094482416,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","52-55 East Terrace","Rymill Park","ADELAIDE","SA","5000","PO Box 7096","Hutt Street Post Office","ADELAIDE","SA",5000,"Bill Jackson","08 8404 7969","jackson.bill@electranet.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"ElectraNet"]
[null,"Endeavour Energy","Endeavour Energy",59253130878,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","51 Huntingwood Drive",null,"HUNTINGWOOD","NSW","2148","PO Box 811",null,"SEVEN HILLS","NSW","1730","Jon Hocking","02 9853 4386 / 0407 348 156","Jon.Hocking@Endeavourenergy.com.au",null,"NO","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Endeavour Energy"]
[null,"Energex","Energex",40078849055,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","26 Reddacliff Street",null,"NEWSTEAD","Qld","4006","26 Reddacliff Street",null,"NEWSTEAD","QLD","4006","Nicola Roscoe","07 3664 5891","nicolaroscoe@energex.com.au",null,"YES","YES","YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"Energex"]
[null,"Ergon Energy","Ergon Energy",50087646062,"Qld","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","22 Walker Street",null,"TOWNSVILLE","Qld","4810","Po Box 264",null,"FORTITUDE VALLEY","QLD",4006,"Jenny Doyle, Group Manager Regulatory Affairs","(07) 3851 6416","jenny.doyle@ergon.com.au",null,"NO","YES","YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Ergon Energy"]
[null,"Essential Energy","Essential Energy",37428185226,"NSW","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2014-19 Distribution Determination","8 Buller Street",null,"PORT MACQUARIE","NSW","2444","PO Box 5730",null,"PORT MACQUARIE","NSW","2444","Catherine Waddell","02 6338 3553","catherine.waddell@essentialenergy.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Essential Energy"]
[null,"Jemena Electricity","Jemena Electricity",82064651083,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 16","567 Collins Street","MELBOURNE","VIC","3000","PO Box 16182",null,"MELBOURNE","VIC",8001,"Matthew Serpell","03 9173 8231","matthew.serpell@jemena.com.au",null,null,null,"YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"Jemena Electricity"]
[null,"JGN","Jemena Gas Networks (NSW) Ltd","003 004 322","NSW","Gas","Distribution","Weighted average price cap","Financial","June",5,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"JGN"]
[null,"Multinet Gas","Multinet Gas (DB No.1) Pty Ltd (ACN 086 026 986), Multinet Gas (DB No.2) Pty Ltd (ACN 086 230 122)","086026986","Vic","Gas","Distribution","Weighted average price cap","Calendar","December",5,5,"x",null,"6 Nexus Court",null,"MULGRAVE","Vic","3149",null,null,null,null,null,"Stephanie McDougall","03 8846 9538","Stephanie.McDougall@ue.com.au",null,null,null,null,null,null,null,null,null,null,null,null,"Multinet Gas"]
[null,"Murraylink","Murraylink",79181207909,"SA","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Murraylink"]
[null,"Power and Water","Power and Water Corporation",15947352360,"NT","Electricity","Distribution","Revenue cap","Financial","June",5,5,"x","distribution determination","GPO Box 1921",null,"DARWIN","NT","0801","GPO Box 1921",null,"DARWIN","NT","0801","Lucy Moon","08 8924 5822","Lucy.Moon@powerwater.com.au",null,"YES","YES","YES","YES","NO"]
[null,"Powercor Australia","Powercor Australia",89064651109,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","40 Market Street",null,"MELBOURNE","Vic","3000","Locked bag 14090",null,"MELBOURNE","VIC",8001,"Hannah Williams","03 9683 4088","hwilliams@powercor.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Powercor Australia"]
[null,"Powerlink","Queensland Electricity Transmission Corporation Limited trading as Powerlink Queensland",82078849233,"Qld","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","33 Harold St",null,"VIRGINIA","Qld","4014","PO Box 1193",null,"VIRGINIA","QLD",4014,"Jennifer Harris","07 3860 2667","jharris@powerlink.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Powerlink"]
[null,"Roma to Brisbane Pipeline","APT Petroleum Pipelines Limited t/a Roma to Brisbane Pipeline","009 737 393","Qld","Gas","Transmission","Weighted average price cap","Financial","June",5,5,"x","n/a","580 George Street",null,"SYDNEY","NSW","2000","PO Box R41",null,"ROYAL EXCHANGE","NSW","1225","Mark Allen","02 9275 0010","mark.allen@apa.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"Roma to Brisbane Pipeline"]
[null,"SA Power Networks","SA Power Networks",13332330749,"SA","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"2015-20 Distribution Determination","1 Anzac Highway",null,"KESWICK","SA","5035","GPO Box 77",null,"ADELAIDE","SA","5000","Richard Sibly","08 8404 5613","richard.sibly@sapowernetworks.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"SA Power Networks"]
[null,"TasNetworks (D)","TasNetworks (D)",24167357299,"Tas","Electricity","Distribution","Revenue cap","Financial","June",5,5,5,"distribution determination","1-7 Maria Street",null,"LENAH VALLEY","Tas","7008","PO Box 606",null,"MOONAH","Tas","7009","John Sayers","03 6271 6469","john.sayers@tasnetworks.com.au",null,null,null,"YES","YES","YES",null,"Critical Infrastructure","High density commercial","Urban","High density rural","Low density rural","TasNetworks (D)"]
[null,"TasNetworks (T)","TasNetworks (T)",24167357299,"Tas","Electricity","Transmission","Revenue cap","Financial","June",5,5,5,"transmission determination","1-7 Maria Street",null,"LENAH VALLEY","Tas","7008","PO Box 606",null,"MOONAH","Tas","7009","John Sayers","03 6271 6469","john.sayers@tasnetworks.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"TasNetworks (T)"]
[null,"TransGrid","NSW Electricity Networks Operations Pty Ltd trading as TransGrid",609169959,"NSW","Electricity","Transmission","Revenue cap","Financial","June",5,4,5,"transmission determination","180 Thomas Street",null,"SYDNEY","NSW","2000","PO Box A1000",null,"SYDNEY SOUTH","NSW","1235","Garrie Chubb","0408 210 221","garrie.chubb@transgrid.com.au",null,null,null,null,null,null,null,"CBD","Urban","Short rural","Long rural",null,"TransGrid"]
[null,"United Energy","United Energy",70064651029,"Vic","Electricity","Distribution","Revenue cap","Calendar","December",5,5,2,"2016-20 Distribution Determination","Level 3","6 Nexus Court","MULGRAVE","Vic","3149","PO Box 449",null,"MOUNT WAVERLEY","VIC",3170,"Mathew Abraham","03 8846 9758","mathew.abraham@ue.com.au",null,null,null,"YES","NO","NO",null,"CBD","Urban","Short rural","Long rural",null,"United Energy"]
[null,"Western Power (D)","Western Power (D)",18540492861,"WA","Electricity","Distribution","Revenue cap","Financial","June",12,4,"x","distribution determination","363 Wellington Street",null,"PERTH","WA","6000","GPO Box L921",null,"PERTH","WA",6842,"Judy Hunter","08 9326 6239","judy.hunter@westernpower.com.au",null,null,null,"YES","YES","NO","NO","CBD","Urban","Short rural","Long rural",null,"Western Power (D)"]
[null,"Western Power (T)","Western Power (T)",18540492861,"WA","Electricity","Transmission","Revenue cap","Financial","June",12,4,"x","transmission determination","363 Wellington Street",null,"PERTH","WA","6000","GPO Box L921",null,"PERTH","WA",6842,"Judy Hunter","08 9326 6239","judy.hunter@westernpower.com.au",null,null,null,"YES","YES","NO",null,"CBD","Urban","Short rural","Long rural",null,"Western Power (T)"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"For EB & Reset RINs only",null,null,null,null,null,"For AARs only"]
[null,"The Reg Year Ending (dms_RYE) must be set to the last year of the regulatory period. For forecast data is is usually (FRCP_y5) for actual it is a single year (CRY). For historical actual data the RYE will need to be set manually in the business details sheet by setting the dms_Multiyear_flag to 1 and putting the correct value in 'dms_Specified_FinalYear. See cells C67:C68",null,null,null,null,{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"00\"),VALUE(LEFT(CRCP_y1,4)-1))","v":"2011-12"},null,null,null,null,null,null,"Drop down selector box for CA & Reset RINs.","For CA & Reset RINs only",null,null,null,null,null,null,null,"for DNSP only",null,null,null,null,null,"For DNSPs only",null,null,null,null,null,"Reason for interruption","dms_Reason_Interruption_Detailed","dms_Reason_Interruption"]
[null,"dms_Model_List ","DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)",null,"dms_RYE_Formula_Result",null,null,null,null,null,null,null,null,"dms_0203_ProjectType","dms_020303_01_UOM","dms_020501_01_UOM","dms_020501_02_UOM","dms_020501_03_UOM","dms_020501_04_UOM","dms_020603_01_UOM","dms_040102_01_UOM","dms_040102_04_UOM","dms_030601_01_UOM","dms_030601_02_UOM","dms_030701_01_UOM","dms_030702_01_UOM","dms_030703_01_UOM",null,"dms_030605_UOM","dms_03060703_UOM",null,null,null,null,"Animal","Animal impact","Animal"]
[null,"ARR","ANNUAL REPORTING STATEMENT",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - single circuit","Circuit line length in km","0's","0's","0's","0's","0's","0's","days","minutes/customer","minutes/customer","Customer / km","%","km",null,"number","number",null,null,null,null,null,"Animal nesting/burrowing, etc and other","Asset failure"]
[null,"CA","CATEGORY ANALYSIS",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"New line on new route - dual circuit","Circuit line length in km","0's","0's","0's","0's","0's","0's","0's","minutes/customer","minutes/customer","MWh/customer","Number of spans",null,null,"number","number",null,null,null,null,null,"Other","Other"]
[null,"CPI","CPI",null,null,null,null,null,null,null,null,null,null,"New line on new route - other","Circuit line length in km","MVA added","MVA added","MVA added","MVA added","0's","0's","$0s","interruptions/customer","interruptions/customer","kVA / customer","Number of spans",null,null,"number","number",null,null,null,null,"Asset failure","LV","Overloads"]
[null,"EB","ECONOMIC BENCHMARKING",null,{"$f":"LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_SingleYear_FinalYear_Result,2)&RIGHT(dms_SingleYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Line rebuild over existing route - single circuit","Circuit line length in km","0's","0's","0's","0's","0's","$0s","0's","interruptions/customer","interruptions/customer",null,"Number of spans",null,null,"number","number",null,null,null,null,null,"Distribution substation","Planned"]
[null,"PTRM","POST TAX REVENUE MODEL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2022"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit","Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s","(per cent)",null,null,null,null,null,"Number of spans",null,null,"number","(per cent)",null,null,null,null,null,"HV","Network business"]
[null,"Reset","REGULATORY REPORTING STATEMENT",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2022"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,"Formula errors are OK",null,null,null,null,null,"Reconductor - Single circuit","Number","net circuit km added","net circuit km added","net circuit km added","net circuit km added",null,null,null,null,null,null,"Years",null,null,"number",null,null,null,null,null,null,"Zone substation","Third party"]
[null,"RFM","ROLL FORWARD MODEL",null,{"$f":"LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)","v":"2017"},"=LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)",null,null,null,null,null,null,null,"Reconductor - Dual circuit","Number","total spend $0s","total spend $0s","total spend $0s","total spend $0s",null,null,null,null,null,null,"Years",null,null,"number",null,null,null,null,null,null,"Subtransmission","Unknown"]
[null,"WACC","WEIGHTED AVERAGE COST OF CAPITAL",null,{"$f":"LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)","v":"2022"},"=LEFT(dms_MultiYear_FinalYear_Result,2)&RIGHT(dms_MultiYear_FinalYear_Result,2)",null,null,null,null,null,null,null,"Other",null,"net circuit km added","net circuit km added","net circuit km added","net circuit km added",null,null,null,null,null,null,"Trees",null,null,"number",null,null,null,null,null,"Other","insert description of 'other'","Vegetation"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"total spend $0s","total spend $0s","total spend $0s","total spend $0s",null,null,null,null,null,null,"Trees",null,null,"number",null,null,null,null,null,"Overloads","-","Weather"]
[null,"dms_DataQuality_List",null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,"$0s",null,null,null,null,null,null,null,"Defects",null,null,"number",null,null,null,null,null,"Planned","-","2 - STPIS Exclusion (3.3)(a)"]
[null,"Actual",null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,null,null,null,null,null,null,null,null,"Defects",null,null,"number",null,null,null,null,null,"Network business","Network error","3 - STPIS Exclusion (3.3)(a)"]
[null,"Estimate",null,null,null,null,null,null,null,null,null,null,null,null,null,"0's",null,null,null,null,null,null,null,null,null,"Spans",null,null,"number",null,null,null,null,null,null,"Switching and protection error","4 - STPIS Exclusion (3.3)(a)"]
[null,"Consolidated",null,null,null,null,null,null,null,null,null,null,null,null,null,"$0s",null,null,null,null,null,null,null,null,null,"km",null,null,"(per cent)",null,null,null,null,null,"Third party","Fire","5 - STPIS Exclusion (3.3)(a)"]
[null,"Recast",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Spans",null,null,"(per cent)","",null,null,null,null,null,"Other","6 - STPIS Exclusion (3.3)(a)"]
[null,"Public",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dig-in","7 - STPIS Exclusion (3.3)(a)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Unauthorised access"]
[null,"For all files either AER or business needs to be able to specify the type of submission","For PTRM & RFM templates we must provide a choice in case they change their form of control - otherwise it is drawn from the business specific lookup table above.",null,null,null,null,null,null,null,null,null,null,null,"For PTRM files - this field set the text for the named range \"DMS_Xfactor\" which in all cases is simply the text \"x factors\" - this saves putting in each old gas PTRM file ",null,null,null,null,null,null,null,"for TNSP only",null,null,null,null,null,null,null,null,null,null,null,null,"Vehicle impact"]
[null,"dms_SourceList","dms_FormControl_Choices",null,null,null,null,null,null,null,null,null,null,null,"DMS_Xfactor",null,null,null,null,null,null,null,"dms_030601_01_UOM",null,"dms_030701_01_UOM","dms_030702_01_UOM",null,null,null,null,null,null,null,null,"Unknown","Unknown"]
[null,"After appeal","Revenue cap",null,null,null,null,null,null,null,null,null,null,null,"x factors",null,null,null,null,null,null,null,"%",null,"Number of spans","km",null,null,null,null,null,null,null,null,"Vegetation","Blow-in/Fall-in - NSP responsibility"]
[null,"Draft decision","Revenue yield",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Years","%",null,null,null,null,null,null,null,null,null,"Grow-in - NSP responsibility"]
[null,"Final decision","Weighted average price cap",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Trees","km",null,null,null,null,null,null,null,null,null,"Blow-in/Fall-in - Other responsible party"]
[null,"PTRM update 1",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%",null,"Defects","number",null,null,null,null,null,null,null,null,null,"Grow-in - Other responsible party"]
[null,"PTRM update 2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Number of spans",null,null,null,null,null,null,null,null,null,"Weather"]
[null,"PTRM update 3",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"km",null,null,null,null,null,null,null,null,null,"2 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 4",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%",null,"km",null,null,null,null,null,null,null,null,null,"3 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 5",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,"Number of spans",null,null,null,null,null,null,null,null,null,"4 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 6",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,null,null,null,null,null,null,null,null,null,null,"5 - STPIS Exclusion (3.3)(a)"]
[null,"PTRM update 7",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%",null,null,null,null,null,null,null,null,null,null,null,"6 - STPIS Exclusion (3.3)(a)"]
[null,"Regulatory proposal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number",null,null,null,null,null,null,null,null,null,null,null,"7 - STPIS Exclusion (3.3)(a)"]
[null,"Reporting",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%"]
[null,"Revised regulatory proposal",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"number"]
[]
[]
[]
[null,"These are indeces and lookup values for various dates. All step from the value placed in FRCP_y1 on the business and other details worksheet",null,null,null,null,null,null,null,null,null,"These date tables are currently used in the Recast templates to provide column headings and conditional formatting"]
[null,"dms_FRCPlength_Num_List","dms_FinalYear_List","dms_CRCPlength_Num_List","dms_CFinalYear_List","dms_FRCP_years",null,"dms_CRCP_years",null,"dms_CRCP_index",null,"CRY from input cell on business sheet","CRY - financial","dms_FinYears","CRY calendar","dms_CalYears"]
[null,1,"dms_FRCP_y1",1,"CRCP_y1",{"$f":"FRCP_y1","v":"2017-18"},"dms_FRCP_y1",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)-1)&\"-\"&TEXT(VALUE(MID(dms_FRCP_y1,3,2)),\"00\"),VALUE(LEFT(dms_FRCP_y1,4)-1))","v":"2016-17"},"dms_CRCP_yZ",1,null,{"$f":"CRY","v":"2016-17"},{"$f":"VALUE(LEFT(CRY,4))&\"-\"&TEXT(MID(CRY,3,2)+1,\"00\")","v":"2016-17"},"dms_CRYf_y1",{"$f":"VALUE(LEFT(CRY,4)+1)","v":2017},"dms_CRYc_y1"]
[null,2,"dms_FRCP_y2",2,"CRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y1,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y1,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y1,4)+1))","v":"2018-19"},"dms_FRCP_y2",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yZ,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yZ,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yZ,4)-1))","v":"2015-16"},"dms_CRCP_yY",2,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y1,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y1,3,2)+2,\"00\")","v":"2017-18"},"dms_CRYf_y2",{"$f":"VALUE(LEFT(dms_CRYc_y1,4)+1)","v":2018},"dms_CRYc_y2"]
[null,3,"dms_FRCP_y3",3,"CRCP_y3",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y2,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y2,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y2,4)+1))","v":"2019-20"},"dms_FRCP_y3",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yY,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yY,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yY,4)-1))","v":"2014-15"},"dms_CRCP_yX",3,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y2,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y2,3,2)+2,\"00\")","v":"2018-19"},"dms_CRYf_y3",{"$f":"VALUE(LEFT(dms_CRYc_y2,4)+1)","v":2019},"dms_CRYc_y3"]
[null,4,"dms_FRCP_y4",4,"CRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y3,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y3,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y3,4)+1))","v":"2020-21"},"dms_FRCP_y4",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yX,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yX,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yX,4)-1))","v":"2013-14"},"dms_CRCP_yW",4,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y3,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y3,3,2)+2,\"00\")","v":"2019-20"},"dms_CRYf_y4",{"$f":"VALUE(LEFT(dms_CRYc_y3,4)+1)","v":2020},"dms_CRYc_y4"]
[null,5,"dms_FRCP_y5",5,"CRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y4,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y4,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y4,4)+1))","v":"2021-22"},"dms_FRCP_y5",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yW,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yW,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yW,4)-1))","v":"2012-13"},"dms_CRCP_yV",5,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y4,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y4,3,2)+2,\"00\")","v":"2020-21"},"dms_CRYf_y5",{"$f":"VALUE(LEFT(dms_CRYc_y4,4)+1)","v":2021},"dms_CRYc_y5"]
[null,6,"dms_FRCP_y6",6,"CRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y5,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y5,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y5,4)+1))","v":"2022-23"},"dms_FRCP_y6",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yV,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yV,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yV,4)-1))","v":"2011-12"},"dms_CRCP_yU",6,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y5,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y5,3,2)+2,\"00\")","v":"2021-22"},"dms_CRYf_y6",{"$f":"VALUE(LEFT(dms_CRYc_y5,4)+1)","v":2022},"dms_CRYc_y6"]
[null,7,"dms_FRCP_y7",7,"CRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y6,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y6,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y6,4)+1))","v":"2023-24"},"dms_FRCP_y7",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yU,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yU,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yU,4)-1))","v":"2010-11"},"dms_CRCP_yT",7,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y6,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y6,3,2)+2,\"00\")","v":"2022-23"},"dms_CRYf_y7",{"$f":"VALUE(LEFT(dms_CRYc_y6,4)+1)","v":2023},"dms_CRYc_y7"]
[null,8,"dms_FRCP_y8",8,"CRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y7,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y7,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y7,4)+1))","v":"2024-25"},"dms_FRCP_y8",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yT,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yT,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yT,4)-1))","v":"2009-10"},"dms_CRCP_yS",8,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y7,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y7,3,2)+2,\"00\")","v":"2023-24"},"dms_CRYf_y8",{"$f":"VALUE(LEFT(dms_CRYc_y7,4)+1)","v":2024},"dms_CRYc_y8"]
[null,9,"dms_FRCP_y9",9,"CRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y8,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y8,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y8,4)+1))","v":"2025-26"},"dms_FRCP_y9",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yS,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yS,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yS,4)-1))","v":"2008-09"},"dms_CRCP_yR",9,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y8,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y8,3,2)+2,\"00\")","v":"2024-25"},"dms_CRYf_y9",{"$f":"VALUE(LEFT(dms_CRYc_y8,4)+1)","v":2025},"dms_CRYc_y9"]
[null,10,"dms_FRCP_y10",10,"CRCP_y10",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y9,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y9,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y9,4)+1))","v":"2026-27"},"dms_FRCP_y10",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yR,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yR,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yR,4)-1))","v":"2007-08"},"dms_CRCP_yQ",10,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y9,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y9,3,2)+2,\"00\")","v":"2025-26"},"dms_CRYf_y10",{"$f":"VALUE(LEFT(dms_CRYc_y9,4)+1)","v":2026},"dms_CRYc_y10"]
[null,11,"dms_FRCP_y11",11,"CRCP_y11",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y10,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y10,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y10,4)+1))","v":"2027-28"},"dms_FRCP_y11",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yQ,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yQ,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yQ,4)-1))","v":"2006-07"},"dms_CRCP_yP",11,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y10,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y10,3,2)+2,\"00\")","v":"2026-27"},"dms_CRYf_y11",{"$f":"VALUE(LEFT(dms_CRYc_y10,4)+1)","v":2027},"dms_CRYc_y11"]
[null,12,"dms_FRCP_y12",12,"CRCP_y12",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y11,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y11,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y11,4)+1))","v":"2028-29"},"dms_FRCP_y12",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yP,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yP,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yP,4)-1))","v":"2005-06"},"dms_CRCP_yO",12,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y11,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y11,3,2)+2,\"00\")","v":"2027-28"},"dms_CRYf_y12",{"$f":"VALUE(LEFT(dms_CRYc_y11,4)+1)","v":2028},"dms_CRYc_y12"]
[null,13,"dms_FRCP_y13",13,"CRCP_y13",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y12,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y12,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y12,4)+1))","v":"2029-30"},"dms_FRCP_y13",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yO,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yO,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yO,4)-1))","v":"2004-05"},"dms_CRCP_yN",13,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y12,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y12,3,2)+2,\"00\")","v":"2028-29"},"dms_CRYf_y13",{"$f":"VALUE(LEFT(dms_CRYc_y12,4)+1)","v":2029},"dms_CRYc_y13"]
[null,14,"dms_FRCP_y14",14,"CRCP_y14",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y13,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y13,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y13,4)+1))","v":"2030-31"},"dms_FRCP_y14",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yN,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yN,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yN,4)-1))","v":"2003-04"},"dms_CRCP_yM",14,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y13,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y13,3,2)+2,\"00\")","v":"2029-30"},"dms_CRYf_y14",{"$f":"VALUE(LEFT(dms_CRYc_y13,4)+1)","v":2030},"dms_CRYc_y14"]
[null,15,"dms_FRCP_y15",15,"CRCP_y15",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_FRCP_y14,4)+1)&\"-\"&TEXT(VALUE(RIGHT(dms_FRCP_y14,2)+1),\"00\"),VALUE(LEFT(dms_FRCP_y14,4)+1))","v":"2031-32"},"dms_FRCP_y15",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(dms_CRCP_yM,4)-1)&\"-\"&TEXT(VALUE(MID(dms_CRCP_yM,3,2)),\"00\"),VALUE(LEFT(dms_CRCP_yM,4)-1))","v":"2002-03"},"dms_CRCP_yL",15,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y14,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y14,3,2)+2,\"00\")","v":"2030-31"},"dms_CRYf_y15",{"$f":"VALUE(LEFT(dms_CRYc_y14,4)+1)","v":2031},"dms_CRYc_y15"]
[null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y15,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y15,3,2)+2,\"00\")","v":"2031-32"},"dms_CRYf_y16",{"$f":"VALUE(LEFT(dms_CRYc_y15,4)+1)","v":2032},"dms_CRYc_y16"]
[null,"These are drop down lists for businesses to select the correct FRCP_y1 on the business and other details worksheet.\nThis also populates the column headings in the worksheets",null,null,null,null,null,null,null,null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y16,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y16,3,2)+2,\"00\")","v":"2032-33"},"dms_CRYf_y17",{"$f":"VALUE(LEFT(dms_CRYc_y16,4)+1)","v":2033},"dms_CRYc_y17"]
[null,"dms_RCP_fyear_list","dms_CRY_ListF","dms_CRY_ListC","dms_RCP_cyear_list","dms_FRCP_fyear_list","dms_FRCP_ListF","dms_FRCP_ListC","dms_FRCP_cyear_list",null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y17,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y17,3,2)+2,\"00\")","v":"2033-34"},"dms_CRYf_y18",{"$f":"VALUE(LEFT(dms_CRYc_y17,4)+1)","v":2034},"dms_CRYc_y18"]
[null,"dms_fy1","2006-07",2007,"dms_cy1","dms_frcp_fy1","2015-16",2016,"dms_crcp_cy1",null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y18,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y18,3,2)+2,\"00\")","v":"2034-35"},"dms_CRYf_y19",{"$f":"VALUE(LEFT(dms_CRYc_y18,4)+1)","v":2035},"dms_CRYc_y19"]
[null,"dms_fy2","2007-08","2008","dms_cy2","dms_frcp_fy2","2016-17",2017,"dms_crcp_cy2",null,null,null,{"$f":"VALUE(LEFT(dms_CRYf_y19,4)+1)&\"-\"&TEXT(MID(dms_CRYf_y19,3,2)+2,\"00\")","v":"2035-36"},"dms_CRYf_y20",{"$f":"VALUE(LEFT(dms_CRYc_y19,4)+1)","v":2036},"dms_CRYc_y20"]
[null,"dms_fy3","2008-09","2009","dms_cy3","dms_frcp_fy3","2017-18",2018,"dms_crcp_cy3"]
[null,"dms_fy4","2009-10","2010","dms_cy4","dms_frcp_fy4","2018-19",2019,"dms_crcp_cy4"]
[null,"dms_fy5","2010-11","2011","dms_cy5","dms_frcp_fy5","2019-20",2020,"dms_crcp_cy5"]
[null,"dms_fy6","2011-12","2012","dms_cy6","dms_frcp_fy6","2020-21",2021,"dms_crcp_cy6"]
[null,"dms_fy7","2012-13","2013","dms_cy7","dms_frcp_fy7","2021-22",2022,"dms_crcp_cy7"]
[null,"dms_fy8","2013-14","2014","dms_cy8","dms_frcp_fy8","2022-23",2023,"dms_crcp_cy8",null,null,"2005-06","2006"]
[null,"dms_fy9","2014-15","2015","dms_cy9","dms_frcp_fy9","2023-24",2024,"dms_crcp_cy9",null,null,"2006-07","2007"]
[null,"dms_fy10","2015-16","2016","dms_cy10","dms_frcp_fy10","2024-25",2025,"dms_crcp_cy10",null,null,"2007-08","2008"]
[null,"dms_fy11","2016-17","2017","dms_cy11","dms_frcp_fy11","2025-26",2026,"dms_crcp_cy11",null,null,"2008-09","2009"]
[null,"dms_fy12","2017-18","2018","dms_cy12","dms_frcp_fy12","2026-27",2027,"dms_crcp_cy12",null,null,"2009-10",2010]
[null,"dms_fy13","2018-19",2019,"dms_cy13","dms_frcp_fy13","2027-28",2028,"dms_crcp_cy13",null,null,"2010-11",2011]
[null,"dms_fy14","2019-20","2020","dms_cy14","dms_frcp_fy14","2028-29",2029,"dms_crcp_cy14",null,null,"2011-12",2012]
[null,"dms_fy15","2019-20","2020","dms_cy15","dms_frcp_fy15","2029-30",2030,"dms_crcp_cy15",null,null,"2012-13",2013]
[null,"dms_fy16","2020-21","2021","dms_cy16",null,null,null,null,null,null,"2013-14",2014]
[null,"dms_fy17","2021-22","2022","dms_cy17",null,null,null,null,null,null,"2014-15",2015]
[null,"dms_fy18","2022-23","2023","dms_cy18",null,null,null,null,null,null,"2015-16",2016]
[null,"dms_fy19","2023-24","2024","dms_cy19",null,null,null,null,null,null,"2016-17",2017]
[null,"dms_fy20","2024-25","2025","dms_cy20",null,null,null,null,null,null,"2017-18",2018]
[null,null,null,null,null,null,null,null,null,null,null,"2018-19",2019]
[null,null,null,null,null,null,null,null,null,null,null,"2019-20",2020]
[null,null,null,null,null,null,null,null,null,null,null,"2020-21",2021]
[null,null,null,null,null,null,null,null,null,null,null,"2021-22",2022]
[null,null,null,null,null,null,null,null,null,null,null,"2022-23",2023]
[null,null,null,null,null,null,null,null,null,null,null,"2023-24",2024]
[null,null,null,null,null,null,null,null,null,null,null,"2024-25",2025]
[null,null,null,null,null,null,null,null,null,null,null,"2025-26",2026]
[null,null,null,null,null,null,null,null,null,null,null,"2026-27",2027]
[null,null,null,null,null,null,null,null,null,null,null,"2027-28",2028]
[null,null,null,null,null,null,null,null,null,null,null,"2028-29",2029]
[null,null,null,null,null,null,null,null,null,null,null,"2029-30",2030]
[null,null,null,null,null,null,null,null,null,null,null,"2030-31",2031]
[null,null,null,null,null,null,null,null,null,null,null,"2031-32",2032]
[null,null,null,null,null,null,null,null,null,null,null,"2032-33",2033]
[null,null,null,null,null,null,null,null,null,null,null,"2033-34",2034]
[null,null,null,null,null,null,null,null,null,null,null,"2034-35",2035]
[null,null,null,null,null,null,null,null,null,null,null,"2035-36",2036]

{"sheet":"Instructions","index":1,"n_rows":27,"n_cols":4,"rows_kept":27,"cut":false,"hidden":false,"merged":[[24,2,24,4],[25,2,25,3],[26,2,26,4],[8,2,8,4],[10,2,10,4],[12,2,12,4],[20,2,20,4],[22,2,22,4],[7,2,7,3],[1,1,1,5],[2,1,2,5],[3,2,3,4],[4,2,4,4],[5,2,5,4]]}
[]
[null,{"$f":"CONCATENATE(dms_Segment,\" Network Service Provider\")","v":"Distribution Network Service Provider"}]
[null,"Annual Reporting RIN Template"]
[null,null,{"$f":"CONCATENATE(\"This template is to be used by \",dms_TradingName,\" to fulfil its reporting obligations to the AER.\")","v":"This template is to be used by SA Power Networks to fulfil its reporting obligations to the AER."}]
[null,null,"INSTRUCTIONS"]
[null,null,"Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting."]
[]
[null,null,"Identifying CONFIDENTIAL INFORMATION:\n\nPlease use the macro at the top of each \nworksheet to identify confidential information. \n\n"]
[null,null,"-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential.\n\n-To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro"]
[]
[null,null,"UNITS OF MEASURE\n\nAll amounts are to be unrounded and reported in nominal terms on a one for one basis: that is 1000 is to be entered as '1000'.\n\n"]
[]
[null,null,"COLOUR CODING OF INPUT / NON-INPUT CELLS:"]
[null,null,null,"Yellow = Input cell (mandatory)"]
[null,null,null,"Darker yellow = input cell (mandatory)"]
[null,null,null,"Orange = input cell (if data available)"]
[null,null,null,"Grey = Not applicable/No inputs required"]
[null,null,null,"Leave coloured cells blank if no information exists. \nPLEASE DO NOT ENTER TEXT into cells that are to contain numeric data."]
[]
[]
[null,null,"WORKSHEET NAVIGATION\n\nMany tables in the worksheets have been \"grouped\" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin of excel (for Row groupings) or above the columns (for column groupings). \n\n\n\n"]
[]
[null,null,"RETURNING COMPLETED RESPONSES\n\nPlease return four (4) files to the AER: \n1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. \n\n2. An actual and an estimate version with confidential information marked using the Mark selected cells CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER.\n\n3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response.\n\n\nUse the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public. "]
[]
[null,null,"SUBMITTING AMENDED DATA TO THE AER\n\nIf an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. \n\nNSPs must identify the reason for the amendments in the Amendment Reason box on the  Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. \n\n."]
[null,null,"NSP may use Amended Data macro \nto highlight cells that contain amended data.\nNB: if data is also CONFIDENTIAL, re-apply \nthe Confidentiality macro after applying the \nAmended macro"]
[null,null,"Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER"]

{"sheet":"Contents","index":2,"n_rows":27,"n_cols":19,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"CONTENTS"]
[]
[]
[null,null,null,null,"1. Business details",null,null,null,null,null,null,"2. Expenditure"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,"4. Alternative control services",null,null,null,null,null,null,"5. Network information",null,null,null,null,null,null,"6. Service & quality"]

{"sheet":"Business & other details","index":3,"n_rows":90,"n_cols":12,"rows_kept":90,"cut":false,"hidden":false,"merged":[[7,1,7,8],[11,1,11,8],[13,2,13,4],[14,2,14,4],[17,2,17,3],[17,4,17,7],[84,4,84,8],[18,4,18,7],[19,2,19,3],[19,4,19,7],[22,2,22,3],[22,4,22,7],[23,4,23,7],[24,2,24,3],[24,4,24,7],[32,1,32,8],[51,2,51,3],[53,2,53,8]]}
[null,{"$f":"IF(dms_DataQuality=\"backcast\",INDEX(dms_Worksheet_List,MATCH(dms_Model,dms_Model_List))&\" BACKCAST\",INDEX(dms_Worksheet_List,MATCH(dms_Model,dms_Model_List)))","v":"CATEGORY ANALYSIS"}]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"BUSINESS & OTHER DETAILS"]
[]
[]
[null,"Instructions"]
[null,"Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells. "]
[]
[null,"SUBMISSION PARTICULARS INPUT SHEETS"]
[]
[null,"ENTITY DETAILS"]
[]
[null,"Short name","SA Power Networks",null,null,"Select business name from drop down list first"]
[null,"ACN / ABN",{"$f":"INDEX(dms_ABN_List,MATCH(dms_TradingName,dms_TradingName_List))","v":13332330749}]
[]
[]
[null,"Business address","Address 1",null,{"$f":"INDEX(dms_Addr1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"1 Anzac Highway"}]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",INDEX(dms_Addr2_List,MATCH(dms_TradingName,dms_TradingName_List)))","v":""}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_Suburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"KESWICK"}]
[null,null,null,"State",{"$f":"INDEX(dms_State_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA"},"p/code",{"$f":"INDEX(dms_PostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"5035"}]
[]
[null,"Postal address","Address 1",null,{"$f":"INDEX(dms_PAddr1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"GPO Box 77"}]
[null,null,null,"Address 2",{"$f":"IF(ISBLANK(INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List))),\"\",INDEX(dms_PAddr2_List,MATCH(dms_TradingName,dms_TradingName_List)))","v":""}]
[null,null,"Suburb",null,{"$f":"INDEX(dms_PSuburb_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"ADELAIDE"}]
[null,null,null,"State",{"$f":"INDEX(dms_PState_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA"},"p/code",{"$f":"INDEX(dms_PPostCode_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"5000"}]
[]
[]
[null,"Contact name/s",{"$f":"INDEX(dms_ContactName1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Richard Sibly"}]
[null,"Contact phone/s",{"$f":"INDEX(dms_ContactPh1_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"08 8404 5613"}]
[null,"Contact email address/s",{"$f":"INDEX(dms_ContactEmail_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"richard.sibly@sapowernetworks.com.au"}]
[]
[null,"REGULATORY CONTROL PERIODS"]
[]
[null,"Forthcoming regulatory control period","2017-18",{"$f":"dms_FRCP_y2","v":"2018-19"},{"$f":"dms_FRCP_y3","v":"2019-20"},{"$f":"dms_FRCP_y4","v":"2020-21"},{"$f":"dms_FRCP_y5","v":"2021-22"},{"$f":"dms_FRCP_y6","v":"2022-23"},{"$f":"dms_FRCP_y7","v":"2023-24"},{"$f":"dms_FRCP_y8","v":"2024-25"},{"$f":"dms_FRCP_y9","v":"2025-26"},{"$f":"dms_FRCP_y10","v":"2026-27"}]
[]
[]
[null,"Current regulatory control period",{"$f":"dms_CRCP_FirstYear_Result","v":"2012-13"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)+1)&\"-\"&TEXT(MID(CRCP_y1,3,2)+2,\"00\"),VALUE(LEFT(CRCP_y1,4)+1))","v":"2013-14"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y2,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y2,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y2,4)+1))","v":"2014-15"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y3,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y3,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y3,4)+1))","v":"2015-16"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y4,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y4,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y4,4)+1))","v":"2016-17"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y5,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y5,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y5,4)+1))","v":"2017-18"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y6,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y6,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y6,4)+1))","v":"2018-19"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y7,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y7,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y7,4)+1))","v":"2019-20"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y8,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y8,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y8,4)+1))","v":"2020-21"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y9,4)+1)&\"-\"&TEXT(VALUE(MID(CRCP_y9,3,2)+2),\"00\"),VALUE(LEFT(CRCP_y9,4)+1))","v":"2021-22"}]
[]
[]
[null,"Previous regulatory control period",{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y2,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y2,3,2)),\"00\"),VALUE(LEFT(PRCP_y2,4)-1))","v":"2007-08"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y3,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y3,3,2)),\"00\"),VALUE(LEFT(PRCP_y3,4)-1))","v":"2008-09"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y4,4)-1)&\"-\"&TEXT(VALUE(MID(PRCP_y4,3,2)),\"00\"),VALUE(LEFT(PRCP_y4,4)-1))","v":"2009-10"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(PRCP_y5,4)-1)&\"-\"&TEXT(VALUE(RIGHT(PRCP_y5,2)-1),\"00\"),VALUE(LEFT(PRCP_y5,4)-1))","v":"2010-11"},{"$f":"IF(dms_RPT=\"financial\",VALUE(LEFT(CRCP_y1,4)-1)&\"-\"&TEXT(VALUE(RIGHT(CRCP_y1,2)-1),\"00\"),VALUE(LEFT(CRCP_y1,4)-1))","v":"2011-12"}]
[]
[]
[null,"Commencing regulatory year","2016-17","CRY"]
[]
[null,"Last completed regulatory year","2021-22","dms_FinalYear"]
[]
[]
[null,null,"DELETE NR 'CRY' IF NOT AN ANNUAL RIN (EB, CA , ARR)"]
[null,null,"APPLY NR 'CRY' IF AN ANNUAL RIN (EB, CA , ARR) - including multi year annual RINs eg. Recast CA. EB"]
[]
[null,"Source","Reporting",null,"Please select the correct submission type from the dropdown list."]
[null,"Data quality (actual, estimate, public, consolidated)","Public"]
[null,"Amended RIN submission - amendment reason","Updated on 11 September 2018 -  Total Labour Expenditure updated as $0's, not$’000 as previously recorded. See D18/132291."]
[null,"Submission Date","2017-10-31","dms_SubmissionDate","Please enter date this file submitted to AER (dd/mm/yyyy)"]
[null,"EBSS - First application of scheme in forthcoming period?","No"]
[null,"Sector",{"$f":"INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Electricity"},"dms_Sector","=INDEX(dms_Sector_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Segment",{"$f":"INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Distribution"},"dms_Segment","=INDEX(dms_Segment_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Regulatory Year Ending",{"$f":"IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))","v":"2017"},"dms_RYE","=IF(dms_MultiYear_Flag=1,LEFT(dms_Specified_FinalYear,2)&RIGHT(dms_Specified_FinalYear,2),INDEX(dms_RYE_Formula_Result,MATCH(dms_Model,dms_Model_List)))"]
[null,"Reporting Period Type",{"$f":"INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Financial"},"dms_RPT","=INDEX(dms_RPT_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Model or RIN Type","CA","dms_Model","Drop down selection"]
[null,"Security Classification","Public","dms_Classification","Always Public"]
[null,"Template - version no.",5,"dms_TemplateNumber"]
[null,"Dollar $ real month",{"$f":"INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"June"},"dms_RPTMonth","=INDEX(dms_RPTMonth_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Dollar $ real  (the last month before the FRCP_y1)",{"$f":"CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2)))","v":"June 2017"},"dms_DollarReal","=IF(SUM(dms_SingleYear_Model)>0,CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(CRY,2))&RIGHT(CRY,2)),CONCATENATE(dms_RPTMonth)&\" \"&VALUE((LEFT(dms_CRCP_FinalYear_Result,2)&RIGHT(dms_CRCP_FinalYear_Result,2))))"]
[null,"Form of control",{"$f":"INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"Revenue cap"},"dms_FormControl","=INDEX(dms_FormControl_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"RIN response - version no.",1,"dms_RINversion"]
[null,"Jurisdiction",{"$f":"INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA"},"dms_Jurisdiction","=INDEX(dms_JurisdictionList,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Backcast Multiyear EB, CA or ARR?",0,"dms_MultiYear_Flag","1=y, 0-n"]
[null,null,2013,"dms_Specified_FinalYear","The result here is returned to dms_CRCP_FinalYear_Result if dms_MultiYear_Flag is set to 1"]
[null,"Single Year Model T/F",{"$f":"IF(dms_Model=\"EB\",1,0)","v":0},"dms_EB"]
[null,null,{"$f":"IF(dms_Model=\"CA\",1,0)","v":1},"dms_CA","=dms_SingleYear_Model"]
[null,null,{"$f":"IF(dms_Model=\"ARR\",1,0)","v":0},"dms_ARR"]
[null,"Single Year Final Year Reference","CRY","dms_SingleYear_FinalYear_Ref","This is the reference for EB, CA & ARR RINs"]
[null,"Single Year Final Year Result",{"$f":"INDIRECT(dms_SingleYear_FinalYear_Ref)","v":"2016-17"},"dms_SingleYear_FinalYear_Result","=INDIRECT(dms_SingleYear_FinalYear_Ref)",null,null,null,"Formula errors OK"]
[null,"FRCP length in years",{"$f":"INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_FRCPlength_Num","=INDEX(dms_FRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"Multi Year Final Year Reference",{"$f":"INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))","v":"dms_FRCP_y5"},"dms_MultiYear_FinalYear_Ref","=INDEX(dms_FinalYear_List,MATCH(dms_FRCPlength_Num,dms_FRCPlength_Num_List))"]
[null,"Multi Year Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)","v":"2021-22"},"dms_MultiYear_FinalYear_Result","=IF(dms_MultiYear_Flag=0,INDIRECT(dms_MultiYear_FinalYear_Ref),dms_Specified_FinalYear)",null,null,null,"Formula errors OK"]
[null,"CRCP length in years",{"$f":"INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_CRCPlength_Num","=INDEX(dms_CRCPlength_List,MATCH(dms_TradingName,dms_TradingName_List))"]
[null,"CRCP Final Year Reference",{"$f":"INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))","v":"CRCP_y5"},"dms_CRCP_FinalYear_Ref","=INDEX(dms_CFinalYear_List,MATCH(dms_CRCPlength_Num,dms_CRCPlength_Num_List))"]
[null,"CRCP First Year Result",{"$f":"INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))","v":"2012-13"},"dms_CRCP_FirstYear_Result","=INDEX(dms_CRCP_years,MATCH(dms_CRCPlength_Num,dms_CRCP_index))"]
[null,"CRCP Final Year Result",{"$f":"IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)","v":"2016-17"},"dms_CRCP_FinalYear_Result","=IF(dms_MultiYear_Flag=0,(IF(SUM(dms_SingleYear_Model)>0,CRY,dms_CRCP_yZ)),dms_Specified_FinalYear)"]
[null,"Table 6.6.3 - Public lighting repair - no. business days",{"$f":"INDEX(dms_663_List,MATCH(dms_TradingName,dms_TradingName_List))","v":5},"dms_663"]
[null,"Distribution Determination Reference",{"$f":"INDEX(dms_DeterminationRef_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"2015-20 Distribution Determination"}]
[null,"Backcast templates only - unit of measure ","$0s","dms_Backcast_UOM","If the cover sheet is for Backcast data ensure to apply dms_Backcast_UOM named range to this field. Otherwise, do not apply this named range."]
[null,"EB/CA Unit of Measure for Monetary Values","$0s","dms_dollar_nom_UOM","If the cover sheet is attached to an EB files make sure this field is set"]
[]
[null,"discard this record?","NO","dms_DISCARD","If record is to be discarded from DB set this flag to YES"]
[]
[null,"USES NAMED RANGES FLAG","yes","dms_Defined_Names_Used"]

{"sheet":"2.1 Expenditure summary","index":4,"n_rows":126,"n_cols":3,"rows_kept":126,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.1 EXPENDITURE SUMMARY & RECONCILIATION"]
[]
[null,"There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.1.1 - STANDARD CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Replacement expenditure",97755302.76000002]
[null,"Connections",58216593.900000006]
[null,"Augmentation Expenditure",60077472.890000008]
[null,"Non-network",86239351.39000009]
[null,"capitalised network overheads",11307921.5]
[null,"capitalised corporate overheads",-9361715.3000000007]
[null,"Metering",0]
[null,"Public Lighting",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-2248990.4200000018]
[null,"capcons (included in the above)",27770975.236429609]
[null,"TOTAL GROSS CAPEX \n(including capcons)",{"$f":"+SUM(C11:C26)","v":301985936.72000009}]
[]
[null,"2.1.2 - STANDARD CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Vegetation management",29750410.349999994]
[null,"Maintenance",27404540.430000003]
[null,"Emergency response",43002001.479999989]
[null,"Non-network",35928982.085820213]
[null,"network overheads",93624261.63817668]
[null,"corporate overheads",58995611.877521463]
[null,"Metering",0]
[null,"Public Lighting",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-37995497.235820219]
[null,"TOTAL OPEX",{"$f":"+SUM(C33:C48)","v":250710310.62569809}]
[]
[null,"2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Connections",0]
[null,"capitalised network overheads",324540.77]
[null,"capitalised corporate overheads",-145107.64000000001]
[null,"Metering",6308184.9199999999]
[null,"Public lighting",0]
[null,"Fee and quoted",0]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item",0]
[null,"TOTAL CAPEX",{"$f":"+SUM(C54:C67)","v":6487618.0499999998}]
[]
[null,"2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Connections",0]
[null,"network overheads",2501637.3417895064]
[null,"corporate overheads",1014888.1358298482]
[null,"Metering",5478694.3499999987]
[null,"Public lighting",0]
[null,"Fee and quoted",0]
[null,null,356954.89012286917]
[]
[]
[]
[]
[]
[]
[null,"balancing item",-356954.89012286917]
[null,"TOTAL OPEX",{"$f":"+SUM(C73:C86)","v":8995219.8276193533}]
[]
[null,"2.1.5 - DUAL FUNCTION ASSETS CAPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Replacement expenditure"]
[null,"Connections"]
[null,"Augmentation Expenditure"]
[null,"Non-network"]
[null,"Capitalised network overheads"]
[null,"Capitalised corporate overheads"]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item"]
[null,"capcons (included in the above)"]
[null,"TOTAL GROSS CAPEX (including capcons)",{"$f":"SUM(C92:C105)","v":0}]
[]
[null,"2.1.6 - DUAL FUNCTION ASSETS OPEX"]
[null,null,"EXPENDITURE\n($0's)"]
[null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Vegetation management"]
[null,"Maintenance"]
[null,"Emergency response"]
[null,"Non-network"]
[null,"Network overheads"]
[null,"Corporate overheads"]
[]
[]
[]
[]
[]
[]
[]
[null,"balancing item"]
[null,"TOTAL OPEX",{"$f":"SUM(C112:C125)","v":0}]

{"sheet":"2.2 Repex","index":5,"n_rows":180,"n_cols":7,"rows_kept":180,"cut":false,"hidden":false,"merged":[[159,1,162,1],[163,1,166,1],[174,1,177,1],[178,1,179,1],[167,1,173,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.2 REPEX"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY"]
[null,null,null,null,"EXPENDITURE ($0's)","ASSET REPLACEMENTS\n(0's)","ASSET FAILURES\n(0's)"]
[null,"ASSET GROUP","ASSET CATEGORY",null,{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole"]
[null,null,"˂ = 1 kV; Wood"]
[null,null,"> 1 kV & < = 11 kV; Wood"]
[null,null,"˃ 11 kV & < = 22 kV; Wood"]
[null,null,"> 22 kV & < = 66 kV; Wood"]
[null,null,"> 66 kV & < = 132 kV; Wood"]
[null,null,"> 132 kV; Wood"]
[null,null,"˂ = 1 kV; Concrete",null,"",""]
[null,null,"> 1 kV & < = 11 kV; Concrete",null,"",""]
[null,null,"˃ 11 kV & < = 22 kV; Concrete",null,""]
[null,null,"> 22 kV & < = 66 kV; Concrete",null,"",""]
[null,null,"> 66 kV & < = 132 kV; Concrete",null,"",""]
[null,null,"> 132 kV; Concrete",null,null,""]
[null,null,"˂ = 1 kV; Steel"]
[null,null,"> 1 kV & < = 11 kV; Steel",null,""]
[null,null,"˃ 11 kV & < = 22 kV; Steel",null,"",""]
[null,null,"> 22 kV & < = 66 kV; Steel",null,"",""]
[null,null,"> 66 kV & < = 132 kV; Steel",null,"",""]
[null,null,"> 132 kV; Steel",null,"",""]
[null,null,"Other",null,"",""]
[null,"POLE TOP STRUCTURES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,6750082.6234143162,7860,3516]
[null,null,"> 1 kV & < = 11 kV",null,7154441.8571619038,3087,1293]
[null,null,"˃ 11 kV & < = 22 kV",null,3075153.32186316,1275,423]
[null,null,"> 22 kV & < = 66 kV",null,2790832.3222848279,485,57]
[null,null,"> 66 kV & < = 132 kV",null,15429.614359154375,4,0]
[null,null,"> 132 kV",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",null,2109991.0918505834,30.999999999999527,1324]
[null,null,"> 1 kV & < = 11 kV",null,1994043.3182483204,21.049999999999944,340]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",null,437634.53487722483,2.0400000000000009,90]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase",null,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase",null,0,0,0]
[null,null,"> 22 kV & < = 66 kV",null,264064.38076156814,9.0399999999999991,2]
[null,null,"> 66 kV & < = 132 kV",null,0,0,0]
[null,null,"> 132 kV",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",null,5648854.4487387966,7.3699999999998917,716]
[null,null,"> 1 kV & < = 11 kV",null,4092229.0732571185,1.7800000000000014,172]
[null,null,"> 11 kV & < = 22 kV",null,77006.599557767127,0.05,5]
[null,null,"> 22 kV & < = 33 kV",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV",null,0,0,0]
[null,null,">  132 kV",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",null,5484412.1911070487,10940.87,7087.96]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",null,0,0,0]
[null,null,"˂ = 11 kV ; Residential ; Complex Type",null,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type",null,677848.69777727558,1352.13,876.04]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type",null,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  ",null,0,0,0]
[null,null,"> 132 kV ; Commercial & Industrial  ",null,0,0,0]
[null,null,"> 132 kV ; Subdivision  ",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,2688973.8329477613,174,78]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,237043.4514556104,8,3]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,906828.47978485015,60,23]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,628777.72018504841,46,9]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",null,19959.367004876927,2,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",null,653853.1732474732,23,6]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",null,200751.97001040174,6,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",null,790818.94511839701,5,2]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA",null,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  FUSE",null,0,0,0]
[null,null,"˂ = 11 kV  ; Switch",null,193263.66183300386,"",""]
[null,null,"˂ = 11 kV ;  Circuit Breaker",null,5975486.3814337878,15,1]
[null,null,"> 11 kV & < = 22 kV  ; Switch",null,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Switch",null,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",null,289728.35079833964,2,""]
[null,null,"> 33 kV & < = 66 kV ; Switch",null,337169.18587280257,6,""]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",null,115984.66857367862,2,""]
[null,null,"> 66 kV & < = 132 kV ; Switch",null,0,0,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",null,0,0,0]
[null,null,"> 132 kV ; Switch",null,0,0,0]
[null,null,"> 132 kV ; Circuit Breaker",null,0,0,0]
[null,null,"Other",null,0,0,0]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road",null,null,"",""]
[null,null,"Luminaires ;  Minor Road",null,null,"",""]
[null,null,"Brackets ; Major Road",null,null,"",""]
[null,null,"Brackets ; Minor Road",null,null,"",""]
[null,null,"Lamps ; Major Road",null,null,"",""]
[null,null,"Lamps ; Minor Road",null,null,"",""]
[null,null,"Poles / Columns ; Major Road",null,null,"",""]
[null,null,"Poles / Columns ; Minor Road",null,null,"",""]
[null,null,"Other"]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",null,3472721.5096337874,90,47]
[null,null,"Local Network Wiring Assets",null,null,"",""]
[null,null,"Communications Network Assets",null,3425504.8764945231,27,6]
[null,null,"Master Station Assets",null,null,"",""]
[null,null,"Communications Site Infrastructure",null,7187.5379123650655,"",""]
[null,null,"Communications Linear Assets",null,263269.05991800188,0.71,0.71]
[null,null,"AFLC",null,0]
[null,null,"Other",null,0]
[null,"OTHER BY: \nDNSP DEFINED","˂ = 1 kV; stobie pole",null,7574689.6411375683,1074,143]
[null,null,"> 1 kV & < = 11 kV; stobie pole",null,7972636.4584800052,677,197]
[null,null,"˃ 11 kV & < = 22 kV; stobie pole",null,2376845.0884873085,282,49]
[null,null,"> 22 kV & < = 66 kV; stobie pole",null,1449265.5846122198,36,1]
[null,null,"> 66 kV & < = 132 kV; stobie pole",null,0,0,0]
[null,null,"> 132 kV; stobie pole",null,0,0,0]
[null,null,"Pole REFURBISHED; STOBIE Pole",null,4965358.1458824445,4102,0]
[null,null,"Pole Mounted ;> = 22 kV & < = 33 kV ;  < = 60kVA",null,94108.197487166442,10,1]
[null,null,"Pole Mounted ;> = 22 kV & < = 33 kV ; > 60 KVA AND < = 600 KVA ",null,205045.99437047535,8,6]
[null,null,"Kiosk Mounted; > = 22 kV & < = 33 kV ; ",null,12700.166679483598,1,0]
[null,null,"Recloser ;SWITCHGEAR",null,1304554.0859533544,161,61]
[null,null,"Sectionalizer ;SWITCHGEAR",null,78491.926870018506,18,19]
[null,null,">= 11 kV & < ≈ 22 kV  ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR",null,3073540.8303051605,73,8]
[null,null,"> 22 kV & < ≈ 33 kV  ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR",null,0,0,0]
[null,null,"˂ = 11 kV ;  Circuit Breaker REFURBISHED",null,1010842.4563113519,85,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker REFURBISHED",null,125839.99038143017,2,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker REFURBISHED",null,10052.864829755985,1,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA REFURBISHED",null,265158.55319369456,4,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA REFURBISHED",null,96030.178748322709,1,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA REFURBISHED",null,25883.795223973997,1,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase ; REFURBISHED",null,12440.146787941945,1,0]
[null,null,"Pipework Bus Substation Replacements",null,972804.53408983606,1,0]
[null,null,"OTHER - Non Category Substation asset replacement/refurbishment",null,5349667.8736578654,96,4]
[null,null,null,null,"","",""]
[]
[]
[null,"2.2.2 - SELECTED ASSET CHARACTERISTICS"]
[null,null,null,null,"ASSET VOLUMES CURRENTLY IN COMMISSION","ASSET REPLACEMENTS\n(0's)"]
[null,"ASSET GROUP","METRIC","UNITS",{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"TOTAL POLES BY: \nFEEDER TYPE","Total CBD poles","Number",326,27]
[null,null,"Total urban poles","Number",257609,881]
[null,null,"Total rural long poles","Number",372537,699]
[null,null,"Total rural short poles","Number",114668,462]
[null,"OVERHEAD CONDUCTORS BY:\nCONDUCTOR LENGTH BY FEEDER TYPE","Conductors CBD","KM",55.906383597422305,0.18]
[null,null,"Conductors urban","KM",51841.883560372698,20.449999999999712]
[null,null,"Conductors rural long","KM",82569.319385603347,27.439999999999994]
[null,null,"Conductors rural short","KM",29457.571982628724,15.059999999999995]
[null,"OVERHEAD CONDUCTORS BY: \nCONDUCTOR LENGTH MATERIAL TYPE","OH conductor LV ABC","KM",7662.0307479855992,0]
[null,null,"OH conductor steel","KM",39148.986741762827,6.2500000000000027]
[null,null,"OH conductor ACSR","KM",36619.527044889321,28.589999999999989]
[null,null,"OH conductor AAAC","KM",5860.1782360391344,0]
[null,null,"OH conductor AAC","KM",31945.088945598793,14.189999999999866]
[null,null,"OH conductor HDBC","KM",42688.869595926524,14.099999999999886]
[null,null,"Other","KM",0,0]
[null,"UNDERGROUND CABLES BY: \nCABLE LENGTH BY FEEDER TYPE","Cable CBD","KM",267.27997803272649,0.14000000000000001]
[null,null,"Cable urban","KM",10951.877546109476,7.3399999999999208]
[null,null,"Cable rural long","KM",3150.7427014690415,0.81000000000000039]
[null,null,"Cable rural short","KM",3384.0997743887583,0.91000000000000036]
[null,"TRANSFORMERS BY: \nTOTAL MVA","Total MVA replaced","MVA",40.256999999999998,0]
[null,null,"Total MVA disposed of","MVA",9.827,0]

{"sheet":"2.3(a) Augex","index":6,"n_rows":129,"n_cols":34,"rows_kept":129,"cut":false,"hidden":false,"merged":[[6,1,6,3],[11,21,11,22],[10,11,10,22],[12,17,12,19],[72,11,72,13],[72,14,72,16],[71,1,71,10],[72,1,73,1],[72,2,73,2],[72,3,73,3],[72,4,73,4],[72,6,73,6],[11,3,12,3],[11,4,12,4],[11,5,12,5],[11,14,11,15],[73,7,73,10],[72,7,72,10],[71,11,71,22],[72,17,72,19],[72,21,72,22],[12,30,12,31],[71,23,71,24],[71,25,73,25],[71,26,73,26],[71,30,71,31],[73,23,73,24],[73,27,73,29],[73,30,73,31],[71,29,72,29],[71,27,71,28],[11,6,12,6],[11,16,11,19],[12,23,12,24],[10,30,10,31],[10,23,10,24],[10,25,12,25],[10,26,12,26],[10,27,10,28],[10,29,11,29],[11,7,11,8],[11,9,11,10],[11,11,11,13],[10,1,10,10],[11,1,12,1],[11,2,12,2],[12,27,12,29]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.3 AUGEX PROJECT DATA"]
[]
[]
[null,"There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped.  See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS. "]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTY CONTRACTS","LAND AND EASEMENTS"]
[null,"SUBSTATION ID","SUBSTATION TYPE\n(drop down)","PROJECT ID","PROJECT TYPE\n(drop down)","PROJECT TRIGGER\n(drop down)","VOLTAGE (KV)","SUBSTATION RATING\nNORMAL CYCLIC\n(MVA)",null,"SUBSTATION RATING\nN-1 EMERGENCY\n(MVA)",null,"TRANSFORMERS",null,null,"SWITCHGEAR",null,"CAPACITORS",null,null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"PRE","POST","PRE","POST","UNITS ADDED ","MVA ADDED","EXPENDITURE ($0's)","UNITS ADDED ","EXPENDITURE ($0's)","MVAR ADDED","EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N14,P14,R14,U14,W14,X14,Y14)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N46,P46,R46,U46,W46,X46,Y46)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,30813844.910057694]
[]
[]
[null,"AUG232_1","AUG232_2","AUG232_3","AUG232_4","AUG232_5","AUG232_6","ED_AUG232_00001","ED_AUG232_00002","ED_AUG232_00003","ED_AUG232_00004","ED_AUG232_00005","ED_AUG232_00006","ED_AUG232_00007","ED_AUG232_00008","ED_AUG232_00009","ED_AUG232_00010","ED_AUG232_00011","ED_AUG232_00012","ED_AUG232_00013","ED_AUG232_00014","ED_AUG232_00015","ED_AUG232_00016","ED_AUG232_00017","ED_AUG232_00018","ED_AUG232_00019","ED_AUG232_00020","ED_AUG232_00021"]
[null,"2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS."]
[null,"PROJECT DESCRIPTION AND CHANGES",null,null,null,null,null,null,null,null,null,"PLANT AND EQUIPMENT EXPENDITURE AND VOLUME",null,null,null,null,null,null,null,null,null,null,null,"OTHER EXPENDITURE",null,"TOTAL DIRECT EXPENDITURE ($0's)","YEARS INCURRED","ALL RELATED PARTY CONTRACTS",null,"ALL NON RELATED PARTY CONTRACTS","LAND AND EASEMENTS"]
[null,"LINE ID","PROJECT ID","PROJECT TYPE","PROJECT TRIGGER",null,"VOLTAGE (KV)","ROUTE LINE LENGTH ADDED",null,null,null,"POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS)",null,null,"OVERHEAD LINES",null,null,"UNDERGROUND CABLES",null,null,"OTHER PLANT ITEM","INSTALLATION (LABOUR)",null,"CIVIL WORKS","OTHER DIRECT",null,null,"RELATED PARTY MARGINS","TOTAL",null,"LAND PURCHASE","EASEMENTS"]
[null,null,null,null,null,null,null,"KM ADDED",null,null,null,"POLES/TOWERS ADDED","POLES/TOWERS UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","CIRCUIT KM ADDED","CIRCUIT KM UPGRADED","EXPENDITURE ($0's)","EXPENDITURE ($0's)","VOLUME","EXPENDITURE ($0's)","EXPENDITURE ($0's)",null,null,null,"EXPENDITURE ($0's)",null,null,"EXPENDITURE ($0's)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N75,Q75,T75,U75,W75,X75,Y75)","v":0},null,null,null,null,null,null,null,"New line on new route - single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"New line on new route - other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line rebuild over existing route - single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line rebuild over existing route - dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Single circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Dual circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Reconductor - Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - raising/retensoring"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - voltage upgrade"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Line upgrade - capacity"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"String spare circuit"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,"Other"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(N107,Q107,T107,U107,W107,X107,Y107)","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0]
[null,null,"Non material projects - [actual]",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1793508.2307996314]

{"sheet":"2.3(b) Augex","index":7,"n_rows":46,"n_cols":5,"rows_kept":46,"cut":false,"hidden":false,"merged":[[10,1,11,1],[21,1,22,1],[35,1,36,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.3 AUGEX  DATA"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS"]
[null,"NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS."]
[null,"DESCRIPTOR METRICS"]
[null,"PROJECT TYPE",null,"UNITS ADDED\n(0's)","UNITS UPGRADED\n(0's)"]
[null,null,"UNITS",{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"HV Feeder Augmentations - Overhead Lines","Circuit line length in km",null,0.31]
[null,"HV Feeder Augmentations - Underground Cables","Circuit line length in km",null,1.1000000000000001]
[null,"LV Feeder Augmentations - Overhead Lines","Circuit line length in km",0.28199999999999997,1.0549999999999999]
[null,"LV Feeder Augmentations - Underground Cables","Circuit line length in km",0.04,0]
[null,"Distribution Substation Augmentations - Pole Mounted","Number",31,100]
[null,"Distribution Substation Augmentations - Ground Mounted","Number",1,10]
[null,"Distribution Substation Augmentations - Indoor","Number",0,0]
[]
[null,"COST METRICS"]
[null,"TOTAL DIRECT EXPENDITURE - Project Type",null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"HV Feeder Augmentations - Overhead Lines",null,145370.87828978623]
[null,"HV Feeder Augmentations - Underground Cables",null,519858.9017102138]
[null,"HV Feeder Non-Material Projects",null,17959797.728205405]
[null,"LV Feeder Augmentations - Overhead Lines",null,271253.65720496897]
[null,"LV Feeder Augmentations - Underground Cables",null,7164.3527950310572]
[null,"LV Feeder Non-Material Projects",null,539719.67179458938]
[null,"Distribution Substation Augmentations - Pole Mounted",null,1817294.9799999993]
[null,"Distribution Substation Augmentations - Ground Mounted",null,580259.19999999995]
[null,"Distribution Substation Augmentations - Indoor",null,0]
[]
[]
[null,"2.3.4 - AUGEX DATA - TOTAL EXPENDITURE"]
[null,"AUGMENTATION CAPEX (As incurred)",null,"EXPENDITURE\n ($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Subtransmission Substations, Switching Stations, Zone Substations",null,32606408.42377444]
[null,"Subtransmission Lines",null,2374521.5431233179]
[null,"HV Feeders",null,20027357.777305242]
[null,"HV Feeders - Land Purchases and Easements",null,0]
[null,"Distribution Substations",null,2582136.9462200985]
[null,"Distribution Substations - Land Purchases And Easements",null,0]
[null,"LV Feeders",null,881124.41957690008]
[null,"LV Feeders - Land Purchases And Easements",null,0]
[null,"Other Assets",null,1605923.7800000003]

{"sheet":"2.5 Connections","index":8,"n_rows":73,"n_cols":5,"rows_kept":73,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.5 CONNECTIONS"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.5.1 - DESCRIPTOR METRICS"]
[null,"<<<GROUP-ROW>>>"]
[]
[null,null,null,null,"VOLUMES AND EXPENDITURE"]
[null,"CONNECTION SUBCATEGORY","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2016-17"}]
[null,"RESIDENTIAL","Underground connections","0's",9818]
[null,null,"Overhead connections","0's",331]
[null,null,"Distribution substation installed","MVA added",7.9009999999999998]
[null,null,"Distribution substations installed","0's",154]
[null,null,"Distribution substation installed","total spend $0s",3122082.2672916944]
[null,null,"Augmentation HV","net circuit km added",6.1230000000000002]
[null,null,"Augmentation HV","total spend $0s",874563.79611861368]
[null,null,"Augmentation LV","net circuit km added",5.742]
[null,null,"Augmentation LV","total spend $0s",942763.70187397557]
[null,null,"Mean days to connect residential customer with LV single phase connection","0's",22]
[null,null,"Volume of GSL breaches for residential customers","0's",238]
[null,null,"Volume of customer complaints relating to connection services","0's",103]
[null,null,"GSL payments","$0s",71930]
[null,"COMMERCIAL/INDUSTRIAL","Underground connections","0's",834]
[null,null,"Overhead connections","0's",168]
[null,null,"Distribution substation installed","MVA added",129.63200000000001]
[null,null,"Distribution substations installed","0's",341]
[null,null,"Distribution substation installed","total spend $0s",15188939.531337537]
[null,null,"Augmentation HV","net circuit km added",43.67]
[null,null,"Augmentation HV","total spend $0s",7821692.5655265758]
[null,null,"Augmentation LV","net circuit km added",5.3310000000000004]
[null,null,"Augmentation LV","total spend $0s",1717679.952626735]
[null,"SUBDIVISION","Underground connections","0's",283]
[null,null,"Overhead connections","0's",14]
[null,null,"Distribution substation installed","MVA added",29.257999999999999]
[null,null,"Distribution substations installed","0's",112]
[null,null,"Distribution substation installed","total spend $0s",4680417.5071406551]
[null,null,"Augmentation HV","net circuit km added",11.44]
[null,null,"Augmentation HV","total spend $0s",1915186.4620738584]
[null,null,"Augmentation LV","net circuit km added",16.998999999999999]
[null,null,"Augmentation LV","total spend $0s",4439337.756971526]
[null,null,"Cost per lot ($)","$0s",2928.2171915820018]
[null,"EMBEDDED GENERATION","Underground connections","0's",8743]
[null,null,"Overhead connections","0's",1085]
[null,null,"Distribution substation installed","MVA added",3.43]
[null,null,"Distribution substations installed","0's",13]
[null,null,"Distribution substation installed","total spend $0s",511481.65153001656]
[null,null,"Augmentation HV","net circuit km added",7.0000000000000007E-2]
[null,null,"Augmentation HV","total spend $0s",12536.772825014546]
[null,null,"Augmentation LV","net circuit km added",0.06]
[null,null,"Augmentation LV","total spend $0s",19332.357373401632]
[]
[]
[]
[null,"2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION"]
[null,null,null,"EXPENDITURE\n($0's)","VOLUMES\n(0's)"]
[null,"CONNECTION SUBCATEGORY","CONNECTION CLASSIFICATION",{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"RESIDENTIAL","Simple connection LV",9884116.5079372544,9915]
[null,null,"Complex connection LV",3299994.3267888832,234]
[null,null,"Complex connection HV",0,0]
[null,"COMMERCIAL/INDUSTRIAL","Simple connection LV",1307694.8489757881,674]
[null,null,"Complex connection HV (customer connected at LV, minor HV works)",17391929.738684744,328]
[null,null,"Complex connection HV (customer connected at LV, upstream asset works)",7927225.425466598,57]
[null,null,"Complex connection HV (customer connected at HV)",902939.7505859934,12]
[null,null,"Complex connection sub-transmission"]
[null,"SUBDIVISION","Complex connection LV",1935652.9355607673,150]
[null,null,"Complex connection HV (no upstream asset works)",6306975.8621580284,100]
[null,null,"Complex connection HV (with upstream asset works)",4498449.8033446604,47]
[null,"EMBEDDED GENERATION","Simple connection LV",1637932.780016819,9828]
[null,null,"Complex connection HV (small capacity)",465513.3218318352,84]
[null,null,"Complex connection HV (large capacity)"]

{"sheet":"2.6 Non-network","index":9,"n_rows":94,"n_cols":6,"rows_kept":94,"cut":false,"hidden":false,"merged":[[89,2,93,2],[69,2,73,2],[74,2,78,2],[79,2,83,2],[84,2,88,2],[58,5,59,5],[61,2,61,4],[62,2,62,4],[63,2,63,4],[5,1,5,2],[60,2,60,4],[9,2,9,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.6 NON NETWORK EXPENDITURE"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.6.1 - NON-NETWORK EXPENDITURE"]
[null,null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","ASSET CATEGORY",null,null,{"$f":"CRY","v":"2016-17"}]
[null,"OPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,1447800.6040804104]
[null,null,"Recurrent expenditure",null,null,16351152.3481174]
[null,null,"Non-recurrent expenditure",null,null,330618.68632618838]
[null,"MOTOR VEHICLES","Car",null,null,562751.97591124068]
[null,null,"Light commercial vehicle",null,null,1960251.1638097453]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,4460624.4937466243]
[null,null,"Heavy commercial vehicle",null,null,1803498.421425676]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,3778759.4274192266]
[null,"OTHER","Other expenditure",null,null,{"$f":"SUM(dms_020601_05_opex_Values)","v":5590479.565566143}]
[null,"OTHER - DNSP nominated","TEC Vehicles",null,null,283423.39037738444]
[null,null,"Cranes",null,null,1168588.1386603164]
[null,null,"Other Commercial Vehicles",null,null,1362208.1265284421]
[null,null,"Network Telephony (A80)",null,null,2776259.91]
[null,null,"ADMS",null,null,0]
[null,null,"V&V Rollout",null,null,0]
[null,null,"Other Network Strategic",null,null,0]
[null,null,"Non-Network Telecommunications",null,null,0]
[null,null,"Non-Network Other Plant and Tools",null,null,0]
[]
[]
[null,"CAPEX"]
[null,"IT & COMMUNICATIONS","Client device expenditure",null,null,4279467.5800000411]
[null,null,"Recurrent expenditure",null,null,27787605.709999703]
[null,null,"Non-recurrent expenditure",null,null,22699334.110000774]
[null,"MOTOR VEHICLES","Car",null,null,180213.84999999998]
[null,null,"Light commercial vehicle",null,null,3867685.55]
[null,null,"Elevated work platform (LCV)  ",null,null,0]
[null,null,"Elevated work platform (HCV)",null,null,7025729.120000001]
[null,null,"Heavy commercial vehicle",null,null,529069.26]
[null,"BUILDINGS AND PROPERTY","Total buildings and property expenditure",null,null,6839633.9200000875]
[null,"OTHER","Other expenditure",null,null,{"$f":"SUM(F44:F52)","v":13030612.43}]
[null,"OTHER - DNSP nominated",{"$f":"IF(ISBLANK(C22),\"\",C22)","v":"TEC Vehicles"},null,null,1635073.49]
[null,null,{"$f":"IF(ISBLANK(C23),\"\",C23)","v":"Cranes"},null,null,533887.52]
[null,null,"Other Commercial Vehicles",null,null,337865.65]
[null,null,"Network Telephony (A80)",null,null,0]
[null,null,"ADMS",null,null,968968.49]
[null,null,"V&V Rollout",null,null,1635844.66]
[null,null,"Other Network Strategic",null,null,4118118.7900000005]
[null,null,"Non-Network Telecommunications",null,null,1032682]
[null,null,"Non-Network Other Plant and Tools",null,null,2768171.83]
[null,null,""]
[null,null,""]
[]
[]
[]
[null,"2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE"]
[null,null,null,null,null,"VOLUMES\n(0's)"]
[]
[null,"NON-NETWORK CATEGORY","DESCRIPTOR METRIC",null,null,{"$f":"CRY","v":"2016-17"}]
[null,"IT & COMMUNICATIONS","Employee numbers",null,null,1636]
[null,null,"User numbers",null,null,1583.9785000000002]
[null,null,"Number of devices",null,null,5345.7920000000004]
[]
[]
[null,"2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES"]
[null,null,null,null,null,"VOLUMES / %"]
[null,"NON-NETWORK CATEGORY","ASSET CATEGORY","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2016-17"}]
[null,"MOTOR VEHICLES","CAR","Average kilometres travelled","0's",10461.472]
[null,null,null,"Number purchased","0's",18]
[null,null,null,"Number leased","0's",1]
[null,null,null,"Number in fleet","0's",59]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.81830000000000003]
[null,null,"LIGHT COMMERCIAL VEHICLE","Average kilometres travelled","0's",19921.021000000001]
[null,null,null,"Number purchased","0's",84]
[null,null,null,"Number leased","0's",22]
[null,null,null,"Number in fleet","0's",431]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.9103]
[null,null,"ELEVATED WORK PLATFORM (LCV) ","Average kilometres travelled","0's",0]
[null,null,null,"Number purchased","0's",0]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",0]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0]
[null,null,"ELEVATED WORK PLATFORM (HCV)","Average kilometres travelled","0's",14139.467000000001]
[null,null,null,"Number purchased","0's",13]
[null,null,null,"Number leased","0's",0]
[null,null,null,"Number in fleet","0's",109]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.89780000000000004]
[null,null,"HEAVY COMMERCIAL VEHICLE ","Average kilometres travelled","0's",8779.6970000000001]
[null,null,null,"Number purchased","0's",4]
[null,null,null,"Number leased","0's",2]
[null,null,null,"Number in fleet","0's",63]
[null,null,null,"Proportion of total fleet expenditure allocated as regulatory expenditure","(per cent)",0.81520000000000004]

{"sheet":"2.7 Vegetation management","index":10,"n_rows":410,"n_cols":5,"rows_kept":410,"cut":false,"hidden":false,"merged":[[405,1,405,3],[5,1,5,2],[7,1,7,2],[12,4,13,4],[124,4,125,4],[14,1,19,1],[20,1,25,1],[26,1,31,1],[32,1,37,1],[38,1,43,1],[44,1,49,1],[50,1,55,1],[56,1,61,1],[62,1,67,1],[68,1,73,1],[74,1,79,1],[80,1,85,1],[86,1,91,1],[92,1,97,1],[98,1,103,1],[104,1,109,1],[110,1,115,1],[116,1,121,1],[126,1,131,1],[132,1,137,1],[138,1,143,1],[144,1,149,1],[150,1,155,1],[156,1,161,1],[162,1,167,1],[168,1,173,1],[174,1,179,1],[180,1,185,1],[186,1,191,1],[192,1,197,1],[198,1,203,1],[240,1,248,1],[249,1,257,1],[258,1,266,1],[204,1,209,1],[210,1,215,1],[216,1,221,1],[222,1,227,1],[228,1,233,1],[267,1,275,1],[276,1,284,1],[285,1,293,1],[294,1,302,1],[303,1,311,1],[312,1,320,1],[321,1,329,1],[330,1,338,1],[339,1,347,1],[348,1,356,1],[357,1,365,1],[366,1,374,1],[375,1,383,1],[384,1,392,1],[393,1,401,1]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.7 VEGETATION MANAGEMENT"]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"Please enter a description for each Zone in table 2.7.1 - Urban and CBD.  The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2."]
[]
[]
["`","2.7.1 - DESCRIPTOR METRICS BY ZONE"]
[null,"URBAN AND CBD"]
[null,null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"ZONES","ASSET","UNITS"]
[null,"ZONE 1","Route line length within zone","km"]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km"]
[null,null,"Length of vegetation corridors","km"]
[null,null,"Average number of trees per maintenance span","0's"]
[null,null,"Average frequency of cutting cycle","years"]
[null,"ZONE 2","Route line length within zone","km"]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 3","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 4","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 5","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 6","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 7","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 8","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 9","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 10","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 11","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 12","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 13","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 14","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 15","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 16","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 17","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,"ZONE 18","Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[]
[null,"RURAL"]
[null,null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"ZONES","ASSET","UNITS"]
[null,{"$f":"B15","v":"ZONE 1"},"Route line length within zone","km"]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km"]
[null,null,"Length of vegetation corridors","km"]
[null,null,"Average number of trees per maintenance span","0's"]
[null,null,"Average frequency of cutting cycle","years"]
[null,{"$f":"B21","v":"ZONE 2"},"Route line length within zone","km"]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B27","v":"ZONE 3"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's"]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B33","v":"ZONE 4"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B39","v":"ZONE 5"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B45","v":"ZONE 6"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B51","v":"ZONE 7"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B57","v":"ZONE 8"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B63","v":"ZONE 9"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B69","v":"ZONE 10"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B75","v":"ZONE 11"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B81","v":"ZONE 12"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B87","v":"ZONE 13"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B93","v":"ZONE 14"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B99","v":"ZONE 15"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B105","v":"ZONE 16"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B111","v":"ZONE 17"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[null,{"$f":"B117","v":"ZONE 18"},"Route line length within zone","km",""]
[null,null,"Number of maintenance spans","0's",""]
[null,null,"Total length of maintenance spans","km",""]
[null,null,"Length of vegetation corridors","km",""]
[null,null,"Average number of trees per maintenance span","0's",""]
[null,null,"Average frequency of cutting cycle","years",""]
[]
[]
[]
[null,"2.7.2 - EXPENDITURE METRICS BY ZONE"]
[null,null,null,null,"EXPENDITURE\n($0's)"]
[null,"ZONES","SERVICE SUBCATEGORY",null,{"$f":"CRY","v":"2016-17"}]
[null,{"$f":"B15","v":"ZONE 1"},"Tree trimming (excluding hazard trees) "]
[null,null,"Hazard tree cutting "]
[null,null,"Ground clearance "]
[null,null,"Vegetation corridor clearance "]
[null,null,"Inspection "]
[null,null,"Audit "]
[null,null,"Contractor liaison expenditure "]
[null,null,"Tree replacement program costs "]
[null,null,"Other vegetation management costs not specified in sheet "]
[null,{"$f":"B21","v":"ZONE 2"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B27","v":"ZONE 3"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B33","v":"ZONE 4"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B39","v":"ZONE 5"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B45","v":"ZONE 6"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B51","v":"ZONE 7"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B57","v":"ZONE 8"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B63","v":"ZONE 9"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B69","v":"ZONE 10"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B75","v":"ZONE 11"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B81","v":"ZONE 12"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B87","v":"ZONE 13"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B93","v":"ZONE 14"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B99","v":"ZONE 15"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B105","v":"ZONE 16"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B111","v":"ZONE 17"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[null,{"$f":"B117","v":"ZONE 18"},"Tree trimming (excluding hazard trees) ",null,""]
[null,null,"Hazard tree cutting ",null,""]
[null,null,"Ground clearance ",null,""]
[null,null,"Vegetation corridor clearance ",null,""]
[null,null,"Inspection ",null,""]
[null,null,"Audit ",null,""]
[null,null,"Contractor liaison expenditure ",null,""]
[null,null,"Tree replacement program costs ",null,""]
[null,null,"Other vegetation management costs not specified in sheet ",null,""]
[]
[null,"2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS"]
[null,null,null,null,"VOLUMES\n(0's)"]
[null,"DESCRIPTOR METRIC",null,null,{"$f":"CRY","v":"2016-17"}]
[null,"Number of fire starts caused by vegetation grow-ins (NSP responsibility)",null,null,1]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility)",null,null,2]
[null,"Number of fire starts caused by vegetation grow-ins (other party responsibility)",null,null,0]
[null,"Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility)",null,null,0]

{"sheet":"2.8 Maintenance","index":11,"n_rows":85,"n_cols":10,"rows_kept":85,"cut":false,"hidden":false,"merged":[[8,7,9,7],[8,8,10,8],[8,9,10,9],[68,1,69,1],[5,1,5,2],[28,1,29,1],[48,5,48,6],[8,5,8,6]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.8 MAINTENANCE"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"ASSET QUANTITY\n(0's)",null,"AVERAGE AGE OF ASSET GROUP ","INSPECTION \nCYCLE \n(YEARS)","MAINTENANCE \nCYCLE \n(YEARS)"]
[null,null,null,null,null," AT YEAR END","INSPECTED / MAINTAINED"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units",{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",745140,88616,46.85,5,0]
[null,null,"Service lines","Number of customers","Number",776103,0,28.7,10,0]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",745140,88616,46.85,5,0]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",71222,49876,0,5,0]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",17581,555.71,38.5,0,0]
[null,null,"33 KV and above","Length (KM)","KM",172,16.57,29.8,0.5,0]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",266,572.28000000000009,29.8,0,0]
[null,null,"Non-CBD","Length (KM)","KM",17487,null,38.4,0,0]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",77847,405,30,5,0]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",10107,4405,13.9,1,0]
[null,null,"Distribution substation - other equipment","Earth mat","Number",0,0,0,0,0]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",721,80,40.15,0,0]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",693,594,35.1,0.5,6]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",324,0,18.8,0.5,0]
[null,null,"Transformers - HV","Number of HV transformers","Number",0,0,0,0,0]
[null,null,"Zone substation - other equipment","Number",{"$f":"D27","v":"Number"},355,451,4.5999999999999996,0.5,10]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",416,1197,41.5,0.5,4.5]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",0,0,0,0,0]
[null,null,"Major roads","Number of public lights maintained","Number",0,0,0,0,0]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",340,0,9.5,0,0]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",3002,342,35,0.5,4.5]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets","<DNSP to nominate>",{"$f":"D33","v":"<DNSP to nominate>"},0,0,0,0,0]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number",5615,350,11,1.5,1.5]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",0,0,0,0,0]
[null,"Other","Substation asset inspection","No. of Sites",null,408,874,41.5,0.5,0]
[null,null,"Zone substation equipment maintenance (switchgear)","No. of CBs and disconnectors",null,5996,1323,34.4,0.5,4.5]
[null,null,"Number of signages and IDs replaced","No. of sites",null,78864,671,30,0,0]
[null,null,"Power Station Maintenance, Asset Records, Feeder Diagram Maintenance, Compliance Auditing, Asset Location Services, Customer Service Penalties","Units not quoted as various UOM",null,0,0,0,0,0]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE"]
[null,null,null,null,null,"EXPENDITURE ($0'S)"]
[null,null,null,null,null," ROUTINE MAINTENANCE ","NON-ROUTINE MAINTENANCE"]
[null,"MAINTENANCE ACTIVITY","MAINTENANCE ASSET CATEGORY","ASSET QUANTITY","Units",{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"Pole top, overhead line & service line maintenance","Pole tops and overhead lines","Number of poles","Number",7284,971132]
[null,null,"Service lines","Number of customers","Number",0,0]
[null,"Pole inspection and treatment","All poles","Number of poles","Number",5745181,0]
[null,"Overhead asset inspection","All overhead assets","Line patrolled (route KM)","KM",5727497,0]
[null,"Network underground cable maintenance: by voltage","LV - 11 to 22 KV","Length (KM)","KM",429981,517499]
[null,null,"33 KV and above","Length (KM)","KM",80287,0]
[null,"Network underground cable maintenance: by location","Cbd","Length (KM)","KM",510268,517499]
[null,null,"Non-CBD","Length (KM)","KM"]
[null,"Distribution substation equipment & property maintenance","Distribution substation transformers","Number of installed transformers","Number",8371,550049]
[null,null,"Distribution substation switchgear\n (within-substations and stand-alone switchgear)","Number of switches","Number",288857,84464]
[null,null,"Distribution substation - other equipment","Earth mat","Number",0,0]
[null,null,"Distribution substation - property","Number of distribution substation properties maintained","Number",0,139767]
[null,"Zone substation equipment maintenance","Transformers - zone substation","Number","Number",1481535,1303438]
[null,null,"Transformers - distribution","Number of distribution transformers within zone substation","Number",0,0]
[null,null,"Transformers - HV","Number of HV transformers","Number",0,0]
[null,null,"Zone substation - other equipment",{"$f":"IF(ISBLANK(D27),\"\",D27)","v":"Number"},{"$f":"IF(ISBLANK(E27),\"\",E27)","v":"Number"},675733,642354]
[null,"Zone substation property maintenance","All zone substation properties","Number of zone substation properties maintained","Number",964907,597462]
[null,"Public lighting maintenance","Minor roads","Number of public lights maintained","Number",0,0]
[null,null,"Major roads","Number of public lights maintained","Number",0,0]
[null,"SCADA & network control maintenance","SCADA & network control","Number of systems","Number",0,500344]
[null,"Protection systems maintenance","Protection systems","Number of systems","Number",813357,81874]
[null,"Subtransmission asset maintenance","Subtransmission asset maintenance\n- for DNSPs with dual function assets",{"$f":"IF(ISBLANK(D33),\"\",D33)","v":"<DNSP to nominate>"},{"$f":"IF(ISBLANK(E33),\"\",E33)","v":"<DNSP to nominate>"},0,0]
[null,"Various assets"," includes rates, electricity, communications equip, metering","Various","Number",634506,1432010]
[null,"Ground clearance - access tracks","Access tracks","Number","Number",0,0]
[null,"Other",{"$f":"IF(ISBLANK(C36),\"\",C36)","v":"Substation asset inspection"},"No. of Sites",null,940563,0]
[null,null,"Zone substation equipment maintenance (switchgear)","No. of CBs and disconnectors",null,774001,553706]
[null,null,"Number of signages and IDs replaced","No. of sites",null,0,362267]
[null,null,"Power Station Maintenance, Asset Records, Feeder Diagram Maintenance, Compliance Auditing, Asset Location Services, Customer Service Penalties","Units not quoted as various UOM",null,1096115,0]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]
[null,null,"",""]

{"sheet":"2.9 Emergency Response","index":12,"n_rows":377,"n_cols":4,"rows_kept":377,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.9 EMERGENCY RESPONSE"]
[]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"(A) TOTAL EMERGENCY RESPONSE EXPENDITURE","Total Expenditure",43002001.479999997]
[null,"(B) MAJOR EVENTS O&M EXPENDITURE"]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"(C) MAJOR EVENT DAYS O&M EXPENDITURE","2016-07-11",183246]
[null,null,"2016-07-12",473562]
[null,null,"2016-09-28",72178]
[null,null,"2016-09-29",162338]
[null,null,"2016-11-11",158511]
[null,null,"2016-12-23",68173]
[null,null,"2016-12-27",73768]
[null,null,"2016-12-28",334489]
[null,null,"2017-01-19",127454]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]

{"sheet":"2.10 Overheads","index":13,"n_rows":174,"n_cols":4,"rows_kept":174,"cut":false,"hidden":false,"merged":[[5,1,8,2],[10,1,10,2],[106,1,106,3],[152,1,152,3],[17,1,17,3],[12,1,12,2],[78,1,78,3]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.10 OVERHEADS"]
[]
[null,{"$f":"CONCATENATE(\"Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. \",dms_TradingName, \" is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If \",dms_TradingName,\" is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. \n\n\",dms_TradingName, \" is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN.\")","v":"Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. SA Power Networks is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If SA Power Networks is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. \n\nSA Power Networks is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN."},null,"Choose Response\ndrop down selection"]
[null,null,null,"Worksheet 2.10"]
[]
[]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,{"$f":"CONCATENATE(\"Instructions\nPlease enter a description for each expenditure category as currently reported under \",dms_TradingName,\"'s annual RIN.\")","v":"Instructions\nPlease enter a description for each expenditure category as currently reported under SA Power Networks's annual RIN."}]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"NETWORK OVERHEADS"]
[null,"Standard Control Services","Network management",4882331.5999999996]
[null,null,"Network planning",835522.83]
[null,null,"Network control and operational switching",10395016.93]
[null,null,"Quality and standard functions",7629800.75]
[null,null,"Other Network Overheads",2011381.41]
[null,null,"Network Telephony",4996194.04]
[null,null,"Guaranteed Service Level Payments",25515380.57]
[null,null,"Call Centre",3297340.35]
[null,null,"Full Retail Contestability",15528517.489]
[null,null,"Network Insurance",1827737.5349999999]
[null,null,"Distribution Licence Fee",2263400]
[null,null,"Substation Property Maintenance",6762167.8880000003]
[null,null,"Other Customer Services",7679470.2460000003]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","Network management",142562.29]
[null,null,"Other Customer Services",165968.17618950631]
[null,null,"Full Retail Contestability",2193106.8755999999]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total  ",2199538.31]
[null,"Unregulated Services","Total  ",11344.72]
[]
[]
[null,"CAPITALISED NETWORK OVERHEADS"]
[null,"Standard Control Services","Network management - Standard Control Services",11307921.5]
[null,null,"Network management - Alternative Control Services",324540.77]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"CORPORATE OVERHEADS"]
[null,"Standard Control Services","   CEO, Planning and Audit",4317772.6296587531]
[null,null,"Communications",1709150.5074897639]
[null,null,"Regulation and Company Secretary",4350810.4494616594]
[null,null,"Finance",9999837.2968129944]
[null,null,"HR and Training",8257553.3445694745]
[null,null,"Property",6276254.4771348601]
[null,null,"Information Systems",17834184.49868536]
[null,null,"Risk Management",8304296.6284225788]
[null,null,"Other Allocated Costs",-2054247.9547139884]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Alternative Control Services","   CEO, Planning and Audit",79005.05]
[null,null,"Communications",38357.538999999997]
[null,null,"Regulation and Company Secretary",107644.694]
[null,null,"Finance",303562.342]
[null,null,"HR and Training",128383.374]
[null,null,"Property",61567.75]
[null,null,"Information Systems",295387.14]
[null,null,"Risk Management",111266.317]
[null,null,"Other Allocated Costs",-110286.071]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,"Negotiated Services","Total",5146926.7537277751]
[null,"Unregulated Services","Total",4807205.3123692991]
[]
[null,"CAPITALISED CORPORATE OVERHEADS"]
[null,"Standard Control Services","   Other Allocated Costs - Standard Control",-9361715.3008001391]
[null,null,"Other Allocated Costs - Alternative Control",-145107.63715231529]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]
[null,null,null,""]

{"sheet":"2.10(A) Overheads","index":14,"n_rows":37,"n_cols":4,"rows_kept":37,"cut":false,"hidden":false,"merged":[[8,1,8,2],[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.10(A) OVERHEADS"]
[]
[null,"This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options."]
[]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped (and sub-grouped)  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.10.1 - NETWORK OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"OPEX"]
[null,"Standard Control Services","Total  ",""]
[null,"Alternative Control Services","Total  "]
[null,"CAPEX"]
[null,"Standard Control Services","Total  ",""]
[null,"Alternative Control Services","Total  ",""]
[null,"OTHER DISTRIBUTION SERVICES"]
[null,"Negotiated Services","Total  ",""]
[null,"Unregulated Services","Total  ",""]
[]
[]
[]
[null,"2.10.2 - CORPORATE OVERHEADS EXPENDITURE"]
[null,null,null,"EXPENDITURE\n($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"OPEX"]
[null,"Standard Control Services","Total",""]
[null,"Alternative Control Services","Total",""]
[null,"CAPEX"]
[null,"Standard Control Services","Total",""]
[null,"Alternative Control Services","Total",""]
[null,"OTHER DISTRIBUTION SERVICES"]
[null,"Negotiated Services","Total",""]
[null,"Unregulated Services","Total",""]

{"sheet":"2.11 Labour","index":15,"n_rows":55,"n_cols":7,"rows_kept":55,"cut":false,"hidden":false,"merged":[[36,1,36,2],[5,1,5,2],[11,1,11,2],[33,5,33,6],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,6,9,6],[33,3,33,4],[10,1,10,2],[35,1,35,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.11 LABOUR"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.11.1 - COST METRICS PER ANNUM"]
[null,null,null,"ASL \n(0's)","TOTAL LABOUR EXPENDITURE\n($0's)","AVERAGE PRODUCTIVE WORK HOURS \nPER ASL \n(0's)","STAND-DOWN OCCURENCES \nPER ASL \n(0's)"]
[]
[null,null,null,{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"INTERNAL LABOUR EXPENDITURE"]
[null,"CORPORATE OVERHEADS","Executive manager",23.727305584341643,8319997.4662970202,1939.8,0]
[null,null,"Senior manager",16.813583090900753,3440483.6034969999,1830.7,0]
[null,null,"Manager",18.448719639985711,2966451.8787659202,1677,0]
[null,null,"Professional",28.831472661442611,4686101.2038295101,1737.9,1.7]
[null,null,"Semi professional",110.76705273551853,15823701.6941485,1690.4,0.5]
[null,null,"Support staff",126.804460793933,15463661.331275901,1668.1,0.3]
[null,null,"Intern, junior staff, apprentice",0.89233393381309511,35573.456327235297,1635.6,0]
[null,"NETWORK OVERHEADS ","Executive manager",15.028092519205847,5051320.4327244898,1944.7,0]
[null,null,"Senior manager",28.786621230305901,5442927.1180790896,1865.1,0.3]
[null,null,"Manager",71.189687089664218,11653213.6786146,1778.4,4.8]
[null,null,"Professional",89.072346130653472,12445063.719578199,1697,0.1]
[null,null,"Semi professional",302.78614099438289,44725649.463047698,1749.4,5.2]
[null,null,"Support staff",147.38294570006667,19294758.965411998,1750.9,2.2000000000000002]
[null,null,"Intern, junior staff, apprentice",4.8574786108027475,275763.21770273498,1755.3,1.1000000000000001]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker",507.20619597221662,76653805.953862399,1998.4,81.8]
[null,null,"Skilled non electical worker",19.127220944339715,2174161.51382733,1800.7,5.0999999999999996]
[null,null,"Apprentice",75.194882993454101,5239873.1256706202,1853.9,21.1]
[null,null,"Unskilled worker",49.281653180034084,5101276.1282800902,1799.6,12.3]
[]
[]
[null,"2.11.2 - DESCRIPTOR METRICS"]
[null,null,null,"ORDINARY TIME (0's)",null,"OVERTIME (0's)"]
[null,null,null,"PER ASL","HOURLY RATE\nPER ASL","PER ASL","HOURLY RATE\nPER ASL"]
[null,null,null,{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"AVERAGE PRODUCTIVE WORK HOURS PER ASL"]
[null,"CORPORATE OVERHEADS","Executive manager",1939.8,180.7,0,0]
[null,null,"Senior manager",1829.9,111.8,0.8,145.6]
[null,null,"Manager",1657,95.7,20,113.7]
[null,null,"Professional",1704.3,93.1,33.6,105.1]
[null,null,"Semi professional",1666.3,84.3,24,94.1]
[null,null,"Support staff",1649.4,73,18.8,84.4]
[null,null,"Intern, junior staff, apprentice",1635.6,24.4,0,0]
[null,"NETWORK OVERHEADS ","Executive manager",1944.7,172.8,0,0]
[null,null,"Senior manager",1841.1,100.9,24,135]
[null,null,"Manager",1643.7,90,134.69999999999999,116.4]
[null,null,"Professional",1669.3,82,27.8,101.3]
[null,null,"Semi professional",1666.4,83.5,83,105.4]
[null,null,"Support staff",1704.9,74.5,46,88.2]
[null,null,"Intern, junior staff, apprentice",1719.9,32.299999999999997,35.4,27.5]
[null,"TOTAL DIRECT NETWORK LABOUR ","Skilled electrical worker",1646.9,68.900000000000006,351.5,106.8]
[null,null,"Skilled non electical worker",1664.7,61.8,136,79.8]
[null,null,"Apprentice",1669.4,36.4,184.5,48.1]
[null,null,"Unskilled worker",1696.9,56.7,102.8,71.900000000000006]

{"sheet":"2.12 Input tables","index":16,"n_rows":82,"n_cols":9,"rows_kept":82,"cut":false,"hidden":false,"merged":[[9,3,9,8],[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"2.12 INPUT TABLES"]
[]
[null,"There is ONE table on this worksheet. It has been sub-grouped  for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"2.12.1 - INPUT TABLES"]
[null,null,null,"DIRECT MATERIAL EXPENDITURE","DIRECT LABOUR EXPENDITURE","CONTRACT EXPENDITURE","OTHER EXPENDITURE","RELATED PARTY CONTRACT EXPENDITURE","RELATED PARTY CONTRACT MARGIN\nEXPENDITURE"]
[null,null,null,"EXPENDITURE ($0's)"]
[null,null,null,{"$f":"CRY","v":"2016-17"},"2016-17","2016-17","2016-17","2016-17","2016-17"]
[null,"VEGETATION MANAGEMENT",{"$f":"'2.7 Vegetation management'!B15","v":"ZONE 1"}]
[null,null,{"$f":"'2.7 Vegetation management'!B21","v":"ZONE 2"}]
[null,null,{"$f":"'2.7 Vegetation management'!B27","v":"ZONE 3"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B33","v":"ZONE 4"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B39","v":"ZONE 5"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B45","v":"ZONE 6"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B51","v":"ZONE 7"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B57","v":"ZONE 8"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B63","v":"ZONE 9"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B69","v":"ZONE 10"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B75","v":"ZONE 11"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B81","v":"ZONE 12"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B87","v":"ZONE 13"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B93","v":"ZONE 14"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B99","v":"ZONE 15"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B105","v":"ZONE 16"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B111","v":"ZONE 17"},"","","","","",""]
[null,null,{"$f":"'2.7 Vegetation management'!B117","v":"ZONE 18"},"","","","","",""]
[null,"ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",0,5220.8663382117466,1005.8550811234013,1057.428580664852,"",""]
[null,null,"Pole inspection and treatment",154.38999999999999,123589.13999999997,5620718.5000000028,719.36,"",""]
[null,null,"Overhead asset inspection",16200.34538945637,1524301.9383443035,4174997.3424253976,11997.823840845591,"",""]
[null,null,"Network underground cable maintenance",21581.475473014591,263967.80484734784,214734.59435932973,9984.2653203077516,null,""]
[null,null,"Distribution substation equipment & property maintenance",770.67909903041891,288443.45331193937,7101.0413058866261,912.3462831426948,"",""]
[null,null,"Zone substation equipment maintenance",80097.079222314351,1660062.4330022712,303093.10127277375,114014.82650264044,"",""]
[null,null,"Zone substation property maintenance",12277.131012055057,166721.12936886077,782428.65745043394,3479.7521686515597,"",""]
[null,null,"Public lighting maintenance",0,0,0,0,"",""]
[null,null,"Scada & network control maintenance",0,0,0,0,"",""]
[null,null,"Protection systems maintenance",3867.5278192318151,699512.51001656498,47581.374088947923,62395.378075255408,"",""]
[null,null,"Subtransmission asset maintenance - for dnsps with dual function assets",0,0,0,0,"",""]
[null,null,"Other",83561.216503343458,2118235.3890402094,1172633.8954695147,70754.668986933175,"",""]
[null,"NON-ROUTINE MAINTENANCE","Pole top, overhead line & service line maintenance",52146.125292211436,629598.86345774587,197407.73410653343,91979.027143508894,"",""]
[null,null,"Pole inspection and treatment",0,0,0,0,"",""]
[null,null,"Overhead asset inspection",0,0,0,0,"",""]
[null,null,"Network underground cable maintenance",38331.982528104534,304966.73966878961,136679.82658560635,37520.361217499369,"",""]
[null,null,"Distribution substation equipment & property maintenance",44181.58183414115,217913.64282635332,461728.78431236971,50455.971027135805,"",""]
[null,null,"Zone substation equipment maintenance",139141.42131240602,1493780.4106461166,192407.47082044836,120463.24722102923,"",""]
[null,null,"Zone substation property maintenance",9705.8039455913586,66600.801671302033,516771.46200302953,4384.1223800772859,"",""]
[null,null,"Public lighting maintenance",0,0,0,0,"",""]
[null,null,"SCADA & network control maintenance",24137.629772359811,292051.79901223734,170988.5543212695,13165.896894133439,"",""]
[null,null,"Protection systems maintenance",2525.8714387207569,68346.093326235845,5595.6506940597446,5406.8145409836588,"",""]
[null,null,"Subtransmission asset maintenance - for DNSP with dual function assets",0,0,0,0,"",""]
[null,null,"Other",82940.160276935261,1479245.4626621194,651026.1493200633,134770.24774088248,"",""]
[null,"OVERHEADS","Network overheads",3301851.9935591384,36535253.491180621,11619073.300199939,39910260.115026496,16391922.35,""]
[null,null,"Corporate overheads",6425433.1205779547,14583212.193283724,2716458.5480342014,26426201.363502976,352371.85,""]
[null,"AUGMENTATION","Subtransmission substations, switching stations, zone substations",7611414.3696168642,14685191.913089508,8632111.2990826387,1677690.8419854308]
[null,null,"Subtransmission lines",441840.2356129199,1297381.4934443191,521527.7610873137,113772.05297876536]
[null,null,"HV feeders",3885667.2436217787,6391500.5799703673,8895235.1814507302,854954.77226236858]
[null,null,"Distribution substations",920218.36402075784,1064667.682808724,556815.90542983706,40434.99396077951]
[null,null,"LV feeders",294750.91573283216,363305.55411880044,190006.99873849025,33060.95098677725]
[null,null,"Other assets",123908.89514981835,1217740.411772042,154512.51289087711,109761.96018726252]
[null,"CONNECTIONS","Simple and complex customer connections",14934675.166970255,32410152.064720966,8949642.381492272,1922124.2868165004,"",""]
[null,"EMERGENCY RESPONSE","Major storms",1878930.3931876218,26763309.108253382,11118534.340355791,3241227.6382028908,"",""]
[null,null,"Major event days",0,0,0,0,"",""]
[null,"PUBLIC LIGHTING","All public lighting services",0,0,0,0,"",""]
[null,"METERING","All metering services",4237501.7718931306,2996066.6315494981,4033021.313572227,520289.5529851428,"",""]
[null,"FEE-BASED SERVICES","All fee-based services",0,0,0,0,"",""]
[null,"QUOTED SERVICES","All quoted services",0,0,0,0,"",""]
[null,"REPLACEMENT","Poles",3357706.0906755901,8030182.8752531642,11464599.647415131,1486306.3052557027,"",""]
[null,null,"Pole top structures",3087814.9489938268,12239558.798381288,2654709.8615698013,1803854.9570902858,"",""]
[null,null,"Overhead conductors",565805.5682339475,3176141.0607524621,657166.44377501309,406620.25297627517,"",""]
[null,null,"Underground cables",429128.33573294315,3711083.5910488591,4988858.9880417725,689019.20673011278,"",""]
[null,null,"Service lines",283352.39679161779,4708003.4553963821,581285.29308564158,589619.74361063784,"",""]
[null,null,"Transformers",2843724.3485201602,2379094.2493957481,871478.2954125494,344564.4049630849,"",""]
[null,null,"Switchgear",4019763.4666147339,5466241.5801933426,1482041.7265408672,400172.31829120213,"",""]
[null,null,"Public lighting",null,null,null,null,"",""]
[null,null,"SCADA network control and protection systems",1639294.0733870436,3839949.2858998161,1568360.0207768085,121080.69019803751,"",""]
[null,null,"Other",2302649.8873803644,4341717.3504854497,1019610.3815043687,204742.77385401475,"",""]
[null,"NON-NETWORK EXPENDITURE","IT and communications",10623226.729116395,17934058.240120742,6363795.5043264441,37033155.116436929,941743.45,""]
[null,null,"Motor vehicles",13760088.290000001,2521196,236420,3872120.49,"",""]
[null,null,"Buildings and property",337489.82436472899,1060331.2561901254,197952.89864452562,9022619.3682199344,"",""]
[null,null,"Other",5572360.9478882989,3419253.541104761,6531201.4892595783,3098276.3617473673,"",""]

{"sheet":"4.1 Public lighting","index":17,"n_rows":539,"n_cols":5,"rows_kept":539,"cut":false,"hidden":false,"merged":[[9,2,10,2],[6,1,6,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"4.1 PUBLIC LIGHTING"]
[]
[]
[null,"There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.1.1 - DESCRIPTOR METRICS OVER YEAR"]
[null,null,"LIGHT TYPE",null,"VOLUME \n(0's)"]
[null,null,null,null,{"$f":"CRY","v":"2016-17"}]
[null,"POPULATION OF LIGHTS","DNSP to enter description for type of light"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"4.1.2 - DESCRIPTOR METRICS ANNUALLY"]
[]
[]
[null,null,null,null,"VOLUMES \n& EXPENDITURE"]
[null,"SERVICE/SERVICE QUALITY ","DESCRIPTOR METRIC","UNITS",{"$f":"CRY","v":"2016-17"}]
[null,"LIGHT INSTALLATION","Major road light installation","0's"]
[null,null,"Minor road light installation","0's"]
[null,null,"Number of poles installed","0's"]
[null,null,"Total cost","$0s"]
[null,"LIGHT REPLACEMENT","Major road light replacement","0's"]
[null,null,"Minor road light replacement","0's"]
[null,null,"Number of poles replaced","0's"]
[null,null,"Total cost","$0s"]
[null,"LIGHT MAINTENANCE","Major road light maintenance","0's"]
[null,null,"Minor road light maintenance","0's"]
[null,null,"Number of poles installed","0's"]
[null,null,"Total cost","$0s"]
[null,"QUALITY OF SUPPLY","Mean days to rectify/replace public lighting assets","days"]
[null,null,"GSO breaches","0's"]
[null,null,"GSL payments","$0s"]
[null,null,"Customer complaints","0's"]
[]
[]
[null,"4.1.3 - COST METRICS"]
[null,null,null,null,"AVERAGE UNIT COST \n($)"]
[null,"ACTIVITY TYPE","LIGHT TYPE",null,{"$f":"CRY","v":"2016-17"}]
[null,"LIGHT INSTALLATION","DNSP to enter description for type of light",null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,"LIGHT REPLACEMENT","DNSP to enter description for type of light",null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[]
[]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,null,null,null,""]
[null,"LIGHT MAINTENANCE","DNSP to enter description for type of light",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]
[null,null,"",null,""]

{"sheet":"4.2 Metering","index":18,"n_rows":61,"n_cols":5,"rows_kept":61,"cut":false,"hidden":false,"merged":[[5,1,5,2]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"4.2 METERING"]
[]
[null,"There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables. "]
[]
[null,"4.2.1 - METERING DESCRIPTOR METRIC"]
[null,null,null,"VOLUMES\n(0's)"]
[null,"ASSET CATEGORY","ASSET SUBCATEGORY",{"$f":"CRY","v":"2016-17"}]
[null,"Meter Type 4","Single phase meter population ",0]
[null,null,"Multi phase meter population ",2091]
[null,null,"Current transformer connected meter population ",2023]
[null,null,"Direct connect meter population ",68]
[null,"Meter Type 5","Single phase meter population ",359]
[null,null,"Multi phase meter population ",8501]
[null,null,"Current transformer connected meter population ",4945]
[null,null,"Direct connect meter population ",3915]
[null,"Meter Type 6","Single phase meter population ",858458]
[null,null,"Multi phase meter population ",191796]
[null,null,"Current transformer connected meter population ",650]
[null,null,"Direct connect meter population ",1049604]
[]
[]
[null,"4.2.2 - COST METRICS"]
[null,null,null,"VOLUMES\n(0's)","EXPENDITURE\n($0's)"]
[null,"SERVICE SUBCATEGORY","METER TYPE",{"$f":"CRY","v":"2016-17"},{"$f":"CRY","v":"2016-17"}]
[null,"Meter purchase ","Meter Type 4",0,0]
[null,null,"Meter Type 5",375,67732]
[null,null,"Meter Type 6",23980,1340409]
[null,"Meter testing ","Meter Type 4",90,79805.469578623321]
[null,null,"Meter Type 5",14,5402.5109135100711]
[null,null,"Meter Type 6",1889,433383.39172884024]
[null,"Meter investigation ","Meter Type 4",141,21777.244036651722]
[null,null,"Meter Type 5",3220,243955.05100588762]
[null,null,"Meter Type 6",4742,725007.51413664315]
[null,"Scheduled meter reading ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6"]
[null,"Special meter reading ","Meter Type 4",0,0]
[null,null,"Meter Type 5",0,0]
[null,null,"Meter Type 6",0,0]
[null,"New meter installation ","Meter Type 4",112,43453.154418617567]
[null,null,"Meter Type 5",712,246073.92856752753]
[null,null,"Meter Type 6",9537,2531180.6006359113]
[null,"Meter replacement ","Meter Type 4",88,247982.39055990116]
[null,null,"Meter Type 5",1946,983515.83871247037]
[null,null,"Meter Type 6",11689,2255979.0071055717]
[null,"Meter maintenance ","Meter Type 4",237,100134.85522961804]
[null,null,"Meter Type 5",782,236438.30337022571]
[null,null,"Meter Type 6",0,0]
[null,"Remote meter reading ","Meter Type 4"]
[null,"Remote meter re-configuration ","Meter Type 4"]
[null,"Other metering ","Meter Type 4"]
[null,null,"Meter Type 5"]
[null,null,"Meter Type 6"]
[null,null,"Meter Type 7"]
[null,"IT infrastructure capex ","Meter Type 4"]
[null,"IT infrastructure opex ","Meter Type 4"]
[null,"Communications infrastructure capex ","Meter Type 4"]
[null,"Communications infrastructure opex ","Meter Type 4"]

{"sheet":"4.3 Fee-based services","index":19,"n_rows":479,"n_cols":6,"rows_kept":479,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"4.3 ANCILLARY SERVICES - FEE BASED SERVICES"]
[]
[null,"4.3.1 - COST METRICS FOR FEE-BASED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY",{"$f":"CRY","v":"2016-17"},null,{"$f":"CRY","v":"2016-17"}]
[null,"Common Fee-Based Services","Energisation",null,"ED_FEE431_00001"]
[null,null,"De-energisation",null,"ED_FEE431_00002"]
[null,null,"Re-energisation",null,"ED_FEE431_00003"]
[null,"Miscellaneous Fee-Based Services","< Enter description for service >",null,"ED_FEE431_00004"]
[null,null,null,null,"ED_FEE431_00005"]
[null,null,null,null,"ED_FEE431_00006"]
[null,null,null,null,"ED_FEE431_00007"]
[null,null,null,null,"ED_FEE431_00008"]
[null,null,null,null,"ED_FEE431_00009"]
[null,null,null,null,"ED_FEE431_00010"]
[null,null,null,null,"ED_FEE431_00011"]
[null,null,null,null,"ED_FEE431_00012"]
[null,null,null,"","ED_FEE431_00013",""]
[null,null,null,"","ED_FEE431_00014",""]
[null,null,null,"","ED_FEE431_00015",""]
[null,null,null,"","ED_FEE431_00016",""]
[null,null,null,"","ED_FEE431_00017",""]
[null,null,null,"","ED_FEE431_00018",""]
[null,null,null,"","ED_FEE431_00019",""]
[null,null,null,"","ED_FEE431_00020",""]
[null,null,null,"","ED_FEE431_00021",""]
[null,null,null,"","ED_FEE431_00022",""]
[null,null,null,"","ED_FEE431_00023",""]
[null,null,null,"","ED_FEE431_00024",""]
[null,null,null,"","ED_FEE431_00025",""]
[null,null,null,"","ED_FEE431_00026",""]
[null,null,null,"","ED_FEE431_00027",""]
[null,null,null,"","ED_FEE431_00028",""]
[null,null,null,"","ED_FEE431_00029",""]
[null,null,null,"","ED_FEE431_00030",""]
[null,null,null,"","ED_FEE431_00031",""]
[null,null,null,"","ED_FEE431_00032",""]
[null,null,null,"","ED_FEE431_00033",""]
[null,null,null,"","ED_FEE431_00034",""]
[null,null,null,"","ED_FEE431_00035",""]
[null,null,null,"","ED_FEE431_00036",""]
[null,null,null,"","ED_FEE431_00037",""]
[null,null,null,"","ED_FEE431_00038",""]
[null,null,null,"","ED_FEE431_00039",""]
[null,null,null,"","ED_FEE431_00040",""]
[null,null,null,"","ED_FEE431_00041",""]
[null,null,null,"","ED_FEE431_00042",""]
[null,null,null,"","ED_FEE431_00043",""]
[null,null,null,"","ED_FEE431_00044",""]
[null,null,null,"","ED_FEE431_00045",""]
[null,null,null,"","ED_FEE431_00046",""]
[null,null,null,"","ED_FEE431_00047",""]
[null,null,null,"","ED_FEE431_00048",""]
[null,null,null,"","ED_FEE431_00049",""]
[null,null,null,"","ED_FEE431_00050",""]
[null,null,null,"","ED_FEE431_00051",""]
[null,null,null,"","ED_FEE431_00052",""]
[null,null,null,"","ED_FEE431_00053",""]
[null,null,null,"","ED_FEE431_00054",""]
[null,null,null,"","ED_FEE431_00055",""]
[null,null,null,"","ED_FEE431_00056",""]
[null,null,null,"","ED_FEE431_00057",""]
[null,null,null,"","ED_FEE431_00058",""]
[null,null,null,"","ED_FEE431_00059",""]
[null,null,null,"","ED_FEE431_00060",""]
[null,null,null,"","ED_FEE431_00061",""]
[null,null,null,"","ED_FEE431_00062",""]
[null,null,null,"","ED_FEE431_00063",""]
[null,null,null,"","ED_FEE431_00064",""]
[null,null,null,"","ED_FEE431_00065",""]
[null,null,null,"","ED_FEE431_00066",""]
[null,null,null,"","ED_FEE431_00067",""]
[null,null,null,"","ED_FEE431_00068",""]
[null,null,null,"","ED_FEE431_00069",""]
[null,null,null,"","ED_FEE431_00070",""]
[null,null,null,"","ED_FEE431_00071",""]
[null,null,null,"","ED_FEE431_00072",""]
[null,null,null,"","ED_FEE431_00073",""]
[null,null,null,"","ED_FEE431_00074",""]
[null,null,null,"","ED_FEE431_00075",""]
[null,null,null,"","ED_FEE431_00076",""]
[null,null,null,"","ED_FEE431_00077",""]
[null,null,null,"","ED_FEE431_00078",""]
[null,null,null,"","ED_FEE431_00079",""]
[null,null,null,"","ED_FEE431_00080",""]
[null,null,null,"","ED_FEE431_00081",""]
[null,null,null,"","ED_FEE431_00082",""]
[null,null,null,"","ED_FEE431_00083",""]
[null,null,null,"","ED_FEE431_00084",""]
[null,null,null,"","ED_FEE431_00085",""]
[null,null,null,"","ED_FEE431_00086",""]
[null,null,null,"","ED_FEE431_00087",""]
[null,null,null,"","ED_FEE431_00088",""]
[null,null,null,"","ED_FEE431_00089",""]
[null,null,null,"","ED_FEE431_00090",""]
[null,null,null,"","ED_FEE431_00091",""]
[null,null,null,"","ED_FEE431_00092",""]
[null,null,null,"","ED_FEE431_00093",""]
[null,null,null,"","ED_FEE431_00094",""]
[null,null,null,"","ED_FEE431_00095",""]
[null,null,null,"","ED_FEE431_00096",""]
[null,null,null,"","ED_FEE431_00097",""]
[null,null,null,"","ED_FEE431_00098",""]
[null,null,null,"","ED_FEE431_00099",""]
[null,null,null,"","ED_FEE431_00100",""]
[null,null,null,"","ED_FEE431_00101",""]
[null,null,null,"","ED_FEE431_00102",""]
[null,null,null,"","ED_FEE431_00103",""]
[null,null,null,"","ED_FEE431_00104",""]
[null,null,null,"","ED_FEE431_00105",""]
[null,null,null,"","ED_FEE431_00106",""]
[null,null,null,"","ED_FEE431_00107",""]
[null,null,null,"","ED_FEE431_00108",""]
[null,null,null,"","ED_FEE431_00109",""]
[null,null,null,"","ED_FEE431_00110",""]
[null,null,null,"","ED_FEE431_00111",""]
[null,null,null,"","ED_FEE431_00112",""]
[null,null,null,"","ED_FEE431_00113",""]
[null,null,null,"","ED_FEE431_00114",""]
[null,null,null,"","ED_FEE431_00115",""]
[null,null,null,"","ED_FEE431_00116",""]
[null,null,null,"","ED_FEE431_00117",""]
[null,null,null,"","ED_FEE431_00118",""]
[null,null,null,"","ED_FEE431_00119",""]
[null,null,null,"","ED_FEE431_00120",""]
[null,null,null,"","ED_FEE431_00121",""]
[null,null,null,"","ED_FEE431_00122",""]
[null,null,null,"","ED_FEE431_00123",""]
[null,null,null,"","ED_FEE431_00124",""]
[null,null,null,"","ED_FEE431_00125",""]
[null,null,null,"","ED_FEE431_00126",""]
[null,null,null,"","ED_FEE431_00127",""]
[null,null,null,"","ED_FEE431_00128",""]
[null,null,null,"","ED_FEE431_00129",""]
[null,null,null,"","ED_FEE431_00130",""]
[null,null,null,"","ED_FEE431_00131",""]
[null,null,null,"","ED_FEE431_00132",""]
[null,null,null,"","ED_FEE431_00133",""]
[null,null,null,"","ED_FEE431_00134",""]
[null,null,null,"","ED_FEE431_00135",""]
[null,null,null,"","ED_FEE431_00136",""]
[null,null,null,"","ED_FEE431_00137",""]
[null,null,null,"","ED_FEE431_00138",""]
[null,null,null,"","ED_FEE431_00139",""]
[null,null,null,"","ED_FEE431_00140",""]
[null,null,null,"","ED_FEE431_00141",""]
[null,null,null,"","ED_FEE431_00142",""]
[null,null,null,"","ED_FEE431_00143",""]
[null,null,null,"","ED_FEE431_00144",""]
[null,null,null,"","ED_FEE431_00145",""]
[null,null,null,"","ED_FEE431_00146",""]
[null,null,null,"","ED_FEE431_00147",""]
[null,null,null,"","ED_FEE431_00148",""]
[null,null,null,"","ED_FEE431_00149",""]
[null,null,null,"","ED_FEE431_00150",""]
[null,null,null,"","ED_FEE431_00151",""]
[null,null,null,"","ED_FEE431_00152",""]
[null,null,null,"","ED_FEE431_00153",""]
[null,null,null,"","ED_FEE431_00154",""]
[null,null,null,"","ED_FEE431_00155",""]
[null,null,null,"","ED_FEE431_00156",""]
[null,null,null,"","ED_FEE431_00157",""]
[null,null,null,"","ED_FEE431_00158",""]
[null,null,null,"","ED_FEE431_00159",""]
[null,null,null,"","ED_FEE431_00160",""]
[null,null,null,"","ED_FEE431_00161",""]
[null,null,null,"","ED_FEE431_00162",""]
[null,null,null,"","ED_FEE431_00163",""]
[null,null,null,"","ED_FEE431_00164",""]
[null,null,null,"","ED_FEE431_00165",""]
[null,null,null,"","ED_FEE431_00166",""]
[null,null,null,"","ED_FEE431_00167",""]
[null,null,null,"","ED_FEE431_00168",""]
[null,null,null,"","ED_FEE431_00169",""]
[null,null,null,"","ED_FEE431_00170",""]
[null,null,null,"","ED_FEE431_00171",""]
[null,null,null,"","ED_FEE431_00172",""]
[null,null,null,"","ED_FEE431_00173",""]
[null,null,null,"","ED_FEE431_00174",""]
[null,null,null,"","ED_FEE431_00175",""]
[null,null,null,"","ED_FEE431_00176",""]
[null,null,null,"","ED_FEE431_00177",""]
[null,null,null,"","ED_FEE431_00178",""]
[null,null,null,"","ED_FEE431_00179",""]
[null,null,null,"","ED_FEE431_00180",""]
[null,null,null,"","ED_FEE431_00181",""]
[null,null,null,"","ED_FEE431_00182",""]
[null,null,null,"","ED_FEE431_00183",""]
[null,null,null,"","ED_FEE431_00184",""]
[null,null,null,"","ED_FEE431_00185",""]
[null,null,null,"","ED_FEE431_00186",""]
[null,null,null,"","ED_FEE431_00187",""]
[null,null,null,"","ED_FEE431_00188",""]
[null,null,null,"","ED_FEE431_00189",""]
[null,null,null,"","ED_FEE431_00190",""]
[null,null,null,"","ED_FEE431_00191",""]
[null,null,null,"","ED_FEE431_00192",""]
[null,null,null,"","ED_FEE431_00193",""]
[null,null,null,"","ED_FEE431_00194",""]
[null,null,null,"","ED_FEE431_00195",""]
[null,null,null,"","ED_FEE431_00196",""]
[null,null,null,"","ED_FEE431_00197",""]
[null,null,null,"","ED_FEE431_00198",""]
[null,null,null,"","ED_FEE431_00199",""]
[null,null,null,"","ED_FEE431_00200",""]
[null,null,null,"","ED_FEE431_00201",""]
[null,null,null,"","ED_FEE431_00202",""]
[null,null,null,"","ED_FEE431_00203",""]
[null,null,null,"","ED_FEE431_00204",""]
[null,null,null,"","ED_FEE431_00205",""]
[null,null,null,"","ED_FEE431_00206",""]
[null,null,null,"","ED_FEE431_00207",""]
[null,null,null,"","ED_FEE431_00208",""]
[null,null,null,"","ED_FEE431_00209",""]
[null,null,null,"","ED_FEE431_00210",""]
[null,null,null,"","ED_FEE431_00211",""]
[null,null,null,"","ED_FEE431_00212",""]
[null,null,null,"","ED_FEE431_00213",""]
[null,null,null,"","ED_FEE431_00214",""]
[null,null,null,"","ED_FEE431_00215",""]
[null,null,null,"","ED_FEE431_00216",""]
[null,null,null,"","ED_FEE431_00217",""]
[null,null,null,"","ED_FEE431_00218",""]
[null,null,null,"","ED_FEE431_00219",""]
[null,null,null,"","ED_FEE431_00220",""]
[null,null,null,"","ED_FEE431_00221",""]
[null,null,null,"","ED_FEE431_00222",""]
[null,null,null,"","ED_FEE431_00223",""]
[null,null,null,"","ED_FEE431_00224",""]
[null,null,null,"","ED_FEE431_00225",""]
[null,null,null,"","ED_FEE431_00226",""]
[null,null,null,"","ED_FEE431_00227",""]
[null,null,null,"","ED_FEE431_00228",""]
[null,null,null,"","ED_FEE431_00229",""]
[null,null,null,"","ED_FEE431_00230",""]
[null,null,null,"","ED_FEE431_00231",""]
[null,null,null,"","ED_FEE431_00232",""]
[null,null,null,null,"ED_FEE431_00233"]
[null,null,null,"","ED_FEE431_00234",""]
[null,null,null,"","ED_FEE431_00235",""]
[null,null,null,"","ED_FEE431_00236",""]
[null,null,null,"","ED_FEE431_00237",""]
[null,null,null,"","ED_FEE431_00238",""]
[null,null,null,"","ED_FEE431_00239",""]
[null,null,null,"","ED_FEE431_00240",""]
[null,null,null,"","ED_FEE431_00241",""]
[null,null,null,"","ED_FEE431_00242",""]
[null,null,null,"","ED_FEE431_00243",""]
[null,null,null,"","ED_FEE431_00244",""]
[null,null,null,"","ED_FEE431_00245",""]
[null,null,null,"","ED_FEE431_00246",""]
[null,null,null,"","ED_FEE431_00247",""]
[null,null,null,"","ED_FEE431_00248",""]
[null,null,null,"","ED_FEE431_00249",""]
[null,null,null,"","ED_FEE431_00250",""]
[null,null,null,"","ED_FEE431_00251",""]
[null,null,null,"","ED_FEE431_00252",""]
[null,null,null,"","ED_FEE431_00253",""]
[null,null,null,"","ED_FEE431_00254",""]
[null,null,null,"","ED_FEE431_00255",""]
[null,null,null,"","ED_FEE431_00256",""]
[null,null,null,"","ED_FEE431_00257",""]
[null,null,null,"","ED_FEE431_00258",""]
[null,null,null,"","ED_FEE431_00259",""]
[null,null,null,"","ED_FEE431_00260",""]
[null,null,null,"","ED_FEE431_00261",""]
[null,null,null,"","ED_FEE431_00262",""]
[null,null,null,"","ED_FEE431_00263",""]
[null,null,null,"","ED_FEE431_00264",""]
[null,null,null,"","ED_FEE431_00265",""]
[null,null,null,"","ED_FEE431_00266",""]
[null,null,null,"","ED_FEE431_00267",""]
[null,null,null,"","ED_FEE431_00268",""]
[null,null,null,"","ED_FEE431_00269",""]
[null,null,null,"","ED_FEE431_00270",""]
[null,null,null,"","ED_FEE431_00271",""]
[null,null,null,"","ED_FEE431_00272",""]
[null,null,null,"","ED_FEE431_00273",""]
[null,null,null,"","ED_FEE431_00274",""]
[null,null,null,"","ED_FEE431_00275",""]
[null,null,null,"","ED_FEE431_00276",""]
[null,null,null,"","ED_FEE431_00277",""]
[null,null,null,"","ED_FEE431_00278",""]
[null,null,null,"","ED_FEE431_00279",""]
[null,null,null,"","ED_FEE431_00280",""]
[null,null,null,"","ED_FEE431_00281",""]
[null,null,null,"","ED_FEE431_00282",""]
[null,null,null,"","ED_FEE431_00283",""]
[null,null,null,"","ED_FEE431_00284",""]
[null,null,null,"","ED_FEE431_00285",""]
[null,null,null,"","ED_FEE431_00286",""]
[null,null,null,"","ED_FEE431_00287",""]
[null,null,null,"","ED_FEE431_00288",""]
[null,null,null,"","ED_FEE431_00289",""]
[null,null,null,"","ED_FEE431_00290",""]
[null,null,null,"","ED_FEE431_00291",""]
[null,null,null,"","ED_FEE431_00292",""]
[null,null,null,"","ED_FEE431_00293",""]
[null,null,null,"","ED_FEE431_00294",""]
[null,null,null,"","ED_FEE431_00295",""]
[null,null,null,"","ED_FEE431_00296",""]
[null,null,null,"","ED_FEE431_00297",""]
[null,null,null,"","ED_FEE431_00298",""]
[null,null,null,"","ED_FEE431_00299",""]
[null,null,null,"","ED_FEE431_00300",""]
[null,null,null,"","ED_FEE431_00301",""]
[null,null,null,"","ED_FEE431_00302",""]
[null,null,null,"","ED_FEE431_00303",""]
[null,null,null,"","ED_FEE431_00304",""]
[null,null,null,"","ED_FEE431_00305",""]
[null,null,null,"","ED_FEE431_00306",""]
[null,null,null,"","ED_FEE431_00307",""]
[null,null,null,"","ED_FEE431_00308",""]
[null,null,null,"","ED_FEE431_00309",""]
[null,null,null,"","ED_FEE431_00310",""]
[null,null,null,"","ED_FEE431_00311",""]
[null,null,null,"","ED_FEE431_00312",""]
[null,null,null,"","ED_FEE431_00313",""]
[null,null,null,"","ED_FEE431_00314",""]
[null,null,null,"","ED_FEE431_00315",""]
[null,null,null,"","ED_FEE431_00316",""]
[null,null,null,"","ED_FEE431_00317",""]
[null,null,null,"","ED_FEE431_00318",""]
[null,null,null,"","ED_FEE431_00319",""]
[null,null,null,"","ED_FEE431_00320",""]
[null,null,null,"","ED_FEE431_00321",""]
[null,null,null,"","ED_FEE431_00322",""]
[null,null,null,"","ED_FEE431_00323",""]
[null,null,null,"","ED_FEE431_00324",""]
[null,null,null,"","ED_FEE431_00325",""]
[null,null,null,"","ED_FEE431_00326",""]
[null,null,null,"","ED_FEE431_00327",""]
[null,null,null,"","ED_FEE431_00328",""]
[null,null,null,"","ED_FEE431_00329",""]
[null,null,null,"","ED_FEE431_00330",""]
[null,null,null,"","ED_FEE431_00331",""]
[null,null,null,"","ED_FEE431_00332",""]
[null,null,null,"","ED_FEE431_00333",""]
[null,null,null,"","ED_FEE431_00334",""]
[null,null,null,"","ED_FEE431_00335",""]
[null,null,null,"","ED_FEE431_00336",""]
[null,null,null,"","ED_FEE431_00337",""]
[null,null,null,"","ED_FEE431_00338",""]
[null,null,null,"","ED_FEE431_00339",""]
[null,null,null,"","ED_FEE431_00340",""]
[null,null,null,"","ED_FEE431_00341",""]
[null,null,null,"","ED_FEE431_00342",""]
[null,null,null,"","ED_FEE431_00343",""]
[null,null,null,"","ED_FEE431_00344",""]
[null,null,null,"","ED_FEE431_00345",""]
[null,null,null,"","ED_FEE431_00346",""]
[null,null,null,"","ED_FEE431_00347",""]
[null,null,null,"","ED_FEE431_00348",""]
[null,null,null,"","ED_FEE431_00349",""]
[null,null,null,"","ED_FEE431_00350",""]
[null,null,null,"","ED_FEE431_00351",""]
[null,null,null,"","ED_FEE431_00352",""]
[null,null,null,"","ED_FEE431_00353",""]
[null,null,null,"","ED_FEE431_00354",""]
[null,null,null,"","ED_FEE431_00355",""]
[null,null,null,"","ED_FEE431_00356",""]
[null,null,null,"","ED_FEE431_00357",""]
[null,null,null,"","ED_FEE431_00358",""]
[null,null,null,"","ED_FEE431_00359",""]
[null,null,null,"","ED_FEE431_00360",""]
[null,null,null,"","ED_FEE431_00361",""]
[null,null,null,"","ED_FEE431_00362",""]
[null,null,null,"","ED_FEE431_00363",""]
[null,null,null,"","ED_FEE431_00364",""]
[null,null,null,"","ED_FEE431_00365",""]
[null,null,null,"","ED_FEE431_00366",""]
[null,null,null,"","ED_FEE431_00367",""]
[null,null,null,"","ED_FEE431_00368",""]
[null,null,null,"","ED_FEE431_00369",""]
[null,null,null,"","ED_FEE431_00370",""]
[null,null,null,"","ED_FEE431_00371",""]
[null,null,null,"","ED_FEE431_00372",""]
[null,null,null,"","ED_FEE431_00373",""]
[null,null,null,"","ED_FEE431_00374",""]
[null,null,null,"","ED_FEE431_00375",""]
[null,null,null,"","ED_FEE431_00376",""]
[null,null,null,"","ED_FEE431_00377",""]
[null,null,null,"","ED_FEE431_00378",""]
[null,null,null,"","ED_FEE431_00379",""]
[null,null,null,"","ED_FEE431_00380",""]
[null,null,null,"","ED_FEE431_00381",""]
[null,null,null,"","ED_FEE431_00382",""]
[null,null,null,"","ED_FEE431_00383",""]
[null,null,null,"","ED_FEE431_00384",""]
[null,null,null,"","ED_FEE431_00385",""]
[null,null,null,"","ED_FEE431_00386",""]
[null,null,null,"","ED_FEE431_00387",""]
[null,null,null,"","ED_FEE431_00388",""]
[null,null,null,"","ED_FEE431_00389",""]
[null,null,null,"","ED_FEE431_00390",""]
[null,null,null,"","ED_FEE431_00391",""]
[null,null,null,"","ED_FEE431_00392",""]
[null,null,null,"","ED_FEE431_00393",""]
[null,null,null,"","ED_FEE431_00394",""]
[null,null,null,"","ED_FEE431_00395",""]
[null,null,null,"","ED_FEE431_00396",""]
[null,null,null,"","ED_FEE431_00397",""]
[null,null,null,"","ED_FEE431_00398",""]
[null,null,null,"","ED_FEE431_00399",""]
[null,null,null,"","ED_FEE431_00400",""]
[null,null,null,"","ED_FEE431_00401",""]
[null,null,null,"","ED_FEE431_00402",""]
[null,null,null,"","ED_FEE431_00403",""]
[null,null,null,"","ED_FEE431_00404",""]
[null,null,null,"","ED_FEE431_00405",""]
[null,null,null,"","ED_FEE431_00406",""]
[null,null,null,"","ED_FEE431_00407",""]
[null,null,null,"","ED_FEE431_00408",""]
[null,null,null,"","ED_FEE431_00409",""]
[null,null,null,"","ED_FEE431_00410",""]
[null,null,null,"","ED_FEE431_00411",""]
[null,null,null,"","ED_FEE431_00412",""]
[null,null,null,"","ED_FEE431_00413",""]
[null,null,null,"","ED_FEE431_00414",""]
[null,null,null,"","ED_FEE431_00415",""]
[null,null,null,"","ED_FEE431_00416",""]
[null,null,null,"","ED_FEE431_00417",""]
[null,null,null,"","ED_FEE431_00418",""]
[null,null,null,"","ED_FEE431_00419",""]
[null,null,null,"","ED_FEE431_00420",""]
[null,null,null,"","ED_FEE431_00421",""]
[null,null,null,"","ED_FEE431_00422",""]
[null,null,null,"","ED_FEE431_00423",""]
[null,null,null,"","ED_FEE431_00424",""]
[null,null,null,"","ED_FEE431_00425",""]
[null,null,null,"","ED_FEE431_00426",""]
[null,null,null,"","ED_FEE431_00427",""]
[null,null,null,"","ED_FEE431_00428",""]
[null,null,null,"","ED_FEE431_00429",""]
[null,null,null,"","ED_FEE431_00430",""]
[null,null,null,"","ED_FEE431_00431",""]
[null,null,null,"","ED_FEE431_00432",""]
[null,null,null,"","ED_FEE431_00433",""]
[null,null,null,"","ED_FEE431_00434",""]
[null,null,null,"","ED_FEE431_00435",""]
[null,null,null,"","ED_FEE431_00436",""]
[null,null,null,"","ED_FEE431_00437",""]
[null,null,null,"","ED_FEE431_00438",""]
[null,null,null,"","ED_FEE431_00439",""]
[null,null,null,"","ED_FEE431_00440",""]
[null,null,null,"","ED_FEE431_00441",""]
[null,null,null,"","ED_FEE431_00442",""]
[null,null,null,"","ED_FEE431_00443",""]
[null,null,null,"","ED_FEE431_00444",""]
[null,null,null,"","ED_FEE431_00445",""]
[null,null,null,"","ED_FEE431_00446",""]
[null,null,null,"","ED_FEE431_00447",""]
[null,null,null,"","ED_FEE431_00448",""]
[null,null,null,"","ED_FEE431_00449",""]
[null,null,null,"","ED_FEE431_00450",""]
[null,null,null,"","ED_FEE431_00451",""]
[null,null,null,"","ED_FEE431_00452",""]
[null,null,null,"","ED_FEE431_00453",""]
[null,null,null,"","ED_FEE431_00454",""]
[null,null,null,"","ED_FEE431_00455",""]
[null,null,null,"","ED_FEE431_00456",""]
[null,null,null,"","ED_FEE431_00457",""]
[null,null,null,"","ED_FEE431_00458",""]
[null,null,null,"","ED_FEE431_00459",""]
[null,null,null,"","ED_FEE431_00460",""]
[null,null,null,"","ED_FEE431_00461",""]
[null,null,null,"","ED_FEE431_00462",""]
[null,null,null,"","ED_FEE431_00463",""]
[null,null,null,"","ED_FEE431_00464",""]
[null,null,null,"","ED_FEE431_00465",""]
[null,null,null,"","ED_FEE431_00466",""]
[null,null,null,"","ED_FEE431_00467",""]
[null,null,null,"","ED_FEE431_00468",""]
[null,null,null,"","ED_FEE431_00469",""]
[null,null,null,"","ED_FEE431_00470",""]
[null,null,null,"","ED_FEE431_00471",""]

{"sheet":"4.4 Quoted services","index":20,"n_rows":481,"n_cols":6,"rows_kept":481,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"4.4 ANCILLARY SERVICES - QUOTED SERVICES"]
[]
[null,"4.4.1 - COST METRICS FOR QUOTED SERVICES"]
[null,null,null,"EXPENDITURE \n($0's)",null,"VOLUMES \n(0's)"]
[null,"SERVICE","SERVICE SUBCATEGORY",{"$f":"CRY","v":"2016-17"},null,{"$f":"CRY","v":"2016-17"}]
[null,"Quoted Services ","< Enter description for service subcategory >",null,"ED_QUO441_00001"]
[null,null,null,null,"ED_QUO441_00002"]
[null,null,null,null,"ED_QUO441_00003"]
[null,null,null,null,"ED_QUO441_00004"]
[null,null,null,null,"ED_QUO441_00005"]
[null,null,null,null,"ED_QUO441_00006"]
[null,null,null,null,"ED_QUO441_00007"]
[null,null,null,null,"ED_QUO441_00008"]
[null,null,null,null,"ED_QUO441_00009"]
[null,null,null,null,"ED_QUO441_00010"]
[null,null,null,null,"ED_QUO441_00011"]
[null,null,null,null,"ED_QUO441_00012"]
[null,null,null,null,"ED_QUO441_00013"]
[null,null,null,null,"ED_QUO441_00014"]
[null,null,null,null,"ED_QUO441_00015"]
[null,null,null,null,"ED_QUO441_00016"]
[null,null,null,null,"ED_QUO441_00017"]
[null,null,null,null,"ED_QUO441_00018"]
[null,null,null,null,"ED_QUO441_00019"]
[null,null,null,null,"ED_QUO441_00020"]
[null,null,null,null,"ED_QUO441_00021"]
[null,null,null,null,"ED_QUO441_00022"]
[null,null,null,null,"ED_QUO441_00023"]
[null,null,null,null,"ED_QUO441_00024"]
[null,null,null,null,"ED_QUO441_00025"]
[null,null,null,null,"ED_QUO441_00026"]
[null,null,null,null,"ED_QUO441_00027"]
[null,null,null,null,"ED_QUO441_00028"]
[null,null,null,null,"ED_QUO441_00029"]
[null,null,null,null,"ED_QUO441_00030"]
[null,null,null,null,"ED_QUO441_00031"]
[null,null,null,null,"ED_QUO441_00032"]
[null,null,null,null,"ED_QUO441_00033"]
[null,null,null,"","ED_QUO441_00034",""]
[null,null,null,"","ED_QUO441_00035",""]
[null,null,null,"","ED_QUO441_00036",""]
[null,null,null,"","ED_QUO441_00037",""]
[null,null,null,"","ED_QUO441_00038",""]
[null,null,null,"","ED_QUO441_00039",""]
[null,null,null,"","ED_QUO441_00040",""]
[null,null,null,"","ED_QUO441_00041",""]
[null,null,null,"","ED_QUO441_00042",""]
[null,null,null,"","ED_QUO441_00043",""]
[null,null,null,"","ED_QUO441_00044",""]
[null,null,null,"","ED_QUO441_00045",""]
[null,null,null,"","ED_QUO441_00046",""]
[null,null,null,"","ED_QUO441_00047",""]
[null,null,null,"","ED_QUO441_00048",""]
[null,null,null,"","ED_QUO441_00049",""]
[null,null,null,"","ED_QUO441_00050",""]
[null,null,null,"","ED_QUO441_00051",""]
[null,null,null,"","ED_QUO441_00052",""]
[null,null,null,"","ED_QUO441_00053",""]
[null,null,null,"","ED_QUO441_00054",""]
[null,null,null,"","ED_QUO441_00055",""]
[null,null,null,"","ED_QUO441_00056",""]
[null,null,null,"","ED_QUO441_00057",""]
[null,null,null,"","ED_QUO441_00058",""]
[null,null,null,"","ED_QUO441_00059",""]
[null,null,null,"","ED_QUO441_00060",""]
[null,null,null,"","ED_QUO441_00061",""]
[null,null,null,"","ED_QUO441_00062",""]
[null,null,null,"","ED_QUO441_00063",""]
[null,null,null,"","ED_QUO441_00064",""]
[null,null,null,"","ED_QUO441_00065",""]
[null,null,null,"","ED_QUO441_00066",""]
[null,null,null,"","ED_QUO441_00067",""]
[null,null,null,"","ED_QUO441_00068",""]
[null,null,null,"","ED_QUO441_00069",""]
[null,null,null,"","ED_QUO441_00070",""]
[null,null,null,"","ED_QUO441_00071",""]
[null,null,null,"","ED_QUO441_00072",""]
[null,null,null,"","ED_QUO441_00073",""]
[null,null,null,"","ED_QUO441_00074",""]
[null,null,null,"","ED_QUO441_00075",""]
[null,null,null,"","ED_QUO441_00076",""]
[null,null,null,"","ED_QUO441_00077",""]
[null,null,null,"","ED_QUO441_00078",""]
[null,null,null,"","ED_QUO441_00079",""]
[null,null,null,"","ED_QUO441_00080",""]
[null,null,null,"","ED_QUO441_00081",""]
[null,null,null,"","ED_QUO441_00082",""]
[null,null,null,"","ED_QUO441_00083",""]
[null,null,null,"","ED_QUO441_00084",""]
[null,null,null,"","ED_QUO441_00085",""]
[null,null,null,"","ED_QUO441_00086",""]
[null,null,null,"","ED_QUO441_00087",""]
[null,null,null,"","ED_QUO441_00088",""]
[null,null,null,"","ED_QUO441_00089",""]
[null,null,null,"","ED_QUO441_00090",""]
[null,null,null,"","ED_QUO441_00091",""]
[null,null,null,"","ED_QUO441_00092",""]
[null,null,null,"","ED_QUO441_00093",""]
[null,null,null,"","ED_QUO441_00094",""]
[null,null,null,"","ED_QUO441_00095",""]
[null,null,null,"","ED_QUO441_00096",""]
[null,null,null,"","ED_QUO441_00097",""]
[null,null,null,"","ED_QUO441_00098",""]
[null,null,null,"","ED_QUO441_00099",""]
[null,null,null,"","ED_QUO441_00100",""]
[null,null,null,"","ED_QUO441_00101",""]
[null,null,null,"","ED_QUO441_00102",""]
[null,null,null,"","ED_QUO441_00103",""]
[null,null,null,"","ED_QUO441_00104",""]
[null,null,null,"","ED_QUO441_00105",""]
[null,null,null,"","ED_QUO441_00106",""]
[null,null,null,"","ED_QUO441_00107",""]
[null,null,null,"","ED_QUO441_00108",""]
[null,null,null,"","ED_QUO441_00109",""]
[null,null,null,"","ED_QUO441_00110",""]
[null,null,null,"","ED_QUO441_00111",""]
[null,null,null,"","ED_QUO441_00112",""]
[null,null,null,"","ED_QUO441_00113",""]
[null,null,null,"","ED_QUO441_00114",""]
[null,null,null,"","ED_QUO441_00115",""]
[null,null,null,"","ED_QUO441_00116",""]
[null,null,null,"","ED_QUO441_00117",""]
[null,null,null,"","ED_QUO441_00118",""]
[null,null,null,"","ED_QUO441_00119",""]
[null,null,null,"","ED_QUO441_00120",""]
[null,null,null,"","ED_QUO441_00121",""]
[null,null,null,"","ED_QUO441_00122",""]
[null,null,null,"","ED_QUO441_00123",""]
[null,null,null,"","ED_QUO441_00124",""]
[null,null,null,"","ED_QUO441_00125",""]
[null,null,null,"","ED_QUO441_00126",""]
[null,null,null,"","ED_QUO441_00127",""]
[null,null,null,"","ED_QUO441_00128",""]
[null,null,null,"","ED_QUO441_00129",""]
[null,null,null,"","ED_QUO441_00130",""]
[null,null,null,"","ED_QUO441_00131",""]
[null,null,null,"","ED_QUO441_00132",""]
[null,null,null,"","ED_QUO441_00133",""]
[null,null,null,"","ED_QUO441_00134",""]
[null,null,null,"","ED_QUO441_00135",""]
[null,null,null,"","ED_QUO441_00136",""]
[null,null,null,"","ED_QUO441_00137",""]
[null,null,null,"","ED_QUO441_00138",""]
[null,null,null,"","ED_QUO441_00139",""]
[null,null,null,"","ED_QUO441_00140",""]
[null,null,null,"","ED_QUO441_00141",""]
[null,null,null,"","ED_QUO441_00142",""]
[null,null,null,"","ED_QUO441_00143",""]
[null,null,null,"","ED_QUO441_00144",""]
[null,null,null,"","ED_QUO441_00145",""]
[null,null,null,"","ED_QUO441_00146",""]
[null,null,null,"","ED_QUO441_00147",""]
[null,null,null,"","ED_QUO441_00148",""]
[null,null,null,"","ED_QUO441_00149",""]
[null,null,null,"","ED_QUO441_00150",""]
[null,null,null,"","ED_QUO441_00151",""]
[null,null,null,"","ED_QUO441_00152",""]
[null,null,null,"","ED_QUO441_00153",""]
[null,null,null,"","ED_QUO441_00154",""]
[null,null,null,"","ED_QUO441_00155",""]
[null,null,null,"","ED_QUO441_00156",""]
[null,null,null,"","ED_QUO441_00157",""]
[null,null,null,"","ED_QUO441_00158",""]
[null,null,null,"","ED_QUO441_00159",""]
[null,null,null,"","ED_QUO441_00160",""]
[null,null,null,"","ED_QUO441_00161",""]
[null,null,null,"","ED_QUO441_00162",""]
[null,null,null,"","ED_QUO441_00163",""]
[null,null,null,"","ED_QUO441_00164",""]
[null,null,null,"","ED_QUO441_00165",""]
[null,null,null,"","ED_QUO441_00166",""]
[null,null,null,"","ED_QUO441_00167",""]
[null,null,null,"","ED_QUO441_00168",""]
[null,null,null,"","ED_QUO441_00169",""]
[null,null,null,"","ED_QUO441_00170",""]
[null,null,null,"","ED_QUO441_00171",""]
[null,null,null,"","ED_QUO441_00172",""]
[null,null,null,"","ED_QUO441_00173",""]
[null,null,null,"","ED_QUO441_00174",""]
[null,null,null,"","ED_QUO441_00175",""]
[null,null,null,"","ED_QUO441_00176",""]
[null,null,null,"","ED_QUO441_00177",""]
[null,null,null,"","ED_QUO441_00178",""]
[null,null,null,"","ED_QUO441_00179",""]
[null,null,null,"","ED_QUO441_00180",""]
[null,null,null,"","ED_QUO441_00181",""]
[null,null,null,"","ED_QUO441_00182",""]
[null,null,null,"","ED_QUO441_00183",""]
[null,null,null,"","ED_QUO441_00184",""]
[null,null,null,"","ED_QUO441_00185",""]
[null,null,null,"","ED_QUO441_00186",""]
[null,null,null,"","ED_QUO441_00187",""]
[null,null,null,"","ED_QUO441_00188",""]
[null,null,null,"","ED_QUO441_00189",""]
[null,null,null,"","ED_QUO441_00190",""]
[null,null,null,"","ED_QUO441_00191",""]
[null,null,null,"","ED_QUO441_00192",""]
[null,null,null,"","ED_QUO441_00193",""]
[null,null,null,"","ED_QUO441_00194",""]
[null,null,null,"","ED_QUO441_00195",""]
[null,null,null,"","ED_QUO441_00196",""]
[null,null,null,"","ED_QUO441_00197",""]
[null,null,null,"","ED_QUO441_00198",""]
[null,null,null,"","ED_QUO441_00199",""]
[null,null,null,"","ED_QUO441_00200",""]
[null,null,null,"","ED_QUO441_00201",""]
[null,null,null,"","ED_QUO441_00202",""]
[null,null,null,"","ED_QUO441_00203",""]
[null,null,null,"","ED_QUO441_00204",""]
[null,null,null,"","ED_QUO441_00205",""]
[null,null,null,"","ED_QUO441_00206",""]
[null,null,null,"","ED_QUO441_00207",""]
[null,null,null,"","ED_QUO441_00208",""]
[null,null,null,"","ED_QUO441_00209",""]
[null,null,null,"","ED_QUO441_00210",""]
[null,null,null,"","ED_QUO441_00211",""]
[null,null,null,"","ED_QUO441_00212",""]
[null,null,null,"","ED_QUO441_00213",""]
[null,null,null,"","ED_QUO441_00214",""]
[null,null,null,"","ED_QUO441_00215",""]
[null,null,null,"","ED_QUO441_00216",""]
[null,null,null,"","ED_QUO441_00217",""]
[null,null,null,"","ED_QUO441_00218",""]
[null,null,null,"","ED_QUO441_00219",""]
[null,null,null,"","ED_QUO441_00220",""]
[null,null,null,"","ED_QUO441_00221",""]
[null,null,null,"","ED_QUO441_00222",""]
[null,null,null,"","ED_QUO441_00223",""]
[null,null,null,"","ED_QUO441_00224",""]
[null,null,null,"","ED_QUO441_00225",""]
[null,null,null,"","ED_QUO441_00226",""]
[null,null,null,"","ED_QUO441_00227",""]
[null,null,null,"","ED_QUO441_00228",""]
[null,null,null,"","ED_QUO441_00229",""]
[null,null,null,"","ED_QUO441_00230",""]
[null,null,null,"","ED_QUO441_00231",""]
[null,null,null,"","ED_QUO441_00232",""]
[null,null,null,"","ED_QUO441_00233",""]
[null,null,null,"","ED_QUO441_00234",""]
[null,null,null,"","ED_QUO441_00235",""]
[null,null,null,"","ED_QUO441_00236",""]
[null,null,null,"","ED_QUO441_00237",""]
[null,null,null,"","ED_QUO441_00238",""]
[null,null,null,"","ED_QUO441_00239",""]
[null,null,null,"","ED_QUO441_00240",""]
[null,null,null,"","ED_QUO441_00241",""]
[null,null,null,"","ED_QUO441_00242",""]
[null,null,null,"","ED_QUO441_00243",""]
[null,null,null,"","ED_QUO441_00244",""]
[null,null,null,"","ED_QUO441_00245",""]
[null,null,null,"","ED_QUO441_00246",""]
[null,null,null,"","ED_QUO441_00247",""]
[null,null,null,"","ED_QUO441_00248",""]
[null,null,null,"","ED_QUO441_00249",""]
[null,null,null,"","ED_QUO441_00250",""]
[null,null,null,"","ED_QUO441_00251",""]
[null,null,null,"","ED_QUO441_00252",""]
[null,null,null,"","ED_QUO441_00253",""]
[null,null,null,"","ED_QUO441_00254",""]
[null,null,null,"","ED_QUO441_00255",""]
[null,null,null,"","ED_QUO441_00256",""]
[null,null,null,"","ED_QUO441_00257",""]
[null,null,null,"","ED_QUO441_00258",""]
[null,null,null,"","ED_QUO441_00259",""]
[null,null,null,"","ED_QUO441_00260",""]
[null,null,null,"","ED_QUO441_00261",""]
[null,null,null,"","ED_QUO441_00262",""]
[null,null,null,"","ED_QUO441_00263",""]
[null,null,null,"","ED_QUO441_00264",""]
[null,null,null,"","ED_QUO441_00265",""]
[null,null,null,"","ED_QUO441_00266",""]
[null,null,null,"","ED_QUO441_00267",""]
[null,null,null,"","ED_QUO441_00268",""]
[null,null,null,"","ED_QUO441_00269",""]
[null,null,null,"","ED_QUO441_00270",""]
[null,null,null,"","ED_QUO441_00271",""]
[null,null,null,"","ED_QUO441_00272",""]
[null,null,null,"","ED_QUO441_00273",""]
[null,null,null,"","ED_QUO441_00274",""]
[null,null,null,"","ED_QUO441_00275",""]
[null,null,null,"","ED_QUO441_00276",""]
[null,null,null,"","ED_QUO441_00277",""]
[null,null,null,"","ED_QUO441_00278",""]
[null,null,null,"","ED_QUO441_00279",""]
[null,null,null,"","ED_QUO441_00280",""]
[null,null,null,"","ED_QUO441_00281",""]
[null,null,null,"","ED_QUO441_00282",""]
[null,null,null,"","ED_QUO441_00283",""]
[null,null,null,"","ED_QUO441_00284",""]
[null,null,null,"","ED_QUO441_00285",""]
[null,null,null,"","ED_QUO441_00286",""]
[null,null,null,"","ED_QUO441_00287",""]
[null,null,null,"","ED_QUO441_00288",""]
[null,null,null,"","ED_QUO441_00289",""]
[null,null,null,"","ED_QUO441_00290",""]
[null,null,null,"","ED_QUO441_00291",""]
[null,null,null,"","ED_QUO441_00292",""]
[null,null,null,"","ED_QUO441_00293",""]
[null,null,null,"","ED_QUO441_00294",""]
[null,null,null,"","ED_QUO441_00295",""]
[null,null,null,"","ED_QUO441_00296",""]
[null,null,null,"","ED_QUO441_00297",""]
[null,null,null,"","ED_QUO441_00298",""]
[null,null,null,"","ED_QUO441_00299",""]
[null,null,null,"","ED_QUO441_00300",""]
[null,null,null,"","ED_QUO441_00301",""]
[null,null,null,"","ED_QUO441_00302",""]
[null,null,null,"","ED_QUO441_00303",""]
[null,null,null,"","ED_QUO441_00304",""]
[null,null,null,"","ED_QUO441_00305",""]
[null,null,null,"","ED_QUO441_00306",""]
[null,null,null,"","ED_QUO441_00307",""]
[null,null,null,"","ED_QUO441_00308",""]
[null,null,null,"","ED_QUO441_00309",""]
[null,null,null,"","ED_QUO441_00310",""]
[null,null,null,"","ED_QUO441_00311",""]
[null,null,null,"","ED_QUO441_00312",""]
[null,null,null,"","ED_QUO441_00313",""]
[null,null,null,"","ED_QUO441_00314",""]
[null,null,null,"","ED_QUO441_00315",""]
[null,null,null,"","ED_QUO441_00316",""]
[null,null,null,"","ED_QUO441_00317",""]
[null,null,null,"","ED_QUO441_00318",""]
[null,null,null,"","ED_QUO441_00319",""]
[null,null,null,"","ED_QUO441_00320",""]
[null,null,null,"","ED_QUO441_00321",""]
[null,null,null,"","ED_QUO441_00322",""]
[null,null,null,"","ED_QUO441_00323",""]
[null,null,null,"","ED_QUO441_00324",""]
[null,null,null,"","ED_QUO441_00325",""]
[null,null,null,"","ED_QUO441_00326",""]
[null,null,null,"","ED_QUO441_00327",""]
[null,null,null,"","ED_QUO441_00328",""]
[null,null,null,"","ED_QUO441_00329",""]
[null,null,null,"","ED_QUO441_00330",""]
[null,null,null,"","ED_QUO441_00331",""]
[null,null,null,"","ED_QUO441_00332",""]
[null,null,null,"","ED_QUO441_00333",""]
[null,null,null,"","ED_QUO441_00334",""]
[null,null,null,"","ED_QUO441_00335",""]
[null,null,null,"","ED_QUO441_00336",""]
[null,null,null,"","ED_QUO441_00337",""]
[null,null,null,"","ED_QUO441_00338",""]
[null,null,null,"","ED_QUO441_00339",""]
[null,null,null,"","ED_QUO441_00340",""]
[null,null,null,"","ED_QUO441_00341",""]
[null,null,null,"","ED_QUO441_00342",""]
[null,null,null,"","ED_QUO441_00343",""]
[null,null,null,"","ED_QUO441_00344",""]
[null,null,null,"","ED_QUO441_00345",""]
[null,null,null,"","ED_QUO441_00346",""]
[null,null,null,"","ED_QUO441_00347",""]
[null,null,null,"","ED_QUO441_00348",""]
[null,null,null,"","ED_QUO441_00349",""]
[null,null,null,"","ED_QUO441_00350",""]
[null,null,null,"","ED_QUO441_00351",""]
[null,null,null,"","ED_QUO441_00352",""]
[null,null,null,"","ED_QUO441_00353",""]
[null,null,null,"","ED_QUO441_00354",""]
[null,null,null,"","ED_QUO441_00355",""]
[null,null,null,"","ED_QUO441_00356",""]
[null,null,null,"","ED_QUO441_00357",""]
[null,null,null,"","ED_QUO441_00358",""]
[null,null,null,"","ED_QUO441_00359",""]
[null,null,null,"","ED_QUO441_00360",""]
[null,null,null,"","ED_QUO441_00361",""]
[null,null,null,"","ED_QUO441_00362",""]
[null,null,null,"","ED_QUO441_00363",""]
[null,null,null,"","ED_QUO441_00364",""]
[null,null,null,"","ED_QUO441_00365",""]
[null,null,null,"","ED_QUO441_00366",""]
[null,null,null,"","ED_QUO441_00367",""]
[null,null,null,"","ED_QUO441_00368",""]
[null,null,null,"","ED_QUO441_00369",""]
[null,null,null,"","ED_QUO441_00370",""]
[null,null,null,"","ED_QUO441_00371",""]
[null,null,null,"","ED_QUO441_00372",""]
[null,null,null,"","ED_QUO441_00373",""]
[null,null,null,"","ED_QUO441_00374",""]
[null,null,null,"","ED_QUO441_00375",""]
[null,null,null,"","ED_QUO441_00376",""]
[null,null,null,"","ED_QUO441_00377",""]
[null,null,null,"","ED_QUO441_00378",""]
[null,null,null,"","ED_QUO441_00379",""]
[null,null,null,"","ED_QUO441_00380",""]
[null,null,null,"","ED_QUO441_00381",""]
[null,null,null,"","ED_QUO441_00382",""]
[null,null,null,"","ED_QUO441_00383",""]
[null,null,null,"","ED_QUO441_00384",""]
[null,null,null,"","ED_QUO441_00385",""]
[null,null,null,"","ED_QUO441_00386",""]
[null,null,null,"","ED_QUO441_00387",""]
[null,null,null,"","ED_QUO441_00388",""]
[null,null,null,"","ED_QUO441_00389",""]
[null,null,null,"","ED_QUO441_00390",""]
[null,null,null,"","ED_QUO441_00391",""]
[null,null,null,"","ED_QUO441_00392",""]
[null,null,null,"","ED_QUO441_00393",""]
[null,null,null,"","ED_QUO441_00394",""]
[null,null,null,"","ED_QUO441_00395",""]
[null,null,null,"","ED_QUO441_00396",""]
[null,null,null,"","ED_QUO441_00397",""]
[null,null,null,"","ED_QUO441_00398",""]
[null,null,null,"","ED_QUO441_00399",""]
[null,null,null,"","ED_QUO441_00400",""]
[null,null,null,"","ED_QUO441_00401",""]
[null,null,null,"","ED_QUO441_00402",""]
[null,null,null,"","ED_QUO441_00403",""]
[null,null,null,"","ED_QUO441_00404",""]
[null,null,null,"","ED_QUO441_00405",""]
[null,null,null,"","ED_QUO441_00406",""]
[null,null,null,"","ED_QUO441_00407",""]
[null,null,null,"","ED_QUO441_00408",""]
[null,null,null,"","ED_QUO441_00409",""]
[null,null,null,"","ED_QUO441_00410",""]
[null,null,null,"","ED_QUO441_00411",""]
[null,null,null,"","ED_QUO441_00412",""]
[null,null,null,"","ED_QUO441_00413",""]
[null,null,null,"","ED_QUO441_00414",""]
[null,null,null,"","ED_QUO441_00415",""]
[null,null,null,"","ED_QUO441_00416",""]
[null,null,null,"","ED_QUO441_00417",""]
[null,null,null,"","ED_QUO441_00418",""]
[null,null,null,"","ED_QUO441_00419",""]
[null,null,null,"","ED_QUO441_00420",""]
[null,null,null,"","ED_QUO441_00421",""]
[null,null,null,"","ED_QUO441_00422",""]
[null,null,null,"","ED_QUO441_00423",""]
[null,null,null,"","ED_QUO441_00424",""]
[null,null,null,"","ED_QUO441_00425",""]
[null,null,null,"","ED_QUO441_00426",""]
[null,null,null,"","ED_QUO441_00427",""]
[null,null,null,"","ED_QUO441_00428",""]
[null,null,null,"","ED_QUO441_00429",""]
[null,null,null,"","ED_QUO441_00430",""]
[null,null,null,"","ED_QUO441_00431",""]
[null,null,null,"","ED_QUO441_00432",""]
[null,null,null,"","ED_QUO441_00433",""]
[null,null,null,"","ED_QUO441_00434",""]
[null,null,null,"","ED_QUO441_00435",""]
[null,null,null,"","ED_QUO441_00436",""]
[null,null,null,"","ED_QUO441_00437",""]
[null,null,null,"","ED_QUO441_00438",""]
[null,null,null,"","ED_QUO441_00439",""]
[null,null,null,"","ED_QUO441_00440",""]
[null,null,null,"","ED_QUO441_00441",""]
[null,null,null,"","ED_QUO441_00442",""]
[null,null,null,"","ED_QUO441_00443",""]
[null,null,null,"","ED_QUO441_00444",""]
[null,null,null,"","ED_QUO441_00445",""]
[null,null,null,"","ED_QUO441_00446",""]
[null,null,null,"","ED_QUO441_00447",""]
[null,null,null,"","ED_QUO441_00448",""]
[null,null,null,"","ED_QUO441_00449",""]
[null,null,null,"","ED_QUO441_00450",""]
[null,null,null,"","ED_QUO441_00451",""]
[null,null,null,"","ED_QUO441_00452",""]
[null,null,null,"","ED_QUO441_00453",""]
[null,null,null,"","ED_QUO441_00454",""]
[null,null,null,"","ED_QUO441_00455",""]
[null,null,null,"","ED_QUO441_00456",""]
[null,null,null,"","ED_QUO441_00457",""]
[null,null,null,"","ED_QUO441_00458",""]
[null,null,null,"","ED_QUO441_00459",""]
[null,null,null,"","ED_QUO441_00460",""]
[null,null,null,"","ED_QUO441_00461",""]
[null,null,null,"","ED_QUO441_00462",""]
[null,null,null,"","ED_QUO441_00463",""]
[null,null,null,"","ED_QUO441_00464",""]
[null,null,null,"","ED_QUO441_00465",""]
[null,null,null,"","ED_QUO441_00466",""]
[null,null,null,"","ED_QUO441_00467",""]
[null,null,null,"","ED_QUO441_00468",""]
[null,null,null,"","ED_QUO441_00469",""]
[null,null,null,"","ED_QUO441_00470",""]
[null,null,null,"","ED_QUO441_00471",""]
[null,null,null,"","ED_QUO441_00472",""]
[null,null,null,"","ED_QUO441_00473",""]

{"sheet":"5.2 Asset Age Profile","index":21,"n_rows":146,"n_cols":112,"rows_kept":146,"cut":false,"hidden":false,"merged":[[8,3,8,4]]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"5.2 ASSET AGE PROFILE"]
[]
[null,"There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.2.1 - ASSET AGE PROFILE"]
[null,null,null,"ECONOMIC LIFE (YEARS)",null,"INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR"]
[null,"ASSET GROUP","ASSET CATEGORY","MEAN ","STANDARD DEVIATION ",{"$f":"CRY","v":"2016-17"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(F10,4)-1)&\"-\"&MID(F10,3,2)),VALUE(LEFT(F10,4)-1))","v":"2015-16"},{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(G10,4)-1)&\"-\"&MID(G10,3,2)),VALUE(LEFT(G10,4)-1))","v":"2014-15"},"2013-14","2012-13","2011-12","2010-11","2009-10","2008-09","2007-08","2006-07","2005-06","2004-05","2003-04","2002-03","2001-02","2000-01","1999-00","1998-99","1997-98","1996-97","1995-96","1994-95","1993-94","1992-93","1991-92","1990-91","1989-90","1988-89","1987-88","1986-87","1985-86","1984-85",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(AL10,4)-1)&\"-\"&MID(AL10,3,2)),VALUE(LEFT(AL10,4)-1))","v":"1983-84"},"1982-83","1981-82","1980-81","1979-80","1978-79","1977-78","1976-77","1975-76","1974-75","1973-74","1972-73","1971-72","1970-71","1969-70","1968-69","1967-68","1966-67","1965-66","1964-65","1963-64","1962-63","1961-62","1960-61","1959-60","1958-59","1957-58","1956-57","1955-56","1954-55","1953-54","1952-53",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(BR10,4)-1)&\"-\"&MID(BR10,3,2)),VALUE(LEFT(BR10,4)-1))","v":"1951-52"},"1950-51","1949-50","1948-49","1947-48","1946-47","1945-46","1944-45","1943-44","1942-43","1941-42","1940-41","1939-40","1938-39","1937-38","1936-37","1935-36","1934-35","1933-34","1932-33","1931-32","1930-31","1929-30","1928-29","1927-28","1926-27","1925-26","1924-25","1923-24","1922-23","1921-22","1920-21",{"$f":"IF(dms_RPT=\"financial\",(VALUE(LEFT(CX10,4)-1)&\"-\"&MID(CX10,3,2)),VALUE(LEFT(CX10,4)-1))","v":"1919-20"},"1918-19","1917-18","1916-17","1915-16","1914-15","1913-14","1912-13","1911-12","1910-11"]
[null,"POLES BY: \nHIGHEST OPERATING VOLTAGE ; MATERIAL TYPE;  STAKING (IF WOOD)","Staking of a wooden pole"]
[null,null,"˂ = 1 kV; Wood"]
[null,null,"> 1 kV & < = 11 kV; Wood"]
[null,null,"˃ 11 kV & < = 22 kV; Wood"]
[null,null,"> 22 kV & < = 66 kV; Wood"]
[null,null,"> 66 kV & < = 132 kV; Wood"]
[null,null,"> 132 kV; Wood"]
[null,null,"˂ = 1 kV; Concrete"]
[null,null,"> 1 kV & < = 11 kV; Concrete"]
[null,null,"˃ 11 kV & < = 22 kV; Concrete"]
[null,null,"> 22 kV & < = 66 kV; Concrete"]
[null,null,"> 66 kV & < = 132 kV; Concrete"]
[null,null,"> 132 kV; Concrete"]
[null,null,"˂ = 1 kV; Steel"]
[null,null,"> 1 kV & < = 11 kV; Steel"]
[null,null,"˃ 11 kV & < = 22 kV; Steel"]
[null,null,"> 22 kV & < = 66 kV; Steel"]
[null,null,"> 66 kV & < = 132 kV; Steel"]
[null,null,"> 132 kV; Steel"]
[null,null,"Other"]
[null,"OVERHEAD CONDUCTORS BY: \nHIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV)","˂ = 1 kV",82.665946274475715,9.0920815149489123,34.096952090489587,17.555638948192641,18.41391463010428,0,0,0,0,0,0,1.1102722493138222,1.1102722493138222,0,0,0,0,2.9114076569027696,2.9114076569027696,0,0,0,48.698947440410052,52.691743443990489,3.9927960035804402,0,87.326712472879436,87.326712472879436,9.1572212145986356,112.40788815646282,265.51116647565112,261.53519462606278,477.82819588627831,506.12687642152531,208.36470403138867,271.70193335211172,223.65678228896422,35.58597262041166,65.674284743170176,66.333494109108429,13.971938097768831,197.60096142007455,871.62792058423702,951.74071866618885,543.23495707470988,331.49779041854151,312.47833303545036,697.52489417890206,1079.4363351830211,1205.6433505546397,1673.7862028410939,1742.9457500658525,4224.3300644608198,4554.758448256267,1900.1376733007119,1488.2004816438528,1301.4876055245095,1364.7948927276932,1009.768464432518,758.48746487386416,1595.1955859404104,1451.8533160249128,6910.6849049123293,19009.322303034045,12441.144685714014,178.99094054978619,85.401073449183187,39.858259272613701,71.917040693749215,57.884208911662043,0,0,1.6758905533927164,1.6758905533927164,0,4.6847710189889504,4.6847710189889504,0.34124260862186895,52.82887249044137,52.487629881819501,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV",81.847575238913265,9.0469649738966744,34.329602995216355,275.14652112410658,280.16853728279546,0,0,0,0,3.1826840017028144,3.1826840017028144,0,0,0,1.5126012848110687E-2,1.5126012848110687E-2,0,4.6772210194356142E-3,3.2835890487599335,3.2789118277404978,0,1.5558156089308115,75.935742621109981,74.379927012179166,0,10.990944707418308,25.880148256265048,14.889203548846742,0,118.0104688353106,220.1311336306305,224.06260773714035,419.84186508554427,351.89961311539383,281.37968267824817,302.73674833341681,80.725321882663138,5.6256625009632844,65.36221990155228,72.079119042004123,56.090108945497526,161.03342165870578,661.31548303487489,674.85362931719726,238.35280218848408,323.2354090116819,491.60235843966149,644.02843916782376,1131.6227340067821,1001.9073596653418,1104.6808415880123,1115.8271939596448,2125.0333520287845,2573.7188246251349,1296.2914807295651,825.7277371532706,864.68876337877407,1535.1996929200454,1302.9247945324187,950.86534638334126,1668.9265638224881,1462.4422369133549,5363.4111681363183,11266.885431664983,6279.4883989506416,44.670244081879154,2.940113125691636,0,11.07817288061838,11.07817288061838,0,0,0,0,0,1.0015249418796617,1.0015249418796617,0,4.1735202942656251E-2,4.1735202942656251E-2,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV  ; SWER",80.451455233398605,8.9694735204134819,2.3693038053112976,19.237936880732743,52.975203031575639,0,0,0,0,0,0,4.1827324870687875E-2,4.1827324870687875E-2,0,0,0,0,0,0,0,0,0,0,5.7662981987913353,5.7662981987913353,0,0,0,25.16770691686062,69.089997550325577,429.89258794933363,392.43045727179839,20.585949243195621,54.11665564070411,58.420885824404664,158.88150359312036,140.45148412215386,12.554844674660153,63.315766233878421,50.760921559218268,21.90420861748796,24.03467343642496,331.76489909737973,442.48584268376067,468.14386386033152,561.55495735154636,609.54454272556563,511.1374684039539,1672.3227837740353,1970.4211060133791,976.51972642505643,929.42038670542274,2834.1494160204948,3196.2052871306732,1400.5960481658585,1027.222701293344,993.46426834931719,1010.4318147959955,823.03319847323951,880.82916016853346,3109.5305597428455,2687.3533818178344,337.40308276177518,537.46405851327984,200.31752882765414,0.13328852689366624,0.63944877145568191,0.63944877145568191,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Single-Phase",0,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV ; Multiple-Phase",0,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV",86.354264324069888,9.2926995175820615,80.5240502318117,41.982913690916348,30.096214235998296,11.048017640347346,11.048017640347346,4.5125130546012073,38.689674361493438,42.490068255093952,8.3129069482017197,104.48544171659769,114.9875993016997,16.159801137455933,40.202272577490945,51.117859140869228,16.573230115732194,0,2.6153542495689122,2.6153542495689122,53.401541121344891,53.401541121344891,0,0,0,17.022062992669625,31.715671898173284,27.117897515802309,127.11231311520305,141.16194714690241,46.383883195325524,29.764213257851399,11.421614815651452,59.777162590185206,83.359407517408343,39.058698613786426,13.909091575435736,125.08757169174311,266.79207246752765,141.70450077578454,164.33359579445874,295.38493584664081,137.81973983639847,27.429663551322818,281.04370304665389,390.96861251519954,413.0516734561881,423.79286053077641,209.37255622884683,210.535949414904,230.28636522829268,423.13487201658188,913.04553809590993,1203.7412410999573,787.94316482883903,459.89675478961652,588.44760990461157,670.1975080426746,593.29276685359696,267.60386298113548,327.54410393358626,450.93265103634349,378.09340759263807,568.24039001973449,608.60291792879491,698.15549888839575,709.66512071920624,467.19160145908609,298.27958644476854,83.615447700421228,0,8.41517413554139,83.302579522779624,74.887405387238246,0,0,24.632982753053856,45.719731386374903,99.926551681691279,78.839803048370229,0,0.954846627340589,0.954846627340589,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",80.710201205143278,8.9838856406981975,0,0,0,0,0,0,0,0,0,0,16.499999999999996,16.499999999999996,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV",0,0]
[null,null,"Other",null,0]
[null,"UNDERGROUND CABLES BY: \nHIGHEST OPERATING VOLTAGE","˂ = 1 kV",75.5044746310802,8.6893310807610611,242.5499999999999,426,98,138,0,112.05727377999999,126.01874943999998,89.965535209999985,100.20415332999998,30.8810027,6.6809089200000003,5.4802182500000001,12.828740419999999,7.4046089200000003,97.467264670000006,97.411177920000014,1.0997345199999999,45.626534939999999,50.087059889999999,51.565796100000014,47.971395309999998,2.1158816900000001,0.15002301000000001,14.654563150000001,14.694511390000001,0.16529307999999998,445.37655919999969,450.04304916999985,34.905064180000004,84.064992000000004,70.214387180000017,55.339312640000003,196.24855142999999,210.68918886000003,112.80521773000001,65.617734260000006,334.62136645999988,393.43111007999988,154.76273841000003,151.01947253,360.48025301000007,532.50026924999997,302.69193957000005,218.93987545000002,576.95267331000036,648.83866275000037,827.17879082112893,942.46141972922794,637.45000000000016,576.8085674742365,448.48353123653612,476.48591523715487,494.4386166763498,352.06411793868944,230.46448590583296,172.34773191913931,309.82054515198882,324.05217259741562,123.11431964052106,58.030987333951352,106.2743727350331,122.6416041044,66.930668945086552,0.93230206716342401,0.32180333100467184,0.50189903110573442,0.71339017813408179,0.52252013147388277,0,0,0.23853404335889533,0.23853404335889533,0,0,0,0,1.9303205130087335,4.6220519672926006,2.6917314542838673,0,0,0,0,0,0,0,4.0181177336731899,4.0181177336731899,0,0,0]
[null,null,"> 1 kV & < = 11 kV",73.10430680990703,8.5501056607451957,32.830000000000005,95,20.3,63,49.988045570981441,144.81751697707313,173.37034813297751,159.01637602908053,140.94603623521178,104.08103330936407,86.686402496905487,75.039761835879617,65.980208538719822,68.663929076738611,67.515001218665176,61.453233489582502,40.419508983484185,13.231311677638317,3.0881417640811484,11.696714495283979,10.915385596192262,2.312796646578009,1.6054649999999999,3.7614278057037556,5.1754628057037557,1.618844770729478,106.23193371848667,107.09906894775722,10.730447261258197,13.098977261258195,9.0399087755045873,15.930677468551114,42.986081141943409,54.751152315633838,31.78042177132264,12.368587206611164,75.126446823417183,85.116016257443547,37.129208994668105,38.434634778171436,72.200176847921966,104.78241191486595,65.519811592809447,46.650636440060296,87.55830193257799,121.0542953200445,198.41094651302097,199.35923606499873,112.17,129.39957385392614,114.7327293336551,115.89870001700329,110.79107711261173,66.113517029273893,48.750414653357005,46.717490233019731,69.704289054780929,65.73660285486865,30.796501045825419,14.210575386439812,16.342071823320943,21.962650491155639,11.972906151208839,7.1661973812421911E-2,0,0,0,0,9.5713216426946537E-2,9.5713216426946537E-2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV",74.618876401159412,8.6382218309765246,1.05,0.02,7.0000000000000007E-2,3,4.7152120331062419E-2,0.15660780965672422,0.61778714539942903,0.83561176161231276,0.6403129907149443,0.59748992626888364,0.44461581730114469,0.22285515930770317,0.63160397819651948,0.68261371078267019,0.20190279651648224,0.27195654919253448,0.32722828107685831,0.14346821271561208,0,0,0,0,0,0.15292424000000002,0.15292424000000002,0,0.57448883053671795,0.57448883053671795,7.7543678140695668E-2,0.87651997814069571,1.8129362450000002,1.0420562870398837,2.8096342039883666E-2,0,0,0,0.36199992963600386,0.36199992963600386,4.8757815000000003E-2,0.11520993982175282,0.35058800012822733,0.84090209686922079,1.3466247384887022,1.3042544066080175,1.4290766050137185,3.4589588724514937,4.1470019140572436,2.1501427067679417,0,0.8347696943020344,0.58567733633090968,1.0163270658267725,1.4354430589536549,2.8124763059188189,6.1902672369547682,5.0881561300592129,5.0821722308243746,3.8392763571315518,0,0.49343079938638512,0.49343079938638512,4.2652443557110356E-2,0.17703492012619176,0.13438247656908142,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV",96.070733371993441,9.8015679037587375,1,3.01,0.08,3,1.3918682324234448,4.7753466096574444,3.8774583224278549,1.7878146826280092,7.8050183999452711,8.6987642051629859,5.8859947941595818,8.9550905673227241,6.1636682680438399,1.8179967269935144,1.4053244310462594,0.74788643711128011,0.58169685174868524,0.32813007091897822,2.1455976292256214E-2,0.20524127129225625,0.19246683952822563,0.74626055452822571,0.73757901000000003,0,0.22185980154284216,0.74007831579492489,0.56173939835755293,0.92195947514282517,0.94918080603735466,0.65380835233652213,0.58306613733652213,5.4083710000000007E-2,8.8250607778598916E-2,9.8996146085561704E-2,0.11168231646839158,4.6853068161428792E-2,0.267032675,0.28395939165663847,0.19036271296736526,0.17343599631072681,0,1.311324691008341E-2,1.311324691008341E-2,2.0169431649999998,2.1563080720328234,1.2663646870328236,1.1269997799999998,0,0,2.486627069407616,2.486627069407616,4,4.7107137443719962,1.9441468221760311E-2,2.6244080010383892,2.7984765716991111,3.9335948036089916,4.4867343304206484,0.75300094002206519,1.5520305155918155,2.0917843761508883,0.56554670310875932,4.099282656351054E-2,0.29687989969287387,0.25588707312936343,0.26476744896115068,1.1245746690511373,0.85980722008998667,0,0,0.61424286999999989,0.61424286999999989,0,0,0,0,1.2962653691621022,3.0348491139577756,1.7385837447956733,0,0,0,0,0,0,0,0.49277945765131903,0.49277945765131903,0,0,0]
[null,null,"> 33 kV & < = 66 kV",91.657043597942319,9.5737685159994506,0,0,6,0,0.14423267222836456,0.89500295037261546,3.3133147052262988,2.6223871369072436,0.5497152526970972,0.49477322658654438,3.6021215824740355E-2,3.6120880819188642E-2,0.25501055543455137,0.25272509233977719,1.6174485235102991E-2,9.2876333611224174E-2,7.9422232993302658E-2,5.4990028648058003,0,0,1.0373514472316054,1.0892421857881955,5.1890738556589926E-2,0,0,2.2051627370015479,3.5459985556870115,1.3984037284510213,9.4332687805817508E-2,0.75022893504474053,1.1631913919649775,0.44972723496049699,6.3654952445741805E-2,6.5500320554940747E-2,1.8453681091989528E-3,7.2889719999999991E-2,7.2889719999999991E-2,5.5479444926145725,6.0781191567385671,0.64688062912399513,0.22596066903324585,0.11676233115512215,0.48659392811793567,1.9197315405951232,1.7392225280542324,0.30806834651159959,0.14010372302759619,0.64136173547326214,0.22700000000000001,0.74208202828317804,5.2956405973292264E-2,4.7569374504960578E-2,1.4348482410434932E-2,8.644862266474429E-2,0.14129025408531085,5.4841631420566535E-2,5.9992752622256207E-3,5.9992752622256207E-3,3.0395689203145228E-3,1.5651217207490718E-2,1.2611648287176194E-2,1.3272295246865339E-2,1.3272295246865339E-2,0,0.39190387709982022,0.39190387709982022,0,1.4986868614071721E-3,1.4986868614071721E-3,0,0,0,0,0,0,0,0,0,0.28802733523258778,0.28802733523258778,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,">  132 kV",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",null,0]
[null,"SERVICE LINES BY: \nCONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY ","˂ = 11 kV ; Residential ; Simple Type",54.034350781778855,7.3508061314238766,18846,18759,13148,13315,5803,6454,7928,8539,8756,8607,8302,8357,8631,9607,11477,13145,14986,14238,11711,10625,10196,11618,14504,15997,16273,16491,15826,15392,15612,16043,16566,16276,16247,15054,12707,11648,10039,7843,6923,7564,11936,15690,15583,17652,14908,15049,10068,8741,8708,9871,9873,9841,9840,6875,5229.4818871103616,13175.591401026582,10649.073049252707,2045.3982676833448,2042.0022079409864,1017.8476199240174,1017.8476199240174,234.32812222273611,234.32812222273611,82.960887991900378,82.960887991900378,69.376649022466381,69.861800414231894,41.237868300067433,40.752716908301934,17.950601495323472,17.950601495323472,5.3366653094204928,5.3366653094204928,1.940605567061997,1.940605567061997,8.2475736600134866,8.2475736600134866,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Simple Type",null,0]
[null,null,"˂ = 11 kV ; Residential ; Complex Type",null,0]
[null,null,"˂ = 11 kV ; Commercial & Industrial ; Complex Type",51.892430093383112,7.2036400585664406,2087,2160,1958,1709,901,864,844,831,868,891,909,956,922,1349,1740,2211,2454,2137,2025,1860,2012,2191,2126,1954,1909,1980,2048,2354,2413,2354,2505,2251,1849,1836,1854,1736,1608,1305,1070,1020,1111,1213,1197,1320,1181,1402,933,943,937,1043,1045,1175,1173,781,460.4489264801561,572.03352601113011,377.43323173663583,104.85670362474306,103.83867737595915,52.428351812371531,52.428351812371531,19.342498726894355,19.342498726894355,7.6351968658793492,7.6351968658793492,6.8716771792914138,6.8716771792914138,4.0721049951356525,4.0721049951356525,2.2905590597638046,2.2905590597638046,0.76351968658793479,0.76351968658793479,0,0,2.2905590597638046,2.2905590597638046,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ; Subdivision ; Complex Type",null,0]
[null,null,"> 11 kV  & < = 22 kV ; Commercial & Industrial  ",null,0]
[null,null,"> 11 kV  & < = 22 kV ; Subdivision  ",null,0]
[null,null,"> 22 kV & < = 33 kV ; Commercial & Industrial  ",null,0]
[null,null,"> 22 kV & < = 33 kV ; Subdivision  ",null,0]
[null,null,"> 33 kV & < = 66 kV ; Commercial & Industrial  ",null,0]
[null,null,"> 33 kV & < = 66 kV ; Subdivision  ",null,0]
[null,null,"> 66 kV & < = 132 kV ; Commercial & Industrial  ",null,0]
[null,null,"> 66 kV & < = 132 kV ; Subdivision  ",null,0]
[null,null,"> 132 kV ; Commercial & Industrial  ",null,0]
[null,null,"> 132 kV ; Subdivision  ",null,0]
[null,null,"Other",null,0]
[null,"TRANSFORMERS BY: \nMOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV)","Pole Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",62.736842874997393,7.9206592449743347,555,464,537,299,209,311,347,364,381,405,439,455,438,419,463,506,592,659,582,552,589,728,1014,1020,825,958,1231,1150,914,930,963,1040,1046,1034,1089,1098,988,874,762,687,693,931,863,605,576,649,959,928,589,509,652,837,701,491,511,478,575,520,510,407,145,318,202,17,9,3,4,2,1,1,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",70.983357658427551,8.4251621740134794,13,13,9,18,68,129,129,181,349,448,469,480,478,444,336,460,479,247,206,176,137,141,184,198,173,175,230,258,228,225,215,230,249,245,294,276,216,191,282,286,147,149,166,144,130,160,153,122,116,141,153,181,156,78,64,50,142,131,36,56,101,293,219,9,14,7,14,14,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",63.488844224861396,7.9679887189215695,0,0,0,0,0,0,0,0,1,1,1,1,1,1,1,1,1,1,1,1,0,0,0,1,1,0,0,1,2,2,1,0,0,0,2,3,2,1,4,8,5,2,4,2,0,4,29,26,1,2,6,8,6,4,13,11,6,6,6,8,7,13,8,1,1,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",56.288450989248751,7.5025629613651859,185,138,175,60,23,29,26,23,12,2,2,2,0,1,0,1,3,3,7,36,37,45,69,63,62,69,81,99,85,61,65,70,70,60,76,84,75,70,52,54,56,54,49,54,51,40,44,30,36,35,35,38,31,21,27,20,20,14,10,10,27,56,32,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",56.119475301151887,7.4912932996347088,456,345,366,220,189,270,333,276,101,13,20,18,5,7,8,6,1,0,10,34,37,47,60,42,53,53,64,62,68,80,76,63,70,64,61,62,56,51,66,76,55,50,45,31,32,32,26,27,19,19,20,38,39,21,7,7,36,28,5,8,32,76,45,1,2,1,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",60.901168439510066,7.8039200687545529,1,0,0,0,0,0,1,1,0,0,0,0,0,0,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,0,0,0,1,1,1,0,0,0,1,4,0,0,0,0,0,1,2,1,1,1,0,0,1,2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA ; Single Phase",70.346168863272183,8.3872622984661795,3,1,4,0,1,2,2,1,4,8,9,10,7,6,8,5,3,7,8,8,9,9,10,12,14,16,17,14,19,31,25,8,4,2,1,1,1,1,1,1,0,0,0,1,1,0,2,2,0,0,0,1,1,2,2,1,2,2,0,0,2,3,2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA ; Single Phase",73.172787834092503,8.5541094120950145,0,0,0,0,13,27,41,134,263,241,210,253,263,238,218,172,153,167,171,143,115,163,229,233,199,243,321,347,305,277,341,374,304,190,162,158,132,134,201,268,230,188,149,86,48,43,38,21,6,17,30,79,80,32,31,22,69,63,9,16,50,104,63,4,6,2,5,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA ; Single Phase",73.899132885752039,8.5964604859065137,0,0,0,0,2,1,0,11,33,39,40,53,60,61,50,38,40,48,53,36,20,23,27,31,25,18,28,35,34,27,27,28,15,10,17,14,9,10,17,22,11,3,8,9,17,17,7,5,5,4,7,12,8,5,23,23,15,17,4,5,21,33,12,1,2,1,6,6,0,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  < = 60 kVA  ; Multiple Phase",62.592871509869134,7.9115656800578442,1,5,3,6,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,0,0,1,2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 60 kVA and < = 600 kVA  ; Multiple Phase",56.293446592310538,7.5028958804124786,159,239,211,193,82,161,237,174,46,21,31,22,16,5,7,7,2,2,2,23,23,28,52,47,56,61,41,32,34,33,43,49,41,21,27,28,22,24,18,20,24,25,20,16,9,3,11,7,2,4,7,14,15,3,6,6,15,16,2,5,11,22,14,1,1,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted ; < = 22kV ;  > 600 kVA  ; Multiple Phase",61.282287858587274,7.8283004450894245,61,60,59,38,23,33,41,28,6,6,7,3,1,1,2,2,3,1,0,5,5,3,6,5,4,4,4,4,0,2,2,3,2,1,1,4,4,3,0,3,2,0,0,0,2,2,1,1,0,2,2,2,3,1,4,4,2,2,0,0,3,5,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ;  < = 60 kVA ; Single Phase",63.488844224861396,7.9679887189215695,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,2,1,0,0,0,0,0,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,1,1,1,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Single Phase",100.42028053865567,10.020991993742719,0,0,0,0,0,0,0,1,2,1,2,2,1,1,1,2,3,5,4,4,2,1,1,1,2,3,2,2,3,5,7,9,9,7,15,17,8,4,2,3,6,25,27,12,20,21,17,17,17,17,14,14,10,5,4,3,5,4,1,3,5,6,3,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Single Phase",63.488844224861396,7.9679887189215695,0,0,0,0,0,0,0,0,0,0,0,0,0,1,2,2,2,1,1,2,2,4,5,4,3,3,2,5,5,4,8,7,6,7,9,9,8,7,3,3,4,7,7,5,3,1,5,6,4,5,4,2,0,0,7,8,2,2,0,0,2,2,0,0,1,1,2,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  < = 60 kVA ; Multiple Phase",null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  > 60 kVA  and < = 600 kVA ; Multiple Phase",67.387405076563454,8.2089831938287858,0,0,0,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,1,0,0,0,0,0,0,0,0,2,0,0,0,0,0,0,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase",63.486269170996785,7.9678271298388985,0,0,0,0,0,0,0,0,0,0,3,0,0,0,0,1,0,2,0,0,0,0,0,0,0,3,0,0,4,2,0,8,0,5,1,2,1,3,2,4,0,2,2,1,1,10,5,2,1,5,3,2,6,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA",63.203889771067786,7.950087406504899,7,5,6,2,7,11,6,7,4,3,5,3,2,6,5,9,14,6,3,4,3,5,2,2,1,16,4,5,11,39,4,9,1,11,19,2,4,5,3,2,8,7,15,2,4,1,5,21,4,1,15,11,1,7,10,7,3,1,5,5,9,9,5,2,1,5,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 15 MVA and < = 40 MVA",63.488844224861396,7.9679887189215695,0,0,0,1,0,0,0,0,0,0,0,1,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  > 40 MVA",null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA",76.732622485572577,8.7597158906880406,0,2,0,1,0,0,4,3,0,4,0,0,0,1,0,0,6,1,1,0,0,0,0,0,0,4,1,2,1,2,5,0,0,9,0,0,1,0,5,5,0,0,3,0,0,3,0,11,7,5,7,5,5,18,5,14,5,0,2,5,0,2,5,2,0,2,1,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA",63.626357107966321,7.9766131351574474,1,0,2,5,1,8,4,4,4,2,4,2,5,2,5,4,4,0,1,0,0,2,0,3,0,1,5,1,3,0,1,4,0,2,4,2,0,4,1,4,0,0,0,0,1,4,0,5,6,4,3,0,0,0,0,0,0,0,0,0,3,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 40 MVA",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  < = 100 MVA",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ;  > 100 MVA",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  < = 100 MVA",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 132 kV ;  > 100 MVA",null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Other",null,0]
[null,"SWITCHGEAR BY: \nHIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION","˂ = 11 kV ;  Fuse",null,0]
[null,null,"˂ = 11 kV  ; Switch",63.985236102658867,7.9990772031940578,7,7,0,20,37,17,5,5,13,16,4,1,2,2,0,3,0,0,1,0,4,12,0,0,0,6,11,4,10,5,19,0,10,42,22,14,28,23,4,44,30,29,6,8,78,45,109,147,85,84,119,148,39,45,11,9,0,3,5,65,3,37,0,0,3,0,3,0,0,0,0,0,0,0,0,8,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ;  Circuit Breaker",62.40011671517788,7.8993744508776063,7,20,27,28,65,135,34,21,32,13,32,13,14,17,30,31,10,4,32,11,10,0,0,6,4,9,20,28,0,26,0,31,0,0,4,0,0,0,0,0,2,11,0,0,0,38,42,45,37,13,75,64,1,81,20,21,14,0,1,39,2,10,0,0,8,0,7,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Switch",61.028060333074343,7.8120458481165063,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 11 kV & < = 22 kV  ; Circuit Breaker"]
[null,null,"> 22 kV & < = 33 kV ; Switch",65.894103079455661,8.1175182832843475,4,9,9,60,42,35,33,40,4,6,14,20,21,19,6,7,9,4,0,0,0,9,0,0,3,21,21,4,6,0,10,3,3,15,4,3,11,22,13,6,5,9,3,16,49,18,6,23,78,40,71,71,32,16,4,3,0,0,7,26,24,34,8,1,1,0,1,0,0,0,0,0,0,0,0,4,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker",65.714643594399092,8.1064569075767672,0,11,1,14,18,19,13,10,3,4,7,7,11,7,7,2,0,3,0,0,0,0,0,0,0,0,0,10,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,20,17,0,5,0,2,0,9,0,3,27,0,0,0,19,0,0,3,0,0,0,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Switch",71.918922728729953,8.480502504494055,5,6,35,58,73,74,80,70,19,24,18,22,12,7,20,20,12,3,2,9,1,12,0,0,0,17,12,0,2,25,9,4,21,1,5,0,0,7,4,10,18,6,3,0,12,20,86,76,38,49,31,73,35,65,22,25,4,0,30,33,0,40,15,10,13,0,0,0,0,0,0,0,0,0,0,0,8,0,0,6,15,0,0,0,6,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker",59.115756641818791,7.6886771711276047,5,7,10,11,14,40,40,30,15,24,16,19,11,2,15,10,8,6,2,7,1,1,1,0,0,2,8,0,13,6,4,2,12,11,0,10,0,0,0,0,0,0,0,0,2,9,11,24,6,6,3,0,15,12,0,0,0,0,2,6,0,0,3,8,0,8,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV ; Switch",null,0]
[null,null,"> 66 kV & < = 132 kV  ; Circuit Breaker",null,0]
[null,null,"> 132 kV ; Switch",null,0]
[null,null,"> 132 kV ; Circuit Breaker",null,0]
[null,null,"Other",null,0]
[null,"PUBLIC LIGHTING BY: \nASSET TYPE ; LIGHTING OBLIGATION","Luminaires ;  Major Road"]
[null,null,"Luminaires ;  Minor Road"]
[null,null,"Brackets ; Major Road"]
[null,null,"Brackets ; Minor Road"]
[null,null,"Lamps ; Major Road"]
[null,null,"Lamps ; Minor Road"]
[null,null,"Poles / Columns ; Major Road"]
[null,null,"Poles / Columns ; Minor Road"]
[null,null,"Other"]
[null,"SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: \nFUNCTION","Field Devices",35.635583391324516,5.9695547062845913,109,172,191,209,221,241,211,155,114,80,75,63,68,72,69,58,46,40,19,19,14,6,15,35,141,214,202,188,188,168,122,103,121,121,94,85,96,103,98,93,80,82,76,69,83,111,136,150,161,147,109,99,105,104,92,80,81,81,78,80,58,35,23,6,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,1,1,1,0,1,1,1,1,1]
[null,null,"Local Network Wiring Assets"]
[null,null,"Communications Network Assets",10,3.1622776601683795,10,3.2,209,257,206,141,414,274,283,202,88,63,254,190,42,49,0,18,0,0,1,12,0,3,14,3,24,1,2,4,0,0,0,7,1,4,3,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Master Station Assets",12,3.4641016151377544,9,12,33,23,22,14,8,18,18,16,24,34,29,28,14,22,0,16,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0]
[null,null,"Communications Site Infrastructure",25,5,25,5,0,0,2,0,0,1,0,0,1,3,7,1,5,8,5,2,0,0,1,0,0,0,0,0,0,2,1,4,1,7,0,3,1,1,0,0,6,0,1,0,1,1,1,0,0,0,2,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Communications Linear Assets",32.5,5.7008771254956896,32.5,5.6970000000000001,17.89,117.51,92.930999999999997,91.674999999999997,210.8,205.9,186.56,180.26,172.8,157.9,182,161.55000000000001,153.95000000000002,169.6,90.8,82.91,26.630000000000003,25.21,23.31,24.55,8.74,1.46,2.91,4.37,4.37,7.28,26.22,4.37,7.28,5.83,5.83,2.91,2.91,11.65,8.74,10.199999999999999,2.91,5.83,17.48,17.48,13.11,8.74,1.46,0,1.46,15.95,29.13,28.63,17.05,19.91,13.11,28.25,7.28,1.46,13.11,0,7.28,0,1.46,7.28,5.83,11.65,0,0,0,0,0,0,0,0,0,8.74,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"AFLC",null,0]
[null,null,"Other",null,0]
[null,"OTHER BY: \nDNSP DEFINED","˂ = 1 kV; stobie pole",80.31030418060277,8.9616016526401552,1498.392783217952,1281.5528646860826,1396.2381063538355,1564.5162493886201,1800.4544204379863,801.75704896794275,572.09201058178269,516.84338443444688,535.62634014705782,545.44821827816509,433.50948757702008,368.55209111013903,413.59996793273461,477.82837774110186,474.8561075558265,552.54074405648851,761.18566815446923,751.77362959608274,436.86905300642923,229.45847190693047,587.41528054912294,838.4518163851186,700.45035194572824,1001.7754151268373,1706.3498779057697,2114.7767935536071,2128.2869038948352,1922.501210815162,1970.4424689858602,1478.7276674836369,1596.015435612791,1845.391665960711,2156.4798484659232,2388.2856473692373,2231.0740499483672,2295.3724774401244,2347.6761640500158,2503.5563988091303,2792.9058727646893,3376.6271357813062,3527.3471031887075,3405.2774156619794,3932.9509928242705,3725.2257886048578,3883.4295841264111,4860.7420105225829,5192.3049612061295,4888.3510493051217,4524.6647436523117,4624.0522525733786,6309.7142131932414,7302.6274820452609,7194.9814254464645,8255.4198560459172,8433.9762321566668,8631.6085680022788,8822.7298028220612,8074.4525487859119,8472.8217278131724,7949.0636203952372,7052.2939738505565,7361.1235255204647,6791.0654190619471,5777.8058854531901,6194.0112013875496,3090.9220495272857,1487.8950739416014,2190.80961974409,1017.7211403872553,628.05813122679615,602.42269235205265,603.04541048987028,549.29056887579338,462.05035081312889,640.69319971040511,925.18317544000968,1482.2835013557221,1975.8950232656869,1755.0573323312274,1187.1906343659462,1685.1720458122556,1861.513376671415,1073.6337598553589,754.96871055367194,419.94715009231089,50.314875660704502,0,0,0,0,0]
[null,null,"> 1 kV & < = 11 kV; stobie pole",82.312438200361186,9.0726202499807727,1528.3406736220418,1214.9359134885315,1728.8630713207756,1542.5512721204211,1305.6043715113881,1187.6401174238356,982.44073021374197,923.72295943978759,916.95206836893522,862.12858788824201,764.61432540980923,719.1245212340599,649.10464784321641,682.06515246366189,593.82149276698669,727.08007061007879,774.12112371535704,933.71849607010461,694.79089668938332,255.39793999836553,1245.041384076595,1561.5772025580541,1658.839497524478,1503.4654386308496,2256.3583657925806,3059.662366084206,2913.2457720729926,3657.7312928697529,4150.9370477988468,3326.3856613884454,3432.9318867106817,3964.5385103654257,4332.1765031500399,4627.804978480096,4027.2503843518425,3932.6230433290452,4515.4333062552523,4754.7429282503426,5091.5720865875737,5928.68502334815,5909.5242318986284,5494.1377199868584,5715.4377198709726,5280.4726738231657,5366.6901410719502,6782.382501228768,7497.7920820120498,7357.890089941553,7225.9694702023589,7470.9885773637743,8605.4367174291201,10143.203305890453,9376.6896481766962,9543.7535177993068,9981.288410076726,9158.1917445280324,8543.8947052664735,6956.721738618282,6205.765490446548,6065.3149312610003,7119.8207134552931,8165.1852543188033,6576.2416053095712,5771.1839520836675,6050.2158839441781,5069.4291841898012,2955.5033302064876,1430.8032229734745,526.40748640720085,530.84550100767422,504.5818485055371,569.23719206458691,631.49674497252045,365.76949327479213,394.18552581264078,660.93620837696574,965.46436712326954,1066.4486327316247,1251.8261142184631,1208.6039478107036,1651.3867209573878,1938.4003637435549,1454.4897365692414,492.13743812506669,38.449267193883621,0,0,0,0,0,0]
[null,null,"˃ 11 kV & < = 22 kV; stobie pole",71.505377452083152,8.4560852320730042,248.56749035394409,257.43174455714166,195.56830206666575,237.92790231218248,133.96084123923893,188.94418000886091,157.35937689141477,131.96001304709284,168.9502386380893,200.93911077625501,170.94819872009751,73.259394947208918,87.973342031395219,92.97182737408815,98.970009785319633,94.155338611945908,95.97235263477279,137.95819545832433,101.96910099093536,22.993032576387385,361.327486570622,699.12911614363895,720.68370219324697,362.05287125920125,648.61058566241809,990.02571781760753,982.97804920479734,1177.8966869018016,1062.8615574028718,845.78299399574166,874.29652417810667,944.35680674690616,984.31565929120598,1080.8399915211551,1333.5445840449936,1436.336954377512,1263.8282958814641,1066.2977958761742,937.87576947243633,1254.4886737556119,2103.0261135819142,3829.2806353569486,4407.3186195508315,4139.3578238448172,4216.0567411107595,4648.2535292832808,5646.1268091874599,4983.1813216243036,4093.4662068478929,4539.5086720467925,4360.9445015154615,4296.9488001670261,4143.5331627112546,5526.9043312235126,6609.5278595838936,4697.9988927427876,3834.6646450112789,3741.3611760722602,2184.1201644479511,734.6298820748666,323.90028758008026,226.94763975788715,186.241416975167,125.57207199263031,105.15103356647298,162.39939932922329,821.53625519184027,212.40618278918944,0,0,0.2242076960564876,1.6917749410688954,0,0,4.3774994772784517,34.43117248769375,0,0,13.719462750382647,38.063490860383659,31.739249221787954,18.027625420978246,42.37139162782406,16.863777007159204,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 66 kV; stobie pole",97.744437094724347,9.8865786344278046,93.836723266147573,158.649796064285,101.77534087142811,95.970918579703891,175.94668406279041,256.92214661441562,203.53459851509706,174.94698699425186,158.95183389763451,187.94304888525343,211.93577853017942,88.487776853551267,91.972130305549555,81.975159620163737,122.96273943024561,58.579913769757773,106.96758633362828,100.96940392239676,47.985459289851946,17.994547233694476,217.50475194250748,350.55280582187208,385.98238673403227,488.68933406713199,871.94292134899149,872.41325453385434,717.51759647947335,766.2512604825904,871.66060745223638,882.77849386931859,1027.9300006811416,1315.9765770413831,1249.7647857038291,733.05920622228814,485.38317047539351,454.8850313549583,589.43639206445778,519.23942904078967,380.14129609045852,669.40088765495955,1415.6005346853278,1383.5264216107157,779.37300853447141,949.39795281988927,1147.1140115857997,1149.5639074222508,1344.0723912388773,2077.514976793319,2254.132772110655,2087.2025262447296,3086.159359493633,3222.5183266118265,2450.5802796659582,2532.3147523290754,2190.2215054617095,2292.6007001856869,1892.0149475041128,1829.8830505522715,1934.964155377342,1820.1682346515395,1931.1462705051431,2352.5964136925509,2132.5918646154591,1611.6402689090842,3055.2214237232411,4726.4787345177574,2196.0843259498147,242.36288568256273,155.78259579564278,304.73162785870869,461.53888260023177,513.28470276841745,237.70047258625789,206.90126869936182,580.5971261680902,698.12255757221158,444.59487506596679,607.17250625136455,1164.6142831501529,1346.9799651598807,807.04186604113397,376.47460650613675,429.81436457263356,254.06247655048043,268.99106603222793,200.29190888011215,0,0,0,0,0]
[null,null,"> 66 kV & < = 132 kV; stobie pole",86.284285667035562,9.2889335053619355,0,0,0,0,0,0,0,0,0,0,73.871462996754474,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 132 kV; stobie pole",50,7.0710678118654755]
[null,null,"Pole REFURBISHED; STOBIE Pole",20,4.4721359549995796,4102,2676,3715,2563,3210,3005,1811,917,1232,2349,2467,430,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ;> = 22 kV & < = 33 kV ;  < = 60kVA",60.143473166537113,7.7552223157390605,44,15,29,24,6,13,17,11,8,9,12,15,12,10,12,13,12,15,17,19,19,32,29,23,26,24,30,32,27,34,27,17,10,8,9,12,10,12,18,14,11,15,13,17,18,25,26,21,24,22,19,18,14,22,16,6,9,7,5,10,8,4,3,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Pole Mounted ;> = 22 kV & < = 33 kV ; > 60 KVA AND < = 600 KVA ",55.431558518263593,7.4452373043620037,20,23,34,14,10,21,25,18,14,15,13,12,13,17,14,9,10,11,7,12,14,16,20,16,15,12,10,15,21,18,10,10,11,9,4,8,7,6,8,8,5,4,3,5,7,9,16,13,16,13,9,9,13,8,4,1,2,2,5,2,1,3,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Kiosk Mounted; > = 22 kV & < = 33 kV ; ",63.488844224861396,7.9679887189215695,3,4,3,3,1,1,1,2,3,4,4,3,2,2,1,1,1,2,2,3,2,0,0,0,0,0,0,0,1,2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,1,2,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Recloser ;SWITCHGEAR",36.318582429520603,6.0264900588585233,161,203,195,158,189,162,69,83,265,48,5,18,82,86,34,9,13,5,8,11,10,13,16,16,9,9,11,11,20,21,21,29,15,20,16,12,5,9,6,0,0,6,2,2,0,11,37,0,0,0,0]
[null,null,"Sectionalizer ;SWITCHGEAR",42.430848789884685,6.5138965903585451,18,45,7,16,14,50,35,38,33,44,33,4,0,0,21,26,12,6,7,4,1,1,1,1,2,6,6,15,18.270450751252088,15.554257095158601,9.7061769616026723,12.560934891485811,23.979966611018366,13.131886477462439,10.2771285475793,11.989983305509183,19.983305509181971,19.412353923205345,13.702838063439067,18.841402337228715,21.125208681135227,18.270450751252088,14.841402337228715,17.979966611018366,12.270450751252088,7.1318864774624391,5.9933222036727889,5.4223706176961608,4.8514190317195336,3.1385642737896502,6,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,">= 11 kV & < ≈ 22 kV  ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR",47.405342832965829,6.8851537987880729,123,259,257,301,256,399,378,450,454,417,335,553,377,289,278,153,52,25,115,84,422,0,4,0,1,457,13,39,50,25,23,265,2,1,0,1,115,1,0,0,0,100,0,2,4,4,5,4,7,10,8,10,10,10,10,7,9,9,10,9,10,3,4,0,0,0,0]
[null,null,"> 22 kV & < ≈ 33 kV  ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR",61,7.810249675906654,null,null,null,null,null,null,null,2,2]
[]
[null,null,"Pipework Switchyard Substations",null,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1,1,0,1,0,0,0,0,3,0,0,0,0,0,0,0,0,1,0,3,7,2,4,1,2,5,3,2,3,1,2,0,0,1,1,0,2,1,0,0,0,1,0,0,0,0,0,0,1,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  > 15 MVA and < = 40 MVA REFURBISHED",null,null,1,0,2,5,1,8,4,4,4,2,4,2,5,2,5,4,4,0,1,0,0,2,0,3,0,1,5,1,3,0,1,4,0,2,4,2,0,4,1,4,0,0,0,0,1,4,0,5,6,4,3,0,0,0,0,0,0,0,0,0,3,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ;  < = 15 MVA REFURBISHED",null,null,7,5,6,2,7,11,6,7,4,3,4,2,2,5,4,8,9,1,1,2,0,2,0,1,0,14,2,3,0,27,0,7,0,9,16,0,0,1,3,0,6,5,13,0,3,0,3,19,2,0,14,9,0,5,8,6,2,0,3,4,7,7,5,2,0,4,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ;  < = 15 MVA REFURBISHED",null,null,0,2,0,1,0,0,4,3,0,4,0,0,0,1,0,0,6,1,1,0,0,0,0,0,0,4,1,2,1,2,5,0,0,9,0,0,1,0,5,5,0,0,3,0,0,3,0,11,7,5,7,5,5,18,5,14,5,0,2,5,0,2,5,2,0,2,1,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"Ground Outdoor / Indoor Chamber Mounted; ˂  22 kV ;  >  600 kVA ; Multiple Phase ; REFURBISHED",null,null,0,0,0,0,0,0,0,0,0,0,3,0,0,0,0,1,0,2,0,0,0,0,0,0,0,3,0,0,4,2,0,8,0,5,1,2,1,3,2,4,0,2,2,1,1,10,5,2,1,5,3,2,6,1,1,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"˂ = 11 kV ;  Circuit Breaker REFURBISHED",null,null,7,20,27,28,65,135,34,21,32,13,32,13,14,17,30,31,10,4,32,11,10,0,0,6,4,9,20,28,0,26,0,31,0,0,4,0,0,0,0,0,2,11,0,0,0,38,42,45,37,13,75,64,1,81,20,21,14,0,1,39,2,10,0,0,8,0,7,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 22 kV & < = 33 kV ; Circuit Breaker REFURBISHED",null,null,0,11,1,14,18,19,13,10,3,4,7,7,11,7,7,2,0,3,0,0,0,0,0,0,0,0,0,10,2,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,20,17,0,5,0,2,0,9,0,3,27,0,0,0,19,0,0,3,0,0,0,3,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,"> 33 kV & < = 66 kV ; Circuit Breaker REFURBISHED",null,null,5,7,10,11,14,40,40,30,15,24,16,19,11,2,15,10,8,6,2,7,1,1,1,0,0,2,8,0,13,6,4,2,12,11,0,10,0,0,0,0,0,0,0,0,2,9,11,24,6,6,3,0,15,12,0,0,0,0,2,6,0,0,3,8,0,8,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]

{"sheet":"5.3 MD - Network level","index":22,"n_rows":15,"n_cols":4,"rows_kept":15,"cut":false,"hidden":false,"merged":[]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"5.3 MAXIMUM DEMAND AT NETWORK LEVEL"]
[]
[]
[null,"5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL  (Summed at transmission connection point)"]
[null,null,"UNIT",{"$f":"CRY","v":"2016-17"}]
[null,"Raw network coincident MD","MW",2736.116]
[null,"Date MD occurred",null,"2017-02-08"]
[null,"Half hour time period MD occurred",null,"18:30:00"]
[null,"Winter/summer peaking",null,"Summer"]
[null,"Embedded generation","MW",123.521]
[null,"Weather corrected (10% POE) network coincident MD","MW",2912.07875076357]
[null,"Weather corrected (50% POE) network coincident MD","MW",2627.9439042293802]

{"sheet":"5.4 MD & utilisation-Spatial","index":23,"n_rows":11431,"n_cols":7,"rows_kept":11431,"cut":false,"hidden":false,"merged":[[5,1,5,2],[25,3,26,3],[25,4,26,4],[27,3,28,3],[27,4,28,4],[29,3,30,3],[29,4,30,4],[17,4,18,4],[19,3,20,3],[19,4,20,4],[21,3,22,3],[21,4,22,4],[23,3,24,3],[23,4,24,4],[9,2,30,2],[9,3,10,3],[9,4,10,4],[11,3,12,3],[11,4,12,4],[13,3,14,3],[13,4,14,4],[15,3,16,3],[15,4,16,4],[17,3,18,3],[69,3,70,3],[69,4,70,4],[71,3,72,3],[71,4,72,4],[73,3,74,3],[73,4,74,4],[61,4,62,4],[63,3,64,3],[63,4,64,4],[65,3,66,3],[65,4,66,4],[67,3,68,3],[67,4,68,4],[53,2,74,2],[53,3,54,3],[53,4,54,4],[55,3,56,3],[55,4,56,4],[57,3,58,3],[57,4,58,4],[59,3,60,3],[59,4,60,4],[61,3,62,3],[47,3,48,3],[47,4,48,4],[49,3,50,3],[49,4,50,4],[51,3,52,3],[51,4,52,4],[39,4,40,4],[41,3,42,3],[41,4,42,4],[43,3,44,3],[43,4,44,4],[45,3,46,3],[45,4,46,4],[31,2,52,2],[31,3,32,3],[31,4,32,4],[33,3,34,3],[33,4,34,4],[35,3,36,3],[35,4,36,4],[37,3,38,3],[37,4,38,4],[39,3,40,3],[113,3,114,3],[113,4,114,4],[115,3,116,3],[115,4,116,4],[117,3,118,3],[117,4,118,4],[105,4,106,4],[107,3,108,3],[107,4,108,4],[109,3,110,3],[109,4,110,4],[111,3,112,3],[111,4,112,4],[97,2,118,2],[97,3,98,3],[97,4,98,4],[99,3,100,3],[99,4,100,4],[101,3,102,3],[101,4,102,4],[103,3,104,3],[103,4,104,4],[105,3,106,3],[91,3,92,3],[91,4,92,4],[93,3,94,3],[93,4,94,4],[95,3,96,3],[95,4,96,4],[83,4,84,4],[85,3,86,3],[85,4,86,4],[87,3,88,3],[87,4,88,4],[89,3,90,3],[89,4,90,4],[75,2,96,2],[75,3,76,3],[75,4,76,4],[77,3,78,3],[77,4,78,4],[79,3,80,3],[79,4,80,4],[81,3,82,3],[81,4,82,4],[83,3,84,3],[157,3,158,3],[157,4,158,4],[159,3,160,3],[159,4,160,4],[161,3,162,3],[161,4,162,4],[149,4,150,4],[151,3,152,3],[151,4,152,4],[153,3,154,3],[153,4,154,4],[155,3,156,3],[155,4,156,4],[141,2,162,2],[141,3,142,3],[141,4,142,4],[143,3,144,3],[143,4,144,4],[145,3,146,3],[145,4,146,4],[147,3,148,3],[147,4,148,4],[149,3,150,3],[135,3,136,3],[135,4,136,4],[137,3,138,3],[137,4,138,4],[139,3,140,3],[139,4,140,4],[127,4,128,4],[129,3,130,3],[129,4,130,4],[131,3,132,3],[131,4,132,4],[133,3,134,3],[133,4,134,4],[119,2,140,2],[119,3,120,3],[119,4,120,4],[121,3,122,3],[121,4,122,4],[123,3,124,3],[123,4,124,4],[125,3,126,3],[125,4,126,4],[127,3,128,3],[201,3,202,3],[201,4,202,4],[203,3,204,3],[203,4,204,4],[205,3,206,3],[205,4,206,4],[193,4,194,4],[195,3,196,3],[195,4,196,4],[197,3,198,3],[197,4,198,4],[199,3,200,3],[199,4,200,4],[185,2,206,2],[185,3,186,3],[185,4,186,4],[187,3,188,3],[187,4,188,4],[189,3,190,3],[189,4,190,4],[191,3,192,3],[191,4,192,4],[193,3,194,3],[179,3,180,3],[179,4,180,4],[181,3,182,3],[181,4,182,4],[183,3,184,3],[183,4,184,4],[171,4,172,4],[173,3,174,3],[173,4,174,4],[175,3,176,3],[175,4,176,4],[177,3,178,3],[177,4,178,4],[163,2,184,2],[163,3,164,3],[163,4,164,4],[165,3,166,3],[165,4,166,4],[167,3,168,3],[167,4,168,4],[169,3,170,3],[169,4,170,4],[171,3,172,3],[245,3,246,3],[245,4,246,4],[247,3,248,3],[247,4,248,4],[249,3,250,3],[249,4,250,4],[237,4,238,4],[239,3,240,3],[239,4,240,4],[241,3,242,3],[241,4,242,4],[243,3,244,3],[243,4,244,4],[229,2,250,2],[229,3,230,3],[229,4,230,4],[231,3,232,3],[231,4,232,4],[233,3,234,3],[233,4,234,4],[235,3,236,3],[235,4,236,4],[237,3,238,3],[223,3,224,3],[223,4,224,4],[225,3,226,3],[225,4,226,4],[227,3,228,3],[227,4,228,4],[215,4,216,4],[217,3,218,3],[217,4,218,4],[219,3,220,3],[219,4,220,4],[221,3,222,3],[221,4,222,4],[207,2,228,2],[207,3,208,3],[207,4,208,4],[209,3,210,3],[209,4,210,4],[211,3,212,3],[211,4,212,4],[213,3,214,3],[213,4,214,4],[215,3,216,3],[289,3,290,3],[289,4,290,4],[291,3,292,3],[291,4,292,4],[293,3,294,3],[293,4,294,4],[281,4,282,4],[283,3,284,3],[283,4,284,4],[285,3,286,3],[285,4,286,4],[287,3,288,3],[287,4,288,4],[273,2,294,2],[273,3,274,3],[273,4,274,4],[275,3,276,3],[275,4,276,4],[277,3,278,3],[277,4,278,4],[279,3,280,3],[279,4,280,4],[281,3,282,3],[267,3,268,3],[267,4,268,4],[269,3,270,3],[269,4,270,4],[271,3,272,3],[271,4,272,4],[259,4,260,4],[261,3,262,3],[261,4,262,4],[263,3,264,3],[263,4,264,4],[265,3,266,3],[265,4,266,4],[251,2,272,2],[251,3,252,3],[251,4,252,4],[253,3,254,3],[253,4,254,4],[255,3,256,3],[255,4,256,4],[257,3,258,3],[257,4,258,4],[259,3,260,3],[333,3,334,3],[333,4,334,4],[335,3,336,3],[335,4,336,4],[337,3,338,3],[337,4,338,4],[325,4,326,4],[327,3,328,3],[327,4,328,4],[329,3,330,3],[329,4,330,4],[331,3,332,3],[331,4,332,4],[317,2,338,2],[317,3,318,3],[317,4,318,4],[319,3,320,3],[319,4,320,4],[321,3,322,3],[321,4,322,4],[323,3,324,3],[323,4,324,4],[325,3,326,3],[311,3,312,3],[311,4,312,4],[313,3,314,3],[313,4,314,4],[315,3,316,3],[315,4,316,4],[303,4,304,4],[305,3,306,3],[305,4,306,4],[307,3,308,3],[307,4,308,4],[309,3,310,3],[309,4,310,4],[295,2,316,2],[295,3,296,3],[295,4,296,4],[297,3,298,3],[297,4,298,4],[299,3,300,3],[299,4,300,4],[301,3,302,3],[301,4,302,4],[303,3,304,3],[377,3,378,3],[377,4,378,4],[379,3,380,3],[379,4,380,4],[381,3,382,3],[381,4,382,4],[369,4,370,4],[371,3,372,3],[371,4,372,4],[373,3,374,3],[373,4,374,4],[375,3,376,3],[375,4,376,4],[361,2,382,2],[361,3,362,3],[361,4,362,4],[363,3,364,3],[363,4,364,4],[365,3,366,3],[365,4,366,4],[367,3,368,3],[367,4,368,4],[369,3,370,3],[355,3,356,3],[355,4,356,4],[357,3,358,3],[357,4,358,4],[359,3,360,3],[359,4,360,4],[347,4,348,4],[349,3,350,3],[349,4,350,4],[351,3,352,3],[351,4,352,4],[353,3,354,3],[353,4,354,4],[339,2,360,2],[339,3,340,3],[339,4,340,4],[341,3,342,3],[341,4,342,4],[343,3,344,3],[343,4,344,4],[345,3,346,3],[345,4,346,4],[347,3,348,3],[421,3,422,3],[421,4,422,4],[423,3,424,3],[423,4,424,4],[425,3,426,3],[425,4,426,4],[413,4,414,4],[415,3,416,3],[415,4,416,4],[417,3,418,3],[417,4,418,4],[419,3,420,3],[419,4,420,4],[405,2,426,2],[405,3,406,3],[405,4,406,4],[407,3,408,3],[407,4,408,4],[409,3,410,3],[409,4,410,4],[411,3,412,3],[411,4,412,4],[413,3,414,3],[399,3,400,3],[399,4,400,4],[401,3,402,3],[401,4,402,4],[403,3,404,3],[403,4,404,4],[391,4,392,4],[393,3,394,3],[393,4,394,4],[395,3,396,3],[395,4,396,4],[397,3,398,3],[397,4,398,4],[383,2,404,2],[383,3,384,3],[383,4,384,4],[385,3,386,3],[385,4,386,4],[387,3,388,3],[387,4,388,4],[389,3,390,3],[389,4,390,4],[391,3,392,3],[465,3,466,3],[465,4,466,4],[467,3,468,3],[467,4,468,4],[469,3,470,3],[469,4,470,4],[457,4,458,4],[459,3,460,3],[459,4,460,4],[461,3,462,3],[461,4,462,4],[463,3,464,3],[463,4,464,4],[449,2,470,2],[449,3,450,3],[449,4,450,4],[451,3,452,3],[451,4,452,4],[453,3,454,3],[453,4,454,4],[455,3,456,3],[455,4,456,4],[457,3,458,3],[443,3,444,3],[443,4,444,4],[445,3,446,3],[445,4,446,4],[447,3,448,3],[447,4,448,4],[435,4,436,4],[437,3,438,3],[437,4,438,4],[439,3,440,3],[439,4,440,4],[441,3,442,3],[441,4,442,4],[427,2,448,2],[427,3,428,3],[427,4,428,4],[429,3,430,3],[429,4,430,4],[431,3,432,3],[431,4,432,4],[433,3,434,3],[433,4,434,4],[435,3,436,3],[509,3,510,3],[509,4,510,4],[511,3,512,3],[511,4,512,4],[513,3,514,3],[513,4,514,4],[501,4,502,4],[503,3,504,3],[503,4,504,4],[505,3,506,3],[505,4,506,4],[507,3,508,3],[507,4,508,4],[493,2,514,2],[493,3,494,3],[493,4,494,4],[495,3,496,3],[495,4,496,4],[497,3,498,3],[497,4,498,4],[499,3,500,3],[499,4,500,4],[501,3,502,3],[487,3,488,3],[487,4,488,4],[489,3,490,3],[489,4,490,4],[491,3,492,3],[491,4,492,4],[479,4,480,4],[481,3,482,3],[481,4,482,4],[483,3,484,3],[483,4,484,4],[485,3,486,3],[485,4,486,4],[471,2,492,2],[471,3,472,3],[471,4,472,4],[473,3,474,3],[473,4,474,4],[475,3,476,3],[475,4,476,4],[477,3,478,3],[477,4,478,4],[479,3,480,3],[553,3,554,3],[553,4,554,4],[555,3,556,3],[555,4,556,4],[557,3,558,3],[557,4,558,4],[545,4,546,4],[547,3,548,3],[547,4,548,4],[549,3,550,3],[549,4,550,4],[551,3,552,3],[551,4,552,4],[537,2,558,2],[537,3,538,3],[537,4,538,4],[539,3,540,3],[539,4,540,4],[541,3,542,3],[541,4,542,4],[543,3,544,3],[543,4,544,4],[545,3,546,3],[531,3,532,3],[531,4,532,4],[533,3,534,3],[533,4,534,4],[535,3,536,3],[535,4,536,4],[523,4,524,4],[525,3,526,3],[525,4,526,4],[527,3,528,3],[527,4,528,4],[529,3,530,3],[529,4,530,4],[515,2,536,2],[515,3,516,3],[515,4,516,4],[517,3,518,3],[517,4,518,4],[519,3,520,3],[519,4,520,4],[521,3,522,3],[521,4,522,4],[523,3,524,3],[597,3,598,3],[597,4,598,4],[599,3,600,3],[599,4,600,4],[601,3,602,3],[601,4,602,4],[589,4,590,4],[591,3,592,3],[591,4,592,4],[593,3,594,3],[593,4,594,4],[595,3,596,3],[595,4,596,4],[581,2,602,2],[581,3,582,3],[581,4,582,4],[583,3,584,3],[583,4,584,4],[585,3,586,3],[585,4,586,4],[587,3,588,3],[587,4,588,4],[589,3,590,3],[575,3,576,3],[575,4,576,4],[577,3,578,3],[577,4,578,4],[579,3,580,3],[579,4,580,4],[567,4,568,4],[569,3,570,3],[569,4,570,4],[571,3,572,3],[571,4,572,4],[573,3,574,3],[573,4,574,4],[559,2,580,2],[559,3,560,3],[559,4,560,4],[561,3,562,3],[561,4,562,4],[563,3,564,3],[563,4,564,4],[565,3,566,3],[565,4,566,4],[567,3,568,3],[641,3,642,3],[641,4,642,4],[643,3,644,3],[643,4,644,4],[645,3,646,3],[645,4,646,4],[633,4,634,4],[635,3,636,3],[635,4,636,4],[637,3,638,3],[637,4,638,4],[639,3,640,3],[639,4,640,4],[625,2,646,2],[625,3,626,3],[625,4,626,4],[627,3,628,3],[627,4,628,4],[629,3,630,3],[629,4,630,4],[631,3,632,3],[631,4,632,4],[633,3,634,3],[619,3,620,3],[619,4,620,4],[621,3,622,3],[621,4,622,4],[623,3,624,3],[623,4,624,4],[611,4,612,4],[613,3,614,3],[613,4,614,4],[615,3,616,3],[615,4,616,4],[617,3,618,3],[617,4,618,4],[603,2,624,2],[603,3,604,3],[603,4,604,4],[605,3,606,3],[605,4,606,4],[607,3,608,3],[607,4,608,4],[609,3,610,3],[609,4,610,4],[611,3,612,3],[685,3,686,3],[685,4,686,4],[687,3,688,3],[687,4,688,4],[689,3,690,3],[689,4,690,4],[677,4,678,4],[679,3,680,3],[679,4,680,4],[681,3,682,3],[681,4,682,4],[683,3,684,3],[683,4,684,4],[669,2,690,2],[669,3,670,3],[669,4,670,4],[671,3,672,3],[671,4,672,4],[673,3,674,3],[673,4,674,4],[675,3,676,3],[675,4,676,4],[677,3,678,3],[663,3,664,3],[663,4,664,4],[665,3,666,3],[665,4,666,4],[667,3,668,3],[667,4,668,4],[655,4,656,4],[657,3,658,3],[657,4,658,4],[659,3,660,3],[659,4,660,4],[661,3,662,3],[661,4,662,4],[647,2,668,2],[647,3,648,3],[647,4,648,4],[649,3,650,3],[649,4,650,4],[651,3,652,3],[651,4,652,4],[653,3,654,3],[653,4,654,4],[655,3,656,3],[729,3,730,3],[729,4,730,4],[731,3,732,3],[731,4,732,4],[733,3,734,3],[733,4,734,4],[721,4,722,4],[723,3,724,3],[723,4,724,4],[725,3,726,3],[725,4,726,4],[727,3,728,3],[727,4,728,4],[713,2,734,2],[713,3,714,3],[713,4,714,4],[715,3,716,3],[715,4,716,4],[717,3,718,3],[717,4,718,4],[719,3,720,3],[719,4,720,4],[721,3,722,3],[707,3,708,3],[707,4,708,4],[709,3,710,3],[709,4,710,4],[711,3,712,3],[711,4,712,4],[699,4,700,4],[701,3,702,3],[701,4,702,4],[703,3,704,3],[703,4,704,4],[705,3,706,3],[705,4,706,4],[691,2,712,2],[691,3,692,3],[691,4,692,4],[693,3,694,3],[693,4,694,4],[695,3,696,3],[695,4,696,4],[697,3,698,3],[697,4,698,4],[699,3,700,3],[773,3,774,3],[773,4,774,4],[775,3,776,3],[775,4,776,4],[777,3,778,3],[777,4,778,4],[765,4,766,4],[767,3,768,3],[767,4,768,4],[769,3,770,3],[769,4,770,4],[771,3,772,3],[771,4,772,4],[757,2,778,2],[757,3,758,3],[757,4,758,4],[759,3,760,3],[759,4,760,4],[761,3,762,3],[761,4,762,4],[763,3,764,3],[763,4,764,4],[765,3,766,3],[751,3,752,3],[751,4,752,4],[753,3,754,3],[753,4,754,4],[755,3,756,3],[755,4,756,4],[743,4,744,4],[745,3,746,3],[745,4,746,4],[747,3,748,3],[747,4,748,4],[749,3,750,3],[749,4,750,4],[735,2,756,2],[735,3,736,3],[735,4,736,4],[737,3,738,3],[737,4,738,4],[739,3,740,3],[739,4,740,4],[741,3,742,3],[741,4,742,4],[743,3,744,3],[817,3,818,3],[817,4,818,4],[819,3,820,3],[819,4,820,4],[821,3,822,3],[821,4,822,4],[809,4,810,4],[811,3,812,3],[811,4,812,4],[813,3,814,3],[813,4,814,4],[815,3,816,3],[815,4,816,4],[801,2,822,2],[801,3,802,3],[801,4,802,4],[803,3,804,3],[803,4,804,4],[805,3,806,3],[805,4,806,4],[807,3,808,3],[807,4,808,4],[809,3,810,3],[795,3,796,3],[795,4,796,4],[797,3,798,3],[797,4,798,4],[799,3,800,3],[799,4,800,4],[787,4,788,4],[789,3,790,3],[789,4,790,4],[791,3,792,3],[791,4,792,4],[793,3,794,3],[793,4,794,4],[779,2,800,2],[779,3,780,3],[779,4,780,4],[781,3,782,3],[781,4,782,4],[783,3,784,3],[783,4,784,4],[785,3,786,3],[785,4,786,4],[787,3,788,3],[861,3,862,3],[861,4,862,4],[863,3,864,3],[863,4,864,4],[865,3,866,3],[865,4,866,4],[853,4,854,4],[855,3,856,3],[855,4,856,4],[857,3,858,3],[857,4,858,4],[859,3,860,3],[859,4,860,4],[845,2,866,2],[845,3,846,3],[845,4,846,4],[847,3,848,3],[847,4,848,4],[849,3,850,3],[849,4,850,4],[851,3,852,3],[851,4,852,4],[853,3,854,3],[839,3,840,3],[839,4,840,4],[841,3,842,3],[841,4,842,4],[843,3,844,3],[843,4,844,4],[831,4,832,4],[833,3,834,3],[833,4,834,4],[835,3,836,3],[835,4,836,4],[837,3,838,3],[837,4,838,4],[823,2,844,2],[823,3,824,3],[823,4,824,4],[825,3,826,3],[825,4,826,4],[827,3,828,3],[827,4,828,4],[829,3,830,3],[829,4,830,4],[831,3,832,3],[905,3,906,3],[905,4,906,4],[907,3,908,3],[907,4,908,4],[909,3,910,3],[909,4,910,4],[897,4,898,4],[899,3,900,3],[899,4,900,4],[901,3,902,3],[901,4,902,4],[903,3,904,3],[903,4,904,4],[889,2,910,2],[889,3,890,3],[889,4,890,4],[891,3,892,3],[891,4,892,4],[893,3,894,3],[893,4,894,4],[895,3,896,3],[895,4,896,4],[897,3,898,3],[883,3,884,3],[883,4,884,4],[885,3,886,3],[885,4,886,4],[887,3,888,3],[887,4,888,4],[875,4,876,4],[877,3,878,3],[877,4,878,4],[879,3,880,3],[879,4,880,4],[881,3,882,3],[881,4,882,4],[867,2,888,2],[867,3,868,3],[867,4,868,4],[869,3,870,3],[869,4,870,4],[871,3,872,3],[871,4,872,4],[873,3,874,3],[873,4,874,4],[875,3,876,3],[949,3,950,3],[949,4,950,4],[951,3,952,3],[951,4,952,4],[953,3,954,3],[953,4,954,4],[941,4,942,4],[943,3,944,3],[943,4,944,4],[945,3,946,3],[945,4,946,4],[947,3,948,3],[947,4,948,4],[933,2,954,2],[933,3,934,3],[933,4,934,4],[935,3,936,3],[935,4,936,4],[937,3,938,3],[937,4,938,4],[939,3,940,3],[939,4,940,4],[941,3,942,3],[927,3,928,3],[927,4,928,4],[929,3,930,3],[929,4,930,4],[931,3,932,3],[931,4,932,4],[919,4,920,4],[921,3,922,3],[921,4,922,4],[923,3,924,3],[923,4,924,4],[925,3,926,3],[925,4,926,4],[911,2,932,2],[911,3,912,3],[911,4,912,4],[913,3,914,3],[913,4,914,4],[915,3,916,3],[915,4,916,4],[917,3,918,3],[917,4,918,4],[919,3,920,3],[993,3,994,3],[993,4,994,4],[995,3,996,3],[995,4,996,4],[997,3,998,3],[997,4,998,4],[985,4,986,4],[987,3,988,3],[987,4,988,4],[989,3,990,3]],"merged_total":11938,"flags":["merged_cut"]}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL"]
[]
[null,"There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data."]
[]
[null,"5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND"]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND",{"$f":"CRY","v":"2016-17"}]
[null,"SUBTRANSMISSION SUBSTATION","Angas Creek 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.556784]
[null,null,null,null,null,"Coincident",15.038294]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.086058000000001]
[null,null,null,null,null,"Coincident",15.424064]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.46365097333333338]
[null,null,null,null,null,"Coincident",0.85907104359048625]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.432156245921892]
[null,null,null,null,null,"Coincident",15.833382296955115]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.989413444234323]
[null,null,null,null,null,"Coincident",16.239548308119435]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.610465392102071]
[null,null,null,null,null,"Coincident",14.178766120477032]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.109488237356285]
[null,null,null,null,null,"Coincident",14.542487072221718]
[null,null,"Ardrossan West 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.542]
[null,null,null,null,null,"Coincident",9.1699000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.744948871446526]
[null,null,null,null,null,"Coincident",9.3182295534076633]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4700785904489138]
[null,null,null,null,null,"Coincident",0.60889036663900153]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.8419771727362786]
[null,null,null,null,null,"Coincident",7.6911446097775]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.0121981259294852]
[null,null,null,null,null,"Coincident",7.8155542593006198]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.0699605760823552]
[null,null,null,null,null,"Coincident",7.0196102719235052]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.225319084101125]
[null,null,null,null,null,"Coincident",7.1331573833129704]
[null,null,"Baroota 33kV","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.2371999999999996]
[null,null,null,null,null,"Coincident",7.4630000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.2587263334003271]
[null,null,null,null,null,"Coincident",7.478924912044512]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.0853355253114919E-2]
[null,null,null,null,null,"Coincident",0.37755976684904896]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.2448025820525803]
[null,null,null,null,null,"Coincident",7.4698880286818836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.266348783334708]
[null,null,null,null,null,"Coincident",7.4858276387367022]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4697942493496949]
[null,null,null,null,null,"Coincident",6.7677213716914455]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.4893151158387141]
[null,null,null,null,null,"Coincident",6.7821626644136686]
[null,null,"Berri / Monash 66kV","Substation Rating","MVA","Non-Coincident",160]
[null,null,null,null,null,"Coincident",160]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",85.547799999999995]
[null,null,null,null,null,"Coincident",76.216800000000006]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",88.134175636298991]
[null,null,null,null,null,"Coincident",77.880621152376548]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.27119232366587404]
[null,null,null,null,null,"Coincident",2.5063133703499734]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",90.69780988231777]
[null,null,null,null,null,"Coincident",80.805080156808685]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",93.439886309125995]
[null,null,null,null,null,"Coincident",82.569063971195803]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",83.470022939704762]
[null,null,null,null,null,"Coincident",74.36565340535806]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",85.993580923575422]
[null,null,null,null,null,"Coincident",75.9890638233517]
[null,null,"Blanche 33kV","Substation Rating","MVA","Non-Coincident",110]
[null,null,null,null,null,"Coincident",110]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.913600000000002]
[null,null,null,null,null,"Coincident",35.638300000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.112208952119268]
[null,null,null,null,null,"Coincident",37.599328139343129]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.96318451999999843]
[null,null,null,null,null,"Coincident",0.58104126820895496]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",34.965827467794675]
[null,null,null,null,null,"Coincident",34.697792731597694]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",37.106414356576394]
[null,null,null,null,null,"Coincident",36.607068648792357]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",33.152348902334495]
[null,null,null,null,null,"Coincident",32.898215603171707]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",35.181915726057369]
[null,null,null,null,null,"Coincident",34.708468239576838]
[null,null,"Brinkworth 33kV","Substation Rating","MVA","Non-Coincident",20]
[null,null,null,null,null,"Coincident",20]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.6211000000000002]
[null,null,null,null,null,"Coincident",4.2363]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.6237866484084238]
[null,null,null,null,null,"Coincident",4.244965594678006]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7909709401656763E-2]
[null,null,null,null,null,"Coincident",0.16551849081008277]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.5826774461030872]
[null,null,null,null,null,"Coincident",4.2010769005056172]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.5853417561303305]
[null,null,null,null,null,"Coincident",4.2096704443129287]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.1341784681045208]
[null,null,null,null,null,"Coincident",3.7899245297507478]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.1365820265649464]
[null,null,null,null,null,"Coincident",3.7976770377966966]
[null,null,"Clare North 33kV","Substation Rating","MVA","Non-Coincident",80]
[null,null,null,null,null,"Coincident",80]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.039778]
[null,null,null,null,null,"Coincident",10.582722000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.753091]
[null,null,null,null,null,"Coincident",11.201452999999999]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.6971325247679392E-2]
[null,null,null,null,null,"Coincident",0.43410100588378209]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.258978508768944]
[null,null,null,null,null,"Coincident",10.775394825575383]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.985278340628426]
[null,null,null,null,null,"Coincident",11.405390663680461]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.115774389820622]
[null,null,null,null,null,"Coincident",9.7705414653153326]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.774343540956641]
[null,null,null,null,null,"Coincident",10.341787397257605]
[null,null,"Dalrymple 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.0262000000000002]
[null,null,null,null,null,"Coincident",5.7572999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.0282514525307072]
[null,null,null,null,null,"Coincident",5.7606319184617236]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-01"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.40045229608738514]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9481549617592284]
[null,null,null,null,null,"Coincident",4.873945028797416]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9498916554982824]
[null,null,null,null,null,"Coincident",4.8767657238146764]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.4516390255660792]
[null,null,null,null,null,"Coincident",4.4670976291440017]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.4532307506344662]
[null,null,null,null,null,"Coincident",4.4696828696318809]
[null,null,"Davenport West 33kV","Substation Rating","MVA","Non-Coincident",120]
[null,null,null,null,null,"Coincident",120]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.168184]
[null,null,null,null,null,"Coincident",29.831499999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.343342]
[null,null,null,null,null,"Coincident",30.030889999999999]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.0625026666666669E-2]
[null,null,null,null,null,"Coincident",1.0456968894094032]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.587391395608961]
[null,null,null,null,null,"Coincident",31.189843027688383]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.770525013598125]
[null,null,null,null,null,"Coincident",31.398312021915654]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.66924084149526]
[null,null,null,null,null,"Coincident",28.396840770802232]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.835975126922815]
[null,null,null,null,null,"Coincident",28.58664168866725]
[null,null,"Dorrien 33kV","Substation Rating","MVA","Non-Coincident",180]
[null,null,null,null,null,"Coincident",180]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",57.138672]
[null,null,null,null,null,"Coincident",52.239636000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",58.713568241792153]
[null,null,null,null,null,"Coincident",53.417123234244812]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.84870501333333337]
[null,null,null,null,null,"Coincident",1.5725145496040458]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",63.749877418118665]
[null,null,null,null,null,"Coincident",58.284000569126619]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",65.506996350818142]
[null,null,null,null,null,"Coincident",59.597728456335936]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",58.068696450985222]
[null,null,null,null,null,"Coincident",53.089920703686637]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",59.669226680431684]
[null,null,null,null,null,"Coincident",54.286573450188548]
[null,null,"Hummocks 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.7006]
[null,null,null,null,null,"Coincident",13.3597]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.178081414987007]
[null,null,null,null,null,"Coincident",13.873946568298438]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.8231357420102169E-2]
[null,null,null,null,null,"Coincident",0.35332770844460437]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.49492714749657]
[null,null,null,null,null,"Coincident",14.134262602543679]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.000091762514909]
[null,null,null,null,null,"Coincident",14.678323924189153]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.383427611852827]
[null,null,null,null,null,"Coincident",13.050419533894152]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.849855210168498]
[null,null,null,null,null,"Coincident",13.552761162834919]
[null,null,"Kadina East 33kV","Substation Rating","MVA","Non-Coincident",120]
[null,null,null,null,null,"Coincident",120]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.397099999999998]
[null,null,null,null,null,"Coincident",23.1953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.748961351091424]
[null,null,null,null,null,"Coincident",24.4604908801929]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.3630220255745088]
[null,null,null,null,null,"Coincident",1.1675063671390407]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",26.342052912487357]
[null,null,null,null,null,"Coincident",25.044444623378109]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.801685542627702]
[null,null,null,null,null,"Coincident",26.410497355483063]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.305197156456032]
[null,null,null,null,null,"Coincident",22.157184239239278]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.596555363594533]
[null,null,null,null,null,"Coincident",23.365750950178107]
[null,null,"Kanmantoo Copper Mine 11kV","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0693999999999999]
[null,null,null,null,null,"Coincident",1.0286]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1832829796798396]
[null,null,null,null,null,"Coincident",1.1501439562072218]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.5454193652902211E-3]
[null,null,null,null,null,"Coincident",8.8217143676603743E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4498461848164979]
[null,null,null,null,null,"Coincident",1.354247921214655]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4870971453438853]
[null,null,null,null,null,"Coincident",1.3907065619445735]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.3144313204065405]
[null,null,null,null,null,"Coincident",1.2277618839030768]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3482030609850921]
[null,null,null,null,null,"Coincident",1.2608153069328585]
[null,null,"Keith 33kV","Substation Rating","MVA","Non-Coincident",51]
[null,null,null,null,null,"Coincident",51]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.5001]
[null,null,null,null,null,"Coincident",18.664200000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.569597446154699]
[null,null,null,null,null,"Coincident",18.668483691114446]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.49063238781001089]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.883769206006704]
[null,null,null,null,null,"Coincident",19.988556223545025]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.958197984623308]
[null,null,null,null,null,"Coincident",19.993143872663946]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.102623010860405]
[null,null,null,null,null,"Coincident",18.28376143708498]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.170703867579643]
[null,null,null,null,null,"Coincident",18.287957812306349]
[null,null,"Kincraig 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.0166]
[null,null,null,null,null,"Coincident",18.347100000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.749321804051906]
[null,null,null,null,null,"Coincident",19.012791678498978]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.1981563831850684E-2]
[null,null,null,null,null,"Coincident",0.66524138077279005]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.796654929561978]
[null,null,null,null,null,"Coincident",19.09969225088431]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.559432750738303]
[null,null,null,null,null,"Coincident",19.792690391915048]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.907126492137344]
[null,null,null,null,null,"Coincident",17.276686708659437]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.597099569801308]
[null,null,null,null,null,"Coincident",17.903540357137313]
[null,null,"Leigh Creek South 33kV","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.168288]
[null,null,null,null,null,"Coincident",1.138652]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.192259]
[null,null,null,null,null,"Coincident",1.150525]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",3.6855555762869134E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3181780792561131]
[null,null,null,null,null,"Coincident",1.2847398127012617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3452245324747101]
[null,null,null,null,null,"Coincident",1.2981361056829648]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2136224739945081]
[null,null,null,null,null,"Coincident",1.1828364729063334]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2385236493246683]
[null,null,null,null,null,"Coincident",1.1951701950996083]
[null,null,"Mannum 33kV","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.1891]
[null,null,null,null,null,"Coincident",9.5637000000000008]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.626658380189115]
[null,null,null,null,null,"Coincident",9.7947516405470942]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.4842009999999857E-2]
[null,null,null,null,null,"Coincident",0.49133846805597237]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.482887148579614]
[null,null,null,null,null,"Coincident",9.0095977408398387]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.895094243494489]
[null,null,null,null,null,"Coincident",9.2272626967345683]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.466591945286114]
[null,null,null,null,null,"Coincident",8.2122015068489738]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.842316569555324]
[null,null,null,null,null,"Coincident",8.410601982675356]
[null,null,"Mobilong 33kV","Substation Rating","MVA","Non-Coincident",120]
[null,null,null,null,null,"Coincident",120]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",40.714700000000001]
[null,null,null,null,null,"Coincident",40.714700000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",43.45864519114695]
[null,null,null,null,null,"Coincident",43.45864519114695]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1813884616147987]
[null,null,null,null,null,"Coincident",1.1813884616147987]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",40.212762327291394]
[null,null,null,null,null,"Coincident",40.212762327291394]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",42.922879700395129]
[null,null,null,null,null,"Coincident",42.922879700395129]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",37.121035848771029]
[null,null,null,null,null,"Coincident",37.121035848771029]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",39.622787987620853]
[null,null,null,null,null,"Coincident",39.622787987620853]
[null,null,"Mount Barker / Mount Barker South 66kV","Substation Rating","MVA","Non-Coincident",345]
[null,null,null,null,null,"Coincident",345]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",87.913499999999999]
[null,null,null,null,null,"Coincident",87.913499999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",91.382122506866736]
[null,null,null,null,null,"Coincident",91.382122506866736]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.2387337385958537]
[null,null,null,null,null,"Coincident",4.2387337385958537]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",81.866572003512204]
[null,null,null,null,null,"Coincident",81.866572003512204]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",85.096613285128896]
[null,null,null,null,null,"Coincident",85.096613285128896]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",74.21658928995268]
[null,null,null,null,null,"Coincident",74.21658928995268]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",77.144800906985495]
[null,null,null,null,null,"Coincident",77.144800906985495]
[null,null,"Mount Gambier 33kV","Substation Rating","MVA","Non-Coincident",66.099999999999994]
[null,null,null,null,null,"Coincident",66.099999999999994]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.850200000000001]
[null,null,null,null,null,"Coincident",20.793700000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.277404666218107]
[null,null,null,null,null,"Coincident",21.277299453878072]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.7165786666666598E-2]
[null,null,null,null,null,"Coincident",0.61173457477158155]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.817208102943297]
[null,null,null,null,null,"Coincident",20.760797504588542]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.243736790400046]
[null,null,null,null,null,"Coincident",21.243631744540654]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.499118850461933]
[null,null,null,null,null,"Coincident",19.44628001845787]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.898640896296445]
[null,null,null,null,null,"Coincident",19.898542501656447]
[null,null,"Mount Gunson 33kV","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.14710000000000001]
[null,null,null,null,null,"Coincident",0.1229]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.20578051414067369]
[null,null,null,null,null,"Coincident",0.2027063146525041]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-18"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.17606285023767396]
[null,null,null,null,null,"Coincident",0.14709805774446041]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.24629710294344651]
[null,null,null,null,null,"Coincident",0.2426176173956128]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.15957028698655928]
[null,null,null,null,null,"Coincident",0.13331875099013007]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.22322539563337201]
[null,null,null,null,null,"Coincident",0.21989058329767414]
[null,null,"Neuroodla 33kV","Substation Rating","MVA","Non-Coincident",10]
[null,null,null,null,null,"Coincident",10]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.92210000000000003]
[null,null,null,null,null,"Coincident",0.80130000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.92467054673543059]
[null,null,null,null,null,"Coincident",0.80830695283413223]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.2427199999999997E-3]
[null,null,null,null,null,"Coincident",2.9087808398652597E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.89842122138881964]
[null,null,null,null,null,"Coincident",0.78072326721490204]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.90092575857316248]
[null,null,null,null,null,"Coincident",0.78755028719479026]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.81424976982861597]
[null,null,null,null,null,"Coincident",0.70757872309258207]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.81651966147557187]
[null,null,null,null,null,"Coincident",0.71376613197707628]
[null,null,"North West Bend 66kV","Substation Rating","MVA","Non-Coincident",65]
[null,null,null,null,null,"Coincident",65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.24]
[null,null,null,null,null,"Coincident",16.682300000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.509550707333126]
[null,null,null,null,null,"Coincident",17.499529404529714]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.10641212999999987]
[null,null,null,null,null,"Coincident",0.61675374524887405]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.503700470674662]
[null,null,null,null,null,"Coincident",14.799141186548512]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.629939667985916]
[null,null,null,null,null,"Coincident",15.524118757952587]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.923400716386634]
[null,null,null,null,null,"Coincident",13.71155725127792]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.966872971830941]
[null,null,null,null,null,"Coincident",14.383256463475094]
[null,null,"Penola West 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.5258000000000003]
[null,null,null,null,null,"Coincident",5.0317999999999996]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.8079979511015676]
[null,null,null,null,null,"Coincident",5.2265390843272179]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-01"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.8679734554149495E-4]
[null,null,null,null,null,"Coincident",0.13667053871834872]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.5262019345278679]
[null,null,null,null,null,"Coincident",5.9427671819749754]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.8594895696936087]
[null,null,null,null,null,"Coincident",6.1727622214017508]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.8009348953892292]
[null,null,null,null,null,"Coincident",5.2823381603785009]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.0971837538264557]
[null,null,null,null,null,"Coincident",5.4867734909677202]
[null,null,"Port Lincoln Terminal 33kV","Substation Rating","MVA","Non-Coincident",75]
[null,null,null,null,null,"Coincident",75]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",30.971399999999999]
[null,null,null,null,null,"Coincident",29.6511]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.884725697576478]
[null,null,null,null,null,"Coincident",32.635717371769232]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.14835820416692136]
[null,null,null,null,null,"Coincident",1.3711013117125934]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",29.988428396591942]
[null,null,null,null,null,"Coincident",28.710032133845655]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.809290839933979]
[null,null,null,null,null,"Coincident",31.599923593209006]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",27.328051721452681]
[null,null,null,null,null,"Coincident",26.163066390216962]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.898665750679879]
[null,null,null,null,null,"Coincident",28.796585633921016]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Snuggery Rural 33kV","Substation Rating","MVA","Non-Coincident",25]
[null,null,null,null,null,"Coincident",25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.257860000000001]
[null,null,null,null,null,"Coincident",11.430324000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.788568999999999]
[null,null,null,null,null,"Coincident",11.744382]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2235201499999984]
[null,null,null,null,null,"Coincident",0.58578201860395562]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.71397980230182]
[null,null,null,null,null,"Coincident",9.2371061747345156]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.142857879676281]
[null,null,null,null,null,"Coincident",9.4909036253601293]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9617553718581124]
[null,null,null,null,null,"Coincident",8.5885724776908727]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.360522083200925]
[null,null,null,null,null,"Coincident",8.8245509062287368]
[null,null,"Stony Point 11kV","Substation Rating","MVA","Non-Coincident",30]
[null,null,null,null,null,"Coincident",30]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.134048]
[null,null,null,null,null,"Coincident",4.2360000000000002E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.13822100000000001]
[null,null,null,null,null,"Coincident",4.2418999999999998E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-19"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",4.2105417165489139E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.13065216109436051]
[null,null,null,null,null,"Coincident",4.1286893828756201E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.13471944645666931]
[null,null,null,null,null,"Coincident",4.1344399181350543E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.12224861804364887]
[null,null,null,null,null,"Coincident",3.863132206619245E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.12605429573444729]
[null,null,null,null,null,"Coincident",3.868512867624687E-2]
[null,null,"Tailem Bend 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.976199999999999]
[null,null,null,null,null,"Coincident",19.976199999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.820603164211569]
[null,null,null,null,null,"Coincident",21.820603164211569]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.62728182885752759]
[null,null,null,null,null,"Coincident",0.62728182885752759]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.008354938990461]
[null,null,null,null,null,"Coincident",20.008354938990461]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.85572696971413]
[null,null,null,null,null,"Coincident",21.85572696971413]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.337828912580896]
[null,null,null,null,null,"Coincident",18.337828912580896]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.030961223587724]
[null,null,null,null,null,"Coincident",20.030961223587724]
[null,null,"Templers 33kV","Substation Rating","MVA","Non-Coincident",120]
[null,null,null,null,null,"Coincident",120]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.983899999999998]
[null,null,null,null,null,"Coincident",28.5045]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.319100993642842]
[null,null,null,null,null,"Coincident",29.826107293108162]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.13376831358087624]
[null,null,null,null,null,"Coincident",1.2362640222441765]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.110855503865757]
[null,null,null,null,null,"Coincident",30.526511918394252]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.540771097750586]
[null,null,null,null,null,"Coincident",31.941869521036047]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.257617615153407]
[null,null,null,null,null,"Coincident",27.814052251746446]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.5604768199725]
[null,null,null,null,null,"Coincident",29.103647028248385]
[null,null,"Waterloo 33kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.5469860000000004]
[null,null,null,null,null,"Coincident",7.5926599999999995]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.7338680000000011]
[null,null,null,null,null,"Coincident",7.7570879999999995]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.0602223528462898E-2]
[null,null,null,null,null,"Coincident",0.37523885012579433]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.7568305260599555]
[null,null,null,null,null,"Coincident",7.7790740340506437]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.9483008294360395]
[null,null,null,null,null,"Coincident",7.9475390496408158]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.9321317475083122]
[null,null,null,null,null,"Coincident",7.0464581823389505]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.1055698045307363]
[null,null,null,null,null,"Coincident",7.1990575382966293]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Whyalla Central 33kV","Substation Rating","MVA","Non-Coincident",240]
[null,null,null,null,null,"Coincident",240]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",64.146600000000007]
[null,null,null,null,null,"Coincident",36.757300000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",66.881301392242662]
[null,null,null,null,null,"Coincident",40.236645145687781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-12-04"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.26111748457727763]
[null,null,null,null,null,"Coincident",1.3186589004980358]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",69.190295482382936]
[null,null,null,null,null,"Coincident",39.647439585801806]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",72.140019978854355]
[null,null,null,null,null,"Coincident",43.400357413330191]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",65.085014947431915]
[null,null,null,null,null,"Coincident",37.29503075653642]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",67.859722897516193]
[null,null,null,null,null,"Coincident",40.825276019954337]
[null,null,"Wudinna 66kV","Substation Rating","MVA","Non-Coincident",50]
[null,null,null,null,null,"Coincident",50]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.893644]
[null,null,null,null,null,"Coincident",13.850243999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.901380000000001]
[null,null,null,null,null,"Coincident",13.851648000000001]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.411970565142866E-2]
[null,null,null,null,null,"Coincident",0.59258342347137327]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.073229773247883]
[null,null,null,null,null,"Coincident",11.22741877189678]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.079500804402237]
[null,null,null,null,null,"Coincident",11.228556895958405]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.054645651954992]
[null,null,null,null,null,"Coincident",10.280193323616148]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.060387614013676]
[null,null,null,null,null,"Coincident",10.281235427381713]
[null,null,"Yadnarie 66kV","Substation Rating","MVA","Non-Coincident",40]
[null,null,null,null,null,"Coincident",40]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.1583000000000006]
[null,null,null,null,null,"Coincident",7.7039]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.3192274551186554]
[null,null,null,null,null,"Coincident",7.8938333305181958]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.8135571465367536E-2]
[null,null,null,null,null,"Coincident",0.35244247092829861]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.6067983622772557]
[null,null,null,null,null,"Coincident",7.1831158333412288]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.7568471104284678]
[null,null,null,null,null,"Coincident",7.3602096577320548]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.8678769927689078]
[null,null,null,null,null,"Coincident",6.4853508162965792]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.0033500651631888]
[null,null,null,null,null,"Coincident",6.645241816973912]
[null,null,"Bungama / Port Pirie 33kV","Substation Rating","MVA","Non-Coincident",180]
[null,null,null,null,null,"Coincident",180]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",59.224000000000004]
[null,null,null,null,null,"Coincident",55.571199999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",61.733477123518647]
[null,null,null,null,null,"Coincident",57.984507568228949]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.126587693333333]
[null,null,null,null,null,"Coincident",1.6418271426247517]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",40.0868137740649]
[null,null,null,null,null,"Coincident",37.614351371087992]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",41.785397829866056]
[null,null,null,null,null,"Coincident",39.247841359388943]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",38.854994302579584]
[null,null,null,null,null,"Coincident",36.458507689239333]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",40.501382917613533]
[null,null,null,null,null,"Coincident",38.041802499010842]
[null,null,"Metro North Region 66kV","Substation Rating","MVA","Non-Coincident",875]
[null,null,null,null,null,"Coincident",875]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",314.37179999999995]
[null,null,null,null,null,"Coincident",306.74979999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",318.36538845559193]
[null,null,null,null,null,"Coincident",309.76655331350736]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.0857423866666709]
[null,null,null,null,null,"Coincident",9.4230666402701253]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",339.03762626802143]
[null,null,null,null,null,"Coincident",330.81759893918706]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",343.34455440303628]
[null,null,null,null,null,"Coincident",334.07104877930544]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",308.87621795624409]
[null,null,null,null,null,"Coincident",301.3874593167526]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",312.79999387455791]
[null,null,null,null,null,"Coincident",304.35147629913814]
[null,null,"Metro South Region 66kV","Substation Rating","MVA","Non-Coincident",1515]
[null,null,null,null,null,"Coincident",1515]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",667.46769999999992]
[null,null,null,null,null,"Coincident",658.55010000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",673.96637600119243]
[null,null,null,null,null,"Coincident",665.0748336149843]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",12.037774373333427]
[null,null,null,null,null,"Coincident",22.304069198991343]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",654.44737270255621]
[null,null,null,null,null,"Coincident",645.70372879167894]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",660.81927869145363]
[null,null,null,null,null,"Coincident",652.10118408713447]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",586.721147850688]
[null,null,null,null,null,"Coincident",578.88234979638025]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",592.43364995817478]
[null,null,null,null,null,"Coincident",584.61775721160575]
[null,null,"Metro East Region 66kV","Substation Rating","MVA","Non-Coincident",1650]
[null,null,null,null,null,"Coincident",1650]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",719.84318199999996]
[null,null,null,null,null,"Coincident",673.24432999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",728.83324609257852]
[null,null,null,null,null,"Coincident",688.73626311666567]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",41.206571649253497]
[null,null,null,null,null,"Coincident",19.666492514264501]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",785.19413481395475]
[null,null,null,null,null,"Coincident",734.36480671251388]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",795.00036174449508]
[null,null,null,null,null,"Coincident",751.26317475197936]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",698.64769059791297]
[null,null,null,null,null,"Coincident",653.42092295129839]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",707.37304588870916]
[null,null,null,null,null,"Coincident",668.45670236200874]
[null,null,"Metro West Region 66kV","Substation Rating","MVA","Non-Coincident",845]
[null,null,null,null,null,"Coincident",845]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",423.53700000000003]
[null,null,null,null,null,"Coincident",409.19400000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",424.26492345990874]
[null,null,null,null,null,"Coincident",409.60632859379086]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.5206017066666906]
[null,null,null,null,null,"Coincident",10.83180339751592]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",462.04984822893493]
[null,null,null,null,null,"Coincident",446.40261794410122]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",462.84396284979005]
[null,null,null,null,null,"Coincident",446.85244018910345]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",421.55002433719983]
[null,null,null,null,null,"Coincident",407.27431289034052]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",422.27453282698974]
[null,null,null,null,null,"Coincident",407.68470709143145]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[]
[]
[]
[null,"NETWORK LEVEL","SUBSTATION","FORECASTING ELEMENTS","UNIT","MAX DEMAND",{"$f":"CRY","v":"2016-17"}]
[null,"ZONE SUBSTATION",null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Aldgate 11kV","Substation Rating","MVA","Non-Coincident",12.6]
[null,null,null,null,null,"Coincident",12.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.2118000000000002]
[null,null,null,null,null,"Coincident",6.1890999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.2218901372492912]
[null,null,null,null,null,"Coincident",6.2015079795159496]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.15905045333333331]
[null,null,null,null,null,"Coincident",0.29469503308984729]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9414300330471033]
[null,null,null,null,null,"Coincident",5.9197180555606792]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9510809948440873]
[null,null,null,null,null,"Coincident",5.9315859750277413]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3245500064318332]
[null,null,null,null,null,"Coincident",5.3050923154008913]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.333198939165599]
[null,null,null,null,null,"Coincident",5.3157280260502136]
[null,null,"Aldinga 11kV","Substation Rating","MVA","Non-Coincident",33.200000000000003]
[null,null,null,null,null,"Coincident",33.200000000000003]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.049099999999999]
[null,null,null,null,null,"Coincident",17.601900000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.473600544019565]
[null,null,null,null,null,"Coincident",18.036928504044141]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.45267469333333332]
[null,null,null,null,null,"Coincident",0.83873375356702207]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.302071441702392]
[null,null,null,null,null,"Coincident",15.898157321401143]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.68548325700889]
[null,null,null,null,null,"Coincident",16.291078062718135]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.544058083696694]
[null,null,null,null,null,"Coincident",14.183702011924188]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.886122816496746]
[null,null,null,null,null,"Coincident",14.534250229335676]
[null,null,"Allendale East 11kV","Substation Rating","MVA","Non-Coincident",6.8]
[null,null,null,null,null,"Coincident",6.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.8877190960994517]
[null,null,null,null,null,"Coincident",3.4825918348588214]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.2722187869224744]
[null,null,null,null,null,"Coincident",3.8270239943503532]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.14992572657231759]
[null,null,null,null,null,"Coincident",0.10741170084057394]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.5839337306286314]
[null,null,null,null,null,"Coincident",3.2104630088848118]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9383887149765178]
[null,null,null,null,null,"Coincident",3.5279813284448482]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3292676716083647]
[null,null,null,null,null,"Coincident",2.9823349173646503]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.6585359028663347]
[null,null,null,null,null,"Coincident",3.2772911179831321]
[null,null,"Alma 11kV","Substation Rating","MVA","Non-Coincident",0.19500000000000001]
[null,null,null,null,null,"Coincident",0.19500000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.3597309883471194E-2]
[null,null,null,null,null,"Coincident",8.3597309883471194E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.8464481133055051E-2]
[null,null,null,null,null,"Coincident",8.8464481133055051E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.6601445900636428E-4]
[null,null,null,null,null,"Coincident",1.6601445900636428E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3597309883471194E-2]
[null,null,null,null,null,"Coincident",8.3597309883471194E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.8464481133055051E-2]
[null,null,null,null,null,"Coincident",8.8464481133055051E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.5237578895124085E-2]
[null,null,null,null,null,"Coincident",7.5237578895124085E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.9618033019749554E-2]
[null,null,null,null,null,"Coincident",7.9618033019749554E-2]
[null,null,"American River 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.43099999999999999]
[null,null,null,null,null,"Coincident",0.29499999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.44766281954167242]
[null,null,null,null,null,"Coincident",0.30991934434623469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",3.2923607060340268E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.31405080176111816]
[null,null,null,null,null,"Coincident",0.21495356501051011]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.3261922677394547]
[null,null,null,null,null,"Coincident",0.22582463706082384]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.29419682721065488]
[null,null,null,null,null,"Coincident",0.20136441769638791]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.30557072197061713]
[null,null,null,null,null,"Coincident",0.21154823154957927]
[null,null,"Angaston 11kV","Substation Rating","MVA","Non-Coincident",28.96]
[null,null,null,null,null,"Coincident",28.96]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.3439]
[null,null,null,null,null,"Coincident",12.013199999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.343956331849313]
[null,null,null,null,null,"Coincident",12.032187861315995]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-02"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4518354500000001]
[null,null,null,null,null,"Coincident",0.31870470129191464]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.381031157397469]
[null,null,null,null,null,"Coincident",13.719323440629624]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.381095489537177]
[null,null,null,null,null,"Coincident",13.741007971881912]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.233202628196747]
[null,null,null,null,null,"Coincident",12.758002343369178]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.233262452545425]
[null,null,null,null,null,"Coincident",12.778167426707926]
[null,null,"Angle Vale 11kV","Substation Rating","MVA","Non-Coincident",27.3]
[null,null,null,null,null,"Coincident",27.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.273200000000003]
[null,null,null,null,null,"Coincident",17.034700000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.246616515124117]
[null,null,null,null,null,"Coincident",18.09533201961213]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.39695954666666661]
[null,null,null,null,null,"Coincident",0.73550250432230213]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.321112151155873]
[null,null,null,null,null,"Coincident",18.068143086474706]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.353582865521261]
[null,null,null,null,null,"Coincident",19.193120402919877]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.713959067433716]
[null,null,null,null,null,"Coincident",16.483180796031604]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.655860034790571]
[null,null,null,null,null,"Coincident",17.50947355946899]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Ardrossan 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0760000000000001]
[null,null,null,null,null,"Coincident",2.0760000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1582112964211824]
[null,null,null,null,null,"Coincident",2.1582112964211824]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11298407991615944]
[null,null,null,null,null,"Coincident",0.11298407991615944]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.7416685763077615]
[null,null,null,null,null,"Coincident",1.7416685763077615]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8106400751489444]
[null,null,null,null,null,"Coincident",1.8106400751489444]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5470299606820914]
[null,null,null,null,null,"Coincident",1.5470299606820914]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6082936112938859]
[null,null,null,null,null,"Coincident",1.6082936112938859]
[null,null,"Arno Bay 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.72112862714065062]
[null,null,null,null,null,"Coincident",0.49071923651766225]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.78115491421356353]
[null,null,null,null,null,"Coincident",0.53156639284288831]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.17776730000000002]
[null,null,null,null,null,"Coincident",2.7573099391947655E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.64213971096854017]
[null,null,null,null,null,"Coincident",0.43696824234200654]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.69559101102904519]
[null,null,null,null,null,"Coincident",0.47334120018805742]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.57490314923538088]
[null,null,null,null,null,"Coincident",0.39121458204066156]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.62275772077271896]
[null,null,null,null,null,"Coincident",0.42377903437948428]
[null,null,"Ascot Park 11kV","Substation Rating","MVA","Non-Coincident",27]
[null,null,null,null,null,"Coincident",27]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.5151]
[null,null,null,null,null,"Coincident",17.038599999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.5151]
[null,null,null,null,null,"Coincident",17.038599999999999]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.0419373333333335E-2]
[null,null,null,null,null,"Coincident",0.52423440603981242]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.163090821815885]
[null,null,null,null,null,"Coincident",17.668962168448488]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.163090821815885]
[null,null,null,null,null,"Coincident",17.668962168448488]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.977609366209874]
[null,null,null,null,null,"Coincident",15.542936948524618]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.977609366209874]
[null,null,null,null,null,"Coincident",15.542936948524618]
[null,null,"Athol Park 11kV","Substation Rating","MVA","Non-Coincident",26.5]
[null,null,null,null,null,"Coincident",26.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.908300000000001]
[null,null,null,null,null,"Coincident",16.0153]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.831612562390934]
[null,null,null,null,null,"Coincident",16.940780660288357]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.983774357073576]
[null,null,null,null,null,"Coincident",0.4845591984497572]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.890260515496376]
[null,null,null,null,null,"Coincident",17.892584661605785]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.039020317267791]
[null,null,null,null,null,"Coincident",18.926548500365485]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.37517970190877]
[null,null,null,null,null,"Coincident",16.45752177806045]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.351599649182067]
[null,null,null,null,null,"Coincident",17.40855723302348]
[null,null,"Auburn 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2072675445663008]
[null,null,null,null,null,"Coincident",3.2072675445663008]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.3411716948680272]
[null,null,null,null,null,"Coincident",3.3411716948680272]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.14645968505269588]
[null,null,null,null,null,"Coincident",0.14645968505269588]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.2072675445663008]
[null,null,null,null,null,"Coincident",3.2072675445663008]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.3411716948680272]
[null,null,null,null,null,"Coincident",3.3411716948680272]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8865407901096707]
[null,null,null,null,null,"Coincident",2.8865407901096707]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.0070545253812244]
[null,null,null,null,null,"Coincident",3.0070545253812244]
[null,null,"Balaklava 7.6kV","Substation Rating","MVA","Non-Coincident",5]
[null,null,null,null,null,"Coincident",5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.9137597915408193]
[null,null,null,null,null,"Coincident",2.9137597915408193]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.0671155700429678]
[null,null,null,null,null,"Coincident",3.0671155700429678]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.10483086772993751]
[null,null,null,null,null,"Coincident",0.10483086772993751]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.0620583887074799]
[null,null,null,null,null,"Coincident",2.8684614410547415]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.198712004344733]
[null,null,null,null,null,"Coincident",3.0009818582523824]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.7071504791154384]
[null,null,null,null,null,"Coincident",2.5359923877066648]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8279652560019763]
[null,null,null,null,null,"Coincident",2.6531530245619939]
[null,null,"Balhannah 33kV","Substation Rating","MVA","Non-Coincident",30.074368925935243]
[null,null,null,null,null,"Coincident",30.074368925935243]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.912500000000001]
[null,null,null,null,null,"Coincident",18.5823]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.64970095166845]
[null,null,null,null,null,"Coincident",19.359270222299187]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11720540821867566]
[null,null,null,null,null,"Coincident",1.0831924654980873]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.851821170034459]
[null,null,null,null,null,"Coincident",17.540139935383017]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.547677326310168]
[null,null,null,null,null,"Coincident",18.273534963165016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.150842490604241]
[null,null,null,null,null,"Coincident",15.868859241938145]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.780395244302621]
[null,null,null,null,null,"Coincident",16.53237404327292]
[null,null,"Baroota 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.28929462435879133]
[null,null,null,null,null,"Coincident",0.28929462435879133]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.29075585893188494]
[null,null,null,null,null,"Coincident",0.29075585893188494]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.0069565083802805E-3]
[null,null,null,null,null,"Coincident",6.0069565083802805E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.28929462435879133]
[null,null,null,null,null,"Coincident",0.28929462435879133]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.29075585893188494]
[null,null,null,null,null,"Coincident",0.29075585893188494]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.2603651619229122]
[null,null,null,null,null,"Coincident",0.2603651619229122]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.26168027303869645]
[null,null,null,null,null,"Coincident",0.26168027303869645]
[null,null,"Barossa South TF1 11kV","Substation Rating","MVA","Non-Coincident",8.9]
[null,null,null,null,null,"Coincident",8.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.41]
[null,null,null,null,null,"Coincident",1.77]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4311519903124119]
[null,null,null,null,null,"Coincident",1.771016657177453]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.24907134217405941]
[null,null,null,null,null,"Coincident",4.115775129532781E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8649745635946919]
[null,null,null,null,null,"Coincident",2.1041514429720349]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8901197562148]
[null,null,null,null,null,"Coincident",2.1053600309194618]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5872067462331607]
[null,null,null,null,null,"Coincident",1.9001476932915744]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.6099140375329659]
[null,null,null,null,null,"Coincident",1.9012391050376791]
[null,null,"Barossa South TF2 11kV","Substation Rating","MVA","Non-Coincident",8.9]
[null,null,null,null,null,"Coincident",8.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.91]
[null,null,null,null,null,"Coincident",2.14]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.1636515151328926]
[null,null,null,null,null,"Coincident",3.0691366864315444]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-02"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.20531105398011695]
[null,null,null,null,null,"Coincident",4.115775129532781E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.6672418925132719]
[null,null,null,null,null,"Coincident",2.7762940186088665]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.9963125393705274]
[null,null,null,null,null,"Coincident",3.9816943106695946]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.8265973638895785]
[null,null,null,null,null,"Coincident",2.4718981994456342]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.1195883561996975]
[null,null,null,null,null,"Coincident",3.5451371257208755]
[null,null,"Beachport 11kV","Substation Rating","MVA","Non-Coincident",2.7]
[null,null,null,null,null,"Coincident",2.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.228]
[null,null,null,null,null,"Coincident",0.91800000000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2791200100068796]
[null,null,null,null,null,"Coincident",0.95169585477714469]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.15265374794283026]
[null,null,null,null,null,"Coincident",5.6707426425467673E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.87617057665565956]
[null,null,null,null,null,"Coincident",0.65498745062695074]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.91264439477159665]
[null,null,null,null,null,"Coincident",0.67902923931668702]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.81517921590044584]
[null,null,null,null,null,"Coincident",0.60939293175619647]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.84911404462538975]
[null,null,null,null,null,"Coincident",0.63176114061314115]
[null,null,"Belvedere Road 7.6kV","Substation Rating","MVA","Non-Coincident",0.4]
[null,null,null,null,null,"Coincident",0.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.10506531634944399]
[null,null,null,null,null,"Coincident",0.10506531634944399]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.110118437464039]
[null,null,null,null,null,"Coincident",0.110118437464039]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7369262773540863E-3]
[null,null,null,null,null,"Coincident",1.7369262773540863E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.10506531634944399]
[null,null,null,null,null,"Coincident",0.10506531634944399]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.110118437464039]
[null,null,null,null,null,"Coincident",0.110118437464039]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.4558784714499591E-2]
[null,null,null,null,null,"Coincident",9.4558784714499591E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.9106593717635097E-2]
[null,null,null,null,null,"Coincident",9.9106593717635097E-2]
[null,null,"Berri 11kV","Substation Rating","MVA","Non-Coincident",28]
[null,null,null,null,null,"Coincident",28]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.5657]
[null,null,null,null,null,"Coincident",9.7350999999999992]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.382118049025376]
[null,null,null,null,null,"Coincident",10.139944357342401]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.5430969999999995]
[null,null,null,null,null,"Coincident",0.43978215901636242]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.031445584414064]
[null,null,null,null,null,"Coincident",10.127128138273459]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.88074042441357]
[null,null,null,null,null,"Coincident",10.548275397455539]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.926485107942106]
[null,null,null,null,null,"Coincident",9.1970589911831713]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.697781238269792]
[null,null,null,null,null,"Coincident",9.5795283481210252]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Binnies 11kV","Substation Rating","MVA","Non-Coincident",0.78]
[null,null,null,null,null,"Coincident",0.78]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.28582042194344964]
[null,null,null,null,null,"Coincident",0.28582042194344964]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.29483645519352664]
[null,null,null,null,null,"Coincident",0.29483645519352664]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.1879518439488831E-4]
[null,null,null,null,null,"Coincident",5.1879518439488831E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.28582042194344964]
[null,null,null,null,null,"Coincident",0.28582042194344964]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.29483645519352664]
[null,null,null,null,null,"Coincident",0.29483645519352664]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.25493877753103039]
[null,null,null,null,null,"Coincident",0.25493877753103039]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.26298066788765623]
[null,null,null,null,null,"Coincident",0.26298066788765623]
[null,null,"Birdwood 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4948182704092896]
[null,null,null,null,null,"Coincident",2.2863070659909179]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5987690316763432]
[null,null,null,null,null,"Coincident",2.3815698604072062]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.47721343999999993]
[null,null,null,null,null,"Coincident",0.141526634576013]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5100775531090438]
[null,null,null,null,null,"Coincident",2.3002910127465577]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6146641178219205]
[null,null,null,null,null,"Coincident",2.3961364716109976]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2349159064028177]
[null,null,null,null,null,"Coincident",2.0481267470700306]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3280374025029351]
[null,null,null,null,null,"Coincident",2.133465361531282]
[null,null,"Black Point 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.60542669159490925]
[null,null,null,null,null,"Coincident",0.60542669159490925]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.62529221506706434]
[null,null,null,null,null,"Coincident",0.62529221506706434]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1946296711061094E-2]
[null,null,null,null,null,"Coincident",1.1946296711061094E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.60542669159490925]
[null,null,null,null,null,"Coincident",0.60542669159490925]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.62529221506706434]
[null,null,null,null,null,"Coincident",0.62529221506706434]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.54488402243541834]
[null,null,null,null,null,"Coincident",0.54488402243541834]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.56276299356035797]
[null,null,null,null,null,"Coincident",0.56276299356035797]
[null,null,"Blackpool 7.6kV","Substation Rating","MVA","Non-Coincident",19.899999999999999]
[null,null,null,null,null,"Coincident",19.899999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.839600000000001]
[null,null,null,null,null,"Coincident",14.0359]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.310110944078753]
[null,null,null,null,null,"Coincident",14.479867555333509]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.3962879999999996E-2]
[null,null,null,null,null,"Coincident",0.57019326090325873]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.705289120209555]
[null,null,null,null,null,"Coincident",12.963022423943318]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.139835100075727]
[null,null,null,null,null,"Coincident",13.373053941358775]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.057938380629565]
[null,null,null,null,null,"Coincident",11.404890786589833]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.440252726778615]
[null,null,null,null,null,"Coincident",11.765637263934924]
[null,null,"Blackwood 11kV","Substation Rating","MVA","Non-Coincident",57.87557735849056]
[null,null,null,null,null,"Coincident",57.87557735849056]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.375300000000003]
[null,null,null,null,null,"Coincident",26.72]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.068039063140841]
[null,null,null,null,null,"Coincident",27.4158893497913]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.57130677333333335]
[null,null,null,null,null,"Coincident",1.0585400100625548]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.4397084254113]
[null,null,null,null,null,"Coincident",26.782866639890333]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.1340773604541]
[null,null,null,null,null,"Coincident",27.480393273557265]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",23.990723625121525]
[null,null,null,null,null,"Coincident",23.416442386503419]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.597815105694796]
[null,null,null,null,null,"Coincident",24.026294664451374]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Booleroo Centre 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.6148451277216076]
[null,null,null,null,null,"Coincident",0.52625072891445956]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.66112379324904036]
[null,null,null,null,null,"Coincident",0.5658609988327522]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.12567974333333337]
[null,null,null,null,null,"Coincident",2.9840753142937718E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.62839200502573633]
[null,null,null,null,null,"Coincident",0.53784560660704239]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.67569032798466266]
[null,null,null,null,null,"Coincident",0.57832860925488427]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.55923449406895853]
[null,null,null,null,null,"Coincident",0.47865315486593857]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.60132741297737469]
[null,null,null,null,null,"Coincident",0.51468081168380486]
[null,null,"Booyoolie 11kV","Substation Rating","MVA","Non-Coincident",0.2]
[null,null,null,null,null,"Coincident",0.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9599999999999999E-2]
[null,null,null,null,null,"Coincident",1.9599999999999999E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9946814501517363E-2]
[null,null,null,null,null,"Coincident",1.9946814501517363E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.1542747211209211E-4]
[null,null,null,null,null,"Coincident",3.1542747211209211E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9599999999999999E-2]
[null,null,null,null,null,"Coincident",1.9599999999999999E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9946814501517363E-2]
[null,null,null,null,null,"Coincident",1.9946814501517363E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9599999999999999E-2]
[null,null,null,null,null,"Coincident",1.9599999999999999E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9946814501517363E-2]
[null,null,null,null,null,"Coincident",1.9946814501517363E-2]
[null,null,"Bordertown 11kV","Substation Rating","MVA","Non-Coincident",13.4]
[null,null,null,null,null,"Coincident",13.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.6252999999999993]
[null,null,null,null,null,"Coincident",9.1829999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.6255603852451106]
[null,null,null,null,null,"Coincident",9.1860758918049434]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.1359636726451735E-2]
[null,null,null,null,null,"Coincident",0.28982043353727294]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.023373050148194]
[null,null,null,null,null,"Coincident",9.5627808711947555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.02364420413285]
[null,null,null,null,null,"Coincident",9.5659839725030622]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.237446094443527]
[null,null,null,null,null,"Coincident",8.8129686851604543]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.2376959873991229]
[null,null,null,null,null,"Coincident",8.8159206331247262]
[null,null,"Brinkworth Town 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.78877593776686672]
[null,null,null,null,null,"Coincident",0.63102075021349335]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.85736514974659417]
[null,null,null,null,null,"Coincident",0.68589211979727538]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.0569173333333329E-2]
[null,null,null,null,null,"Coincident",3.8111385972561015E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.8347799380722053]
[null,null,null,null,null,"Coincident",0.66782395045776421]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.90736949790457078]
[null,null,null,null,null,"Coincident",0.72589559832365669]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.74805990807274259]
[null,null,null,null,null,"Coincident",0.598447926458194]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.81310859573124183]
[null,null,null,null,null,"Coincident",0.65048687658499349]
[null,null,"Brukunga 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.48578164375905625]
[null,null,null,null,null,"Coincident",0.48578164375905625]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.51366403248944414]
[null,null,null,null,null,"Coincident",0.51366403248944414]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.5778240985669477E-2]
[null,null,null,null,null,"Coincident",2.5778240985669477E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.48578164375905625]
[null,null,null,null,null,"Coincident",0.48578164375905625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.51366403248944414]
[null,null,null,null,null,"Coincident",0.51366403248944414]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.43720347938315057]
[null,null,null,null,null,"Coincident",0.43720347938315057]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.46229762924049972]
[null,null,null,null,null,"Coincident",0.46229762924049972]
[null,null,"Bungama Napperby 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.98871349068777237]
[null,null,null,null,null,"Coincident",0.90011909188062433]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0631327856857766]
[null,null,null,null,null,"Coincident",0.96786999126948847]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.0453600000000005E-3]
[null,null,null,null,null,"Coincident",7.8407591398337056E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0382844317222915]
[null,null,null,null,null,"Coincident",0.94524819232065249]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1164348728196682]
[null,null,null,null,null,"Coincident",1.0163959057211316]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.93079887778294712]
[null,null,null,null,null,"Coincident",0.84739396041888382]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0008590083687603]
[null,null,null,null,null,"Coincident",0.91117630152568152]
[null,null,"Burnside 11kV","Substation Rating","MVA","Non-Coincident",31.2]
[null,null,null,null,null,"Coincident",31.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.47]
[null,null,null,null,null,"Coincident",12.83]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.945357650487134]
[null,null,null,null,null,"Coincident",13.245112306054637]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.19949635999999998]
[null,null,null,null,null,"Coincident",0.36963482454396079]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.56949616709592]
[null,null,null,null,null,"Coincident",12.924768806521206]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.048365047295242]
[null,null,null,null,null,"Coincident",13.342947339997281]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.919266836856192]
[null,null,null,null,null,"Coincident",11.352946808972897]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.339898958541207]
[null,null,null,null,null,"Coincident",11.720269328878459]
[null,null,"Burra 11kV","Substation Rating","MVA","Non-Coincident",11.4]
[null,null,null,null,null,"Coincident",11.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.9621]
[null,null,null,null,null,"Coincident",2.5906000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.0928595910580872]
[null,null,null,null,null,"Coincident",2.7021844145061604]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.1160000000000002E-2]
[null,null,null,null,null,"Coincident",7.6262892106048585E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.022053926308335]
[null,null,null,null,null,"Coincident",2.6430346380926957]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.1554601366184412]
[null,null,null,null,null,"Coincident",2.756877559659543]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8000636511828114]
[null,null,null,null,null,"Coincident",2.448885889995001]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9236702741750396]
[null,null,null,null,null,"Coincident",2.5543662799538867]
[null,null,"Cadell 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3117653428866558]
[null,null,null,null,null,"Coincident",2.3117653428866558]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4307657686002742]
[null,null,null,null,null,"Coincident",2.4307657686002742]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.7091138665644807E-2]
[null,null,null,null,null,"Coincident",2.7091138665644807E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3117653428866558]
[null,null,null,null,null,"Coincident",2.3117653428866558]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4307657686002742]
[null,null,null,null,null,"Coincident",2.4307657686002742]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0805888085979904]
[null,null,null,null,null,"Coincident",2.0805888085979904]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.187689191740247]
[null,null,null,null,null,"Coincident",2.187689191740247]
[null,null,"Caloote 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5642046496046815]
[null,null,null,null,null,"Coincident",1.0716194316839192]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7121899583087541]
[null,null,null,null,null,"Coincident",1.1730025419125625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",7.4523198921044392E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.432461714633134]
[null,null,null,null,null,"Coincident",0.98136379337069646]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5679831690031383]
[null,null,null,null,null,"Coincident",1.0742080538385741]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.302493041897689]
[null,null,null,null,null,"Coincident",0.89232368263539719]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4257185002409112]
[null,null,null,null,null,"Coincident",0.97674409122587624]
[null,null,"Caltowie 11kV","Substation Rating","MVA","Non-Coincident",0.3]
[null,null,null,null,null,"Coincident",0.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.10276950261629177]
[null,null,null,null,null,"Coincident",8.1506846902576216E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.11050484152289436]
[null,null,null,null,null,"Coincident",8.7641770862985177E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.8380800000000002E-3]
[null,null,null,null,null,"Coincident",5.2585079890265889E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.9105043598469458E-2]
[null,null,null,null,null,"Coincident",7.860055181947577E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.10656456300910692]
[null,null,null,null,null,"Coincident",8.4516722386533086E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.9298111670384456E-2]
[null,null,null,null,null,"Coincident",7.0822640290304911E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.6019474914391875E-2]
[null,null,null,null,null,"Coincident",7.6153376656241833E-2]
[null,null,"Cambrai 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.92682111020040003]
[null,null,null,null,null,"Coincident",0.92682111020040003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.97139661317446802]
[null,null,null,null,null,"Coincident",0.97139661317446802]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.2976055263024552E-2]
[null,null,null,null,null,"Coincident",2.2976055263024552E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.92682111020040003]
[null,null,null,null,null,"Coincident",0.92682111020040003]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.97139661317446802]
[null,null,null,null,null,"Coincident",0.97139661317446802]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.83413899918036005]
[null,null,null,null,null,"Coincident",0.83413899918036005]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.87425695185702124]
[null,null,null,null,null,"Coincident",0.87425695185702124]
[null,null,"Campbell Park 11kV","Substation Rating","MVA","Non-Coincident",1.95]
[null,null,null,null,null,"Coincident",1.95]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4163265418390578]
[null,null,null,null,null,"Coincident",1.4163265418390578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4610037104869789]
[null,null,null,null,null,"Coincident",1.4610037104869789]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1161359597071627E-2]
[null,null,null,null,null,"Coincident",1.1161359597071627E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4163265418390578]
[null,null,null,null,null,"Coincident",1.4163265418390578]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4610037104869789]
[null,null,null,null,null,"Coincident",1.4610037104869789]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2746938876551521]
[null,null,null,null,null,"Coincident",1.2746938876551521]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.314903339438281]
[null,null,null,null,null,"Coincident",1.314903339438281]
[null,null,"Campbelltown 11kV","Substation Rating","MVA","Non-Coincident",57.8]
[null,null,null,null,null,"Coincident",57.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",49.079899999999995]
[null,null,null,null,null,"Coincident",46.326499999999996]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",51.170302380384655]
[null,null,null,null,null,"Coincident",48.163252363705666]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.73082986666666672]
[null,null,null,null,null,"Coincident",1.3541107694236607]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",51.399518279746609]
[null,null,null,null,null,"Coincident",48.515986861967555]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",53.588717429757246]
[null,null,null,null,null,"Coincident",50.439547967301053]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",45.584920339613362]
[null,null,null,null,null,"Coincident",43.027589952569144]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",47.526465167283611]
[null,null,null,null,null,"Coincident",44.733547181151913]
[null,null,"Cape Jervis 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.52409954201996745]
[null,null,null,null,null,"Coincident",0.40724345684271696]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.5696715106094038]
[null,null,null,null,null,"Coincident",0.44265445138768594]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.6422699999999996E-3]
[null,null,null,null,null,"Coincident",3.8450678023155278E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.3820396685997845]
[null,null,null,null,null,"Coincident",0.29685802565668856]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.4152591209775634]
[null,null,null,null,null,"Coincident",0.32267068820664613]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.34865582593352679]
[null,null,null,null,null,"Coincident",0.27091762617131332]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.37897245679095526]
[null,null,null,null,null,"Coincident",0.2944746960794824]
[null,null,"Caralue 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2195]
[null,null,null,null,null,"Coincident",2.0800999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2713827374531137]
[null,null,null,null,null,"Coincident",2.1531777562477274]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",6.2219106464478958E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4786809164627641]
[null,null,null,null,null,"Coincident",2.323002556582201]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5366222326235577]
[null,null,null,null,null,"Coincident",2.4046139284358437]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1964476516920013]
[null,null,null,null,null,"Coincident",2.0584954991144544]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2477915205103138]
[null,null,null,null,null,"Coincident",2.1308142493290263]
[null,null,"Cavan 11kV","Substation Rating","MVA","Non-Coincident",58.2263989747971]
[null,null,null,null,null,"Coincident",58.2263989747971]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.58]
[null,null,null,null,null,"Coincident",31.48]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.402329356433576]
[null,null,null,null,null,"Coincident",33.294083558494293]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2751891266666666]
[null,null,null,null,null,"Coincident",0.42272330869481783]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.174674820123485]
[null,null,null,null,null,"Coincident",33.775681937534777]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",41.202822808238729]
[null,null,null,null,null,"Coincident",35.722057708812244]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",35.382741428189341]
[null,null,null,null,null,"Coincident",31.305472179859485]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",38.189423548590618]
[null,null,null,null,null,"Coincident",33.109498303505724]
[null,null,"Ceduna 11kV","Substation Rating","MVA","Non-Coincident",14.2]
[null,null,null,null,null,"Coincident",14.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.9801219194824951]
[null,null,null,null,null,"Coincident",5.8376999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.4302386230994566]
[null,null,null,null,null,"Coincident",6.0597579530869048]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-12-12"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.5771826666666657E-2]
[null,null,null,null,null,"Coincident",0.24708727419866594]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.3302380526423461]
[null,null,null,null,null,"Coincident",6.1794778062163873]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.8067075834863937]
[null,null,null,null,null,"Coincident",6.4145365096088822]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.7050101158853499]
[null,null,null,null,null,"Coincident",5.5691402285634277]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.1344194794466125]
[null,null,null,null,null,"Coincident",5.7809825431066093]
[null,null,"Chain of Ponds 11kV","Substation Rating","MVA","Non-Coincident",0.62]
[null,null,null,null,null,"Coincident",0.62]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.49713841894084176]
[null,null,null,null,null,"Coincident",0.3178728924082706]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.51251383395963068]
[null,null,null,null,null,"Coincident",0.32770401279203154]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-01"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.2938053378335374E-5]
[null,null,null,null,null,"Coincident",1.7136496667475687E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.54211812649702329]
[null,null,null,null,null,"Coincident",0.34663315151482532]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.55888466649177659]
[null,null,null,null,null,"Coincident",0.35735376444827355]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.49109333096161778]
[null,null,null,null,null,"Coincident",0.31400763169293033]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.50628178449651318]
[null,null,null,null,null,"Coincident",0.32371920793085601]
[null,null,"Cheltenham 11kV","Substation Rating","MVA","Non-Coincident",29.9]
[null,null,null,null,null,"Coincident",29.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",12.99]
[null,null,null,null,null,"Coincident",12.48]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.247645073748012]
[null,null,null,null,null,"Coincident",12.764513308387437]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.3662948036641696E-2]
[null,null,null,null,null,"Coincident",0.21868894460007424]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.2527003834387417E-3]
[null,null,null,null,null,"Coincident",8.8894303914792538E-3]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.4362194498482359E-3]
[null,null,null,null,null,"Coincident",9.0920875429503743E-3]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.7120717137755829E-3]
[null,null,null,null,null,"Coincident",7.4092882977612991E-3]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.8650337834788673E-3]
[null,null,null,null,null,"Coincident",7.578201849555561E-3]
[null,null,"Cheltenham 33kV","Substation Rating","MVA","Non-Coincident",19]
[null,null,null,null,null,"Coincident",19]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.7767999999999997]
[null,null,null,null,null,"Coincident",2.2774999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.5435863707531423]
[null,null,null,null,null,"Coincident",2.68900769987741]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-02"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.2791094665729269E-2]
[null,null,null,null,null,"Coincident",1.0375903687897767E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.7793231501176816]
[null,null,null,null,null,"Coincident",2.7554866174830472]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.7070375663981112]
[null,null,null,null,null,"Coincident",3.2533588282419643]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3894305132034228]
[null,null,null,null,null,"Coincident",2.5695921943185387]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.2545581852109384]
[null,null,null,null,null,"Coincident",3.0338762661108412]
[null,null,"Clare 11kV","Substation Rating","MVA","Non-Coincident",12.6]
[null,null,null,null,null,"Coincident",12.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.7827999999999999]
[null,null,null,null,null,"Coincident",2.5906000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.1810746037705186]
[null,null,null,null,null,"Coincident",2.7021844145061604]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.7556645570947671E-2]
[null,null,null,null,null,"Coincident",0.34709213619163404]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.440083336025344]
[null,null,null,null,null,"Coincident",2.7844741870823948]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.8681638399894744]
[null,null,null,null,null,"Coincident",2.9044093070828216]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.4730416766042858]
[null,null,null,null,null,"Coincident",2.499232792208756]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.8572696353965465]
[null,null,null,null,null,"Coincident",2.6068817645831905]
[null,null,"Clarence Gardens 11kV","Substation Rating","MVA","Non-Coincident",35.9]
[null,null,null,null,null,"Coincident",35.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.989999999999998]
[null,null,null,null,null,"Coincident",17.149999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.566318967420546]
[null,null,null,null,null,"Coincident",17.659178916359615]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.3913200000000006E-2]
[null,null,null,null,null,"Coincident",0.56954891728424029]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.549123837079307]
[null,null,null,null,null,"Coincident",17.683016887488055]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.143354626203344]
[null,null,null,null,null,"Coincident",18.208020932779014]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.295631652732158]
[null,null,null,null,null,"Coincident",15.534746128090969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.817670652596981]
[null,null,null,null,null,"Coincident",15.99596858869873]
[null,null,"Clarendon 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6345999999999998]
[null,null,null,null,null,"Coincident",2.4561000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6980318233853358]
[null,null,null,null,null,"Coincident",2.5240217451519711]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.8360346859729523E-2]
[null,null,null,null,null,"Coincident",0.16968320561867678]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5795734252255862]
[null,null,null,null,null,"Coincident",2.4048015978503616]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6416804038631083]
[null,null,null,null,null,"Coincident",2.4713047212045591]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.3032198344000721]
[null,null,null,null,null,"Coincident",2.1471715764328616]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3586731987640244]
[null,null,null,null,null,"Coincident",2.2065501199009732]
[null,null,"Clearview 11kV","Substation Rating","MVA","Non-Coincident",26.6]
[null,null,null,null,null,"Coincident",26.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.892299999999999]
[null,null,null,null,null,"Coincident",20.499000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.362470380975353]
[null,null,null,null,null,"Coincident",20.936174154080781]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.67269162548415584]
[null,null,null,null,null,"Coincident",0.67269162548415584]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.876360485543991]
[null,null,null,null,null,"Coincident",21.420431548679964]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.367665059518302]
[null,null,null,null,null,"Coincident",21.877256712948437]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.124224699839537]
[null,null,null,null,null,"Coincident",18.843450990622763]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.556422979323976]
[null,null,null,null,null,"Coincident",19.24531789860794]
[null,null,"Cleve 11kV","Substation Rating","MVA","Non-Coincident",6.9624697336561745]
[null,null,null,null,null,"Coincident",6.9624697336561745]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5122]
[null,null,null,null,null,"Coincident",2.3597000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6129551852261073]
[null,null,null,null,null,"Coincident",2.4528107244547024]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.0907919999999995E-2]
[null,null,null,null,null,"Coincident",9.4324227655572218E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2317674916534753]
[null,null,null,null,null,"Coincident",2.0962908009134251]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3212755511245171]
[null,null,null,null,null,"Coincident",2.1790077374480594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0345167216959457]
[null,null,null,null,null,"Coincident",1.9110138954645026]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1161137717477279]
[null,null,null,null,null,"Coincident",1.9864200438095052]
[null,null,"Cleve 33kV","Substation Rating","MVA","Non-Coincident",17.8]
[null,null,null,null,null,"Coincident",17.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2000000000000002]
[null,null,null,null,null,"Coincident",2.2000000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2022715545545242]
[null,null,null,null,null,"Coincident",2.2000000000000002]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.2277999999999987E-3]
[null,null,null,null,null,"Coincident",4.0362265345922299E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1589372199291317]
[null,null,null,null,null,"Coincident",2.1589372199291317]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.161166376144978]
[null,null,null,null,null,"Coincident",2.1589372199291317]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.904498994892823]
[null,null,null,null,null,"Coincident",1.904498994892823]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9064654373318846]
[null,null,null,null,null,"Coincident",1.904498994892823]
[null,null,"Coffin Bay 11kV","Substation Rating","MVA","Non-Coincident",2.7]
[null,null,null,null,null,"Coincident",2.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.44]
[null,null,null,null,null,"Coincident",1.026]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4691089135935429]
[null,null,null,null,null,"Coincident",1.0377918866516542]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.9899375E-2]
[null,null,null,null,null,"Coincident",8.0385584504706634E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1108449880050002]
[null,null,null,null,null,"Coincident",0.79147705395356271]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1333001899297626]
[null,null,null,null,null,"Coincident",0.80057355269391905]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.9792742039016632]
[null,null,null,null,null,"Coincident",0.69773287027993502]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.99906976514177359]
[null,null,null,null,null,"Coincident",0.7057519608447248]
[null,null,"Collinsfield 11kV","Substation Rating","MVA","Non-Coincident",2.7]
[null,null,null,null,null,"Coincident",2.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.5658609988327522]
[null,null,null,null,null,"Coincident",0.48393499563474424]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.5658609988327522]
[null,null,null,null,null,"Coincident",0.48393499563474424]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.8366503333333328E-2]
[null,null,null,null,null,"Coincident",2.2663394698562565E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.56614722159321074]
[null,null,null,null,null,"Coincident",0.48417977873628115]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.56614722159321074]
[null,null,null,null,null,"Coincident",0.48417977873628115]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.51341260124944754]
[null,null,null,null,null,"Coincident",0.43908013709548704]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.51341260124944754]
[null,null,null,null,null,"Coincident",0.43908013709548704]
[null,null,"Coomandook 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.47210884727968594]
[null,null,null,null,null,"Coincident",0.47210884727968594]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.48700123682899293]
[null,null,null,null,null,"Coincident",0.48700123682899293]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.3126901619015729E-2]
[null,null,null,null,null,"Coincident",1.3126901619015729E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.47210884727968594]
[null,null,null,null,null,"Coincident",0.47210884727968594]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.48700123682899293]
[null,null,null,null,null,"Coincident",0.48700123682899293]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.42489796255171736]
[null,null,null,null,null,"Coincident",0.42489796255171736]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.43830111314609366]
[null,null,null,null,null,"Coincident",0.43830111314609366]
[null,null,"Coonalpyn 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.4289]
[null,null,null,null,null,"Coincident",0.39019999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.45669773373643974]
[null,null,null,null,null,"Coincident",0.41341939964157459]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7159513953869808E-3]
[null,null,null,null,null,"Coincident",1.5858531196582946E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.42419482736537256]
[null,null,null,null,null,"Coincident",0.38591937896471989]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.45168761091276738]
[null,null,null,null,null,"Coincident",0.40888405423281349]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.37876252261193244]
[null,null,null,null,null,"Coincident",0.34458646846159019]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.40331076171873759]
[null,null,null,null,null,"Coincident",0.36509157077396465]
[null,null,"Coonawarra 11kV","Substation Rating","MVA","Non-Coincident",13.5]
[null,null,null,null,null,"Coincident",13.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8058000000000001]
[null,null,null,null,null,"Coincident",1.6092]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.1499193957941212]
[null,null,null,null,null,"Coincident",1.8398882139956221]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.9244079999999998E-2]
[null,null,null,null,null,"Coincident",2.1411714850345834E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.6402097017092729]
[null,null,null,null,null,"Coincident",2.0877558813851884]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.0866658864395076]
[null,null,null,null,null,"Coincident",2.3870478746337622]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.1368823068209899]
[null,null,null,null,null,"Coincident",1.7990843995068562]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5216075345993447]
[null,null,null,null,null,"Coincident",2.0569936506562616]
[null,null,"Cordola 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9418828880247907]
[null,null,null,null,null,"Coincident",1.9418828880247907]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0418432456242299]
[null,null,null,null,null,"Coincident",2.0418432456242299]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.4125309639126966E-2]
[null,null,null,null,null,"Coincident",3.4125309639126966E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9418828880247907]
[null,null,null,null,null,"Coincident",1.9418828880247907]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0418432456242299]
[null,null,null,null,null,"Coincident",2.0418432456242299]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7476945992223119]
[null,null,null,null,null,"Coincident",1.7476945992223119]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8376589210618071]
[null,null,null,null,null,"Coincident",1.8376589210618071]
[null,null,"Coromandel Place 11kV","Substation Rating","MVA","Non-Coincident",93]
[null,null,null,null,null,"Coincident",93]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",47.782300000000006]
[null,null,null,null,null,"Coincident",30.294499999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",49.853493493836524]
[null,null,null,null,null,"Coincident",31.250836466565175]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.8932466666666674E-2]
[null,null,null,null,null,"Coincident",8.1890090539451822E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",52.026934810579426]
[null,null,null,null,null,"Coincident",32.985644822854866]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",54.282118191955554]
[null,null,null,null,null,"Coincident",34.026935321699966]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",48.844823254710235]
[null,null,null,null,null,"Coincident",30.968151346624566]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",50.962073368931406]
[null,null,null,null,null,"Coincident",31.945753632019159]
[null,null,"Cowell 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.077]
[null,null,null,null,null,"Coincident",1.9750000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0994201580436442]
[null,null,null,null,null,"Coincident",1.9976548750972978]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0841364599322669E-2]
[null,null,null,null,null,"Coincident",0.10019404930354413]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0592978646357714]
[null,null,null,null,null,"Coincident",1.9581672039747948]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0815269371365286]
[null,null,null,null,null,"Coincident",1.9806289930510852]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8033184133441464]
[null,null,null,null,null,"Coincident",1.7147587223662444]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8227843179325862]
[null,null,null,null,null,"Coincident",1.7344284158736918]
[null,null,"Croydon 11kV","Substation Rating","MVA","Non-Coincident",48.4]
[null,null,null,null,null,"Coincident",48.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.083600000000001]
[null,null,null,null,null,"Coincident",24.606999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.170420624216831]
[null,null,null,null,null,"Coincident",24.623354692039833]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7930871108594089]
[null,null,null,null,null,"Coincident",0.49136146797581476]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.302030932825375]
[null,null,null,null,null,"Coincident",26.78327971918042]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",27.396530102321584]
[null,null,null,null,null,"Coincident",26.801080844535964]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.718044203348818]
[null,null,null,null,null,"Coincident",24.248389932537766]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",24.803599547364588]
[null,null,null,null,null,"Coincident",24.264506279504417]
[null,null,"Croydon Park 11kV","Substation Rating","MVA","Non-Coincident",26.4]
[null,null,null,null,null,"Coincident",26.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.7148]
[null,null,null,null,null,"Coincident",15.8963]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.392622754489906]
[null,null,null,null,null,"Coincident",16.499704463413885]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.43334944459332209]
[null,null,null,null,null,"Coincident",0.43334944459332209]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",17.458110000113123]
[null,null,null,null,null,"Coincident",16.603211165840946]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.166075647830382]
[null,null,null,null,null,"Coincident",17.233449128415362]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.805692048046598]
[null,null,null,null,null,"Coincident",15.031709772379157]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.446648429255237]
[null,null,null,null,null,"Coincident",15.602295428751754]
[null,null,"Crystal Brook 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0579999999999998]
[null,null,null,null,null,"Coincident",2.0579999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0944155226593231]
[null,null,null,null,null,"Coincident",2.0944155226593231]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.2868834231616529E-2]
[null,null,null,null,null,"Coincident",9.2868834231616529E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0579999999999998]
[null,null,null,null,null,"Coincident",2.0579999999999998]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0944155226593231]
[null,null,null,null,null,"Coincident",2.0944155226593231]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8521999999999998]
[null,null,null,null,null,"Coincident",1.8521999999999998]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8849739703933908]
[null,null,null,null,null,"Coincident",1.8849739703933908]
[null,null,"Cudmore Park 11kV","Substation Rating","MVA","Non-Coincident",22.1]
[null,null,null,null,null,"Coincident",22.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.6553]
[null,null,null,null,null,"Coincident",11.446100000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.111423635374443]
[null,null,null,null,null,"Coincident",11.938780410913003]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4348091666666669]
[null,null,null,null,null,"Coincident",0.24012002780397082]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.413582264390286]
[null,null,null,null,null,"Coincident",12.654452574041755]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.02342731954332]
[null,null,null,null,null,"Coincident",13.19914473067659]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.986718973010085]
[null,null,null,null,null,"Coincident",11.673862616522712]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.471817589310209]
[null,null,null,null,null,"Coincident",12.176346731710446]
[null,null,"Cummins 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8119772315239238]
[null,null,null,null,null,"Coincident",1.7880870651853729]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8785823058892039]
[null,null,null,null,null,"Coincident",1.8538139793409689]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.14614373878539938]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5879412480500432]
[null,null,null,null,null,"Coincident",1.5670049029946165]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6463111563877533]
[null,null,null,null,null,"Coincident",1.6246052283623567]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4075219884627153]
[null,null,null,null,null,"Coincident",1.38896439632274]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4592600043060389]
[null,null,null,null,null,"Coincident",1.4400202679409488]
[null,null,"Curramulka 7.6kV","Substation Rating","MVA","Non-Coincident",0.26]
[null,null,null,null,null,"Coincident",0.26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.25145029348323494]
[null,null,null,null,null,"Coincident",0.25145029348323494]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.25970098968909988]
[null,null,null,null,null,"Coincident",0.25970098968909988]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1631388034133397E-2]
[null,null,null,null,null,"Coincident",1.1631388034133397E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.25145029348323494]
[null,null,null,null,null,"Coincident",0.25145029348323494]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.25970098968909988]
[null,null,null,null,null,"Coincident",0.25970098968909988]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.22630526413491148]
[null,null,null,null,null,"Coincident",0.22630526413491148]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.2337308907201899]
[null,null,null,null,null,"Coincident",0.2337308907201899]
[null,null,"Curramulka South 11kV","Substation Rating","MVA","Non-Coincident",0.2]
[null,null,null,null,null,"Coincident",0.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.9727548947198201E-2]
[null,null,null,null,null,"Coincident",2.9727548947198201E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.0702982190526931E-2]
[null,null,null,null,null,"Coincident",3.0702982190526931E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4834083639131174E-3]
[null,null,null,null,null,"Coincident",1.4834083639131174E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.9727548947198201E-2]
[null,null,null,null,null,"Coincident",2.9727548947198201E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.0702982190526931E-2]
[null,null,null,null,null,"Coincident",3.0702982190526931E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6754794052478381E-2]
[null,null,null,null,null,"Coincident",2.6754794052478381E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7632683971474239E-2]
[null,null,null,null,null,"Coincident",2.7632683971474239E-2]
[null,null,"Darke Peak 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.6865819293567953]
[null,null,null,null,null,"Coincident",0.6865819293567953]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.6944473388845166]
[null,null,null,null,null,"Coincident",0.6944473388845166]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2553805871987509E-2]
[null,null,null,null,null,"Coincident",1.2553805871987509E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.6865819293567953]
[null,null,null,null,null,"Coincident",0.6865819293567953]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.6944473388845166]
[null,null,null,null,null,"Coincident",0.6944473388845166]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.61792373642111575]
[null,null,null,null,null,"Coincident",0.61792373642111575]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.62500260499606497]
[null,null,null,null,null,"Coincident",0.62500260499606497]
[null,null,"Deloraine 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.37625435973714239]
[null,null,null,null,null,"Coincident",0.37625435973714239]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.39023529527137457]
[null,null,null,null,null,"Coincident",0.39023529527137457]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.9666314918313294E-2]
[null,null,null,null,null,"Coincident",1.9666314918313294E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.37625435973714239]
[null,null,null,null,null,"Coincident",0.37625435973714239]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.39023529527137457]
[null,null,null,null,null,"Coincident",0.39023529527137457]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.33862892376342818]
[null,null,null,null,null,"Coincident",0.33862892376342818]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.35121176574423713]
[null,null,null,null,null,"Coincident",0.35121176574423713]
[null,null,"Desert Camp 11kV","Substation Rating","MVA","Non-Coincident",0.7]
[null,null,null,null,null,"Coincident",0.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.7491929837694827E-2]
[null,null,null,null,null,"Coincident",5.7491929837694827E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.9178899609927657E-2]
[null,null,null,null,null,"Coincident",5.9178899609927657E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.1256964218214973E-4]
[null,null,null,null,null,"Coincident",5.1256964218214973E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.7491929837694827E-2]
[null,null,null,null,null,"Coincident",5.7491929837694827E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9178899609927657E-2]
[null,null,null,null,null,"Coincident",5.9178899609927657E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.1742736853925345E-2]
[null,null,null,null,null,"Coincident",5.1742736853925345E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.326100964893489E-2]
[null,null,null,null,null,"Coincident",5.326100964893489E-2]
[null,null,"Direk 11kV","Substation Rating","MVA","Non-Coincident",56.4]
[null,null,null,null,null,"Coincident",56.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.55]
[null,null,null,null,null,"Coincident",21.439999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.343063800651873]
[null,null,null,null,null,"Coincident",22.192487467609393]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.82929111999999994]
[null,null,null,null,null,"Coincident",0.50027004595051572]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.416075337346719]
[null,null,null,null,null,"Coincident",23.296550126808054]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.277812771378589]
[null,null,null,null,null,"Coincident",24.114197608569114]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.639821822938909]
[null,null,null,null,null,"Coincident",21.529363335675644]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.436191165877624]
[null,null,null,null,null,"Coincident",22.284987220736518]
[null,null,"Dorrien TF4 11kV","Substation Rating","MVA","Non-Coincident",13.6]
[null,null,null,null,null,"Coincident",13.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.98]
[null,null,null,null,null,"Coincident",7.2210000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.3908047820218066]
[null,null,null,null,null,"Coincident",7.6262414995854941]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.1378287416357254E-2]
[null,null,null,null,null,"Coincident",0.19757449939038665]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.2730074916797616]
[null,null,null,null,null,"Coincident",8.3910259520575892]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.750375389086539]
[null,null,null,null,null,"Coincident",8.8619291427337572]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.3557823273291731]
[null,null,null,null,null,"Coincident",7.5610406247674131]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.7859321190083861]
[null,null,null,null,null,"Coincident",7.9853651561630068]
[null,null,"Dorrien TF5 11kV","Substation Rating","MVA","Non-Coincident",13.6]
[null,null,null,null,null,"Coincident",13.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.5]
[null,null,null,null,null,"Coincident",2.931]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9037283729788372]
[null,null,null,null,null,"Coincident",3.1296690384128478]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-20"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.32397487348931375]
[null,null,null,null,null,"Coincident",0.19757449939038665]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.2620848266695246]
[null,null,null,null,null,"Coincident",3.5691916077052506]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.7537204188321178]
[null,null,null,null,null,"Coincident",3.8111185488905144]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.7931733577711801]
[null,null,null,null,null,"Coincident",3.1765117461792367]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.2307195601025036]
[null,null,null,null,null,"Coincident",3.3918220614711321]
[null,null,"Dowlingville 11kV","Substation Rating","MVA","Non-Coincident",0.3]
[null,null,null,null,null,"Coincident",0.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.6143151450710884E-2]
[null,null,null,null,null,"Coincident",3.6143151450710884E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.9064021291644047E-2]
[null,null,null,null,null,"Coincident",3.9064021291644047E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.8676626638215979E-3]
[null,null,null,null,null,"Coincident",1.8676626638215979E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.6143151450710884E-2]
[null,null,null,null,null,"Coincident",3.6143151450710884E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9064021291644047E-2]
[null,null,null,null,null,"Coincident",3.9064021291644047E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6143151450710884E-2]
[null,null,null,null,null,"Coincident",3.6143151450710884E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9064021291644047E-2]
[null,null,null,null,null,"Coincident",3.9064021291644047E-2]
[null,null,"East Terrace 11kV","Substation Rating","MVA","Non-Coincident",77.099999999999994]
[null,null,null,null,null,"Coincident",77.099999999999994]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",43.302999999999997]
[null,null,null,null,null,"Coincident",30.040099999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",46.186494418715085]
[null,null,null,null,null,"Coincident",31.716753908620596]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.47882128500000004]
[null,null,null,null,null,"Coincident",9.3563155120064939E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",46.439653298511622]
[null,null,null,null,null,"Coincident",32.216054985858236]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",49.532013668308686]
[null,null,null,null,null,"Coincident",34.014157339458102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",43.296988481025224]
[null,null,null,null,null,"Coincident",30.035929696992032]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.180082599959427]
[null,null,null,null,null,"Coincident",31.712350844908158]
[null,null,"East Terrace 33kV","Substation Rating","MVA","Non-Coincident",47.5]
[null,null,null,null,null,"Coincident",47.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.279]
[null,null,null,null,null,"Coincident",6.6153000000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.034082989991386]
[null,null,null,null,null,"Coincident",7.0425019943199167]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.8855200000000003E-2]
[null,null,null,null,null,"Coincident",3.0712674916177391E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.489143382530937]
[null,null,null,null,null,"Coincident",6.7505428756160049]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.280107204912564]
[null,null,null,null,null,"Coincident",7.1864785669988986]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9428953499393735]
[null,null,null,null,null,"Coincident",6.3989916926212613]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.640590310533112]
[null,null,null,null,null,"Coincident",6.8122249568306517]
[null,null,"Edinburgh 11kV","Substation Rating","MVA","Non-Coincident",56.3]
[null,null,null,null,null,"Coincident",56.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.6624]
[null,null,null,null,null,"Coincident",10.7927]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.059314268050176]
[null,null,null,null,null,"Coincident",11.206240927715234]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2260827366666667]
[null,null,null,null,null,"Coincident",0.19971297314046235]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.370356411813908]
[null,null,null,null,null,"Coincident",12.049892626431141]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.92999088125476]
[null,null,null,null,null,"Coincident",12.511605059427822]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.152620631139152]
[null,null,null,null,null,"Coincident",11.153541622496693]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.596239135476079]
[null,null,null,null,null,"Coincident",11.580908819757596]
[null,null,"Edithburgh 11kV","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1009330625101601]
[null,null,null,null,null,"Coincident",0.84755308192171663]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1837989919464087]
[null,null,null,null,null,"Coincident",0.91134739991582425]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.42372492500000003]
[null,null,null,null,null,"Coincident",9.1945032939937277E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.83031814348177246]
[null,null,null,null,null,"Coincident",0.63922024457958337]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.89281520804491654]
[null,null,null,null,null,"Coincident",0.68733359632213265]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.75830100449489524]
[null,null,null,null,null,"Coincident",0.58377786558485767]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.81537742418805936]
[null,null,null,null,null,"Coincident",0.62771813503748131]
[null,null,"Elizabeth Downs 11kV","Substation Rating","MVA","Non-Coincident",59.6]
[null,null,null,null,null,"Coincident",59.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.494100000000003]
[null,null,null,null,null,"Coincident",40.522100000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",43.632013417902229]
[null,null,null,null,null,"Coincident",41.471018035490765]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.69812269333333321]
[null,null,null,null,null,"Coincident",1.2935096122075811]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",44.94441432912614]
[null,null,null,null,null,"Coincident",42.858703958579717]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",46.147942633640639]
[null,null,null,null,null,"Coincident",43.862338942059239]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",40.462457703172177]
[null,null,null,null,null,"Coincident",38.584738994206567]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",41.545967497278674]
[null,null,null,null,null,"Coincident",39.488289272358642]
[null,null,"Elizabeth Heights 11kV","Substation Rating","MVA","Non-Coincident",27.6]
[null,null,null,null,null,"Coincident",27.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.872]
[null,null,null,null,null,"Coincident",18.190899999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.434710593162944]
[null,null,null,null,null,"Coincident",18.702639835595399]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.38412854666666624]
[null,null,null,null,null,"Coincident",0.71172871499740564]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.479209984404221]
[null,null,null,null,null,"Coincident",20.704014460857287]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.119660333651545]
[null,null,null,null,null,"Coincident",21.286452325743788]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.22344620640261]
[null,null,null,null,null,"Coincident",18.529662335526137]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.796635948742622]
[null,null,null,null,null,"Coincident",19.050932110920449]
[null,null,"Elizabeth South 11kV","Substation Rating","MVA","Non-Coincident",53.33]
[null,null,null,null,null,"Coincident",53.33]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.741400000000001]
[null,null,null,null,null,"Coincident",12.225100000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.708570220099624]
[null,null,null,null,null,"Coincident",12.618882789296366]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1341556666666668]
[null,null,null,null,null,"Coincident",0.18980467684543256]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.360693984515766]
[null,null,null,null,null,"Coincident",14.259298412473079]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.488796722657604]
[null,null,null,null,null,"Coincident",14.718604782341044]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.980969461452336]
[null,null,null,null,null,"Coincident",13.187775532239888]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.024300294258683]
[null,null,null,null,null,"Coincident",13.612567070444056]
[null,null,"Eudunda 11kV","Substation Rating","MVA","Non-Coincident",2.4]
[null,null,null,null,null,"Coincident",2.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6883615579987594]
[null,null,null,null,null,"Coincident",1.3871787071722228]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7772226926302732]
[null,null,null,null,null,"Coincident",1.4601881128128662]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.241541333333333E-2]
[null,null,null,null,null,"Coincident",6.0060572633939956E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.673720822444982]
[null,null,null,null,null,"Coincident",1.3751496980294107]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.7618113920473495]
[null,null,null,null,null,"Coincident",1.4475259979256956]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5284413151850433]
[null,null,null,null,null,"Coincident",1.2557862606751902]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6088855949316245]
[null,null,null,null,null,"Coincident",1.3218802743949372]
[null,null,"Evanston 11kV","Substation Rating","MVA","Non-Coincident",57.660208695652173]
[null,null,null,null,null,"Coincident",57.660208695652173]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",37.891599999999997]
[null,null,null,null,null,"Coincident",35.985299999999995]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.198070521428171]
[null,null,null,null,null,"Coincident",36.654780221002547]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.67917752000000009]
[null,null,null,null,null,"Coincident",1.2584072383045106]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",39.817696365421533]
[null,null,null,null,null,"Coincident",37.814495799032066]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",40.139745319996678]
[null,null,null,null,null,"Coincident",38.518006871737754]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",36.065186364815162]
[null,null,null,null,null,"Coincident",34.250771962487278]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",36.356884695596371]
[null,null,null,null,null,"Coincident",34.887982556339601]
[null,null,"Findon 11kV","Substation Rating","MVA","Non-Coincident",24.8]
[null,null,null,null,null,"Coincident",24.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.126600000000003]
[null,null,null,null,null,"Coincident",16.4971]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.991053388203436]
[null,null,null,null,null,"Coincident",17.14988419698512]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.34159895984753291]
[null,null,null,null,null,"Coincident",0.34159895984753291]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.513901050485501]
[null,null,null,null,null,"Coincident",16.831155407650304]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.395859050347404]
[null,null,null,null,null,"Coincident",17.497158054607333]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.131762539732005]
[null,null,null,null,null,"Coincident",14.776510189694603]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.906056464076528]
[null,null,null,null,null,"Coincident",15.361211278881324]
[null,null,"Flinders Park 11kV","Substation Rating","MVA","Non-Coincident",27.3]
[null,null,null,null,null,"Coincident",27.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.151299999999999]
[null,null,null,null,null,"Coincident",19.748799999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.940669763022274]
[null,null,null,null,null,"Coincident",21.404174011860395]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.80086066666666655]
[null,null,null,null,null,"Coincident",0.48311936888133317]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.021803739780996]
[null,null,null,null,null,"Coincident",19.621890284804799]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.79967465694914]
[null,null,null,null,null,"Coincident",21.266626534148649]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.591470750174743]
[null,null,null,null,null,"Coincident",17.240100517140384]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.153536018790341]
[null,null,null,null,null,"Coincident",18.685191578771224]
[null,null,"Forreston 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.90002382908620793]
[null,null,null,null,null,"Coincident",0.63944198123989326]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.92785961761464741]
[null,null,null,null,null,"Coincident",0.65921853736071467]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-12-24"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.17084952]
[null,null,null,null,null,"Coincident",4.1033067519344907E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.90838361313355642]
[null,null,null,null,null,"Coincident",0.64538137606614088]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.93647795168407877]
[null,null,null,null,null,"Coincident",0.66534162481045445]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.82205008773387833]
[null,null,null,null,null,"Coincident",0.58404379949881313]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.84747431725142097]
[null,null,null,null,null,"Coincident",0.6021070097925908]
[null,null,"Freeling 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.37154359948209426]
[null,null,null,null,null,"Coincident",0.37154359948209426]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.39317547170246697]
[null,null,null,null,null,"Coincident",0.39317547170246697]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.3314309723250017E-2]
[null,null,null,null,null,"Coincident",2.3314309723250017E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.37154359948209426]
[null,null,null,null,null,"Coincident",0.37154359948209426]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.39317547170246697]
[null,null,null,null,null,"Coincident",0.39317547170246697]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.33438923953388483]
[null,null,null,null,null,"Coincident",0.33438923953388483]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.35385792453222026]
[null,null,null,null,null,"Coincident",0.35385792453222026]
[null,null,"Freeling North 11kV","Substation Rating","MVA","Non-Coincident",4.3]
[null,null,null,null,null,"Coincident",4.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.7641452427830195]
[null,null,null,null,null,"Coincident",2.4097676475544278]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9721991857881931]
[null,null,null,null,null,"Coincident",2.5911480081230405]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1273383767698033E-2]
[null,null,null,null,null,"Coincident",0.10418669704264717]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.9262086346810348]
[null,null,null,null,null,"Coincident",2.5510536815168003]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.1464608975064894]
[null,null,null,null,null,"Coincident",2.7430684747492475]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6275601986685553]
[null,null,null,null,null,"Coincident",2.2906935065315617]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8253335469554361]
[null,null,null,null,null,"Coincident",2.4631112973457649]
[null,null,"Fulham Gardens 11kV","Substation Rating","MVA","Non-Coincident",49]
[null,null,null,null,null,"Coincident",49]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",41.018900000000002]
[null,null,null,null,null,"Coincident",40.364100000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.868602038904889]
[null,null,null,null,null,"Coincident",42.266707360048763]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.12933259494175309]
[null,null,null,null,null,"Coincident",1.1952698643636526]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.899547304479896]
[null,null,null,null,null,"Coincident",38.278579322038304]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",40.653679471885006]
[null,null,null,null,null,"Coincident",40.082883313712102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",33.834179718630907]
[null,null,null,null,null,"Coincident",33.294072088251752]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",35.359894723426891]
[null,null,null,null,null,"Coincident",34.863425711919859]
[null,null,"Fullerville 11kV","Substation Rating","MVA","Non-Coincident",0.26]
[null,null,null,null,null,"Coincident",0.26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8929462435879134E-2]
[null,null,null,null,null,"Coincident",2.8929462435879134E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9075585893188493E-2]
[null,null,null,null,null,"Coincident",2.9075585893188493E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8929462435879134E-2]
[null,null,null,null,null,"Coincident",2.8929462435879134E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.9075585893188493E-2]
[null,null,null,null,null,"Coincident",2.9075585893188493E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8929462435879134E-2]
[null,null,null,null,null,"Coincident",2.8929462435879134E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9075585893188493E-2]
[null,null,null,null,null,"Coincident",2.9075585893188493E-2]
[null,null,"Gawler Belt TF1 11kV","Substation Rating","MVA","Non-Coincident",14.6]
[null,null,null,null,null,"Coincident",14.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.2397]
[null,null,null,null,null,"Coincident",3.7021000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.6853269448353334]
[null,null,null,null,null,"Coincident",3.8683303439597818]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2176518952269559]
[null,null,null,null,null,"Coincident",0.19774431834741191]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.0780357966587211]
[null,null,null,null,null,"Coincident",4.434133623324823]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.6117786505940188]
[null,null,null,null,null,"Coincident",4.6332334740497947]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.5859827147535128]
[null,null,null,null,null,"Coincident",4.004473573198335]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.0680067886840394]
[null,null,null,null,null,"Coincident",4.1842809850593365]
[null,null,"Gawler Belt TF2 11kV","Substation Rating","MVA","Non-Coincident",14.6]
[null,null,null,null,null,"Coincident",14.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.8581000000000003]
[null,null,null,null,null,"Coincident",4.6421999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.058552522214236]
[null,null,null,null,null,"Coincident",4.8287741021919839]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11895912]
[null,null,null,null,null,"Coincident",0.22041220927090591]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.5455508399772695]
[null,null,null,null,null,"Coincident",5.2990996705177906]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.7743686191379942]
[null,null,null,null,null,"Coincident",5.5120751484060104]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.9116333853172325]
[null,null,null,null,null,"Coincident",4.6933542951605887]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.1142947756300057]
[null,null,null,null,null,"Coincident",4.881984333480454]
[null,null,"Georgetown 11kV","Substation Rating","MVA","Non-Coincident",0.41]
[null,null,null,null,null,"Coincident",0.41]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.13513619560999995]
[null,null,null,null,null,"Coincident",0.13513619560999995]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.13517613368896261]
[null,null,null,null,null,"Coincident",0.13517613368896261]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.1702040597365389E-3]
[null,null,null,null,null,"Coincident",6.1702040597365389E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.13513619560999995]
[null,null,null,null,null,"Coincident",0.13513619560999995]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.13517613368896261]
[null,null,null,null,null,"Coincident",0.13517613368896261]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.12162257604899997]
[null,null,null,null,null,"Coincident",0.12162257604899997]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.12165852032006635]
[null,null,null,null,null,"Coincident",0.12165852032006635]
[null,null,"Geranium 11kV","Substation Rating","MVA","Non-Coincident",0.19500000000000001]
[null,null,null,null,null,"Coincident",0.19500000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.14163265418390578]
[null,null,null,null,null,"Coincident",0.14163265418390578]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.14610037104869789]
[null,null,null,null,null,"Coincident",0.14610037104869789]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.2514623523308976E-3]
[null,null,null,null,null,"Coincident",3.2514623523308976E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.14163265418390578]
[null,null,null,null,null,"Coincident",0.14163265418390578]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.14610037104869789]
[null,null,null,null,null,"Coincident",0.14610037104869789]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.1274693887655152]
[null,null,null,null,null,"Coincident",0.1274693887655152]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.13149033394382811]
[null,null,null,null,null,"Coincident",0.13149033394382811]
[null,null,"Gladstone 11kV","Substation Rating","MVA","Non-Coincident",4.8]
[null,null,null,null,null,"Coincident",4.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4500000000000002]
[null,null,null,null,null,"Coincident",2.4500000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4933518126896708]
[null,null,null,null,null,"Coincident",2.4933518126896708]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11891840509872445]
[null,null,null,null,null,"Coincident",0.11891840509872445]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4500000000000002]
[null,null,null,null,null,"Coincident",2.4500000000000002]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4933518126896708]
[null,null,null,null,null,"Coincident",2.4933518126896708]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2050000000000005]
[null,null,null,null,null,"Coincident",2.2050000000000005]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.244016631420704]
[null,null,null,null,null,"Coincident",2.244016631420704]
[null,null,"Glanville 7.6kV","Substation Rating","MVA","Non-Coincident",20.399999999999999]
[null,null,null,null,null,"Coincident",20.399999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.4751000000000012]
[null,null,null,null,null,"Coincident",8.7961999999999989]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.6726901128900025]
[null,null,null,null,null,"Coincident",8.9797468856310196]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.268953333333334E-2]
[null,null,null,null,null,"Coincident",0.42397931183623794]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.51799044032105]
[null,null,null,null,null,"Coincident",7.90766825797638]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.6956213563746001]
[null,null,null,null,null,"Coincident",8.0726744971881814]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.4646084298998696]
[null,null,null,null,null,"Coincident",6.929762078615024]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.620272520235968]
[null,null,null,null,null,"Coincident",7.0743627297704927]
[null,null,"Glencoe 11kV","Substation Rating","MVA","Non-Coincident",1.8]
[null,null,null,null,null,"Coincident",1.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0409999999999999]
[null,null,null,null,null,"Coincident",0.66300000000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1329121766491876]
[null,null,null,null,null,"Coincident",0.7181538832311638]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",4.0285483658631875E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0950802130720503]
[null,null,null,null,null,"Coincident",0.69744301754732896]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1917672505253725]
[null,null,null,null,null,"Coincident",0.75546215895033941]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.98268590089472263]
[null,null,null,null,null,"Coincident",0.62586047290413183]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0694493976417945]
[null,null,null,null,null,"Coincident",0.67792477975414001]
[null,null,"Glenelg North 11kV","Substation Rating","MVA","Non-Coincident",27.9]
[null,null,null,null,null,"Coincident",27.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.306600000000003]
[null,null,null,null,null,"Coincident",19.997399999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.326849423203608]
[null,null,null,null,null,"Coincident",21.052354244834472]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.9719005546546511E-2]
[null,null,null,null,null,"Coincident",0.36707629962625338]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.74261354366606]
[null,null,null,null,null,"Coincident",19.442001126634079]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.73452701418584]
[null,null,null,null,null,"Coincident",20.467655542539109]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.396236734235956]
[null,null,null,null,null,"Coincident",17.131351603380676]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.270262937244709]
[null,null,null,null,null,"Coincident",18.035108696489694]
[null,null,"Glossop 11kV","Substation Rating","MVA","Non-Coincident",15.4]
[null,null,null,null,null,"Coincident",15.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.8350000000000009]
[null,null,null,null,null,"Coincident",6.8174999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.1932827243591291]
[null,null,null,null,null,"Coincident",7.0091629072236579]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-21"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.24391674389510071]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.092942176012027]
[null,null,null,null,null,"Coincident",7.7881871290279552]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.50223779792722]
[null,null,null,null,null,"Coincident",8.0071393236962898]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.205670567473474]
[null,null,null,null,null,"Coincident",7.1035267791454899]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.5789849682054538]
[null,null,null,null,null,"Coincident",7.3032308633452887]
[null,null,"Golden Grove 11kV","Substation Rating","MVA","Non-Coincident",84.6]
[null,null,null,null,null,"Coincident",84.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",46.827500000000001]
[null,null,null,null,null,"Coincident",38.267800000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",48.426311368304724]
[null,null,null,null,null,"Coincident",40.102954649252467]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0422631333333328]
[null,null,null,null,null,"Coincident",1.9311467658773587]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",50.113803034660449]
[null,null,null,null,null,"Coincident",40.953392595585484]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",51.824817246412067]
[null,null,null,null,null,"Coincident",42.917336402766722]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",44.740554660433233]
[null,null,null,null,null,"Coincident",36.562331912541282]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.268112343746665]
[null,null,null,null,null,"Coincident",38.315699845811864]
[null,null,"Gomersal North 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.4136100028465791E-2]
[null,null,null,null,null,"Coincident",3.1551037510674673E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.1452282639636728E-2]
[null,null,null,null,null,"Coincident",3.4294605989863773E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-11-28"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.10678924700537988]
[null,null,null,null,null,"Coincident",4.0045967627017454E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.11607526848410857]
[null,null,null,null,null,"Coincident",4.352822568154071E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.6080884423012825E-2]
[null,null,null,null,null,"Coincident",3.6030331658629809E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.10443574393805741]
[null,null,null,null,null,"Coincident",3.9163403976771531E-2]
[null,null,"Goolwa 11kV","Substation Rating","MVA","Non-Coincident",33.4]
[null,null,null,null,null,"Coincident",33.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.5686]
[null,null,null,null,null,"Coincident",13.3133]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.592611422080651]
[null,null,null,null,null,"Coincident",13.313526153878243]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.5327227199999998]
[null,null,null,null,null,"Coincident",0.75484595570419377]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.057218335869308]
[null,null,null,null,null,"Coincident",9.4554465315396925]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.074271862615481]
[null,null,null,null,null,"Coincident",9.4556071518144265]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9014363980123594]
[null,null,null,null,null,"Coincident",8.4670935856568956]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.9167073644805974]
[null,null,null,null,null,"Coincident",8.4672374167169515]
[null,null,"Gulnare 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.4991528190328314E-2]
[null,null,null,null,null,"Coincident",9.4991528190328314E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.5019601935756218E-2]
[null,null,null,null,null,"Coincident",9.5019601935756218E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7791216190182039E-3]
[null,null,null,null,null,"Coincident",1.7791216190182039E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.4991528190328314E-2]
[null,null,null,null,null,"Coincident",9.4991528190328314E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.5019601935756218E-2]
[null,null,null,null,null,"Coincident",9.5019601935756218E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.549237537129549E-2]
[null,null,null,null,null,"Coincident",8.549237537129549E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.55176417421806E-2]
[null,null,null,null,null,"Coincident",8.55176417421806E-2]
[null,null,"Gumeracha 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.2915971287962853]
[null,null,null,null,null,"Coincident",0.2915971287962853]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.30243235383531525]
[null,null,null,null,null,"Coincident",0.30243235383531525]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.6732528150560203E-2]
[null,null,null,null,null,"Coincident",1.6732528150560203E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.2915971287962853]
[null,null,null,null,null,"Coincident",0.2915971287962853]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.30243235383531525]
[null,null,null,null,null,"Coincident",0.30243235383531525]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.26243741591665676]
[null,null,null,null,null,"Coincident",0.26243741591665676]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.27218911845178373]
[null,null,null,null,null,"Coincident",0.27218911845178373]
[null,null,"Gumeracha Weir 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.28219076980285679]
[null,null,null,null,null,"Coincident",0.28219076980285679]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.29267647145353093]
[null,null,null,null,null,"Coincident",0.29267647145353093]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.7947050941775579E-3]
[null,null,null,null,null,"Coincident",4.7947050941775579E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.28219076980285679]
[null,null,null,null,null,"Coincident",0.28219076980285679]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.29267647145353093]
[null,null,null,null,null,"Coincident",0.29267647145353093]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.25397169282257115]
[null,null,null,null,null,"Coincident",0.25397169282257115]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.26340882430817786]
[null,null,null,null,null,"Coincident",0.26340882430817786]
[null,null,"Gumhaven 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.525087194742848E-2]
[null,null,null,null,null,"Coincident",7.525087194742848E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.804705905427492E-2]
[null,null,null,null,null,"Coincident",7.804705905427492E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.6950072904583287E-4]
[null,null,null,null,null,"Coincident",8.6950072904583287E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.525087194742848E-2]
[null,null,null,null,null,"Coincident",7.525087194742848E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.804705905427492E-2]
[null,null,null,null,null,"Coincident",7.804705905427492E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.7725784752685633E-2]
[null,null,null,null,null,"Coincident",6.7725784752685633E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.0242353148847428E-2]
[null,null,null,null,null,"Coincident",7.0242353148847428E-2]
[null,null,"Hackham 11kV","Substation Rating","MVA","Non-Coincident",31.6]
[null,null,null,null,null,"Coincident",31.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.31]
[null,null,null,null,null,"Coincident",13.71]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.566210900573973]
[null,null,null,null,null,"Coincident",13.997017539461757]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.6010935959346118E-2]
[null,null,null,null,null,"Coincident",0.70248015324519875]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",13.818441010333439]
[null,null,null,null,null,"Coincident",13.239051450151743]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.065850878662289]
[null,null,null,null,null,"Coincident",13.516209726740374]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.279107026668665]
[null,null,null,null,null,"Coincident",11.76425977188172]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",12.498956158013666]
[null,null,null,null,null,"Coincident",12.010543425661035]
[null,null,"Hahndorf 11kV","Substation Rating","MVA","Non-Coincident",6.8]
[null,null,null,null,null,"Coincident",6.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.9795999999999996]
[null,null,null,null,null,"Coincident",4.9795999999999996]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.1897278734053094]
[null,null,null,null,null,"Coincident",5.1897278734053094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.18013969549188386]
[null,null,null,null,null,"Coincident",0.18013969549188386]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.8713185729917168]
[null,null,null,null,null,"Coincident",4.8713185729917168]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.0771434239350581]
[null,null,null,null,null,"Coincident",5.0771434239350581]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.4201767972201429]
[null,null,null,null,null,"Coincident",4.4201767972201429]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.6069398300209947]
[null,null,null,null,null,"Coincident",4.6069398300209947]
[null,null,"Halbury 11kV","Substation Rating","MVA","Non-Coincident",0.19500000000000001]
[null,null,null,null,null,"Coincident",0.19500000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.549237537129549E-2]
[null,null,null,null,null,"Coincident",8.549237537129549E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.55176417421806E-2]
[null,null,null,null,null,"Coincident",8.55176417421806E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.3703306333425394E-3]
[null,null,null,null,null,"Coincident",4.3703306333425394E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.549237537129549E-2]
[null,null,null,null,null,"Coincident",8.549237537129549E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.55176417421806E-2]
[null,null,null,null,null,"Coincident",8.55176417421806E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.6943137834165939E-2]
[null,null,null,null,null,"Coincident",7.6943137834165939E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.696587756796254E-2]
[null,null,null,null,null,"Coincident",7.696587756796254E-2]
[null,null,"Hamley Bridge 11kV","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2962143966102118]
[null,null,null,null,null,"Coincident",2.2436293340924207]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4958852137067518]
[null,null,null,null,null,"Coincident",2.438727537056979]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.4299733333333326E-3]
[null,null,null,null,null,"Coincident",7.0426100418149826E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5062542176180398]
[null,null,null,null,null,"Coincident",2.4488590828634282]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7241893669761299]
[null,null,null,null,null,"Coincident",2.6618033509385088]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2759599919230391]
[null,null,null,null,null,"Coincident",2.2238387707339622]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.4738695564380859]
[null,null,null,null,null,"Coincident",2.417216055145611]
[null,null,"Happy Valley 11kV","Substation Rating","MVA","Non-Coincident",59.8]
[null,null,null,null,null,"Coincident",59.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.336199999999998]
[null,null,null,null,null,"Coincident",31.848700000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.334087095625534]
[null,null,null,null,null,"Coincident",32.869747986408413]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.167066872094708]
[null,null,null,null,null,"Coincident",1.5440036414504386]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.612801000309652]
[null,null,null,null,null,"Coincident",31.157579904685061]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.589033842397612]
[null,null,null,null,null,"Coincident",32.156471043822229]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.722010898604594]
[null,null,null,null,null,"Coincident",27.44040138067291]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.581776679831417]
[null,null,null,null,null,"Coincident",28.320122266485352]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Harrow 11kV","Substation Rating","MVA","Non-Coincident",28.3]
[null,null,null,null,null,"Coincident",28.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",20.3079]
[null,null,null,null,null,"Coincident",19.0108]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.193363263295424]
[null,null,null,null,null,"Coincident",19.778838789979556]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.27517690666666667]
[null,null,null,null,null,"Coincident",0.50985876441195821]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.328762654521778]
[null,null,null,null,null,"Coincident",19.030330121410024]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.215135569438193]
[null,null,null,null,null,"Coincident",19.799157930831999]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.83745189419211]
[null,null,null,null,null,"Coincident",16.698143602741169]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.615198897235583]
[null,null,null,null,null,"Coincident",17.372750773799421]
[null,null,"Hatherleigh 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.4400000000000013E-2]
[null,null,null,null,null,"Coincident",6.4400000000000013E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.9804790808999526E-2]
[null,null,null,null,null,"Coincident",6.9804790808999526E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.487687092958703E-3]
[null,null,null,null,null,"Coincident",3.487687092958703E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.4400000000000013E-2]
[null,null,null,null,null,"Coincident",6.4400000000000013E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.9804790808999526E-2]
[null,null,null,null,null,"Coincident",6.9804790808999526E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.7960000000000012E-2]
[null,null,null,null,null,"Coincident",5.7960000000000012E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.2824311728099574E-2]
[null,null,null,null,null,"Coincident",6.2824311728099574E-2]
[null,null,"Hawker 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.8]
[null,null,null,null,null,"Coincident",0.8]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.88888888888888895]
[null,null,null,null,null,"Coincident",0.88888888888888895]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.9087808398652597E-2]
[null,null,null,null,null,"Coincident",2.9087808398652597E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.8]
[null,null,null,null,null,"Coincident",0.8]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.88888888888888895]
[null,null,null,null,null,"Coincident",0.88888888888888895]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.72000000000000008]
[null,null,null,null,null,"Coincident",0.72000000000000008]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.8]
[null,null,null,null,null,"Coincident",0.8]
[null,null,"Hay Flat 11kV","Substation Rating","MVA","Non-Coincident",0.26]
[null,null,null,null,null,"Coincident",0.26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.8973428819243603E-2]
[null,null,null,null,null,"Coincident",4.8973428819243603E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.9468109918427886E-2]
[null,null,null,null,null,"Coincident",4.9468109918427886E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.8973428819243603E-2]
[null,null,null,null,null,"Coincident",4.8973428819243603E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.9468109918427886E-2]
[null,null,null,null,null,"Coincident",4.9468109918427886E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.8973428819243603E-2]
[null,null,null,null,null,"Coincident",4.8973428819243603E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.9468109918427886E-2]
[null,null,null,null,null,"Coincident",4.9468109918427886E-2]
[null,null,"Henley South 11kV","Substation Rating","MVA","Non-Coincident",55.7]
[null,null,null,null,null,"Coincident",55.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.719499999999996]
[null,null,null,null,null,"Coincident",31.778400000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",35.20314288653784]
[null,null,null,null,null,"Coincident",33.037306218425257]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.86625237946460831]
[null,null,null,null,null,"Coincident",0.86625237946460831]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.033331622761501]
[null,null,null,null,null,"Coincident",30.18929775473433]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.442783856460629]
[null,null,null,null,null,"Coincident",31.385251442564009]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",28.008424490315878]
[null,null,null,null,null,"Coincident",26.396088815761036]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.240782614196405]
[null,null,null,null,null,"Coincident",27.441773946298348]
[null,null,"Hermitage 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.15729792614017513]
[null,null,null,null,null,"Coincident",0.10974273916756405]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.16385200639601577]
[null,null,null,null,null,"Coincident",0.1143153532995459]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0512865616578016E-2]
[null,null,null,null,null,"Coincident",1.0512865616578016E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.15302667348304669]
[null,null,null,null,null,"Coincident",0.10676279545328839]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.15940278487817364]
[null,null,null,null,null,"Coincident",0.11121124526384207]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.13299244631198515]
[null,null,null,null,null,"Coincident",9.2785427659524522E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.13853379824165121]
[null,null,null,null,null,"Coincident",9.6651487145338041E-2]
[null,null,"Hillcrest 11kV","Substation Rating","MVA","Non-Coincident",61.7]
[null,null,null,null,null,"Coincident",61.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",37.090000000000003]
[null,null,null,null,null,"Coincident",36.68]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.542165222000705]
[null,null,null,null,null,"Coincident",38.098719138574722]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.51898083999999955]
[null,null,null,null,null,"Coincident",0.96158843066147792]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",39.913057817798943]
[null,null,null,null,null,"Coincident",39.471851193229035]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",41.475752734669008]
[null,null,null,null,null,"Coincident",40.998554320895543]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",35.760184404752316]
[null,null,null,null,null,"Coincident",35.364884442337953]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",37.160284057621368]
[null,null,null,null,null,"Coincident",36.732737179301651]
[null,null,"Hindley Street 11kV","Substation Rating","MVA","Non-Coincident",77.099999999999994]
[null,null,null,null,null,"Coincident",77.099999999999994]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.3018]
[null,null,null,null,null,"Coincident",30.387500000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.519251302557059]
[null,null,null,null,null,"Coincident",30.455303700012582]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","12:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.22396983333333334]
[null,null,null,null,null,"Coincident",3.7482087413890024E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",46.148456281395021]
[null,null,null,null,null,"Coincident",33.150745718879371]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",46.38568122050841]
[null,null,null,null,null,"Coincident",33.22471505554465]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",42.909825248942312]
[null,null,null,null,null,"Coincident",30.824274965893522]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",43.130402089475773]
[null,null,null,null,null,"Coincident",30.89305324291179]
[null,null,"Hindley Street 33kV","Substation Rating","MVA","Non-Coincident",23.75]
[null,null,null,null,null,"Coincident",23.75]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8646999999999991]
[null,null,null,null,null,"Coincident",6.8745000000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.9381943556161136]
[null,null,null,null,null,"Coincident",6.8797688107958974]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.8500000000000002E-3]
[null,null,null,null,null,"Coincident",1.7293172813162944E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.496589714370868]
[null,null,null,null,null,"Coincident",7.3148505267714716]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.57479179828872]
[null,null,null,null,null,"Coincident",7.3204568346376186]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.9447775492497108]
[null,null,null,null,null,"Coincident",6.9303043440061165]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.018868501607889]
[null,null,null,null,null,"Coincident",6.9356159248260383]
[null,null,"Holden Hill 11kV","Substation Rating","MVA","Non-Coincident",46.7]
[null,null,null,null,null,"Coincident",46.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",36.733600000000003]
[null,null,null,null,null,"Coincident",33.933800000000005]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",38.160494529290368]
[null,null,null,null,null,"Coincident",35.175965751205759]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.60458019999999935]
[null,null,null,null,null,"Coincident",1.1201903440732075]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",39.037042270532837]
[null,null,null,null,null,"Coincident",36.061676094905131]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",40.553412625072006]
[null,null,null,null,null,"Coincident",37.381733942130211]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",35.041009930714992]
[null,null,null,null,null,"Coincident",32.370217533454287]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",36.402156819964794]
[null,null,null,null,null,"Coincident",33.555147472899236]
[null,null,"Hope Valley 11kV","Substation Rating","MVA","Non-Coincident",31.2]
[null,null,null,null,null,"Coincident",31.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.12]
[null,null,null,null,null,"Coincident",17.170000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.773452000098438]
[null,null,null,null,null,"Coincident",17.814920712705966]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.4277269466500729E-2]
[null,null,null,null,null,"Coincident",0.77887620278190861]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.610774324018056]
[null,null,null,null,null,"Coincident",18.593840065949436]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.302891947294356]
[null,null,null,null,null,"Coincident",19.276534193909079]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.253048205611428]
[null,null,null,null,null,"Coincident",16.358375946040969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.861955254412376]
[null,null,null,null,null,"Coincident",16.958992449232785]
[null,null,"Houghton 7.6kV","Substation Rating","MVA","Non-Coincident",3.6]
[null,null,null,null,null,"Coincident",3.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.073]
[null,null,null,null,null,"Coincident",1.65]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1902461048932378]
[null,null,null,null,null,"Coincident",1.7647594736960615]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.5045655090728922E-2]
[null,null,null,null,null,"Coincident",0.13904938757052743]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1234384673155815]
[null,null,null,null,null,"Coincident",1.6901463922193485]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2435373043986586]
[null,null,null,null,null,"Coincident",1.8076980955165542]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8639838495936667]
[null,null,null,null,null,"Coincident",1.4836340336852629]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9694082808279938]
[null,null,null,null,null,"Coincident",1.5868225554205875]
[null,null,"Hoyleton 11kV","Substation Rating","MVA","Non-Coincident",0.19500000000000001]
[null,null,null,null,null,"Coincident",0.19500000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.9000000000000001E-2]
[null,null,null,null,null,"Coincident",7.3999999999999996E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.0062475604992384E-2]
[null,null,null,null,null,"Coincident",7.496665925596524E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.6443200000000004E-3]
[null,null,null,null,null,"Coincident",4.8995017214253263E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.9419006842279441E-2]
[null,null,null,null,null,"Coincident",7.4392487421882009E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.0487117694717988E-2]
[null,null,null,null,null,"Coincident",7.5364273726485256E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.1514802318204604E-2]
[null,null,null,null,null,"Coincident",6.6988549006925829E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2476609063254538E-2]
[null,null,null,null,null,"Coincident",6.7863617938564019E-2]
[null,null,"Ingle Farm 11kV","Substation Rating","MVA","Non-Coincident",51.7]
[null,null,null,null,null,"Coincident",51.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",35.722200000000001]
[null,null,null,null,null,"Coincident",33.638499999999993]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",37.029118591319452]
[null,null,null,null,null,"Coincident",34.729022436717095]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2986778498345231]
[null,null,null,null,null,"Coincident",1.2986778498345231]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",38.498231865553088]
[null,null,null,null,null,"Coincident",36.252604056004593]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",39.906713284895076]
[null,null,null,null,null,"Coincident",37.427872813900883]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",34.58961337448271]
[null,null,null,null,null,"Coincident",32.57197791562492]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",35.855095589622415]
[null,null,null,null,null,"Coincident",33.627924902715392]
[null,null,"Inverness 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.94162603127120836]
[null,null,null,null,null,"Coincident",0.94162603127120836]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0017951515048575]
[null,null,null,null,null,"Coincident",1.0017951515048575]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.94162603127120836]
[null,null,null,null,null,"Coincident",0.94162603127120836]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0017951515048575]
[null,null,null,null,null,"Coincident",1.0017951515048575]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.84746342814408759]
[null,null,null,null,null,"Coincident",0.84746342814408759]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.90161563635437181]
[null,null,null,null,null,"Coincident",0.90161563635437181]
[null,null,"Jabuk 11kV","Substation Rating","MVA","Non-Coincident",0.26]
[null,null,null,null,null,"Coincident",0.26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.5537415564749744E-2]
[null,null,null,null,null,"Coincident",7.5537415564749744E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7920197892638862E-2]
[null,null,null,null,null,"Coincident",7.7920197892638862E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.3871888143840275E-4]
[null,null,null,null,null,"Coincident",8.3871888143840275E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.5537415564749744E-2]
[null,null,null,null,null,"Coincident",7.5537415564749744E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.7920197892638862E-2]
[null,null,null,null,null,"Coincident",7.7920197892638862E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.7983674008274764E-2]
[null,null,null,null,null,"Coincident",6.7983674008274764E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.0128178103374975E-2]
[null,null,null,null,null,"Coincident",7.0128178103374975E-2]
[null,null,"James Well 7.6kV","Substation Rating","MVA","Non-Coincident",0.9]
[null,null,null,null,null,"Coincident",0.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.43388912897635157]
[null,null,null,null,null,"Coincident",0.43388912897635157]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.44812608746472937]
[null,null,null,null,null,"Coincident",0.44812608746472937]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.3769861784209126E-2]
[null,null,null,null,null,"Coincident",1.3769861784209126E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.43388912897635157]
[null,null,null,null,null,"Coincident",0.43388912897635157]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.44812608746472937]
[null,null,null,null,null,"Coincident",0.44812608746472937]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.39050021607871643]
[null,null,null,null,null,"Coincident",0.39050021607871643]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.40331347871825646]
[null,null,null,null,null,"Coincident",0.40331347871825646]
[null,null,"Jamestown 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4710000000000001]
[null,null,null,null,null,"Coincident",2.2370000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.59604641715051]
[null,null,null,null,null,"Coincident",2.345763202030418]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.29080357633923054]
[null,null,null,null,null,"Coincident",0.12468049028007033]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4714603025384325]
[null,null,null,null,null,"Coincident",2.2374167125772861]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5965300135712717]
[null,null,null,null,null,"Coincident",2.3462001752220232]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2285873790908628]
[null,null,null,null,null,"Coincident",2.0175434913096963]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3413663621188503]
[null,null,null,null,null,"Coincident",2.1156366921816101]
[null,null,"Jervois 11kV","Substation Rating","MVA","Non-Coincident",8.9]
[null,null,null,null,null,"Coincident",8.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.2629999999999999]
[null,null,null,null,null,"Coincident",0.96399999999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3417816513874379]
[null,null,null,null,null,"Coincident",1.0698560650853925]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-11-23"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",5.1411219319708386E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3327928161929512]
[null,null,null,null,null,"Coincident",1.0172702096674624]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4159279064676897]
[null,null,null,null,null,"Coincident",1.1289758336550038]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2144193678348751]
[null,null,null,null,null,"Coincident",0.92692024591672184]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2901707243470841]
[null,null,null,null,null,"Coincident",1.0287046130129134]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Kadina 11kV","Substation Rating","MVA","Non-Coincident",16]
[null,null,null,null,null,"Coincident",16]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.0383999999999993]
[null,null,null,null,null,"Coincident",7.6955]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.4204770559630404]
[null,null,null,null,null,"Coincident",8.0645232227330101]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.20602269333333331]
[null,null,null,null,null,"Coincident",0.38172707563356495]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.9367725949679713]
[null,null,null,null,null,"Coincident",8.5555500478423596]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.3615506307582468]
[null,null,null,null,null,"Coincident",8.9658153523590709]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.9338415267509266]
[null,null,null,null,null,"Coincident",7.5954017552139428]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.310948763641143]
[null,null,null,null,null,"Coincident",7.9596249549619786]
[null,null,"Kalangadoo 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.55200000000000005]
[null,null,null,null,null,"Coincident",0.55200000000000005]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.59832677836285297]
[null,null,null,null,null,"Coincident",0.59832677836285297]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.55200000000000005]
[null,null,null,null,null,"Coincident",0.55200000000000005]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.59832677836285297]
[null,null,null,null,null,"Coincident",0.59832677836285297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.49680000000000007]
[null,null,null,null,null,"Coincident",0.49680000000000007]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.53849410052656765]
[null,null,null,null,null,"Coincident",0.53849410052656765]
[null,null,"Kalangadoo West 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.81399999999999995]
[null,null,null,null,null,"Coincident",0.746]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.88331477967936212]
[null,null,null,null,null,"Coincident",0.78365553657203235]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.8216770000000001E-2]
[null,null,null,null,null,"Coincident",2.805955634318193E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.80374896206860302]
[null,null,null,null,null,"Coincident",0.73660531413166819]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.8721908321217986]
[null,null,null,null,null,"Coincident",0.77378663899150524]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.72528039580470338]
[null,null,null,null,null,"Coincident",0.66469186151143589]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.78704040912284046]
[null,null,null,null,null,"Coincident",0.69824324046622965]
[null,null,"Kapunda TF1 11kV","Substation Rating","MVA","Non-Coincident",17.399999999999999]
[null,null,null,null,null,"Coincident",17.399999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.7044000000000001]
[null,null,null,null,null,"Coincident",3.4950000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.8784727110036497]
[null,null,null,null,null,"Coincident",3.733566557596101]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.5440000000000003E-2]
[null,null,null,null,null,"Coincident",0.10272144651018789]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0399859688007318]
[null,null,null,null,null,"Coincident",3.811616175617794]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.2298281321755962]
[null,null,null,null,null,"Coincident",4.0717947592786672]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6629730557515536]
[null,null,null,null,null,"Coincident",3.4559148120752834]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.8350990815986532]
[null,null,null,null,null,"Coincident",3.6918134387025159]
[null,null,"Kapunda TF2 11kV","Substation Rating","MVA","Non-Coincident",17.399999999999999]
[null,null,null,null,null,"Coincident",17.399999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.7881999999999998]
[null,null,null,null,null,"Coincident",2.4874000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8450486902687624]
[null,null,null,null,null,"Coincident",2.5483909433209027]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.5440000000000003E-2]
[null,null,null,null,null,"Coincident",0.10272144651018789]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8010981779772348]
[null,null,null,null,null,"Coincident",2.4989066809771803]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8582098495690227]
[null,null,null,null,null,"Coincident",2.5601797676313991]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5213843413404993]
[null,null,null,null,null,"Coincident",2.249369274316892]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5727929194444279]
[null,null,null,null,null,"Coincident",2.3045237142612685]
[null,null,"Karoonda 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.75537415564749755]
[null,null,null,null,null,"Coincident",0.75537415564749755]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.77920197892638876]
[null,null,null,null,null,"Coincident",0.77920197892638876]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.7746672957931417E-2]
[null,null,null,null,null,"Coincident",3.7746672957931417E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.75537415564749755]
[null,null,null,null,null,"Coincident",0.75537415564749755]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.77920197892638876]
[null,null,null,null,null,"Coincident",0.77920197892638876]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.67983674008274786]
[null,null,null,null,null,"Coincident",0.67983674008274786]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.70128178103374994]
[null,null,null,null,null,"Coincident",0.70128178103374994]
[null,null,"Keith 11kV","Substation Rating","MVA","Non-Coincident",16.600000000000001]
[null,null,null,null,null,"Coincident",16.600000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.8881999999999994]
[null,null,null,null,null,"Coincident",4.8881999999999994]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.9431194887439238]
[null,null,null,null,null,"Coincident",4.9431194887439238]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11155428038796712]
[null,null,null,null,null,"Coincident",0.11155428038796712]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1635671160059324]
[null,null,null,null,null,"Coincident",5.1635671160059324]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.2215803859429206]
[null,null,null,null,null,"Coincident",5.2215803859429206]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.6875405888703359]
[null,null,null,null,null,"Coincident",4.6875405888703359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.740205646070768]
[null,null,null,null,null,"Coincident",4.740205646070768]
[null,null,"Kent Town 11kV","Substation Rating","MVA","Non-Coincident",59.182192121630955]
[null,null,null,null,null,"Coincident",59.182192121630955]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",31.269999999999996]
[null,null,null,null,null,"Coincident",25.66]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.454222453974324]
[null,null,null,null,null,"Coincident",27.239221721627807]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0813967416666665]
[null,null,null,null,null,"Coincident",0.35848141980638321]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.367010787630065]
[null,null,null,null,null,"Coincident",27.380796188378238]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.697710313832339]
[null,null,null,null,null,"Coincident",29.06592277045738]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",30.044057342795099]
[null,null,null,null,null,"Coincident",24.653997806719612]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",32.142647194302143]
[null,null,null,null,null,"Coincident",26.171306024230756]
[null,null,"Kersbrook 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.50800000000000001]
[null,null,null,null,null,"Coincident",0.45900000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.52801515129776344]
[null,null,null,null,null,"Coincident",0.47678296949450699]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.3926488040835987E-2]
[null,null,null,null,null,"Coincident",2.3926488040835987E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.51607415183364391]
[null,null,null,null,null,"Coincident",0.46629534584969012]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.53640742393957952]
[null,null,null,null,null,"Coincident",0.48436095785551936]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.45045536907517386]
[null,null,null,null,null,"Coincident",0.40700593386910394]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.46820326743133422]
[null,null,null,null,null,"Coincident",0.42277450490631002]
[null,null,"Keswick 11kV","Substation Rating","MVA","Non-Coincident",49.1]
[null,null,null,null,null,"Coincident",49.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.377700000000004]
[null,null,null,null,null,"Coincident",25.697099999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",35.758631926990724]
[null,null,null,null,null,"Coincident",27.096020867463174]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0862783649217798]
[null,null,null,null,null,"Coincident",0.29767395503864275]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",36.027587347055146]
[null,null,null,null,null,"Coincident",27.737217208375974]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",38.597543724128776]
[null,null,null,null,null,"Coincident",29.247199733958855]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",33.492259157103256]
[null,null,null,null,null,"Coincident",25.785297752271667]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",35.881362934002034]
[null,null,null,null,null,"Coincident",27.189020004954038]
[null,null,"Ki Ki 11kV","Substation Rating","MVA","Non-Coincident",0.26]
[null,null,null,null,null,"Coincident",0.26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.10386394640153092]
[null,null,null,null,null,"Coincident",0.10386394640153092]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.10714027210237846]
[null,null,null,null,null,"Coincident",0.10714027210237846]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1911537433706638E-3]
[null,null,null,null,null,"Coincident",1.1911537433706638E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.10386394640153092]
[null,null,null,null,null,"Coincident",0.10386394640153092]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.10714027210237846]
[null,null,null,null,null,"Coincident",0.10714027210237846]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.3477551761377828E-2]
[null,null,null,null,null,"Coincident",9.3477551761377828E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.642624489214062E-2]
[null,null,null,null,null,"Coincident",9.642624489214062E-2]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Kilburn 11kV","Substation Rating","MVA","Non-Coincident",76.2]
[null,null,null,null,null,"Coincident",76.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",40.7408]
[null,null,null,null,null,"Coincident",21.8385]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",45.936161062174101]
[null,null,null,null,null,"Coincident",23.921541682968513]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4215421221321298]
[null,null,null,null,null,"Coincident",0.91177790101702194]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",46.311765355053694]
[null,null,null,null,null,"Coincident",24.824733134998333]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",52.217548806684235]
[null,null,null,null,null,"Coincident",27.192613433039462]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",43.366759095820683]
[null,null,null,null,null,"Coincident",23.246106323736399]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",48.896988536556044]
[null,null,null,null,null,"Coincident",25.463411012202222]
[null,null,"Kilburn South 11kV","Substation Rating","MVA","Non-Coincident",36.195]
[null,null,null,null,null,"Coincident",36.195]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.23]
[null,null,null,null,null,"Coincident",13.75]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",14.82000337381878]
[null,null,null,null,null,"Coincident",14.300608378666972]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.14703266666666667]
[null,null,null,null,null,"Coincident",0.27242799791216249]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.277114273678523]
[null,null,null,null,null,"Coincident",14.761793482999275]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.910533034302935]
[null,null,null,null,null,"Coincident",15.352918368518614]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.921647139574461]
[null,null,null,null,null,"Coincident",13.452048360446158]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.498865606297125]
[null,null,null,null,null,"Coincident",13.990725490445792]
[null,null,"Kilkenny 11kV","Substation Rating","MVA","Non-Coincident",55.9]
[null,null,null,null,null,"Coincident",55.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.29]
[null,null,null,null,null,"Coincident",21.582999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.849480194525214]
[null,null,null,null,null,"Coincident",22.010800331882525]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.178111129703256]
[null,null,null,null,null,"Coincident",0.32283898011635737]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.472426599552996]
[null,null,null,null,null,"Coincident",22.727922086054388]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.061585765093451]
[null,null,null,null,null,"Coincident",23.178416114290236]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.68142356739633]
[null,null,null,null,null,"Coincident",20.993726552495065]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.225628460849467]
[null,null,null,null,null,"Coincident",21.409846794658268]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Kingscote 11kV","Substation Rating","MVA","Non-Coincident",8]
[null,null,null,null,null,"Coincident",8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8845000000000001]
[null,null,null,null,null,"Coincident",2.8039000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.0375078370269271]
[null,null,null,null,null,"Coincident",2.9170871258843127]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0082186666666665E-2]
[null,null,null,null,null,"Coincident",0.13076474727092544]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.7908783848858101]
[null,null,null,null,null,"Coincident",2.7128944022816164]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.9389200784467673]
[null,null,null,null,null,"Coincident",2.8224078372193451]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6298079963159378]
[null,null,null,null,null,"Coincident",2.5563247151569621]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7693057371072078]
[null,null,null,null,null,"Coincident",2.659517784573008]
[null,null,"Kingston SE 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2240000000000002]
[null,null,null,null,null,"Coincident",2.5510000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2240038771688848]
[null,null,null,null,null,"Coincident",2.5696462791598385]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.14354794999999998]
[null,null,null,null,null,"Coincident",0.16517262735381946]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.7115121033023826]
[null,null,null,null,null,"Coincident",2.1454923621353532]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.711515364155471]
[null,null,null,null,null,"Coincident",2.1611746238051599]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4896444998011562]
[null,null,null,null,null,"Coincident",1.9699389326900587]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.4896474938371949]
[null,null,null,null,null,"Coincident",1.9843380041392054]
[null,null,"Kingswood 11kV","Substation Rating","MVA","Non-Coincident",71.2]
[null,null,null,null,null,"Coincident",71.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",46.69277607774557]
[null,null,null,null,null,"Coincident",46.69277607774557]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",48.7155994203356]
[null,null,null,null,null,"Coincident",48.7155994203356]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0771440053749555]
[null,null,null,null,null,"Coincident",1.0771440053749555]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",50.123968075691927]
[null,null,null,null,null,"Coincident",50.123968075691927]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",52.295437436989381]
[null,null,null,null,null,"Coincident",52.295437436989381]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",44.287037605155291]
[null,null,null,null,null,"Coincident",44.287037605155291]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",46.205639602447292]
[null,null,null,null,null,"Coincident",46.205639602447292]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Kongorong 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.91867939411816746]
[null,null,null,null,null,"Coincident",0.91867939411816746]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.96548944809548398]
[null,null,null,null,null,"Coincident",0.96548944809548398]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4059818403225474E-2]
[null,null,null,null,null,"Coincident",2.4059818403225474E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.91867939411816746]
[null,null,null,null,null,"Coincident",0.91867939411816746]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.96548944809548398]
[null,null,null,null,null,"Coincident",0.96548944809548398]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.82681145470635076]
[null,null,null,null,null,"Coincident",0.82681145470635076]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.86894050328593564]
[null,null,null,null,null,"Coincident",0.86894050328593564]
[null,null,"Kumorna 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.13629339022356435]
[null,null,null,null,null,"Coincident",0.13629339022356435]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.14029260942026517]
[null,null,null,null,null,"Coincident",0.14029260942026517]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.13629339022356435]
[null,null,null,null,null,"Coincident",0.13629339022356435]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.14029260942026517]
[null,null,null,null,null,"Coincident",0.14029260942026517]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.51742736853925342]
[null,null,null,null,null,"Coincident",0.51742736853925342]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.53261009648934887]
[null,null,null,null,null,"Coincident",0.53261009648934887]
[null,null,"Kybunga 11kV","Substation Rating","MVA","Non-Coincident",0.13]
[null,null,null,null,null,"Coincident",0.13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.6000000000000001E-2]
[null,null,null,null,null,"Coincident",4.2000000000000003E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.7723478758647251E-2]
[null,null,null,null,null,"Coincident",4.4598206241955519E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.0128000000000002E-4]
[null,null,null,null,null,"Coincident",2.6105773678750783E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.8909023721159776E-2]
[null,null,null,null,null,"Coincident",4.4181767790869832E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0722031776089522E-2]
[null,null,null,null,null,"Coincident",4.6914942668366669E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.0615253726228659E-2]
[null,null,null,null,null,"Coincident",3.7961440294671495E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.2173009345169663E-2]
[null,null,null,null,null,"Coincident",4.030981294055809E-2]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Lameroo 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.2841360646007458]
[null,null,null,null,null,"Coincident",1.2841360646007458]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3246433641748609]
[null,null,null,null,null,"Coincident",1.3246433641748609]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.4568556922875275E-2]
[null,null,null,null,null,"Coincident",6.4568556922875275E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2841360646007458]
[null,null,null,null,null,"Coincident",1.2841360646007458]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3246433641748609]
[null,null,null,null,null,"Coincident",1.3246433641748609]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1557224581406713]
[null,null,null,null,null,"Coincident",1.1557224581406713]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.1921790277573749]
[null,null,null,null,null,"Coincident",1.1921790277573749]
[null,null,"Langhorne Creek 11kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.54]
[null,null,null,null,null,"Coincident",3.54]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.8996300452735255]
[null,null,null,null,null,"Coincident",3.8996300452735255]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.6826203898180641E-2]
[null,null,null,null,null,"Coincident",9.6826203898180641E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.6094819635040558]
[null,null,null,null,null,"Coincident",3.6094819635040558]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9761707098173149]
[null,null,null,null,null,"Coincident",3.9761707098173149]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.2542990101066387]
[null,null,null,null,null,"Coincident",3.2542990101066387]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5849045751739381]
[null,null,null,null,null,"Coincident",3.5849045751739381]
[null,null,"Largs North 7.6kV","Substation Rating","MVA","Non-Coincident",27.5]
[null,null,null,null,null,"Coincident",27.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.371499999999999]
[null,null,null,null,null,"Coincident",13.882200000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.943266861280343]
[null,null,null,null,null,"Coincident",14.428745122151129]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.973362666666666E-2]
[null,null,null,null,null,"Coincident",0.51534035433027459]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",14.281506105527439]
[null,null,null,null,null,"Coincident",12.89781244889263]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",14.812728947820872]
[null,null,null,null,null,"Coincident",13.405602026939508]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",12.586399560567141]
[null,null,null,null,null,"Coincident",11.366939854907146]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.054570277254893]
[null,null,null,null,null,"Coincident",11.814458658229729]
[null,null,"LeFevre 11kV","Substation Rating","MVA","Non-Coincident",72.2]
[null,null,null,null,null,"Coincident",72.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.4]
[null,null,null,null,null,"Coincident",5.98]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.772933676580397]
[null,null,null,null,null,"Coincident",6.2008063991709985]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-17"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.1000000000000011E-2]
[null,null,null,null,null,"Coincident",8.6465864065814729E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.887859028106407]
[null,null,null,null,null,"Coincident",6.2605189411611848]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.27828684516802]
[null,null,null,null,null,"Coincident",6.4916832629571095]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.29129871614068]
[null,null,null,null,null,"Coincident",5.9174967617808916]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.660334472582743]
[null,null,null,null,null,"Coincident",6.1359952821947514]
[null,null,"Leigh Creek South 11kV","Substation Rating","MVA","Non-Coincident",6.6]
[null,null,null,null,null,"Coincident",6.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.168288]
[null,null,null,null,null,"Coincident",1.138652]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.192259]
[null,null,null,null,null,"Coincident",1.150525]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",3.7374350947264018E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3181780792561131]
[null,null,null,null,null,"Coincident",1.2847398127012617]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3452245324747101]
[null,null,null,null,null,"Coincident",1.2981361056829648]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2136224739945081]
[null,null,null,null,null,"Coincident",1.1828364729063334]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2385236493246683]
[null,null,null,null,null,"Coincident",1.1951701950996083]
[null,null,"Linden Park 11kV","Substation Rating","MVA","Non-Coincident",55.7]
[null,null,null,null,null,"Coincident",55.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",40.927899999999994]
[null,null,null,null,null,"Coincident",37.532300000000006]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",42.993845928225582]
[null,null,null,null,null,"Coincident",39.236975920424861]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.51374735999999999]
[null,null,null,null,null,"Coincident",0.95189162986995379]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",42.146796010980815]
[null,null,null,null,null,"Coincident",38.650069803799745]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",44.274268996563762]
[null,null,null,null,null,"Coincident",40.40551360333447]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",37.111989767066746]
[null,null,null,null,null,"Coincident",34.032978323698003]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",38.985317354058047]
[null,null,null,null,null,"Coincident",35.57871888979038]
[null,null,"Little Swamp 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.26427804426966683]
[null,null,null,null,null,"Coincident",0.26427804426966683]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.27245159203058439]
[null,null,null,null,null,"Coincident",0.27245159203058439]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4997504122215566E-2]
[null,null,null,null,null,"Coincident",1.4997504122215566E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.20413879239225444]
[null,null,null,null,null,"Coincident",0.20413879239225444]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.21045236329098399]
[null,null,null,null,null,"Coincident",0.21045236329098399]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.1858513256658485]
[null,null,null,null,null,"Coincident",0.1858513256658485]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.19159930481015311]
[null,null,null,null,null,"Coincident",0.19159930481015311]
[null,null,"Lobethal 11kV","Substation Rating","MVA","Non-Coincident",12.8]
[null,null,null,null,null,"Coincident",12.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.1312999999999995]
[null,null,null,null,null,"Coincident",5.9653]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.3488648221552166]
[null,null,null,null,null,"Coincident",6.0903647263526013]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.49079970666666667]
[null,null,null,null,null,"Coincident",0.29607502828033777]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.392490990201031]
[null,null,null,null,null,"Coincident",6.2194194549029103]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.6193239889797431]
[null,null,null,null,null,"Coincident",6.34981188985161]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.8477079834209418]
[null,null,null,null,null,"Coincident",5.6893860084322974]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.0552097444550821]
[null,null,null,null,null,"Coincident",5.8086660956465037]
[null,null,"Lock 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.88274819488730838]
[null,null,null,null,null,"Coincident",0.88274819488730838]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.89286086428009293]
[null,null,null,null,null,"Coincident",0.89286086428009293]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4782673026815687E-2]
[null,null,null,null,null,"Coincident",2.4782673026815687E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.88274819488730838]
[null,null,null,null,null,"Coincident",0.88274819488730838]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.89286086428009293]
[null,null,null,null,null,"Coincident",0.89286086428009293]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.79447337539857754]
[null,null,null,null,null,"Coincident",0.79447337539857754]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.80357477785208364]
[null,null,null,null,null,"Coincident",0.80357477785208364]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Loveday 11kV","Substation Rating","MVA","Non-Coincident",20.399999999999999]
[null,null,null,null,null,"Coincident",20.399999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.7462]
[null,null,null,null,null,"Coincident",9.7074999999999996]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.986761314049762]
[null,null,null,null,null,"Coincident",9.7797654951435309]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.205748144438845E-2]
[null,null,null,null,null,"Coincident",0.38868809648604752]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.834013940592223]
[null,null,null,null,null,"Coincident",9.780072732313343]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.076373677701422]
[null,null,null,null,null,"Coincident",9.8528784802958693]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.684741417483451]
[null,null,null,null,null,"Coincident",8.8302708373959735]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.903564137654378]
[null,null,null,null,null,"Coincident",8.8960059797411617]
[null,null,"Lower Mitcham 11kV","Substation Rating","MVA","Non-Coincident",28.2]
[null,null,null,null,null,"Coincident",28.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.730499999999999]
[null,null,null,null,null,"Coincident",17.853400000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.304770581646391]
[null,null,null,null,null,"Coincident",18.38311195091843]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.9999640000000003E-2]
[null,null,null,null,null,"Coincident",0.51879051523822872]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.269016445327772]
[null,null,null,null,null,"Coincident",18.366699138037685]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.859797752917654]
[null,null,null,null,null,"Coincident",18.911640719604321]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.961181711155433]
[null,null,null,null,null,"Coincident",16.166934228234293]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.481205612635659]
[null,null,null,null,null,"Coincident",16.646608591123599]
[null,null,"Loxton 11kV","Substation Rating","MVA","Non-Coincident",19.899999999999999]
[null,null,null,null,null,"Coincident",19.899999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.490400000000001]
[null,null,null,null,null,"Coincident",8.2748999999999988]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.493318631274434]
[null,null,null,null,null,"Coincident",8.3148205302339502]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-02"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1412217248171494E-3]
[null,null,null,null,null,"Coincident",0.26640409409442528]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.639580195115139]
[null,null,null,null,null,"Coincident",9.1024909625912276]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.642790725127425]
[null,null,null,null,null,"Coincident",9.1464040329215521]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.756134399040317]
[null,null,null,null,null,"Coincident",8.4662706727893458]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.759120528463441]
[null,null,null,null,null,"Coincident",8.5071144309449611]
[null,null,"Lucindale 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.194]
[null,null,null,null,null,"Coincident",1.0780000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2188769421069545]
[null,null,null,null,null,"Coincident",1.09585263607841]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.3648799999999998E-3]
[null,null,null,null,null,"Coincident",4.3642088501666794E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3076704515211828]
[null,null,null,null,null,"Coincident",1.1806270910718888]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.3349157129260969]
[null,null,null,null,null,"Coincident",1.2001793227984361]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1792785552121967]
[null,null,null,null,null,"Coincident",1.0647087793289349]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2038487766074955]
[null,null,null,null,null,"Coincident",1.0823413010050458]
[null,null,"Lyndoch 11kV","Substation Rating","MVA","Non-Coincident",4.3]
[null,null,null,null,null,"Coincident",4.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.806]
[null,null,null,null,null,"Coincident",2.548]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9672986031068733]
[null,null,null,null,null,"Coincident",2.6650075046798647]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.6252480000000002E-2]
[null,null,null,null,null,"Coincident",0.12275524135078089]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.9872387523265487]
[null,null,null,null,null,"Coincident",2.7125746047498382]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.1589555869298955]
[null,null,null,null,null,"Coincident",2.837139591311749]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6713904893896787]
[null,null,null,null,null,"Coincident",2.4257672726175699]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8249512713895153]
[null,null,null,null,null,"Coincident",2.5371616900049569]
[null,null,"Lyndoch South 7.6kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.43797615118071831]
[null,null,null,null,null,"Coincident",0.43797615118071831]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.45186226058385071]
[null,null,null,null,null,"Coincident",0.45186226058385071]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0957127226148174E-2]
[null,null,null,null,null,"Coincident",1.0957127226148174E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.43797615118071831]
[null,null,null,null,null,"Coincident",0.43797615118071831]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.45186226058385071]
[null,null,null,null,null,"Coincident",0.45186226058385071]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.39417853606264647]
[null,null,null,null,null,"Coincident",0.39417853606264647]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.40667603452546564]
[null,null,null,null,null,"Coincident",0.40667603452546564]
[null,null,"Lyrup 11kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.4847000000000001]
[null,null,null,null,null,"Coincident",2.5971000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.8725354394763127]
[null,null,null,null,null,"Coincident",2.8562100938131287]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.12581593261185736]
[null,null,null,null,null,"Coincident",8.9590913324881394E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.4869524249759416]
[null,null,null,null,null,"Coincident",2.598778702013091]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.8750385518085348]
[null,null,null,null,null,"Coincident",2.8580562782628207]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.1583062857295618]
[null,null,null,null,null,"Coincident",2.3538431585698181]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5098151979247936]
[null,null,null,null,null,"Coincident",2.5886837583304807]
[null,null,"MacGillivray 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.679]
[null,null,null,null,null,"Coincident",1.64]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.691712150455863]
[null,null,null,null,null,"Coincident",1.6553624980650008]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.9136512094578624E-3]
[null,null,null,null,null,"Coincident",8.2378449739695533E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5266871143351546]
[null,null,null,null,null,"Coincident",1.4912250550980664]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.5382460638863491]
[null,null,null,null,null,"Coincident",1.5051939221855206]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4480974778909972]
[null,null,null,null,null,"Coincident",1.4144609075290264]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4590614046412689]
[null,null,null,null,null,"Coincident",1.4277106959161814]
[null,null,"Maitland 11kV","Substation Rating","MVA","Non-Coincident",7.125]
[null,null,null,null,null,"Coincident",7.125]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1968870562988281]
[null,null,null,null,null,"Coincident",2.087042703483887]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.3371138896796047]
[null,null,null,null,null,"Coincident",2.2202581951956244]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4111508479481878E-2]
[null,null,null,null,null,"Coincident",0.22283446398684559]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.170687178001713]
[null,null,null,null,null,"Coincident",2.0621528191016276]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3092416787252268]
[null,null,null,null,null,"Coincident",2.1937795947889653]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9463314850768385]
[null,null,null,null,null,"Coincident",1.849014910822997]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0705654096562114]
[null,null,null,null,null,"Coincident",1.967037139173401]
[null,null,"Mallala 11kV","Substation Rating","MVA","Non-Coincident",4.8]
[null,null,null,null,null,"Coincident",4.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.0841065222151096]
[null,null,null,null,null,"Coincident",3.8387095637987509]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.4392462197990321]
[null,null,null,null,null,"Coincident",4.1725103954334246]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.678688619403669E-2]
[null,null,null,null,null,"Coincident",0.15514154953181622]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0553316197500369]
[null,null,null,null,null,"Coincident",3.8116636254302922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.4079691519022139]
[null,null,null,null,null,"Coincident",4.1431126363372739]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6695988287230157]
[null,null,null,null,null,"Coincident",3.4491079119757102]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.9886943790467559]
[null,null,null,null,null,"Coincident",3.7490303391040327]
[null,null,"Mannum Town 7.6kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9071059407885693]
[null,null,null,null,null,"Coincident",3.7924730448409689]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.1127430955669153]
[null,null,null,null,null,"Coincident",3.9920768893062832]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.9254137036298209E-2]
[null,null,null,null,null,"Coincident",0.17794346254461219]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0587220082546924]
[null,null,null,null,null,"Coincident",3.9396407586793116]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.2723389560575713]
[null,null,null,null,null,"Coincident",4.1469902722940128]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6096021577183546]
[null,null,null,null,null,"Coincident",3.5036979015172931]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.7995812186508999]
[null,null,null,null,null,"Coincident",3.6881030542287299]
[null,null,"Marion Bay 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.73327954069755552]
[null,null,null,null,null,"Coincident",0.73327954069755552]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.7454889055476871]
[null,null,null,null,null,"Coincident",0.7454889055476871]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.58363460463217E-2]
[null,null,null,null,null,"Coincident",2.58363460463217E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.73327954069755552]
[null,null,null,null,null,"Coincident",0.73327954069755552]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.7454889055476871]
[null,null,null,null,null,"Coincident",0.7454889055476871]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.65995158662780007]
[null,null,null,null,null,"Coincident",0.65995158662780007]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.67094001499291844]
[null,null,null,null,null,"Coincident",0.67094001499291844]
[null,null,"Marrabel 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1385463399792537]
[null,null,null,null,null,"Coincident",1.1385463399792537]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1860809089279374]
[null,null,null,null,null,"Coincident",1.1860809089279374]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.3208325838452274E-2]
[null,null,null,null,null,"Coincident",5.3208325838452274E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1385463399792537]
[null,null,null,null,null,"Coincident",1.1385463399792537]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1860809089279374]
[null,null,null,null,null,"Coincident",1.1860809089279374]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.92869940634905879]
[null,null,null,null,null,"Coincident",0.92869940634905879]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.96747281803514373]
[null,null,null,null,null,"Coincident",0.96747281803514373]
[null,null,"McLaren Flat TF1 11kV","Substation Rating","MVA","Non-Coincident",15.5]
[null,null,null,null,null,"Coincident",15.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.2069426329876762]
[null,null,null,null,null,"Coincident",5.8659653375069754]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.8208160802062379]
[null,null,null,null,null,"Coincident",6.4461157555021709]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.5170454458303371E-2]
[null,null,null,null,null,"Coincident",0.32503936342510431]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.804329696235488]
[null,null,null,null,null,"Coincident",6.4305350481182684]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.4772853804785591]
[null,null,null,null,null,"Coincident",7.0665220308991961]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.0434431409863985]
[null,null,null,null,null,"Coincident",5.7114476611742964]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.6411463087762623]
[null,null,null,null,null,"Coincident",6.2763161111805452]
[null,null,"McLaren Flat TF2 11kV","Substation Rating","MVA","Non-Coincident",15.5]
[null,null,null,null,null,"Coincident",15.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.903]
[null,null,null,null,null,"Coincident",1.7257]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9852738753129251]
[null,null,null,null,null,"Coincident",1.7943279354677617]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-01"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.5361009999999998E-2]
[null,null,null,null,null,"Coincident",7.5629270254174291E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.058806640741579]
[null,null,null,null,null,"Coincident",1.8669903415279785]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.1478166254256541]
[null,null,null,null,null,"Coincident",1.9412371356853153]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8427836191899667]
[null,null,null,null,null,"Coincident",1.6710938999664349]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9224541129965542]
[null,null,null,null,null,"Coincident",1.737550250622671]
[null,null,"McLaren Vale 11kV","Substation Rating","MVA","Non-Coincident",5.4]
[null,null,null,null,null,"Coincident",5.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4284010501422535]
[null,null,null,null,null,"Coincident",2.4284010501422535]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.5035062372600554]
[null,null,null,null,null,"Coincident",2.5035062372600554]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.1226272718719635]
[null,null,null,null,null,"Coincident",0.1226272718719635]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1024537224366942]
[null,null,null,null,null,"Coincident",2.1024537224366942]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.1674822593713921]
[null,null,null,null,null,"Coincident",2.1674822593713921]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8579395049115388]
[null,null,null,null,null,"Coincident",1.8579395049115388]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9154052585822297]
[null,null,null,null,null,"Coincident",1.9154052585822297]
[null,null,"McLaren Vale Vineyard 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.9697991492591007E-2]
[null,null,null,null,null,"Coincident",4.9697991492591007E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.0130728199631283E-2]
[null,null,null,null,null,"Coincident",5.0130728199631283E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.9697991492591007E-2]
[null,null,null,null,null,"Coincident",4.9697991492591007E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.0130728199631283E-2]
[null,null,null,null,null,"Coincident",5.0130728199631283E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.4728192343331911E-2]
[null,null,null,null,null,"Coincident",4.4728192343331911E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.5117655379668158E-2]
[null,null,null,null,null,"Coincident",4.5117655379668158E-2]
[null,null,"Meadows 11kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1763000000000003]
[null,null,null,null,null,"Coincident",4.9354999999999993]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.4415472919014496]
[null,null,null,null,null,"Coincident",5.1591925279058923]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.0497799999999999E-2]
[null,null,null,null,null,"Coincident",0.39555279436596064]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.6282275975416685]
[null,null,null,null,null,"Coincident",4.4129237694235073]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.865390211097969]
[null,null,null,null,null,"Coincident",4.6129314836243678]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.2330921747156269]
[null,null,null,null,null,"Coincident",4.0361699337961428]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.4500070049442719]
[null,null,null,null,null,"Coincident",4.2191019681490189]
[null,null,"Melrose 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.30858093264937747]
[null,null,null,null,null,"Coincident",0.30858093264937747]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.31013958286067728]
[null,null,null,null,null,"Coincident",0.31013958286067728]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.0102621668389397E-2]
[null,null,null,null,null,"Coincident",2.0102621668389397E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.30858093264937747]
[null,null,null,null,null,"Coincident",0.30858093264937747]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.31013958286067728]
[null,null,null,null,null,"Coincident",0.31013958286067728]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.27772283938443976]
[null,null,null,null,null,"Coincident",0.27772283938443976]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.27912562457460954]
[null,null,null,null,null,"Coincident",0.27912562457460954]
[null,null,"Meningie 11kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1162000000000001]
[null,null,null,null,null,"Coincident",2.0530999999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2007086222396639]
[null,null,null,null,null,"Coincident",2.1221913250223219]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.1101817588968119E-3]
[null,null,null,null,null,"Coincident",8.4194751680262025E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9109222004310398]
[null,null,null,null,null,"Coincident",1.8539430912508115]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9872332307521881]
[null,null,null,null,null,"Coincident",1.9163323488079194]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7379408640772707]
[null,null,null,null,null,"Coincident",1.686119642773388]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8073440338897557]
[null,null,null,null,null,"Coincident",1.7428612726332964]
[null,null,"Milang 11kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9996894201166591]
[null,null,null,null,null,"Coincident",1.8050518127631039]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1049362317017466]
[null,null,null,null,null,"Coincident",1.9000545397506357]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.7232134999999983E-2]
[null,null,null,null,null,"Coincident",0.11155237813895769]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1168953065323732]
[null,null,null,null,null,"Coincident",1.9108495909645054]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2283108489814456]
[null,null,null,null,null,"Coincident",2.0114206220679001]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9433573619907727]
[null,null,null,null,null,"Coincident",1.7542027746005298]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0456393284113399]
[null,null,null,null,null,"Coincident",1.8465292364216102]
[null,null,"Millicent 11kV","Substation Rating","MVA","Non-Coincident",13.2]
[null,null,null,null,null,"Coincident",13.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.0228999999999999]
[null,null,null,null,null,"Coincident",5.5093999999999994]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.415595562377665]
[null,null,null,null,null,"Coincident",5.8552703712125878]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.2217493333333331E-2]
[null,null,null,null,null,"Coincident",0.28815821376647166]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.9619712196259096]
[null,null,null,null,null,"Coincident",4.5389238136789558]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.2854937882544419]
[null,null,null,null,null,"Coincident",4.8238694092688199]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.5668823382358381]
[null,null,null,null,null,"Coincident",4.1775193933614245]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.8646449489592687]
[null,null,null,null,null,"Coincident",4.439776659729759]
[null,null,"Minlaton 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6412636324393466]
[null,null,null,null,null,"Coincident",1.223021859834075]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7096496171243194]
[null,null,null,null,null,"Coincident",1.2739811039938282]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.1976016037574717E-2]
[null,null,null,null,null,"Coincident",0.10234289895730775]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3836270021993478]
[null,null,null,null,null,"Coincident",1.031038546215413]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4412781272909874]
[null,null,null,null,null,"Coincident",1.0739984856410554]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2676109216396623]
[null,null,null,null,null,"Coincident",0.94458674175674706]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3204280433746483]
[null,null,null,null,null,"Coincident",0.98394452266327836]
[null,null,"Monarto South 11kV","Substation Rating","MVA","Non-Coincident",14.5]
[null,null,null,null,null,"Coincident",14.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.6370117810072466]
[null,null,null,null,null,"Coincident",4.3475399030409516]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3918741639619148]
[null,null,null,null,null,"Coincident",5.0552789570243624]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-12-13"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.37681399999999993]
[null,null,null,null,null,"Coincident",6.6982337984136553E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1213441422877271]
[null,null,null,null,null,"Coincident",4.8016371463616379]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.9550513282415434]
[null,null,null,null,null,"Coincident",5.5832990073972537]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.8040564039317353]
[null,null,null,null,null,"Coincident",4.5041565341927692]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.5861120975950413]
[null,null,null,null,null,"Coincident",5.2373913188288013]
[null,null,"Moonta 11kV","Substation Rating","MVA","Non-Coincident",12.8]
[null,null,null,null,null,"Coincident",12.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",8.4273278452425231]
[null,null,null,null,null,"Coincident",7.0597351686022893]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.6879668507654877]
[null,null,null,null,null,"Coincident",7.2780774934044219]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.38584386750000005]
[null,null,null,null,null,"Coincident",0.44476743487494114]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3432275997707457]
[null,null,null,null,null,"Coincident",6.9892827699833884]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.6012655667739644]
[null,null,null,null,null,"Coincident",7.2054461546220505]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.254115655805256]
[null,null,null,null,null,"Coincident",6.076912676573702]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.4784697482528415]
[null,null,null,null,null,"Coincident",6.2648584294574245]
[null,null,"Moorkitabie 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.59099999999999997]
[null,null,null,null,null,"Coincident",0.52]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.5915285284751699]
[null,null,null,null,null,"Coincident",0.52034699960699304]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.9761195742421197E-3]
[null,null,null,null,null,"Coincident",2.750479135933567E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.49142899075586877]
[null,null,null,null,null,"Coincident",0.43239099017436849]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.49186847335339584]
[null,null,null,null,null,"Coincident",0.43267952768140278]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.45551367963498179]
[null,null,null,null,null,"Coincident",0.400790378020627]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.45592104334143951]
[null,null,null,null,null,"Coincident",0.40105782821997266]
[null,null,"Morgan 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0171767508701284]
[null,null,null,null,null,"Coincident",1.0171767508701284]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0695369381841204]
[null,null,null,null,null,"Coincident",1.0695369381841204]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.3288961912822006E-2]
[null,null,null,null,null,"Coincident",4.3288961912822006E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0171767508701284]
[null,null,null,null,null,"Coincident",1.0171767508701284]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0695369381841204]
[null,null,null,null,null,"Coincident",1.0695369381841204]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.91545907578311558]
[null,null,null,null,null,"Coincident",0.91545907578311558]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.96258324436570841]
[null,null,null,null,null,"Coincident",0.96258324436570841]
[null,null,"Morphett Vale East 11kV","Substation Rating","MVA","Non-Coincident",57.3]
[null,null,null,null,null,"Coincident",57.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",34.077199999999998]
[null,null,null,null,null,"Coincident",33.2134]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.913815705677315]
[null,null,null,null,null,"Coincident",34.084549664033993]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.88773701333333288]
[null,null,null,null,null,"Coincident",1.6448345983086925]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.702852846776999]
[null,null,null,null,null,"Coincident",31.873890247471717]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",33.505727505260317]
[null,null,null,null,null,"Coincident",32.70990609591064]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.165895319547975]
[null,null,null,null,null,"Coincident",28.426588675310025]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.881935548630011]
[null,null,null,null,null,"Coincident",29.172185728732103]
[null,null,"Morphettville 11kV","Substation Rating","MVA","Non-Coincident",28]
[null,null,null,null,null,"Coincident",28]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.8127]
[null,null,null,null,null,"Coincident",22.253499999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.005970245351531]
[null,null,null,null,null,"Coincident",22.445690527359588]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.2979194723068522E-2]
[null,null,null,null,null,"Coincident",0.48962471463018881]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.030239116539036]
[null,null,null,null,null,"Coincident",21.490219315552363]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",22.216880317238928]
[null,null,null,null,null,"Coincident",21.675817831890434]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",19.312583087299252]
[null,null,null,null,null,"Coincident",18.839180269464546]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.476200180920532]
[null,null,null,null,null,"Coincident",19.001883304538165]
[null,null,"Mount Barker 11kV","Substation Rating","MVA","Non-Coincident",72.400000000000006]
[null,null,null,null,null,"Coincident",72.400000000000006]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.015000000000001]
[null,null,null,null,null,"Coincident",22.509999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.063181155252629]
[null,null,null,null,null,"Coincident",22.55287564812966]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.53086413333333338]
[null,null,null,null,null,"Coincident",0.98360627121892585]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.87916914960179]
[null,null,null,null,null,"Coincident",20.421034002065444]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",20.922879012314926]
[null,null,null,null,null,"Coincident",20.45993071767257]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.664515059600824]
[null,null,null,null,null,"Coincident",18.254974320730586]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.703588615881582]
[null,null,null,null,null,"Coincident",18.289745260561403]
[null,null,"Mount Burr 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.37270760276534182]
[null,null,null,null,null,"Coincident",0.37270760276534182]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.40398720875711758]
[null,null,null,null,null,"Coincident",0.40398720875711758]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7540811047847438E-2]
[null,null,null,null,null,"Coincident",1.7540811047847438E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.37270760276534182]
[null,null,null,null,null,"Coincident",0.37270760276534182]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.40398720875711758]
[null,null,null,null,null,"Coincident",0.40398720875711758]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.33543684248880767]
[null,null,null,null,null,"Coincident",0.33543684248880767]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.36358848788140585]
[null,null,null,null,null,"Coincident",0.36358848788140585]
[null,null,"Mount Gambier 11kV","Substation Rating","MVA","Non-Coincident",25.4]
[null,null,null,null,null,"Coincident",25.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.4137]
[null,null,null,null,null,"Coincident",13.4137]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.431230162944868]
[null,null,null,null,null,"Coincident",13.431230162944868]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.45673119769054354]
[null,null,null,null,null,"Coincident",0.45673119769054354]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.562433802979342]
[null,null,null,null,null,"Coincident",11.562433802979342]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.577544573952711]
[null,null,null,null,null,"Coincident",11.577544573952711]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.711273386313293]
[null,null,null,null,null,"Coincident",10.711273386313293]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.725271788529616]
[null,null,null,null,null,"Coincident",10.725271788529616]
[null,null,"Mount Gambier North 11kV","Substation Rating","MVA","Non-Coincident",17]
[null,null,null,null,null,"Coincident",17]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.230462017954027]
[null,null,null,null,null,"Coincident",9.9804924454056856]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.656731268702112]
[null,null,null,null,null,"Coincident",10.396346297297589]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.54878339693606248]
[null,null,null,null,null,"Coincident",0.23528796945651678]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.7436008424502258]
[null,null,null,null,null,"Coincident",9.5055271627479243]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.149584210885653]
[null,null,null,null,null,"Coincident",9.9015907945290866]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.028406575556577]
[null,null,null,null,null,"Coincident",8.8078078451645503]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.4045901828714342]
[null,null,null,null,null,"Coincident",9.1747998387130725]
[null,null,"Mount Gambier West 11kV","Substation Rating","MVA","Non-Coincident",25.6]
[null,null,null,null,null,"Coincident",25.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.2265]
[null,null,null,null,null,"Coincident",14.274000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.647092844998395]
[null,null,null,null,null,"Coincident",14.593881644031516]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1830088350871837]
[null,null,null,null,null,"Coincident",0.32418110325838717]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.118283977887298]
[null,null,null,null,null,"Coincident",15.10999806261211]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.563510058388509]
[null,null,null,null,null,"Coincident",15.448614499601137]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.012681412904229]
[null,null,null,null,null,"Coincident",14.073556922982627]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",15.427368070147057]
[null,null,null,null,null,"Coincident",14.38894661934628]
[null,null,"Mount Pleasant 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1399834137674989]
[null,null,null,null,null,"Coincident",1.9241560267379563]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.2291493893411447]
[null,null,null,null,null,"Coincident",2.0043291945187045]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.1385800000000011E-2]
[null,null,null,null,null,"Coincident",0.11373806225081336]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1990373523291531]
[null,null,null,null,null,"Coincident",1.9772540979916831]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2906639086762013]
[null,null,null,null,null,"Coincident",2.0596396854080035]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9587675822427375]
[null,null,null,null,null,"Coincident",1.7612166636917606]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0403828981695185]
[null,null,null,null,null,"Coincident",1.8346006913455839]
[null,null,"Mount Schank 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.4689999999999999]
[null,null,null,null,null,"Coincident",1.323]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.747359823539683]
[null,null,null,null,null,"Coincident",1.5774060986315477]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-16"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","00:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",1.1520020001216626E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1336903482979865]
[null,null,null,null,null,"Coincident",1.1433261769130159]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3742467147785669]
[null,null,null,null,null,"Coincident",1.363181923044356]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9387271793658039]
[null,null,null,null,null,"Coincident",1.0388562407051269]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1573030220307907]
[null,null,null,null,null,"Coincident",1.2386229551698491]
[null,null,"Murray Bridge North 11kV","Substation Rating","MVA","Non-Coincident",26]
[null,null,null,null,null,"Coincident",26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.941000000000003]
[null,null,null,null,null,"Coincident",16.8368]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.280608895811518]
[null,null,null,null,null,"Coincident",17.248879357222023]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.0884552928791182E-2]
[null,null,null,null,null,"Coincident",0.470266391119678]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",16.93883922314447]
[null,null,null,null,null,"Coincident",16.83465251356111]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",17.278404802797436]
[null,null,null,null,null,"Coincident",17.246679311221257]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",15.714971734239985]
[null,null,null,null,null,"Coincident",15.618312738035046]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.030002971969424]
[null,null,null,null,null,"Coincident",16.000569715250549]
[null,null,"Murray Bridge South 11kV","Substation Rating","MVA","Non-Coincident",28.5]
[null,null,null,null,null,"Coincident",28.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.6168]
[null,null,null,null,null,"Coincident",15.6168]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.354362666884942]
[null,null,null,null,null,"Coincident",16.354362666884942]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.92151551333333326]
[null,null,null,null,null,"Coincident",0.55590443100292664]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.597937255405473]
[null,null,null,null,null,"Coincident",15.597937255405473]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.334609057567302]
[null,null,null,null,null,"Coincident",16.334609057567302]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.112573969833862]
[null,null,null,null,null,"Coincident",14.112573969833862]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.779093851871263]
[null,null,null,null,null,"Coincident",14.779093851871263]
[null,null,"Mylor 11kV","Substation Rating","MVA","Non-Coincident",4.5999999999999996]
[null,null,null,null,null,"Coincident",4.5999999999999996]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.294]
[null,null,null,null,null,"Coincident",2.0979999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.340455511219985]
[null,null,null,null,null,"Coincident",2.1337584211901777]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.17483259368725232]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.1924701168871588]
[null,null,null,null,null,"Coincident",2.0051448584260063]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2368695589597536]
[null,null,null,null,null,"Coincident",2.0393206517505615]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9656800665562399]
[null,null,null,null,null,"Coincident",1.7977318132672151]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0054868112758579]
[null,null,null,null,null,"Coincident",1.8283724478552947]
[null,null,"Mypolonga 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5230000000000001]
[null,null,null,null,null,"Coincident",1.4330000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.6361382740668216]
[null,null,null,null,null,"Coincident",1.5240898923619959]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.5489359999999997E-2]
[null,null,null,null,null,"Coincident",8.9792032924698478E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2490029733004882]
[null,null,null,null,null,"Coincident",1.2773766392150614]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3498544654805782]
[null,null,null,null,null,"Coincident",1.3585741971856322]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0005938575976696]
[null,null,null,null,null,"Coincident",1.1362865627972496]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0903060003472871]
[null,null,null,null,null,"Coincident",1.2085156072477616]
[null,null,"Myponga 11kV","Substation Rating","MVA","Non-Coincident",14.2]
[null,null,null,null,null,"Coincident",14.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.4620999999999995]
[null,null,null,null,null,"Coincident",4.8114999999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.7871448271146617]
[null,null,null,null,null,"Coincident",5.0551540530432897]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-28"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.4558291296672575E-2]
[null,null,null,null,null,"Coincident",0.22696355485944458]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.2370292955507898]
[null,null,null,null,null,"Coincident",5.494126152128783]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.6081894920102817]
[null,null,null,null,null,"Coincident",5.7723483499667365]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.5076739240513888]
[null,null,null,null,null,"Coincident",4.8516455366202118]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.8354308158049664]
[null,null,null,null,null,"Coincident",5.0973325570768058]
[null,null,"Nairne 11kV","Substation Rating","MVA","Non-Coincident",9.1999999999999993]
[null,null,null,null,null,"Coincident",9.1999999999999993]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.0519999999999996]
[null,null,null,null,null,"Coincident",6.6959999999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.2863291855364318]
[null,null,null,null,null,"Coincident",6.8999015210363694]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.2027074689857523E-2]
[null,null,null,null,null,"Coincident",0.38840708242783356]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.010278462112554]
[null,null,null,null,null,"Coincident",5.7068667870541212]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.2099925371088665]
[null,null,null,null,null,"Coincident",5.8806479725726808]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3219084424271621]
[null,null,null,null,null,"Coincident",5.0532471540686723]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.4987488381749525]
[null,null,null,null,null,"Coincident",5.2071248095177927]
[null,null,"Nangwarry 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.97399999999999998]
[null,null,null,null,null,"Coincident",0.73099999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.037709015090454]
[null,null,null,null,null,"Coincident",0.78066446057188998]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-01"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.1420175586448581]
[null,null,null,null,null,"Coincident",2.8858155063693797E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1826043346672046]
[null,null,null,null,null,"Coincident",0.88756033741450369]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.2599580897014442]
[null,null,null,null,null,"Coincident",0.94786157596812348]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0593877981875246]
[null,null,null,null,null,"Coincident",0.79508468221260831]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.1286820006735327]
[null,null,null,null,null,"Coincident",0.84910308419764502]
[null,null,"Naracoorte 11kV","Substation Rating","MVA","Non-Coincident",27.8]
[null,null,null,null,null,"Coincident",27.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.9628000000000014]
[null,null,null,null,null,"Coincident",9.6440999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.587505506019822]
[null,null,null,null,null,"Coincident",10.25323416147315]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.22229816000000005]
[null,null,null,null,null,"Coincident",0.41188291038515862]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.692233617208309]
[null,null,null,null,null,"Coincident",10.350199765901015]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.362677389272413]
[null,null,null,null,null,"Coincident",11.003932126150465]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.4335201769114558]
[null,null,null,null,null,"Coincident",9.1317513086834783]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.02503782211819]
[null,null,null,null,null,"Coincident",9.7085248465145106]
[null,null,"Naracoorte East 11kV","Substation Rating","MVA","Non-Coincident",17.2]
[null,null,null,null,null,"Coincident",17.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.7377000000000002]
[null,null,null,null,null,"Coincident",4.0517000000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3112297803804349]
[null,null,null,null,null,"Coincident",4.4291253877035359]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.25483509999999998]
[null,null,null,null,null,"Coincident",3.9222472325806744E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.4323955746149712]
[null,null,null,null,null,"Coincident",4.6458064355420303]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0900228285247948]
[null,null,null,null,null,"Coincident",5.0785742355099526]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.0360492172429741]
[null,null,null,null,null,"Coincident",4.3068494445624159]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.6456961348507635]
[null,null,null,null,null,"Coincident",4.7080426033339755]
[null,null,"Narrung 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0682007663487236]
[null,null,null,null,null,"Coincident",0.89078333802782805]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1012379034522923]
[null,null,null,null,null,"Coincident",0.91833333817301865]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.2048529757128268E-3]
[null,null,null,null,null,"Coincident",2.9955233946960852E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1845625378615854]
[null,null,null,null,null,"Coincident",0.98781858693647739]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.2211984926408095]
[null,null,null,null,null,"Coincident",1.0183696772541004]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0878403690574121]
[null,null,null,null,null,"Coincident",0.90716099980220144]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.121484916554033]
[null,null,null,null,null,"Coincident",0.93521752556927984]
[null,null,"New Richmond 11kV","Substation Rating","MVA","Non-Coincident",51.1]
[null,null,null,null,null,"Coincident",51.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.4603]
[null,null,null,null,null,"Coincident",26.72]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",31.403006265802006]
[null,null,null,null,null,"Coincident",27.991886246017792]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.5183614350000001]
[null,null,null,null,null,"Coincident",0.50333456910473628]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.226383146180829]
[null,null,null,null,null,"Coincident",29.228791209388625]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",34.351493768347666]
[null,null,null,null,null,"Coincident",30.6200972545588]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.059527013423782]
[null,null,null,null,null,"Coincident",26.356505595621343]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.975805028590667]
[null,null,null,null,null,"Coincident",27.61108931419027]
[null,null,"Nildottie 11kV","Substation Rating","MVA","Non-Coincident",4.9400000000000004]
[null,null,null,null,null,"Coincident",4.9400000000000004]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.75]
[null,null,null,null,null,"Coincident",1.0620000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7532680913083429]
[null,null,null,null,null,"Coincident",1.0658067367022972]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2739980697183497E-4]
[null,null,null,null,null,"Coincident",2.9682693543425405E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0910727912840374]
[null,null,null,null,null,"Coincident",1.2689824596249417]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0949778294636419]
[null,null,null,null,null,"Coincident",1.2735311245059451]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.8999177844551931]
[null,null,null,null,null,"Coincident",1.1529786783379514]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9034658443397328]
[null,null,null,null,null,"Coincident",1.157111527915913]
[null,null,"Ninnes 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.81322090764099475]
[null,null,null,null,null,"Coincident",0.81322090764099475]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.87894047906199091]
[null,null,null,null,null,"Coincident",0.87894047906199091]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.9098726362071835E-2]
[null,null,null,null,null,"Coincident",5.9098726362071835E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.81322090764099475]
[null,null,null,null,null,"Coincident",0.81322090764099475]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.87894047906199091]
[null,null,null,null,null,"Coincident",0.87894047906199091]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.73189881687689529]
[null,null,null,null,null,"Coincident",0.73189881687689529]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.79104643115579187]
[null,null,null,null,null,"Coincident",0.79104643115579187]
[null,null,"Noarlunga Centre 11kV","Substation Rating","MVA","Non-Coincident",28.3]
[null,null,null,null,null,"Coincident",28.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",18.427199999999999]
[null,null,null,null,null,"Coincident",14.431000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.617334045430333]
[null,null,null,null,null,"Coincident",15.080269105357504]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1712495460620458]
[null,null,null,null,null,"Coincident",0.32095869343638234]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.67641557834256]
[null,null,null,null,null,"Coincident",14.62616964113167]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.882645392225893]
[null,null,null,null,null,"Coincident",15.284219677699102]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.06520349157034]
[null,null,null,null,null,"Coincident",13.364371775790765]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.167372006999404]
[null,null,null,null,null,"Coincident",13.965651916219892]
[null,null,"North Adelaide 11kV","Substation Rating","MVA","Non-Coincident",72.104033832140544]
[null,null,null,null,null,"Coincident",72.104033832140544]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.48]
[null,null,null,null,null,"Coincident",18.649999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.486293305267896]
[null,null,null,null,null,"Coincident",18.674691429846973]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.79100264500000006]
[null,null,null,null,null,"Coincident",0.26221620643426163]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.080507642094144]
[null,null,null,null,null,"Coincident",20.039640015132949]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.087269871159773]
[null,null,null,null,null,"Coincident",20.066171241170068]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.9201943346443]
[null,null,null,null,null,"Coincident",18.163948991672076]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.92632362557594]
[null,null,null,null,null,"Coincident",18.18799692048022]
[null,null,"North Unley 11kV","Substation Rating","MVA","Non-Coincident",25.4]
[null,null,null,null,null,"Coincident",25.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.488799999999998]
[null,null,null,null,null,"Coincident",14.448345601388047]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.474626218952306]
[null,null,null,null,null,"Coincident",15.09610981131094]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.85801437999999997]
[null,null,null,null,null,"Coincident",0.28443049743486631]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.406284047419959]
[null,null,null,null,null,"Coincident",15.206323655964914]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.443827927356271]
[null,null,null,null,null,"Coincident",15.888070376357014]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.484899237188667]
[null,null,null,null,null,"Coincident",13.618974508425969]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.414136571071349]
[null,null,null,null,null,"Coincident",14.229555436221817]
[null,null,"Northfield 11kV","Substation Rating","MVA","Non-Coincident",26.5]
[null,null,null,null,null,"Coincident",26.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.021999999999998]
[null,null,null,null,null,"Coincident",18.694600000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",20.19935506792234]
[null,null,null,null,null,"Coincident",19.789157768838976]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.72910109054205274]
[null,null,null,null,null,"Coincident",0.72910109054205274]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.389663827916849]
[null,null,null,null,null,"Coincident",20.038724077246052]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.651669612851702]
[null,null,null,null,null,"Coincident",21.211979515520756]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.022627137375402]
[null,null,null,null,null,"Coincident",17.71242799297541]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.138126632563271]
[null,null,null,null,null,"Coincident",18.749480171931481]
[null,null,"Norwood 11kV","Substation Rating","MVA","Non-Coincident",73.8]
[null,null,null,null,null,"Coincident",73.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",58.319499999999998]
[null,null,null,null,null,"Coincident",55.682499999999997]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",59.456985548377737]
[null,null,null,null,null,"Coincident",56.669388564373975]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.71746117333333337]
[null,null,null,null,null,"Coincident",1.3293407204129988]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",60.393765478042269]
[null,null,null,null,null,"Coincident",57.662974583648499]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",61.571708283508492]
[null,null,null,null,null,"Coincident",58.684964081325333]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",53.684173677216336]
[null,null,null,null,null,"Coincident",51.256766618053973]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",54.731250070779971]
[null,null,null,null,null,"Coincident",52.165215714666793]
[null,null,"Nuriootpa 11kV","Substation Rating","MVA","Non-Coincident",13.4]
[null,null,null,null,null,"Coincident",13.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.435600000000001]
[null,null,null,null,null,"Coincident",10.700100000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.031616656542878]
[null,null,null,null,null,"Coincident",11.280129625584983]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.3521204720505175]
[null,null,null,null,null,"Coincident",0.3521204720505175]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",12.118185347542605]
[null,null,null,null,null,"Coincident",11.338783713774582]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.749777945588114]
[null,null,null,null,null,"Coincident",11.953435022836159]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",10.982139567614592]
[null,null,null,null,null,"Coincident",10.275804644044291]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.554522136677596]
[null,null,null,null,null,"Coincident",10.832834122298648]
[null,null,"Oaklands 11kV","Substation Rating","MVA","Non-Coincident",57.5]
[null,null,null,null,null,"Coincident",57.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",42.903400000000005]
[null,null,null,null,null,"Coincident",40.707999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",43.395061032334091]
[null,null,null,null,null,"Coincident",41.017019749855059]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.2631133333333329E-2]
[null,null,null,null,null,"Coincident",1.0717158513606317]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",42.727398171877908]
[null,null,null,null,null,"Coincident",40.541004320888455]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",43.217042272208765]
[null,null,null,null,null,"Coincident",40.848756384711635]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",37.947916216786659]
[null,null,null,null,null,"Coincident",36.006092136123272]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",38.382788783111771]
[null,null,null,null,null,"Coincident",36.279419088691881]
[null,null,"Orroroo 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4464731217939564]
[null,null,null,null,null,"Coincident",1.4464731217939564]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4537792946594243]
[null,null,null,null,null,"Coincident",1.4537792946594243]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.966381736054561E-2]
[null,null,null,null,null,"Coincident",6.966381736054561E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.4464731217939564]
[null,null,null,null,null,"Coincident",1.4464731217939564]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4537792946594243]
[null,null,null,null,null,"Coincident",1.4537792946594243]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.301825809614561]
[null,null,null,null,null,"Coincident",1.301825809614561]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.308401365193482]
[null,null,null,null,null,"Coincident",1.308401365193482]
[null,null,"Padthaway 11kV","Substation Rating","MVA","Non-Coincident",13.8]
[null,null,null,null,null,"Coincident",13.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.1837999999999997]
[null,null,null,null,null,"Coincident",2.7384000000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.3541692861273411]
[null,null,null,null,null,"Coincident",2.8669314606387091]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","22:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",4.5669194218825759E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.7057583731677082]
[null,null,null,null,null,"Coincident",3.1873386296508746]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9040583318953295]
[null,null,null,null,null,"Coincident",3.3369417882906669]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3611850756097059]
[null,null,null,null,null,"Coincident",2.8909696623687484]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5410464682453928]
[null,null,null,null,null,"Coincident",3.0266622395548608]
[null,null,"Palmer 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8654177186212E-2]
[null,null,null,null,null,"Coincident",2.8654177186212E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.0032301126556093E-2]
[null,null,null,null,null,"Coincident",3.0032301126556093E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.9769751356282949E-3]
[null,null,null,null,null,"Coincident",4.9769751356282949E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8654177186212E-2]
[null,null,null,null,null,"Coincident",2.8654177186212E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.0032301126556093E-2]
[null,null,null,null,null,"Coincident",3.0032301126556093E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.5788759467590801E-2]
[null,null,null,null,null,"Coincident",2.5788759467590801E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.7029071013900483E-2]
[null,null,null,null,null,"Coincident",2.7029071013900483E-2]
[null,null,"Panorama 11kV","Substation Rating","MVA","Non-Coincident",58.2]
[null,null,null,null,null,"Coincident",58.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",23.060000000000002]
[null,null,null,null,null,"Coincident",22.32]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.775779692788205]
[null,null,null,null,null,"Coincident",23.006929390946546]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.72228308422873599]
[null,null,null,null,null,"Coincident",0.72228308422873599]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.562786135023615]
[null,null,null,null,null,"Coincident",23.774561428175499]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.325212133017956]
[null,null,null,null,null,"Coincident",24.506256992775761]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.780565126681669]
[null,null,null,null,null,"Coincident",21.081622446987634]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.456631311205935]
[null,null,null,null,null,"Coincident",21.730439027080568]
[null,null,"Parafield Gardens 11kV","Substation Rating","MVA","Non-Coincident",70.2]
[null,null,null,null,null,"Coincident",70.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",27.48]
[null,null,null,null,null,"Coincident",26.84]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",28.186225359206933]
[null,null,null,null,null,"Coincident",27.533347054072447]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.65359195999999953]
[null,null,null,null,null,"Coincident",1.2110012907400578]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",28.648323468606879]
[null,null,null,null,null,"Coincident",27.981113606164797]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",29.384574288559328]
[null,null,null,null,null,"Coincident",28.703938594559016]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",25.580934917462265]
[null,null,null,null,null,"Coincident",24.98516350744859]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",26.238355039403093]
[null,null,null,null,null,"Coincident",25.630595307501043]
[null,null,"Paralowie 11kV","Substation Rating","MVA","Non-Coincident",27.5]
[null,null,null,null,null,"Coincident",27.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.6752]
[null,null,null,null,null,"Coincident",17.1388]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",18.19103836316113]
[null,null,null,null,null,"Coincident",17.645229209335877]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.7799984501570367E-2]
[null,null,null,null,null,"Coincident",0.53417763454392486]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.904417478951615]
[null,null,null,null,null,"Coincident",18.330713671599526]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.456129695438957]
[null,null,null,null,null,"Coincident",18.872362376950569]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.524322647206731]
[null,null,null,null,null,"Coincident",16.992501413616068]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.035757760237566]
[null,null,null,null,null,"Coincident",17.49460769034118]
[null,null,"Parilla 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.47904483885470817]
[null,null,null,null,null,"Coincident",0.44405163903912487]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.50425772511021916]
[null,null,null,null,null,"Coincident",0.46742277793592096]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-01"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.8157900000000001E-2]
[null,null,null,null,null,"Coincident",3.5215817116725019E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.58043427927578106]
[null,null,null,null,null,"Coincident",0.53803479791810427]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.6109834518692433]
[null,null,null,null,null,"Coincident",0.5663524188611625]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.52806484394384068]
[null,null,null,null,null,"Coincident",0.48949083771116708]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.55585773046720077]
[null,null,null,null,null,"Coincident",0.515253513380176]
[null,null,"Paringa 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3405]
[null,null,null,null,null,"Coincident",1.9414]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4546975882988114]
[null,null,null,null,null,"Coincident",2.019172840546346]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4319373385889981E-2]
[null,null,null,null,null,"Coincident",0.13233721547482635]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4335091216962681]
[null,null,null,null,null,"Coincident",2.0185492881269536]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5522448075757262]
[null,null,null,null,null,"Coincident",2.0994127433244594]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1856212168823892]
[null,null,null,null,null,"Coincident",1.8129310106624525]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2922619653988097]
[null,null,null,null,null,"Coincident",1.8855573599020614]
[null,null,"Paringa 33kV","Substation Rating","MVA","Non-Coincident",37.700000000000003]
[null,null,null,null,null,"Coincident",37.700000000000003]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.9]
[null,null,null,null,null,"Coincident",7.95]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",12.401213650284395]
[null,null,null,null,null,"Coincident",8.3072618834366843]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",11.956590807041984]
[null,null,null,null,null,"Coincident",7.987806463528047]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",12.460187993878485]
[null,null,null,null,null,"Coincident",8.3467673165705314]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",11.157230119774933]
[null,null,null,null,null,"Coincident",7.4537797859000596]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",11.627159198379589]
[null,null,null,null,null,"Coincident",7.7887422267847066]
[null,null,"Paskeville 11kV","Substation Rating","MVA","Non-Coincident",1.2]
[null,null,null,null,null,"Coincident",1.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.28273271699346408]
[null,null,null,null,null,"Coincident",0.28273271699346408]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.30558145687818317]
[null,null,null,null,null,"Coincident",0.30558145687818317]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.47171319018538E-2]
[null,null,null,null,null,"Coincident",2.47171319018538E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.28273271699346408]
[null,null,null,null,null,"Coincident",0.28273271699346408]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.30558145687818317]
[null,null,null,null,null,"Coincident",0.30558145687818317]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.25445944529411768]
[null,null,null,null,null,"Coincident",0.25445944529411768]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.27502331119036488]
[null,null,null,null,null,"Coincident",0.27502331119036488]
[null,null,"Peake 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.15107483112949949]
[null,null,null,null,null,"Coincident",0.15107483112949949]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.15584039578527772]
[null,null,null,null,null,"Coincident",0.15584039578527772]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.8225916665644557E-3]
[null,null,null,null,null,"Coincident",2.8225916665644557E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.15107483112949949]
[null,null,null,null,null,"Coincident",0.15107483112949949]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.15584039578527772]
[null,null,null,null,null,"Coincident",0.15584039578527772]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.13596734801654953]
[null,null,null,null,null,"Coincident",0.13596734801654953]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.14025635620674995]
[null,null,null,null,null,"Coincident",0.14025635620674995]
[null,null,"Pellaring Flat 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.5513923954040014E-2]
[null,null,null,null,null,"Coincident",9.5513923954040014E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.10010767042185366]
[null,null,null,null,null,"Coincident",0.10010767042185366]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7224000121910292E-3]
[null,null,null,null,null,"Coincident",1.7224000121910292E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.5513923954040014E-2]
[null,null,null,null,null,"Coincident",9.5513923954040014E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.10010767042185366]
[null,null,null,null,null,"Coincident",0.10010767042185366]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.5962531558636007E-2]
[null,null,null,null,null,"Coincident",8.5962531558636007E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.0096903379668289E-2]
[null,null,null,null,null,"Coincident",9.0096903379668289E-2]
[null,null,"Penfield 11kV","Substation Rating","MVA","Non-Coincident",56.2]
[null,null,null,null,null,"Coincident",56.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.18]
[null,null,null,null,null,"Coincident",16.8]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.413722472088885]
[null,null,null,null,null,"Coincident",17.533978441871085]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2982291447111773]
[null,null,null,null,null,"Coincident",0.23537581877440758]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.263294737421106]
[null,null,null,null,null,"Coincident",18.377968962519144]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.61289671958848]
[null,null,null,null,null,"Coincident",19.180887594892056]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.468990955471934]
[null,null,null,null,null,"Coincident",17.018893059149168]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",23.718788027921331]
[null,null,null,null,null,"Coincident",17.76243476212089]
[null,null,"Penneshaw 11kV","Substation Rating","MVA","Non-Coincident",1.95]
[null,null,null,null,null,"Coincident",1.95]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.54200395997537465]
[null,null,null,null,null,"Coincident",0.47468869299770489]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.59316966656542158]
[null,null,null,null,null,"Coincident",0.5194997722168252]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.1071399999999996E-3]
[null,null,null,null,null,"Coincident",2.9553340610782946E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.53515352198588773]
[null,null,null,null,null,"Coincident",0.46868905886986734]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.58567254049601858]
[null,null,null,null,null,"Coincident",0.51293376672991764]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.49519522173005126]
[null,null,null,null,null,"Coincident",0.43369345971646878]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.54194213741860853]
[null,null,null,null,null,"Coincident",0.47463454861715387]
[null,null,"Penola 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.653]
[null,null,null,null,null,"Coincident",2.431]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.762761299859255]
[null,null,null,null,null,"Coincident",2.5697567978312654]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.009390108148127E-2]
[null,null,null,null,null,"Coincident",9.3286118491598152E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.656035653985497]
[null,null,null,null,null,"Coincident",2.4337816339384633]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.7659225465048993]
[null,null,null,null,null,"Coincident",2.5726972020774372]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.3710463919765479]
[null,null,null,null,null,"Coincident",2.1726399468130371]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.4691425600918673]
[null,null,null,null,null,"Coincident",2.2966500504165204]
[null,null,"Peterborough 11kV","Substation Rating","MVA","Non-Coincident",6.2]
[null,null,null,null,null,"Coincident",6.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.1155999999999997]
[null,null,null,null,null,"Coincident",1.6257999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1625348482741265]
[null,null,null,null,null,"Coincident",1.6606445134344676]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.23033500565897019]
[null,null,null,null,null,"Coincident",9.8754911462032691E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9458298659902504]
[null,null,null,null,null,"Coincident",1.4953347495400593]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9889983427947111]
[null,null,null,null,null,"Coincident",1.52738310220913]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7626573669250534]
[null,null,null,null,null,"Coincident",1.3545700260667197]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8017621391295813]
[null,null,null,null,null,"Coincident",1.383601477334532]
[null,null,"Piccadilly 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6836174708368283]
[null,null,null,null,null,"Coincident",1.5579467924428609]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7356881142647715]
[null,null,null,null,null,"Coincident",1.6061307138586196]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.5399466666666664E-2]
[null,null,null,null,null,"Coincident",6.5589545845764416E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6170582319577151]
[null,null,null,null,null,"Coincident",1.4963557514164147]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6670703422244486]
[null,null,null,null,null,"Coincident",1.5426347952746544]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4475512754561142]
[null,null,null,null,null,"Coincident",1.3395013449061519]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4923209025320765]
[null,null,null,null,null,"Coincident",1.380929221552734]
[null,null,"Pinnaroo 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.494100696707056]
[null,null,null,null,null,"Coincident",1.2609510415760103]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5679998759821236]
[null,null,null,null,null,"Coincident",1.3281748408142147]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.4994685396320755E-3]
[null,null,null,null,null,"Coincident",5.0825153693070294E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.5664240664004132]
[null,null,null,null,null,"Coincident",1.3219885797728124]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.6439004059529145]
[null,null,null,null,null,"Coincident",1.3924664111490193]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4012549112724639]
[null,null,null,null,null,"Coincident",1.1825935452521559]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.4705618784175947]
[null,null,null,null,null,"Coincident",1.2456399510563538]
[null,null,"Pinnaroo South 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.11330612334712462]
[null,null,null,null,null,"Coincident",0.11330612334712462]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.1168802968389583]
[null,null,null,null,null,"Coincident",0.1168802968389583]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.11330612334712462]
[null,null,null,null,null,"Coincident",0.11330612334712462]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.1168802968389583]
[null,null,null,null,null,"Coincident",0.1168802968389583]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.10197551101241216]
[null,null,null,null,null,"Coincident",0.10197551101241216]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.10519226715506247]
[null,null,null,null,null,"Coincident",0.10519226715506247]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Plympton 11kV","Substation Rating","MVA","Non-Coincident",28.4]
[null,null,null,null,null,"Coincident",28.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.700800000000001]
[null,null,null,null,null,"Coincident",20.8078]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.720445612371769]
[null,null,null,null,null,"Coincident",20.812934971550746]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.5084359999999995E-2]
[null,null,null,null,null,"Coincident",0.45503992538941607]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",23.150443928194004]
[null,null,null,null,null,"Coincident",22.197790273587849]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",23.171401895072997]
[null,null,null,null,null,"Coincident",22.203268268452479]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.880592504467153]
[null,null,null,null,null,"Coincident",20.021344499486268]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",20.899495587599368]
[null,null,null,null,null,"Coincident",20.026285388691878]
[null,null,"Point Boston 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.95]
[null,null,null,null,null,"Coincident",0.85799999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0103642907387413]
[null,null,null,null,null,"Coincident",0.90253199389273731]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4064412703285806E-2]
[null,null,null,null,null,"Coincident",2.4383373666559752E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0362136414557039]
[null,null,null,null,null,"Coincident",0.93586453091473054]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1020560641086323]
[null,null,null,null,null,"Coincident",0.98443785675986373]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.99687484216759925]
[null,null,null,null,null,"Coincident",0.90033538376821076]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0602176240652224]
[null,null,null,null,null,"Coincident",0.94706467259266447]
[null,null,"Polda 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.70699999999999996]
[null,null,null,null,null,"Coincident",0.67]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.70836784229664174]
[null,null,null,null,null,"Coincident",0.67054380915791034]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.6701253333333332E-2]
[null,null,null,null,null,"Coincident",3.0944749295330035E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.55749626897943372]
[null,null,null,null,null,"Coincident",0.52832036805688909]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.55857486442063597]
[null,null,null,null,null,"Coincident",0.52874918216802325]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.51340209199683828]
[null,null,null,null,null,"Coincident",0.48653380712571664]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.51439537784778255]
[null,null,null,null,null,"Coincident",0.48692870494653445]
[null,null,"Poonindie 11kV","Substation Rating","MVA","Non-Coincident",1.95]
[null,null,null,null,null,"Coincident",1.95]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.49593810773119645]
[null,null,null,null,null,"Coincident",0.42534837706872702]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.52204011340125944]
[null,null,null,null,null,"Coincident",0.44773513375655477]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.651281876607142E-3]
[null,null,null,null,null,"Coincident",2.4502696558970579E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.46374033112123142]
[null,null,null,null,null,"Coincident",0.39773349566966937]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.48814771696971732]
[null,null,null,null,null,"Coincident",0.41866683754702039]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.43216521491784665]
[null,null,null,null,null,"Coincident",0.37065264783099994]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.45491075254510177]
[null,null,null,null,null,"Coincident",0.39016068192736836]
[null,null,"Port Adelaide 7.6kV","Substation Rating","MVA","Non-Coincident",19.899999999999999]
[null,null,null,null,null,"Coincident",19.899999999999999]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.2879000000000005]
[null,null,null,null,null,"Coincident",6.9995000000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.334870544423865]
[null,null,null,null,null,"Coincident",7.6750688733066106]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.75910208000000001]
[null,null,null,null,null,"Coincident",0.22652257895270889]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.1955867466014016]
[null,null,null,null,null,"Coincident",6.9299313550788133]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",10.232151358880403]
[null,null,null,null,null,"Coincident",7.5987856900517041]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.462701926308128]
[null,null,null,null,null,"Coincident",6.3776184210848239]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",9.4166527271440224]
[null,null,null,null,null,"Coincident",6.993165316021857]
[null,null,"Port Adelaide North 11kV","Substation Rating","MVA","Non-Coincident",47.2]
[null,null,null,null,null,"Coincident",47.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.273499999999999]
[null,null,null,null,null,"Coincident",13.0183]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",21.220001457587131]
[null,null,null,null,null,"Coincident",14.001717677842244]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-23"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","08:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.533570792986612]
[null,null,null,null,null,"Coincident",1.4040649730106229]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",22.006011517006371]
[null,null,null,null,null,"Coincident",14.863976949274603]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",24.228479335178061]
[null,null,null,null,null,"Coincident",16.298599445235297]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",20.421407087395544]
[null,null,null,null,null,"Coincident",13.793654701317426]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.483839892106445]
[null,null,null,null,null,"Coincident",15.124973190545148]
[null,null,"Port Augusta 11kV","Substation Rating","MVA","Non-Coincident",28.4]
[null,null,null,null,null,"Coincident",28.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",13.942699999999999]
[null,null,null,null,null,"Coincident",13.1539]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",13.946201616927814]
[null,null,null,null,null,"Coincident",13.223188678227352]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.5432145166666666]
[null,null,null,null,null,"Coincident",0.36641293351714044]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.382554558750767]
[null,null,null,null,null,"Coincident",14.512295639320342]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.386417785631927]
[null,null,null,null,null,"Coincident",14.588739719242881]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",14.004539217674475]
[null,null,null,null,null,"Coincident",13.212240700536359]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.008056365112981]
[null,null,null,null,null,"Coincident",13.281836690665658]
[null,null,"Port Augusta West TF1 11kV","Substation Rating","MVA","Non-Coincident",14.8]
[null,null,null,null,null,"Coincident",14.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.5865]
[null,null,null,null,null,"Coincident",5.2563000000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.7657015132592493]
[null,null,null,null,null,"Coincident",5.4349691903450577]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.6041828546027056]
[null,null,null,null,null,"Coincident",0.16556483651322204]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9166220264758733]
[null,null,null,null,null,"Coincident",5.5669095780479969]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.10641306210238]
[null,null,null,null,null,"Coincident",5.7561368342993484]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3453092900954147]
[null,null,null,null,null,"Coincident",5.0293652951809777]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.5167739842015315]
[null,null,null,null,null,"Coincident",5.2003206488022542]
[null,null,"Port Augusta West TF2 11kV","Substation Rating","MVA","Non-Coincident",14.8]
[null,null,null,null,null,"Coincident",14.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.0121000000000002]
[null,null,null,null,null,"Coincident",1.8492999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0705503278114255]
[null,null,null,null,null,"Coincident",1.9086833812866921]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.3631546666666669E-2]
[null,null,null,null,null,"Coincident",0.1767995191630215]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9243523507476366]
[null,null,null,null,null,"Coincident",1.7686520561789196]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9802536606854557]
[null,null,null,null,null,"Coincident",1.8254457291446713]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.744134102804485]
[null,null,null,null,null,"Coincident",1.6030153552588509]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.7948001780770897]
[null,null,null,null,null,"Coincident",1.654490222532824]
[null,null,"Port Broughton 11kV","Substation Rating","MVA","Non-Coincident",5.4]
[null,null,null,null,null,"Coincident",5.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0061127406003916]
[null,null,null,null,null,"Coincident",2.5626453800336866]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2675138484786865]
[null,null,null,null,null,"Coincident",2.7854841087322679]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.3389554375944913E-2]
[null,null,null,null,null,"Coincident",0.17132450065037408]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.9830833119239384]
[null,null,null,null,null,"Coincident",2.5430132956459466]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.2424818607868895]
[null,null,null,null,null,"Coincident",2.7641448865716809]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.6712217257656583]
[null,null,null,null,null,"Coincident",2.2771581125769051]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9035018758322373]
[null,null,null,null,null,"Coincident",2.4751718614966358]
[null,null,"Port Clinton 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.47250346030478974]
[null,null,null,null,null,"Coincident",0.36323703510930716]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.50806823688687064]
[null,null,null,null,null,"Coincident",0.39057745710678188]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.3978154776263045E-2]
[null,null,null,null,null,"Coincident",3.1370161346533851E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.34744240162337542]
[null,null,null,null,null,"Coincident",0.26709634624796991]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.37359398024018858]
[null,null,null,null,null,"Coincident",0.28720037230964507]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.31229478278202127]
[null,null,null,null,null,"Coincident",0.24007661426367891]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.33580084170109814]
[null,null,null,null,null,"Coincident",0.25814689705771926]
[null,null,"Port Germein 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.92514406142094918]
[null,null,null,null,null,"Coincident",0.92514406142094918]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.92981698782128175]
[null,null,null,null,null,"Coincident",0.92981698782128175]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.933010901431196E-2]
[null,null,null,null,null,"Coincident",5.933010901431196E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.92514406142094918]
[null,null,null,null,null,"Coincident",0.92514406142094918]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.92981698782128175]
[null,null,null,null,null,"Coincident",0.92981698782128175]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.83262965527885435]
[null,null,null,null,null,"Coincident",0.83262965527885435]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.83683528903915361]
[null,null,null,null,null,"Coincident",0.83683528903915361]
[null,null,"Port Giles 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.6860371458150023]
[null,null,null,null,null,"Coincident",0.88689661601564362]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7204460671581656]
[null,null,null,null,null,"Coincident",0.90499654695473841]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-24"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.10872696648668795]
[null,null,null,null,null,"Coincident",1.796656896250751E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8826093171258516]
[null,null,null,null,null,"Coincident",0.9902983672588922]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9210299154345425]
[null,null,null,null,null,"Coincident",1.0105085380192778]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6921009632896555]
[null,null,null,null,null,"Coincident",0.8900863317415133]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.7266336360098526]
[null,null,null,null,null,"Coincident",0.9082513589199116]
[null,null,"Port Julia 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.25873374963463891]
[null,null,null,null,null,"Coincident",0.1934342794887538]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.26673582436560711]
[null,null,null,null,null,"Coincident",0.1994167829780967]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.7514681568305794E-2]
[null,null,null,null,null,"Coincident",1.8621115553485727E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.19844015875433779]
[null,null,null,null,null,"Coincident",0.14835764249729058]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.20457748325189462]
[null,null,null,null,null,"Coincident",0.15294602319308309]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.18551818332101849]
[null,null,null,null,null,"Coincident",0.13869692753047569]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.19125585909383347]
[null,null,null,null,null,"Coincident",0.14298652322729452]
[null,null,"Port Lincoln City 11kV","Substation Rating","MVA","Non-Coincident",29]
[null,null,null,null,null,"Coincident",29]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",11.3544]
[null,null,null,null,null,"Coincident",10.5488]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",11.85588867398813]
[null,null,null,null,null,"Coincident",11.041433744310563]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.3024183031415118E-2]
[null,null,null,null,null,"Coincident",0.58245878958445085]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",10.715465989014001]
[null,null,null,null,null,"Coincident",9.95519865646013]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",11.188734927046442]
[null,null,null,null,null,"Coincident",10.420110948804988]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.7776143374915243]
[null,null,null,null,null,"Coincident",9.0838880190349638]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",10.2094612733821]
[null,null,null,null,null,"Coincident",9.5081097094371945]
[null,null,"Port Lincoln Docks 11kV","Substation Rating","MVA","Non-Coincident",12.3]
[null,null,null,null,null,"Coincident",12.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.1782000000000004]
[null,null,null,null,null,"Coincident",4.8700999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3072612645318307]
[null,null,null,null,null,"Coincident",4.9234159655669965]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-15"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.53341548000000005]
[null,null,null,null,null,"Coincident",0.1167437886174692]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9073485042233731]
[null,null,null,null,null,"Coincident",5.5558645765745336]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.0545830390009572]
[null,null,null,null,null,"Coincident",5.6166880267007206]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.4420600866952515]
[null,null,null,null,null,"Coincident",5.1182605593091308]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.5776977902306673]
[null,null,null,null,null,"Coincident",5.1742932904117858]
[null,null,"Port Lincoln Marina 11kV","Substation Rating","MVA","Non-Coincident",16.8]
[null,null,null,null,null,"Coincident",16.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.3563999999999998]
[null,null,null,null,null,"Coincident",5.1176000000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.7835188812694307]
[null,null,null,null,null,"Coincident",5.4269537468086089]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-15"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.74333465909357399]
[null,null,null,null,null,"Coincident",0.17963421605055516]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.8804455873294685]
[null,null,null,null,null,"Coincident",5.6182824915460552]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.3493518192438003]
[null,null,null,null,null,"Coincident",5.9579019888473246]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3943288866222563]
[null,null,null,null,null,"Coincident",5.1538379340934322]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.8244722140909806]
[null,null,null,null,null,"Coincident",5.4653822273864092]
[null,null,"Port Noarlunga 11kV","Substation Rating","MVA","Non-Coincident",63.1]
[null,null,null,null,null,"Coincident",63.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",29.3]
[null,null,null,null,null,"Coincident",28.67]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",29.764871913045418]
[null,null,null,null,null,"Coincident",29.116581186670938]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.59524593333333331]
[null,null,null,null,null,"Coincident",1.1028954419427646]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",27.591323369987251]
[null,null,null,null,null,"Coincident",26.998062833362955]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",28.029085529661678]
[null,null,null,null,null,"Coincident",27.418600919792663]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",24.643061698208253]
[null,null,null,null,null,"Coincident",24.113193818690466]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",25.034046928069767]
[null,null,null,null,null,"Coincident",24.488795447918825]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Port Pirie South 11kV","Substation Rating","MVA","Non-Coincident",40.5]
[null,null,null,null,null,"Coincident",40.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",22.918400000000002]
[null,null,null,null,null,"Coincident",22.918400000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",23.672246947005263]
[null,null,null,null,null,"Coincident",23.672246947005263]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.86718845890898488]
[null,null,null,null,null,"Coincident",0.86718845890898488]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",24.231449759939458]
[null,null,null,null,null,"Coincident",24.231449759939458]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.02848639526486]
[null,null,null,null,null,"Coincident",25.02848639526486]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",21.725177251201131]
[null,null,null,null,null,"Coincident",21.725177251201131]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.439775938018975]
[null,null,null,null,null,"Coincident",22.439775938018975]
[null,null,"Port Stanvac 11kV","Substation Rating","MVA","Non-Coincident",88.6]
[null,null,null,null,null,"Coincident",88.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.034300000000002]
[null,null,null,null,null,"Coincident",32.172899999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",33.354955399460515]
[null,null,null,null,null,"Coincident",32.50868841663717]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.11669451860700929]
[null,null,null,null,null,"Coincident",1.0784709105249093]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",35.279254153666272]
[null,null,null,null,null,"Coincident",34.359314892717251]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",35.621700742009686]
[null,null,null,null,null,"Coincident",34.71792291203051]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",31.9364027127131]
[null,null,null,null,null,"Coincident",31.103631402386224]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",32.246401107387022]
[null,null,null,null,null,"Coincident",31.428259867345041]
[null,null,"Port Vincent 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.514824500837088]
[null,null,null,null,null,"Coincident",0.62806508864881572]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.5616747431310185]
[null,null,null,null,null,"Coincident",0.64748978211218122]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.13020371249999999]
[null,null,null,null,null,"Coincident",6.2050498029550621E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.83206754673312289]
[null,null,null,null,null,"Coincident",0.34498555919313301]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.85780159457022975]
[null,null,null,null,null,"Coincident",0.35565521566302377]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.73593708389892909]
[null,null,null,null,null,"Coincident",0.30512867304662172]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.75869802463807123]
[null,null,null,null,null,"Coincident",0.3145656423161049]
[null,null,"Portee 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.63419380266922165]
[null,null,null,null,null,"Coincident",0.53453477653548687]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.66683956091401764]
[null,null,null,null,null,"Coincident",0.56205048705610061]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-12-25"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.1376799999999995E-3]
[null,null,null,null,null,"Coincident",1.7888057957935748E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.7362175497716279]
[null,null,null,null,null,"Coincident",0.62052622052180073]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.7741150821099505]
[null,null,null,null,null,"Coincident",0.6524684263498155]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.6410516089518371]
[null,null,null,null,null,"Coincident",0.54031492754511989]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.67405037961184378]
[null,null,null,null,null,"Coincident",0.56812817710141128]
[null,null,"Prospect 11kV","Substation Rating","MVA","Non-Coincident",49.4]
[null,null,null,null,null,"Coincident",49.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",28.179499999999997]
[null,null,null,null,null,"Coincident",26.839099999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.005582165490473]
[null,null,null,null,null,"Coincident",28.177275185865646]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.4124018300000003]
[null,null,null,null,null,"Coincident",4.1339583770172341]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",30.499721933679073]
[null,null,null,null,null,"Coincident",29.048957112447205]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.476158643894301]
[null,null,null,null,null,"Coincident",30.497313934514722]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",27.246572611165995]
[null,null,null,null,null,"Coincident",25.950548695624313]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.012199407808644]
[null,null,null,null,null,"Coincident",27.244421453059644]
[null,null,"Punyelroo 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.47756961977019996]
[null,null,null,null,null,"Coincident",0.47756961977019996]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.50053835210926823]
[null,null,null,null,null,"Coincident",0.50053835210926823]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.6303657464793762E-2]
[null,null,null,null,null,"Coincident",1.6303657464793762E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.47756961977019996]
[null,null,null,null,null,"Coincident",0.47756961977019996]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.50053835210926823]
[null,null,null,null,null,"Coincident",0.50053835210926823]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.42981265779317995]
[null,null,null,null,null,"Coincident",0.42981265779317995]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.4504845168983414]
[null,null,null,null,null,"Coincident",0.4504845168983414]
[null,null,"Pyap 11kV","Substation Rating","MVA","Non-Coincident",15.2]
[null,null,null,null,null,"Coincident",15.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.6127000000000002]
[null,null,null,null,null,"Coincident",6.335]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7381645194451636]
[null,null,null,null,null,"Coincident",6.3871205946028606]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.27351677607247915]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.9934433455495961]
[null,null,null,null,null,"Coincident",6.6518401610541185]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.1251828766044802]
[null,null,null,null,null,"Coincident",6.7065675271784002]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.155555402358301]
[null,null,null,null,null,"Coincident",5.9545816167640702]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2734857450645851]
[null,null,null,null,null,"Coincident",6.0035723562237395]
[null,null,"Qualco 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6816477977485209]
[null,null,null,null,null,"Coincident",2.6816477977485209]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8196882915763184]
[null,null,null,null,null,"Coincident",2.8196882915763184]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1121931163057616E-2]
[null,null,null,null,null,"Coincident",1.1121931163057616E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.6816477977485209]
[null,null,null,null,null,"Coincident",2.6816477977485209]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8196882915763184]
[null,null,null,null,null,"Coincident",2.8196882915763184]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4134830179736686]
[null,null,null,null,null,"Coincident",2.4134830179736686]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5377194624186865]
[null,null,null,null,null,"Coincident",2.5377194624186865]
[null,null,"Queenstown 7.6kV","Substation Rating","MVA","Non-Coincident",22.7]
[null,null,null,null,null,"Coincident",22.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",14.918100000000001]
[null,null,null,null,null,"Coincident",14.895800000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",15.72300384945574]
[null,null,null,null,null,"Coincident",15.673769825093133]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.3992851798542254]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.74495232270599]
[null,null,null,null,null,"Coincident",15.721416320346684]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",16.594468865298083]
[null,null,null,null,null,"Coincident",16.54250599025071]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.990816607263394]
[null,null,null,null,null,"Coincident",13.969902736841425]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",14.745689020252687]
[null,null,null,null,null,"Coincident",14.699515298016291]
[null,null,"Quorn 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.823]
[null,null,null,null,null,"Coincident",1.575]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8603682431174748]
[null,null,null,null,null,"Coincident",1.6201928897510938]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0708042675610156E-2]
[null,null,null,null,null,"Coincident",9.8961910740606271E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.8958261806489705]
[null,null,null,null,null,"Coincident",1.6379189437861372]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9346872303620615]
[null,null,null,null,null,"Coincident",1.6849172233085215]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.6568874756483916]
[null,null,null,null,null,"Coincident",1.4314853396303986]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6908507087851599]
[null,null,null,null,null,"Coincident",1.4725602343187947]
[null,null,"Ramco 11kV","Substation Rating","MVA","Non-Coincident",8.4]
[null,null,null,null,null,"Coincident",8.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.984]
[null,null,null,null,null,"Coincident",3.766]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3940916751571804]
[null,null,null,null,null,"Coincident",4.15358399457625]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","21:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.12612671832243513]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.1839306750329976]
[null,null,null,null,null,"Coincident",3.9170712123142595]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.6104729732719569]
[null,null,null,null,null,"Coincident",4.3202029455878641]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.8077197257806885]
[null,null,null,null,null,"Coincident",3.6327994557163068]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.2033067715334216]
[null,null,null,null,null,"Coincident",4.0066749003634001]
[null,null,"Rapid Bay 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.8364784592811895E-2]
[null,null,null,null,null,"Coincident",6.8364784592811895E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.9055337972537267E-2]
[null,null,null,null,null,"Coincident",6.9055337972537267E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.0090120694903524E-3]
[null,null,null,null,null,"Coincident",3.0090120694903524E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.8364784592811895E-2]
[null,null,null,null,null,"Coincident",6.8364784592811895E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.9055337972537267E-2]
[null,null,null,null,null,"Coincident",6.9055337972537267E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.1528306133530705E-2]
[null,null,null,null,null,"Coincident",6.1528306133530705E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.2149804175283541E-2]
[null,null,null,null,null,"Coincident",6.2149804175283541E-2]
[null,null,"Renmark 11kV","Substation Rating","MVA","Non-Coincident",28.5]
[null,null,null,null,null,"Coincident",28.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",19.718200000000003]
[null,null,null,null,null,"Coincident",18.8979]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",19.887675979862507]
[null,null,null,null,null,"Coincident",19.031135762481437]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.35421605333333334]
[null,null,null,null,null,"Coincident",0.65630565251677242]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.825407502422841]
[null,null,null,null,null,"Coincident",19.000647545923893]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.995804920171242]
[null,null,null,null,null,"Coincident",19.134607708874391]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.210647013170544]
[null,null,null,null,null,"Coincident",17.453062966710732]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.367165724132359]
[null,null,null,null,null,"Coincident",17.57611220244625]
[null,null,"Riverton 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8404771881226889]
[null,null,null,null,null,"Coincident",1.7353070630871066]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0005186827420531]
[null,null,null,null,null,"Coincident",1.8862033294425071]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.2723025869671438E-3]
[null,null,null,null,null,"Coincident",7.6451214757983929E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9199911547112232]
[null,null,null,null,null,"Coincident",1.8102773744420104]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0869469072948079]
[null,null,null,null,null,"Coincident",1.9676927983065329]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.7236824139082887]
[null,null,null,null,null,"Coincident",1.6251862759706721]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8735678412046615]
[null,null,null,null,null,"Coincident",1.7665068217072522]
[null,null,"Robe 7.6kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.6071516913348676]
[null,null,null,null,null,"Coincident",1.7012136059310285]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.7187130838503792]
[null,null,null,null,null,"Coincident",1.7538284597227098]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.0720175E-2]
[null,null,null,null,null,"Coincident",0.10401324651933117]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0910699832525186]
[null,null,null,null,null,"Coincident",0.98619548354694009]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.1557422507757926]
[null,null,null,null,null,"Coincident",1.0166963747906599]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9282918978786963]
[null,null,null,null,null,"Coincident",0.90942568918243649]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.987929791627522]
[null,null,null,null,null,"Coincident",0.93755225688910981]
[null,null,"Robertstown 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.9163621555903716]
[null,null,null,null,null,"Coincident",0.9163621555903716]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.95462048424800772]
[null,null,null,null,null,"Coincident",0.95462048424800772]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.4342338957932164E-2]
[null,null,null,null,null,"Coincident",3.4342338957932164E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.9163621555903716]
[null,null,null,null,null,"Coincident",0.9163621555903716]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.95462048424800772]
[null,null,null,null,null,"Coincident",0.95462048424800772]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.82472594003133448]
[null,null,null,null,null,"Coincident",0.82472594003133448]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.85915843582320695]
[null,null,null,null,null,"Coincident",0.85915843582320695]
[null,null,"Roonka 11kV","Substation Rating","MVA","Non-Coincident",6.25]
[null,null,null,null,null,"Coincident",6.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.6892999999999998]
[null,null,null,null,null,"Coincident",2.2928999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9719196658052516]
[null,null,null,null,null,"Coincident",2.5531831152504516]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7260566743733163E-2]
[null,null,null,null,null,"Coincident",5.5166950591271115E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.5535199006807763]
[null,null,null,null,null,"Coincident",2.177133744941417]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8218703788563095]
[null,null,null,null,null,"Coincident",2.4242754229257315]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.3600551003604409]
[null,null,null,null,null,"Coincident",2.0121854533211079]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.6080742814655045]
[null,null,null,null,null,"Coincident",2.240602697096266]
[null,null,"Rudall 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8083132765256487E-2]
[null,null,null,null,null,"Coincident",9.8083132765256487E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.9206762697788095E-2]
[null,null,null,null,null,"Coincident",9.9206762697788095E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.1160122450461254E-3]
[null,null,null,null,null,"Coincident",5.1160122450461254E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.8083132765256487E-2]
[null,null,null,null,null,"Coincident",9.8083132765256487E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.9206762697788095E-2]
[null,null,null,null,null,"Coincident",9.9206762697788095E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.8274819488730824E-2]
[null,null,null,null,null,"Coincident",8.8274819488730824E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.9286086428009281E-2]
[null,null,null,null,null,"Coincident",8.9286086428009281E-2]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Salisbury 11kV","Substation Rating","MVA","Non-Coincident",72.599999999999994]
[null,null,null,null,null,"Coincident",72.599999999999994]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",54.960000000000008]
[null,null,null,null,null,"Coincident",52.045800000000007]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",55.220584738754816]
[null,null,null,null,null,"Coincident",52.087410726585375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.7316169274369881]
[null,null,null,null,null,"Coincident",1.7316169274369881]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",58.298171505992954]
[null,null,null,null,null,"Coincident",55.206968241750509]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",58.574583692888368]
[null,null,null,null,null,"Coincident",55.2511063289951]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",53.24218397310274]
[null,null,null,null,null,"Coincident",50.419069480118459]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",53.494623940376506]
[null,null,null,null,null,"Coincident",50.459379632231133]
[null,null,"Salt Cliffs 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.19616437216634475]
[null,null,null,null,null,"Coincident",0.19616437216634475]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.19787243967371154]
[null,null,null,null,null,"Coincident",0.19787243967371154]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.063841405120158E-2]
[null,null,null,null,null,"Coincident",1.063841405120158E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.19616437216634475]
[null,null,null,null,null,"Coincident",0.19616437216634475]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.19787243967371154]
[null,null,null,null,null,"Coincident",0.19787243967371154]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.1765479349497103]
[null,null,null,null,null,"Coincident",0.1765479349497103]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.1780851957063404]
[null,null,null,null,null,"Coincident",0.1780851957063404]
[null,null,"Sandy Creek 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.8804875617775298]
[null,null,null,null,null,"Coincident",1.7193029136251703]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.0005186827420531]
[null,null,null,null,null,"Coincident",1.8290456527927343]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-17"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.1962324999999998E-2]
[null,null,null,null,null,"Coincident",0.10565506034621286]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.142645366205465]
[null,null,null,null,null,"Coincident",1.9589900491021395]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.2794099640483672]
[null,null,null,null,null,"Coincident",2.0840319671299357]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9258388246758922]
[null,null,null,null,null,"Coincident",1.7607669254179588]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.0487647071020132]
[null,null,null,null,null,"Coincident",1.8731563036361263]
[null,null,"Seacombe 11kV","Substation Rating","MVA","Non-Coincident",59.2]
[null,null,null,null,null,"Coincident",59.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",43.833500000000001]
[null,null,null,null,null,"Coincident",42.7545]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",44.07980175930922]
[null,null,null,null,null,"Coincident",43.023347093060998]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.15034665621845222]
[null,null,null,null,null,"Coincident",1.3894782476659573]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",40.610320237855653]
[null,null,null,null,null,"Coincident",39.610661631158806]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",40.838510852812128]
[null,null,null,null,null,"Coincident",39.859739768752739]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",35.795843861919508]
[null,null,null,null,null,"Coincident",34.914697808626684]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",35.996981788828123]
[null,null,null,null,null,"Coincident",35.134246979145637]
[null,null,"Seaford 11kV","Substation Rating","MVA","Non-Coincident",15.8]
[null,null,null,null,null,"Coincident",15.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.1798999999999999]
[null,null,null,null,null,"Coincident",8.8431999999999995]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.3952202752250571]
[null,null,null,null,null,"Coincident",9.0720896843009644]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.25997038666666666]
[null,null,null,null,null,"Coincident",0.48168351674265625]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.3686198037979764]
[null,null,null,null,null,"Coincident",8.0616759059408345]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.5649109964479671]
[null,null,null,null,null,"Coincident",8.2703373014817583]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.3910921954618223]
[null,null,null,null,null,"Coincident",7.1200020155892751]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.5644548688831676]
[null,null,null,null,null,"Coincident",7.3042899445709173]
[null,null,"Second Valley 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.29424655824951707]
[null,null,null,null,null,"Coincident",0.29424655824951707]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.29680865951056729]
[null,null,null,null,null,"Coincident",0.29680865951056729]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.4651367956103386E-2]
[null,null,null,null,null,"Coincident",3.4651367956103386E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.29424655824951707]
[null,null,null,null,null,"Coincident",0.29424655824951707]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.29680865951056729]
[null,null,null,null,null,"Coincident",0.29680865951056729]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.26482190242456533]
[null,null,null,null,null,"Coincident",0.26482190242456533]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.26712779355951055]
[null,null,null,null,null,"Coincident",0.26712779355951055]
[null,null,"Sheidow Park 11kV","Substation Rating","MVA","Non-Coincident",35]
[null,null,null,null,null,"Coincident",35]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",25.451599999999999]
[null,null,null,null,null,"Coincident",24.981999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",25.452802386377808]
[null,null,null,null,null,"Coincident",24.986439622323147]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.12717349082787011]
[null,null,null,null,null,"Coincident",1.1753157910497276]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",25.232295182928738]
[null,null,null,null,null,"Coincident",24.766741511729155]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",25.23348720889209]
[null,null,null,null,null,"Coincident",24.771142879853688]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",22.38381599772891]
[null,null,null,null,null,"Coincident",21.970818779772731]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",22.384873455627002]
[null,null,null,null,null,"Coincident",21.974723276510883]
[null,null,"Sherlock 11kV","Substation Rating","MVA","Non-Coincident",0.19500000000000001]
[null,null,null,null,null,"Coincident",0.19500000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.8326530836781154E-2]
[null,null,null,null,null,"Coincident",2.8326530836781154E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.9220074209739575E-2]
[null,null,null,null,null,"Coincident",2.9220074209739575E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.2621841194750583E-3]
[null,null,null,null,null,"Coincident",3.2621841194750583E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8326530836781154E-2]
[null,null,null,null,null,"Coincident",2.8326530836781154E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.9220074209739575E-2]
[null,null,null,null,null,"Coincident",2.9220074209739575E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.8326530836781154E-2]
[null,null,null,null,null,"Coincident",2.8326530836781154E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.9220074209739575E-2]
[null,null,null,null,null,"Coincident",2.9220074209739575E-2]
[null,null,"Smithfield West 11kV","Substation Rating","MVA","Non-Coincident",36.200000000000003]
[null,null,null,null,null,"Coincident",36.200000000000003]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.149999999999999]
[null,null,null,null,null,"Coincident",16.96]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.27447249556408]
[null,null,null,null,null,"Coincident",17.085856724203211]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.27893319999999999]
[null,null,null,null,null,"Coincident",0.51681857474234383]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.844773096660344]
[null,null,null,null,null,"Coincident",18.635997184802303]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.981546037516331]
[null,null,null,null,null,"Coincident",18.774291144586471]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.877836558302306]
[null,null,null,null,null,"Coincident",16.690851780105373]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.000333726590036]
[null,null,null,null,null,"Coincident",16.814711209893428]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"South End 11kV","Substation Rating","MVA","Non-Coincident",0.78]
[null,null,null,null,null,"Coincident",0.78]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.47]
[null,null,null,null,null,"Coincident",0.253]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.50152268144122858]
[null,null,null,null,null,"Coincident",0.29061658589970391]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.10209031125512856]
[null,null,null,null,null,"Coincident",3.7474651349580362E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.34902425894095762]
[null,null,null,null,null,"Coincident",0.18787901598311124]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.37243315368533358]
[null,null,null,null,null,"Coincident",0.21581327346722406]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.32756413201654888]
[null,null,null,null,null,"Coincident",0.17632707531954656]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.34953370602746425]
[null,null,null,null,null,"Coincident",0.20254376534010499]
[null,null,"Spalding 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.91452282639636717]
[null,null,null,null,null,"Coincident",0.68589211979727538]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.91452282639636717]
[null,null,null,null,null,"Coincident",0.68589211979727538]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.5572533333333338E-3]
[null,null,null,null,null,"Coincident",4.6137147475149951E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.98415008664236203]
[null,null,null,null,null,"Coincident",0.73811256498177147]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.98415008664236203]
[null,null,null,null,null,"Coincident",0.73811256498177147]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.88830661401874456]
[null,null,null,null,null,"Coincident",0.66622996051405847]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.88830661401874456]
[null,null,null,null,null,"Coincident",0.66622996051405847]
[null,null,"Square Water Hole 11kV","Substation Rating","MVA","Non-Coincident",7.13]
[null,null,null,null,null,"Coincident",7.13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.9355000000000002]
[null,null,null,null,null,"Coincident",3.7324000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.2242251668205384]
[null,null,null,null,null,"Coincident",4.0268026671293438]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.2175636723478317E-2]
[null,null,null,null,null,"Coincident",0.20494346618953163]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.6882125609794798]
[null,null,null,null,null,"Coincident",3.4978743647820636]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9587956601888319]
[null,null,null,null,null,"Coincident",3.7737782181405453]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3186148004666673]
[null,null,null,null,null,"Coincident",3.1473504970808763]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.56208262205931]
[null,null,null,null,null,"Coincident",3.395605877193264]
[null,null,"Stansbury 11kV","Substation Rating","MVA","Non-Coincident",2.7]
[null,null,null,null,null,"Coincident",2.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0528126496240122]
[null,null,null,null,null,"Coincident",0.75356045809764538]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1082238417094865]
[null,null,null,null,null,"Coincident",0.79322153483962676]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.2109888]
[null,null,null,null,null,"Coincident",6.2826096830220987E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.8369300685496589]
[null,null,null,null,null,"Coincident",0.59904049032580164]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.8809790195259567]
[null,null,null,null,null,"Coincident",0.63056893718505436]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.75649358719201454]
[null,null,null,null,null,"Coincident",0.5414673297437399]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.79630903914948892]
[null,null,null,null,null,"Coincident",0.56996561025656833]
[null,null,"Stirling East 11kV","Substation Rating","MVA","Non-Coincident",17.7]
[null,null,null,null,null,"Coincident",17.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.5281000000000002]
[null,null,null,null,null,"Coincident",7.1715]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7427982086581597]
[null,null,null,null,null,"Coincident",7.3853106833768338]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.44666794666666659]
[null,null,null,null,null,"Coincident",0.26945253459792962]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.0866093747157413]
[null,null,null,null,null,"Coincident",6.7509224280726787]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.2887164586029884]
[null,null,null,null,null,"Coincident",6.9521940362118704]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.368627790963183]
[null,null,null,null,null,"Coincident",6.0669510504499762]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.5502583455958749]
[null,null,null,null,null,"Coincident",6.2478307757669267]
[null,null,"Stirling North TF1 11kV","Substation Rating","MVA","Non-Coincident",3.25]
[null,null,null,null,null,"Coincident",3.25]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5609380441875325]
[null,null,null,null,null,"Coincident",1.389922275651412]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.7737932320312868]
[null,null,null,null,null,"Coincident",1.5794571314220591]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.4004533333333334E-2]
[null,null,null,null,null,"Coincident",0.10006175653152342]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6210849997904857]
[null,null,null,null,null,"Coincident",1.44347955405619]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.842142045216461]
[null,null,null,null,null,"Coincident",1.6403176750638522]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.4466665728370389]
[null,null,null,null,null,"Coincident",1.2881703425154731]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6439392873148169]
[null,null,null,null,null,"Coincident",1.4638299346766741]
[null,null,"Stirling North TF2 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.734]
[null,null,null,null,null,"Coincident",1.4870000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.791439644531738]
[null,null,null,null,null,"Coincident",1.5385688154905521]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",9.0750593493732101E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.6967165692136168]
[null,null,null,null,null,"Coincident",1.455027415467502]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.7529211808668694]
[null,null,null,null,null,"Coincident",1.5054874291339031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5287040559306453]
[null,null,null,null,null,"Coincident",1.3109474804895442]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.5793431664075093]
[null,null,null,null,null,"Coincident",1.3564108353914739]
[null,null,"Stockwell TF1 11kV","Substation Rating","MVA","Non-Coincident",8.9]
[null,null,null,null,null,"Coincident",8.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3710909530214139]
[null,null,null,null,null,"Coincident",2.1538917817522769]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4958852137067518]
[null,null,null,null,null,"Coincident",2.2672545071076602]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.8953163351664314E-3]
[null,null,null,null,null,"Coincident",6.3725341816505451E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.4505629082217846]
[null,null,null,null,null,"Coincident",2.2260838631938351]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.5795399033913524]
[null,null,null,null,null,"Coincident",2.3432461717829849]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2130985509399204]
[null,null,null,null,null,"Coincident",2.0103719661209967]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3295774220420213]
[null,null,null,null,null,"Coincident",2.1161810169694704]
[null,null,"Stockwell TF2 11kV","Substation Rating","MVA","Non-Coincident",8.9]
[null,null,null,null,null,"Coincident",8.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.0498807320074395]
[null,null,null,null,null,"Coincident",3.5837863259407627]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",5.3156639284288838]
[null,null,null,null,null,"Coincident",3.7724066588850138]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-20"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.3412862995276702]
[null,null,null,null,null,"Coincident",6.3725341816505451E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9015553808218746]
[null,null,null,null,null,"Coincident",4.1882005928413291]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.212163558759868]
[null,null,null,null,null,"Coincident",4.4086322029908738]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3984533698358579]
[null,null,null,null,null,"Coincident",3.8311604560125434]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.6825824945640608]
[null,null,null,null,null,"Coincident",4.0328004800132042]
[null,null,"Strathalbyn 11kV","Substation Rating","MVA","Non-Coincident",16.7]
[null,null,null,null,null,"Coincident",16.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",10.7744]
[null,null,null,null,null,"Coincident",10.3294]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",10.93276644633004]
[null,null,null,null,null,"Coincident",10.457233399422622]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.7761866666666671E-2]
[null,null,null,null,null,"Coincident",0.48976686451071305]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.886123769855919]
[null,null,null,null,null,"Coincident",8.5191126065813148]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.0167355759036791]
[null,null,null,null,null,"Coincident",8.6245424596766931]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.9629747222947351]
[null,null,null,null,null,"Coincident",7.6340910952323311]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.080017713921718]
[null,null,null,null,null,"Coincident",7.7285682009892493]
[null,null,"Streaky Bay 11kV","Substation Rating","MVA","Non-Coincident",6.5]
[null,null,null,null,null,"Coincident",6.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0629999999999997]
[null,null,null,null,null,"Coincident",2.6869999999999998]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.1045136495109822]
[null,null,null,null,null,"Coincident",2.7344136482982964]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.8756395000000004E-2]
[null,null,null,null,null,"Coincident",0.16757655130657728]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.8095419408451594]
[null,null,null,null,null,"Coincident",2.4646553036405301]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8476204062120059]
[null,null,null,null,null,"Coincident",2.508145552893728]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.4882294823258597]
[null,null,null,null,null,"Coincident",2.1827857065000278]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5219531149187975]
[null,null,null,null,null,"Coincident",2.221302205866809]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Swan Reach 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.25]
[null,null,null,null,null,"Coincident",1.016]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.3411547263459203]
[null,null,null,null,null,"Coincident",1.0900830243609889]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.4529992500000008E-2]
[null,null,null,null,null,"Coincident",3.1000952106972818E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3169083329362994]
[null,null,null,null,null,"Coincident",1.0703830930106242]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4129422679054757]
[null,null,null,null,null,"Coincident",1.1484315346987115]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1970511604008331]
[null,null,null,null,null,"Coincident",0.97296318317379715]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2843446571595565]
[null,null,null,null,null,"Coincident",1.043908119395657]
[null,null,"Swan Reach 33kV","Substation Rating","MVA","Non-Coincident",11.88]
[null,null,null,null,null,"Coincident",11.88]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.3360997149170415]
[null,null,null,null,null,"Coincident",2.3360997149170415]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.4563527766908031]
[null,null,null,null,null,"Coincident",2.4563527766908031]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.9817976043884735E-4]
[null,null,null,null,null,"Coincident",1.9817976043884735E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.3360997149170415]
[null,null,null,null,null,"Coincident",2.3360997149170415]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.4563527766908031]
[null,null,null,null,null,"Coincident",2.4563527766908031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.1024897434253376]
[null,null,null,null,null,"Coincident",2.1024897434253376]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.2107174990217229]
[null,null,null,null,null,"Coincident",2.2107174990217229]
[null,null,null,"Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"Tailem Bend Town 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.0214966225899902]
[null,null,null,null,null,"Coincident",3.0214966225899902]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.116807915705555]
[null,null,null,null,null,"Coincident",3.116807915705555]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.15617239556320883]
[null,null,null,null,null,"Coincident",0.15617239556320883]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.0214966225899902]
[null,null,null,null,null,"Coincident",3.0214966225899902]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.116807915705555]
[null,null,null,null,null,"Coincident",3.116807915705555]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.7193469603309914]
[null,null,null,null,null,"Coincident",2.7193469603309914]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.8051271241349998]
[null,null,null,null,null,"Coincident",2.8051271241349998]
[null,null,"Tantanoola 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.52200000000000002]
[null,null,null,null,null,"Coincident",0.36]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.57082834547699191]
[null,null,null,null,null,"Coincident",0.39274546464599691]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2016-12-05"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","07:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.8775541648319513E-2]
[null,null,null,null,null,"Coincident",1.8485710010358661E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.49518063229975945]
[null,null,null,null,null,"Coincident",0.34150388434466167]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.54150027020674785]
[null,null,null,null,null,"Coincident",0.37256694926488043]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.45650656620447327]
[null,null,null,null,null,"Coincident",0.31483211462377464]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.49920859748253321]
[null,null,null,null,null,"Coincident",0.34346912539832258]
[null,null,"Tarlton 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.59963949005502737]
[null,null,null,null,null,"Coincident",0.57617788325780062]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.61818504129384266]
[null,null,null,null,null,"Coincident",0.59399781779154703]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.2663653333333334E-2]
[null,null,null,null,null,"Coincident",2.3463722736355747E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.56106975586764096]
[null,null,null,null,null,"Coincident",0.53911723570127457]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.57842242872952676]
[null,null,null,null,null,"Coincident",0.55579096464048927]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.53668068972507688]
[null,null,null,null,null,"Coincident",0.51568242072041415]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.55327906157224427]
[null,null,null,null,null,"Coincident",0.53163136156743729]
[null,null,"Tarpeena 11kV","Substation Rating","MVA","Non-Coincident",9.5]
[null,null,null,null,null,"Coincident",9.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.3469814646758138]
[null,null,null,null,null,"Coincident",4.3469814646758138]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.52810569237064]
[null,null,null,null,null,"Coincident",4.52810569237064]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.2189215900025639E-2]
[null,null,null,null,null,"Coincident",2.2189215900025639E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.3469814646758138]
[null,null,null,null,null,"Coincident",4.3469814646758138]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.52810569237064]
[null,null,null,null,null,"Coincident",4.52810569237064]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.9122833182082326]
[null,null,null,null,null,"Coincident",3.9122833182082326]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.0752951231335759]
[null,null,null,null,null,"Coincident",4.0752951231335759]
[null,null,"Tea Tree Gully 11kV","Substation Rating","MVA","Non-Coincident",49.1]
[null,null,null,null,null,"Coincident",49.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",33.016000000000005]
[null,null,null,null,null,"Coincident",30.064]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",34.097604842569226]
[null,null,null,null,null,"Coincident",30.974764438168052]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.68345750666666627]
[null,null,null,null,null,"Coincident",1.2663373685614419]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",33.141953541898907]
[null,null,null,null,null,"Coincident",30.178691885257106]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",34.227684625104686]
[null,null,null,null,null,"Coincident",31.092930820845279]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.369756958655543]
[null,null,null,null,null,"Coincident",26.743771904683186]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",30.331910803808285]
[null,null,null,null,null,"Coincident",27.553952732026961]
[null,null,"Teal Flat 11kV","Substation Rating","MVA","Non-Coincident",3.9]
[null,null,null,null,null,"Coincident",3.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.3063354067981439]
[null,null,null,null,null,"Coincident",3.3063354067981439]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.4653537568734132]
[null,null,null,null,null,"Coincident",3.4653537568734132]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.2172414897883423E-2]
[null,null,null,null,null,"Coincident",6.2172414897883423E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.3063354067981439]
[null,null,null,null,null,"Coincident",3.3063354067981439]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.4653537568734132]
[null,null,null,null,null,"Coincident",3.4653537568734132]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.9757018661183294]
[null,null,null,null,null,"Coincident",2.9757018661183294]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.1188183811860721]
[null,null,null,null,null,"Coincident",3.1188183811860721]
[null,null,"Telowie 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.59499999999999997]
[null,null,null,null,null,"Coincident",0.46500000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.60367955075519997]
[null,null,null,null,null,"Coincident",0.47605566901361446]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.9394666666666671E-3]
[null,null,null,null,null,"Coincident",3.8124528783899034E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.64461122284561556]
[null,null,null,null,null,"Coincident",0.50377179600539712]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.65401447633479215]
[null,null,null,null,null,"Coincident",0.51574928898395578]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.57488006716689832]
[null,null,null,null,null,"Coincident",0.44927601887833235]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.583266118799046]
[null,null,null,null,null,"Coincident",0.4599578402987049]
[null,null,"Thebarton 11kV","Substation Rating","MVA","Non-Coincident",49]
[null,null,null,null,null,"Coincident",49]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",30.5642]
[null,null,null,null,null,"Coincident",26.930300000000003]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",30.824184444036796]
[null,null,null,null,null,"Coincident",26.993796291926042]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","16:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.3702771220315098]
[null,null,null,null,null,"Coincident",0.37549842064971994]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",32.188491028744451]
[null,null,null,null,null,"Coincident",28.361472570896563]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",32.462291977059522]
[null,null,null,null,null,"Coincident",28.428343283135714]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",29.711537946682171]
[null,null,null,null,null,"Coincident",26.179014348994411]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",29.964269497795772]
[null,null,null,null,null,"Coincident",26.240739258759238]
[null,null,"Tintinara 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1910959720844119]
[null,null,null,null,null,"Coincident",1.1910959720844119]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2260459712652925]
[null,null,null,null,null,"Coincident",1.2260459712652925]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.3682258551653729E-2]
[null,null,null,null,null,"Coincident",3.3682258551653729E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1910959720844119]
[null,null,null,null,null,"Coincident",1.1910959720844119]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.2260459712652925]
[null,null,null,null,null,"Coincident",1.2260459712652925]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0719863748759706]
[null,null,null,null,null,"Coincident",1.0719863748759706]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.1034413741387632]
[null,null,null,null,null,"Coincident",1.1034413741387632]
[null,null,"Tonsley Park 11kV","Substation Rating","MVA","Non-Coincident",40.1]
[null,null,null,null,null,"Coincident",40.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",21.068899999999999]
[null,null,null,null,null,"Coincident",14.643000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",22.324771534105338]
[null,null,null,null,null,"Coincident",15.202691715942937]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-28"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","14:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.571434]
[null,null,null,null,null,"Coincident",0.271750797264799]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",20.093002041829578]
[null,null,null,null,null,"Coincident",13.964745615504869]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.290702410574706]
[null,null,null,null,null,"Coincident",14.498512769520339]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.111831300921541]
[null,null,null,null,null,"Coincident",12.587821183801438]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",19.19143836922342]
[null,null,null,null,null,"Coincident",13.06895887678407]
[null,null,"Tumby Bay 11kV","Substation Rating","MVA","Non-Coincident",5.4]
[null,null,null,null,null,"Coincident",5.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.5243]
[null,null,null,null,null,"Coincident",1.1397999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.6941673028364113]
[null,null,null,null,null,"Coincident",1.2834500535665578]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","13:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1814932]
[null,null,null,null,null,"Coincident",0.18274041575125546]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2896491144631386]
[null,null,null,null,null,"Coincident",0.96433908066987162]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4333670287052296]
[null,null,null,null,null,"Coincident",1.0858756314634779]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1704770342180217]
[null,null,null,null,null,"Coincident",0.87522779216801228]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.3009144657174492]
[null,null,null,null,null,"Coincident",0.98553356443321249]
[null,null,"Two Wells 11kV","Substation Rating","MVA","Non-Coincident",16.600000000000001]
[null,null,null,null,null,"Coincident",16.600000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.2145999999999999]
[null,null,null,null,null,"Coincident",3.0952999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2574954750544167]
[null,null,null,null,null,"Coincident",3.135089552149986]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.3596613333333333E-2]
[null,null,null,null,null,"Coincident",0.15489114438948159]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.3128065727277156]
[null,null,null,null,null,"Coincident",3.1898619375860444]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.357012511787179]
[null,null,null,null,null,"Coincident",3.230867067271967]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.0056184377905075]
[null,null,null,null,null,"Coincident",2.8940741462368438]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.0457252724577564]
[null,null,null,null,null,"Coincident",2.9312769744498173]
[null,null,"Uley 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.29399726240597385]
[null,null,null,null,null,"Coincident",0.29399726240597385]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.30277778828620622]
[null,null,null,null,null,"Coincident",0.30277778828620622]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4699369822916634E-2]
[null,null,null,null,null,"Coincident",1.4699369822916634E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.29399726240597385]
[null,null,null,null,null,"Coincident",0.29399726240597385]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.30277778828620622]
[null,null,null,null,null,"Coincident",0.30277778828620622]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.26459753616537651]
[null,null,null,null,null,"Coincident",0.26459753616537651]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.27250000945758562]
[null,null,null,null,null,"Coincident",0.27250000945758562]
[null,null,"Uley South 11kV","Substation Rating","MVA","Non-Coincident",1.9500000000000002]
[null,null,null,null,null,"Coincident",1.9500000000000002]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.53594848138603768]
[null,null,null,null,null,"Coincident",1.1088589270055949E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.55252420761447185]
[null,null,null,null,null,"Coincident",1.1431535329954588E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-28"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.69392483432612195]
[null,null,null,null,null,"Coincident",1.4357065537781832E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.71538642714033196]
[null,null,null,null,null,"Coincident",1.480109849255859E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.63184034619486895]
[null,null,null,null,null,"Coincident",1.3072558886790389E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.65138180020089587]
[null,null,null,null,null,"Coincident",1.3476864831742669E-2]
[null,null,"Uraidla 11kV","Substation Rating","MVA","Non-Coincident",17.2]
[null,null,null,null,null,"Coincident",17.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3.8614999999999999]
[null,null,null,null,null,"Coincident",3.5545]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.0276232805464813]
[null,null,null,null,null,"Coincident",3.6546258919347681]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.14440860000000003]
[null,null,null,null,null,"Coincident",0.26756602237574173]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.0772698215520036]
[null,null,null,null,null,"Coincident",3.7531155200586812]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.2526756064618532]
[null,null,null,null,null,"Coincident",3.8588361668388464]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.6777440460411865]
[null,null,null,null,null,"Coincident",3.3853531559376919]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.8359620716630047]
[null,null,null,null,null,"Coincident",3.4807143893748687]
[null,null,"Uraidla 33kV","Substation Rating","MVA","Non-Coincident",31.4]
[null,null,null,null,null,"Coincident",31.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",15.67]
[null,null,null,null,null,"Coincident",15.36]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.182413293449159]
[null,null,null,null,null,"Coincident",15.742684015122707]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.1093999999999999]
[null,null,null,null,null,"Coincident",0.66924578786940603]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",15.049617206728433]
[null,null,null,null,null,"Coincident",14.751890254968011]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",15.541743812857906]
[null,null,null,null,null,"Coincident",15.119423626935506]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",13.461949026677324]
[null,null,null,null,null,"Coincident",13.195630954037249]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",13.902158448311301]
[null,null,null,null,null,"Coincident",13.524391177707072]
[null,null,"Verdun 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.1336050764843753]
[null,null,null,null,null,"Coincident",1.1336050764843753]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.1986705597428484]
[null,null,null,null,null,"Coincident",1.1986705597428484]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.1010559770174337E-2]
[null,null,null,null,null,"Coincident",8.1010559770174337E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.1336050764843753]
[null,null,null,null,null,"Coincident",1.1336050764843753]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.1986705597428484]
[null,null,null,null,null,"Coincident",1.1986705597428484]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0202445688359378]
[null,null,null,null,null,"Coincident",1.0202445688359378]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.0788035037685637]
[null,null,null,null,null,"Coincident",1.0788035037685637]
[null,null,"Victor Harbor 11kV","Substation Rating","MVA","Non-Coincident",62.7]
[null,null,null,null,null,"Coincident",62.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",24.25]
[null,null,null,null,null,"Coincident",22.78]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",24.321227353898077]
[null,null,null,null,null,"Coincident",22.822368413466645]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-07"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","17:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.2937153599999949]
[null,null,null,null,null,"Coincident",1.2770043163477844]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",18.823960826671208]
[null,null,null,null,null,"Coincident",17.682879489961653]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",18.879250761498625]
[null,null,null,null,null,"Coincident",17.71576779327647]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",16.9157158636555]
[null,null,null,null,null,"Coincident",15.890309582435972]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",16.965400881398178]
[null,null,null,null,null,"Coincident",15.919863893520327]
[null,null,"Virginia 11kV","Substation Rating","MVA","Non-Coincident",14.9]
[null,null,null,null,null,"Coincident",14.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.4989905041639959]
[null,null,null,null,null,"Coincident",5.2107834546795093]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.0587137248759317]
[null,null,null,null,null,"Coincident",5.7411710768216375]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-28"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.1737706666666655E-2]
[null,null,null,null,null,"Coincident",0.16997528730749109]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.9802070763899868]
[null,null,null,null,null,"Coincident",5.6667790325540333]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.5889116673120238]
[null,null,null,null,null,"Coincident",6.2435808671384381]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.4905169636957893]
[null,null,null,null,null,"Coincident",5.2027540201058624]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.0493776920360602]
[null,null,null,null,null,"Coincident",5.7323243538790338]
[null,null,"Waikerie 11kV","Substation Rating","MVA","Non-Coincident",12]
[null,null,null,null,null,"Coincident",12]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.4393000000000002]
[null,null,null,null,null,"Coincident",6.2534000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.4847072574683908]
[null,null,null,null,null,"Coincident",6.3681759177962407]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.47666560666666663]
[null,null,null,null,null,"Coincident",0.28754862942480774]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",7.8953634686718859]
[null,null,null,null,null,"Coincident",6.6367623183623152]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.9435544008601982]
[null,null,null,null,null,"Coincident",6.7585745303246947]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.1978101932579612]
[null,null,null,null,null,"Coincident",6.0504061218823457]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.2417434693261225]
[null,null,null,null,null,"Coincident",6.1614562571174245]
[null,null,"Walker Flat 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.7451217488787196]
[null,null,null,null,null,"Coincident",1.7451217488787196]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.8290534578688549]
[null,null,null,null,null,"Coincident",1.8290534578688549]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.0009534509594184E-2]
[null,null,null,null,null,"Coincident",3.0009534509594184E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.7451217488787196]
[null,null,null,null,null,"Coincident",1.7451217488787196]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.8290534578688549]
[null,null,null,null,null,"Coincident",1.8290534578688549]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.5706095739908477]
[null,null,null,null,null,"Coincident",1.5706095739908477]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.6461481120819694]
[null,null,null,null,null,"Coincident",1.6461481120819694]
[null,null,"Wallaroo 11kV","Substation Rating","MVA","Non-Coincident",16.2]
[null,null,null,null,null,"Coincident",16.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.603669847586894]
[null,null,null,null,null,"Coincident",7.0538066473631158]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",8.1322672166704741]
[null,null,null,null,null,"Coincident",7.5441782324739206]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.46599710569361957]
[null,null,null,null,null,"Coincident",0.33478078060248723]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",8.1195095352039921]
[null,null,null,null,null,"Coincident",7.5323431291439435]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.6839674173304715]
[null,null,null,null,null,"Coincident",8.0559819563036825]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",7.2124376998514688]
[null,null,null,null,null,"Coincident",6.6908666486946959]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",7.7138371121406077]
[null,null,null,null,null,"Coincident",7.1560071109034178]
[null,null,"Warooka 11kV","Substation Rating","MVA","Non-Coincident",5.4]
[null,null,null,null,null,"Coincident",5.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9650000000000001]
[null,null,null,null,null,"Coincident",1.141]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.029603163182399]
[null,null,null,null,null,"Coincident",1.1883202430321551]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","20:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0.10431172668208634]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.3806633625723614]
[null,null,null,null,null,"Coincident",0.80169816625703028]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.4260553322986831]
[null,null,null,null,null,"Coincident",0.83494667814635171]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.2503310523276623]
[null,null,null,null,null,"Coincident",0.72601920137702936]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.2914380960963872]
[null,null,null,null,null,"Coincident",0.75612910940084377]
[null,null,"Wasleys 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.2292615968925653]
[null,null,null,null,null,"Coincident",2.2292615968925653]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.3590528302148015]
[null,null,null,null,null,"Coincident",2.3590528302148015]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.2777798989011849E-2]
[null,null,null,null,null,"Coincident",7.2777798989011849E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.2292615968925653]
[null,null,null,null,null,"Coincident",2.2292615968925653]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.3590528302148015]
[null,null,null,null,null,"Coincident",2.3590528302148015]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.0063354372033086]
[null,null,null,null,null,"Coincident",2.0063354372033086]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.1231475471933212]
[null,null,null,null,null,"Coincident",2.1231475471933212]
[null,null,"Waterloo Town 11kV","Substation Rating","MVA","Non-Coincident",0.65]
[null,null,null,null,null,"Coincident",0.65]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.49780525850175583]
[null,null,null,null,null,"Coincident",0.31551037510674662]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.54109267228451718]
[null,null,null,null,null,"Coincident",0.34294605989863763]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.9680799999999998E-3]
[null,null,null,null,null,"Coincident",5.4099961828698957E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.59485844432777268]
[null,null,null,null,null,"Coincident",0.37702295767253197]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.64658526557366591]
[null,null,null,null,null,"Coincident",0.40980756268753471]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.52338309676298977]
[null,null,null,null,null,"Coincident",0.33172168104696531]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.5688946703945541]
[null,null,null,null,null,"Coincident",0.36056704461626665]
[null,null,"Whitmore Square 11kV","Substation Rating","MVA","Non-Coincident",72.400000000000006]
[null,null,null,null,null,"Coincident",72.400000000000006]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",38.965699999999998]
[null,null,null,null,null,"Coincident",25.621600000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",40.908222827812992]
[null,null,null,null,null,"Coincident",26.418407577293529]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","15:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.45405783253009357]
[null,null,null,null,null,"Coincident",9.6969910164258016E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",42.027101251630022]
[null,null,null,null,null,"Coincident",27.634601134555872]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",44.122241427941482]
[null,null,null,null,null,"Coincident",28.494011147181876]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",39.185487643288283]
[null,null,null,null,null,"Coincident",25.766119695046545]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",41.138967351495026]
[null,null,null,null,null,"Coincident",26.567421698452463]
[null,null,"Whyalla City 11kV","Substation Rating","MVA","Non-Coincident",28.5]
[null,null,null,null,null,"Coincident",28.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",17.752600000000001]
[null,null,null,null,null,"Coincident",17.6129]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",17.807615462211668]
[null,null,null,null,null,"Coincident",17.709322874124805]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.39118678666666673]
[null,null,null,null,null,"Coincident",0.72480650400563285]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",21.03724403219238]
[null,null,null,null,null,"Coincident",20.8716962819306]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",21.102438634903571]
[null,null,null,null,null,"Coincident",20.985959631144173]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",18.553433955524277]
[null,null,null,null,null,"Coincident",18.407431977020465]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",18.61093120914779]
[null,null,null,null,null,"Coincident",18.508204563958515]
[null,null,"Whyalla North 11kV","Substation Rating","MVA","Non-Coincident",2.9]
[null,null,null,null,null,"Coincident",2.9]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.0022682372772171]
[null,null,null,null,null,"Coincident",1.0022682372772171]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.0352680585628398]
[null,null,null,null,null,"Coincident",1.0352680585628398]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.6956990173708559E-3]
[null,null,null,null,null,"Coincident",8.6956990173708559E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0022682372772171]
[null,null,null,null,null,"Coincident",1.0022682372772171]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0352680585628398]
[null,null,null,null,null,"Coincident",1.0352680585628398]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.0049696512090374]
[null,null,null,null,null,"Coincident",1.0049696512090374]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.038058416924557]
[null,null,null,null,null,"Coincident",1.038058416924557]
[null,null,"Whyalla Stuart 11kV","Substation Rating","MVA","Non-Coincident",31]
[null,null,null,null,null,"Coincident",31]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",16.341200000000001]
[null,null,null,null,null,"Coincident",15.999499999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",16.643190338694083]
[null,null,null,null,null,"Coincident",16.352978173409269]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.31553974666666668]
[null,null,null,null,null,"Coincident",0.58464464662803461]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",19.481789407611409]
[null,null,null,null,null,"Coincident",19.074418624524437]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",19.841818792330486]
[null,null,null,null,null,"Coincident",19.49583120955776]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",17.063870846801713]
[null,null,null,null,null,"Coincident",16.707059555810098]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",17.379216362214152]
[null,null,null,null,null,"Coincident",17.076169896434969]
[null,null,"Williamstown 11kV","Substation Rating","MVA","Non-Coincident",3]
[null,null,null,null,null,"Coincident",3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.93395643645728998]
[null,null,null,null,null,"Coincident",0.69141736187342007]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.98311203837609473]
[null,null,null,null,null,"Coincident",0.72780774934044223]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.2466666666666666E-2]
[null,null,null,null,null,"Coincident",7.8683936299891399E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.0264627989922324]
[null,null,null,null,null,"Coincident",0.7599007542926991]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.0804871568339289]
[null,null,null,null,null,"Coincident",0.79989553083442011]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.89940303660504795]
[null,null,null,null,null,"Coincident",0.66583713175024861]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.94674003853162947]
[null,null,null,null,null,"Coincident",0.7008811913160512]
[null,null,"Williamstown South 11kV","Substation Rating","MVA","Non-Coincident",4.3]
[null,null,null,null,null,"Coincident",4.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.5591397091991674]
[null,null,null,null,null,"Coincident",2.5591397091991674]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.7816735969556166]
[null,null,null,null,null,"Coincident",2.7816735969556166]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",7.8683936299891399E-2]
[null,null,null,null,null,"Coincident",7.8683936299891399E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.6604524210435154]
[null,null,null,null,null,"Coincident",2.6604524210435154]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.8917961098299081]
[null,null,null,null,null,"Coincident",2.8917961098299081]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.3486155223063148]
[null,null,null,null,null,"Coincident",2.3486155223063148]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.5528429590286028]
[null,null,null,null,null,"Coincident",2.5528429590286028]
[null,null,"Willunga 11kV","Substation Rating","MVA","Non-Coincident",6.7]
[null,null,null,null,null,"Coincident",6.7]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.1338999999999997]
[null,null,null,null,null,"Coincident",3.9384000000000001]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.3599013131033129]
[null,null,null,null,null,"Coincident",4.1881355899731805]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",2.7083230769222609E-2]
[null,null,null,null,null,"Coincident",0.25029861639007039]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.7183448921119373]
[null,null,null,null,null,"Coincident",3.5424972841853104]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.9216277069328802]
[null,null,null,null,null,"Coincident",3.7671285174892937]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.3388244665328863]
[null,null,null,null,null,"Coincident",3.1809251019601636]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.5213588078710663]
[null,null,null,null,null,"Coincident",3.3826288920776024]
[null,null,"Willunga 33kV","Substation Rating","MVA","Non-Coincident",10.6]
[null,null,null,null,null,"Coincident",10.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.7909999999999999]
[null,null,null,null,null,"Coincident",2.7240000000000002]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.8810548571660344]
[null,null,null,null,null,"Coincident",2.8248857038825483]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.3587291007878985E-2]
[null,null,null,null,null,"Coincident",0.12557143454340447]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.6003623784463743]
[null,null,null,null,null,"Coincident",2.5379387742342976]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.6842660912987273]
[null,null,null,null,null,"Coincident",2.6319335391569987]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",2.2859498755115464]
[null,null,null,null,null,"Coincident",2.2310739738063248]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",2.3597087037193236]
[null,null,null,null,null,"Coincident",2.3137037345484264]
[null,null,"Wilmington 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.74252286918756449]
[null,null,null,null,null,"Coincident",0.74252286918756449]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.74627337125850468]
[null,null,null,null,null,"Coincident",0.74627337125850468]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.9549609266371392E-2]
[null,null,null,null,null,"Coincident",4.9549609266371392E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.74252286918756449]
[null,null,null,null,null,"Coincident",0.74252286918756449]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.74627337125850468]
[null,null,null,null,null,"Coincident",0.74627337125850468]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.66827058226880809]
[null,null,null,null,null,"Coincident",0.66827058226880809]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.67164603413265422]
[null,null,null,null,null,"Coincident",0.67164603413265422]
[null,null,"Wirrabara Forest 11kV","Substation Rating","MVA","Non-Coincident",1.3]
[null,null,null,null,null,"Coincident",1.3]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.46777842570174183]
[null,null,null,null,null,"Coincident",0.34374626737173447]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.50298755451800192]
[null,null,null,null,null,"Coincident",0.36961964233519834]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.6229599999999998E-3]
[null,null,null,null,null,"Coincident",1.0418444893018148E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.44817192587709809]
[null,null,null,null,null,"Coincident",0.32933846068241296]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.4819052966420409]
[null,null,null,null,null,"Coincident",0.3541273770778634]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.41621795263779288]
[null,null,null,null,null,"Coincident",0.30585713186262048]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.44754618563203535]
[null,null,null,null,null,"Coincident",0.32887863641141984]
[null,null,"Wirrabara South 11kV","Substation Rating","MVA","Non-Coincident",0.13]
[null,null,null,null,null,"Coincident",0.13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",4.9000000000000002E-2]
[null,null,null,null,null,"Coincident",4.9000000000000002E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",4.9247500257705398E-2]
[null,null,null,null,null,"Coincident",4.9247500257705398E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",3.1542747211209211E-4]
[null,null,null,null,null,"Coincident",3.1542747211209211E-4]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",4.9000000000000002E-2]
[null,null,null,null,null,"Coincident",4.9000000000000002E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",4.9247500257705398E-2]
[null,null,null,null,null,"Coincident",4.9247500257705398E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.9000000000000002E-2]
[null,null,null,null,null,"Coincident",4.9000000000000002E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",4.9247500257705398E-2]
[null,null,null,null,null,"Coincident",4.9247500257705398E-2]
[null,null,"Wirrina Cove 11kV","Substation Rating","MVA","Non-Coincident",1.95]
[null,null,null,null,null,"Coincident",1.95]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",0.68657530258220656]
[null,null,null,null,null,"Coincident",0.68657530258220656]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.69255353885799031]
[null,null,null,null,null,"Coincident",0.69255353885799031]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",5.5206724888741381E-3]
[null,null,null,null,null,"Coincident",5.5206724888741381E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.68657530258220656]
[null,null,null,null,null,"Coincident",0.68657530258220656]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.69255353885799031]
[null,null,null,null,null,"Coincident",0.69255353885799031]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.61791777232398581]
[null,null,null,null,null,"Coincident",0.61791777232398581]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.62329818497219125]
[null,null,null,null,null,"Coincident",0.62329818497219125]
[null,null,"Wongyarra 11kV","Substation Rating","MVA","Non-Coincident",0.26]
[null,null,null,null,null,"Coincident",0.26]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8000000000000004E-2]
[null,null,null,null,null,"Coincident",9.8000000000000004E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",9.8495000515410797E-2]
[null,null,null,null,null,"Coincident",9.8495000515410797E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.4208070783294675E-3]
[null,null,null,null,null,"Coincident",1.4208070783294675E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.8000000000000004E-2]
[null,null,null,null,null,"Coincident",9.8000000000000004E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",9.8495000515410797E-2]
[null,null,null,null,null,"Coincident",9.8495000515410797E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",8.8200000000000001E-2]
[null,null,null,null,null,"Coincident",8.8200000000000001E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.8645500463869722E-2]
[null,null,null,null,null,"Coincident",8.8645500463869722E-2]
[null,null,"Woodforde 11kV","Substation Rating","MVA","Non-Coincident",50.5]
[null,null,null,null,null,"Coincident",50.5]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",39.379000000000005]
[null,null,null,null,null,"Coincident",36.132400000000004]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",41.057218406146326]
[null,null,null,null,null,"Coincident",37.66515883425955]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-09"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.1219073216208483]
[null,null,null,null,null,"Coincident",1.1266467501430031]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",40.348902460371704]
[null,null,null,null,null,"Coincident",37.022338892788909]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",42.068455287431775]
[null,null,null,null,null,"Coincident",38.592849487238013]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",35.335288507203742]
[null,null,null,null,null,"Coincident",32.422072131280338]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",36.841175694772751]
[null,null,null,null,null,"Coincident",33.79743655446341]
[null,null,"Woods Point 11kV","Substation Rating","MVA","Non-Coincident",8.1]
[null,null,null,null,null,"Coincident",8.1]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",3]
[null,null,null,null,null,"Coincident",2.85]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",3.2057604402075959]
[null,null,null,null,null,"Coincident",3.0770277866798668]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.5153724999999996E-2]
[null,null,null,null,null,"Coincident",7.5076234587609342E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",3.2741901111742835]
[null,null,null,null,null,"Coincident",3.1104806056155696]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",3.4987563773738093]
[null,null,null,null,null,"Coincident",3.3582579836519044]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",3.0473531629566519]
[null,null,null,null,null,"Coincident",2.8949855048088193]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",3.2563614057159751]
[null,null,null,null,null,"Coincident",3.125596786081466]
[null,null,"Woodside 11kV","Substation Rating","MVA","Non-Coincident",13]
[null,null,null,null,null,"Coincident",13]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.5261999999999993]
[null,null,null,null,null,"Coincident",6.5261999999999993]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.8643459156717901]
[null,null,null,null,null,"Coincident",6.8643459156717901]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0.41697090769024742]
[null,null,null,null,null,"Coincident",0.41697090769024742]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.9969977411761981]
[null,null,null,null,null,"Coincident",6.9969977411761981]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",7.3595373826434338]
[null,null,null,null,null,"Coincident",7.3595373826434338]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.3302544833546612]
[null,null,null,null,null,"Coincident",6.3302544833546612]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",6.6582477564246592]
[null,null,null,null,null,"Coincident",6.6582477564246592]
[null,null,"Woodville 33kV","Substation Rating","MVA","Non-Coincident",37.89]
[null,null,null,null,null,"Coincident",37.89]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",6.0335999999999999]
[null,null,null,null,null,"Coincident",4.3588000000000005]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.7272903562633131]
[null,null,null,null,null,"Coincident",5.540910958497709]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-10"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","11:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",6.7707153589234066]
[null,null,null,null,null,"Coincident",4.8913076946558194]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",8.6713211843696527]
[null,null,null,null,null,"Coincident",6.2178352773016865]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",6.3580275455957649]
[null,null,null,null,null,"Coincident",4.5931733071040215]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",8.1427878775422062]
[null,null,null,null,null,"Coincident",5.8388465429961993]
[null,null,"Woolpunda 11kV","Substation Rating","MVA","Non-Coincident",18.8]
[null,null,null,null,null,"Coincident",18.8]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",5.9320000000000004]
[null,null,null,null,null,"Coincident",2.5811999999999999]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",6.3720917287810606]
[null,null,null,null,null,"Coincident",2.8180717254889025]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-03-04"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","06:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",8.4656E-4]
[null,null,null,null,null,"Coincident",2.1824675817124162E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.7730663656414594]
[null,null,null,null,null,"Coincident",2.5120429708350867]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",6.2013668978772891]
[null,null,null,null,null,"Coincident",2.7425682896805759]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",5.3545948566932129]
[null,null,null,null,null,"Coincident",2.3299528395307689]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.7518492240911039]
[null,null,null,null,null,"Coincident",2.5437680996452201]
[null,null,"Wudinna 11kV","Substation Rating","MVA","Non-Coincident",5.2]
[null,null,null,null,null,"Coincident",5.2]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",2.11]
[null,null,null,null,null,"Coincident",1.925]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",2.1120928009914715]
[null,null,null,null,null,"Coincident",1.9273922797396488]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",1.0423566436143302E-2]
[null,null,null,null,null,"Coincident",9.63328296778211E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",2.0137118818983843]
[null,null,null,null,null,"Coincident",1.837154205049474]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",2.0157091796343916]
[null,null,null,null,null,"Coincident",1.8394373150667989]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.833337441764741]
[null,null,null,null,null,"Coincident",1.6725945854962685]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.8351558353267443]
[null,null,null,null,null,"Coincident",1.6746731902440757]
[null,null,"Yankalilla 11kV","Substation Rating","MVA","Non-Coincident",16.600000000000001]
[null,null,null,null,null,"Coincident",16.600000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",7.1791]
[null,null,null,null,null,"Coincident",5.2531999999999996]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",7.4542282672319606]
[null,null,null,null,null,"Coincident",5.4524194996350017]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",9.5909558604575382E-2]
[null,null,null,null,null,"Coincident",0.30799763334464486]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",5.545883892033399]
[null,null,null,null,null,"Coincident",4.0581183242509296]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",5.7584215952949211]
[null,null,null,null,null,"Coincident",4.2120161964082632]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",4.9044137139387205]
[null,null,null,null,null,"Coincident",3.5887320307647035]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",5.0923680322940328]
[null,null,null,null,null,"Coincident",3.7248291524225596]
[null,null,"Yankalilla 33kV","Substation Rating","MVA","Non-Coincident",17.600000000000001]
[null,null,null,null,null,"Coincident",17.600000000000001]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.2763]
[null,null,null,null,null,"Coincident",0.77669999999999995]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.2856413885683675]
[null,null,null,null,null,"Coincident",0.78580874263398215]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-01-06"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",0.91644010231464335]
[null,null,null,null,null,"Coincident",0.55770510653277716]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.92314763431758595]
[null,null,null,null,null,"Coincident",0.5642455884190456]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",0.85099050113673602]
[null,null,null,null,null,"Coincident",0.51787536020755531]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.85721899987457828]
[null,null,null,null,null,"Coincident",0.52394873908306894]
[null,null,"Yankalilla Hill 11kV","Substation Rating","MVA","Non-Coincident",0.39]
[null,null,null,null,null,"Coincident",0.39]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.9589371527697443E-2]
[null,null,null,null,null,"Coincident",1.9589371527697443E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.9787243967371155E-2]
[null,null,null,null,null,"Coincident",1.9787243967371155E-2]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",0]
[null,null,null,null,null,"Coincident",0]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.9589371527697443E-2]
[null,null,null,null,null,"Coincident",1.9589371527697443E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.9787243967371155E-2]
[null,null,null,null,null,"Coincident",1.9787243967371155E-2]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.9589371527697443E-2]
[null,null,null,null,null,"Coincident",1.9589371527697443E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.9787243967371155E-2]
[null,null,null,null,null,"Coincident",1.9787243967371155E-2]
[null,null,"Yongala 11kV","Substation Rating","MVA","Non-Coincident",0.4]
[null,null,null,null,null,"Coincident",0.4]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",9.8261303821264398E-2]
[null,null,null,null,null,"Coincident",9.8261303821264398E-2]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",0.1]
[null,null,null,null,null,"Coincident",0.1]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","18:30:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",6.5762477573896054E-3]
[null,null,null,null,null,"Coincident",6.5762477573896054E-3]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",9.8261303821264398E-2]
[null,null,null,null,null,"Coincident",9.8261303821264398E-2]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",0.1]
[null,null,null,null,null,"Coincident",0.1]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",9.8261303821264398E-2]
[null,null,null,null,null,"Coincident",9.8261303821264398E-2]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",0.1]
[null,null,null,null,null,"Coincident",0.1]
[null,null,"Yorketown 11kV","Substation Rating","MVA","Non-Coincident",2.6]
[null,null,null,null,null,"Coincident",2.6]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident",1.4441839633509299]
[null,null,null,null,null,"Coincident",1.3781350925556364]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident",1.4441839633509299]
[null,null,null,null,null,"Coincident",1.3781350925556364]
[null,null,null,"Date MD occurred",null,"Non-Coincident","2017-02-08"]
[null,null,null,null,null,"Coincident","2017-02-08"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident","19:00:00"]
[null,null,null,null,null,"Coincident","18:30:00"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident","Summer"]
[null,null,null,null,null,"Coincident","Summer"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident",4.2456773333333343E-2]
[null,null,null,null,null,"Coincident",7.8665605536709454E-2]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident",1.2338829691997657]
[null,null,null,null,null,"Coincident",1.1774520858238746]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident",1.2338829691997657]
[null,null,null,null,null,"Coincident",1.1774520858238746]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident",1.1321325615810705]
[null,null,null,null,null,"Coincident",1.0803551709019008]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident",1.1321325615810705]
[null,null,null,null,null,"Coincident",1.0803551709019008]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,"<Enter substation name>","Substation Rating","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Raw Adjusted MD","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Date MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Half hour time period MD occurred",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Winter/Summer Peaking",null,"Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Adjustments - Embedded generation","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 10% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MW","Non-Coincident"]
[null,null,null,null,null,"Coincident"]
[null,null,null,"Weather Corrected MD 50% POE","MVA","Non-Coincident"]
[null,null,null,null,null,"Coincident"]

{"sheet":"6.3 Sustained interruptionss","index":24,"n_rows":60015,"n_cols":12,"rows_kept":4500,"cut":true,"hidden":false,"merged":[[7,1,7,4],[11,1,11,4],[11,10,11,11],[10,1,10,4],[10,10,10,11],[10,8,10,9],[11,8,11,9],[10,6,10,7]],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
[null,"REGULATORY REPORTING STATEMENT"]
[null,{"$f":"INDEX(dms_TradingNameFull_List,MATCH(dms_TradingName,dms_TradingName_List))","v":"SA Power Networks"}]
[null,{"$f":"CONCATENATE((LOOKUP(dms_Model,dms_Model_List,dms_Worksheet_List))&\" \"&CRY)","v":"CATEGORY ANALYSIS 2016-17"}]
[null,"6.3 SUSTAINED INTERRUPTIONS TO SUPPLY"]
[]
[null,"6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2015-16)"]
[]
[null,"There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data."]
[]
[null,"Definitions:"]
[null,"Feeder classification definitions\n(column E)",null,null,null,null,"Average duration of sustained customer interruption \n(column I)",null,"Effect on unplanned SAIDI \n(column J)",null,"Effect on unplanned SAIFI \n(column K)"]
[null,"CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas.\nUrban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km.\nShort rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km.\nLong rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km.\n",null,null,null,null,"The average duration of an  interruption experienced by an affected customer.",null,"The sum of the duration of each unplanned sustained customer\ninterruption (in minutes) divided by the total number of distribution\ncustomers. Unplanned SAIDI excludes momentary interruptions (one minute or less).",null,"The total number of unplanned sustained customer interruptions\ndivided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions."]
[]
[null,"Date of event\n(DD/MM/YYYY)","Time of interruption\n(HH:MM)","Asset ID\n(eg. feeder ID)","Feeder classification\n(CBD, Urban, Short rural, Long rural)","Reason for interruption\n(select from options in drop-down box)","Detailed reason for interruption\n(select from options in column 'O' that correspond with reason in column 'F')","Number of customers affected by the interruption","Average duration of sustained customer interruption\n(minutes)","Effect on unplanned SAIDI\n(by feeder classification)","Effect on unplanned SAIFI\n(by feeder classification)","MED"]
[null,"1/07/2016","04:26:00","EL01C","Urban","Unknown","Unknown",177.333156,1,2.92E-4,2.9158999999999999E-4]
[null,"1/07/2016","07:35:46","AP365A","Urban","Overloads",null,1,301,4.95E-4,1.64E-6]
[null,"1/07/2016","08:00:00","R06","Rural Long","Planned",null,36,385,9.8332000000000003E-2,2.5541000000000002E-4]
[null,"1/07/2016","08:20:00","HH177C","Urban","Planned",null,24,332,1.3102000000000001E-2,3.9459999999999998E-5]
[null,"1/07/2016","08:38:04","GU42","Rural Long","Planned",null,51,408,0.14762500000000001,3.6183E-4]
[null,"1/07/2016","08:38:31","AP214A","Urban","Planned",null,14,255,5.8700000000000002E-3,2.302E-5]
[null,"1/07/2016","08:45:00","LM11","Rural Long","Unknown","Unknown",44.333345999999999,67,2.1073000000000001E-2,3.1452999999999999E-4]
[null,"1/07/2016","08:47:06","ME131B","Urban","Planned",null,58,289,2.7562E-2,9.5370000000000003E-5]
[null,"1/07/2016","08:57:00","HH522A","Urban","Planned",null,40,103,6.7739999999999996E-3,6.5770000000000002E-5]
[null,"1/07/2016","09:28:00","AP529E","Urban","Planned",null,225,267,9.8780999999999994E-2,3.6997000000000001E-4]
[null,"1/07/2016","09:43:00","AP214A","Urban","Planned",null,72,152,1.7995000000000001E-2,1.1839E-4]
[null,"1/07/2016","09:50:00","AP529C","Urban","Planned",null,120,305,6.0180999999999998E-2,1.9731999999999999E-4]
[null,"1/07/2016","09:58:00","MV11","Rural Short","Planned",null,1,106,8.5599999999999999E-4,8.0700000000000007E-6]
[null,"1/07/2016","10:10:00","GA27","Rural Long","Planned",null,2,215,3.0509999999999999E-3,1.419E-5]
[null,"1/07/2016","10:46:00","M01","Rural Long","Planned",null,5,74,2.6250000000000002E-3,3.5469999999999998E-5]
[null,"1/07/2016","11:05:00","G29","Rural Long","Planned",null,12,187.00000000000003,1.592E-2,8.5140000000000001E-5]
[null,"1/07/2016","11:30:00","ST16","Rural Short","Planned",null,1,61.999999999999993,5.0000000000000001E-4,8.0700000000000007E-6]
[null,"1/07/2016","11:48:00","GA18","Rural Long","Planned",null,2,146,2.0720000000000001E-3,1.419E-5]
[null,"1/07/2016","13:23:00","W08","Rural Short","Unknown","Unknown",27.666677,74,1.6525000000000001E-2,2.2331E-4]
[null,"1/07/2016","15:45:26","AP227D","Urban","Overloads",null,1,93,1.5300000000000001E-4,1.64E-6]
[null,"1/07/2016","17:38:09","HH432C","Urban","Asset failure","LV",1,463.00000000000006,7.6099999999999996E-4,1.64E-6]
[null,"1/07/2016","18:26:00","ST36","Rural Long","Unknown","Unknown",12.666669000000001,262,2.3545E-2,8.9870000000000005E-5]
[null,"1/07/2016","20:48:00","HH341C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",265.00013200000001,77,3.3551999999999998E-2,4.3574E-4]
[null,"2/07/2016","08:18:00","HH432A","Urban","Planned",null,2,260,8.5499999999999997E-4,3.2899999999999998E-6]
[null,"2/07/2016","09:47:00","W01","Rural Long","Animal","Animal impact",18,108,1.3792E-2,1.2769999999999999E-4]
[null,"2/07/2016","09:52:00","NL760A","Urban","Unknown","Unknown",1,84.000000000000014,1.3799999999999999E-4,1.64E-6]
[null,"2/07/2016","14:19:00","NU13","Rural Long","Third Party","Other",14.000001000000001,78,7.7470000000000004E-3,9.9320000000000005E-5]
[null,"2/07/2016","15:33:00","VH31","Rural Short","Unknown","Unknown",207,31,5.1794E-2,1.6707899999999999E-3]
[null,"2/07/2016","18:30:41","AP139B","Urban","Third Party","Vehicle impact",1,113,1.8599999999999999E-4,1.64E-6]
[null,"2/07/2016","21:17:21","AP125D","Urban","Asset failure","LV",1,115,1.8900000000000001E-4,1.64E-6]
[null,"2/07/2016","22:18:53","ST12","Rural Short","Asset failure","LV",1,207,1.671E-3,8.0700000000000007E-6]
[null,"2/07/2016","23:57:10","NL111Q","Urban","Asset failure","LV",1,586,9.6400000000000001E-4,1.64E-6]
[null,"3/07/2016","00:50:00","MI06","Rural Long","Asset failure","Distribution substation",57,316.19298245614033,0.12786700000000001,4.0439000000000002E-4]
[null,"3/07/2016","07:51:00","SA41","Urban","Planned",null,1,456.00000000000006,7.5000000000000002E-4,1.64E-6]
[null,"3/07/2016","07:52:34","ME200F","Urban","Planned",null,97,427.99999999999994,6.8265000000000006E-2,1.595E-4]
[null,"3/07/2016","08:00:00","EL260C","Urban","Animal","Animal impact",68,100,1.1181E-2,1.1181E-4]
[null,"3/07/2016","08:06:58","SM374A","Urban","Planned",null,40,423,2.7820999999999999E-2,6.5770000000000002E-5]
[null,"3/07/2016","08:29:32","SM350B","Urban","Planned",null,68,295,3.2985E-2,1.1181E-4]
[null,"3/07/2016","08:49:00","AP425C","Urban","Planned",null,2,222,7.2999999999999996E-4,3.2899999999999998E-6]
[null,"3/07/2016","08:55:00","ME200F","Urban","Planned",null,30,335,1.6525000000000001E-2,4.9329999999999997E-5]
[null,"3/07/2016","09:57:00","NU04","Rural Short","Unknown","Unknown",6.6666699999999999,138,7.4260000000000003E-3,5.3810000000000001E-5]
[null,"3/07/2016","13:17:00","EL19","Urban","Unknown","Unknown",18.666668999999999,64,1.964E-3,3.0689999999999999E-5]
[null,"3/07/2016","14:50:00","GU41","Rural Long","Unknown","Unknown",6,70,2.98E-3,4.2570000000000001E-5]
[null,"3/07/2016","16:29:44","AP227A","Urban","Animal","Animal impact",0.99999899999999997,128,2.1000000000000001E-4,1.64E-6]
[null,"3/07/2016","16:37:37","AP226C","Urban","Asset failure","LV",1,222,3.6499999999999998E-4,1.64E-6]
[null,"3/07/2016","21:58:00","GA800A","Rural Short","Unknown","Unknown",27.666642,40.710843079546841,9.0910000000000001E-3,2.2331E-4]
[null,"3/07/2016","22:31:13","GA53","Rural Short","Third Party","Vehicle impact",1,171,1.3799999999999999E-3,8.0700000000000007E-6]
[null,"3/07/2016","23:22:06","SM349F","Urban","Asset failure","LV",21.666644999999999,110,3.9189999999999997E-3,3.5630000000000003E-5]
[null,"4/07/2016","01:55:00","EL11","Urban","Third Party","Vehicle impact",4,143.00000000000003,9.41E-4,6.5799999999999997E-6]
[null,"4/07/2016","03:41:00","SG04","Rural Short","Unknown","Unknown",37.000016000000002,253.00000000000003,7.5556999999999999E-2,2.9863999999999997E-4]
[null,"4/07/2016","04:50:00","SSD324","Rural Long","Planned",null,765,9,4.8847000000000002E-2,5.4273999999999998E-3]
[null,"4/07/2016","08:19:35","KA29","Rural Long","Planned",null,34,96,2.3157000000000001E-2,2.4122E-4]
[null,"4/07/2016","08:24:44","HH522B","Urban","Planned",null,41,397.99999999999994,2.6832000000000002E-2,6.7420000000000002E-5]
[null,"4/07/2016","08:27:27","NU01","Rural Short","Planned",null,6,135,6.5380000000000004E-3,4.8430000000000002E-5]
[null,"4/07/2016","08:34:03","AP424E","Urban","Planned",null,62,371,3.7822000000000001E-2,1.0195E-4]
[null,"4/07/2016","08:37:06","NL544A","Urban","Planned",null,96,255.00000000000003,4.0252000000000003E-2,1.5784999999999999E-4]
[null,"4/07/2016","08:56:00","GA27","Rural Long","Planned",null,19,351,4.7314000000000002E-2,1.348E-4]
[null,"4/07/2016","08:56:45","PA02","Urban","Planned",null,35,319,1.8359E-2,5.7550000000000003E-5]
[null,"4/07/2016","08:59:04","HH496C","Urban","Planned",null,41,276,1.8606999999999999E-2,6.7420000000000002E-5]
[null,"4/07/2016","09:22:00","MB63","Rural Long","Planned",null,3,326,6.9389999999999999E-3,2.128E-5]
[null,"4/07/2016","10:06:00","MG30","Rural Long","Planned",null,1,49,3.48E-4,7.0899999999999999E-6]
[null,"4/07/2016","10:06:00","CBD366Q","Urban","Planned",null,113,201,3.7346999999999998E-2,1.8581000000000001E-4]
[null,"4/07/2016","10:18:00","GA27","Rural Long","Planned",null,65,224,0.103298,4.6115000000000001E-4]
[null,"4/07/2016","10:25:43","HH177G","Urban","Planned",null,31,176.99999999999997,9.0220000000000005E-3,5.0970000000000002E-5]
[null,"4/07/2016","10:27:00","VH43","Rural Short","Planned",null,8,147,9.4920000000000004E-3,6.457E-5]
[null,"4/07/2016","10:34:00","LX34","Rural Short","Planned",null,5,101,4.0759999999999998E-3,4.036E-5]
[null,"4/07/2016","10:41:00","W25","Rural Long","Unknown","Unknown",2,79,1.121E-3,1.419E-5]
[null,"4/07/2016","10:47:21","ME347G","Urban","Planned",null,113,167,3.1029000000000001E-2,1.8581000000000001E-4]
[null,"4/07/2016","10:48:00","LM63","Rural Long","Planned",null,1,28,1.9900000000000001E-4,7.0899999999999999E-6]
[null,"4/07/2016","11:06:00","GA39","Rural Long","Unknown","Unknown",2,62,8.8000000000000003E-4,1.419E-5]
[null,"4/07/2016","11:11:00","W01","Rural Long","Unknown","Unknown",2,239,3.3909999999999999E-3,1.419E-5]
[null,"4/07/2016","11:14:27","GU21","Rural Long","Planned",null,10,195,1.3835E-2,7.0950000000000003E-5]
[null,"4/07/2016","11:34:44","AP132D","Urban","Third Party","Vehicle impact",49,448.00000000000006,3.6096000000000003E-2,8.0569999999999996E-5]
[null,"4/07/2016","11:54:00","ST35","Rural Long","Asset failure","HV",42.666678000000005,37.999999999999993,1.1502999999999999E-2,3.0269999999999999E-4]
[null,"4/07/2016","12:45:00","SM374A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2015,39,0.129217,3.3132499999999998E-3]
[null,"4/07/2016","13:35:00","MV11","Rural Short","Planned",null,1,73,5.8900000000000001E-4,8.0700000000000007E-6]
[null,"4/07/2016","15:12:00","SA18","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1298,48,0.102446,2.1342900000000001E-3]
[null,"4/07/2016","18:59:47","HH432B","Urban","Unknown","Unknown",30.333303000000001,214,1.0673999999999999E-2,4.9879999999999997E-5]
[null,"4/07/2016","20:23:00","BM56","Rural Short","Unknown","Unknown",209,249.60765550239236,0.42107099999999997,1.6869299999999999E-3]
[null,"4/07/2016","21:05:00","MB24","Rural Short","Unknown","Unknown",4.6666619999999996,40.000000000000007,1.5070000000000001E-3,3.7669999999999997E-5]
[null,"4/07/2016","21:24:00","MT18","Rural Long","Unknown","Unknown",0.99999899999999997,9,6.3999999999999997E-5,7.0899999999999999E-6]
[null,"4/07/2016","21:41:00","CBD353A","CBD","Planned",null,1,313,5.9151000000000002E-2,1.8898E-4]
[null,"5/07/2016","01:49:00","AP149A","Urban","Unknown","Unknown",758,158.00527704485486,0.196934,1.2463800000000001E-3]
[null,"5/07/2016","02:03:00","AP214D","Urban","Vegetation","Grow-in - NSP responsibility",1323,166.71579743008314,0.362674,2.1754000000000001E-3]
[null,"5/07/2016","02:38:00","SA42","Urban","Unknown","Unknown",1,1932,3.1770000000000001E-3,1.64E-6]
[null,"5/07/2016","02:52:00","EL19","Urban","Unknown","Unknown",173,175.121387283237,4.9815999999999999E-2,2.8446E-4]
[null,"5/07/2016","03:03:00","MTB14","Rural Short","Vegetation","Grow-in - NSP responsibility",216,130.55555555555554,0.22761500000000001,1.74343E-3]
[null,"5/07/2016","03:43:00","NL115E","Urban","Third Party","Other",2046,5.5000000000000009,1.8502999999999999E-2,3.3642300000000002E-3]
[null,"5/07/2016","04:05:00","AP424A","Urban","Vegetation","Grow-in - NSP responsibility",1838,228.11697497279653,0.68941799999999998,3.02221E-3]
[null,"5/07/2016","05:55:00","GU11","Rural Long","Asset failure","HV",29,678.99999999999989,0.13970099999999999,2.0573999999999999E-4]
[null,"5/07/2016","07:05:00","SM216E","Urban","Unknown","Unknown",81,10.000000000000002,1.3320000000000001E-3,1.3318999999999999E-4]
[null,"5/07/2016","08:09:11","HH428E","Urban","Planned",null,30,400,1.9732E-2,4.9329999999999997E-5]
[null,"5/07/2016","08:16:07","NL451A","Urban","Planned",null,36,38,2.2490000000000001E-3,5.9190000000000001E-5]
[null,"5/07/2016","08:30:00","MG46","Rural Short","Planned",null,119,295,0.28334799999999999,9.6049999999999998E-4]
[null,"5/07/2016","08:32:46","HH177F","Urban","Planned",null,70,203,2.3365E-2,1.1510000000000001E-4]
[null,"5/07/2016","08:37:30","BU01","Rural Long","Planned",null,53,321,0.120701,3.7602000000000002E-4]
[null,"5/07/2016","08:41:00","CD03","Rural Short","Planned",null,67,302,0.16331799999999999,5.4078999999999998E-4]
[null,"5/07/2016","08:41:35","VH31","Rural Short","Planned",null,41,230,7.6114000000000001E-2,3.3093E-4]
[null,"5/07/2016","08:42:36","VH31","Rural Short","Planned",null,56,230,0.10396,4.5199999999999998E-4]
[null,"5/07/2016","08:44:50","MV34","Rural Short","Planned",null,48,382,0.14799799999999999,3.8743000000000002E-4]
[null,"5/07/2016","08:47:11","SA711C","Urban","Planned",null,46,246.00000000000003,1.8606999999999999E-2,7.5640000000000001E-5]
[null,"5/07/2016","09:06:44","KI11","Rural Long","Planned",null,28,283,5.6217999999999997E-2,1.9865E-4]
[null,"5/07/2016","09:17:00","NL234A","Urban","Planned",null,195,320,0.102604,3.2064000000000002E-4]
[null,"5/07/2016","09:24:58","AP529C","Urban","Planned",null,58,184,1.7548000000000001E-2,9.5370000000000003E-5]
[null,"5/07/2016","09:43:00","NU25","Rural Long","Planned",null,55,183.99999999999997,7.1798000000000001E-2,3.9020999999999999E-4]
[null,"5/07/2016","09:54:00","AP529A","Urban","Unknown","Unknown",542.66693799999996,51.999999999999986,4.6399999999999997E-2,8.9229999999999995E-4]
[null,"5/07/2016","11:07:00","SD391","Rural Long","Unknown","Unknown",1967,120,1.6746190000000001,1.3955149999999999E-2]
[null,"5/07/2016","11:09:00","NA32","Rural Long","Unknown","Unknown",12.666672000000002,235.99999999999991,2.1208000000000001E-2,8.9870000000000005E-5]
[null,"5/07/2016","11:54:00","CM20","Rural Long","Unknown","Unknown",15,136,1.4473E-2,1.0642E-4]
[null,"5/07/2016","12:36:00","HH177E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",253,5,2.0799999999999998E-3,4.1601000000000002E-4]
[null,"5/07/2016","12:52:00","EL09","Urban","Planned",null,2430,4.2279835390946507,1.6892999999999998E-2,3.99564E-3]
[null,"5/07/2016","13:50:00","SG02","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",101,474.21782178217825,0.38658999999999999,8.1521999999999996E-4]
[null,"5/07/2016","15:33:51","AP529C","Urban","Asset failure","LV",1,306.00000000000006,5.0299999999999997E-4,1.64E-6]
[null,"5/07/2016","16:03:49","HH130E","Urban","Asset failure","LV",1,747.00000000000011,1.2279999999999999E-3,1.64E-6]
[null,"5/07/2016","17:29:27","AP424B","Urban","Third Party","Vehicle impact",64,680,7.1559999999999999E-2,1.0522999999999999E-4]
[null,"5/07/2016","17:47:08","AP125D","Urban","Asset failure","LV",1,205.00000000000003,3.3700000000000001E-4,1.64E-6]
[null,"5/07/2016","19:02:00","AP424B","Urban","Third Party","Vehicle impact",64,500,5.2616999999999997E-2,1.0522999999999999E-4]
[null,"5/07/2016","19:57:38","G41","Rural Long","Asset failure","LV",1,149,1.057E-3,7.0899999999999999E-6]
[null,"5/07/2016","21:36:59","SM137C","Urban","Planned",null,28,37,1.7030000000000001E-3,4.604E-5]
[null,"5/07/2016","21:57:28","HH121C","Urban","Asset failure","LV",6.9999929999999999,327.00000000000006,3.764E-3,1.151E-5]
[null,"5/07/2016","23:00:29","NL451C","Urban","Asset failure","LV",1,122.00000000000001,2.0100000000000001E-4,1.64E-6]
[null,"5/07/2016","23:46:52","AP226D","Urban","Overloads",null,1,100,1.64E-4,1.64E-6]
[null,"6/07/2016","01:16:05","AP149C","Urban","Asset failure","LV",55,92,8.3199999999999993E-3,9.0439999999999995E-5]
[null,"6/07/2016","01:34:47","HH177F","Urban","Unknown","Unknown",14.666651999999999,121.00000000000001,2.918E-3,2.4119999999999999E-5]
[null,"6/07/2016","06:59:23","NU06","Rural Long","Planned",null,17,173,2.0865000000000002E-2,1.2061E-4]
[null,"6/07/2016","08:20:21","PA04","Urban","Planned",null,18,79.999999999999986,2.3679999999999999E-3,2.9600000000000001E-5]
[null,"6/07/2016","08:37:00","NU06","Rural Long","Planned",null,22,264,4.1206E-2,1.5608000000000001E-4]
[null,"6/07/2016","08:51:43","CV01","Rural Short","Planned",null,27,400,8.7171999999999999E-2,2.1793E-4]
[null,"6/07/2016","08:56:00","BM51","Urban","Planned",null,35,160,9.2079999999999992E-3,5.7550000000000003E-5]
[null,"6/07/2016","08:58:00","LX44","Urban","Planned",null,4,257,1.6900000000000001E-3,6.5799999999999997E-6]
[null,"6/07/2016","09:43:00","SM402E","Urban","Planned",null,121,138,2.7456000000000001E-2,1.9896000000000001E-4]
[null,"6/07/2016","09:45:20","SM349D","Urban","Planned",null,39,200,1.2825E-2,6.4129999999999998E-5]
[null,"6/07/2016","09:50:00","SM402E","Urban","Network business","Switching and protection error",337,5,2.771E-3,5.5413000000000001E-4]
[null,"6/07/2016","09:50:00","GA25","Rural Short","Planned",null,3,310,7.5059999999999997E-3,2.421E-5]
[null,"6/07/2016","10:22:00","EL12","Urban","Planned",null,28,175.99999999999997,8.1030000000000008E-3,4.604E-5]
[null,"6/07/2016","10:32:00","VH31","Rural Short","Planned",null,85,250.00000000000003,0.171518,6.8607E-4]
[null,"6/07/2016","10:40:02","ME347A","Urban","Planned",null,52,171,1.4621E-2,8.5500000000000005E-5]
[null,"6/07/2016","10:40:27","ME347C","Urban","Planned",null,96,170.00000000000003,2.6835000000000001E-2,1.5784999999999999E-4]
[null,"6/07/2016","10:45:00","SB17","Rural Long","Unknown","Unknown",9,5,3.19E-4,6.3849999999999993E-5]
[null,"6/07/2016","11:10:00","M13","Rural Long","Planned",null,3,13,2.7700000000000001E-4,2.128E-5]
[null,"6/07/2016","11:29:00","LM33","Rural Long","Planned",null,69,6,2.9369999999999999E-3,4.8952999999999996E-4]
[null,"6/07/2016","12:00:00","GA21","Rural Long","Unknown","Unknown",3,10,2.13E-4,2.128E-5]
[null,"6/07/2016","12:17:00","GA29","Rural Long","Planned",null,7,143,7.1019999999999998E-3,4.9660000000000002E-5]
[null,"6/07/2016","13:48:18","AP372F","Urban","Asset failure","LV",1,263,4.3199999999999998E-4,1.64E-6]
[null,"6/07/2016","13:51:00","EL16","Urban","Asset failure","HV",255,21,8.8050000000000003E-3,4.193E-4]
[null,"6/07/2016","13:51:00","GA800A","Rural Short","Asset failure","HV",2343,23.598804950917625,0.44628699999999999,1.8911399999999998E-2]
[null,"6/07/2016","13:52:00","NL451D","Urban","Unknown","Unknown",2,1425,4.6860000000000001E-3,3.2899999999999998E-6]
[null,"6/07/2016","14:18:25","AP214B","Urban","Asset failure","LV",28.000014,142,6.5380000000000004E-3,4.604E-5]
[null,"6/07/2016","14:20:38","AP424B","Urban","Asset failure","LV",0.99999899999999997,449.99999999999994,7.3999999999999999E-4,1.64E-6]
[null,"6/07/2016","16:24:00","AP149H","Urban","Asset failure","Distribution substation",48,281,2.2178E-2,7.8930000000000005E-5]
[null,"6/07/2016","17:13:00","PA06","Rural Long","Asset failure","HV",921,303.3376764386536,1.9820580000000001,6.5341599999999998E-3]
[null,"6/07/2016","17:13:00","PA06","Rural Long","Asset failure","HV",737,1,5.2290000000000001E-3,5.2287499999999999E-3]
[null,"6/07/2016","21:13:24","NL451A","Urban","Asset failure","LV",1,259,4.26E-4,1.64E-6]
[null,"6/07/2016","22:44:03","SG13","Rural Short","Asset failure","LV",1,276,2.2279999999999999E-3,8.0700000000000007E-6]
[null,"6/07/2016","23:10:33","NL210D","Urban","Asset failure","LV",1,105.00000000000001,1.73E-4,1.64E-6]
[null,"7/07/2016","07:09:00","MT06","Rural Long","Unknown","Unknown",20,77.999999999999986,1.1068E-2,1.4189000000000001E-4]
[null,"7/07/2016","07:32:00","CN01","Rural Long","Unknown","Unknown",33,124.00000000000001,2.9031000000000001E-2,2.3411999999999999E-4]
[null,"7/07/2016","08:28:19","HH177A","Urban","Planned",null,77,260.00000000000006,3.2918999999999997E-2,1.2661000000000001E-4]
[null,"7/07/2016","08:33:46","SA744D","Urban","Planned",null,16,137,3.604E-3,2.6310000000000001E-5]
[null,"7/07/2016","08:39:07","WK41","Rural Short","Planned",null,43,188,6.5250000000000002E-2,3.4707E-4]
[null,"7/07/2016","08:39:29","ST21","Rural Short","Planned",null,38,330,0.101216,3.0672000000000002E-4]
[null,"7/07/2016","08:52:00","GA27","Rural Long","Planned",null,90,292.73333333333335,0.186915,6.3851999999999995E-4]
[null,"7/07/2016","08:54:00","CD03","Rural Short","Planned",null,8,259,1.6723999999999999E-2,6.457E-5]
[null,"7/07/2016","08:57:00","HH121A","Urban","Planned",null,57,297,2.7836E-2,9.3720000000000004E-5]
[null,"7/07/2016","09:00:00","BM12","Rural Short","Planned",null,6,305,1.4770999999999999E-2,4.8430000000000002E-5]
[null,"7/07/2016","09:00:51","AP529C","Urban","Planned",null,56,286,2.6335000000000001E-2,9.2079999999999999E-5]
[null,"7/07/2016","09:04:54","YK02","Rural Short","Planned",null,27,139,3.0291999999999999E-2,2.1793E-4]
[null,"7/07/2016","09:05:32","AP424A","Urban","Planned",null,40,207.99999999999997,1.3681E-2,6.5770000000000002E-5]
[null,"7/07/2016","09:06:00","SA744G","Urban","Planned",null,1,309,5.0799999999999999E-4,1.64E-6]
[null,"7/07/2016","09:08:55","AP424F","Urban","Planned",null,38,384,2.3994000000000001E-2,6.2479999999999998E-5]
[null,"7/07/2016","09:11:11","VH12","Rural Short","Planned",null,55,374.00000000000006,0.16603000000000001,4.4392999999999999E-4]
[null,"7/07/2016","09:18:00","GU32","Rural Long","Planned",null,6,140,5.9589999999999999E-3,4.2570000000000001E-5]
[null,"7/07/2016","09:31:00","PP13","Rural Long","Planned",null,69,2,9.7900000000000005E-4,4.8952999999999996E-4]
[null,"7/07/2016","09:33:08","LX43","Rural Short","Planned",null,21,350,5.9325000000000003E-2,1.695E-4]
[null,"7/07/2016","09:37:00","SM410B","Urban","Planned",null,109,278,4.9825000000000001E-2,1.7923E-4]
[null,"7/07/2016","09:50:00","MV64","Rural Short","Planned",null,151,230,0.28032099999999999,1.21879E-3]
[null,"7/07/2016","09:56:00","AP424C","Urban","Planned",null,150,41.400000000000006,1.0211E-2,2.4664000000000001E-4]
[null,"7/07/2016","10:34:52","SM349E","Urban","Planned",null,106,264,4.6013999999999999E-2,1.7430000000000001E-4]
[null,"7/07/2016","10:41:00","CL13","Rural Long","Planned",null,1,65,4.6099999999999998E-4,7.0899999999999999E-6]
[null,"7/07/2016","10:48:51","CV01","Rural Short","Planned",null,27,281,6.1238000000000001E-2,2.1793E-4]
[null,"7/07/2016","10:53:54","SA744D","Urban","Planned",null,57,210,1.9682000000000002E-2,9.3720000000000004E-5]
[null,"7/07/2016","10:55:38","SA711C","Urban","Planned",null,41,214,1.4427000000000001E-2,6.7420000000000002E-5]
[null,"7/07/2016","11:06:08","PA04","Urban","Planned",null,48,226,1.7836999999999999E-2,7.8930000000000005E-5]
[null,"7/07/2016","11:11:00","ST21","Rural Short","Planned",null,122,83,8.1730999999999998E-2,9.8471999999999991E-4]
[null,"7/07/2016","12:42:00","GU11","Rural Long","Unknown","Unknown",25.666669999999996,157.00000000000003,2.8589E-2,1.8210000000000001E-4]
[null,"7/07/2016","13:01:00","EL16","Urban","Animal","Animal impact",255,58,2.4319E-2,4.193E-4]
[null,"7/07/2016","13:01:00","GA800A","Rural Short","Animal","Animal impact",2343,66.108834827144676,1.250211,1.8911399999999998E-2]
[null,"7/07/2016","14:06:00","W16","Rural Long","Unknown","Unknown",3,109,2.32E-3,2.128E-5]
[null,"7/07/2016","14:13:00","KA04","Rural Long","Unknown","Unknown",186,95,0.125362,1.3196E-3]
[null,"7/07/2016","16:26:43","ME231E","Urban","Weather",null,2,348,1.1440000000000001E-3,3.2899999999999998E-6]
[null,"7/07/2016","16:46:54","PP14","Rural Long","Overloads",null,1,348,2.4689999999999998E-3,7.0899999999999999E-6]
[null,"7/07/2016","17:53:00","AP355H","Urban","Unknown","Unknown",2576,97.259704968944092,0.41196300000000002,4.2357000000000002E-3]
[null,"7/07/2016","18:16:30","HH496G","Urban","Asset failure","LV",26,526,2.2487E-2,4.2750000000000002E-5]
[null,"7/07/2016","19:45:31","HH496A","Urban","Asset failure","LV",1,416,6.8400000000000004E-4,1.64E-6]
[null,"7/07/2016","23:19:03","HH121E","Urban","Asset failure","LV",1,681,1.1199999999999999E-3,1.64E-6]
[null,"8/07/2016","07:39:00","SM402D","Urban","Asset failure","HV",31,286,1.4578000000000001E-2,5.0970000000000002E-5]
[null,"8/07/2016","08:11:57","SA520A","Urban","Planned",null,20,44,1.4469999999999999E-3,3.2889999999999999E-5]
[null,"8/07/2016","08:15:14","YK04","Rural Short","Planned",null,3,405,9.8069999999999997E-3,2.421E-5]
[null,"8/07/2016","08:16:00","VH15","Rural Short","Planned",null,98,401.00000000000006,0.31719199999999997,7.9100000000000004E-4]
[null,"8/07/2016","08:26:51","ME131C","Urban","Planned",null,82,333,4.4899000000000001E-2,1.3483000000000001E-4]
[null,"8/07/2016","08:31:40","HH496A","Urban","Planned",null,36,231,1.3674E-2,5.9190000000000001E-5]
[null,"8/07/2016","08:34:25","NA13","Rural Long","Planned",null,20,158,2.2419000000000001E-2,1.4189000000000001E-4]
[null,"8/07/2016","08:35:05","NU25","Rural Long","Planned",null,8,143,8.116E-3,5.6759999999999999E-5]
[null,"8/07/2016","08:35:21","NU25","Rural Long","Planned",null,2,142,2.0149999999999999E-3,1.419E-5]
[null,"8/07/2016","08:35:40","NU25","Rural Long","Planned",null,1,141,1E-3,7.0899999999999999E-6]
[null,"8/07/2016","08:35:54","NU25","Rural Long","Planned",null,15,141,1.5004999999999999E-2,1.0642E-4]
[null,"8/07/2016","08:36:25","NU25","Rural Long","Planned",null,38,140,3.7742999999999999E-2,2.6959999999999999E-4]
[null,"8/07/2016","08:36:49","NU25","Rural Long","Planned",null,6,141,6.0020000000000004E-3,4.2570000000000001E-5]
[null,"8/07/2016","08:37:06","NU25","Rural Long","Planned",null,4,140,3.973E-3,2.8379999999999999E-5]
[null,"8/07/2016","08:37:51","NU25","Rural Long","Planned",null,3,138,2.9369999999999999E-3,2.128E-5]
[null,"8/07/2016","08:48:00","SA31","Urban","Planned",null,139,57.208633093525172,1.3075E-2,2.2855999999999999E-4]
[null,"8/07/2016","09:05:12","MV62","Rural Short","Planned",null,35,263,7.4298000000000003E-2,2.8249999999999998E-4]
[null,"8/07/2016","09:17:00","EL01C","Urban","Planned",null,217,184.42857142857142,6.5806000000000003E-2,3.5680999999999999E-4]
[null,"8/07/2016","09:18:00","MG16","Rural Long","Weather",null,67,33,1.5685999999999999E-2,4.7533999999999999E-4]
[null,"8/07/2016","09:18:00","G06","Rural Long","Planned",null,43,116,3.5388000000000003E-2,3.0507E-4]
[null,"8/07/2016","09:25:00","SM179D","Urban","Planned",null,55,297,2.6859999999999998E-2,9.0439999999999995E-5]
[null,"8/07/2016","09:35:00","PL803C","Urban","Planned",null,70,253.00000000000003,2.912E-2,1.1510000000000001E-4]
[null,"8/07/2016","09:37:00","ME131C","Urban","Planned",null,47,214,1.6538000000000001E-2,7.7280000000000005E-5]
[null,"8/07/2016","09:44:00","NL451C","Urban","Unknown","Unknown",1604.3341340000002,4.2000831112404668,1.108E-2,2.6380000000000002E-3]
[null,"8/07/2016","10:04:00","NU07","Rural Long","Planned",null,1,42,2.9799999999999998E-4,7.0899999999999999E-6]
[null,"8/07/2016","11:25:00","LM43","Rural Long","Unknown","Unknown",1,41,2.9100000000000003E-4,7.0899999999999999E-6]
[null,"8/07/2016","11:40:00","SD382","Rural Long","Planned",null,4,107,3.0370000000000002E-3,2.8379999999999999E-5]
[null,"8/07/2016","12:35:00","SM402C","Urban","Asset failure","HV",13,30.000000000000004,6.4099999999999997E-4,2.1379999999999999E-5]
[null,"8/07/2016","15:26:00","PL34","Rural Long","Unknown","Unknown",2,69,9.7900000000000005E-4,1.419E-5]
[null,"8/07/2016","20:20:02","NL111Q","Urban","Asset failure","LV",1,233.00000000000003,3.8299999999999999E-4,1.64E-6]
[null,"8/07/2016","21:15:15","AP227C","Urban","Asset failure","LV",1,220.00000000000003,3.6200000000000002E-4,1.64E-6]
[null,"8/07/2016","21:59:39","VH21","Rural Short","Unknown","Unknown",45.333288000000003,145,5.3055999999999999E-2,3.6591E-4]
[null,"8/07/2016","22:24:57","SA16","Urban","Overloads",null,1,201,3.3100000000000002E-4,1.64E-6]
[null,"9/07/2016","19:10:00","VH22","Rural Short","Unknown","Unknown",1,30,2.42E-4,8.0700000000000007E-6]
[null,"9/07/2016","19:31:43","PL06","Urban","Unknown","Unknown",19.333314000000001,302,9.5999999999999992E-3,3.1789999999999999E-5]
[null,"9/07/2016","19:33:00","NL511B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1640,91,0.245395,2.6966400000000001E-3]
[null,"9/07/2016","20:45:00","KA30","Rural Short","Weather",null,65,967,0.50733099999999998,5.2464000000000005E-4]
[null,"9/07/2016","20:50:00","VH44","Rural Short","Unknown","Unknown",1,30,2.42E-4,8.0700000000000007E-6]
[null,"9/07/2016","21:45:34","NL760B","Urban","Asset failure","LV",12.666653999999999,310.00000000000006,6.4570000000000001E-3,2.0829999999999999E-5]
[null,"9/07/2016","22:34:45","HH341C","Urban","Vegetation","Grow-in - NSP responsibility",19.666647000000001,284,9.1839999999999995E-3,3.2339999999999999E-5]
[null,"9/07/2016","23:50:55","HH102A","Urban","Asset failure","LV",87,299,4.2772999999999999E-2,1.4305000000000001E-4]
[null,"10/07/2016","00:49:00","SA711C","Urban","Vegetation","Grow-in - NSP responsibility",2954,108.69194312796208,0.52794399999999997,4.8572499999999996E-3]
[null,"10/07/2016","01:00:00","HH130B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",206,372,0.12600600000000001,3.3871999999999998E-4]
[null,"10/07/2016","01:13:00","CV31","Rural Long","Asset failure","HV",60,929.4666666666667,0.39565400000000001,4.2568E-4]
[null,"10/07/2016","03:30:00","ME347F","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",801,128,0.16858600000000001,1.31708E-3]
[null,"10/07/2016","05:40:00","HH177D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1059,46,8.0100000000000005E-2,1.74131E-3]
[null,"10/07/2016","08:25:00","HH130B","Urban","Unknown","Unknown",206,409,0.13853799999999999,3.3871999999999998E-4]
[null,"10/07/2016","08:31:00","MV12","Urban","Asset failure","HV",119,223.21008403361344,4.3676E-2,1.9567E-4]
[null,"10/07/2016","08:31:17","SM172C","Urban","Planned",null,26,56,2.3939999999999999E-3,4.2750000000000002E-5]
[null,"10/07/2016","08:33:48","AP132A","Urban","Planned",null,12,236,4.6569999999999997E-3,1.9729999999999999E-5]
[null,"10/07/2016","08:37:02","AP132A","Urban","Planned",null,109,233,4.1759999999999999E-2,1.7923E-4]
[null,"10/07/2016","08:37:51","AP132A","Urban","Planned",null,18,234,6.9259999999999999E-3,2.9600000000000001E-5]
[null,"10/07/2016","08:52:00","ME200F","Urban","Planned",null,34,346,1.9342999999999999E-2,5.5909999999999998E-5]
[null,"10/07/2016","08:58:00","BU03","Rural Long","Asset failure","HV",48,261,8.8882000000000003E-2,3.4054000000000002E-4]
[null,"10/07/2016","12:54:00","EL01N","Urban","Unknown","Unknown",318.99968399999995,2.2988505624977362,1.206E-3,5.2453000000000005E-4]
[null,"10/07/2016","13:39:35","BM43","Rural Short","Overloads",null,1,105,8.4800000000000001E-4,8.0700000000000007E-6]
[null,"10/07/2016","13:50:44","NL210E","Urban","Asset failure","LV",60,455,4.4888999999999998E-2,9.8659999999999994E-5]
[null,"10/07/2016","13:56:00","CM03","Rural Long","Unknown","Unknown",232,328.99999999999994,0.54152,1.6459599999999999E-3]
[null,"10/07/2016","14:02:00","SD48103","Rural Short","Asset failure","Subtransmission",628,235.00000000000003,1.191184,5.0688699999999996E-3]
[null,"10/07/2016","17:48:16","SM349D","Urban","Asset failure","LV",1,123,2.02E-4,1.64E-6]
[null,"10/07/2016","19:14:00","R27","Rural Long","Asset failure","HV",30,807.9,0.17195299999999999,2.1284E-4]
[null,"10/07/2016","19:14:00","R27","Rural Long","Asset failure","HV",339,4,9.6200000000000001E-3,2.40508E-3]
[null,"10/07/2016","19:31:00","MG17","Rural Long","Unknown","Unknown",81,19.000000000000004,1.0919E-2,5.7467E-4]
[null,"10/07/2016","21:01:00","SSD443","Rural Short","Asset failure","Zone substation",19,135,2.0702999999999999E-2,1.5336000000000001E-4]
[null,"10/07/2016","22:46:06","HH145B","Urban","Asset failure","LV",1,309,5.0799999999999999E-4,1.64E-6]
[null,"10/07/2016","22:53:00","KI31","Rural Short","Asset failure","HV",48.000006999999997,189.00000000000006,7.3223999999999997E-2,3.8743000000000002E-4]
[null,"10/07/2016","23:14:27","SG01","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,137,1.106E-3,8.0700000000000007E-6]
[null,"11/07/2016","01:17:00","MTB14","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",216,497.72222222222223,0.86774499999999999,1.74343E-3,"MED"]
[null,"11/07/2016","03:16:00","MTB52","Rural Long","Asset failure","HV",959,193.12095933263817,1.3139479999999999,6.8037599999999998E-3,"MED"]
[null,"11/07/2016","03:28:00","SD412","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1128,868.47163120567382,7.9070809999999998,9.1045899999999992E-3,"MED"]
[null,"11/07/2016","03:51:00","MTB54","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",242,1244.5206611570247,2.1367210000000001,1.7168999999999999E-3,"MED"]
[null,"11/07/2016","04:16:00","MTB14","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",196,1101.5051020408164,1.7425850000000001,1.5820000000000001E-3,"MED"]
[null,"11/07/2016","04:16:00","MTB14","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",null,296,0.68329700000000004,0,"MED"]
[null,"11/07/2016","04:16:00","MTB32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",567,164,0.65971599999999997,4.02266E-3,"MED"]
[null,"11/07/2016","04:16:00","MTB32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",null,239.84732824427482,2.229136,0,"MED"]
[null,"11/07/2016","04:19:00","ST11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",260,2105.0000000000005,4.4175040000000001,2.0985800000000001E-3,"MED"]
[null,"11/07/2016","04:20:00","MV42","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",144,663.34027777777783,0.77099300000000004,1.1622900000000001E-3,"MED"]
[null,"11/07/2016","04:49:00","ST36","Rural Long","Vegetation","Grow-in - NSP responsibility",116,2047,1.684636,8.2297999999999996E-4,"MED"]
[null,"11/07/2016","04:57:00","GU32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1177,602.20475785896349,5.028645,8.3503899999999992E-3,"MED"]
[null,"11/07/2016","05:12:00","ST34","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",536,1844.9999999999998,7.0160299999999998,3.8027299999999998E-3,"MED"]
[null,"11/07/2016","05:34:00","MTB10","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",689,477.94484760522494,0.54147299999999998,1.1329199999999999E-3,"MED"]
[null,"11/07/2016","05:39:00","MTB13","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",109,2385.7431192660551,2.098948,8.7978999999999998E-4,"MED"]
[null,"11/07/2016","05:39:00","MTB13","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",null,2,6.9399999999999996E-4,0,"MED"]
[null,"11/07/2016","05:39:00","MTB13","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",null,11.8,1.5715E-2,0,"MED"]
[null,"11/07/2016","05:51:00","KI13","Rural Long","Asset failure","HV",84,314.1904761904762,0.18724199999999999,5.9595000000000004E-4,"MED"]
[null,"11/07/2016","05:59:00","ST51","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",250,2112.42,4.2625719999999996,2.0178599999999998E-3,"MED"]
[null,"11/07/2016","06:02:00","KI53","Rural Long","Unknown","Unknown",74,4651.9729729729725,2.4423010000000001,5.2499999999999997E-4,"MED"]
[null,"11/07/2016","06:02:00","KI53","Rural Long","Unknown","Unknown",null,117,9.1310000000000002E-3,0,"MED"]
[null,"11/07/2016","06:03:30","ST51","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",2,2096,3.3835999999999998E-2,1.6140000000000001E-5,"MED"]
[null,"11/07/2016","06:32:00","ST15","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",89,1432.943820224719,1.0293680000000001,7.1836000000000003E-4,"MED"]
[null,"11/07/2016","06:36:00","MV41","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",106,2010,1.719703,8.5557000000000005E-4,"MED"]
[null,"11/07/2016","06:37:00","MTB12","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",142,508,0.58224200000000004,1.1461500000000001E-3,"MED"]
[null,"11/07/2016","06:40:00","MTB12","Rural Short","Unknown","Unknown",19.000001000000001,3320,0.50914700000000002,1.5336000000000001E-4,"MED"]
[null,"11/07/2016","06:40:00","MTB12","Rural Short","Unknown","Unknown",100.333355,1,8.0999999999999996E-4,8.0984000000000004E-4,"MED"]
[null,"11/07/2016","06:40:00","MTB12","Rural Short","Unknown","Unknown",null,1,8.0999999999999996E-4,0,"MED"]
[null,"11/07/2016","06:42:00","MTB62","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1481,135.98311951384201,1.6255170000000001,1.195382E-2,"MED"]
[null,"11/07/2016","07:13:00","MTB11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1369,557,6.1547460000000003,1.104981E-2,"MED"]
[null,"11/07/2016","07:15:00","MTB13","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",66,3561,1.897,5.3271999999999998E-4,"MED"]
[null,"11/07/2016","07:19:00","ST12","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",924,911.14285714285711,6.7953200000000002,7.4580200000000001E-3,"MED"]
[null,"11/07/2016","07:19:00","ST12","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",null,2,8.8459999999999997E-3,0,"MED"]
[null,"11/07/2016","07:26:00","NU18","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",542,144.0110701107011,0.55376499999999995,3.8452899999999999E-3,"MED"]
[null,"11/07/2016","07:57:00","MTB41","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",43,802.99999999999977,0.27869899999999997,3.4707E-4,"MED"]
[null,"11/07/2016","07:58:00","MTB61","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",633,362.99999999999994,1.854649,5.1092300000000002E-3,"MED"]
[null,"11/07/2016","08:03:00","GU118","Rural Long","Unknown","Unknown",200,169,0.23979900000000001,1.4189300000000001E-3,"MED"]
[null,"11/07/2016","08:17:00","GU42","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1242,408.55233494363927,3.5999759999999998,8.8115399999999997E-3,"MED"]
[null,"11/07/2016","08:18:00","MTB51","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1017,831,5.9958710000000002,7.2152500000000003E-3,"MED"]
[null,"11/07/2016","08:25:11","EL02","Urban","Planned",null,38,345,2.1557E-2,6.2479999999999998E-5,"MED"]
[null,"11/07/2016","08:27:00","KA32","Rural Long","Planned",null,16,29.999999999999996,3.405E-3,1.1351E-4,"MED"]
[null,"11/07/2016","08:28:00","SSD177","Urban","Planned",null,2084,371,1.271309,3.4267099999999999E-3,"MED"]
[null,"11/07/2016","08:43:00","MTB52","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",912,222.51096491228068,1.4397150000000001,6.47031E-3,"MED"]
[null,"11/07/2016","08:45:24","NL511A","Urban","Planned",null,60,284,2.8018999999999999E-2,9.8659999999999994E-5,"MED"]
[null,"11/07/2016","08:49:52","SA36","Urban","Planned",null,28,365,1.6805E-2,4.604E-5,"MED"]
[null,"11/07/2016","08:54:33","MTB61","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,737,5.9490000000000003E-3,8.0700000000000007E-6,"MED"]
[null,"11/07/2016","09:06:39","MTB13","Rural Short","Vegetation","Grow-in - NSP responsibility",40,1753.9999999999998,0.56629300000000005,3.2286000000000001E-4,"MED"]
[null,"11/07/2016","09:17:00","HH121F","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1781,44.36777091521617,0.12993099999999999,2.9284900000000002E-3,"MED"]
[null,"11/07/2016","09:17:00","MTB11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1821,303,4.4535270000000002,1.469811E-2,"MED"]
[null,"11/07/2016","09:25:00","SA36","Urban","Planned",null,8,295,3.8809999999999999E-3,1.3149999999999999E-5,"MED"]
[null,"11/07/2016","09:27:00","MTB61","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",11,1881.9999999999998,0.16709499999999999,8.8789999999999995E-5,"MED"]
[null,"11/07/2016","09:48:00","GU21","Rural Long","Unknown","Unknown",209,193,0.28617599999999999,1.4827799999999999E-3,"MED"]
[null,"11/07/2016","10:20:00","G20","Rural Long","Planned",null,2,62.999999999999993,8.9400000000000005E-4,1.419E-5,"MED"]
[null,"11/07/2016","10:28:00","ST36","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",295,1532,3.2063510000000002,2.0929199999999998E-3,"MED"]
[null,"11/07/2016","10:33:00","MTB13","Rural Short","Asset failure","HV",203,1731.4581280788179,2.8370009999999999,1.6385E-3,"MED"]
[null,"11/07/2016","10:33:00","MTB13","Rural Short","Asset failure","HV",null,197.34890109890111,1.1596249999999999,0,"MED"]
[null,"11/07/2016","10:33:00","MTB13","Rural Short","Asset failure","HV",null,1,2.405E-3,0,"MED"]
[null,"11/07/2016","10:37:25","ST11","Rural Short","Planned",null,45,38,1.3802E-2,3.6321999999999998E-4,"MED"]
[null,"11/07/2016","10:42:38","NA56","Rural Long","Planned",null,2,106,1.5039999999999999E-3,1.419E-5,"MED"]
[null,"11/07/2016","10:51:00","NA56","Rural Long","Planned",null,1,40,2.8400000000000002E-4,7.0899999999999999E-6,"MED"]
[null,"11/07/2016","11:22:00","SG11","Rural Short","Unknown","Unknown",496,951.19354838709683,3.8080449999999999,4.0034399999999996E-3,"MED"]
[null,"11/07/2016","11:22:17","VH22","Rural Short","Asset failure","LV",1,386,3.1159999999999998E-3,8.0700000000000007E-6,"MED"]
[null,"11/07/2016","11:26:34","MV53","Rural Short","Asset failure","LV",3,2880,6.9736999999999993E-2,2.421E-5,"MED"]
[null,"11/07/2016","11:30:00","GU41","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",156,1045.3589743589744,1.156965,1.10676E-3,"MED"]
[null,"11/07/2016","11:35:59","MTB53","Rural Long","Asset failure","LV",1,1645,1.1671000000000001E-2,7.0899999999999999E-6,"MED"]
[null,"11/07/2016","11:58:00","NU33","Rural Long","Unknown","Unknown",186.333426,46.999999999999986,6.2133000000000001E-2,1.32197E-3,"MED"]
[null,"11/07/2016","12:34:23","GU41","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1.9999979999999999,2880,4.0864999999999999E-2,1.419E-5,"MED"]
[null,"11/07/2016","12:45:00","MV13","Rural Short","Unknown","Unknown",9.0000020000000003,308.99999999999994,2.2447000000000002E-2,7.2639999999999996E-5,"MED"]
[null,"11/07/2016","12:51:00","BM44","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",952,26,0.19978399999999999,7.6840199999999997E-3,"MED"]
[null,"11/07/2016","12:53:00","MTB22","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",18,3029,0.44007200000000002,1.4529000000000001E-4,"MED"]
[null,"11/07/2016","13:06:00","HH522C","Urban","Unknown","Unknown",1380,102,0.23145099999999999,2.2691299999999998E-3,"MED"]
[null,"11/07/2016","13:09:17","SG03","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",2,1152,1.8596999999999999E-2,1.6140000000000001E-5,"MED"]
[null,"11/07/2016","13:16:00","SD381","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",11,470,3.6679000000000003E-2,7.8040000000000005E-5,"MED"]
[null,"11/07/2016","13:37:00","SA744C","Urban","Asset failure","HV",3,16,7.8999999999999996E-5,4.9300000000000002E-6,"MED"]
[null,"11/07/2016","15:24:00","SA18","Urban","Asset failure","HV",2351,90.574223734581025,0.350136,3.8657399999999999E-3,"MED"]
[null,"11/07/2016","15:29:00","GU32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1161,141,1.1613990000000001,8.2368800000000002E-3,"MED"]
[null,"11/07/2016","15:30:00","MTB52","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",882,1327,8.3036650000000005,6.2574700000000002E-3,"MED"]
[null,"11/07/2016","15:34:05","SD38102","Rural Long","Other",null,1,2879.9999999999995,2.0433E-2,7.0899999999999999E-6,"MED"]
[null,"11/07/2016","16:02:00","VH17","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",200,190.99999999999997,0.30832900000000002,1.61429E-3,"MED"]
[null,"11/07/2016","16:25:00","NL544B","Urban","Vegetation","Grow-in - NSP responsibility",166,21,5.7320000000000001E-3,2.7294999999999999E-4,"MED"]
[null,"11/07/2016","17:22:00","MV15","Rural Short","Unknown","Unknown",1,73,5.8900000000000001E-4,8.0700000000000007E-6,"MED"]
[null,"11/07/2016","17:30:00","SG14","Rural Short","Unknown","Unknown",24,4124,0.79888000000000003,1.9370999999999999E-4,"MED"]
[null,"11/07/2016","17:53:00","MTB21","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1377,248,2.756367,1.111438E-2,"MED"]
[null,"11/07/2016","18:04:50","MTB11","Rural Short","Vegetation","Grow-in - NSP responsibility",1,1565,1.2632000000000001E-2,8.0700000000000007E-6,"MED"]
[null,"11/07/2016","18:28:51","MV42","Rural Short","Asset failure","LV",1.9999989999999999,2880.0000000000005,4.6491999999999999E-2,1.6140000000000001E-5,"MED"]
[null,"11/07/2016","20:04:06","WHY10","Urban","Asset failure","LV",1,122.00000000000001,2.0100000000000001E-4,1.64E-6,"MED"]
[null,"11/07/2016","20:37:28","SG04","Rural Short","Other",null,1,1068,8.6199999999999992E-3,8.0700000000000007E-6,"MED"]
[null,"11/07/2016","21:02:56","NL111C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,463.00000000000006,7.6099999999999996E-4,1.64E-6,"MED"]
[null,"11/07/2016","22:06:00","PL07","Urban","Weather",null,15,269,6.6350000000000003E-3,2.4660000000000001E-5,"MED"]
[null,"11/07/2016","22:17:00","ST13","Rural Short","Unknown","Unknown",264,965.34090909090912,2.0570089999999999,2.13086E-3,"MED"]
[null,"11/07/2016","22:17:00","ST13","Rural Short","Unknown","Unknown",null,1.75,4.7460000000000002E-3,0,"MED"]
[null,"11/07/2016","23:18:00","MTB21","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",79,175,0.11158800000000001,6.3763999999999997E-4,"MED"]
[null,"11/07/2016","23:51:00","NL21","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",599,387.00000000000006,0.38116899999999998,9.8492999999999996E-4,"MED"]
[null,"12/07/2016","01:16:00","HH102B","Urban","Unknown","Unknown",1459,8.5723098012337218,2.0565E-2,2.3990299999999999E-3,"MED"]
[null,"12/07/2016","01:20:00","MV15","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1084,110,0.96243999999999996,8.7494500000000006E-3,"MED"]
[null,"12/07/2016","01:53:00","AP425C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1514,140,0.34852499999999997,2.4894600000000002E-3,"MED"]
[null,"12/07/2016","02:28:00","VH71","Rural Short","Unknown","Unknown",320,523.61249999999995,1.35242,2.5828600000000002E-3,"MED"]
[null,"12/07/2016","02:28:00","SSD450","Rural Short","Asset failure","Subtransmission",1536,27,0.33473900000000001,1.2397740000000001E-2,"MED"]
[null,"12/07/2016","02:28:00","SD44301","Rural Long","Asset failure","Subtransmission",2239,48.943278249218395,0.77745900000000001,1.58849E-2,"MED"]
[null,"12/07/2016","02:35:00","W04","Rural Long","Third Party","Other",255,284.8235294117647,0.51528399999999996,1.8091299999999999E-3,"MED"]
[null,"12/07/2016","03:27:00","AP529D","Urban","Asset failure","HV",1443,473.63063063063061,1.1237919999999999,2.37272E-3,"MED"]
[null,"12/07/2016","03:33:00","VH44","Rural Short","Unknown","Unknown",295,339,0.80718500000000004,2.3810799999999998E-3,"MED"]
[null,"12/07/2016","03:36:00","VH32","Rural Short","Unknown","Unknown",5,2280.9999999999995,9.2054999999999998E-2,4.036E-5,"MED"]
[null,"12/07/2016","03:37:00","MV34","Rural Short","Weather",null,1026,935.02534113060437,7.7432309999999998,8.2813100000000001E-3,"MED"]
[null,"12/07/2016","03:38:00","MV31","Rural Short","Asset failure","HV",370,433.89459459459459,1.295798,2.9864399999999999E-3,"MED"]
[null,"12/07/2016","03:39:00","HH409E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2299,138,0.52167200000000002,3.7802299999999999E-3,"MED"]
[null,"12/07/2016","03:39:00","MTB54","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",431,962,2.9415930000000001,3.0577899999999999E-3,"MED"]
[null,"12/07/2016","03:39:00","MTB54","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",null,1,3.058E-3,0,"MED"]
[null,"12/07/2016","03:54:00","GU43","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",506,692.04347826086951,2.4843579999999998,3.5898900000000001E-3,"MED"]
[null,"12/07/2016","03:54:00","GU43","Rural Long","Unknown","Unknown",41,2126,0.61841100000000004,2.9087999999999998E-4,"MED"]
[null,"12/07/2016","04:17:00","SA19","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1824,132.50822368421052,0.39741799999999999,2.9991900000000001E-3,"MED"]
[null,"12/07/2016","04:20:00","HH145A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",870,110.27356321839079,0.15775,1.4305399999999999E-3,"MED"]
[null,"12/07/2016","04:22:00","SD384","Rural Long","Asset failure","Subtransmission",872,813.46559633027528,5.0325249999999997,6.18653E-3,"MED"]
[null,"12/07/2016","04:26:00","MTB51","Rural Long","Unknown","Unknown",2034,472.16420845624384,6.8135640000000004,1.4430500000000001E-2,"MED"]
[null,"12/07/2016","04:26:00","BM44","Rural Short","Third Party","Other",952,102.82878151260505,0.79013800000000001,7.6840199999999997E-3,"MED"]
[null,"12/07/2016","04:42:00","SG10","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1431,557,6.4334850000000001,1.155024E-2,"MED"]
[null,"12/07/2016","04:43:00","MV14","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",558,508.90860215053755,2.2920569999999998,4.5038700000000001E-3,"MED"]
[null,"12/07/2016","04:51:00","NL451C","Urban","Weather",null,1429,150.57662701189645,0.35380899999999998,2.3497000000000001E-3,"MED"]
[null,"12/07/2016","05:07:00","MTB22","Rural Short","Asset failure","HV",382,1285.7984293193717,3.9644940000000002,3.0832899999999998E-3,"MED"]
[null,"12/07/2016","05:07:00","MTB22","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",14,2621.5714285714284,0.296238,1.13E-4,"MED"]
[null,"12/07/2016","05:14:00","NL210C","Urban","Unknown","Unknown",1976,118.99999999999999,0.38664599999999999,3.2491299999999998E-3,"MED"]
[null,"12/07/2016","05:15:00","ST41","Rural Long","Asset failure","HV",116,1785.7413793103447,1.4696260000000001,8.2297999999999996E-4,"MED"]
[null,"12/07/2016","05:16:00","MG03","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",340,168.59705882352944,0.46267999999999998,2.7442899999999999E-3,"MED"]
[null,"12/07/2016","05:23:00","SA16","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1832,203,0.61150700000000002,3.01235E-3,"MED"]
[null,"12/07/2016","05:24:00","HH145A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1229,198.139951179821,0.40040900000000001,2.0208399999999999E-3,"MED"]
[null,"12/07/2016","05:24:00","EL20","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",924,240.3896103896104,0.36523099999999997,1.5193299999999999E-3,"MED"]
[null,"12/07/2016","05:25:00","HH496A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",286,464.99999999999994,0.21867500000000001,4.7027000000000001E-4,"MED"]
[null,"12/07/2016","05:44:00","NL115B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",36.666685000000001,2014,0.12142600000000001,6.029E-5,"MED"]
[null,"12/07/2016","05:48:00","NA58","Rural Long","Unknown","Unknown",88,233,0.14546799999999999,6.2432999999999998E-4,"MED"]
[null,"12/07/2016","05:50:00","SG09","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",103,1829.1844660194176,1.5207090000000001,8.3135999999999995E-4,"MED"]
[null,"12/07/2016","06:00:00","NA01","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",59,283,0.11845899999999999,4.1857999999999999E-4,"MED"]
[null,"12/07/2016","06:02:00","MI07","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",76,308,0.166071,5.3919000000000005E-4,"MED"]
[null,"12/07/2016","06:08:00","BT15","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",106,214.29245283018867,0.16115499999999999,7.5202999999999999E-4,"MED"]
[null,"12/07/2016","06:09:00","LM41","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",478,215.92468619246864,0.73225200000000001,3.3912399999999998E-3,"MED"]
[null,"12/07/2016","06:13:20","HH130F","Urban","Asset failure","LV",13.333320000000001,1176,2.5783E-2,2.192E-5,"MED"]
[null,"12/07/2016","06:23:00","CN22","Rural Long","Weather",null,119,459.72268907563023,0.38812600000000003,8.4426E-4,"MED"]
[null,"12/07/2016","06:32:00","GA15","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",239,190,0.36652400000000002,1.9290799999999999E-3,"MED"]
[null,"12/07/2016","06:35:14","HH107B","Urban","Asset failure","LV",1,1842,3.029E-3,1.64E-6,"MED"]
[null,"12/07/2016","06:41:00","BT26","Rural Long","Asset failure","HV",161,787.03105590062114,0.898976,1.1422400000000001E-3,"MED"]
[null,"12/07/2016","06:56:00","CN74","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",93,521.27956989247309,0.343941,6.5979999999999999E-4,"MED"]
[null,"12/07/2016","07:15:00","MG19","Rural Long","Unknown","Unknown",107,137,0.104,7.5913E-4,"MED"]
[null,"12/07/2016","07:25:00","G11","Rural Long","Unknown","Unknown",10,173.99999999999997,1.2345E-2,7.0950000000000003E-5,"MED"]
[null,"12/07/2016","07:29:00","SD351","Rural Long","Asset failure","Subtransmission",2062,27.144519883608144,0.39710099999999998,1.462915E-2,"MED"]
[null,"12/07/2016","07:37:00","CN32","Rural Long","Asset failure","HV",31,651.45161290322585,0.14327599999999999,2.1992999999999999E-4,"MED"]
[null,"12/07/2016","07:39:00","HH522C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1380,166.93913043478264,0.37880599999999998,2.2691299999999998E-3,"MED"]
[null,"12/07/2016","07:45:30","NL234C","Urban","Weather",null,31.999967999999999,2226,0.11712599999999999,5.2620000000000001E-5,"MED"]
[null,"12/07/2016","07:49:43","HH428F","Urban","Unknown","Unknown",17.999981999999999,1031,3.0515E-2,2.9600000000000001E-5,"MED"]
[null,"12/07/2016","07:56:39","HH428A","Urban","Unknown","Unknown",25.999974000000002,1048,4.4803999999999997E-2,4.2750000000000002E-5,"MED"]
[null,"12/07/2016","07:57:07","HH177C","Urban","Asset failure","LV",1,1374.0000000000002,2.2590000000000002E-3,1.64E-6,"MED"]
[null,"12/07/2016","07:59:00","KI13","Rural Long","Asset failure","HV",17,494.58823529411762,5.9651999999999997E-2,1.2061E-4,"MED"]
[null,"12/07/2016","08:03:00","SA36","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",33,877,4.7587999999999998E-2,5.4259999999999999E-5,"MED"]
[null,"12/07/2016","08:06:00","MTB32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",567,65.962962962962962,0.265347,4.02266E-3,"MED"]
[null,"12/07/2016","08:06:37","HH107B","Urban","Unknown","Unknown",2,1017.0000000000001,3.3440000000000002E-3,3.2899999999999998E-6,"MED"]
[null,"12/07/2016","08:14:00","MV33","Rural Short","Asset failure","HV",284,301.47535211267609,0.69106900000000004,2.2922900000000002E-3,"MED"]
[null,"12/07/2016","08:15:06","MV52","Rural Short","Unknown","Unknown",13.33334,2036.0000000000002,0.219113,1.0762E-4,"MED"]
[null,"12/07/2016","08:15:14","AP227A","Urban","Asset failure","LV",1,136,2.24E-4,1.64E-6,"MED"]
[null,"12/07/2016","08:22:33","SG07","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1940,1.5658999999999999E-2,8.0700000000000007E-6,"MED"]
[null,"12/07/2016","08:29:56","SM216B","Urban","Unknown","Unknown",8.9999909999999996,1001.9999999999999,1.4827999999999999E-2,1.4800000000000001E-5,"MED"]
[null,"12/07/2016","08:35:00","YK16","Rural Long","Asset failure","HV",89,246.29213483146066,0.15551400000000001,6.3142000000000005E-4,"MED"]
[null,"12/07/2016","08:39:59","EL07","Urban","Planned",null,96,292,4.6093000000000002E-2,1.5784999999999999E-4,"MED"]
[null,"12/07/2016","08:48:29","NL115D","Urban","Overloads",null,14.333318999999999,1745,4.1126999999999997E-2,2.357E-5,"MED"]
[null,"12/07/2016","09:00:43","AP226D","Urban","Weather",null,1,289,4.75E-4,1.64E-6,"MED"]
[null,"12/07/2016","09:10:00","MI05","Rural Long","Third Party","Other",56,168,6.6746E-2,3.9730000000000001E-4,"MED"]
[null,"12/07/2016","09:12:00","SM350C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",74,1598,0.194441,1.2168E-4,"MED"]
[null,"12/07/2016","09:22:07","SM411B","Urban","Third Party","Other",75,1974.0000000000002,0.24343799999999999,1.2332000000000001E-4,"MED"]
[null,"12/07/2016","09:33:00","HH177B","Urban","Unknown","Unknown",1401,141,0.32481599999999999,2.3036599999999999E-3,"MED"]
[null,"12/07/2016","09:44:57","SM411D","Urban","Planned",null,57,109,1.0215999999999999E-2,9.3720000000000004E-5,"MED"]
[null,"12/07/2016","09:47:00","EL19","Urban","Unknown","Unknown",637,256.26216640502355,0.26841300000000001,1.0474200000000001E-3,"MED"]
[null,"12/07/2016","09:51:00","HH409A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1124,80.999999999999986,0.149703,1.84819E-3,"MED"]
[null,"12/07/2016","10:03:00","NL234A","Urban","Unknown","Unknown",2658,283.3792325056433,1.2385189999999999,4.37054E-3,"MED"]
[null,"12/07/2016","10:11:50","MT16","Rural Long","Planned",null,2,67,9.5100000000000002E-4,1.419E-5,"MED"]
[null,"12/07/2016","10:12:00","GU38","Rural Long","Unknown","Unknown",16,1949.875,0.22133900000000001,1.1351E-4,"MED"]
[null,"12/07/2016","10:15:00","NL210E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2844,938.11427566807322,4.3869730000000002,4.67637E-3,"MED"]
[null,"12/07/2016","10:15:00","NL210E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1862,6.2706766917293226,1.9199000000000001E-2,3.0616799999999998E-3,"MED"]
[null,"12/07/2016","10:19:00","EL02","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1359,194,0.43351200000000001,2.2346000000000002E-3,"MED"]
[null,"12/07/2016","10:22:00","MB24","Rural Short","Unknown","Unknown",791,208.92793931731987,1.333904,6.3845200000000003E-3,"MED"]
[null,"12/07/2016","10:22:00","GA15","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",239,266.35564853556485,0.51382000000000005,1.9290799999999999E-3,"MED"]
[null,"12/07/2016","10:23:30","VH33","Rural Short","Other",null,2,1680,2.7119999999999998E-2,1.6140000000000001E-5,"MED"]
[null,"12/07/2016","10:33:17","NL111C","Urban","Asset failure","LV",79,1767,0.22953200000000001,1.2990000000000001E-4,"MED"]
[null,"12/07/2016","10:36:00","NA58","Rural Long","Unknown","Unknown",88,524.875,0.32769399999999999,6.2432999999999998E-4,"MED"]
[null,"12/07/2016","10:57:29","NL111C","Urban","Overloads",null,1,1606,2.6410000000000001E-3,1.64E-6,"MED"]
[null,"12/07/2016","11:01:00","SM374A","Urban","Vegetation","Grow-in - NSP responsibility",2015,116.89975186104218,0.38731900000000002,3.3132499999999998E-3,"MED"]
[null,"12/07/2016","11:02:43","SM126A","Urban","Overloads",null,1,1688,2.7759999999999998E-3,1.64E-6,"MED"]
[null,"12/07/2016","11:03:26","HH428D","Urban","Asset failure","LV",65,990.00000000000011,0.10581,1.0688000000000001E-4,"MED"]
[null,"12/07/2016","11:04:27","HH341D","Urban","Unknown","Unknown",16.333317000000001,910,2.444E-2,2.686E-5,"MED"]
[null,"12/07/2016","11:09:00","SSD450","Rural Short","Planned",null,1536,2,2.4795000000000001E-2,1.2397740000000001E-2,"MED"]
[null,"12/07/2016","11:09:00","SSD450","Rural Long","Planned",null,2239,2.6306386779812416,4.1786999999999998E-2,1.58849E-2,"MED"]
[null,"12/07/2016","11:14:00","AP149E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1945,101.51670951156812,0.32466600000000001,3.1981499999999999E-3,"MED"]
[null,"12/07/2016","11:32:58","HH145E","Urban","Unknown","Unknown",5.3333279999999998,1078,9.4540000000000006E-3,8.7700000000000007E-6,"MED"]
[null,"12/07/2016","11:33:00","SA14","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",3217,54,0.28564400000000001,5.2896999999999996E-3,"MED"]
[null,"12/07/2016","11:34:00","HH130B","Urban","Unknown","Unknown",2476,126.77625201938612,0.51614099999999996,4.0712700000000001E-3,"MED"]
[null,"12/07/2016","11:46:46","AP132A","Urban","Asset failure","LV",4.6666619999999996,884.00000000000011,6.783E-3,7.6699999999999994E-6,"MED"]
[null,"12/07/2016","11:49:57","HH432F","Urban","Weather",null,24.333309,779.00000000000011,3.1168999999999999E-2,4.0009999999999998E-5,"MED"]
[null,"12/07/2016","11:53:00","W32","Rural Long","Asset failure","HV",18,377,4.8143999999999999E-2,1.2769999999999999E-4,"MED"]
[null,"12/07/2016","11:57:00","NL760B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2607,914,3.9180220000000001,4.2866800000000002E-3,"MED"]
[null,"12/07/2016","12:02:00","NL210D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2854,284.50875963559918,1.335148,4.6928200000000003E-3,"MED"]
[null,"12/07/2016","12:07:00","ME200F","Urban","Third Party","Other",908,158.1431718061674,0.23611099999999999,1.4930200000000001E-3,"MED"]
[null,"12/07/2016","12:12:00","ST35","Rural Long","Vegetation","Grow-in - NSP responsibility",162,269,0.30917,1.1493300000000001E-3,"MED"]
[null,"12/07/2016","12:13:00","HH148B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1401,556,1.2808330000000001,2.3036599999999999E-3,"MED"]
[null,"12/07/2016","12:14:00","SG02","Rural Short","Vegetation","Grow-in - NSP responsibility",718,99.999999999999986,0.57952999999999999,5.7952999999999998E-3,"MED"]
[null,"12/07/2016","12:15:00","SD412","Rural Short","Unknown","Unknown",1102,543.00000000000011,4.8298420000000002,8.8947399999999999E-3,"MED"]
[null,"12/07/2016","12:20:00","HH522B","Urban","Unknown","Unknown",2333,248.99999999999997,0.95519900000000002,3.83614E-3,"MED"]
[null,"12/07/2016","12:20:00","MV14","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",190,1162.9263157894738,1.7834350000000001,1.5335800000000001E-3,"MED"]
[null,"12/07/2016","12:24:00","HH341H","Urban","Unknown","Unknown",1650,269,0.72982000000000002,2.71309E-3,"MED"]
[null,"12/07/2016","12:26:00","HH341C","Urban","Unknown","Unknown",1216,69,0.137963,1.9994600000000002E-3,"MED"]
[null,"12/07/2016","12:31:00","SM350A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1718,529.53434225844012,1.495881,2.8249E-3,"MED"]
[null,"12/07/2016","12:36:00","VH72","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",100,219,0.17676500000000001,8.0714000000000003E-4,"MED"]
[null,"12/07/2016","12:44:00","NL760C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",127,1421,0.29674099999999998,2.0882999999999999E-4,"MED"]
[null,"12/07/2016","12:45:00","GU42","Rural Long","Unknown","Unknown",1242,152.21900161030595,1.3412839999999999,8.8115399999999997E-3,"MED"]
[null,"12/07/2016","12:45:42","GA800A","Rural Short","Vegetation","Grow-in - NSP responsibility",1,793,6.4009999999999996E-3,8.0700000000000007E-6,"MED"]
[null,"12/07/2016","12:52:07","SM349H","Urban","Vegetation","Grow-in - NSP responsibility",1,1745.0000000000002,2.869E-3,1.64E-6,"MED"]
[null,"12/07/2016","12:52:42","SM126C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",44,2058.9999999999995,0.14896699999999999,7.2349999999999997E-5,"MED"]
[null,"12/07/2016","12:55:00","BM35","Rural Short","Unknown","Unknown",248,111.00000000000001,0.222191,2.0017199999999998E-3,"MED"]
[null,"12/07/2016","12:56:29","CBD103C","Urban","Unknown","Unknown",23.999976,756,2.9833999999999999E-2,3.9459999999999998E-5,"MED"]
[null,"12/07/2016","13:02:00","HH386G","Urban","Unknown","Unknown",47.333356999999999,1403.0000000000002,0.109195,7.7830000000000005E-5,"MED"]
[null,"12/07/2016","13:02:00","MI02","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",230,110.00000000000001,0.204208,1.8564300000000001E-3,"MED"]
[null,"12/07/2016","13:06:00","NU25","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",865,78,0.47867500000000002,6.1368600000000001E-3,"MED"]
[null,"12/07/2016","13:15:00","W17","Rural Long","Third Party","Other",51,1039.2941176470588,0.37604399999999999,3.6183E-4,"MED"]
[null,"12/07/2016","13:15:00","W07","Rural Short","Unknown","Unknown",108,287,0.25018299999999999,8.7171999999999998E-4,"MED"]
[null,"12/07/2016","13:18:00","NL210A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",80,909,0.119573,1.3154E-4,"MED"]
[null,"12/07/2016","13:23:51","SM126C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1724,2.8349999999999998E-3,1.64E-6,"MED"]
[null,"12/07/2016","13:24:00","SD413","Rural Short","Asset failure","Subtransmission",3109,391.69765197812802,9.8293130000000009,2.5094129999999999E-2,"MED"]
[null,"12/07/2016","13:33:00","MV53","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",62,1093.5645161290324,0.54725199999999996,5.0042999999999995E-4,"MED"]
[null,"12/07/2016","13:33:00","NL21","Urban","Asset failure","HV",5.3333360000000001,2112,1.8520999999999999E-2,8.7700000000000007E-6,"MED"]
[null,"12/07/2016","13:42:12","HH409E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",89,1287,0.18834200000000001,1.4634000000000001E-4,"MED"]
[null,"12/07/2016","13:45:00","HH409E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",76,244.99999999999997,3.0616999999999998E-2,1.2496999999999999E-4,"MED"]
[null,"12/07/2016","13:46:00","MTB52","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",66,565,0.26455899999999999,4.6825000000000002E-4,"MED"]
[null,"12/07/2016","13:48:10","SM349E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1494.0000000000002,2.457E-3,1.64E-6,"MED"]
[null,"12/07/2016","14:02:00","HH145A","Urban","Unknown","Unknown",870,219.99999999999997,0.314718,1.4305399999999999E-3,"MED"]
[null,"12/07/2016","14:07:00","MV32","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",13,1541,0.16169500000000001,1.0493E-4,"MED"]
[null,"12/07/2016","14:07:00","MV32","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",4,281,9.0720000000000002E-3,3.2289999999999997E-5,"MED"]
[null,"12/07/2016","14:11:00","GA02","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1590,77,0.98818700000000004,1.2833600000000001E-2,"MED"]
[null,"12/07/2016","14:11:59","HH386A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1430.0000000000002,2.3509999999999998E-3,1.64E-6,"MED"]
[null,"12/07/2016","14:13:00","SM349E","Urban","Unknown","Unknown",72,744,8.8081999999999994E-2,1.1839E-4,"MED"]
[null,"12/07/2016","14:17:44","AP227B","Urban","Unknown","Unknown",1.9999979999999999,770,2.532E-3,3.2899999999999998E-6,"MED"]
[null,"12/07/2016","14:23:52","MV52","Rural Short","Third Party","Other",1,1617,1.3051999999999999E-2,8.0700000000000007E-6,"MED"]
[null,"12/07/2016","14:31:00","GA37","Rural Long","Weather",null,22,502.5454545454545,7.8437999999999994E-2,1.5608000000000001E-4,"MED"]
[null,"12/07/2016","14:41:00","GU41","Rural Long","Unknown","Unknown",318,1193,2.691522,2.2561E-3,"MED"]
[null,"12/07/2016","14:47:00","MI05","Rural Long","Weather",null,56,303,0.120382,3.9730000000000001E-4,"MED"]
[null,"12/07/2016","14:58:00","NL451C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1321,296.21423164269493,0.64341099999999996,2.1721100000000001E-3,"MED"]
[null,"12/07/2016","15:06:00","NL760C","Urban","Vegetation","Grow-in - NSP responsibility",72,1419,0.167994,1.1839E-4,"MED"]
[null,"12/07/2016","15:14:46","SG10","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",39,297,9.3492000000000006E-2,3.1479000000000001E-4,"MED"]
[null,"12/07/2016","15:16:00","MTB82","Rural Short","Asset failure","HV",80,396.1875,0.25582500000000002,6.4572000000000002E-4,"MED"]
[null,"12/07/2016","15:20:48","HH148A","Urban","Vegetation","Grow-in - NSP responsibility",15.666651,734,1.8908000000000001E-2,2.5760000000000001E-5,"MED"]
[null,"12/07/2016","15:20:56","SG03","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",12.999987000000001,1188.9999999999998,0.12476,1.0493E-4,"MED"]
[null,"12/07/2016","15:22:30","NL111P","Urban","Weather",null,36.666685000000001,1509.9999999999998,9.1038999999999995E-2,6.029E-5,"MED"]
[null,"12/07/2016","15:39:00","MTB13","Rural Short","Unknown","Unknown",12.666670999999999,1471,0.150393,1.0224E-4,"MED"]
[null,"12/07/2016","15:41:00","HH130B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2476,264,1.074816,4.0712700000000001E-3,"MED"]
[null,"12/07/2016","15:54:51","NU04","Rural Short","Weather",null,1,520,4.1970000000000002E-3,8.0700000000000007E-6,"MED"]
[null,"12/07/2016","16:10:00","MTB32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",5,2767.9999999999995,9.819E-2,3.5469999999999998E-5,"MED"]
[null,"12/07/2016","16:12:31","NU21","Rural Long","Other",null,4.9999950000000002,557.99999999999989,1.9793999999999999E-2,3.5469999999999998E-5,"MED"]
[null,"12/07/2016","16:18:41","SM349E","Urban","Asset failure","LV",1,1358,2.2330000000000002E-3,1.64E-6,"MED"]
[null,"12/07/2016","16:23:36","SM411C","Urban","Asset failure","LV",11.333322000000001,1185.9999999999998,2.2100999999999999E-2,1.8640000000000001E-5,"MED"]
[null,"12/07/2016","16:25:31","SM410B","Urban","Vegetation","Grow-in - NSP responsibility",1,1306,2.147E-3,1.64E-6,"MED"]
[null,"12/07/2016","16:25:58","NU21","Rural Long","Other",null,2,538,7.6340000000000002E-3,1.419E-5,"MED"]
[null,"12/07/2016","16:32:26","SA520D","Urban","Asset failure","LV",1,1188.0000000000002,1.9530000000000001E-3,1.64E-6,"MED"]
[null,"12/07/2016","16:33:46","NL234B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1825,3.0010000000000002E-3,1.64E-6,"MED"]
[null,"12/07/2016","16:35:49","SM350G","Urban","Other",null,37,1635,9.9472000000000005E-2,6.084E-5,"MED"]
[null,"12/07/2016","16:40:00","BT03","Rural Long","Unknown","Unknown",3,1194.0000000000002,2.5413000000000002E-2,2.128E-5,"MED"]
[null,"12/07/2016","16:46:56","NL234C","Urban","Asset failure","LV",1,1758,2.8909999999999999E-3,1.64E-6,"MED"]
[null,"12/07/2016","16:54:00","SM216A","Urban","Overloads",null,2,302,9.9299999999999996E-4,3.2899999999999998E-6,"MED"]
[null,"12/07/2016","16:55:00","ST36","Rural Long","Unknown","Unknown",35.000002000000002,1358.9999999999998,0.33745700000000001,2.4831000000000001E-4,"MED"]
[null,"12/07/2016","16:55:46","SM172E","Urban","Asset failure","LV",1,1534,2.5219999999999999E-3,1.64E-6,"MED"]
[null,"12/07/2016","17:17:16","ST11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1128,9.1050000000000002E-3,8.0700000000000007E-6,"MED"]
[null,"12/07/2016","17:17:43","AP344E","Urban","Asset failure","LV",1,418.00000000000006,6.87E-4,1.64E-6,"MED"]
[null,"12/07/2016","17:20:00","HH409B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",875,184.00000000000003,0.26473099999999999,1.4387600000000001E-3,"MED"]
[null,"12/07/2016","17:21:58","AP149A","Urban","Asset failure","LV",1,1060,1.743E-3,1.64E-6,"MED"]
[null,"12/07/2016","17:29:46","ST36","Rural Long","Weather",null,4.6666689999999997,1364,4.5159999999999999E-2,3.311E-5,"MED"]
[null,"12/07/2016","17:36:40","HH118D","Urban","Vegetation","Grow-in - NSP responsibility",21.999977999999999,478.99999999999994,1.7328E-2,3.6170000000000001E-5,"MED"]
[null,"12/07/2016","17:43:00","GA23","Rural Short","Asset failure","HV",67.666688999999991,135.05418930723803,7.3761999999999994E-2,5.4617000000000001E-4,"MED"]
[null,"12/07/2016","17:43:32","BM55","Rural Short","Asset failure","LV",1,159,1.2830000000000001E-3,8.0700000000000007E-6,"MED"]
[null,"12/07/2016","17:46:09","SM350F","Urban","Asset failure","LV",30.666636,1319,6.6511000000000001E-2,5.0420000000000002E-5,"MED"]
[null,"12/07/2016","17:50:53","MV62","Rural Short","Asset failure","LV",12.999987000000001,1530,0.16054099999999999,1.0493E-4,"MED"]
[null,"12/07/2016","17:53:43","HH341H","Urban","Unknown","Unknown",14.999985000000001,541,1.3343000000000001E-2,2.4660000000000001E-5,"MED"]
[null,"12/07/2016","17:55:00","ST11","Rural Short","Asset failure","Distribution substation",260,1317.0923076923077,2.7640189999999998,2.0985800000000001E-3,"MED"]
[null,"12/07/2016","17:57:08","ME200A","Urban","Overloads",null,1,1052,1.73E-3,1.64E-6,"MED"]
[null,"12/07/2016","18:00:58","AP425C","Urban","Weather",null,1,1056,1.7359999999999999E-3,1.64E-6,"MED"]
[null,"12/07/2016","18:11:07","SM172B","Urban","Weather",null,1,1371,2.2539999999999999E-3,1.64E-6,"MED"]
[null,"12/07/2016","18:15:36","AP214A","Urban","Vegetation","Grow-in - NSP responsibility",1,619,1.018E-3,1.64E-6,"MED"]
[null,"12/07/2016","18:19:22","HH341H","Urban","Unknown","Unknown",51,374,3.1363000000000002E-2,8.386E-5,"MED"]
[null,"12/07/2016","18:22:18","SM126A","Urban","Weather",null,1,1437,2.3630000000000001E-3,1.64E-6,"MED"]
[null,"12/07/2016","18:25:00","HH341C","Urban","Unknown","Unknown",1623.667475,39.069595575288595,0.104308,2.66979E-3,"MED"]
[null,"12/07/2016","18:32:28","HH428D","Urban","Asset failure","LV",10.666656,629.00000000000011,1.1032E-2,1.7540000000000001E-5,"MED"]
[null,"12/07/2016","18:35:00","ST51","Rural Short","Unknown","Unknown",6,1365,6.6104999999999997E-2,4.8430000000000002E-5,"MED"]
[null,"12/07/2016","18:53:00","AP372B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1461,134,0.32190999999999997,2.4023099999999999E-3,"MED"]
[null,"12/07/2016","19:00:05","SM374A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",63,1295.0000000000002,0.13414999999999999,1.0359E-4,"MED"]
[null,"12/07/2016","19:02:16","AP424D","Urban","Asset failure","LV",1,1009,1.6590000000000001E-3,1.64E-6,"MED"]
[null,"12/07/2016","19:12:00","SA20","Urban","Unknown","Unknown",43,29.999999999999996,2.1210000000000001E-3,7.0699999999999997E-5,"MED"]
[null,"12/07/2016","19:12:48","AP424E","Urban","Other",null,1,1376.0000000000002,2.2629999999999998E-3,1.64E-6,"MED"]
[null,"12/07/2016","19:26:31","SM374B","Urban","Other",null,1,1282.0000000000002,2.1080000000000001E-3,1.64E-6,"MED"]
[null,"12/07/2016","19:31:34","HH102A","Urban","Asset failure","LV",28.999970999999999,465,2.2172999999999998E-2,4.7679999999999998E-5,"MED"]
[null,"12/07/2016","19:33:00","ME347B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1035,92,0.15656999999999999,1.70184E-3,"MED"]
[null,"12/07/2016","19:34:00","R01","Rural Long","Unknown","Unknown",140,305,0.30294100000000002,9.9324999999999999E-4,"MED"]
[null,"12/07/2016","19:34:00","R01","Rural Long","Unknown","Unknown",null,1,4.9700000000000005E-4,0,"MED"]
[null,"12/07/2016","19:43:00","HH121C","Urban","Unknown","Unknown",73.333370000000002,54.999999999999993,6.6319999999999999E-3,1.2058E-4,"MED"]
[null,"12/07/2016","19:49:19","PP02","Urban","Asset failure","LV",1,293,4.8200000000000001E-4,1.64E-6,"MED"]
[null,"12/07/2016","19:55:00","AP365B","Urban","Unknown","Unknown",69,117,1.3273999999999999E-2,1.1346E-4,"MED"]
[null,"12/07/2016","20:15:00","VH72","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",100,836,0.67477299999999996,8.0714000000000003E-4,"MED"]
[null,"12/07/2016","20:18:26","HH177G","Urban","Overloads",null,1,1396,2.2950000000000002E-3,1.64E-6,"MED"]
[null,"12/07/2016","20:31:00","HH130B","Urban","Unknown","Unknown",206,289,9.7891000000000006E-2,3.3871999999999998E-4,"MED"]
[null,"12/07/2016","20:31:00","HH130B","Urban","Unknown","Unknown",2270,2,7.4650000000000003E-3,3.7325499999999998E-3,"MED"]
[null,"12/07/2016","20:31:49","AP355B","Urban","Asset failure","LV",1,340,5.5900000000000004E-4,1.64E-6,"MED"]
[null,"12/07/2016","20:33:29","CN24","Rural Long","Unknown","Unknown",21.666644999999999,347.00000000000006,5.3339999999999999E-2,1.5372000000000001E-4,"MED"]
[null,"12/07/2016","20:33:35","HH130B","Urban","Unknown","Unknown",9.6666570000000007,254.00000000000003,4.0369999999999998E-3,1.5889999999999999E-5,"MED"]
[null,"12/07/2016","20:40:00","MG03","Rural Short","Third Party","Other",7,712,4.0228E-2,5.6499999999999998E-5,"MED"]
[null,"12/07/2016","20:46:00","NL760A","Urban","Vegetation","Grow-in - NSP responsibility",43,72.069767441860463,5.0959999999999998E-3,7.0699999999999997E-5,"MED"]
[null,"12/07/2016","20:47:25","SM179C","Urban","Asset failure","LV",1,1562,2.568E-3,1.64E-6,"MED"]
[null,"12/07/2016","20:58:00","AP149D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1873,110,0.33877400000000002,3.07976E-3,"MED"]
[null,"12/07/2016","21:02:40","HH403A","Urban","Overloads",null,1,918,1.5089999999999999E-3,1.64E-6,"MED"]
[null,"12/07/2016","21:52:46","MG21","Rural Long","Third Party","Other",16,550,6.2433000000000002E-2,1.1351E-4,"MED"]
[null,"12/07/2016","22:12:09","HH177G","Urban","Asset failure","LV",18.999980999999998,746,2.3306E-2,3.1239999999999999E-5,"MED"]
[null,"12/07/2016","22:23:00","GU13","Rural Long","Weather",null,404,946.74009900990086,2.7135790000000002,2.86623E-3,"MED"]
[null,"12/07/2016","22:23:00","GU13","Rural Long","Weather",null,null,43,3.0202E-2,0,"MED"]
[null,"12/07/2016","22:29:00","MTB32","Rural Long","Unknown","Unknown",10.666672,1129.0000000000002,8.5438E-2,7.5679999999999994E-5,"MED"]
[null,"12/07/2016","22:52:43","HH409B","Urban","Unknown","Unknown",18.333314999999999,336.00000000000006,1.0129000000000001E-2,3.0150000000000001E-5,"MED"]
[null,"12/07/2016","23:15:21","GU13","Rural Long","Overloads",null,4,1341,3.8056E-2,2.8379999999999999E-5,"MED"]
[null,"13/07/2016","03:38:35","NL760B","Urban","Asset failure","LV",30.666682000000002,1243.9999999999998,6.2728999999999993E-2,5.0430000000000003E-5]
[null,"13/07/2016","04:40:00","HH107A","Urban","Unknown","Unknown",101.333384,62,1.0331E-2,1.6662E-4]
[null,"13/07/2016","06:06:25","SG03","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",29,765.99999999999989,0.17929899999999999,2.3406999999999999E-4]
[null,"13/07/2016","07:15:34","AP132D","Urban","Asset failure","LV",8,200,2.6310000000000001E-3,1.3149999999999999E-5]
[null,"13/07/2016","07:44:36","MV15","Rural Short","Unknown","Unknown",0.99999899999999997,1030.0000000000002,8.3140000000000002E-3,8.0700000000000007E-6]
[null,"13/07/2016","07:54:00","GA15","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",4.0000010000000001,103.99999999999999,3.3579999999999999E-3,3.2289999999999997E-5]
[null,"13/07/2016","08:12:00","SG04","Rural Short","Unknown","Unknown",16,715,9.2337000000000002E-2,1.2914E-4]
[null,"13/07/2016","08:40:07","MV64","Rural Short","Planned",null,52,90,3.7774000000000002E-2,4.1972E-4]
[null,"13/07/2016","08:53:35","AP226D","Urban","Other",null,1,1148,1.8879999999999999E-3,1.64E-6]
[null,"13/07/2016","09:29:00","NL210A","Urban","Unknown","Unknown",3,1071,5.2830000000000004E-3,4.9300000000000002E-6]
[null,"13/07/2016","09:36:52","HH386D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1038.0000000000002,1.707E-3,1.64E-6]
[null,"13/07/2016","09:43:09","NL111A","Urban","Asset failure","LV",1,1034,1.6999999999999999E-3,1.64E-6]
[null,"13/07/2016","10:17:00","MTB82","Rural Short","Unknown","Unknown",77,278,0.17277699999999999,6.2149999999999998E-4]
[null,"13/07/2016","10:20:00","GU42","Rural Long","Unknown","Unknown",3,297,6.3210000000000002E-3,2.128E-5]
[null,"13/07/2016","10:26:43","AP227D","Urban","Asset failure","LV",1,1101,1.81E-3,1.64E-6]
[null,"13/07/2016","10:42:00","SG14","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1065,156.44131455399062,1.344784,8.5960900000000007E-3]
[null,"13/07/2016","10:51:00","VH72","Rural Short","Weather",null,100,429,0.34626499999999999,8.0714000000000003E-4]
[null,"13/07/2016","11:22:00","GA41","Rural Long","Unknown","Unknown",6,85,3.6180000000000001E-3,4.2570000000000001E-5]
[null,"13/07/2016","13:23:00","SM126C","Urban","Unknown","Unknown",66,159,1.7255E-2,1.0852E-4]
[null,"13/07/2016","13:25:00","ST13","Rural Short","Unknown","Unknown",263,302,0.64108299999999996,2.1227899999999998E-3]
[null,"13/07/2016","14:19:38","AP529D","Urban","Asset failure","LV",1,724,1.1900000000000001E-3,1.64E-6]
[null,"13/07/2016","14:52:00","AP365D1","Urban","Unknown","Unknown",13,4,8.6000000000000003E-5,2.1379999999999999E-5]
[null,"13/07/2016","14:53:00","HH148D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",876,83,0.11955300000000001,1.4404000000000001E-3]
[null,"13/07/2016","15:18:00","SM411E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,64,1.05E-4,1.64E-6]
[null,"13/07/2016","15:30:00","GU36","Rural Long","Unknown","Unknown",2,428,6.0730000000000003E-3,1.419E-5]
[null,"13/07/2016","15:41:00","NU31","Rural Long","Asset failure","HV",402,226.92537313432837,0.64720100000000003,2.8520400000000001E-3]
[null,"13/07/2016","15:44:09","AP529D","Urban","Asset failure","LV",2,666,2.1900000000000001E-3,3.2899999999999998E-6]
[null,"13/07/2016","16:01:22","EL13","Urban","Overloads",null,1,972.00000000000011,1.598E-3,1.64E-6]
[null,"13/07/2016","16:53:36","EL10","Urban","Asset failure","LV",1,1270,2.088E-3,1.64E-6]
[null,"13/07/2016","17:08:00","SD481","Rural Short","Unknown","Unknown",230,170.49565217391304,0.31651400000000002,1.8564300000000001E-3]
[null,"13/07/2016","17:16:09","SG03","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,451,3.64E-3,8.0700000000000007E-6]
[null,"13/07/2016","17:21:15","SA35","Urban","Asset failure","LV",1,948,1.5590000000000001E-3,1.64E-6]
[null,"13/07/2016","17:53:26","NL234C","Urban","Asset failure","LV",1,120.00000000000001,1.9699999999999999E-4,1.64E-6]
[null,"13/07/2016","18:12:37","HH118D","Urban","Overloads",null,1,874,1.4369999999999999E-3,1.64E-6]
[null,"13/07/2016","18:45:00","MTB32","Rural Long","Asset failure","HV",33.000009000000006,235.99999999999991,5.5252999999999997E-2,2.3411999999999999E-4]
[null,"13/07/2016","18:48:54","EL18","Urban","Asset failure","LV",51,855,7.1698999999999999E-2,8.386E-5]
[null,"13/07/2016","18:59:06","HH341A","Urban","Overloads",null,1,545,8.9599999999999999E-4,1.64E-6]
[null,"13/07/2016","19:08:45","GU13","Rural Long","Asset failure","LV",1,1068,7.5770000000000004E-3,7.0899999999999999E-6]
[null,"13/07/2016","19:19:00","W04","Rural Long","Unknown","Unknown",2,906.5,1.2862999999999999E-2,1.419E-5]
[null,"13/07/2016","19:58:00","SA20","Urban","Asset failure","HV",82,593.70731707317066,8.0050999999999997E-2,1.3483000000000001E-4]
[null,"13/07/2016","20:15:31","NL760C","Urban","Overloads",null,1,790.00000000000011,1.299E-3,1.64E-6]
[null,"13/07/2016","21:16:59","NU06","Rural Long","Third Party","Vehicle impact",28,178,3.5360000000000003E-2,1.9865E-4]
[null,"13/07/2016","23:02:06","AP372B","Urban","Overloads",null,1,190.00000000000003,3.1199999999999999E-4,1.64E-6]
[null,"13/07/2016","23:40:36","SA33","Urban","Overloads",null,1,747.00000000000011,1.2279999999999999E-3,1.64E-6]
[null,"14/07/2016","01:46:00","MTB61","Rural Short","Animal","Animal impact",144,512,0.59509199999999995,1.1622900000000001E-3]
[null,"14/07/2016","04:39:00","ST13","Rural Short","Weather",null,263,371.22433460076047,0.78803199999999995,2.1227899999999998E-3]
[null,"14/07/2016","07:54:00","CV30","Rural Long","Unknown","Unknown",15,461,4.9058999999999998E-2,1.0642E-4]
[null,"14/07/2016","08:29:08","AP351E","Urban","Planned",null,69,192,2.1784000000000001E-2,1.1346E-4]
[null,"14/07/2016","08:37:09","AP351E","Urban","Planned",null,63,185,1.9164E-2,1.0359E-4]
[null,"14/07/2016","08:44:46","EL09","Urban","Planned",null,42,357,2.4655E-2,6.9060000000000006E-5]
[null,"14/07/2016","09:09:40","AP226C","Urban","Planned",null,53,199,1.7342E-2,8.7150000000000004E-5]
[null,"14/07/2016","09:13:20","MTB32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",0.99999899999999997,246.99999999999997,1.7520000000000001E-3,7.0899999999999999E-6]
[null,"14/07/2016","09:33:11","ME131E","Urban","Vegetation","Grow-in - NSP responsibility",1,131,2.1499999999999999E-4,1.64E-6]
[null,"14/07/2016","10:30:00","G38","Rural Long","Planned",null,2,135,1.916E-3,1.419E-5]
[null,"14/07/2016","10:45:00","G41","Rural Long","Planned",null,45,115.00000000000001,3.6714999999999998E-2,3.1925999999999998E-4]
[null,"14/07/2016","12:05:49","MG52","Urban","Planned",null,41,125,8.4270000000000005E-3,6.7420000000000002E-5]
[null,"14/07/2016","12:21:00","MG52","Urban","Unknown","Unknown",41,73.999999999999986,4.9890000000000004E-3,6.7420000000000002E-5]
[null,"14/07/2016","14:08:03","AP365A","Urban","Asset failure","LV",29,810,3.8623999999999999E-2,4.7679999999999998E-5]
[null,"14/07/2016","14:21:00","NU04","Rural Short","Unknown","Unknown",23.000010000000003,109.99999999999997,2.0421000000000002E-2,1.8563999999999999E-4]
[null,"14/07/2016","19:31:00","SB02","Rural Long","Unknown","Unknown",2,803.99999999999989,1.1408E-2,1.419E-5]
[null,"14/07/2016","20:21:00","NL210E","Urban","Planned",null,396,63.318181818181813,4.1229000000000002E-2,6.5114000000000003E-4]
[null,"14/07/2016","21:31:10","AP226D","Urban","Overloads",null,1,408,6.7100000000000005E-4,1.64E-6]
[null,"14/07/2016","21:42:46","HH409D","Urban","Asset failure","LV",1,165,2.7099999999999997E-4,1.64E-6]
[null,"14/07/2016","23:29:33","SM410C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",19.999980000000001,139,4.5710000000000004E-3,3.2889999999999999E-5]
[null,"15/07/2016","07:10:23","KA03","Rural Long","Planned",null,30,60,1.277E-2,2.1284E-4]
[null,"15/07/2016","07:11:22","KA03","Rural Long","Planned",null,54,59,2.2603999999999999E-2,3.8310999999999998E-4]
[null,"15/07/2016","07:41:00","GA37","Rural Long","Unknown","Unknown",6,272,1.1578E-2,4.2570000000000001E-5]
[null,"15/07/2016","07:53:00","GU43","Rural Long","Unknown","Unknown",32,39,8.8540000000000008E-3,2.2703E-4]
[null,"15/07/2016","08:35:00","NA51","Rural Long","Asset failure","Distribution substation",9,1666.6666666666667,0.10642,6.3849999999999993E-5]
[null,"15/07/2016","09:00:00","MI20","Rural Long","Planned",null,40,324.99999999999994,9.2230000000000006E-2,2.8379000000000002E-4]
[null,"15/07/2016","09:27:00","AP365B","Urban","Planned",null,82,343,4.6247000000000003E-2,1.3483000000000001E-4]
[null,"15/07/2016","10:43:00","ME347G","Urban","Third Party","Vehicle impact",759,352,0.439303,1.2480200000000001E-3]
[null,"15/07/2016","10:57:00","BT03","Rural Long","Unknown","Unknown",169,11,1.3188999999999999E-2,1.19899E-3]
[null,"15/07/2016","11:46:00","MI14","Rural Long","Asset failure","Distribution substation",49,145.53061224489795,5.0591999999999998E-2,3.4764000000000003E-4]
[null,"15/07/2016","12:09:00","MTB22","Rural Short","Unknown","Unknown",35,87,2.4577999999999999E-2,2.8249999999999998E-4]
[null,"15/07/2016","15:22:29","NL210B","Urban","Asset failure","LV",68,685,7.6591000000000006E-2,1.1181E-4]
[null,"15/07/2016","18:19:39","SA18","Urban","Asset failure","LV",1,393,6.4599999999999998E-4,1.64E-6]
[null,"15/07/2016","18:51:02","G15","Rural Long","Unknown","Unknown",1,789,5.5979999999999997E-3,7.0899999999999999E-6]
[null,"15/07/2016","19:28:00","AP226B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",269,7,3.0959999999999998E-3,4.4232000000000001E-4]
[null,"15/07/2016","22:22:00","HH522A","Urban","Third Party","Vehicle impact",461,6,4.548E-3,7.5801999999999998E-4]
[null,"15/07/2016","22:22:00","HH522A","Urban","Third Party","Vehicle impact",null,6,4.548E-3,0]
[null,"16/07/2016","06:59:00","SD343","Rural Short","Unknown","Unknown",101,153,0.12472800000000001,8.1521999999999996E-4]
[null,"16/07/2016","07:11:00","R18","Rural Long","Unknown","Unknown",14.333335,203.00000000000003,2.0643000000000002E-2,1.0169E-4]
[null,"16/07/2016","07:38:00","EL01Q","Urban","Asset failure","HV",6.0000030000000004,382,3.7690000000000002E-3,9.8700000000000004E-6]
[null,"16/07/2016","08:16:03","SB23","Rural Long","Asset failure","LV",2,586,8.3149999999999995E-3,1.419E-5]
[null,"16/07/2016","08:56:50","WHY02","Urban","Overloads",null,1,210.00000000000003,3.4499999999999998E-4,1.64E-6]
[null,"16/07/2016","14:30:00","VH21","Rural Short","Asset failure","Distribution substation",1975,99.753924050632904,1.5901879999999999,1.5941110000000001E-2]
[null,"16/07/2016","15:39:00","BM53","Rural Short","Unknown","Unknown",14,57,6.4409999999999997E-3,1.13E-4]
[null,"16/07/2016","15:53:00","LX41","Rural Short","Unknown","Unknown",18,132,1.9178000000000001E-2,1.4529000000000001E-4]
[null,"16/07/2016","18:38:00","HH496B","Urban","Unknown","Unknown",24.999975999999997,1,4.1E-5,4.1109999999999998E-5]
[null,"16/07/2016","19:08:00","MT17","Rural Short","Unknown","Unknown",30.666682000000002,100,2.4752E-2,2.4751999999999999E-4]
[null,"16/07/2016","21:10:00","W06","Rural Long","Animal","Animal nesting/burrowing, etc and other",2,802,1.1379999999999999E-2,1.419E-5]
[null,"16/07/2016","21:40:49","MV13","Rural Short","Asset failure","LV",13.999986,186.00000000000003,2.1017999999999998E-2,1.13E-4]
[null,"16/07/2016","23:40:05","HH145E","Urban","Asset failure","LV",1,212,3.4900000000000003E-4,1.64E-6]
[null,"17/07/2016","02:04:29","CBD412S","Urban","Overloads",null,15,125,3.0829999999999998E-3,2.4660000000000001E-5]
[null,"17/07/2016","04:56:00","CD17","Rural Long","Weather",null,76,981.00000000000011,0.52894799999999997,5.3919000000000005E-4]
[null,"17/07/2016","07:24:15","ME347F","Urban","Planned",null,11,292.99999999999994,5.3E-3,1.8090000000000001E-5]
[null,"17/07/2016","07:47:52","NL21","Urban","Asset failure","LV",1,183.00000000000003,3.01E-4,1.64E-6]
[null,"17/07/2016","08:32:57","HH432A","Urban","Planned",null,59,436.99999999999994,4.2395000000000002E-2,9.7009999999999994E-5]
[null,"17/07/2016","08:49:00","SM374A","Urban","Planned",null,33,271,1.4704999999999999E-2,5.4259999999999999E-5]
[null,"17/07/2016","09:11:00","GA50","Urban","Planned",null,23,335.00000000000006,1.2669E-2,3.782E-5]
[null,"17/07/2016","09:32:57","BM54","Rural Short","Asset failure","LV",1,96,7.7499999999999997E-4,8.0700000000000007E-6]
[null,"17/07/2016","09:48:00","HH409E","Urban","Planned",null,46,347,2.6245999999999998E-2,7.5640000000000001E-5]
[null,"17/07/2016","10:17:00","MB31","Rural Long","Unknown","Unknown",652,50.881901840490791,0.23536499999999999,4.6257E-3]
[null,"17/07/2016","10:53:55","ME231A","Urban","Asset failure","LV",1,73,1.2E-4,1.64E-6]
[null,"17/07/2016","11:08:00","M61","Rural Long","Unknown","Unknown",199,205.99999999999997,0.29083799999999999,1.41183E-3]
[null,"17/07/2016","12:14:35","NL115A","Urban","Planned",null,55,66,5.9690000000000003E-3,9.0439999999999995E-5]
[null,"17/07/2016","12:20:00","MT22","Rural Long","Third Party","Other",639,129.34898278560252,0.58640000000000003,4.5334700000000004E-3]
[null,"17/07/2016","12:42:00","NA05","Rural Long","Unknown","Unknown",12.333335999999999,172,1.5049999999999999E-2,8.7499999999999999E-5]
[null,"17/07/2016","15:32:00","ST42","Rural Long","Unknown","Unknown",2.666668,282,5.3350000000000003E-3,1.8919999999999998E-5]
[null,"17/07/2016","16:27:42","NL115F","Urban","Asset failure","LV",24,83,3.2750000000000001E-3,3.9459999999999998E-5]
[null,"17/07/2016","18:23:02","SA17","Urban","Overloads",null,1,344.00000000000006,5.6599999999999999E-4,1.64E-6]
[null,"17/07/2016","18:39:34","NL115D","Urban","Asset failure","LV",14.333318999999999,474,1.1171E-2,2.357E-5]
[null,"17/07/2016","23:48:00","GA36","Rural Long","Unknown","Unknown",3,37,7.8799999999999996E-4,2.128E-5]
[null,"18/07/2016","06:10:00","M13","Rural Long","Unknown","Unknown",918,9.1732026143790861,5.9743999999999998E-2,6.5128800000000004E-3]
[null,"18/07/2016","08:21:37","HH145B","Urban","Planned",null,28,204,9.3919999999999993E-3,4.604E-5]
[null,"18/07/2016","09:14:00","EL260C","Urban","Planned",null,28,136,6.2610000000000001E-3,4.604E-5]
[null,"18/07/2016","09:19:00","LX41","Rural Short","Planned",null,7,8,4.5199999999999998E-4,5.6499999999999998E-5]
[null,"18/07/2016","09:25:00","MV11","Rural Short","Planned",null,1,160,1.291E-3,8.0700000000000007E-6]
[null,"18/07/2016","09:51:00","GA27","Rural Long","Planned",null,84,185.00000000000003,0.110251,5.9595000000000004E-4]
[null,"18/07/2016","10:07:12","MT07","Rural Long","Planned",null,7,276,1.3707E-2,4.9660000000000002E-5]
[null,"18/07/2016","10:08:00","SA31","Urban","Planned",null,667,83.317841079460266,9.1378000000000001E-2,1.0967399999999999E-3]
[null,"18/07/2016","10:12:00","VH51","Rural Short","Planned",null,4,61.999999999999993,2.0019999999999999E-3,3.2289999999999997E-5]
[null,"18/07/2016","10:23:00","HH432C","Urban","Planned",null,59,265,2.5708999999999999E-2,9.7009999999999994E-5]
[null,"18/07/2016","10:52:00","SG04","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",141,96.333333333333343,0.109634,1.1380699999999999E-3]
[null,"18/07/2016","10:57:00","BT37","Rural Long","Planned",null,2,56.999999999999993,8.0900000000000004E-4,1.419E-5]
[null,"18/07/2016","11:00:00","AP424C","Urban","Planned",null,197,5,1.6199999999999999E-3,3.2393E-4]
[null,"18/07/2016","11:25:00","MT07","Rural Long","Planned",null,4,109,3.0929999999999998E-3,2.8379999999999999E-5]
[null,"18/07/2016","11:30:00","NA05","Rural Long","Unknown","Unknown",74,77,4.0425000000000003E-2,5.2499999999999997E-4]
[null,"18/07/2016","11:43:00","NL21","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",599,97,9.5537999999999998E-2,9.8492999999999996E-4]
[null,"18/07/2016","12:20:00","VH51","Rural Short","Planned",null,4,166,5.359E-3,3.2289999999999997E-5]
[null,"18/07/2016","12:37:00","MV11","Rural Short","Planned",null,1,15,1.21E-4,8.0700000000000007E-6]
[null,"18/07/2016","13:13:00","SM350H","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1327,9,1.9637999999999999E-2,2.18198E-3]
[null,"18/07/2016","13:36:00","VH51","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",77,19,1.1809E-2,6.2149999999999998E-4]
[null,"18/07/2016","13:45:00","M01","Rural Long","Unknown","Unknown",2,10,1.4200000000000001E-4,1.419E-5]
[null,"18/07/2016","15:28:29","MB92","Rural Long","Asset failure","LV",5,59,2.0929999999999998E-3,3.5469999999999998E-5]
[null,"18/07/2016","16:48:00","NA05","Rural Long","Unknown","Unknown",59.333348000000001,112.61235937672012,4.7404000000000002E-2,4.2095000000000001E-4]
[null,"18/07/2016","17:23:00","NL210A","Urban","Asset failure","Distribution substation",91,61,9.1269999999999997E-3,1.4962999999999999E-4]
[null,"18/07/2016","18:54:00","SD322","Rural Long","Asset failure","Subtransmission",210,166,0.24731900000000001,1.4898699999999999E-3]
[null,"18/07/2016","21:32:08","SA32","Urban","Overloads",null,1,192,3.1599999999999998E-4,1.64E-6]
[null,"18/07/2016","21:54:13","HH341G","Urban","Asset failure","LV",77,141,1.7852E-2,1.2661000000000001E-4]
[null,"19/07/2016","08:25:37","NL210D","Urban","Planned",null,60,59,5.8209999999999998E-3,9.8659999999999994E-5]
[null,"19/07/2016","08:33:48","HH432A","Urban","Planned",null,59,409,3.9677999999999998E-2,9.7009999999999994E-5]
[null,"19/07/2016","08:39:00","GA47","Rural Long","Planned",null,7,94.999999999999986,4.718E-3,4.9660000000000002E-5]
[null,"19/07/2016","08:41:15","MV62","Rural Short","Planned",null,36,395,0.114776,2.9056999999999998E-4]
[null,"19/07/2016","08:45:18","MV62","Rural Short","Planned",null,36,392,0.11390400000000001,2.9056999999999998E-4]
[null,"19/07/2016","08:47:00","MT02","Rural Long","Planned",null,63,300,0.13408900000000001,4.4695999999999999E-4]
[null,"19/07/2016","08:52:41","NL511A","Urban","Planned",null,24,332,1.3102000000000001E-2,3.9459999999999998E-5]
[null,"19/07/2016","08:56:00","SB18","Rural Long","Planned",null,23,110.99999999999999,1.8113000000000001E-2,1.6317999999999999E-4]
[null,"19/07/2016","09:11:22","EL10","Urban","Planned",null,37,115,6.9959999999999996E-3,6.084E-5]
[null,"19/07/2016","09:26:00","AP125B","Urban","Planned",null,918,38.249455337690634,5.7736000000000003E-2,1.50946E-3]
[null,"19/07/2016","09:27:00","CD03","Rural Short","Planned",null,1,84.999999999999986,6.8599999999999998E-4,8.0700000000000007E-6]
[null,"19/07/2016","09:37:00","NL511A","Urban","Planned",null,44,260,1.8811000000000001E-2,7.2349999999999997E-5]
[null,"19/07/2016","09:41:00","LX43","Rural Short","Planned",null,10,175.99999999999997,1.4206E-2,8.0710000000000005E-5]
[null,"19/07/2016","09:57:00","MT20","Rural Long","Planned",null,2,49,6.9499999999999998E-4,1.419E-5]
[null,"19/07/2016","10:19:00","HH148C","Urban","Planned",null,173,181.00000000000003,5.1487999999999999E-2,2.8446E-4]
[null,"19/07/2016","10:36:00","GU23","Rural Long","Planned",null,1,138,9.7900000000000005E-4,7.0899999999999999E-6]
[null,"19/07/2016","11:40:00","SD311","Rural Long","Animal","Animal impact",2,94,1.3339999999999999E-3,1.419E-5]
[null,"19/07/2016","11:45:00","MB33","Rural Long","Planned",null,1,70,4.9700000000000005E-4,7.0899999999999999E-6]
[null,"19/07/2016","13:50:00","NA57","Rural Long","Asset failure","HV",3,59,1.256E-3,2.128E-5]
[null,"19/07/2016","16:58:00","MB02","Rural Long","Unknown","Unknown",2,50.999999999999993,7.2400000000000003E-4,1.419E-5]
[null,"19/07/2016","18:50:00","HH102B","Urban","Asset failure","HV",26.666640000000001,124,5.437E-3,4.3850000000000002E-5]
[null,"19/07/2016","23:48:56","NL451A","Urban","Asset failure","LV",14.666651999999999,111.00000000000003,2.6770000000000001E-3,2.4119999999999999E-5]
[null,"20/07/2016","07:39:00","ST36","Rural Long","Unknown","Unknown",9.6666690000000006,234,1.6048E-2,6.8579999999999997E-5]
[null,"20/07/2016","08:00:31","ST34","Rural Long","Weather",null,2,476.99999999999994,6.7679999999999997E-3,1.419E-5]
[null,"20/07/2016","08:08:00","MT07","Rural Long","Planned",null,26,341.99999999999994,6.3086000000000003E-2,1.8446000000000001E-4]
[null,"20/07/2016","08:57:34","HH409C","Urban","Planned",null,40,257.99999999999994,1.6969000000000001E-2,6.5770000000000002E-5]
[null,"20/07/2016","09:37:00","SA41","Urban","Planned",null,23,238.00000000000003,9.0010000000000003E-3,3.782E-5]
[null,"20/07/2016","09:42:53","AP226D","Urban","Planned",null,47,198,1.5302E-2,7.7280000000000005E-5]
[null,"20/07/2016","09:55:00","W29","Rural Long","Planned",null,40,239.99999999999997,6.8109000000000003E-2,2.8379000000000002E-4]
[null,"20/07/2016","09:55:00","KI11","Rural Long","Planned",null,24,117,1.9921999999999999E-2,1.7027000000000001E-4]
[null,"20/07/2016","10:00:00","M22","Rural Long","Unknown","Unknown",1,40,2.8400000000000002E-4,7.0899999999999999E-6]
[null,"20/07/2016","10:16:00","CM09","Rural Long","Planned",null,27,269,5.1527999999999997E-2,1.9155999999999999E-4]
[null,"20/07/2016","11:16:55","NL115D","Urban","Planned",null,33,149,8.0850000000000002E-3,5.4259999999999999E-5]
[null,"20/07/2016","11:22:00","ME131D","Urban","Unknown","Unknown",1,12788,2.1027000000000001E-2,1.64E-6]
[null,"20/07/2016","11:31:57","EL14","Urban","Planned",null,45,58,4.2919999999999998E-3,7.3990000000000001E-5]
[null,"20/07/2016","12:34:00","HH403B","Urban","Third Party","Vehicle impact",2343,78.620998719590276,0.302894,3.85258E-3]
[null,"20/07/2016","13:28:00","MB20","Rural Short","Planned",null,1,472,3.81E-3,8.0700000000000007E-6]
[null,"20/07/2016","13:55:00","CN52","Rural Long","Unknown","Unknown",1,13,9.2E-5,7.0899999999999999E-6]
[null,"20/07/2016","23:09:11","NL111Q","Urban","Overloads",null,1,104,1.7100000000000001E-4,1.64E-6]
[null,"21/07/2016","05:28:00","R01","Rural Long","Asset failure","Distribution substation",140,372.75714285714281,0.37024099999999999,9.9324999999999999E-4]
[null,"21/07/2016","08:20:00","GA10","Rural Long","Planned",null,1,34,2.41E-4,7.0899999999999999E-6]
[null,"21/07/2016","08:33:00","MG34","Rural Long","Planned",null,36,339,8.6582999999999993E-2,2.5541000000000002E-4]
[null,"21/07/2016","08:45:00","NL115F","Urban","Planned",null,200,21,6.9059999999999998E-3,3.2885999999999999E-4]
[null,"21/07/2016","08:51:44","PL03","Urban","Planned",null,44,205.99999999999997,1.4904000000000001E-2,7.2349999999999997E-5]
[null,"21/07/2016","08:52:00","KA17","Rural Long","Planned",null,1,66,4.6799999999999999E-4,7.0899999999999999E-6]
[null,"21/07/2016","08:52:22","PL07","Urban","Planned",null,37,205,1.2472E-2,6.084E-5]
[null,"21/07/2016","08:57:00","MV64","Rural Short","Planned",null,263,323.0836501901141,0.68583899999999998,2.1227899999999998E-3]
[null,"21/07/2016","09:00:00","MT02","Rural Long","Planned",null,130,255,0.23518700000000001,9.2230000000000003E-4]
[null,"21/07/2016","09:02:00","HH522B","Urban","Planned",null,1,363,5.9699999999999998E-4,1.64E-6]
[null,"21/07/2016","09:03:00","HH409F","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",194,163.95876288659792,5.2302000000000001E-2,3.1899000000000001E-4]
[null,"21/07/2016","09:04:12","HH496A","Urban","Planned",null,25,137,5.6319999999999999E-3,4.1109999999999998E-5]
[null,"21/07/2016","09:06:00","EL10","Urban","Planned",null,137,64.12408759124088,1.4445E-2,2.2526999999999999E-4]
[null,"21/07/2016","09:06:18","KI11","Rural Long","Planned",null,28,314,6.2376000000000001E-2,1.9865E-4]
[null,"21/07/2016","09:10:00","HH409F","Urban","Planned",null,1,327,5.3799999999999996E-4,1.64E-6]
[null,"21/07/2016","09:10:23","AP365C","Urban","Planned",null,70,380,4.3737999999999999E-2,1.1510000000000001E-4]
[null,"21/07/2016","09:27:00","CD01","Rural Short","Planned",null,45,265,9.6252000000000004E-2,3.6321999999999998E-4]
[null,"21/07/2016","09:27:00","GU118","Rural Long","Planned",null,77,323,0.176451,5.4628999999999995E-4]
[null,"21/07/2016","09:51:00","W24","Rural Long","Planned",null,68,246,0.11867900000000001,4.8244E-4]
[null,"21/07/2016","10:05:00","GA07","Rural Long","Planned",null,3,56,1.1919999999999999E-3,2.128E-5]
[null,"21/07/2016","10:14:25","MI14","Rural Long","Planned",null,42,291,8.6710999999999996E-2,2.9796999999999999E-4]
[null,"21/07/2016","10:17:00","NA52","Rural Long","Planned",null,75,102.46666666666667,5.4522000000000001E-2,5.3209999999999998E-4]
[null,"21/07/2016","10:27:00","SM349H","Urban","Planned",null,229,373,0.14045099999999999,3.7654000000000002E-4]
[null,"21/07/2016","10:31:00","SM126B","Urban","Planned",null,28,223,1.0267E-2,4.604E-5]
[null,"21/07/2016","11:24:00","GU21","Rural Long","Animal","Animal impact",3.0000010000000001,426,9.0670000000000004E-3,2.128E-5]
[null,"21/07/2016","12:09:00","ME347C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2549,64.7995292271479,0.27159499999999998,4.1913100000000002E-3]
[null,"21/07/2016","12:29:00","MV41","Rural Short","Asset failure","HV",356,69,0.198267,2.8734400000000001E-3]
[null,"21/07/2016","13:30:00","R35","Rural Long","Asset failure","HV",41,45,1.3089999999999999E-2,2.9087999999999998E-4]
[null,"21/07/2016","15:11:00","MG06","Rural Short","Asset failure","Distribution substation",2,98,1.5820000000000001E-3,1.6140000000000001E-5]
[null,"21/07/2016","16:35:00","WHY17","Rural Short","Asset failure","HV",4,90,2.9060000000000002E-3,3.2289999999999997E-5]
[null,"21/07/2016","17:02:48","G32","Rural Long","Other",null,1.333332,1183,1.1191E-2,9.4599999999999992E-6]
[null,"21/07/2016","17:47:57","SM349B","Urban","Overloads",null,1,454,7.4700000000000005E-4,1.64E-6]
[null,"21/07/2016","18:08:15","G41","Rural Long","Overloads",null,1,1049,7.4419999999999998E-3,7.0899999999999999E-6]
[null,"21/07/2016","18:52:00","MT09","Rural Long","Asset failure","HV",1,14,9.8999999999999994E-5,7.0899999999999999E-6]
[null,"21/07/2016","20:09:58","NL760B","Urban","Asset failure","LV",1,346,5.6899999999999995E-4,1.64E-6]
[null,"21/07/2016","20:28:00","R01","Rural Long","Unknown","Unknown",140,240.29285714285714,0.23867099999999999,9.9324999999999999E-4]
[null,"21/07/2016","21:39:00","MB65","Rural Long","Unknown","Unknown",2,5.9999999999999991,8.5000000000000006E-5,1.419E-5]
[null,"21/07/2016","22:17:00","MT08","Rural Long","Asset failure","LV",1,224,1.5889999999999999E-3,7.0899999999999999E-6]
[null,"21/07/2016","22:25:54","MI08","Rural Long","Asset failure","LV",9.3333239999999993,241.00000000000003,1.5958E-2,6.622E-5]
[null,"21/07/2016","22:51:04","EL18","Urban","Asset failure","LV",16.999983,109.99999999999999,3.075E-3,2.7949999999999998E-5]
[null,"21/07/2016","23:58:59","HH341J","Urban","Asset failure","LV",55,179.99999999999997,1.6278999999999998E-2,9.0439999999999995E-5]
[null,"22/07/2016","01:26:00","MTB53","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",226,148,0.23730100000000001,1.6033899999999999E-3]
[null,"22/07/2016","07:59:00","MT07","Rural Long","Planned",null,103,354,0.258685,7.3074999999999995E-4]
[null,"22/07/2016","08:13:24","SA31","Urban","Planned",null,41,409,2.7573E-2,6.7420000000000002E-5]
[null,"22/07/2016","08:13:41","EL14","Urban","Planned",null,76,51,6.3730000000000002E-3,1.2496999999999999E-4]
[null,"22/07/2016","08:15:22","SA31","Urban","Planned",null,29,408,1.9455E-2,4.7679999999999998E-5]
[null,"22/07/2016","08:29:51","SA31","Urban","Planned",null,38,394,2.4618000000000001E-2,6.2479999999999998E-5]
[null,"22/07/2016","08:30:00","KA08","Rural Long","Planned",null,2,104.99999999999999,1.49E-3,1.419E-5]
[null,"22/07/2016","08:30:53","SA31","Urban","Planned",null,35,393,2.2617000000000002E-2,5.7550000000000003E-5]
[null,"22/07/2016","08:31:15","SA31","Urban","Planned",null,24,393,1.5509E-2,3.9459999999999998E-5]
[null,"22/07/2016","08:32:16","SA31","Urban","Planned",null,19,392,1.2246999999999999E-2,3.1239999999999999E-5]
[null,"22/07/2016","08:33:10","SA31","Urban","Planned",null,34,391,2.1859E-2,5.5909999999999998E-5]
[null,"22/07/2016","08:33:39","SA31","Urban","Planned",null,43,390.99999999999994,2.7646E-2,7.0699999999999997E-5]
[null,"22/07/2016","08:34:07","SA31","Urban","Planned",null,25,390.99999999999994,1.6073E-2,4.1109999999999998E-5]
[null,"22/07/2016","08:34:36","SA31","Urban","Planned",null,43,390.99999999999994,2.7646E-2,7.0699999999999997E-5]
[null,"22/07/2016","08:39:00","PA06","Rural Long","Planned",null,22,269,4.1986000000000002E-2,1.5608000000000001E-4]
[null,"22/07/2016","08:39:22","BM43","Rural Short","Planned",null,10,152,1.2269E-2,8.0710000000000005E-5]
[null,"22/07/2016","08:47:00","NA62","Rural Long","Unknown","Unknown",1,203.99999999999997,1.4469999999999999E-3,7.0899999999999999E-6]
[null,"22/07/2016","08:56:11","MV61","Urban","Planned",null,64,205.00000000000003,2.1572999999999998E-2,1.0522999999999999E-4]
[null,"22/07/2016","08:58:00","SA31","Urban","Planned",null,265,340,0.148151,4.3574E-4]
[null,"22/07/2016","09:03:00","EL12","Urban","Unknown","Unknown",2,198.00000000000003,6.5099999999999999E-4,3.2899999999999998E-6]
[null,"22/07/2016","09:11:18","SM349C","Urban","Planned",null,65,240.00000000000003,2.5651E-2,1.0688000000000001E-4]
[null,"22/07/2016","09:14:00","MT13","Rural Long","Planned",null,199,202,0.28519,1.41183E-3]
[null,"22/07/2016","09:21:00","SA36","Urban","Planned",null,14,373,8.5869999999999991E-3,2.302E-5]
[null,"22/07/2016","10:14:45","SG14","Rural Short","Planned",null,41,159.00000000000003,5.2617999999999998E-2,3.3093E-4]
[null,"22/07/2016","10:50:00","MTB53","Rural Long","Weather",null,319,242,0.54769199999999996,2.26319E-3]
[null,"22/07/2016","10:52:12","BM52","Urban","Planned",null,61,83,8.3250000000000008E-3,1.003E-4]
[null,"22/07/2016","11:13:00","NA34","Rural Long","Unknown","Unknown",2.666668,272,5.1460000000000004E-3,1.8919999999999998E-5]
[null,"22/07/2016","11:18:00","LM43","Rural Long","Planned",null,2,21,2.9799999999999998E-4,1.419E-5]
[null,"22/07/2016","11:30:00","NU13","Rural Long","Planned",null,2,86,1.2199999999999999E-3,1.419E-5]
[null,"22/07/2016","11:40:00","R09","Rural Long","Unknown","Unknown",2,72,1.0219999999999999E-3,1.419E-5]
[null,"22/07/2016","13:36:00","ST12","Rural Short","Unknown","Unknown",38,277,8.4959999999999994E-2,3.0672000000000002E-4]
[null,"22/07/2016","13:43:00","EL20","Urban","Unknown","Unknown",643,48.999999999999993,5.1806999999999999E-2,1.0572800000000001E-3]
[null,"22/07/2016","14:22:00","MI02","Rural Short","Asset failure","Distribution substation",1,30.999999999999996,2.5000000000000001E-4,8.0700000000000007E-6]
[null,"22/07/2016","14:49:36","SM172F","Urban","Overloads",null,1,697,1.1460000000000001E-3,1.64E-6]
[null,"22/07/2016","14:53:00","R11","Rural Long","Weather",null,60,64,2.7243E-2,4.2568E-4]
[null,"22/07/2016","15:17:00","GU13","Rural Long","Unknown","Unknown",9.000001000000001,202.99999999999997,1.2962E-2,6.3849999999999993E-5]
[null,"22/07/2016","15:20:00","CV23","Rural Long","Asset failure","Distribution substation",22,1147.2727272727273,0.17906900000000001,1.5608000000000001E-4]
[null,"22/07/2016","15:27:00","CM25","Rural Long","Asset failure","HV",78,383.00000000000006,0.21194499999999999,5.5338000000000002E-4]
[null,"22/07/2016","15:39:48","NL451C","Urban","Asset failure","LV",1,547,8.9899999999999995E-4,1.64E-6]
[null,"22/07/2016","15:49:00","SA12","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",393,216.13740458015269,0.13966999999999999,6.4621000000000004E-4]
[null,"22/07/2016","15:50:00","R01","Rural Long","Unknown","Unknown",140,124.17142857142856,0.123333,9.9324999999999999E-4]
[null,"22/07/2016","15:50:44","AP227B","Urban","Weather",null,1.9999979999999999,1133,3.7260000000000001E-3,3.2899999999999998E-6]
[null,"22/07/2016","16:01:00","GA53","Rural Short","Unknown","Unknown",192.00002599999996,342.64409289715417,0.53100199999999997,1.5497200000000001E-3]
[null,"22/07/2016","16:01:01","HH102B","Urban","Unknown","Unknown",21.999977999999999,692,2.5033E-2,3.6170000000000001E-5]
[null,"22/07/2016","16:04:00","SA33","Urban","Third Party","Other",56,166,1.5285E-2,9.2079999999999999E-5]
[null,"22/07/2016","16:13:00","EL20","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",643,222.99999999999997,0.23577400000000001,1.0572800000000001E-3]
[null,"22/07/2016","16:15:21","HH130C","Urban","Vegetation","Grow-in - NSP responsibility",20.333313,563.99999999999989,1.8856999999999999E-2,3.3429999999999997E-5]
[null,"22/07/2016","16:21:35","SD38101","Rural Long","Asset failure","Subtransmission",1,1159,8.2229999999999994E-3,7.0899999999999999E-6]
[null,"22/07/2016","16:23:46","HH102B","Urban","Asset failure","LV",45.999954000000002,606.99999999999989,4.5912000000000001E-2,7.5640000000000001E-5]
[null,"22/07/2016","16:32:49","AP146A","Urban","Asset failure","LV",3.3333300000000001,418,2.2910000000000001E-3,5.48E-6]
[null,"22/07/2016","16:44:00","WK65","Rural Short","Unknown","Unknown",128,352,0.36366700000000002,1.03315E-3]
[null,"22/07/2016","16:46:32","HH341G","Urban","Vegetation","Grow-in - NSP responsibility",1,1437,2.3630000000000001E-3,1.64E-6]
[null,"22/07/2016","16:47:00","WK21","Rural Short","Weather",null,66,194.27272727272725,0.103492,5.3271999999999998E-4]
[null,"22/07/2016","17:02:00","SG09","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",596,291.1174496644295,1.4004449999999999,4.8105800000000001E-3]
[null,"22/07/2016","17:08:29","HH121D","Urban","Asset failure","LV",1,1416,2.3280000000000002E-3,1.64E-6]
[null,"22/07/2016","17:11:15","ME427E","Urban","Asset failure","LV",1,1126,1.851E-3,1.64E-6]
[null,"22/07/2016","17:15:00","SG01","Rural Short","Weather",null,419,286.48210023866346,0.96886399999999995,3.3819399999999999E-3]
[null,"22/07/2016","17:15:00","SG01","Rural Short","Weather",null,null,4,5.0039999999999998E-3,0]
[null,"22/07/2016","17:28:26","SM216C","Urban","Overloads",null,1,589,9.68E-4,1.64E-6]
[null,"22/07/2016","18:00:00","MV53","Rural Short","Unknown","Unknown",2,1306,2.1083000000000001E-2,1.6140000000000001E-5]
[null,"22/07/2016","18:14:03","W04","Rural Long","Asset failure","LV",1,993,7.045E-3,7.0899999999999999E-6]
[null,"22/07/2016","18:19:00","NL115B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1790,107,0.31493199999999999,2.9432899999999999E-3]
[null,"22/07/2016","18:21:00","AP424D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1057,49.447492904446548,8.5941000000000004E-2,1.7380200000000001E-3]
[null,"22/07/2016","18:23:00","AP214C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",77,364.00000000000006,4.6086000000000002E-2,1.2661000000000001E-4]
[null,"22/07/2016","18:25:00","AP372F","Urban","Unknown","Unknown",1153,260.51604509973981,0.49390499999999998,1.89587E-3]
[null,"22/07/2016","18:28:00","NL210D","Urban","Unknown","Unknown",131,382.99999999999994,8.2499000000000003E-2,2.154E-4]
[null,"22/07/2016","18:28:00","NL210D","Urban","Unknown","Unknown",546,19.999999999999996,1.7956E-2,8.9778000000000004E-4]
[null,"22/07/2016","18:30:00","SA520G","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",28,169,7.7809999999999997E-3,4.604E-5]
[null,"22/07/2016","18:31:00","HH341D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2099,200.36969985707481,0.69155100000000003,3.45137E-3]
[null,"22/07/2016","18:31:08","HH429B","Urban","Unknown","Unknown",32.666682999999999,591,3.1745000000000002E-2,5.3709999999999999E-5]
[null,"22/07/2016","18:32:00","HH386C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1343,228.55174981384957,0.50470800000000005,2.2082899999999999E-3]
[null,"22/07/2016","18:33:43","AP425A","Urban","Weather",null,58.000028999999998,619.00000000000011,5.9033000000000002E-2,9.5370000000000003E-5]
[null,"22/07/2016","18:34:24","AP226D","Urban","Asset failure","LV",1,509.00000000000006,8.3699999999999996E-4,1.64E-6]
[null,"22/07/2016","18:35:00","HH148C","Urban","Unknown","Unknown",118,382.99999999999994,7.4312000000000003E-2,1.9403000000000001E-4]
[null,"22/07/2016","18:35:00","HH148C","Urban","Unknown","Unknown",1283,2,4.2189999999999997E-3,2.1096299999999999E-3]
[null,"22/07/2016","18:37:00","HH130B","Urban","Unknown","Unknown",206,323,0.10940800000000001,3.3871999999999998E-4]
[null,"22/07/2016","18:46:19","HH432C","Urban","Asset failure","LV",11.333322000000001,576,1.0734E-2,1.8640000000000001E-5]
[null,"22/07/2016","19:34:00","W16","Rural Long","Unknown","Unknown",42,112.14285714285715,3.3416000000000001E-2,2.9796999999999999E-4]
[null,"22/07/2016","19:34:00","W16","Rural Long","Unknown","Unknown",null,29,8.4360000000000008E-3,0]
[null,"22/07/2016","19:36:53","ST44","Rural Long","Weather",null,4.6666619999999996,884,2.9267999999999999E-2,3.311E-5]
[null,"22/07/2016","19:40:00","VH43","Rural Short","Unknown","Unknown",109,484.52293577981652,0.42627700000000002,8.7978999999999998E-4]
[null,"22/07/2016","19:50:11","ST15","Rural Short","Animal","Animal impact",2,1290,2.0823999999999999E-2,1.6140000000000001E-5]
[null,"22/07/2016","19:51:00","MI05","Rural Long","Unknown","Unknown",56,193,7.6678999999999997E-2,3.9730000000000001E-4]
[null,"22/07/2016","19:52:28","HH102B","Urban","Vegetation","Grow-in - NSP responsibility",22.666644000000002,425.00000000000006,1.584E-2,3.7270000000000001E-5]
[null,"22/07/2016","20:04:00","KA30","Rural Short","Asset failure","HV",31,659.77419354838719,0.16508500000000001,2.5021E-4]
[null,"22/07/2016","20:25:00","MB33","Rural Long","Asset failure","HV",49,426.85714285714278,0.148391,3.4764000000000003E-4]
[null,"22/07/2016","21:35:07","HH148C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",6.0000030000000004,272,2.6830000000000001E-3,9.8700000000000004E-6]
[null,"22/07/2016","21:42:00","R28","Rural Long","Unknown","Unknown",1,18,1.2799999999999999E-4,7.0899999999999999E-6]
[null,"22/07/2016","22:09:00","ST34","Rural Long","Unknown","Unknown",67,1458,0.69304699999999997,4.7533999999999999E-4]
[null,"22/07/2016","22:20:32","SM374E","Urban","Vegetation","Grow-in - NSP responsibility",1,109,1.7899999999999999E-4,1.64E-6]
[null,"22/07/2016","22:20:34","ME200E","Urban","Vegetation","Grow-in - NSP responsibility",1,182,2.99E-4,1.64E-6]
[null,"22/07/2016","22:35:00","SA744D","Urban","Vegetation","Grow-in - NSP responsibility",32,385,2.0258000000000002E-2,5.2620000000000001E-5]
[null,"22/07/2016","23:17:10","EL10","Urban","Asset failure","LV",1,1428,2.3479999999999998E-3,1.64E-6]
[null,"22/07/2016","23:46:04","EL01L","Urban","Overloads",null,1,974.00000000000011,1.6019999999999999E-3,1.64E-6]
[null,"23/07/2016","02:43:00","CL19","Rural Long","Asset failure","Distribution substation",1,139,9.859999999999999E-4,7.0899999999999999E-6]
[null,"23/07/2016","04:21:00","SSD157","Rural Long","Asset failure","Zone substation",923,151,0.98880100000000004,6.5483499999999997E-3]
[null,"23/07/2016","08:34:00","ST12","Rural Short","Weather",null,2,1928,3.1123999999999999E-2,1.6140000000000001E-5]
[null,"23/07/2016","09:16:00","SSD470","Rural Long","Planned",null,505,134.4990099009901,0.48188199999999998,3.5827900000000002E-3]
[null,"23/07/2016","09:50:00","NA06","Rural Long","Unknown","Unknown",6,24,1.0219999999999999E-3,4.2570000000000001E-5]
[null,"23/07/2016","11:57:00","MTB13","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",12.666670999999999,174,1.7788999999999999E-2,1.0224E-4]
[null,"23/07/2016","13:02:00","GA43","Rural Short","Unknown","Unknown",695,290.46906474820145,1.629432,5.6096599999999998E-3]
[null,"23/07/2016","13:12:00","CV33","Rural Long","Asset failure","Distribution substation",2,101,1.433E-3,1.419E-5]
[null,"23/07/2016","18:15:14","SA14","Urban","Asset failure","LV",1,424,6.9700000000000003E-4,1.64E-6]
[null,"23/07/2016","19:50:51","SA16","Urban","Overloads",null,1,281,4.6200000000000001E-4,1.64E-6]
[null,"23/07/2016","22:57:24","AP149E","Urban","Asset failure","LV",1.9999979999999999,111.99999999999999,3.68E-4,3.2899999999999998E-6]
[null,"23/07/2016","23:33:38","HH177G","Urban","Asset failure","LV",17.999981999999999,268,7.9319999999999998E-3,2.9600000000000001E-5]
[null,"23/07/2016","23:43:09","NL234A","Urban","Asset failure","LV",1,90,1.4799999999999999E-4,1.64E-6]
[null,"24/07/2016","00:42:00","SG09","Rural Short","Asset failure","HV",596,151.43624161073825,0.72849699999999995,4.8105800000000001E-3]
[null,"24/07/2016","08:27:00","SA34","Urban","Planned",null,16,368.37500000000006,9.691E-3,2.6310000000000001E-5]
[null,"24/07/2016","08:27:58","AP132A","Urban","Planned",null,12,100,1.9729999999999999E-3,1.9729999999999999E-5]
[null,"24/07/2016","08:29:11","AP132A","Urban","Planned",null,11,98.999999999999986,1.7910000000000001E-3,1.8090000000000001E-5]
[null,"24/07/2016","08:30:34","AP132A","Urban","Planned",null,25,98,4.0289999999999996E-3,4.1109999999999998E-5]
[null,"24/07/2016","08:31:03","AP132A","Urban","Planned",null,6,98,9.6699999999999998E-4,9.8700000000000004E-6]
[null,"24/07/2016","08:31:40","AP344B","Urban","Planned",null,10,97,1.5950000000000001E-3,1.6439999999999998E-5]
[null,"24/07/2016","09:00:00","VH33","Rural Short","Asset failure","HV",114.666692,116.04651191995667,0.107404,9.2553000000000004E-4]
[null,"24/07/2016","09:06:00","SM402B","Urban","Planned",null,31,268,1.3661E-2,5.0970000000000002E-5]
[null,"24/07/2016","09:26:00","SM374A","Urban","Planned",null,135,330,7.3252999999999999E-2,2.2198000000000001E-4]
[null,"24/07/2016","09:49:00","AP132C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",303,124,6.1779000000000001E-2,4.9821999999999996E-4]
[null,"24/07/2016","09:51:00","AP214A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1223,47,9.4516000000000003E-2,2.0109699999999999E-3]
[null,"24/07/2016","09:51:00","AP351D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",176,45.999999999999993,1.3311999999999999E-2,2.8939999999999999E-4]
[null,"24/07/2016","10:06:00","SM411A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",48,402,3.1727999999999999E-2,7.8930000000000005E-5]
[null,"24/07/2016","10:14:00","HH386B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1599,51.999999999999993,0.13672000000000001,2.6292300000000002E-3]
[null,"24/07/2016","10:42:52","SM179D","Urban","Unknown","Unknown",52,29,2.48E-3,8.5500000000000005E-5]
[null,"24/07/2016","11:17:57","W04","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,242.99999999999997,1.7240000000000001E-3,7.0899999999999999E-6]
[null,"24/07/2016","11:34:00","NA32","Rural Long","Third Party","Other",18,232,2.9627000000000001E-2,1.2769999999999999E-4]
[null,"24/07/2016","11:35:00","M71","Rural Long","Asset failure","HV",48,30,1.0215999999999999E-2,3.4054000000000002E-4]
[null,"24/07/2016","11:46:00","CBD412M","Urban","Planned",null,21,131,4.5230000000000001E-3,3.4530000000000003E-5]
[null,"24/07/2016","12:35:00","PL04","Urban","Unknown","Unknown",495,162.6,0.13234399999999999,8.1393000000000004E-4]
[null,"24/07/2016","13:16:00","HH386G","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1959,97.229709035222044,0.31319399999999997,3.2211700000000002E-3]
[null,"24/07/2016","13:31:00","SD1596","Rural Short","Other",null,1759,82,1.16421,1.4197680000000001E-2]
[null,"24/07/2016","14:24:00","GU17","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",4,98.999999999999986,2.8089999999999999E-3,2.8379999999999999E-5]
[null,"24/07/2016","14:34:24","NU12","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",2,193,2.7390000000000001E-3,1.419E-5]
[null,"24/07/2016","15:46:00","MV31","Rural Short","Asset failure","HV",93,993.05376344086028,0.74543099999999995,7.5064000000000001E-4]
[null,"24/07/2016","16:21:03","PL803C","Urban","Overloads",null,1,525,8.6300000000000005E-4,1.64E-6]
[null,"24/07/2016","16:22:00","HH121C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2243,55.314311190370049,0.20400799999999999,3.6881499999999998E-3]
[null,"24/07/2016","16:31:00","SG12","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",532,185.31578947368419,0.79574800000000001,4.29401E-3]
[null,"24/07/2016","16:41:00","SM350D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",755,64,7.9451999999999995E-2,1.2414399999999999E-3]
[null,"24/07/2016","17:16:00","SM216B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2653,64.944591029023755,0.28330899999999998,4.3623100000000003E-3]
[null,"24/07/2016","17:20:00","VH51","Rural Short","Asset failure","HV",92.666713000000001,196.99999999999994,0.14734700000000001,7.4795000000000005E-4]
[null,"24/07/2016","17:48:00","PL04","Urban","Asset failure","Distribution substation",2,229.00000000000003,7.5299999999999998E-4,3.2899999999999998E-6]
[null,"24/07/2016","18:25:00","ME200D","Urban","Asset failure","HV",1,41.000000000000007,6.7000000000000002E-5,1.64E-6]
[null,"24/07/2016","18:30:00","NL760C","Urban","Unknown","Unknown",47,148,1.1438E-2,7.7280000000000005E-5]
[null,"24/07/2016","18:51:27","SG03","Rural Short","Vegetation","Grow-in - NSP responsibility",1,894,7.2160000000000002E-3,8.0700000000000007E-6]
[null,"24/07/2016","20:10:00","MTB32","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",42,166.00000000000003,4.9464000000000001E-2,2.9796999999999999E-4]
[null,"24/07/2016","20:17:00","GU21","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",209,293.66985645933016,0.435448,1.4827799999999999E-3]
[null,"24/07/2016","20:17:00","GU21","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",null,75,9.7374000000000002E-2,0]
[null,"24/07/2016","20:53:28","CD03","Rural Short","Asset failure","LV",1,868,7.0060000000000001E-3,8.0700000000000007E-6]
[null,"24/07/2016","21:18:00","R13","Rural Long","Unknown","Unknown",40,163.54999999999998,4.6413000000000003E-2,2.8379000000000002E-4]
[null,"24/07/2016","21:46:31","NL760C","Urban","Unknown","Unknown",31.333348999999998,137.00000000000003,7.058E-3,5.1520000000000001E-5]
[null,"24/07/2016","22:22:00","HH118C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1729,51.323886639676118,0.14591299999999999,2.8429900000000001E-3]
[null,"24/07/2016","22:34:17","SA744D","Urban","Asset failure","LV",1,357,5.8699999999999996E-4,1.64E-6]
[null,"24/07/2016","22:48:38","SM126D","Urban","Asset failure","LV",1,97.000000000000014,1.5899999999999999E-4,1.64E-6]
[null,"24/07/2016","23:50:49","HH432B","Urban","Overloads",null,1,158,2.5999999999999998E-4,1.64E-6]
[null,"25/07/2016","01:38:00","MV63","Rural Short","Unknown","Unknown",83,17,1.1389E-2,6.6993E-4]
[null,"25/07/2016","01:41:00","NL111Q","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",103,127,2.1509E-2,1.6935999999999999E-4]
[null,"25/07/2016","07:28:05","KI53","Rural Long","Planned",null,7,217,1.0777E-2,4.9660000000000002E-5]
[null,"25/07/2016","09:13:07","MV61","Urban","Planned",null,64,258,2.7151000000000002E-2,1.0522999999999999E-4]
[null,"25/07/2016","09:13:16","NL511A","Urban","Planned",null,56,83,7.6429999999999996E-3,9.2079999999999999E-5]
[null,"25/07/2016","09:23:00","SD495","Rural Long","Unknown","Unknown",543.00014599999997,4,1.541E-2,3.8523899999999998E-3]
[null,"25/07/2016","09:26:00","GA15","Rural Short","Planned",null,2,228,3.6809999999999998E-3,1.6140000000000001E-5]
[null,"25/07/2016","09:36:00","EL10","Urban","Planned",null,391,5.8976982097186701,3.7919999999999998E-3,6.4291999999999995E-4]
[null,"25/07/2016","09:42:12","G41","Rural Long","Planned",null,25,289,5.1258999999999999E-2,1.7736999999999999E-4]
[null,"25/07/2016","10:28:00","SD495","Rural Long","Unknown","Unknown",543.00014599999997,12.411909185748181,4.7815999999999997E-2,3.8523899999999998E-3]
[null,"25/07/2016","10:28:00","AP125B","Urban","Planned",null,929,45.251883745963397,6.9125000000000006E-2,1.5275499999999999E-3]
[null,"25/07/2016","10:37:15","NL511A","Urban","Planned",null,18,50,1.48E-3,2.9600000000000001E-5]
[null,"25/07/2016","11:23:00","R13","Rural Long","Asset failure","HV",2,502,7.123E-3,1.419E-5]
[null,"25/07/2016","12:17:00","KI55","Rural Long","Asset failure","HV",70,314,0.15594,4.9662000000000003E-4]
[null,"25/07/2016","12:21:00","NL511A","Urban","Planned",null,76,90.999999999999986,1.1372E-2,1.2496999999999999E-4]
[null,"25/07/2016","12:46:00","KI42","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",765,286.9032679738562,1.5571379999999999,5.4273999999999998E-3]
[null,"25/07/2016","13:15:00","MV31","Rural Short","Asset failure","HV",112,114,0.10305599999999999,9.0399999999999996E-4]
[null,"25/07/2016","13:20:00","MI05","Rural Long","Unknown","Unknown",56,125.00000000000001,4.9661999999999998E-2,3.9730000000000001E-4]
[null,"25/07/2016","13:24:00","MG05","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1147,62.874455100261549,0.51164399999999999,8.1375500000000003E-3]
[null,"25/07/2016","13:49:00","CD17","Rural Long","Third Party","Vehicle impact",76,969.10526315789468,0.52253400000000005,5.3919000000000005E-4]
[null,"25/07/2016","14:43:00","MV53","Rural Short","Unknown","Unknown",196,146.81632653061226,0.232264,1.5820000000000001E-3]
[null,"25/07/2016","15:00:36","NL210B","Urban","Planned",null,68,84,9.3919999999999993E-3,1.1181E-4]
[null,"25/07/2016","15:25:00","LC02","Rural Long","Planned",null,18,66,8.4279999999999997E-3,1.2769999999999999E-4]
[null,"25/07/2016","15:34:00","GU42","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1242,99,0.87234299999999998,8.8115399999999997E-3]
[null,"25/07/2016","16:00:00","NA13","Rural Long","Unknown","Unknown",1,59.999999999999993,4.26E-4,7.0899999999999999E-6]
[null,"25/07/2016","16:03:00","MG36","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",157,191.99999999999997,0.213861,1.1138599999999999E-3]
[null,"25/07/2016","16:15:00","HH145A","Urban","Unknown","Unknown",287,1,4.7199999999999998E-4,4.7191000000000003E-4]
[null,"25/07/2016","16:21:43","SG12","Rural Short","Vegetation","Grow-in - NSP responsibility",1,242.99999999999997,1.9610000000000001E-3,8.0700000000000007E-6]
[null,"25/07/2016","16:27:48","GU24","Rural Long","Vegetation","Grow-in - NSP responsibility",1,346,2.4550000000000002E-3,7.0899999999999999E-6]
[null,"25/07/2016","16:30:00","AP146D","Urban","Unknown","Unknown",59.000028999999998,94,9.1190000000000004E-3,9.7009999999999994E-5]
[null,"25/07/2016","17:22:36","SM350F","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",19.333342999999999,414.99999999999994,1.3193E-2,3.1789999999999999E-5]
[null,"25/07/2016","17:27:00","VH51","Rural Short","Asset failure","HV",59.000017999999997,49,2.3335000000000002E-2,4.7622000000000002E-4]
[null,"25/07/2016","18:34:14","SG02","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1357,1.0952999999999999E-2,8.0700000000000007E-6]
[null,"25/07/2016","18:40:13","SG14","Rural Short","Asset failure","LV",1,1195,9.6450000000000008E-3,8.0700000000000007E-6]
[null,"25/07/2016","20:23:45","HH409F","Urban","Asset failure","LV",1,297.00000000000006,4.8799999999999999E-4,1.64E-6]
[null,"25/07/2016","22:02:28","ME116B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,173,2.8400000000000002E-4,1.64E-6]
[null,"25/07/2016","23:39:27","WK31","Rural Short","Overloads",null,1,604,4.875E-3,8.0700000000000007E-6]
[null,"26/07/2016","01:56:00","SM350F","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",29,95,4.5300000000000002E-3,4.7679999999999998E-5]
[null,"26/07/2016","04:50:00","WK72","Rural Short","Asset failure","HV",572,183.05069930069928,0.84512100000000001,4.6168700000000003E-3]
[null,"26/07/2016","07:57:08","MTB32","Rural Long","Asset failure","LV",3,364,7.7470000000000004E-3,2.128E-5]
[null,"26/07/2016","08:18:39","NL115A","Urban","Planned",null,43,115,8.1309999999999993E-3,7.0699999999999997E-5]
[null,"26/07/2016","08:36:25","HH121D","Urban","Planned",null,44,202,1.4614E-2,7.2349999999999997E-5]
[null,"26/07/2016","08:40:00","NA20","Rural Long","Planned",null,1,260,1.8450000000000001E-3,7.0899999999999999E-6]
[null,"26/07/2016","08:46:00","LC02","Rural Long","Planned",null,18,513.00000000000011,6.5512000000000001E-2,1.2769999999999999E-4]
[null,"26/07/2016","09:13:00","SD34405","Rural Long","Planned",null,6,304,1.2940999999999999E-2,4.2570000000000001E-5]
[null,"26/07/2016","09:15:13","HH386B","Urban","Planned",null,27,370,1.6427000000000001E-2,4.4400000000000002E-5]
[null,"26/07/2016","09:26:00","AP529D","Urban","Planned",null,269,180,7.9616999999999993E-2,4.4232000000000001E-4]
[null,"26/07/2016","09:42:00","SA31","Urban","Planned",null,44,264,1.9099999999999999E-2,7.2349999999999997E-5]
[null,"26/07/2016","10:05:17","HH496C","Urban","Planned",null,41,280,1.8877000000000001E-2,6.7420000000000002E-5]
[null,"26/07/2016","10:35:10","MV61","Urban","Planned",null,167,188.99999999999997,5.1899000000000001E-2,2.7460000000000001E-4]
[null,"26/07/2016","11:37:00","SM126C","Urban","Planned",null,164,189,5.0966999999999998E-2,2.6966000000000002E-4]
[null,"26/07/2016","12:10:00","SD522","Rural Long","Planned",null,1,1582,1.1224E-2,7.0899999999999999E-6]
[null,"26/07/2016","12:25:25","NL210D","Urban","Planned",null,60,20.999999999999996,2.0720000000000001E-3,9.8659999999999994E-5]
[null,"26/07/2016","13:26:00","NA20","Rural Long","Planned",null,1,218.99999999999997,1.554E-3,7.0899999999999999E-6]
[null,"26/07/2016","14:12:00","EL01L","Urban","Unknown","Unknown",41.666625000000003,40,2.7399999999999998E-3,6.8510000000000006E-5]
[null,"26/07/2016","14:49:00","SA17","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",870,56,8.0110000000000001E-2,1.4305399999999999E-3]
[null,"26/07/2016","16:17:00","EL12","Urban","Asset failure","HV",1,1313,2.1589999999999999E-3,1.64E-6]
[null,"26/07/2016","16:49:00","GA28","Rural Long","Asset failure","HV",176,333,0.41580299999999998,1.24866E-3]
[null,"26/07/2016","17:09:44","EL01N","Urban","Asset failure","LV",1,601,9.8799999999999995E-4,1.64E-6]
[null,"26/07/2016","17:14:00","SG12","Rural Short","Unknown","Unknown",52.666693000000002,55,2.3380000000000001E-2,4.2509999999999998E-4]
[null,"26/07/2016","17:52:00","GU31","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",944,553.37076271186447,3.7061120000000001,6.6973400000000004E-3]
[null,"26/07/2016","18:02:00","GU42","Rural Long","Unknown","Unknown",1242,447,3.9387590000000001,8.8115399999999997E-3]
[null,"26/07/2016","18:04:51","GU41","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1169,8.2939999999999993E-3,7.0899999999999999E-6]
[null,"26/07/2016","18:46:12","MTB54","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,430,3.0509999999999999E-3,7.0899999999999999E-6]
[null,"26/07/2016","18:53:58","SD38101","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1459,1.0351000000000001E-2,7.0899999999999999E-6]
[null,"26/07/2016","19:06:00","SD381","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,1165,8.2649999999999998E-3,7.0899999999999999E-6]
[null,"26/07/2016","19:25:00","SG01","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",22,149.99999999999997,2.6636E-2,1.7757E-4]
[null,"26/07/2016","20:40:00","NU21","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",2207,130.19483461712733,2.0385740000000001,1.5657870000000001E-2]
[null,"26/07/2016","20:45:00","SG04","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",141,404.33333333333337,0.46016099999999999,1.1380699999999999E-3]
[null,"26/07/2016","20:51:12","AP146C","Urban","Planned",null,69,502,5.6954999999999999E-2,1.1346E-4]
[null,"26/07/2016","21:14:52","HH386E","Urban","Overloads",null,2,183.00000000000003,6.02E-4,3.2899999999999998E-6]
[null,"26/07/2016","22:28:36","GU12","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,98,6.9499999999999998E-4,7.0899999999999999E-6]
[null,"26/07/2016","23:22:19","EL01M","Urban","Overloads",null,18.333314999999999,153,4.6119999999999998E-3,3.0150000000000001E-5]
[null,"27/07/2016","00:36:00","NU20","Rural Long","Unknown","Unknown",883,60,0.37587399999999999,6.2645699999999997E-3]
[null,"27/07/2016","01:03:00","EL01M","Urban","Unknown","Unknown",225.99977500000003,4.0825958565666705,1.5169999999999999E-3,3.7160999999999997E-4]
[null,"27/07/2016","08:28:00","NA20","Rural Long","Planned",null,1,164,1.1640000000000001E-3,7.0899999999999999E-6]
[null,"27/07/2016","08:30:26","BM43","Rural Short","Planned",null,10,170,1.3721000000000001E-2,8.0710000000000005E-5]
[null,"27/07/2016","09:00:00","MG19","Rural Long","Planned",null,107,178,0.13512399999999999,7.5913E-4]
[null,"27/07/2016","09:00:23","SM349F","Urban","Planned",null,47,326.00000000000006,2.5194000000000001E-2,7.7280000000000005E-5]
[null,"27/07/2016","09:01:34","SM349F","Urban","Planned",null,58,324,3.09E-2,9.5370000000000003E-5]
[null,"27/07/2016","09:02:00","SM411E","Urban","Planned",null,31,353,1.7994E-2,5.0970000000000002E-5]
[null,"27/07/2016","09:20:00","ME231C","Urban","Planned",null,42,280.99999999999994,1.9406E-2,6.9060000000000006E-5]
[null,"27/07/2016","09:22:56","HH177G","Urban","Planned",null,30,234,1.1542999999999999E-2,4.9329999999999997E-5]
[null,"27/07/2016","09:53:19","WHY02","Urban","Planned",null,57,153,1.434E-2,9.3720000000000004E-5]
[null,"27/07/2016","09:57:00","GA29","Rural Long","Planned",null,7,268,1.3310000000000001E-2,4.9660000000000002E-5]
[null,"27/07/2016","10:46:15","BT06","Rural Long","Planned",null,38,235.99999999999997,6.3625000000000001E-2,2.6959999999999999E-4]
[null,"27/07/2016","11:06:14","SG01","Rural Short","Asset failure","LV",11,153,1.3584000000000001E-2,8.8789999999999995E-5]
[null,"27/07/2016","11:55:00","NA20","Rural Long","Planned",null,2,165,2.3410000000000002E-3,1.419E-5]
[null,"27/07/2016","12:37:00","AP351C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",595,3,2.9350000000000001E-3,9.7835999999999995E-4]
[null,"27/07/2016","14:24:00","CL28","Rural Long","Unknown","Unknown",1,42,2.9799999999999998E-4,7.0899999999999999E-6]
[null,"27/07/2016","16:49:13","HH386C","Urban","Asset failure","LV",9,429,6.3489999999999996E-3,1.4800000000000001E-5]
[null,"27/07/2016","16:57:00","R07","Rural Short","Asset failure","HV",75,24,1.4529E-2,6.0535999999999999E-4]
[null,"27/07/2016","17:59:00","HH145E","Urban","Asset failure","HV",210.66677200000001,43.531645569620245,1.5079E-2,3.4640000000000002E-4]
[null,"27/07/2016","19:06:00","CV29","Rural Long","Unknown","Unknown",1,36,2.5500000000000002E-4,7.0899999999999999E-6]
[null,"27/07/2016","21:17:41","AP355H","Urban","Planned",null,92,357,5.4004999999999997E-2,1.5128E-4]
[null,"27/07/2016","22:00:00","KI13","Rural Long","Unknown","Unknown",2,39,5.53E-4,1.419E-5]
[null,"27/07/2016","23:38:16","HH118C","Urban","Asset failure","LV",1,118.00000000000001,1.94E-4,1.64E-6]
[null,"28/07/2016","00:46:00","VH32","Rural Short","Asset failure","Distribution substation",38,408.36842105263162,0.125253,3.0672000000000002E-4]
[null,"28/07/2016","00:48:14","SG13","Rural Short","Asset failure","LV",1,142,1.1460000000000001E-3,8.0700000000000007E-6]
[null,"28/07/2016","02:22:00","SM350E","Urban","Animal","Animal impact",826,16.639225181598064,2.2599000000000001E-2,1.35819E-3]
[null,"28/07/2016","04:51:00","SG13","Rural Short","Unknown","Unknown",1382,134.61215629522431,1.5015639999999999,1.115474E-2]
[null,"28/07/2016","06:24:00","NL115B","Urban","Unknown","Unknown",26.666679999999999,230,1.0085E-2,4.3850000000000002E-5]
[null,"28/07/2016","07:11:33","PP03","Urban","Planned",null,72,465,5.5051000000000003E-2,1.1839E-4]
[null,"28/07/2016","08:00:00","MG10","Rural Long","Unknown","Unknown",125,37,3.2813000000000002E-2,8.8683000000000002E-4]
[null,"28/07/2016","08:25:04","AP424B","Urban","Planned",null,110,345,6.2400999999999998E-2,1.8086999999999999E-4]
[null,"28/07/2016","08:26:10","AP424B","Urban","Planned",null,111,340,6.2056E-2,1.8252000000000001E-4]
[null,"28/07/2016","08:26:27","AP424B","Urban","Planned",null,104,339,5.7971000000000002E-2,1.7101E-4]
[null,"28/07/2016","08:27:00","KA04","Rural Long","Planned",null,71,347.99999999999994,0.17529400000000001,5.0372000000000004E-4]
[null,"28/07/2016","08:32:00","SD49201","Rural Long","Planned",null,290,281.99999999999994,0.58020000000000005,2.0574500000000002E-3]
[null,"28/07/2016","08:35:00","BM56","Rural Short","Planned",null,8,393,2.5377E-2,6.457E-5]
[null,"28/07/2016","08:45:00","MV61","Urban","Planned",null,179,346,0.101838,2.9432999999999998E-4]
[null,"28/07/2016","08:47:14","AP149H","Urban","Planned",null,42,367,2.5344999999999999E-2,6.9060000000000006E-5]
[null,"28/07/2016","08:47:27","AP149E","Urban","Planned",null,36,367,2.1724E-2,5.9190000000000001E-5]
[null,"28/07/2016","08:50:00","MTB11","Rural Short","Asset failure","HV",1369,105.24105186267349,1.1628940000000001,1.104981E-2]
[null,"28/07/2016","09:18:00","SA32","Urban","Planned",null,57,188.10526315789474,1.763E-2,9.3720000000000004E-5]
[null,"28/07/2016","09:32:00","ST43","Rural Long","Unknown","Unknown",2,1499.9999999999998,2.1284000000000001E-2,1.419E-5]
[null,"28/07/2016","09:56:00","ST21","Rural Short","Planned",null,196,312,0.493585,1.5820000000000001E-3]
[null,"28/07/2016","10:10:00","NA36","Rural Long","Planned",null,3,567.66666666666674,1.2082000000000001E-2,2.128E-5]
[null,"28/07/2016","10:10:00","LX76","Rural Long","Planned",null,1,11,7.7999999999999999E-5,7.0899999999999999E-6]
[null,"28/07/2016","10:10:00","CV19","Rural Long","Planned",null,60,152,6.4702999999999997E-2,4.2568E-4]
[null,"28/07/2016","10:23:00","SM349C","Urban","Planned",null,181,228.00000000000003,6.7857000000000001E-2,2.9762000000000001E-4]
[null,"28/07/2016","10:30:00","BU11","Rural Short","Planned",null,19,24,3.6809999999999998E-3,1.5336000000000001E-4]
[null,"28/07/2016","12:03:00","HH496C","Urban","Planned",null,479,4,3.15E-3,7.8762000000000005E-4]
[null,"28/07/2016","12:10:00","VH22","Rural Short","Unknown","Unknown",28.333345999999999,167.00000000000003,3.8191000000000003E-2,2.2869000000000001E-4]
[null,"28/07/2016","12:24:00","CM03","Rural Long","Unknown","Unknown",14,186,1.8474000000000001E-2,9.9320000000000005E-5]
[null,"28/07/2016","13:15:00","CM25","Rural Long","Planned",null,2,73,1.036E-3,1.419E-5]
[null,"28/07/2016","13:22:00","CV31","Rural Long","Unknown","Unknown",60,82.000000000000014,3.4906E-2,4.2568E-4]
[null,"28/07/2016","14:21:00","R01","Rural Long","Asset failure","HV",12,33,2.8089999999999999E-3,8.5140000000000001E-5]
[null,"28/07/2016","15:30:00","VH22","Rural Short","Unknown","Unknown",28.333345999999999,213.00000000000003,4.8710999999999997E-2,2.2869000000000001E-4]
[null,"28/07/2016","16:31:00","GA49","Rural Long","Unknown","Unknown",2,23,3.2600000000000001E-4,1.419E-5]
[null,"28/07/2016","17:32:00","SD311","Rural Long","Unknown","Unknown",1,35,2.4800000000000001E-4,7.0899999999999999E-6]
[null,"28/07/2016","18:52:50","NL760B","Urban","Asset failure","LV",1,317,5.2099999999999998E-4,1.64E-6]
[null,"28/07/2016","23:26:18","HH107A","Urban","Asset failure","LV",48,67,5.2880000000000002E-3,7.8930000000000005E-5]
[null,"28/07/2016","23:36:27","ST12","Rural Short","Asset failure","LV",5,190,7.6680000000000003E-3,4.036E-5]
[null,"29/07/2016","08:58:00","HH107C","Urban","Planned",null,149,189,4.6304999999999999E-2,2.4499999999999999E-4]
[null,"29/07/2016","09:02:00","MG17","Rural Long","Animal","Animal impact",2,73,1.036E-3,1.419E-5]
[null,"29/07/2016","09:39:00","MV61","Urban","Planned",null,664,306.96385542168673,0.33514699999999997,1.0918099999999999E-3]
[null,"29/07/2016","09:49:00","SD499","Rural Short","Animal","Animal impact",3,146,3.5349999999999999E-3,2.421E-5]
[null,"29/07/2016","10:02:00","SSD309","Rural Long","Planned",null,5,28,9.9299999999999996E-4,3.5469999999999998E-5]
[null,"29/07/2016","10:06:00","MB44","Rural Long","Planned",null,62,5,2.199E-3,4.3986999999999997E-4]
[null,"29/07/2016","10:07:00","CV25","Rural Long","Planned",null,15,168,1.7878000000000002E-2,1.0642E-4]
[null,"29/07/2016","10:08:00","CD03","Rural Short","Asset failure","HV",714,248.04621848739492,1.429494,5.7630099999999998E-3]
[null,"29/07/2016","10:21:40","HH522C","Urban","Planned",null,1,283,4.6500000000000003E-4,1.64E-6]
[null,"29/07/2016","10:36:00","YK12","Rural Long","Unknown","Unknown",2,29,4.1100000000000002E-4,1.419E-5]
[null,"29/07/2016","11:57:39","AP424F","Urban","Planned",null,94,191,2.9522E-2,1.5456000000000001E-4]
[null,"29/07/2016","11:58:57","AP424B","Urban","Planned",null,91,190,2.843E-2,1.4962999999999999E-4]
[null,"29/07/2016","11:59:39","AP424F","Urban","Planned",null,84,188.99999999999997,2.6105E-2,1.3812000000000001E-4]
[null,"29/07/2016","14:44:00","SD499","Rural Short","Unknown","Unknown",3,194.00000000000003,4.6979999999999999E-3,2.421E-5]
[null,"29/07/2016","16:53:57","BM56","Rural Short","Asset failure","HV",1,1187,9.5809999999999992E-3,8.0700000000000007E-6]
[null,"29/07/2016","18:32:05","NA05","Rural Long","Other",null,2,932,1.3224E-2,1.419E-5]
[null,"29/07/2016","19:35:00","BM56","Rural Short","Unknown","Unknown",3,53.000000000000007,1.2830000000000001E-3,2.421E-5]
[null,"29/07/2016","19:56:00","VH45","Rural Short","Asset failure","HV",3,86.333333333333343,2.091E-3,2.421E-5]
[null,"29/07/2016","20:17:38","KI42","Rural Long","Asset failure","LV",1,239.99999999999997,1.7030000000000001E-3,7.0899999999999999E-6]
[null,"29/07/2016","23:05:00","KI42","Rural Long","Unknown","Unknown",1,50,3.5500000000000001E-4,7.0899999999999999E-6]
[null,"30/07/2016","00:20:00","SA14","Urban","Asset failure","HV",3217,64.782716816910153,0.34268100000000001,5.2896999999999996E-3]
[null,"30/07/2016","03:35:34","CBD366F","CBD","Planned",null,7,151,0.19975399999999999,1.32288E-3]
[null,"30/07/2016","05:28:00","MV42","Rural Short","Third Party","Vehicle impact",30,194.00000000000003,4.6975999999999997E-2,2.4214000000000001E-4]
[null,"30/07/2016","08:33:17","SA36","Urban","Asset failure","LV",1,996,1.6379999999999999E-3,1.64E-6]
[null,"30/07/2016","09:04:00","EL01L","Urban","Unknown","Unknown",100,270,4.4395999999999998E-2,1.6443E-4]
[null,"30/07/2016","09:44:13","MG37","Rural Long","Overloads",null,2,442,6.2719999999999998E-3,1.419E-5]
[null,"30/07/2016","10:46:00","BM56","Rural Short","Unknown","Unknown",3,88.000000000000014,2.1310000000000001E-3,2.421E-5]
[null,"30/07/2016","10:59:00","HH341E","Urban","Unknown","Unknown",2367,104.34136037177863,0.40610099999999999,3.8920500000000002E-3]
[null,"30/07/2016","11:26:00","SG12","Rural Short","Unknown","Unknown",41,157.00000000000003,5.1956000000000002E-2,3.3093E-4]
[null,"30/07/2016","13:10:00","M21","Rural Long","Asset failure","HV",1,14.999999999999998,1.06E-4,7.0899999999999999E-6]
[null,"30/07/2016","13:12:00","MG29","Rural Long","Animal","Animal impact",120,405.63333333333333,0.34533900000000001,8.5136000000000001E-4]
[null,"30/07/2016","17:13:00","AP424E","Urban","Third Party","Vehicle impact",2776,84.083573487031714,0.38380500000000001,4.5645599999999996E-3]
[null,"30/07/2016","18:46:56","SA12","Urban","Asset failure","LV",1,319,5.2499999999999997E-4,1.64E-6]
[null,"30/07/2016","20:40:49","NL451C","Urban","Asset failure","LV",11.999988,272,5.3670000000000002E-3,1.9729999999999999E-5]
[null,"30/07/2016","21:39:00","HH145D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",988,143.63461538461539,0.233344,1.6245599999999999E-3]
[null,"30/07/2016","21:54:00","SSD185","Rural Long","Unknown","Unknown",1862,6,7.9260999999999998E-2,1.321022E-2]
[null,"30/07/2016","22:50:44","GA27","Rural Long","Asset failure","LV",1,89.999999999999986,6.3900000000000003E-4,7.0899999999999999E-6]
[null,"31/07/2016","05:26:00","HH341C","Urban","Planned",null,45,209,1.5465E-2,7.3990000000000001E-5]
[null,"31/07/2016","08:27:00","SB01","Rural Long","Unknown","Unknown",43.333354999999997,164,5.0418999999999999E-2,3.0742999999999998E-4]
[null,"31/07/2016","08:37:14","AP372D","Urban","Planned",null,92,401.00000000000006,6.0661E-2,1.5128E-4]
[null,"31/07/2016","09:27:11","NL115D","Urban","Planned",null,43,211,1.4919E-2,7.0699999999999997E-5]
[null,"31/07/2016","09:40:00","AP365B","Urban","Planned",null,168,286.99999999999994,7.9281000000000004E-2,2.7624000000000003E-4]
[null,"31/07/2016","18:53:23","HH130B","Urban","Overloads",null,1,510.00000000000006,8.3900000000000001E-4,1.64E-6]
[null,"31/07/2016","21:40:11","HH177G","Urban","Asset failure","LV",1,395.00000000000006,6.4899999999999995E-4,1.64E-6]
[null,"31/07/2016","23:57:42","HH177G","Urban","Asset failure","LV",1,231,3.8000000000000002E-4,1.64E-6]
[null,"1/08/2016","03:15:00","WK72","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",240,300,0.58114399999999999,1.9371499999999999E-3]
[null,"1/08/2016","03:51:00","SD421","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",6448,150.85282258064515,7.8510900000000001,5.2044699999999999E-2]
[null,"1/08/2016","08:11:50","NU21","Rural Long","Planned",null,70,165,8.1943000000000002E-2,4.9662000000000003E-4]
[null,"1/08/2016","08:27:45","SA34","Urban","Asset failure","LV",1,1570,2.5820000000000001E-3,1.64E-6]
[null,"1/08/2016","08:28:00","EL01A","Urban","Planned",null,161,155.64596273291923,4.1203999999999998E-2,2.6473000000000002E-4]
[null,"1/08/2016","08:28:59","HH177G","Urban","Planned",null,23,309.00000000000006,1.1686E-2,3.782E-5]
[null,"1/08/2016","08:50:00","MV12","Urban","Planned",null,15,387.99999999999994,9.5700000000000004E-3,2.4660000000000001E-5]
[null,"1/08/2016","09:01:03","HH429C","Urban","Planned",null,98,85,1.3697000000000001E-2,1.6113999999999999E-4]
[null,"1/08/2016","09:15:24","AP424B","Urban","Planned",null,50,82,6.7419999999999997E-3,8.2210000000000001E-5]
[null,"1/08/2016","09:18:00","MB61","Rural Long","Planned",null,51,126.00000000000001,4.5589999999999999E-2,3.6183E-4]
[null,"1/08/2016","09:25:00","HH496F","Urban","Planned",null,119,435,8.5116999999999998E-2,1.9567E-4]
[null,"1/08/2016","09:29:02","NL451C","Urban","Planned",null,48,19,1.5E-3,7.8930000000000005E-5]
[null,"1/08/2016","09:32:00","MT06","Rural Long","Planned",null,239,229,0.388297,1.6956199999999999E-3]
[null,"1/08/2016","10:05:00","NL544A","Urban","Planned",null,72,198,2.3441E-2,1.1839E-4]
[null,"1/08/2016","10:22:00","SA744C","Urban","Planned",null,5,310,2.5490000000000001E-3,8.2199999999999992E-6]
[null,"1/08/2016","10:30:00","BT13","Rural Long","Planned",null,2,13,1.84E-4,1.419E-5]
[null,"1/08/2016","11:21:00","PA11","Rural Long","Planned",null,1,14,9.8999999999999994E-5,7.0899999999999999E-6]
[null,"1/08/2016","11:31:00","R04","Rural Long","Planned",null,22,159,2.4816999999999999E-2,1.5608000000000001E-4]
[null,"1/08/2016","12:10:46","HH429A","Urban","Planned",null,84,22.999999999999996,3.1770000000000001E-3,1.3812000000000001E-4]
[null,"1/08/2016","12:36:00","NA51","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",725,103,0.52979200000000004,5.1436099999999998E-3]
[null,"1/08/2016","13:05:00","NA27","Rural Long","Planned",null,1,119.99999999999999,8.5099999999999998E-4,7.0899999999999999E-6]
[null,"1/08/2016","13:19:00","AP132B","Urban","Planned",null,10,12756.999999999998,0.20976300000000001,1.6439999999999998E-5]
[null,"1/08/2016","14:29:00","CD19","Rural Long","Unknown","Unknown",1,25,1.7699999999999999E-4,7.0899999999999999E-6]
[null,"1/08/2016","16:43:04","EL10","Urban","Asset failure","LV",1,1071,1.761E-3,1.64E-6]
[null,"1/08/2016","18:39:44","EL09","Urban","Asset failure","LV",1,404.00000000000006,6.6399999999999999E-4,1.64E-6]
[null,"1/08/2016","19:13:00","NU18","Rural Long","Unknown","Unknown",542,173.40774907749079,0.66680399999999995,3.8452899999999999E-3]
[null,"1/08/2016","20:42:59","WHY03","Urban","Asset failure","LV",11.666655,256,4.9109999999999996E-3,1.9179999999999999E-5]
[null,"1/08/2016","22:47:00","SG07","Rural Short","Unknown","Unknown",88,118.99999999999999,8.4524000000000002E-2,7.1029000000000003E-4]
[null,"2/08/2016","08:19:39","CBD366J","CBD","Planned",null,20,218,0.823963,3.7796499999999999E-3]
[null,"2/08/2016","08:34:35","MV61","Urban","Planned",null,73,254,3.0488999999999999E-2,1.2003E-4]
[null,"2/08/2016","08:44:28","AP344E","Urban","Planned",null,80,238.99999999999997,3.1439000000000002E-2,1.3154E-4]
[null,"2/08/2016","08:45:00","NU03","Rural Long","Planned",null,2,52,7.3800000000000005E-4,1.419E-5]
[null,"2/08/2016","08:54:14","GA26","Urban","Asset failure","LV",1,970,1.5950000000000001E-3,1.64E-6]
[null,"2/08/2016","09:04:08","HH121D","Urban","Planned",null,44,160,1.1575999999999999E-2,7.2349999999999997E-5]
[null,"2/08/2016","09:26:00","SM179D","Urban","Planned",null,92,249,3.7668E-2,1.5128E-4]
[null,"2/08/2016","09:34:53","HH496F","Urban","Planned",null,44,119.99999999999999,8.6820000000000005E-3,7.2349999999999997E-5]
[null,"2/08/2016","09:52:00","NU25","Rural Long","Planned",null,4,88,2.4970000000000001E-3,2.8379999999999999E-5]
[null,"2/08/2016","10:19:00","G14","Rural Long","Planned",null,99,149,0.104653,7.0237000000000001E-4]
[null,"2/08/2016","10:20:00","MI13","Rural Long","Planned",null,2,236.99999999999997,3.3630000000000001E-3,1.419E-5]
[null,"2/08/2016","10:21:53","EL14","Urban","Planned",null,18,75,2.2200000000000002E-3,2.9600000000000001E-5]
[null,"2/08/2016","10:37:00","ME427B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",149,65.348993288590606,1.601E-2,2.4499999999999999E-4]
[null,"2/08/2016","11:14:00","G02","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",930,292.52580645161294,1.9300889999999999,6.5980099999999996E-3]
[null,"2/08/2016","11:54:00","ME116C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1572,71,0.18352299999999999,2.5848300000000002E-3]
[null,"2/08/2016","12:04:26","AP125B","Urban","Planned",null,1,28.000000000000004,4.6E-5,1.64E-6]
[null,"2/08/2016","12:41:00","VH10","Rural Short","Asset failure","HV",2421,175.11111111111111,3.4218419999999998,1.9540979999999999E-2]
[null,"2/08/2016","13:19:00","WK11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",281,203.45195729537366,0.46144499999999999,2.26808E-3]
[null,"2/08/2016","16:46:00","MTB13","Rural Short","Third Party","Other",109,170,0.149564,8.7978999999999998E-4]
[null,"2/08/2016","18:08:40","MV33","Rural Short","Overloads",null,0.99999899999999997,1036,8.3619999999999996E-3,8.0700000000000007E-6]
[null,"2/08/2016","18:14:47","SA12","Urban","Asset failure","LV",1,414,6.8099999999999996E-4,1.64E-6]
[null,"2/08/2016","18:30:00","AP227A","Urban","Asset failure","HV",2636,60.588770864946881,0.26261400000000001,4.3343599999999998E-3]
[null,"2/08/2016","19:27:22","VH32","Rural Short","Overloads",null,2.6666639999999999,1134,2.4407999999999999E-2,2.1520000000000001E-5]
[null,"2/08/2016","19:29:18","EL01A","Urban","Asset failure","LV",22.333310999999998,292.00000000000006,1.0723E-2,3.6720000000000001E-5]
[null,"2/08/2016","22:12:42","AP424E","Urban","Unknown","Unknown",1,145,2.3800000000000001E-4,1.64E-6]
[null,"2/08/2016","23:08:00","HH409F","Urban","Asset failure","HV",643.66698800000006,166,0.17569100000000001,1.05838E-3]
[null,"2/08/2016","23:08:00","HH409F","Urban","Asset failure","HV",93.333380000000005,110.4,1.6943E-2,1.5347000000000001E-4]
[null,"3/08/2016","00:02:00","SM350H","Urban","Asset failure","HV",1861,125.6485760343901,0.38448900000000003,3.06003E-3]
[null,"3/08/2016","02:11:00","SG07","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1015,205.4512315270936,1.683163,8.19252E-3]
[null,"3/08/2016","08:13:17","HH409F","Urban","Planned",null,12,409,8.0700000000000008E-3,1.9729999999999999E-5]
[null,"3/08/2016","08:21:52","SM374A","Urban","Asset failure","LV",1,125,2.0599999999999999E-4,1.64E-6]
[null,"3/08/2016","08:26:51","MV61","Urban","Planned",null,168,326,9.0054999999999996E-2,2.7624000000000003E-4]
[null,"3/08/2016","08:30:58","GA29","Rural Long","Planned",null,1,410.99999999999994,2.9160000000000002E-3,7.0899999999999999E-6]
[null,"3/08/2016","08:31:39","GA29","Rural Long","Planned",null,1,412,2.9229999999999998E-3,7.0899999999999999E-6]
[null,"3/08/2016","08:32:20","GA29","Rural Long","Planned",null,2,410.99999999999994,5.8320000000000004E-3,1.419E-5]
[null,"3/08/2016","08:32:42","GA29","Rural Long","Planned",null,1,409,2.9020000000000001E-3,7.0899999999999999E-6]
[null,"3/08/2016","08:32:57","GA29","Rural Long","Planned",null,1,410.99999999999994,2.9160000000000002E-3,7.0899999999999999E-6]
[null,"3/08/2016","09:02:00","NL234C","Urban","Planned",null,115,174.00000000000003,3.2902000000000001E-2,1.8908999999999999E-4]
[null,"3/08/2016","10:13:00","BM31","Rural Short","Planned",null,1,96,7.7499999999999997E-4,8.0700000000000007E-6]
[null,"3/08/2016","10:15:10","SA14","Urban","Planned",null,21,203,7.0099999999999997E-3,3.4530000000000003E-5]
[null,"3/08/2016","10:32:00","CN01","Rural Long","Planned",null,3,98,2.0860000000000002E-3,2.128E-5]
[null,"3/08/2016","11:00:00","G23","Rural Long","Planned",null,2,188.99999999999997,2.6819999999999999E-3,1.419E-5]
[null,"3/08/2016","11:49:50","HH496G","Urban","Planned",null,29,298,1.421E-2,4.7679999999999998E-5]
[null,"3/08/2016","14:03:00","SSD167","Rural Short","Planned",null,827,6,4.0051000000000003E-2,6.6750899999999998E-3]
[null,"3/08/2016","18:28:59","HH496A","Urban","Asset failure","LV",1,416,6.8400000000000004E-4,1.64E-6]
[null,"3/08/2016","19:30:00","VH10","Rural Short","Asset failure","HV",421,102.85510688836104,0.34950999999999999,3.3980799999999999E-3]
[null,"3/08/2016","20:25:57","HH130D","Urban","Asset failure","LV",14.333318999999999,323,7.613E-3,2.357E-5]
[null,"4/08/2016","02:57:00","SSD188","Urban","5 - STPIS Exclusion (3.3)(a)",null,8585,19.17344205008736,0.27065699999999998,1.411627E-2]
[null,"4/08/2016","02:57:00","SSD188","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,4760,18.287605042016807,0.61758100000000005,3.3770479999999999E-2]
[null,"4/08/2016","03:45:00","SG04","Rural Short","Unknown","Unknown",37.000016000000002,118,3.524E-2,2.9863999999999997E-4]
[null,"4/08/2016","08:13:25","EL09","Urban","Planned",null,29,170,8.1060000000000004E-3,4.7679999999999998E-5]
[null,"4/08/2016","08:32:27","MV61","Urban","Planned",null,69,336,3.8121000000000002E-2,1.1346E-4]
[null,"4/08/2016","08:32:31","AP424B","Urban","Planned",null,101,161.99999999999997,2.6904000000000001E-2,1.6606999999999999E-4]
[null,"4/08/2016","08:33:00","SD49201","Rural Long","Planned",null,289,147,0.301402,2.0503499999999998E-3]
[null,"4/08/2016","08:36:32","MV61","Urban","Planned",null,117,231.00000000000003,4.444E-2,1.9238E-4]
[null,"4/08/2016","08:37:43","MB92","Rural Long","Planned",null,5,136,4.8240000000000002E-3,3.5469999999999998E-5]
[null,"4/08/2016","08:45:00","WK31","Rural Short","Planned",null,2,20,3.2299999999999999E-4,1.6140000000000001E-5]
[null,"4/08/2016","08:55:00","VH44","Rural Short","Planned",null,2,215,3.4710000000000001E-3,1.6140000000000001E-5]
[null,"4/08/2016","08:57:28","NU34","Rural Long","Planned",null,31,214,4.7065999999999997E-2,2.1992999999999999E-4]
[null,"4/08/2016","08:57:51","AP149H","Urban","Planned",null,42,323.99999999999994,2.2376E-2,6.9060000000000006E-5]
[null,"4/08/2016","08:59:24","AP149E","Urban","Planned",null,36,323,1.9120000000000002E-2,5.9190000000000001E-5]
[null,"4/08/2016","09:12:38","SA711C","Urban","Planned",null,79,326,4.2347000000000003E-2,1.2990000000000001E-4]
[null,"4/08/2016","09:13:53","SA711C","Urban","Planned",null,70,325,3.7407999999999997E-2,1.1510000000000001E-4]
[null,"4/08/2016","09:20:00","NA28","Rural Long","Planned",null,1,80,5.6800000000000004E-4,7.0899999999999999E-6]
[null,"4/08/2016","09:27:24","SA41","Urban","Planned",null,25,355,1.4593E-2,4.1109999999999998E-5]
[null,"4/08/2016","09:45:04","SM349F","Urban","Planned",null,104,312,5.3353999999999999E-2,1.7101E-4]
[null,"4/08/2016","09:50:01","SA744D","Urban","Planned",null,35,81,4.6620000000000003E-3,5.7550000000000003E-5]
[null,"4/08/2016","09:51:00","SG13","Rural Short","Planned",null,5,87,3.5109999999999998E-3,4.036E-5]
[null,"4/08/2016","10:19:05","NA52","Rural Long","Planned",null,51,79,2.8583999999999998E-2,3.6183E-4]
[null,"4/08/2016","10:35:00","MTB13","Rural Short","Planned",null,34,110.00000000000001,3.0186999999999999E-2,2.7442999999999999E-4]
[null,"4/08/2016","11:03:00","NA03","Rural Long","Unknown","Unknown",6.6666690000000006,136.99999999999997,6.4799999999999996E-3,4.7299999999999998E-5]
[null,"4/08/2016","11:18:00","NA28","Rural Long","Planned",null,2,242,3.434E-3,1.419E-5]
[null,"4/08/2016","12:00:00","SG13","Rural Short","Planned",null,2,45,7.2599999999999997E-4,1.6140000000000001E-5]
[null,"4/08/2016","12:28:52","MV61","Urban","Planned",null,120,263,5.1894000000000003E-2,1.9731999999999999E-4]
[null,"4/08/2016","13:00:00","KA30","Rural Short","Planned",null,1,92,7.4299999999999995E-4,8.0700000000000007E-6]
[null,"4/08/2016","14:37:00","SSD341","Urban","Asset failure","Zone substation",9047,6.5201724328506687,9.6993999999999997E-2,1.4875930000000001E-2]
[null,"4/08/2016","15:16:27","NL451C","Urban","Asset failure","LV",1,382.00000000000006,6.2799999999999998E-4,1.64E-6]
[null,"4/08/2016","15:25:00","SSD186","Rural Long","Unknown","Unknown",1318,14,0.13091,9.3507299999999998E-3]
[null,"4/08/2016","17:55:00","SM349E","Urban","Third Party","Vehicle impact",332,358,0.195434,5.4591000000000004E-4]
[null,"4/08/2016","20:00:19","AP149A","Urban","Asset failure","LV",2,1028,3.3809999999999999E-3,3.2899999999999998E-6]
[null,"4/08/2016","20:08:00","VH45","Rural Short","Unknown","Unknown",1150,147.85217391304346,1.3723879999999999,9.2821699999999993E-3]
[null,"4/08/2016","20:08:00","VH45","Rural Short","Unknown","Unknown",null,2,1.6771999999999999E-2,0]
[null,"4/08/2016","22:41:04","EL08G","Urban","Asset failure","LV",48,92,7.2610000000000001E-3,7.8930000000000005E-5]
[null,"5/08/2016","00:15:00","AP139B","Urban","Third Party","Vehicle impact",2053,58.625913297613245,0.197906,3.3757399999999999E-3]
[null,"5/08/2016","07:31:00","BT26","Rural Long","Asset failure","Distribution substation",161,244.9503105590062,0.27979100000000001,1.1422400000000001E-3]
[null,"5/08/2016","08:20:45","SA744D","Urban","Planned",null,56,105.00000000000001,9.6679999999999995E-3,9.2079999999999999E-5]
[null,"5/08/2016","08:36:25","LX43","Rural Short","Planned",null,11,153,1.3584000000000001E-2,8.8789999999999995E-5]
[null,"5/08/2016","08:40:00","NA29","Rural Long","Planned",null,2,173,2.4550000000000002E-3,1.419E-5]
[null,"5/08/2016","08:55:00","SG01","Rural Short","Planned",null,1,187,1.5089999999999999E-3,8.0700000000000007E-6]
[null,"5/08/2016","09:05:00","NU01","Rural Short","Planned",null,13,93,9.7579999999999993E-3,1.0493E-4]
[null,"5/08/2016","09:06:00","WHY17","Rural Short","Planned",null,8,360,2.3245999999999999E-2,6.457E-5]
[null,"5/08/2016","09:10:00","R32","Rural Long","Planned",null,1,58,4.1100000000000002E-4,7.0899999999999999E-6]
[null,"5/08/2016","09:10:00","W15","Rural Long","Planned",null,9,53,3.3839999999999999E-3,6.3849999999999993E-5]
[null,"5/08/2016","09:14:00","AP149D","Urban","Planned",null,49,278,2.2398999999999999E-2,8.0569999999999996E-5]
[null,"5/08/2016","09:22:00","AP355F","Urban","Planned",null,92,173.00000000000003,2.6171E-2,1.5128E-4]
[null,"5/08/2016","09:22:00","NL210D","Urban","Planned",null,482,106.7676348547718,8.4619E-2,7.9255000000000005E-4]
[null,"5/08/2016","09:34:00","SA31","Urban","Asset failure","HV",688,169.67005813953489,0.191943,1.13127E-3]
[null,"5/08/2016","10:02:00","PA18","Rural Long","Planned",null,71,189.99999999999997,9.5707E-2,5.0372000000000004E-4]
[null,"5/08/2016","10:15:00","R25","Rural Long","Planned",null,2,37,5.2499999999999997E-4,1.419E-5]
[null,"5/08/2016","11:51:00","LM11","Rural Long","Planned",null,2,34,4.8200000000000001E-4,1.419E-5]
[null,"5/08/2016","12:05:56","SA711C","Urban","Planned",null,41,85.999999999999986,5.7980000000000002E-3,6.7420000000000002E-5]
[null,"5/08/2016","13:51:00","NL115A","Urban","Unknown","Unknown",46.000022999999999,664.00000000000011,5.0222999999999997E-2,7.5640000000000001E-5]
[null,"5/08/2016","13:59:00","NL760B","Urban","Asset failure","HV",2608,90.594708588957047,0.38849899999999998,4.28832E-3]
[null,"5/08/2016","15:54:00","SSD186","Rural Long","Unknown","Unknown",1318,3,2.8052000000000001E-2,9.3507299999999998E-3]
[null,"5/08/2016","21:19:09","NL115E","Urban","Asset failure","LV",47,447.00000000000006,3.4544999999999999E-2,7.7280000000000005E-5]
[null,"5/08/2016","23:02:13","HH429C","Urban","Overloads",null,1,215,3.5399999999999999E-4,1.64E-6]
[null,"5/08/2016","23:27:36","WHY08","Urban","Overloads",null,1,114.00000000000001,1.8699999999999999E-4,1.64E-6]
[null,"6/08/2016","03:23:00","MG03","Rural Short","Unknown","Unknown",12,169,1.6369000000000002E-2,9.6860000000000004E-5]
[null,"6/08/2016","07:35:00","ME427C","Urban","Planned",null,3,316,1.5590000000000001E-3,4.9300000000000002E-6]
[null,"6/08/2016","09:10:00","SD591","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,325,184,0.424259,2.30576E-3]
[null,"6/08/2016","13:50:00","MI22","Rural Long","Unknown","Unknown",117.333392,97.999999999999986,8.1578999999999999E-2,8.3244000000000005E-4]
[null,"6/08/2016","22:27:00","HH409A","Urban","Unknown","Unknown",1125,7.724444444444444,1.4289E-2,1.84983E-3]
[null,"7/08/2016","08:02:47","AP132A","Urban","Planned",null,12,121,2.3879999999999999E-3,1.9729999999999999E-5]
[null,"7/08/2016","08:03:12","AP132A","Urban","Planned",null,25,120.00000000000001,4.9329999999999999E-3,4.1109999999999998E-5]
[null,"7/08/2016","08:30:00","SM402C","Urban","Planned",null,21,353.99999999999994,1.2224E-2,3.4530000000000003E-5]
[null,"7/08/2016","08:55:00","AP146A","Urban","Planned",null,7,231.99999999999997,2.6700000000000001E-3,1.151E-5]
[null,"7/08/2016","08:57:00","HH145B","Urban","Asset failure","HV",2830,93.424734982332154,0.43473800000000001,4.6533499999999997E-3]
[null,"7/08/2016","09:17:00","CBD412N","Urban","Planned",null,4,208,1.3680000000000001E-3,6.5799999999999997E-6]
[null,"7/08/2016","10:50:00","GU41","Rural Long","Asset failure","HV",92,197.0978260869565,0.12864700000000001,6.5271000000000003E-4]
[null,"7/08/2016","11:02:00","BU11","Rural Short","Planned",null,19,15,2.3E-3,1.5336000000000001E-4]
[null,"7/08/2016","11:28:00","GA800A","Rural Short","Animal","Animal impact",192,47,7.2836999999999999E-2,1.5497200000000001E-3]
[null,"7/08/2016","11:36:51","GA01","Urban","Asset failure","LV",8.9999909999999996,73,1.08E-3,1.4800000000000001E-5]
[null,"7/08/2016","12:00:28","NL115E","Urban","Planned",null,47,152,1.1747E-2,7.7280000000000005E-5]
[null,"7/08/2016","12:26:08","WHY12","Urban","Asset failure","LV",1,118.00000000000001,1.94E-4,1.64E-6]
[null,"7/08/2016","17:23:34","HH428B","Urban","Asset failure","LV",45,392.00000000000006,2.9005E-2,7.3990000000000001E-5]
[null,"7/08/2016","17:59:17","HH130E","Urban","Asset failure","LV",4,70,4.6000000000000001E-4,6.5799999999999997E-6]
[null,"7/08/2016","18:38:00","SSD244","Rural Long","Asset failure","Zone substation",698,207.99999999999997,1.0300279999999999,4.9520600000000003E-3]
[null,"8/08/2016","00:19:00","SG13","Rural Short","Asset failure","HV",1380,79.08695652173914,0.88091799999999998,1.11386E-2]
[null,"8/08/2016","08:11:26","HH496C","Urban","Planned",null,45,290,2.1458000000000001E-2,7.3990000000000001E-5]
[null,"8/08/2016","08:18:12","NL451C","Urban","Planned",null,31,227.99999999999997,1.1622E-2,5.0970000000000002E-5]
[null,"8/08/2016","08:20:26","MV61","Urban","Planned",null,168,276.99999999999994,7.6519000000000004E-2,2.7624000000000003E-4]
[null,"8/08/2016","08:37:00","NL760A","Urban","Planned",null,2,358.00000000000006,1.1770000000000001E-3,3.2899999999999998E-6]
[null,"8/08/2016","08:38:00","CM01","Rural Long","Animal","Animal impact",62,290,0.12756200000000001,4.3986999999999997E-4]
[null,"8/08/2016","08:42:31","AP424B","Urban","Planned",null,35,125,7.1939999999999999E-3,5.7550000000000003E-5]
[null,"8/08/2016","08:49:47","BM44","Rural Short","Planned",null,3,159,3.8500000000000001E-3,2.421E-5]
[null,"8/08/2016","08:51:00","VH12","Rural Short","Planned",null,90,378,0.27459099999999997,7.2643000000000002E-4]
[null,"8/08/2016","08:56:32","PP04","Rural Short","Planned",null,3,402.00000000000006,9.7339999999999996E-3,2.421E-5]
[null,"8/08/2016","09:07:00","SM126D","Urban","Planned",null,37,265,1.6122000000000001E-2,6.084E-5]
[null,"8/08/2016","09:26:00","SM349D","Urban","Planned",null,304,20,9.9970000000000007E-3,4.9987000000000002E-4]
[null,"8/08/2016","09:28:00","CN83","Rural Long","Planned",null,2,79,1.121E-3,1.419E-5]
[null,"8/08/2016","09:43:00","AP372B","Urban","Planned",null,82,196.99999999999997,2.6561999999999999E-2,1.3483000000000001E-4]
[null,"8/08/2016","09:46:00","EL14","Urban","Asset failure","HV",1573,12.405594405594405,3.2086999999999997E-2,2.5864799999999999E-3]
[null,"8/08/2016","10:15:00","LX75","Rural Long","Planned",null,4,88,2.4970000000000001E-3,2.8379999999999999E-5]
[null,"8/08/2016","11:16:04","HH409F","Urban","Planned",null,45,138.00000000000003,1.0211E-2,7.3990000000000001E-5]
[null,"8/08/2016","11:50:00","EL15","Urban","Asset failure","HV",4,109,7.1699999999999997E-4,6.5799999999999997E-6]
[null,"8/08/2016","12:10:27","AP424B","Urban","Planned",null,24,158,6.2350000000000001E-3,3.9459999999999998E-5]
[null,"8/08/2016","12:11:53","HH409D","Urban","Asset failure","LV",1,382.00000000000006,6.2799999999999998E-4,1.64E-6]
[null,"8/08/2016","13:02:00","SSD331","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,325,162,0.373533,2.30576E-3]
[null,"8/08/2016","13:05:00","LX75","Rural Long","Planned",null,8,59.999999999999993,3.405E-3,5.6759999999999999E-5]
[null,"8/08/2016","16:28:00","AP226D","Urban","Unknown","Unknown",1536,52.000000000000007,0.13133300000000001,2.52564E-3]
[null,"8/08/2016","16:34:00","LC06","Rural Long","Planned",null,5,5563.9999999999991,0.19737299999999999,3.5469999999999998E-5]
[null,"8/08/2016","19:01:00","NU02","Rural Long","Asset failure","Distribution substation",1644,425.08576642335765,4.9580250000000001,1.166359E-2]
[null,"8/08/2016","19:01:00","NU02","Rural Long","Asset failure","Distribution substation",null,2,4.2430000000000002E-3,0]
[null,"9/08/2016","05:26:00","HH130B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2463,67.999999999999986,0.275393,4.0499000000000004E-3]
[null,"9/08/2016","07:59:39","SA744D","Urban","Planned",null,16,91,2.3939999999999999E-3,2.6310000000000001E-5]
[null,"9/08/2016","08:07:49","ME347A","Urban","Planned",null,79,156,2.0264000000000001E-2,1.2990000000000001E-4]
[null,"9/08/2016","08:08:45","ME347G","Urban","Planned",null,19,156,4.8739999999999999E-3,3.1239999999999999E-5]
[null,"9/08/2016","08:10:00","SD34405","Rural Long","Planned",null,6,412.33333333333337,1.7552000000000002E-2,4.2570000000000001E-5]
[null,"9/08/2016","08:31:53","SM216G","Urban","Planned",null,83,220,3.0025E-2,1.3647999999999999E-4]
[null,"9/08/2016","08:38:26","AP424B","Urban","Planned",null,77,95.000000000000014,1.2028E-2,1.2661000000000001E-4]
[null,"9/08/2016","08:40:00","BM33","Rural Short","Planned",null,10,199,1.6062E-2,8.0710000000000005E-5]
[null,"9/08/2016","08:42:00","EL01A","Urban","Planned",null,161,130.59006211180122,3.4570999999999998E-2,2.6473000000000002E-4]
[null,"9/08/2016","08:57:49","HH496G","Urban","Planned",null,33,259,1.4054000000000001E-2,5.4259999999999999E-5]
[null,"9/08/2016","09:01:00","YK04","Rural Short","Planned",null,13,278,2.9170000000000001E-2,1.0493E-4]
[null,"9/08/2016","09:20:00","R28","Rural Long","Planned",null,2,19,2.7E-4,1.419E-5]
[null,"9/08/2016","09:20:00","SG09","Rural Short","Planned",null,12,32,3.0990000000000002E-3,9.6860000000000004E-5]
[null,"9/08/2016","09:23:41","SA18","Urban","Planned",null,37,174,1.0586E-2,6.084E-5]
[null,"9/08/2016","09:41:08","BM52","Urban","Planned",null,61,91,9.1269999999999997E-3,1.003E-4]
[null,"9/08/2016","09:43:00","WK65","Rural Short","Planned",null,2,22,3.5500000000000001E-4,1.6140000000000001E-5]
[null,"9/08/2016","09:44:00","AP365B","Urban","Planned",null,119,258,5.0483E-2,1.9567E-4]
[null,"9/08/2016","10:03:13","EL25","Urban","Planned",null,38,169,1.056E-2,6.2479999999999998E-5]
[null,"9/08/2016","10:27:00","G23","Rural Long","Planned",null,3,130,2.7669999999999999E-3,2.128E-5]
[null,"9/08/2016","13:11:08","HH177A","Urban","Planned",null,11,57,1.031E-3,1.8090000000000001E-5]
[null,"9/08/2016","14:24:00","HH177E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2435,152.18767967145789,0.60933800000000005,4.0038599999999997E-3]
[null,"9/08/2016","14:25:00","NA13","Rural Long","Unknown","Unknown",470.6667989999998,1,3.339E-3,3.33921E-3]
[null,"9/08/2016","14:27:00","HH121F","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1780,127.00000000000001,0.37170900000000001,2.92684E-3]
[null,"9/08/2016","14:40:00","SG07","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",8,100,6.4570000000000001E-3,6.457E-5]
[null,"9/08/2016","14:55:00","SM350E","Urban","Animal","Animal impact",48.666691,200.00000000000003,1.6004000000000001E-2,8.0019999999999996E-5]
[null,"9/08/2016","15:15:00","GA08","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",22,202,3.1529000000000001E-2,1.5608000000000001E-4]
[null,"9/08/2016","16:15:00","MG17","Rural Long","Asset failure","HV",55.666691999999998,35.347305045537823,1.396E-2,3.9493999999999998E-4]
[null,"9/08/2016","17:49:00","EL03","Urban","Asset failure","HV",479.99953599999992,126.82500055791722,0.10009800000000001,7.8925999999999996E-4]
[null,"9/08/2016","19:25:00","SG09","Rural Short","Third Party","Vehicle impact",68,270,0.14819199999999999,5.4885999999999997E-4]
[null,"9/08/2016","20:27:00","VH17","Rural Short","Unknown","Unknown",37,232.99999999999997,6.9583999999999993E-2,2.9863999999999997E-4]
[null,"9/08/2016","20:32:00","MTB54","Rural Long","Weather",null,240,248.82916666666668,0.42368499999999998,1.7027100000000001E-3]
[null,"9/08/2016","22:14:00","SG01","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",421,272.97624703087888,0.92759499999999995,3.3980799999999999E-3]
[null,"9/08/2016","22:42:33","MG52","Urban","Other",null,1,123,2.02E-4,1.64E-6]
[null,"9/08/2016","22:47:00","HH148B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1398,67,0.15401500000000001,2.2987200000000002E-3]
[null,"9/08/2016","23:42:27","EL01M","Urban","Asset failure","LV",1,45,7.3999999999999996E-5,1.64E-6]
[null,"10/08/2016","02:55:00","GU38","Rural Long","Asset failure","HV",16,544.6875,6.1830000000000003E-2,1.1351E-4]
[null,"10/08/2016","08:17:01","MV62","Rural Short","Planned",null,17,237.00000000000003,3.252E-2,1.3721E-4]
[null,"10/08/2016","08:22:38","SA711C","Urban","Planned",null,58,367,3.5000000000000003E-2,9.5370000000000003E-5]
[null,"10/08/2016","08:32:45","SA16","Urban","Planned",null,39,307,1.9687E-2,6.4129999999999998E-5]
[null,"10/08/2016","08:37:19","KI11","Rural Long","Planned",null,29,361,7.4274000000000007E-2,2.0573999999999999E-4]
[null,"10/08/2016","08:57:00","PA06","Rural Long","Planned",null,206,333.03883495145635,0.48673499999999997,1.4614999999999999E-3]
[null,"10/08/2016","08:59:00","NU08","Rural Long","Animal","Animal impact",96,197.32291666666666,0.13439400000000001,6.8108999999999997E-4]
[null,"10/08/2016","09:00:11","SA11","Urban","Planned",null,73,280,3.3609E-2,1.2003E-4]
[null,"10/08/2016","09:02:34","HH496G","Urban","Planned",null,29,272,1.2970000000000001E-2,4.7679999999999998E-5]
[null,"10/08/2016","09:05:00","G04","Rural Long","Planned",null,1,293,2.0790000000000001E-3,7.0899999999999999E-6]
[null,"10/08/2016","09:10:00","MG02","Rural Long","Planned",null,2,163,2.313E-3,1.419E-5]
[null,"10/08/2016","09:11:00","GA29","Rural Long","Planned",null,7,276,1.3707E-2,4.9660000000000002E-5]
[null,"10/08/2016","09:16:00","BT06","Rural Long","Planned",null,89,183.99999999999997,0.11618199999999999,6.3142000000000005E-4]
[null,"10/08/2016","09:17:00","KA25","Rural Long","Unknown","Unknown",1,23,1.63E-4,7.0899999999999999E-6]
[null,"10/08/2016","09:22:00","CN22","Rural Long","Planned",null,5,20.999999999999996,7.45E-4,3.5469999999999998E-5]
[null,"10/08/2016","09:22:00","CN22","Rural Long","Planned",null,2,133,1.887E-3,1.419E-5]
[null,"10/08/2016","09:36:00","MT25","Rural Long","Planned",null,2,83,1.178E-3,1.419E-5]
[null,"10/08/2016","09:39:00","SB16","Rural Long","Unknown","Unknown",12,268,2.2815999999999999E-2,8.5140000000000001E-5]
[null,"10/08/2016","09:42:00","W15","Rural Long","Planned",null,22,258,4.0268999999999999E-2,1.5608000000000001E-4]
[null,"10/08/2016","09:53:00","SA11","Urban","Planned",null,47,151,1.167E-2,7.7280000000000005E-5]
[null,"10/08/2016","11:14:00","SM126C","Urban","Planned",null,3,226,1.1150000000000001E-3,4.9300000000000002E-6]
[null,"10/08/2016","11:17:00","AP355A","Urban","Asset failure","HV",1301.3339819999997,143.30635245333971,0.30664400000000003,2.13978E-3]
[null,"10/08/2016","11:26:00","CV29","Rural Long","Unknown","Unknown",0.99999899999999997,18.999999999999996,1.35E-4,7.0899999999999999E-6]
[null,"10/08/2016","12:15:00","GU41","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",530,222.21132075471698,0.83555000000000001,3.7601599999999998E-3]
[null,"10/08/2016","12:17:30","NL210B","Urban","Planned",null,68,75,8.3859999999999994E-3,1.1181E-4]
[null,"10/08/2016","12:44:58","CL16","Rural Long","Planned",null,24,31,5.2779999999999997E-3,1.7027000000000001E-4]
[null,"10/08/2016","13:37:00","ST11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",263,284,0.60287299999999999,2.1227899999999998E-3]
[null,"10/08/2016","15:16:00","AP146E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",554,57,5.1923999999999998E-2,9.1093999999999995E-4]
[null,"10/08/2016","18:02:03","NL234C","Urban","Asset failure","LV",1,477,7.8399999999999997E-4,1.64E-6]
[null,"10/08/2016","21:45:00","SSD382","CBD","Planned",null,10,348,0.65765899999999999,1.88982E-3]
[null,"10/08/2016","21:53:02","AP355E","Urban","Overloads",null,1,146,2.4000000000000001E-4,1.64E-6]
[null,"10/08/2016","23:27:19","NL234B","Urban","Third Party","Vehicle impact",74,1050,0.12776199999999999,1.2168E-4]
[null,"11/08/2016","00:23:00","NL234B","Urban","Third Party","Vehicle impact",37,914,5.5606999999999997E-2,6.084E-5]
[null,"11/08/2016","08:30:00","MG05","Rural Long","Planned",null,7,84,4.1720000000000004E-3,4.9660000000000002E-5]
[null,"11/08/2016","08:33:20","NL451C","Urban","Planned",null,48,105,8.2869999999999992E-3,7.8930000000000005E-5]
[null,"11/08/2016","08:35:04","WK52","Rural Short","Planned",null,4,369,1.1913E-2,3.2289999999999997E-5]
[null,"11/08/2016","08:42:28","SA14","Urban","Planned",null,21,207,7.1479999999999998E-3,3.4530000000000003E-5]
[null,"11/08/2016","08:43:00","BT31","Rural Long","Planned",null,2,141,2.0010000000000002E-3,1.419E-5]
[null,"11/08/2016","08:52:43","NU01","Rural Short","Planned",null,4,316,1.0201999999999999E-2,3.2289999999999997E-5]
[null,"11/08/2016","08:57:00","CD15","Rural Long","Planned",null,26,238,4.3901999999999997E-2,1.8446000000000001E-4]
[null,"11/08/2016","08:57:00","AP125A","Urban","Planned",null,2,330,1.085E-3,3.2899999999999998E-6]
[null,"11/08/2016","09:11:00","WK31","Rural Short","Planned",null,8,140,9.0399999999999994E-3,6.457E-5]
[null,"11/08/2016","09:15:00","PP08","Rural Long","Planned",null,22,155,2.4192999999999999E-2,1.5608000000000001E-4]
[null,"11/08/2016","10:02:00","AP365B","Urban","Planned",null,79,272,3.5333000000000003E-2,1.2990000000000001E-4]
[null,"11/08/2016","10:03:00","LM51","Rural Long","Planned",null,2,53,7.5199999999999996E-4,1.419E-5]
[null,"11/08/2016","10:16:00","CV19","Rural Long","Planned",null,60,106.00000000000001,4.5122000000000002E-2,4.2568E-4]
[null,"11/08/2016","10:22:00","YK20","Rural Long","Planned",null,15,199,2.1177000000000001E-2,1.0642E-4]
[null,"11/08/2016","12:00:00","BT33","Rural Long","Planned",null,1,100,7.0899999999999999E-4,7.0899999999999999E-6]
[null,"11/08/2016","12:15:00","MI09","Rural Long","Third Party","Vehicle impact",2,56,7.9500000000000003E-4,1.419E-5]
[null,"11/08/2016","12:40:00","CV21","Rural Long","Planned",null,56,64,2.5427000000000002E-2,3.9730000000000001E-4]
[null,"11/08/2016","13:00:00","PA13","Rural Long","Unknown","Unknown",2,35,4.9700000000000005E-4,1.419E-5]
[null,"11/08/2016","20:54:13","HH386F","Urban","Overloads",null,1,203,3.3399999999999999E-4,1.64E-6]
[null,"12/08/2016","07:52:52","VH12","Rural Short","Planned",null,76,386,0.23678399999999999,6.1342999999999999E-4]
[null,"12/08/2016","08:32:42","AP146C","Urban","Planned",null,18,178,5.2680000000000001E-3,2.9600000000000001E-5]
[null,"12/08/2016","08:53:00","BT07","Rural Long","Planned",null,2,182,2.5820000000000001E-3,1.419E-5]
[null,"12/08/2016","08:54:21","NL760B","Urban","Planned",null,46,312.00000000000006,2.3598999999999998E-2,7.5640000000000001E-5]
[null,"12/08/2016","08:55:00","KI41","Rural Long","Unknown","Unknown",1,78,5.53E-4,7.0899999999999999E-6]
[null,"12/08/2016","09:25:00","GA47","Rural Long","Planned",null,7,289,1.4352E-2,4.9660000000000002E-5]
[null,"12/08/2016","09:36:00","HH429C","Urban","Planned",null,53,115,1.0022E-2,8.7150000000000004E-5]
[null,"12/08/2016","10:00:13","GA04","Rural Long","Planned",null,2,261,3.7030000000000001E-3,1.419E-5]
[null,"12/08/2016","10:05:00","GA04","Rural Long","Planned",null,25,250.99999999999997,4.4519000000000003E-2,1.7736999999999999E-4]
[null,"12/08/2016","10:45:36","SA14","Urban","Planned",null,42,138,9.5300000000000003E-3,6.9060000000000006E-5]
[null,"12/08/2016","13:07:43","AP424A","Urban","Asset failure","LV",1,88.000000000000014,1.45E-4,1.64E-6]
[null,"12/08/2016","13:10:00","NA33","Rural Long","Planned",null,2,56,7.9500000000000003E-4,1.419E-5]
[null,"12/08/2016","13:10:42","HH428E","Urban","Asset failure","LV",48.000024000000003,455.00000000000006,3.5910999999999998E-2,7.8930000000000005E-5]
[null,"12/08/2016","14:30:00","BT04","Rural Long","Unknown","Unknown",2,11,1.56E-4,1.419E-5]
[null,"12/08/2016","21:38:34","NL111P","Urban","Asset failure","LV",1,277,4.55E-4,1.64E-6]
[null,"12/08/2016","22:05:00","HH121D","Urban","Asset failure","HV",50.000025000000001,558.31999999999982,4.5901999999999998E-2,8.2210000000000001E-5]
[null,"12/08/2016","22:05:00","HH121D","Urban","Asset failure","HV",838.333752,8,1.1028E-2,1.3784699999999999E-3]
[null,"12/08/2016","22:05:00","HH121D","Urban","Asset failure","HV",null,38.999999999999993,9.41E-4,0]
[null,"12/08/2016","23:22:03","EL09","Urban","Asset failure","LV",1,152,2.5000000000000001E-4,1.64E-6]
[null,"13/08/2016","05:22:00","NA13","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",166,221,0.26027400000000001,1.17771E-3]
[null,"13/08/2016","10:33:00","SG04","Rural Short","Asset failure","Distribution substation",4,500.24999999999994,1.6150999999999999E-2,3.2289999999999997E-5]
[null,"13/08/2016","13:56:00","ME347G","Urban","Unknown","Unknown",1451,11.029634734665747,2.6315000000000002E-2,2.38587E-3]
[null,"13/08/2016","14:08:00","EL23","Urban","Unknown","Unknown",9.6666699999999999,217,3.4489999999999998E-3,1.5889999999999999E-5]
[null,"13/08/2016","14:28:32","AP424E","Urban","Unknown","Unknown",109,28.000000000000004,5.0179999999999999E-3,1.7923E-4]
[null,"13/08/2016","14:44:00","SD332","Rural Long","Unknown","Unknown",1229,127.00000000000001,1.107353,8.7193099999999992E-3]
[null,"13/08/2016","18:12:06","HH177G","Urban","Asset failure","LV",1,372,6.1200000000000002E-4,1.64E-6]
[null,"13/08/2016","18:52:00","HH121D","Urban","Unknown","Unknown",2290,157.10131004366812,0.59155500000000005,3.7654300000000002E-3]
[null,"13/08/2016","21:04:49","HH177G","Urban","Overloads",null,1,143.00000000000003,2.3499999999999999E-4,1.64E-6]
[null,"13/08/2016","23:03:39","SG04","Rural Short","Asset failure","LV",0.99999899999999997,117,9.4399999999999996E-4,8.0700000000000007E-6]
[null,"14/08/2016","00:00:00","VH31","Rural Short","Vegetation","Grow-in - NSP responsibility",138.000069,107.99999999999999,0.120297,1.1138599999999999E-3]
[null,"14/08/2016","06:54:02","ME427E","Urban","Planned",null,51,291,2.4403000000000001E-2,8.386E-5]
[null,"14/08/2016","07:30:00","ME427E","Urban","Planned",null,35,205,1.1797999999999999E-2,5.7550000000000003E-5]
[null,"14/08/2016","09:37:08","CBD103F","Urban","Planned",null,41,320.99999999999994,2.1641000000000001E-2,6.7420000000000002E-5]
[null,"14/08/2016","09:48:17","NL111P","Urban","Planned",null,66,163.00000000000003,1.7689E-2,1.0852E-4]
[null,"14/08/2016","09:50:02","NL111P","Urban","Planned",null,102,162,2.717E-2,1.6772E-4]
[null,"14/08/2016","10:16:00","SM172C","Urban","Planned",null,27,176,7.8139999999999998E-3,4.4400000000000002E-5]
[null,"14/08/2016","10:17:00","NL111P","Urban","Planned",null,242,218.00000000000003,8.6746000000000004E-2,3.9792000000000001E-4]
[null,"14/08/2016","13:01:14","EL01Q","Urban","Asset failure","LV",63.333365000000001,700,7.2897000000000003E-2,1.0414E-4]
[null,"14/08/2016","13:08:00","NL115C","Urban","Unknown","Unknown",1090,106,0.18998200000000001,1.79228E-3]
[null,"14/08/2016","13:53:00","ST34","Rural Long","Unknown","Unknown",4,110,3.1220000000000002E-3,2.8379999999999999E-5]
[null,"14/08/2016","15:20:30","AP227A","Urban","Overloads",null,1,126,2.0699999999999999E-4,1.64E-6]
[null,"14/08/2016","16:05:00","LX73","Rural Long","Unknown","Unknown",8,325,1.8446000000000001E-2,5.6759999999999999E-5]
[null,"14/08/2016","17:53:25","AP125C","Urban","Asset failure","LV",1,80.000000000000014,1.3200000000000001E-4,1.64E-6]
[null,"14/08/2016","17:57:29","HH130D","Urban","Asset failure","LV",1,376,6.1799999999999995E-4,1.64E-6]
[null,"14/08/2016","18:07:59","AP372F","Urban","Asset failure","LV",9.9999900000000004,130,2.1380000000000001E-3,1.6439999999999998E-5]
[null,"14/08/2016","23:04:00","AP132A","Urban","Planned",null,136,368,8.2294000000000006E-2,2.2362E-4]
[null,"14/08/2016","23:04:08","NU19","Rural Long","Asset failure","LV",21,979.00000000000011,0.14585899999999999,1.4898999999999999E-4]
[null,"15/08/2016","07:18:00","HH409C","Urban","Asset failure","HV",26,108.00000000000001,4.6169999999999996E-3,4.2750000000000002E-5]
[null,"15/08/2016","07:56:26","SA711C","Urban","Planned",null,45,214.00000000000003,1.5834999999999998E-2,7.3990000000000001E-5]
[null,"15/08/2016","08:25:31","AP424B","Urban","Planned",null,64,164.00000000000003,1.7259E-2,1.0522999999999999E-4]
[null,"15/08/2016","08:30:00","MG02","Rural Long","Planned",null,19,221,2.9790000000000001E-2,1.348E-4]
[null,"15/08/2016","08:33:03","MV64","Rural Short","Planned",null,76,391,0.23985100000000001,6.1342999999999999E-4]
[null,"15/08/2016","08:43:16","SA20","Urban","Planned",null,73,132,1.5844E-2,1.2003E-4]
[null,"15/08/2016","08:44:09","SA20","Urban","Planned",null,17,130,3.6340000000000001E-3,2.7949999999999998E-5]
[null,"15/08/2016","08:47:00","VH31","Rural Short","Third Party","Vehicle impact",18.666675999999999,328,4.9418999999999998E-2,1.5066999999999999E-4]
[null,"15/08/2016","08:55:00","EL260A","Urban","Planned",null,65,360,3.8476000000000003E-2,1.0688000000000001E-4]
[null,"15/08/2016","09:05:00","GA52","Rural Long","Planned",null,1,95,6.7400000000000001E-4,7.0899999999999999E-6]
[null,"15/08/2016","09:10:00","PP05","Rural Long","Planned",null,63,200.00000000000003,8.9391999999999999E-2,4.4695999999999999E-4]
[null,"15/08/2016","09:13:00","HH429C","Urban","Planned",null,189,380.00000000000006,0.118093,3.1076999999999998E-4]
[null,"15/08/2016","09:15:00","GA26","Urban","Unknown","Unknown",1646,62.577764277035236,0.16936699999999999,2.7065100000000001E-3]
[null,"15/08/2016","09:15:00","GA25","Rural Short","Unknown","Unknown",1,56,4.5199999999999998E-4,8.0700000000000007E-6]
[null,"15/08/2016","09:30:00","MV64","Rural Short","Planned",null,263,306,0.64957399999999998,2.1227899999999998E-3]
[null,"15/08/2016","09:31:00","CD17","Rural Long","Planned",null,9,290,1.8516999999999999E-2,6.3849999999999993E-5]
[null,"15/08/2016","09:32:00","PL14","Urban","Planned",null,2,175.00000000000003,5.7600000000000001E-4,3.2899999999999998E-6]
[null,"15/08/2016","09:42:00","BT34","Rural Long","Planned",null,2,184,2.611E-3,1.419E-5]
[null,"15/08/2016","10:06:00","LX34","Rural Short","Planned",null,1,81,6.5399999999999996E-4,8.0700000000000007E-6]
[null,"15/08/2016","10:20:00","AP214A","Urban","Planned",null,93,217,3.3183999999999998E-2,1.5291999999999999E-4]
[null,"15/08/2016","10:53:51","SA11","Urban","Planned",null,44,64,4.6299999999999996E-3,7.2349999999999997E-5]
[null,"15/08/2016","11:24:00","SD408","Rural Long","Planned",null,46,32,1.0442999999999999E-2,3.2634999999999999E-4]
[null,"15/08/2016","12:13:31","EL01Q","Urban","Asset failure","LV",82,140,1.8877000000000001E-2,1.3483000000000001E-4]
[null,"15/08/2016","13:20:00","BT34","Rural Long","Planned",null,2,104.99999999999999,1.49E-3,1.419E-5]
[null,"15/08/2016","14:26:00","GU31","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",19.666671000000001,237.99999999999997,3.3208000000000001E-2,1.3952999999999999E-4]
[null,"15/08/2016","18:30:00","CM35","Rural Long","Other",null,1,104.99999999999999,7.45E-4,7.0899999999999999E-6]
[null,"15/08/2016","20:36:13","AP529E","Urban","Asset failure","LV",1,88.000000000000014,1.45E-4,1.64E-6]
[null,"15/08/2016","21:05:18","NL111P","Urban","Asset failure","LV",1,284,4.6700000000000002E-4,1.64E-6]
[null,"15/08/2016","23:10:53","SG14","Rural Short","Asset failure","LV",15.666651,41,5.1850000000000004E-3,1.2645000000000001E-4]
[null,"16/08/2016","08:18:04","SA17","Urban","Planned",null,37,124.99999999999999,7.6049999999999998E-3,6.084E-5]
[null,"16/08/2016","08:26:00","KA02","Rural Short","Planned",null,2,482,7.7809999999999997E-3,1.6140000000000001E-5]
[null,"16/08/2016","08:30:00","KA05","Rural Long","Planned",null,137,185,0.179814,9.7196999999999995E-4]
[null,"16/08/2016","08:31:00","BT13","Rural Long","Planned",null,1,125.99999999999999,8.9400000000000005E-4,7.0899999999999999E-6]
[null,"16/08/2016","08:34:00","LX41","Rural Short","Planned",null,4,234.5,7.5709999999999996E-3,3.2289999999999997E-5]
[null,"16/08/2016","08:40:00","CL12","Rural Long","Planned",null,2,31,4.4000000000000002E-4,1.419E-5]
[null,"16/08/2016","08:49:27","SA711C","Urban","Planned",null,30,153,7.5469999999999999E-3,4.9329999999999997E-5]
[null,"16/08/2016","08:52:55","HH130A","Urban","Planned",null,1,133,2.1900000000000001E-4,1.64E-6]
[null,"16/08/2016","08:53:00","PA11","Rural Long","Planned",null,1,22,1.56E-4,7.0899999999999999E-6]
[null,"16/08/2016","09:00:00","SG07","Rural Short","Planned",null,12,316.00000000000006,3.0606999999999999E-2,9.6860000000000004E-5]
[null,"16/08/2016","09:05:00","MV61","Urban","Planned",null,123,311,6.2898999999999997E-2,2.0225000000000001E-4]
[null,"16/08/2016","09:12:04","SM350F","Urban","Planned",null,53,331,2.8846E-2,8.7150000000000004E-5]
[null,"16/08/2016","09:23:00","AP365B","Urban","Planned",null,66,243,2.6370999999999999E-2,1.0852E-4]
[null,"16/08/2016","09:24:00","AP425C","Urban","Planned",null,1,1729,2.843E-3,1.64E-6]
[null,"16/08/2016","09:29:59","AP372B","Urban","Asset failure","LV",2,428.00000000000006,1.408E-3,3.2899999999999998E-6]
[null,"16/08/2016","09:35:00","NA12","Rural Long","Planned",null,3,1581.0000000000002,3.3649999999999999E-2,2.128E-5]
[null,"16/08/2016","10:13:00","SD35403","Rural Short","Planned",null,8,276,1.7822000000000001E-2,6.457E-5]
[null,"16/08/2016","10:41:00","M51","Rural Short","Planned",null,8,179,1.1558000000000001E-2,6.457E-5]
[null,"16/08/2016","11:18:00","MG19","Rural Long","Asset failure","Distribution substation",106,130.74528301886792,9.8324999999999996E-2,7.5202999999999999E-4]
[null,"16/08/2016","12:48:14","SA11","Urban","Planned",null,20,71.999999999999986,2.3679999999999999E-3,3.2889999999999999E-5]
[null,"16/08/2016","13:01:00","AP125B","Urban","Planned",null,1,11.000000000000002,1.8E-5,1.64E-6]
[null,"16/08/2016","13:26:00","VH23","Rural Short","Planned",null,109,121,0.10645399999999999,8.7978999999999998E-4]
[null,"16/08/2016","14:17:01","AP529C","Urban","Asset failure","LV",1,222,3.6499999999999998E-4,1.64E-6]
[null,"16/08/2016","17:49:00","MG05","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",20,85.199999999999989,1.2089000000000001E-2,1.4189000000000001E-4]
[null,"16/08/2016","18:41:19","VH12","Rural Short","Asset failure","LV",1,879.99999999999989,7.1029999999999999E-3,8.0700000000000007E-6]
[null,"16/08/2016","22:27:25","SA31","Urban","Unknown","Unknown",24,199.00000000000003,7.8530000000000006E-3,3.9459999999999998E-5]
[null,"16/08/2016","22:57:37","AP226D","Urban","Asset failure","LV",1,191.00000000000003,3.1399999999999999E-4,1.64E-6]
[null,"17/08/2016","03:50:00","VH22","Rural Short","Planned",null,74,155,9.2579999999999996E-2,5.9729E-4]
[null,"17/08/2016","08:17:24","HH496C","Urban","Planned",null,38,116,7.2480000000000001E-3,6.2479999999999998E-5]
[null,"17/08/2016","08:29:19","HH496C","Urban","Planned",null,29,74,3.529E-3,4.7679999999999998E-5]
[null,"17/08/2016","08:42:42","SM216B","Urban","Planned",null,149,360.99999999999994,8.8444999999999996E-2,2.4499999999999999E-4]
[null,"17/08/2016","08:55:40","SA16","Urban","Planned",null,46,386.00000000000006,2.9196E-2,7.5640000000000001E-5]
[null,"17/08/2016","09:03:00","NU23","Rural Long","Planned",null,45,331,0.10567500000000001,3.1925999999999998E-4]
[null,"17/08/2016","09:04:06","SM216C","Urban","Planned",null,147,176,4.2541000000000002E-2,2.4170999999999999E-4]
[null,"17/08/2016","09:04:56","SM216B","Urban","Planned",null,105,173.99999999999997,3.0041000000000002E-2,1.7265E-4]
[null,"17/08/2016","09:10:00","HH432B","Urban","Planned",null,34,345,1.9288E-2,5.5909999999999998E-5]
[null,"17/08/2016","09:15:00","SG13","Rural Short","Planned",null,37,147,4.3901000000000003E-2,2.9863999999999997E-4]
[null,"17/08/2016","09:30:00","W30","Rural Short","Planned",null,59,104,4.9526000000000001E-2,4.7622000000000002E-4]
[null,"17/08/2016","09:30:54","MV53","Rural Short","Planned",null,3,405,9.8069999999999997E-3,2.421E-5]
[null,"17/08/2016","09:34:00","NL210C","Urban","Planned",null,291,95.450171821305844,4.5671999999999997E-2,4.7848999999999998E-4]
[null,"17/08/2016","10:45:00","CV757A","Rural Long","Asset failure","HV",1,66,4.6799999999999999E-4,7.0899999999999999E-6]
[null,"17/08/2016","10:46:00","AP365B","Urban","Planned",null,132,281,6.0990000000000003E-2,2.1704999999999999E-4]
[null,"17/08/2016","11:17:00","GU31","Rural Long","Planned",null,1,20,1.4200000000000001E-4,7.0899999999999999E-6]
[null,"17/08/2016","12:56:00","AP351D","Urban","Asset failure","HV",8,84.000000000000014,1.1050000000000001E-3,1.3149999999999999E-5]
[null,"17/08/2016","13:32:01","HH432D","Urban","Overloads",null,1,497,8.1700000000000002E-4,1.64E-6]
[null,"17/08/2016","14:15:00","YK29","Rural Long","Asset failure","Distribution substation",143,200.02797202797203,0.202935,1.01453E-3]
[null,"17/08/2016","14:33:23","AP344F","Urban","Asset failure","LV",1,392,6.4499999999999996E-4,1.64E-6]
[null,"17/08/2016","16:09:00","EL23","Urban","Unknown","Unknown",9.6666699999999999,59.999999999999993,9.5399999999999999E-4,1.5889999999999999E-5]
[null,"17/08/2016","16:20:00","MG19","Rural Long","Unknown","Unknown",3,15,3.19E-4,2.128E-5]
[null,"17/08/2016","18:31:58","AP424A","Urban","Asset failure","LV",1,249,4.0900000000000002E-4,1.64E-6]
[null,"17/08/2016","22:27:00","HH118B","Urban","Planned",null,5,315,2.5899999999999999E-3,8.2199999999999992E-6]
[null,"18/08/2016","03:55:14","MTB21","Rural Short","Asset failure","LV",2,122,1.9689999999999998E-3,1.6140000000000001E-5]
[null,"18/08/2016","08:31:50","NL760C","Urban","Planned",null,37,115,6.9959999999999996E-3,6.084E-5]
[null,"18/08/2016","08:33:00","MV42","Rural Short","Asset failure","HV",144,98.645833333333329,0.11465500000000001,1.1622900000000001E-3]
[null,"18/08/2016","08:35:45","GU31","Rural Long","Planned",null,41,232,6.7484000000000002E-2,2.9087999999999998E-4]
[null,"18/08/2016","08:45:00","SD391","Rural Long","Planned",null,37,359,9.4238000000000002E-2,2.6249999999999998E-4]
[null,"18/08/2016","08:48:00","MTB13","Rural Short","Planned",null,51,191.99999999999997,7.9035999999999995E-2,4.1164000000000001E-4]
[null,"18/08/2016","08:50:00","MG21","Rural Long","Planned",null,2,300,4.2570000000000004E-3,1.419E-5]
[null,"18/08/2016","08:55:00","CD16","Rural Short","Planned",null,34,279,7.6565999999999995E-2,2.7442999999999999E-4]
[null,"18/08/2016","08:56:00","KI11","Rural Long","Planned",null,112,242,0.19229299999999999,7.9460000000000002E-4]
[null,"18/08/2016","09:28:52","NL210A","Urban","Planned",null,25,291,1.1962E-2,4.1109999999999998E-5]
[null,"18/08/2016","09:30:09","NL210A","Urban","Planned",null,48,290.00000000000006,2.2889E-2,7.8930000000000005E-5]
[null,"18/08/2016","09:34:00","MV13","Rural Short","Planned",null,1,177,1.4289999999999999E-3,8.0700000000000007E-6]
[null,"18/08/2016","09:45:00","SG10","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1429,77.256123163051086,0.89107999999999998,1.15341E-2]
[null,"18/08/2016","09:48:00","GA39","Rural Long","Planned",null,37,170,4.4624999999999998E-2,2.6249999999999998E-4]
[null,"18/08/2016","10:03:00","AP226A","Urban","Planned",null,82,181,2.4405E-2,1.3483000000000001E-4]
[null,"18/08/2016","10:33:27","EL11","Urban","Planned",null,36,132,7.8139999999999998E-3,5.9190000000000001E-5]
[null,"18/08/2016","10:41:00","SG09","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",596,126.99999999999999,0.61094400000000004,4.8105800000000001E-3]
[null,"18/08/2016","10:51:00","MTB41","Rural Short","Unknown","Unknown",35.333340999999997,134,3.8216E-2,2.8519E-4]
[null,"18/08/2016","10:55:00","EL02","Urban","Unknown","Unknown",1360,81.602205882352948,0.18248200000000001,2.23624E-3]
[null,"18/08/2016","11:13:00","GU43","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",144,215.75,0.220416,1.0216299999999999E-3]
[null,"18/08/2016","12:10:00","ST36","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",14,218,2.1652999999999999E-2,9.9320000000000005E-5]
[null,"18/08/2016","12:15:00","SD492","Rural Long","Network business","Switching and protection error",1419,110.2536997885835,1.1099559999999999,1.006729E-2]
[null,"18/08/2016","12:38:00","EL11","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",25,131,5.385E-3,4.1109999999999998E-5]
[null,"18/08/2016","13:09:36","SG09","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",4,327,1.0557E-2,3.2289999999999997E-5]
[null,"18/08/2016","13:28:00","BM13","Rural Short","Asset failure","LV",2,116,1.8730000000000001E-3,1.6140000000000001E-5]
[null,"18/08/2016","13:38:51","AP373E","Urban","Asset failure","HV",2,8,2.5999999999999998E-5,3.2899999999999998E-6]
[null,"18/08/2016","13:39:22","AP373E","Urban","Animal","Animal impact",2,7.0000000000000009,2.3E-5,3.2899999999999998E-6]
[null,"18/08/2016","15:06:00","NA13","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",2,58,8.2299999999999995E-4,1.419E-5]
[null,"18/08/2016","16:08:00","HH522B","Urban","Asset failure","HV",72.000035999999994,87,1.03E-2,1.1839E-4]
[null,"18/08/2016","17:50:00","NU04","Rural Short","Asset failure","HV",1,72,5.8100000000000003E-4,8.0700000000000007E-6]
[null,"18/08/2016","18:06:00","MB42","Rural Long","Asset failure","HV",1,14,9.8999999999999994E-5,7.0899999999999999E-6]
[null,"18/08/2016","21:54:00","SD1543","Urban","Planned",null,26,4,1.7100000000000001E-4,4.2750000000000002E-5]
[null,"18/08/2016","22:19:00","PP06","Rural Long","Animal","Animal impact",431,102.99999999999999,0.31495200000000001,3.0577899999999999E-3]
[null,"18/08/2016","22:19:00","PP06","Rural Long","Animal","Animal impact",null,98.614849187935036,0.30154300000000001,0]
[null,"18/08/2016","23:44:00","MB71","Rural Long","Animal","Animal impact",148,145.64864864864865,0.15293200000000001,1.0500100000000001E-3]
[null,"19/08/2016","01:43:00","MG10","Rural Long","Asset failure","Distribution substation",20,166.74999999999997,2.3661000000000001E-2,1.4189000000000001E-4]
[null,"19/08/2016","03:13:00","SG04","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",211,19,3.2357999999999998E-2,1.70308E-3]
[null,"19/08/2016","07:12:00","AP132E","Urban","Weather",null,69,222.52173913043481,2.5246999999999999E-2,1.1346E-4]
[null,"19/08/2016","07:23:46","HH145E","Urban","Asset failure","LV",1,121,1.9900000000000001E-4,1.64E-6]
[null,"19/08/2016","07:37:08","PL14","Urban","Weather",null,1,279,4.5899999999999999E-4,1.64E-6]
[null,"19/08/2016","07:44:52","EL17","Urban","Planned",null,1,81,1.3300000000000001E-4,1.64E-6]
[null,"19/08/2016","07:46:22","EL17","Urban","Planned",null,1,80.000000000000014,1.3200000000000001E-4,1.64E-6]
[null,"19/08/2016","07:46:52","EL17","Urban","Planned",null,1,79,1.2999999999999999E-4,1.64E-6]
[null,"19/08/2016","07:47:16","EL17","Urban","Planned",null,2,78.000000000000014,2.5700000000000001E-4,3.2899999999999998E-6]
[null,"19/08/2016","07:48:04","EL17","Urban","Planned",null,3,77,3.8000000000000002E-4,4.9300000000000002E-6]
[null,"19/08/2016","08:12:00","KI31","Rural Short","Planned",null,1,40,3.2299999999999999E-4,8.0700000000000007E-6]
[null,"19/08/2016","08:35:13","HH177F","Urban","Planned",null,70,342,3.9364000000000003E-2,1.1510000000000001E-4]
[null,"19/08/2016","08:36:54","SM179D","Urban","Planned",null,54,359.99999999999994,3.1965E-2,8.8789999999999995E-5]
[null,"19/08/2016","08:38:31","CL23","Rural Long","Planned",null,56,401,0.15931699999999999,3.9730000000000001E-4]
[null,"19/08/2016","09:04:27","SM349C","Urban","Planned",null,63,207,2.1443E-2,1.0359E-4]
[null,"19/08/2016","09:08:46","HH130D","Urban","Planned",null,43,8,5.6599999999999999E-4,7.0699999999999997E-5]
[null,"19/08/2016","09:12:00","HH177G","Urban","Planned",null,140,187,4.3048000000000003E-2,2.3020000000000001E-4]
[null,"19/08/2016","09:29:43","GA25","Rural Short","Planned",null,50,330,0.13317899999999999,4.0357000000000001E-4]
[null,"19/08/2016","09:42:00","ST22","Rural Short","Unknown","Unknown",265,188,0.40211999999999998,2.1389299999999998E-3]
[null,"19/08/2016","09:50:06","EL01C","Urban","Planned",null,86,237,3.3514000000000002E-2,1.4140999999999999E-4]
[null,"19/08/2016","09:53:00","MG17","Rural Long","Animal","Animal impact",2,72,1.0219999999999999E-3,1.419E-5]
[null,"19/08/2016","09:54:00","MV13","Rural Short","Planned",null,10,207,1.6708000000000001E-2,8.0710000000000005E-5]
[null,"19/08/2016","10:05:00","AP365B","Urban","Planned",null,208,258,8.8238999999999998E-2,3.4201000000000001E-4]
[null,"19/08/2016","10:12:00","NU05","Rural Short","Planned",null,7,21,1.1869999999999999E-3,5.6499999999999998E-5]
[null,"19/08/2016","10:16:00","EL260C","Urban","Asset failure","HV",1647,87,0.23560900000000001,2.7081499999999999E-3]
[null,"19/08/2016","10:30:00","NA13","Rural Long","Asset failure","HV",7,264,1.3110999999999999E-2,4.9660000000000002E-5]
[null,"19/08/2016","10:44:00","GA28","Rural Long","Planned",null,13,183,1.6878000000000001E-2,9.2230000000000003E-5]
[null,"19/08/2016","10:54:00","MG11","Rural Short","Planned",null,3,86,2.0820000000000001E-3,2.421E-5]
[null,"19/08/2016","11:19:00","LM12","Rural Long","Planned",null,2,44.999999999999993,6.3900000000000003E-4,1.419E-5]
[null,"19/08/2016","14:36:00","HH148B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1398,46,0.105741,2.2987200000000002E-3]
[null,"19/08/2016","16:16:00","LX24","Rural Short","Asset failure","HV",3,78.666666666666671,1.905E-3,2.421E-5]
[null,"19/08/2016","17:53:49","MTB52","Rural Long","Asset failure","LV",18.666647999999999,110.99999999999999,1.47E-2,1.3243E-4]
[null,"19/08/2016","18:48:06","MI08","Rural Long","Asset failure","LV",1,206.99999999999997,1.469E-3,7.0899999999999999E-6]
[null,"19/08/2016","19:18:12","SA33","Urban","Asset failure","LV",1,467,7.6800000000000002E-4,1.64E-6]
[null,"19/08/2016","19:34:00","SA12","Urban","Vegetation","Grow-in - NSP responsibility",390,130.56666666666666,8.3728999999999998E-2,6.4126999999999999E-4]
[null,"19/08/2016","19:56:34","HH145B","Urban","Asset failure","LV",1,321.00000000000006,5.2800000000000004E-4,1.64E-6]
[null,"19/08/2016","20:48:40","AP529A","Urban","Overloads",null,1,709,1.1659999999999999E-3,1.64E-6]
[null,"20/08/2016","00:37:00","HH409C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",132,491,0.10657,2.1704999999999999E-4]
[null,"20/08/2016","02:05:00","NL21","Urban","Unknown","Unknown",21,258,8.9090000000000003E-3,3.4530000000000003E-5]
[null,"20/08/2016","02:29:00","SA744D","Urban","Asset failure","HV",123,422.90243902439028,8.5530999999999996E-2,2.0225000000000001E-4]
[null,"20/08/2016","07:47:00","MTB51","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1013,65,0.46714699999999998,7.1868699999999997E-3]
[null,"20/08/2016","16:19:00","MI02","Rural Short","Unknown","Unknown",2.666668,276,5.9410000000000001E-3,2.1520000000000001E-5]
[null,"21/08/2016","00:15:00","SD412","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1129,219.00354295837028,1.995706,9.1126699999999998E-3]
[null,"21/08/2016","08:19:00","HH428D","Urban","Planned",null,1,172.00000000000003,2.8299999999999999E-4,1.64E-6]
[null,"21/08/2016","08:43:00","AP372F","Urban","Planned",null,21,173,5.9740000000000001E-3,3.4530000000000003E-5]
[null,"21/08/2016","09:26:00","AP227B","Urban","Planned",null,16,343.00000000000006,9.0240000000000008E-3,2.6310000000000001E-5]
[null,"21/08/2016","11:16:59","NL111A","Urban","Planned",null,11,227,4.1060000000000003E-3,1.8090000000000001E-5]
[null,"21/08/2016","15:05:00","HK05","Rural Long","Asset failure","HV",3,120,2.5539999999999998E-3,2.128E-5]
[null,"21/08/2016","23:31:45","EL23","Urban","Asset failure","LV",0.99999899999999997,58,9.5000000000000005E-5,1.64E-6]
[null,"22/08/2016","06:31:00","MI33","Rural Long","Asset failure","HV",49,314.36734693877548,0.10928599999999999,3.4764000000000003E-4]
[null,"22/08/2016","08:12:58","NA52","Rural Long","Planned",null,74,352,0.18480099999999999,5.2499999999999997E-4]
[null,"22/08/2016","08:29:00","NA30","Rural Long","Planned",null,1,191.99999999999997,1.3619999999999999E-3,7.0899999999999999E-6]
[null,"22/08/2016","08:37:58","NU19","Rural Long","Planned",null,21,399.00000000000006,5.9445999999999999E-2,1.4898999999999999E-4]
[null,"22/08/2016","08:41:08","SA711C","Urban","Planned",null,94,233,3.6013000000000003E-2,1.5456000000000001E-4]
[null,"22/08/2016","08:42:00","SA711C","Urban","Planned",null,33,232,1.2588999999999999E-2,5.4259999999999999E-5]
[null,"22/08/2016","08:45:47","SA11","Urban","Planned",null,44,165,1.1938000000000001E-2,7.2349999999999997E-5]
[null,"22/08/2016","08:49:01","PL803C","Urban","Planned",null,64,357,3.7568999999999998E-2,1.0522999999999999E-4]
[null,"22/08/2016","08:52:36","MV64","Rural Short","Planned",null,70,78,4.4069999999999998E-2,5.6499999999999996E-4]
[null,"22/08/2016","08:54:27","MV64","Rural Short","Planned",null,65,76,3.9872999999999999E-2,5.2464000000000005E-4]
[null,"22/08/2016","08:55:29","MV64","Rural Short","Planned",null,62,75,3.7532000000000003E-2,5.0042999999999995E-4]
[null,"22/08/2016","08:56:59","MV64","Rural Short","Planned",null,57,73,3.3584999999999997E-2,4.6006999999999998E-4]
[null,"22/08/2016","08:58:22","MV64","Rural Short","Planned",null,31,71,1.7765E-2,2.5021E-4]
[null,"22/08/2016","08:59:23","MV64","Rural Short","Planned",null,31,71,1.7765E-2,2.5021E-4]
[null,"22/08/2016","09:12:01","AP529C","Urban","Planned",null,59,323,3.1335000000000002E-2,9.7009999999999994E-5]
[null,"22/08/2016","09:21:00","SA31","Urban","Planned",null,44,338.99999999999994,2.4525999999999999E-2,7.2349999999999997E-5]
[null,"22/08/2016","09:24:00","BM44","Rural Short","Planned",null,23,167,3.1001999999999998E-2,1.8563999999999999E-4]
[null,"22/08/2016","09:46:00","AP214C","Urban","Planned",null,71,206,2.4049000000000001E-2,1.1674E-4]
[null,"22/08/2016","10:05:00","MB42","Rural Long","Planned",null,71,4,2.0149999999999999E-3,5.0372000000000004E-4]
[null,"22/08/2016","10:11:09","SA14","Urban","Planned",null,22,94,3.3999999999999998E-3,3.6170000000000001E-5]
[null,"22/08/2016","10:12:02","G41","Rural Long","Planned",null,42,92,2.7414000000000001E-2,2.9796999999999999E-4]
[null,"22/08/2016","10:16:00","SM126C","Urban","Planned",null,62,119,1.2132E-2,1.0195E-4]
[null,"22/08/2016","10:17:00","PA15","Rural Long","Planned",null,2,33,4.6799999999999999E-4,1.419E-5]
[null,"22/08/2016","11:31:48","SA11","Urban","Planned",null,56,102,9.3919999999999993E-3,9.2079999999999999E-5]
[null,"22/08/2016","12:32:00","BT06","Rural Long","Asset failure","HV",143,315.51048951048955,0.32009599999999999,1.01453E-3]
[null,"22/08/2016","13:40:00","NA22","Rural Long","Planned",null,1,175,1.242E-3,7.0899999999999999E-6]
[null,"22/08/2016","14:04:00","NA29","Rural Long","Asset failure","HV",5,76,2.696E-3,3.5469999999999998E-5]
[null,"22/08/2016","15:52:00","MB41","Rural Long","Asset failure","HV",71,155,7.8076999999999994E-2,5.0372000000000004E-4]
[null,"22/08/2016","18:22:00","SB15","Rural Long","Asset failure","HV",103,1243,0.90832000000000002,7.3074999999999995E-4]
[null,"22/08/2016","22:38:41","HH107C","Urban","Asset failure","LV",41,85.999999999999986,5.7980000000000002E-3,6.7420000000000002E-5]
[null,"22/08/2016","22:49:00","MTB52","Rural Long","Asset failure","HV",961,63.285119667013532,0.431475,6.8179499999999997E-3]
[null,"22/08/2016","23:31:31","GA53","Rural Short","Unknown","Unknown",1,216,1.743E-3,8.0700000000000007E-6]
[null,"23/08/2016","00:10:00","NA05","Rural Long","Third Party","Vehicle impact",74,173.5,9.1088000000000002E-2,5.2499999999999997E-4]
[null,"23/08/2016","00:51:00","NL115B","Urban","Asset failure","HV",40,158,1.0392E-2,6.5770000000000002E-5]
[null,"23/08/2016","06:07:00","ME231F","Urban","Planned",null,13,2,4.3000000000000002E-5,2.1379999999999999E-5]
[null,"23/08/2016","07:03:00","KA28","Rural Long","Unknown","Unknown",28,178,3.5360000000000003E-2,1.9865E-4]
[null,"23/08/2016","08:04:00","GA28","Rural Long","Planned",null,670,55.856716417910448,0.26551000000000002,4.7534099999999996E-3]
[null,"23/08/2016","08:11:35","CBD366S","CBD","Planned",null,17,280,0.89955600000000002,3.2127000000000002E-3]
[null,"23/08/2016","08:12:45","LX51","Rural Short","Planned",null,45,438,0.15908800000000001,3.6321999999999998E-4]
[null,"23/08/2016","08:16:53","LX51","Rural Short","Planned",null,42,434,0.14712600000000001,3.39E-4]
[null,"23/08/2016","08:25:50","MG39","Rural Short","Planned",null,114,339,0.31192900000000001,9.2015E-4]
[null,"23/08/2016","08:28:00","EL18","Urban","Planned",null,1,588,9.6699999999999998E-4,1.64E-6]
[null,"23/08/2016","08:33:27","NL234A","Urban","Planned",null,45,399.00000000000006,2.9523000000000001E-2,7.3990000000000001E-5]
[null,"23/08/2016","08:34:23","NL234A","Urban","Planned",null,80,406.99999999999994,5.3538000000000002E-2,1.3154E-4]
[null,"23/08/2016","08:36:06","SA36","Urban","Planned",null,19,189,5.9049999999999997E-3,3.1239999999999999E-5]
[null,"23/08/2016","08:36:32","SA36","Urban","Planned",null,9,188,2.7820000000000002E-3,1.4800000000000001E-5]
[null,"23/08/2016","08:37:00","HH496F","Urban","Planned",null,88,49.090909090909086,7.1029999999999999E-3,1.4469999999999999E-4]
[null,"23/08/2016","08:41:46","SM126C","Urban","Planned",null,43,141.99999999999997,1.004E-2,7.0699999999999997E-5]
[null,"23/08/2016","08:58:20","ST12","Rural Short","Planned",null,5,344.99999999999994,1.3923E-2,4.036E-5]
[null,"23/08/2016","09:04:17","SA744D","Urban","Planned",null,35,52,2.993E-3,5.7550000000000003E-5]
[null,"23/08/2016","09:07:43","AP529C","Urban","Planned",null,72,381,4.5106E-2,1.1839E-4]
[null,"23/08/2016","09:10:00","M81","Rural Long","Planned",null,84,81,4.8272000000000002E-2,5.9595000000000004E-4]
[null,"23/08/2016","09:13:00","KI42","Rural Long","Planned",null,13,112,1.0330000000000001E-2,9.2230000000000003E-5]
[null,"23/08/2016","09:16:30","CV01","Rural Short","Planned",null,27,127,2.7677E-2,2.1793E-4]
[null,"23/08/2016","09:40:03","GA29","Rural Long","Planned",null,3,55,1.1709999999999999E-3,2.128E-5]
[null,"23/08/2016","09:40:37","EL01C","Urban","Planned",null,127,135,2.8191000000000001E-2,2.0882999999999999E-4]
[null,"23/08/2016","10:11:07","NL234A","Urban","Planned",null,124,102.99999999999999,2.1000999999999999E-2,2.0389E-4]
[null,"23/08/2016","10:26:33","M51","Rural Short","Planned",null,22,141,2.5038000000000001E-2,1.7757E-4]
[null,"23/08/2016","10:50:00","BM53","Rural Short","Vegetation","Grow-in - NSP responsibility",64,94.84375,4.8994000000000003E-2,5.1657000000000005E-4]
[null,"23/08/2016","11:14:00","AP214C","Urban","Planned",null,139,188.99999999999997,4.3196999999999999E-2,2.2855999999999999E-4]
[null,"23/08/2016","11:18:00","LM31","Rural Long","Planned",null,2,101.99999999999999,1.4469999999999999E-3,1.419E-5]
[null,"23/08/2016","11:43:00","MI02","Rural Short","Animal","Animal impact",19.666668000000001,157,2.4922E-2,1.5873999999999999E-4]
[null,"23/08/2016","11:46:00","PL02","Urban","Planned",null,2,299.00000000000006,9.8299999999999993E-4,3.2899999999999998E-6]
[null,"23/08/2016","13:03:00","CN02","Rural Long","Unknown","Unknown",77,285.10389610389609,0.155749,5.4628999999999995E-4]
[null,"23/08/2016","13:22:00","CM28","Rural Long","Third Party","Vehicle impact",61,140,6.0588000000000003E-2,4.3277000000000002E-4]
[null,"23/08/2016","13:45:00","GA26","Urban","Asset failure","HV",144,74,1.7521999999999999E-2,2.3677999999999999E-4]
[null,"23/08/2016","14:20:00","CL23","Rural Long","Asset failure","Distribution substation",16,174,1.9751000000000001E-2,1.1351E-4]
[null,"23/08/2016","15:58:00","SG09","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",30,107,2.5909000000000001E-2,2.4214000000000001E-4]
[null,"23/08/2016","20:27:00","CBD103C","Urban","Asset failure","HV",71,266,3.1053999999999998E-2,1.1674E-4]
[null,"23/08/2016","20:57:14","NL760B","Urban","Asset failure","LV",1,233.00000000000003,3.8299999999999999E-4,1.64E-6]
[null,"23/08/2016","23:23:55","CBD412M","Urban","Planned",null,38,22,1.3749999999999999E-3,6.2479999999999998E-5]
[null,"23/08/2016","23:35:46","MTB13","Rural Short","Unknown","Unknown",15.999984,72,9.2980000000000007E-3,1.2914E-4]
[null,"24/08/2016","05:49:52","ME231E","Urban","Planned",null,39,64,4.104E-3,6.4129999999999998E-5]
[null,"24/08/2016","05:51:05","ME231E","Urban","Planned",null,19,64,1.9989999999999999E-3,3.1239999999999999E-5]
[null,"24/08/2016","07:32:00","MG29","Rural Long","Asset failure","HV",2,149,2.114E-3,1.419E-5]
[null,"24/08/2016","08:09:00","MT07","Rural Long","Planned",null,101,343,0.24578,7.1655999999999998E-4]
[null,"24/08/2016","08:14:00","SA32","Urban","Planned",null,51,326,2.7338000000000001E-2,8.386E-5]
[null,"24/08/2016","08:19:21","HH496F","Urban","Planned",null,39,211.99999999999997,1.3594999999999999E-2,6.4129999999999998E-5]
[null,"24/08/2016","08:22:04","NL234C","Urban","Planned",null,127,243,5.0744999999999998E-2,2.0882999999999999E-4]
[null,"24/08/2016","08:26:53","HH130D","Urban","Planned",null,43,306,2.1635999999999999E-2,7.0699999999999997E-5]
[null,"24/08/2016","08:45:32","MG41","Urban","Planned",null,58,304,2.8992E-2,9.5370000000000003E-5]
[null,"24/08/2016","08:52:00","SA36","Urban","Planned",null,27,39.333333333333336,1.7459999999999999E-3,4.4400000000000002E-5]
[null,"24/08/2016","08:54:18","ME231E","Urban","Planned",null,101,331.99999999999994,5.5135999999999998E-2,1.6606999999999999E-4]
[null,"24/08/2016","08:54:43","NL451C","Urban","Planned",null,36,343,2.0303999999999999E-2,5.9190000000000001E-5]
[null,"24/08/2016","08:57:00","PL803C","Urban","Planned",null,61,216.99999999999997,2.1766000000000001E-2,1.003E-4]
[null,"24/08/2016","08:57:00","M81","Rural Long","Planned",null,26,228,4.2056999999999997E-2,1.8446000000000001E-4]
[null,"24/08/2016","09:06:00","YK30","Rural Long","Planned",null,37,163.99999999999997,4.3049999999999998E-2,2.6249999999999998E-4]
[null,"24/08/2016","09:08:20","MV14","Rural Short","Planned",null,5,151,6.0939999999999996E-3,4.036E-5]
[null,"24/08/2016","09:24:00","MI31","Rural Long","Planned",null,3,119,2.5330000000000001E-3,2.128E-5]
[null,"24/08/2016","09:31:00","G21","Rural Long","Planned",null,3,149,3.1710000000000002E-3,2.128E-5]
[null,"24/08/2016","09:42:00","KI12","Rural Long","Planned",null,13,210,1.9368E-2,9.2230000000000003E-5]
[null,"24/08/2016","09:55:58","M51","Rural Short","Planned",null,22,157,2.7879000000000001E-2,1.7757E-4]
[null,"24/08/2016","10:02:00","SD37301","Rural Short","Planned",null,1,73,5.8900000000000001E-4,8.0700000000000007E-6]
[null,"24/08/2016","10:05:00","ST16","Rural Short","Planned",null,16,137,1.7693E-2,1.2914E-4]
[null,"24/08/2016","10:06:00","SD342","Rural Short","Planned",null,1,70,5.6499999999999996E-4,8.0700000000000007E-6]
[null,"24/08/2016","10:36:00","W18","Rural Long","Planned",null,25,136,2.4122000000000001E-2,1.7736999999999999E-4]
[null,"24/08/2016","10:37:41","BM32","Rural Short","Asset failure","LV",1,289,2.333E-3,8.0700000000000007E-6]
[null,"24/08/2016","10:42:18","SG14","Rural Short","Planned",null,41,196,6.4862000000000003E-2,3.3093E-4]
[null,"24/08/2016","10:55:00","SM126C","Urban","Planned",null,73,211,2.5326999999999999E-2,1.2003E-4]
[null,"24/08/2016","10:59:00","LX71","Rural Long","Planned",null,124,22.048387096774196,1.9397000000000001E-2,8.7973999999999995E-4]
[null,"24/08/2016","11:01:00","GA37","Rural Long","Third Party","Vehicle impact",22,197,3.0748000000000001E-2,1.5608000000000001E-4]
[null,"24/08/2016","11:37:00","CD15","Rural Long","Asset failure","HV",1,20,1.4200000000000001E-4,7.0899999999999999E-6]
[null,"24/08/2016","12:06:00","SD354","Rural Short","Asset failure","Subtransmission",823,2,1.3285999999999999E-2,6.6427999999999999E-3]
[null,"24/08/2016","12:06:00","SD355","Rural Long","Asset failure","Subtransmission",3544,2,5.0286999999999998E-2,2.51434E-2]
[null,"24/08/2016","13:57:00","VH45","Rural Short","Unknown","Unknown",11,53,4.7060000000000001E-3,8.8789999999999995E-5]
[null,"24/08/2016","14:52:00","AP373A","Urban","Unknown","Unknown",159.66673900000001,2.8455110992152224,7.4700000000000005E-4,2.6254000000000002E-4]
[null,"24/08/2016","14:53:00","MTB41","Rural Short","Asset failure","HV",35.333340999999997,215.99999999999997,6.1601000000000003E-2,2.8519E-4]
[null,"24/08/2016","15:29:00","EL02","Urban","Asset failure","HV",1,93,1.5300000000000001E-4,1.64E-6]
[null,"24/08/2016","21:43:00","EL01C","Urban","Animal","Animal impact",57.333362000000001,111,1.0463999999999999E-2,9.4270000000000004E-5]
[null,"25/08/2016","06:12:00","SM350H","Urban","Planned",null,240,26.024999999999999,1.027E-2,3.9462999999999998E-4]
[null,"25/08/2016","08:16:40","SA744D","Urban","Planned",null,53,426,3.7124999999999998E-2,8.7150000000000004E-5]
[null,"25/08/2016","08:19:07","NL234A","Urban","Planned",null,54,386,3.4273999999999999E-2,8.8789999999999995E-5]
[null,"25/08/2016","08:19:36","NL234A","Urban","Planned",null,51,386,3.2370000000000003E-2,8.386E-5]
[null,"25/08/2016","08:25:20","HH496D","Urban","Planned",null,41,362.99999999999994,2.4472000000000001E-2,6.7420000000000002E-5]
[null,"25/08/2016","08:37:00","SA36","Urban","Planned",null,24,448.00000000000006,1.7679E-2,3.9459999999999998E-5]
[null,"25/08/2016","08:38:18","EL01R","Urban","Planned",null,81,241,3.2098000000000002E-2,1.3318999999999999E-4]
[null,"25/08/2016","08:40:00","SD322","Rural Long","Planned",null,108,312,0.239061,7.6621999999999997E-4]
[null,"25/08/2016","08:57:00","GA22","Rural Short","Planned",null,9,328,2.3827000000000001E-2,7.2639999999999996E-5]
[null,"25/08/2016","08:59:00","EL16","Urban","Planned",null,44,176.99999999999997,1.2806E-2,7.2349999999999997E-5]
[null,"25/08/2016","09:01:00","M13","Rural Long","Planned",null,89,376.99999999999994,0.23804600000000001,6.3142000000000005E-4]
[null,"25/08/2016","09:20:00","MV62","Rural Short","Planned",null,80,286,0.18467500000000001,6.4572000000000002E-4]
[null,"25/08/2016","09:24:00","EL09","Urban","Asset failure","HV",2432,114.4346217105263,0.45761499999999999,3.9989200000000004E-3]
[null,"25/08/2016","09:31:00","GA27","Rural Long","Planned",null,166,253.81927710843371,0.29892600000000003,1.17771E-3]
[null,"25/08/2016","09:34:00","CM20","Rural Long","Planned",null,218,325,0.50265499999999996,1.54663E-3]
[null,"25/08/2016","09:46:00","MI32","Rural Long","Planned",null,1,52,3.6900000000000002E-4,7.0899999999999999E-6]
[null,"25/08/2016","09:51:00","SM126C","Urban","Planned",null,17,303,8.4700000000000001E-3,2.7949999999999998E-5]
[null,"25/08/2016","09:55:00","MI15","Rural Long","Planned",null,1,127,9.01E-4,7.0899999999999999E-6]
[null,"25/08/2016","10:15:45","SM126C","Urban","Planned",null,90,55,8.1390000000000004E-3,1.4799E-4]
[null,"25/08/2016","15:50:00","M23","Rural Long","Unknown","Unknown",2,20,2.8400000000000002E-4,1.419E-5]
[null,"25/08/2016","18:02:00","CN12","Rural Long","Asset failure","HV",48,63,2.1454000000000001E-2,3.4054000000000002E-4]
[null,"25/08/2016","19:28:24","EL01A","Urban","Asset failure","LV",106,716,0.124795,1.7430000000000001E-4]
[null,"25/08/2016","21:44:09","HH145B","Urban","Asset failure","LV",1,761.00000000000011,1.2509999999999999E-3,1.64E-6]
[null,"25/08/2016","23:21:17","HH428F","Urban","Asset failure","LV",17.666649,68,1.9750000000000002E-3,2.9050000000000001E-5]
[null,"26/08/2016","08:34:26","KI11","Rural Long","Planned",null,33,273.00000000000006,6.3916000000000001E-2,2.3411999999999999E-4]
[null,"26/08/2016","08:42:16","SA14","Urban","Planned",null,44,384.99999999999994,2.7854E-2,7.2349999999999997E-5]
[null,"26/08/2016","08:42:46","SA14","Urban","Planned",null,43,385,2.7220999999999999E-2,7.0699999999999997E-5]
[null,"26/08/2016","08:43:00","MI20","Rural Long","Planned",null,26,204,3.7629999999999997E-2,1.8446000000000001E-4]
[null,"26/08/2016","08:43:13","SA14","Urban","Planned",null,40,384,2.5256000000000001E-2,6.5770000000000002E-5]
[null,"26/08/2016","08:56:00","SM410B","Urban","Planned",null,109,379.00000000000006,6.7927000000000001E-2,1.7923E-4]
[null,"26/08/2016","08:59:00","MI11","Rural Long","Planned",null,2,125.99999999999999,1.7880000000000001E-3,1.419E-5]
[null,"26/08/2016","09:06:53","SD31200","Rural Long","Planned",null,49,103,3.5806999999999999E-2,3.4764000000000003E-4]
[null,"26/08/2016","09:07:34","NL115E","Urban","Planned",null,40,67,4.4070000000000003E-3,6.5770000000000002E-5]
[null,"26/08/2016","09:23:00","YK12","Rural Long","Planned",null,3,37,7.8799999999999996E-4,2.128E-5]
[null,"26/08/2016","09:46:00","M73","Rural Long","Unknown","Unknown",1,26.999999999999996,1.92E-4,7.0899999999999999E-6]
[null,"26/08/2016","09:46:00","GA39","Rural Long","Planned",null,1,118,8.3699999999999996E-4,7.0899999999999999E-6]
[null,"26/08/2016","10:10:00","SM126C","Urban","Planned",null,115,145,2.7418999999999999E-2,1.8908999999999999E-4]
[null,"26/08/2016","10:41:00","AP149D","Urban","Planned",null,71,209,2.4400000000000002E-2,1.1674E-4]
[null,"26/08/2016","11:27:00","MI11","Rural Long","Planned",null,1,158,1.121E-3,7.0899999999999999E-6]
[null,"26/08/2016","11:32:00","AP529C","Urban","Planned",null,56,69,6.3540000000000003E-3,9.2079999999999999E-5]
[null,"26/08/2016","13:47:00","LX63","Rural Long","Unknown","Unknown",19,195,2.6286E-2,1.348E-4]
[null,"26/08/2016","14:59:00","VH45","Rural Short","Asset failure","HV",48,94.250000000000014,3.6514999999999999E-2,3.8743000000000002E-4]
[null,"26/08/2016","18:46:10","EL10","Urban","Asset failure","LV",47,1147.0000000000002,8.8641999999999999E-2,7.7280000000000005E-5]
[null,"26/08/2016","20:45:00","SG12","Rural Short","Unknown","Unknown",181,125,0.182617,1.46093E-3]
[null,"26/08/2016","23:17:05","EL09","Urban","Asset failure","LV",1,112.00000000000001,1.84E-4,1.64E-6]
[null,"27/08/2016","08:10:55","SM410D","Urban","Planned",null,76,454,5.6735000000000001E-2,1.2496999999999999E-4]
[null,"27/08/2016","09:01:00","SA12","Urban","Planned",null,1,304,5.0000000000000001E-4,1.64E-6]
[null,"27/08/2016","15:11:00","VH34","Rural Short","Asset failure","HV",139,125.54676258992806,0.14085500000000001,1.1219299999999999E-3]
[null,"27/08/2016","19:15:03","HH121A","Urban","Asset failure","LV",65,791.00000000000011,8.4541000000000005E-2,1.0688000000000001E-4]
[null,"28/08/2016","00:40:00","HH130D","Urban","Planned",null,112,373,6.8692000000000003E-2,1.8416E-4]
[null,"28/08/2016","08:03:00","AP365D1","Urban","Planned",null,3,297,1.4649999999999999E-3,4.9300000000000002E-6]
[null,"28/08/2016","09:01:00","AP355A","Urban","Planned",null,70,371,4.2701999999999997E-2,1.1510000000000001E-4]
[null,"28/08/2016","09:15:00","SA744C","Urban","Planned",null,16,388.75,1.0227999999999999E-2,2.6310000000000001E-5]
[null,"28/08/2016","10:55:00","GU41","Rural Long","Unknown","Unknown",2,257,3.6470000000000001E-3,1.419E-5]
[null,"28/08/2016","16:50:00","HH403B","Urban","Unknown","Unknown",18.333314999999999,40,1.206E-3,3.0150000000000001E-5]
[null,"28/08/2016","22:30:00","HH118B","Urban","Planned",null,7,469,5.398E-3,1.151E-5]
[null,"28/08/2016","22:51:08","AP355A","Urban","Asset failure","LV",1,391,6.4300000000000002E-4,1.64E-6]
[null,"28/08/2016","23:42:23","NL234C","Urban","Planned",null,5,448,3.6830000000000001E-3,8.2199999999999992E-6]
[null,"29/08/2016","02:01:00","NL234C","Urban","Planned",null,205,254,8.5618E-2,3.3708000000000002E-4]
[null,"29/08/2016","05:36:00","HH409D","Urban","Unknown","Unknown",118.66672199999999,263.77528193624499,5.1469000000000001E-2,1.9511999999999999E-4]
[null,"29/08/2016","07:43:45","ST36","Rural Long","Planned",null,4,242,6.868E-3,2.8379999999999999E-5]
[null,"29/08/2016","08:04:27","KA01","Rural Short","Planned",null,68,407.00000000000006,0.223385,5.4885999999999997E-4]
[null,"29/08/2016","08:05:16","KA01","Rural Short","Planned",null,104,406.00000000000006,0.34080899999999997,8.3942999999999995E-4]
[null,"29/08/2016","08:53:08","AP425A","Urban","Planned",null,57,352.99999999999994,3.3085000000000003E-2,9.3720000000000004E-5]
[null,"29/08/2016","08:55:42","AP344E","Urban","Planned",null,105,483,8.3390000000000006E-2,1.7265E-4]
[null,"29/08/2016","08:56:00","MI11","Rural Long","Planned",null,2,136,1.9300000000000001E-3,1.419E-5]
[null,"29/08/2016","09:00:00","YK06","Rural Short","Asset failure","HV",3,7,1.7000000000000001E-4,2.421E-5]
[null,"29/08/2016","09:04:32","EL01L","Urban","Planned",null,9,210,3.1080000000000001E-3,1.4800000000000001E-5]
[null,"29/08/2016","09:05:22","EL01M","Urban","Planned",null,39,208.99999999999997,1.3403E-2,6.4129999999999998E-5]
[null,"29/08/2016","09:12:00","MV61","Urban","Planned",null,123,303,6.1281000000000002E-2,2.0225000000000001E-4]
[null,"29/08/2016","09:25:00","G28","Rural Long","Planned",null,1,313,2.2209999999999999E-3,7.0899999999999999E-6]
[null,"29/08/2016","09:48:00","CN52","Rural Long","Planned",null,1,56.999999999999993,4.0400000000000001E-4,7.0899999999999999E-6]
[null,"29/08/2016","10:00:22","HH148A","Urban","Planned",null,24,150.00000000000003,5.9189999999999998E-3,3.9459999999999998E-5]
[null,"29/08/2016","10:06:00","W25","Rural Long","Planned",null,42,204,6.0787000000000001E-2,2.9796999999999999E-4]
[null,"29/08/2016","10:16:58","HH121A","Urban","Planned",null,65,369.00000000000006,3.9438000000000001E-2,1.0688000000000001E-4]
[null,"29/08/2016","10:26:00","SG14","Rural Short","Planned",null,1,89,7.18E-4,8.0700000000000007E-6]
[null,"29/08/2016","10:31:57","PP02","Urban","Asset failure","LV",4.9999950000000002,119.00000000000001,9.7799999999999992E-4,8.2199999999999992E-6]
[null,"29/08/2016","10:32:00","BT15","Rural Long","Unknown","Unknown",29,43.517241379310342,8.9529999999999992E-3,2.0573999999999999E-4]
[null,"29/08/2016","11:09:00","LX73","Rural Long","Planned",null,2,121,1.717E-3,1.419E-5]
[null,"29/08/2016","11:46:00","MI11","Rural Long","Planned",null,1,100,7.0899999999999999E-4,7.0899999999999999E-6]
[null,"29/08/2016","12:05:00","SA744G","Urban","Planned",null,2,32,1.05E-4,3.2899999999999998E-6]
[null,"29/08/2016","14:42:00","AP424F","Urban","Asset failure","HV",1219,156.78917145200984,0.31426700000000002,2.0043999999999999E-3]
[null,"29/08/2016","15:32:00","M81","Rural Long","Unknown","Unknown",492,300.71544715447158,1.049666,3.4905600000000002E-3]
[null,"29/08/2016","15:32:00","M81","Rural Long","Unknown","Unknown",null,115.62343358395989,1.3092090000000001,0]
[null,"29/08/2016","18:00:00","PA04","Urban","Asset failure","HV",679,152,0.16970399999999999,1.11648E-3]
[null,"29/08/2016","18:05:00","CN41","Rural Long","Unknown","Unknown",29,133,2.7363999999999999E-2,2.0573999999999999E-4]
[null,"29/08/2016","18:50:03","MB12","Rural Long","Asset failure","LV",16,141,1.6005999999999999E-2,1.1351E-4]
[null,"29/08/2016","22:01:00","CN41","Rural Long","Animal","Animal impact",29,168.99999999999997,3.4771000000000003E-2,2.0573999999999999E-4]
[null,"30/08/2016","02:46:00","KI11","Rural Long","Unknown","Unknown",305,205.99999999999997,0.44575599999999999,2.1638600000000001E-3]
[null,"30/08/2016","04:49:00","PA14","Rural Long","Unknown","Unknown",446,201,0.63600599999999996,3.1642100000000002E-3]
[null,"30/08/2016","05:43:00","MG35","Rural Long","Asset failure","Distribution substation",15,132,1.4047E-2,1.0642E-4]
[null,"30/08/2016","06:38:54","GU41","Rural Long","Asset failure","LV",2,406,5.7609999999999996E-3,1.419E-5]
[null,"30/08/2016","06:59:00","NL115F","Urban","Asset failure","HV",2154,78.873259052924794,0.27935399999999999,3.5418099999999998E-3]
[null,"30/08/2016","07:34:00","W21","Rural Long","Unknown","Unknown",2,316,4.4840000000000001E-3,1.419E-5]
[null,"30/08/2016","08:40:00","LX41","Rural Short","Planned",null,29,198.99999999999997,4.6580000000000003E-2,2.3406999999999999E-4]
[null,"30/08/2016","08:43:00","SA744C","Urban","Planned",null,2,177,5.8200000000000005E-4,3.2899999999999998E-6]
[null,"30/08/2016","08:53:00","SA32","Urban","Planned",null,204,16.990196078431371,5.6990000000000001E-3,3.3544E-4]
[null,"30/08/2016","08:53:00","MG35","Rural Long","Planned",null,3,265,5.64E-3,2.128E-5]
[null,"30/08/2016","08:54:37","MV61","Urban","Planned",null,168,390,0.107734,2.7624000000000003E-4]
[null,"30/08/2016","08:55:38","MV61","Urban","Planned",null,60,389,3.8378000000000002E-2,9.8659999999999994E-5]
[null,"30/08/2016","09:08:44","NL210D","Urban","Planned",null,36,374,2.2138999999999999E-2,5.9190000000000001E-5]
[null,"30/08/2016","09:12:00","MV22","Rural Short","Planned",null,9,353,2.5642999999999999E-2,7.2639999999999996E-5]
[null,"30/08/2016","09:25:00","MI11","Rural Long","Planned",null,2,128,1.8159999999999999E-3,1.419E-5]
[null,"30/08/2016","09:35:00","AP425A","Urban","Planned",null,119,302.00840336134456,5.9094000000000001E-2,1.9567E-4]
[null,"30/08/2016","09:55:00","GA02","Rural Short","Planned",null,3,52,1.2589999999999999E-3,2.421E-5]
[null,"30/08/2016","10:11:42","CL04","Rural Long","Planned",null,6,107,4.555E-3,4.2570000000000001E-5]
[null,"30/08/2016","10:26:00","W28","Rural Long","Planned",null,79,240,0.13451399999999999,5.6048000000000003E-4]
[null,"30/08/2016","10:53:00","PL04","Urban","Planned",null,2,170,5.5900000000000004E-4,3.2899999999999998E-6]
[null,"30/08/2016","10:54:00","AP365B","Urban","Planned",null,55,339,3.0658000000000001E-2,9.0439999999999995E-5]
[null,"30/08/2016","11:52:00","MI11","Rural Long","Planned",null,2,88,1.2489999999999999E-3,1.419E-5]
[null,"30/08/2016","12:27:00","EL09","Urban","Asset failure","HV",2432,9.213815789473685,3.6845000000000003E-2,3.9989200000000004E-3]
[null,"30/08/2016","12:53:00","CV17","Rural Long","Asset failure","Distribution substation",2,148,2.0999999999999999E-3,1.419E-5]
[null,"30/08/2016","13:37:00","VH71","Rural Short","Asset failure","HV",1,18,1.45E-4,8.0700000000000007E-6]
[null,"30/08/2016","14:41:00","PP04","Rural Short","Planned",null,3,30,7.2599999999999997E-4,2.421E-5]
[null,"30/08/2016","15:23:00","SD344","Rural Long","Weather",null,52,121.99999999999999,4.5007999999999999E-2,3.6892000000000001E-4]
[null,"30/08/2016","16:33:00","YK16","Rural Long","Asset failure","HV",15,303,3.2245000000000003E-2,1.0642E-4]
[null,"30/08/2016","16:44:33","WK41","Rural Short","Overloads",null,1,187,1.5089999999999999E-3,8.0700000000000007E-6]
[null,"30/08/2016","17:03:00","NU13","Rural Long","Weather",null,3,566,1.2047E-2,2.128E-5]
[null,"30/08/2016","17:11:00","SD373","Rural Short","Weather",null,89,336.37078651685391,0.24163499999999999,7.1836000000000003E-4]
[null,"30/08/2016","17:13:00","PP14","Rural Long","Weather",null,31,704.35483870967744,0.15491099999999999,2.1992999999999999E-4]
[null,"30/08/2016","17:20:00","NU21","Rural Long","Weather",null,37,165.99999999999997,4.3575000000000003E-2,2.6249999999999998E-4]
[null,"30/08/2016","17:22:40","KI32","Rural Short","Asset failure","LV",1,97,7.8299999999999995E-4,8.0700000000000007E-6]
[null,"30/08/2016","17:30:00","NU18","Rural Long","Weather",null,1,280,1.9859999999999999E-3,7.0899999999999999E-6]
[null,"30/08/2016","17:42:00","NU04","Rural Short","Weather",null,5.3333360000000001,199,8.567E-3,4.3050000000000003E-5]
[null,"30/08/2016","17:46:00","M101","Rural Long","Weather",null,42,184,5.4827000000000001E-2,2.9796999999999999E-4]
[null,"30/08/2016","18:31:00","M81","Rural Long","Asset failure","HV",492,187.51016260162604,0.65451599999999999,3.4905600000000002E-3]
[null,"30/08/2016","18:31:00","M81","Rural Long","Asset failure","HV",null,30,5.2997000000000002E-2,0]
[null,"30/08/2016","19:21:00","LM14","Rural Long","Weather",null,48,663.4375,0.22592899999999999,3.4054000000000002E-4]
[null,"30/08/2016","19:45:00","VH17","Rural Short","Animal","Animal impact",4.6666689999999997,95,3.578E-3,3.7669999999999997E-5]
[null,"30/08/2016","20:09:55","CBD103F","Urban","Planned",null,35,53,3.0500000000000002E-3,5.7550000000000003E-5]
[null,"30/08/2016","21:34:00","BT15","Rural Long","Asset failure","HV",106,274.88679245283015,0.20672399999999999,7.5202999999999999E-4]
[null,"30/08/2016","22:09:00","AP355H","Urban","Planned",null,8,354,4.6569999999999997E-3,1.3149999999999999E-5]
[null,"30/08/2016","22:10:19","AP424F","Urban","Asset failure","LV",2.999997,909,4.4840000000000001E-3,4.9300000000000002E-6]
[null,"30/08/2016","23:33:58","AP365B","Urban","Asset failure","LV",24,60,2.3679999999999999E-3,3.9459999999999998E-5]
[null,"30/08/2016","23:46:00","LM54","Rural Long","Unknown","Unknown",2,11.999999999999998,1.7000000000000001E-4,1.419E-5]
[null,"31/08/2016","02:04:00","EL14","Urban","Animal","Animal impact",206,182.05825242718447,6.1668000000000001E-2,3.3871999999999998E-4]
[null,"31/08/2016","05:58:07","SM179B","Urban","Planned",null,64,35,3.6830000000000001E-3,1.0522999999999999E-4]
[null,"31/08/2016","06:00:18","SM179B","Urban","Planned",null,13,32,6.8400000000000004E-4,2.1379999999999999E-5]
[null,"31/08/2016","08:35:00","MG06","Rural Short","Planned",null,5,310,1.2511E-2,4.036E-5]
[null,"31/08/2016","08:39:57","NL234A","Urban","Planned",null,84,445.99999999999994,6.1601999999999997E-2,1.3812000000000001E-4]
[null,"31/08/2016","08:40:00","MI11","Rural Long","Planned",null,2,140,1.9859999999999999E-3,1.419E-5]
[null,"31/08/2016","08:41:31","SM137B","Urban","Planned",null,74,240,2.9203E-2,1.2168E-4]
[null,"31/08/2016","08:42:49","WHY08","Urban","Planned",null,24,386.00000000000006,1.5233E-2,3.9459999999999998E-5]
[null,"31/08/2016","09:02:00","WK61","Rural Short","Planned",null,14,99,1.1187000000000001E-2,1.13E-4]
[null,"31/08/2016","09:16:14","ST21","Rural Short","Planned",null,30,221,5.3513999999999999E-2,2.4214000000000001E-4]
[null,"31/08/2016","09:37:00","VH16","Rural Short","Planned",null,90,303,0.220108,7.2643000000000002E-4]
[null,"31/08/2016","09:42:42","HH496G","Urban","Planned",null,29,91,4.339E-3,4.7679999999999998E-5]
[null,"31/08/2016","09:43:48","SA35","Urban","Planned",null,40,313,2.0587000000000001E-2,6.5770000000000002E-5]
[null,"31/08/2016","09:49:00","AP132B","Urban","Planned",null,5,219,1.8010000000000001E-3,8.2199999999999992E-6]
[null,"31/08/2016","10:00:36","ME231B","Urban","Planned",null,29,72,3.4329999999999999E-3,4.7679999999999998E-5]
[null,"31/08/2016","10:32:00","CD16","Rural Short","Planned",null,1,22,1.7799999999999999E-4,8.0700000000000007E-6]
[null,"31/08/2016","10:40:00","CM03","Rural Long","Planned",null,42,45,1.3409000000000001E-2,2.9796999999999999E-4]
[null,"31/08/2016","10:55:00","EL23","Urban","Third Party","Vehicle impact",27,94.999999999999986,4.2180000000000004E-3,4.4400000000000002E-5]
[null,"31/08/2016","11:04:00","LX24","Rural Short","Planned",null,3,43,1.041E-3,2.421E-5]
[null,"31/08/2016","11:40:00","AP424B","Urban","Planned",null,64,244.00000000000003,2.5676999999999998E-2,1.0522999999999999E-4]
[null,"31/08/2016","12:41:00","CV26","Rural Long","Asset failure","HV",2,101.99999999999999,1.4469999999999999E-3,1.419E-5]
[null,"31/08/2016","18:58:00","CN26","Rural Long","Other",null,2,22,3.1199999999999999E-4,1.419E-5]
[null,"1/09/2016","07:57:16","NL234A","Urban","Planned",null,27,200.99999999999997,8.9239999999999996E-3,4.4400000000000002E-5]
[null,"1/09/2016","07:58:14","NL234A","Urban","Planned",null,70,200,2.3019999999999999E-2,1.1510000000000001E-4]
[null,"1/09/2016","08:27:27","NL115A","Urban","Planned",null,15,134,3.3050000000000002E-3,2.4660000000000001E-5]
[null,"1/09/2016","08:29:46","MV61","Urban","Planned",null,60,129,1.2727E-2,9.8659999999999994E-5]
[null,"1/09/2016","08:30:00","MV63","Rural Short","Planned",null,9,116.99999999999999,8.4989999999999996E-3,7.2639999999999996E-5]
[null,"1/09/2016","08:36:00","SA36","Urban","Planned",null,24,339,1.3377999999999999E-2,3.9459999999999998E-5]
[null,"1/09/2016","08:43:00","SM411C","Urban","Third Party","Vehicle impact",57,192,1.7995000000000001E-2,9.3720000000000004E-5]
[null,"1/09/2016","08:45:00","MI10","Rural Long","Planned",null,3,180,3.8310000000000002E-3,2.128E-5]
[null,"1/09/2016","08:52:02","HH496A","Urban","Planned",null,35,224,1.2891E-2,5.7550000000000003E-5]
[null,"1/09/2016","08:57:00","SG13","Rural Short","Planned",null,8,221,1.427E-2,6.457E-5]
[null,"1/09/2016","08:58:00","MV52","Rural Short","Planned",null,112,399,0.36069699999999999,9.0399999999999996E-4]
[null,"1/09/2016","08:59:00","EL19","Urban","Planned",null,17,188,5.2550000000000001E-3,2.7949999999999998E-5]
[null,"1/09/2016","09:00:00","ST21","Rural Short","Planned",null,28,298,6.7348000000000005E-2,2.2599999999999999E-4]
[null,"1/09/2016","09:04:00","GA29","Rural Long","Planned",null,12,249.00000000000003,2.1198999999999999E-2,8.5140000000000001E-5]
[null,"1/09/2016","09:07:00","SSD495","Urban","Asset failure","Zone substation",2,206.00000000000003,6.7699999999999998E-4,3.2899999999999998E-6]
[null,"1/09/2016","09:13:00","SA32","Urban","Planned",null,163,6,1.6080000000000001E-3,2.6802E-4]
[null,"1/09/2016","09:17:00","AP365B","Urban","Planned",null,78,343,4.3991000000000002E-2,1.2825E-4]
[null,"1/09/2016","09:29:00","SB22","Rural Long","Planned",null,17,105,1.2664E-2,1.2061E-4]
[null,"1/09/2016","09:30:00","VH18","Rural Short","Planned",null,1,157,1.2669999999999999E-3,8.0700000000000007E-6]
[null,"1/09/2016","09:54:00","BM52","Urban","Planned",null,65,74,7.9089999999999994E-3,1.0688000000000001E-4]
[null,"1/09/2016","10:02:00","NA22","Rural Long","Third Party","Vehicle impact",94,279,0.18606400000000001,6.669E-4]
[null,"1/09/2016","10:03:00","PA11","Rural Long","Planned",null,42,307,9.1478000000000004E-2,2.9796999999999999E-4]
[null,"1/09/2016","10:12:00","YK19","Rural Long","Planned",null,4,62,1.7589999999999999E-3,2.8379999999999999E-5]
[null,"1/09/2016","10:16:00","PP13","Rural Long","Planned",null,70,230,0.11422400000000001,4.9662000000000003E-4]
[null,"1/09/2016","10:50:00","GA35","Rural Long","Planned",null,36,136,3.4735000000000002E-2,2.5541000000000002E-4]
[null,"1/09/2016","13:23:04","NL451C","Urban","Asset failure","LV",1,213.00000000000003,3.5E-4,1.64E-6]
[null,"1/09/2016","15:56:27","MV64","Rural Short","Asset failure","LV",1,161,1.2999999999999999E-3,8.0700000000000007E-6]
[null,"1/09/2016","16:51:00","MB42","Rural Long","Asset failure","HV",59,7,2.9299999999999999E-3,4.1857999999999999E-4]
[null,"1/09/2016","17:19:53","SA34","Urban","Asset failure","LV",17,76,2.124E-3,2.7949999999999998E-5]
[null,"1/09/2016","20:05:00","M43","Rural Long","Asset failure","HV",1,67,4.75E-4,7.0899999999999999E-6]
[null,"1/09/2016","20:09:51","HH121C","Urban","Asset failure","LV",13.333320000000001,292,6.4019999999999997E-3,2.192E-5]
[null,"1/09/2016","20:41:10","SM349E","Urban","Asset failure","LV",35,81,4.6620000000000003E-3,5.7550000000000003E-5]
[null,"1/09/2016","22:11:04","NL234A","Urban","Asset failure","LV",1,139,2.2900000000000001E-4,1.64E-6]
[null,"2/09/2016","06:03:18","PL06","Urban","Asset failure","LV",40.000019999999999,406.99999999999994,2.6769000000000001E-2,6.5770000000000002E-5]
[null,"2/09/2016","06:51:00","LX41","Rural Short","Asset failure","HV",4.0000020000000003,116.99999999999997,3.777E-3,3.2289999999999997E-5]
[null,"2/09/2016","07:15:01","SM349C","Urban","Asset failure","LV",1,135,2.22E-4,1.64E-6]
[null,"2/09/2016","08:33:49","ME427D","Urban","Planned",null,52,81,6.9259999999999999E-3,8.5500000000000005E-5]
[null,"2/09/2016","08:52:00","YK15","Rural Long","Planned",null,2,284,4.0299999999999997E-3,1.419E-5]
[null,"2/09/2016","08:55:00","GA29","Rural Long","Planned",null,7,276,1.3707E-2,4.9660000000000002E-5]
[null,"2/09/2016","08:59:35","HH409C","Urban","Planned",null,73,323,3.8771E-2,1.2003E-4]
[null,"2/09/2016","09:01:00","YK16","Rural Long","Planned",null,4,14,3.97E-4,2.8379999999999999E-5]
[null,"2/09/2016","09:29:26","MB13","Rural Long","Planned",null,29,251,5.1642E-2,2.0573999999999999E-4]
[null,"2/09/2016","09:50:00","MI13","Rural Long","Planned",null,4,55,1.5610000000000001E-3,2.8379999999999999E-5]
[null,"2/09/2016","09:56:00","SB01","Rural Long","Planned",null,16,89.999999999999986,1.0215999999999999E-2,1.1351E-4]
[null,"2/09/2016","09:56:00","GA28","Rural Long","Planned",null,13,348.99999999999994,3.2188000000000001E-2,9.2230000000000003E-5]
[null,"2/09/2016","10:07:00","LX24","Rural Short","Planned",null,1,24,1.94E-4,8.0700000000000007E-6]
[null,"2/09/2016","10:18:00","CV32","Rural Long","Planned",null,65,280,0.12912199999999999,4.6115000000000001E-4]
[null,"2/09/2016","10:40:00","SM216B","Urban","Planned",null,47,220,1.7002E-2,7.7280000000000005E-5]
[null,"2/09/2016","10:50:44","MV64","Rural Short","Planned",null,32,114,2.9444999999999999E-2,2.5829E-4]
[null,"2/09/2016","11:27:00","YK06","Rural Short","Planned",null,3,10,2.42E-4,2.421E-5]
[null,"2/09/2016","11:38:00","MI09","Rural Long","Unknown","Unknown",53,498.01886792452831,0.18726300000000001,3.7602000000000002E-4]
[null,"2/09/2016","12:22:00","VH18","Rural Short","Asset failure","Distribution substation",247,120.98380566801619,0.241199,1.99365E-3]
[null,"2/09/2016","13:03:00","MB42","Rural Long","Unknown","Unknown",2,82,1.1640000000000001E-3,1.419E-5]
[null,"2/09/2016","13:20:00","YK30","Rural Long","Planned",null,1,10,7.1000000000000005E-5,7.0899999999999999E-6]
[null,"2/09/2016","13:46:56","SM402B","Urban","Asset failure","LV",1,145,2.3800000000000001E-4,1.64E-6]
[null,"2/09/2016","14:15:00","CM03","Rural Long","Unknown","Unknown",2,35,4.9700000000000005E-4,1.419E-5]
[null,"2/09/2016","14:47:00","SG12","Rural Short","Unknown","Unknown",11.000001000000001,35.999999999999993,3.1960000000000001E-3,8.8789999999999995E-5]
[null,"2/09/2016","14:49:57","SG01","Rural Short","Asset failure","LV",1,121,9.77E-4,8.0700000000000007E-6]
[null,"2/09/2016","16:06:20","NL451A","Urban","Asset failure","LV",1,251.00000000000003,4.1300000000000001E-4,1.64E-6]
[null,"2/09/2016","17:29:16","MG44","Urban","Overloads",null,1,298.00000000000006,4.8999999999999998E-4,1.64E-6]
[null,"2/09/2016","17:47:45","MG11","Rural Short","Asset failure","LV",1,331,2.6719999999999999E-3,8.0700000000000007E-6]
[null,"2/09/2016","18:29:04","MI01","Rural Long","Asset failure","LV",1,379,2.689E-3,7.0899999999999999E-6]
[null,"3/09/2016","06:50:41","VH32","Rural Short","Other",null,1,283,2.284E-3,8.0700000000000007E-6]
[null,"3/09/2016","09:54:00","NL115B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",917,80,0.120625,1.50782E-3]
[null,"3/09/2016","13:10:00","SM216E","Urban","Animal","Animal impact",97,141,2.2488999999999999E-2,1.595E-4]
[null,"3/09/2016","13:46:00","LM64","Rural Long","Asset failure","HV",70,460,0.22844700000000001,4.9662000000000003E-4]
[null,"3/09/2016","16:52:01","HH145B","Urban","Asset failure","LV",1,326,5.3600000000000002E-4,1.64E-6]
[null,"3/09/2016","17:01:00","HH429C","Urban","Asset failure","HV",1707,89.263034563561817,0.25054399999999999,2.8068099999999999E-3]
[null,"3/09/2016","19:00:00","HH130D","Urban","Planned",null,112,230,4.2356999999999999E-2,1.8416E-4]
[null,"3/09/2016","20:42:00","AP125B","Urban","Asset failure","HV",554.00027299999999,183.15643788319935,0.16684399999999999,9.1093999999999995E-4]
[null,"3/09/2016","20:42:00","AP125B","Urban","Asset failure","HV",null,49,7.4120000000000002E-3,0]
[null,"4/09/2016","01:39:00","HH130E","Urban","Unknown","Unknown",801,127,0.167269,1.31708E-3]
[null,"4/09/2016","06:27:00","CV24","Rural Long","Asset failure","HV",75,461.00000000000006,0.24529699999999999,5.3209999999999998E-4]
[null,"4/09/2016","07:12:00","PA26","Rural Long","Unknown","Unknown",144.66672100000002,11.020733939217434,1.1311E-2,1.02636E-3]
[null,"4/09/2016","07:33:56","SA744C","Urban","Planned",null,3,495.00000000000006,2.4420000000000002E-3,4.9300000000000002E-6]
[null,"4/09/2016","07:34:17","SA744C","Urban","Planned",null,2,495.00000000000006,1.6280000000000001E-3,3.2899999999999998E-6]
[null,"4/09/2016","07:34:36","SA744C","Urban","Planned",null,6,495.00000000000006,4.8840000000000003E-3,9.8700000000000004E-6]
[null,"4/09/2016","07:49:00","BM21","Rural Short","Asset failure","HV",2,151,2.4380000000000001E-3,1.6140000000000001E-5]
[null,"4/09/2016","08:00:00","SA744C","Urban","Planned",null,2,453,1.49E-3,3.2899999999999998E-6]
[null,"4/09/2016","08:50:00","HH432A","Urban","Planned",null,69,27.217391304347828,3.088E-3,1.1346E-4]
[null,"4/09/2016","09:16:37","HH118E","Urban","Planned",null,20,394,1.2957E-2,3.2889999999999999E-5]
[null,"4/09/2016","09:20:00","AP365B","Urban","Planned",null,13,394.00000000000006,8.4220000000000007E-3,2.1379999999999999E-5]
[null,"4/09/2016","09:50:16","NU33","Rural Long","Weather",null,4,151,4.2849999999999997E-3,2.8379999999999999E-5]
[null,"4/09/2016","10:27:00","NU25","Rural Long","Planned",null,9,130,8.3009999999999994E-3,6.3849999999999993E-5]
[null,"4/09/2016","11:31:26","HH121B","Urban","Asset failure","LV",1,152,2.5000000000000001E-4,1.64E-6]
[null,"4/09/2016","12:19:15","HH428D","Urban","Asset failure","LV",28.333304999999999,71.000000000000014,3.3080000000000002E-3,4.6589999999999999E-5]
[null,"4/09/2016","12:21:42","SM216B","Urban","Asset failure","LV",1,222,3.6499999999999998E-4,1.64E-6]
[null,"4/09/2016","13:53:35","HH409A","Urban","Asset failure","LV",9,487,7.2069999999999999E-3,1.4800000000000001E-5]
[null,"4/09/2016","17:24:00","NA04","Rural Long","Unknown","Unknown",44.000018000000004,82,2.5597000000000002E-2,3.1216000000000002E-4]
[null,"4/09/2016","20:45:33","HH522B","Urban","Asset failure","LV",38.000019000000002,99.000000000000014,6.1859999999999997E-3,6.2479999999999998E-5]
[null,"4/09/2016","21:45:31","AP149C","Urban","Asset failure","LV",1,128,2.1000000000000001E-4,1.64E-6]
[null,"4/09/2016","22:54:46","PP04","Rural Short","Asset failure","LV",1,106,8.5599999999999999E-4,8.0700000000000007E-6]
[null,"4/09/2016","23:21:00","SSD244","Rural Long","Planned",null,701,229.00000000000003,1.138895,4.9733399999999997E-3]
[null,"5/09/2016","07:57:31","NL115A","Urban","Planned",null,22,66.999999999999986,2.4239999999999999E-3,3.6170000000000001E-5]
[null,"5/09/2016","08:00:07","NL115A","Urban","Planned",null,44,65,4.7029999999999997E-3,7.2349999999999997E-5]
[null,"5/09/2016","08:01:26","NL115A","Urban","Planned",null,53,64,5.5770000000000004E-3,8.7150000000000004E-5]
[null,"5/09/2016","08:02:45","NL115A","Urban","Planned",null,43,62.999999999999993,4.4539999999999996E-3,7.0699999999999997E-5]
[null,"5/09/2016","08:15:46","SA32","Urban","Vegetation","Grow-in - NSP responsibility",21.666644999999999,59.000000000000007,2.1020000000000001E-3,3.5630000000000003E-5]
[null,"5/09/2016","08:35:10","ME131E","Urban","Planned",null,89,266,3.8927000000000003E-2,1.4634000000000001E-4]
[null,"5/09/2016","08:35:44","KA06","Rural Long","Planned",null,45,352,0.11237900000000001,3.1925999999999998E-4]
[null,"5/09/2016","08:36:02","SM179D","Urban","Planned",null,67,325,3.5804999999999997E-2,1.1017E-4]
[null,"5/09/2016","08:36:03","HH130E","Urban","Asset failure","LV",1,228.00000000000003,3.7500000000000001E-4,1.64E-6]
[null,"5/09/2016","08:38:00","EL18","Urban","Planned",null,37,327.99999999999994,1.9955000000000001E-2,6.084E-5]
[null,"5/09/2016","08:40:17","CBD103C","Urban","Planned",null,37,241,1.4662E-2,6.084E-5]
[null,"5/09/2016","08:40:28","HH496H","Urban","Planned",null,49,393,3.1663999999999998E-2,8.0569999999999996E-5]
[null,"5/09/2016","08:42:20","CBD103C","Urban","Planned",null,45,238.00000000000003,1.7610000000000001E-2,7.3990000000000001E-5]
[null,"5/09/2016","08:46:38","HH522A","Urban","Planned",null,42,178.99999999999997,1.2362E-2,6.9060000000000006E-5]
[null,"5/09/2016","08:50:02","SM349F","Urban","Planned",null,58,159,1.5164E-2,9.5370000000000003E-5]
[null,"5/09/2016","08:51:44","SM349F","Urban","Planned",null,72,159,1.8824E-2,1.1839E-4]
[null,"5/09/2016","08:52:54","SM349F","Urban","Planned",null,47,158,1.2211E-2,7.7280000000000005E-5]
[null,"6/09/2016","08:30:00","CD15","Rural Long","Planned",null,26,324,5.9764999999999999E-2,1.8446000000000001E-4]
[null,"6/09/2016","09:02:20","VH16","Rural Short","Planned",null,54,316,0.13773099999999999,4.3585999999999999E-4]
[null,"7/09/2016","09:00:00","PP08","Rural Long","Planned",null,199,341,0.481435,1.41183E-3]
[null,"7/09/2016","16:02:13","EL02","Urban","Asset failure","LV",32,63,3.3149999999999998E-3,5.2620000000000001E-5]
[null,"8/09/2016","12:40:47","AP365B","Urban","Asset failure","LV",53,68,5.9259999999999998E-3,8.7150000000000004E-5]
[null,"8/09/2016","17:51:04","AP125B","Urban","Asset failure","LV",1,128,2.1000000000000001E-4,1.64E-6]
[null,"9/09/2016","11:40:00","HH496G","Urban","Unknown","Unknown",4,20.000000000000004,1.3200000000000001E-4,6.5799999999999997E-6]
[null,"10/09/2016","18:07:57","EL09","Urban","Overloads",null,1,107.00000000000001,1.76E-4,1.64E-6]
[null,"11/09/2016","13:33:00","MG35","Rural Long","Asset failure","HV",2,232,3.2919999999999998E-3,1.419E-5]
[null,"12/09/2016","08:32:50","MG39","Rural Short","Planned",null,14,194,2.1922000000000001E-2,1.13E-4]
[null,"12/09/2016","22:26:12","HH403D","Urban","Asset failure","LV",29.333303999999998,79.000000000000014,3.81E-3,4.8229999999999997E-5]
[null,"13/09/2016","09:30:10","ME116B","Urban","Planned",null,41,351,2.3663E-2,6.7420000000000002E-5]
[null,"13/09/2016","18:46:35","NL210D","Urban","Asset failure","LV",1,345,5.6700000000000001E-4,1.64E-6]
[null,"14/09/2016","08:55:00","EL260B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",3057,61.411187438665358,0.30869000000000002,5.0266099999999999E-3]
[null,"14/09/2016","13:26:50","M04","Rural Long","Asset failure","LV",2,330,4.6820000000000004E-3,1.419E-5]
[null,"14/09/2016","13:46:29","SM411D","Urban","Asset failure","LV",2,523,1.72E-3,3.2899999999999998E-6]
[null,"14/09/2016","18:29:26","HH386G","Urban","Asset failure","LV",1.9999979999999999,337,1.108E-3,3.2899999999999998E-6]
[null,"15/09/2016","08:09:00","MTB22","Rural Short","Vegetation","Grow-in - NSP responsibility",14,238.28571428571431,2.6925999999999999E-2,1.13E-4]
[null,"15/09/2016","19:00:00","SG01","Rural Short","Unknown","Unknown",16,72,9.2980000000000007E-3,1.2914E-4]
[null,"16/09/2016","10:40:00","CD20","Rural Long","Planned",null,3,65,1.3829999999999999E-3,2.128E-5]
[null,"17/09/2016","08:53:46","VH16","Rural Short","Asset failure","LV",1,206,1.663E-3,8.0700000000000007E-6]
[null,"17/09/2016","14:12:12","SA14","Urban","Asset failure","LV",1,450.00000000000006,7.3999999999999999E-4,1.64E-6]
[null,"18/09/2016","09:11:50","SA34","Urban","Planned",null,17,289,8.0780000000000001E-3,2.7949999999999998E-5]
[null,"19/09/2016","07:09:00","WHY07","Urban","Planned",null,2,247.00000000000003,8.12E-4,3.2899999999999998E-6]
[null,"19/09/2016","12:59:30","SM172D","Urban","Third Party","Vehicle impact",14,256,5.8929999999999998E-3,2.302E-5]
[null,"20/09/2016","16:43:58","PA05","Rural Long","Weather",null,5.3333360000000001,91,3.4429999999999999E-3,3.7839999999999997E-5]
[null,"20/09/2016","17:38:16","EL02","Urban","Unknown","Unknown",21.999977999999999,162,5.8599999999999998E-3,3.6170000000000001E-5]
[null,"22/09/2016","08:08:10","AP365C","Urban","Planned",null,35,390,2.2445E-2,5.7550000000000003E-5]
[null,"22/09/2016","09:24:05","NL234A","Urban","Planned",null,86,261,3.6908000000000003E-2,1.4140999999999999E-4]
[null,"22/09/2016","20:02:57","HH386D","Urban","Asset failure","LV",8.3333250000000003,247.99999999999997,3.398E-3,1.3699999999999999E-5]
[null,"25/09/2016","07:48:00","AP132A","Urban","Asset failure","HV",443,285.2257336343115,0.20776500000000001,7.2842000000000002E-4]
[null,"26/09/2016","14:30:47","EL01N","Urban","Asset failure","LV",7.9999919999999998,34,4.4700000000000002E-4,1.3149999999999999E-5]
[null,"27/09/2016","12:23:24","NL210D","Urban","Planned",null,60,52,5.13E-3,9.8659999999999994E-5]
[null,"27/09/2016","15:30:28","HH102D","Urban","Asset failure","LV",1,219,3.6000000000000002E-4,1.64E-6]
[null,"28/09/2016","09:38:00","NL111C","Urban","Planned",null,156,157,4.0272000000000002E-2,2.5651E-4,"MED"]
[null,"28/09/2016","15:48:00","MT06","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,997,1006,7.1157950000000003,7.0733599999999999E-3,"MED"]
[null,"28/09/2016","15:48:00","SD443","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,2239,65.413577489950868,1.039088,1.58849E-2,"MED"]
[null,"28/09/2016","21:40:00","BT02","Rural Long","Unknown","Unknown",828,186,1.0926309999999999,5.8743600000000003E-3,"MED"]
[null,"29/09/2016","06:14:09","MV64","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",1,610,4.9240000000000004E-3,8.0700000000000007E-6,"MED"]
[null,"29/09/2016","09:09:00","BU01","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,668,81,0.38387700000000002,4.7392199999999997E-3,"MED"]
[null,"29/09/2016","10:23:00","SA18","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",2355,130.36178343949044,0.50480199999999997,3.8723099999999999E-3,"MED"]
[null,"29/09/2016","13:43:00","G16","Rural Long","5 - STPIS Exclusion (3.3)(a)",null,57,1786.6140350877195,0.72249699999999994,4.0439000000000002E-4,"MED"]
[null,"29/09/2016","16:59:00","YK24","Rural Long","Asset failure","HV",1,2644.9999999999995,1.8765E-2,7.0899999999999999E-6,"MED"]
[null,"29/09/2016","17:05:49","SM349H","Urban","Asset failure","LV",1,552,9.0799999999999995E-4,1.64E-6,"MED"]
[null,"29/09/2016","18:33:09","SA36","Urban","Vegetation","Grow-in - NSP responsibility",2.999997,400.00000000000006,1.9729999999999999E-3,4.9300000000000002E-6,"MED"]
[null,"29/09/2016","21:03:00","NL234A","Urban","Asset failure","LV",1,84.000000000000014,1.3799999999999999E-4,1.64E-6,"MED"]
[null,"30/09/2016","06:45:00","W28","Rural Long","Weather",null,81,3221.0000000000005,1.8509979999999999,5.7467E-4]
[null,"30/09/2016","09:19:23","AP227B","Urban","Asset failure","LV",11.666655,2061,3.9537000000000003E-2,1.9179999999999999E-5]
[null,"30/09/2016","12:07:52","AP355F","Urban","Unknown","Unknown",2,57.000000000000007,1.8699999999999999E-4,3.2899999999999998E-6]
[null,"30/09/2016","15:36:00","G11","Rural Long","Unknown","Unknown",107,1208.9999999999998,0.91778400000000004,7.5913E-4]
[null,"30/09/2016","18:25:39","SM216A","Urban","Asset failure","LV",15.999984,291,7.6559999999999996E-3,2.6310000000000001E-5]
[null,"1/10/2016","07:55:34","SM179C","Urban","Asset failure","LV",1,970,1.5950000000000001E-3,1.64E-6]
[null,"1/10/2016","14:55:00","CM09","Rural Long","Asset failure","HV",61,1139.9180327868851,0.49332599999999999,4.3277000000000002E-4]
[null,"2/10/2016","11:59:29","NL451C","Urban","Asset failure","LV",1,764.00000000000011,1.256E-3,1.64E-6]
[null,"2/10/2016","13:56:34","NL111P","Urban","Asset failure","LV",1,693,1.139E-3,1.64E-6]
[null,"3/10/2016","08:38:12","ME427C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,605,9.9500000000000001E-4,1.64E-6]
[null,"3/10/2016","13:10:14","EL01B","Urban","Unknown","Unknown",1,90,1.4799999999999999E-4,1.64E-6]
[null,"3/10/2016","15:05:46","SM411F","Urban","Vegetation","Grow-in - NSP responsibility",1,71,1.17E-4,1.64E-6]
[null,"4/10/2016","08:16:46","SG11","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",2,633,1.0218E-2,1.6140000000000001E-5]
[null,"4/10/2016","11:38:00","CD16","Rural Short","Planned",null,11,49.999999999999993,4.4390000000000002E-3,8.8789999999999995E-5]
[null,"4/10/2016","14:59:00","MV62","Rural Short","Asset failure","HV",32,35,9.0399999999999994E-3,2.5829E-4]
[null,"5/10/2016","00:32:19","NL115E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",46,54.000000000000007,4.084E-3,7.5640000000000001E-5]
[null,"5/10/2016","08:53:51","SA36","Urban","Asset failure","LV",1,210.00000000000003,3.4499999999999998E-4,1.64E-6]
[null,"6/10/2016","02:26:58","NL115C","Urban","Asset failure","LV",1,95.000000000000014,1.56E-4,1.64E-6]
[null,"6/10/2016","10:39:10","HH177B","Urban","Asset failure","LV",1.333332,649,1.423E-3,2.1900000000000002E-6]
[null,"6/10/2016","15:20:41","VH12","Rural Short","Asset failure","LV",1,207,1.671E-3,8.0700000000000007E-6]
[null,"7/10/2016","08:50:00","MV61","Urban","Planned",null,116,305,5.8174999999999998E-2,1.9074000000000001E-4]
[null,"7/10/2016","14:16:00","GA21","Rural Long","Planned",null,1,44,3.1199999999999999E-4,7.0899999999999999E-6]
[null,"8/10/2016","18:23:26","SA18","Urban","Asset failure","LV",1,453,7.45E-4,1.64E-6]
[null,"9/10/2016","08:16:00","NA05","Rural Long","Planned",null,1,235,1.6670000000000001E-3,7.0899999999999999E-6]
[null,"9/10/2016","12:35:47","CBD103G","Urban","Planned",null,102,216,3.6227000000000002E-2,1.6772E-4]
[null,"9/10/2016","19:34:03","EL01N","Urban","Asset failure","LV",1,274,4.5100000000000001E-4,1.64E-6]
[null,"10/10/2016","09:49:17","AP529B","Urban","Unknown","Unknown",2,453,1.49E-3,3.2899999999999998E-6]
[null,"10/10/2016","18:36:19","AP355A","Urban","Asset failure","LV",1,130,2.14E-4,1.64E-6]
[null,"11/10/2016","11:40:00","M21","Rural Long","Planned",null,163,237.99999999999997,0.275229,1.15643E-3]
[null,"12/10/2016","08:27:00","WK41","Rural Short","Planned",null,8,258.125,1.6667999999999999E-2,6.457E-5]
[null,"12/10/2016","12:06:00","PL11","Rural Long","Animal","Animal impact",98,342.73469387755102,0.23829500000000001,6.9527E-4]
[null,"13/10/2016","09:01:00","MG52","Urban","Planned",null,136,384,8.5872000000000004E-2,2.2362E-4]
[null,"14/10/2016","09:02:00","MT09","Rural Long","Planned",null,1,185.99999999999997,1.32E-3,7.0899999999999999E-6]
[null,"14/10/2016","10:31:00","CM17","Rural Long","Planned",null,11,186,1.4515999999999999E-2,7.8040000000000005E-5]
[null,"15/10/2016","15:43:09","MTB54","Rural Long","Asset failure","LV",2,284,4.0299999999999997E-3,1.419E-5]
[null,"16/10/2016","21:06:00","MB28","Rural Short","Unknown","Unknown",6,206,9.9760000000000005E-3,4.8430000000000002E-5]
[null,"17/10/2016","13:18:00","SM374B","Urban","Asset failure","LV",86,206,2.913E-2,1.4140999999999999E-4]
[null,"18/10/2016","06:42:12","MV61","Urban","Overloads",null,1,206.00000000000003,3.39E-4,1.64E-6]
[null,"19/10/2016","08:49:19","SM402D","Urban","Overloads",null,1,200,3.2899999999999997E-4,1.64E-6]
[null,"20/10/2016","08:48:01","SA36","Urban","Planned",null,24,343,1.3535999999999999E-2,3.9459999999999998E-5]
[null,"20/10/2016","11:26:01","ME131E","Urban","Asset failure","LV",1,150,2.4699999999999999E-4,1.64E-6]
[null,"20/10/2016","19:06:56","ME347B","Urban","Asset failure","LV",125,53,1.0893E-2,2.0553999999999999E-4]
[null,"21/10/2016","06:39:26","MG05","Rural Long","Unknown","Unknown",3,99,2.1069999999999999E-3,2.128E-5]
[null,"21/10/2016","11:53:12","LX43","Rural Short","Asset failure","LV",1,111,8.9599999999999999E-4,8.0700000000000007E-6]
[null,"21/10/2016","19:30:00","EL01P","Urban","Asset failure","HV",674,75.089020771513347,8.3218E-2,1.1082500000000001E-3]
[null,"23/10/2016","12:21:42","HH496C","Urban","Asset failure","LV",1,186,3.0600000000000001E-4,1.64E-6]
[null,"24/10/2016","10:52:37","SM172C","Urban","Overloads",null,1,231,3.8000000000000002E-4,1.64E-6]
[null,"25/10/2016","09:18:11","VH12","Rural Short","Planned",null,65,377,0.19779099999999999,5.2464000000000005E-4]
[null,"25/10/2016","10:54:00","KA18","Rural Long","Planned",null,1,50.999999999999993,3.6200000000000002E-4,7.0899999999999999E-6]
[null,"26/10/2016","09:12:00","GA26","Urban","Planned",null,53,494.00000000000006,4.3050999999999999E-2,8.7150000000000004E-5]
[null,"26/10/2016","19:04:44","SM349H","Urban","Overloads",null,1,198.00000000000003,3.2600000000000001E-4,1.64E-6]
[null,"27/10/2016","10:27:00","NL511B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1835,82,0.247417,3.0172799999999998E-3]
[null,"28/10/2016","12:33:00","SA16","Urban","Third Party","Other",1836,93.099673202614369,0.28106100000000001,3.01893E-3]
[null,"29/10/2016","08:46:07","MB01","Rural Long","Asset failure","LV",1,313,2.2209999999999999E-3,7.0899999999999999E-6]
[null,"29/10/2016","23:43:00","PL27","Rural Long","Asset failure","Distribution substation",142,958.01408450704218,0.96514,1.0074400000000001E-3]
[null,"30/10/2016","13:02:22","HH148B","Urban","Vegetation","Grow-in - NSP responsibility",40.000019999999999,111.99999999999999,7.3660000000000002E-3,6.5770000000000002E-5]
[null,"31/10/2016","08:08:34","HH145E","Urban","Planned",null,27,89.000000000000014,3.9509999999999997E-3,4.4400000000000002E-5]
[null,"31/10/2016","19:45:35","HH403A","Urban","Asset failure","LV",55,47,4.2509999999999996E-3,9.0439999999999995E-5]
[null,"2/11/2016","08:39:16","G40","Rural Long","Planned",null,42,437,0.130215,2.9796999999999999E-4]
[null,"2/11/2016","10:50:51","EL01P","Urban","Unknown","Unknown",1,243.00000000000003,4.0000000000000002E-4,1.64E-6]
[null,"3/11/2016","08:47:01","YK04","Rural Short","Planned",null,24,456.00000000000006,8.8333999999999996E-2,1.9370999999999999E-4]
[null,"3/11/2016","13:31:39","AP425B","Urban","Asset failure","LV",74,80,9.7339999999999996E-3,1.2168E-4]
[null,"4/11/2016","08:45:06","HH409C","Urban","Planned",null,34,80,4.4720000000000003E-3,5.5909999999999998E-5]
[null,"5/11/2016","07:56:00","G23","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",94,389.69148936170211,0.259884,6.669E-4]
[null,"5/11/2016","20:59:00","SM402D","Urban","Planned",null,43,336.99999999999994,2.3827000000000001E-2,7.0699999999999997E-5]
[null,"7/11/2016","08:50:00","LX41","Rural Short","Planned",null,43,140,4.8590000000000001E-2,3.4707E-4]
[null,"7/11/2016","17:27:53","EL20","Urban","Overloads",null,7.9999919999999998,270,3.552E-3,1.3149999999999999E-5]
[null,"8/11/2016","22:41:00","M92","Rural Long","Unknown","Unknown",450,207,0.66086599999999995,3.1925899999999999E-3]
[null,"9/11/2016","17:14:05","BM34","Rural Short","Animal","Animal impact",3.3333349999999999,240.00000000000003,6.4570000000000001E-3,2.69E-5]
[null,"10/11/2016","08:41:00","EL18","Urban","Planned",null,33,304.00000000000006,1.6496E-2,5.4259999999999999E-5]
[null,"11/11/2016","08:18:42","NL115A","Urban","Planned",null,50,106.00000000000001,8.7150000000000005E-3,8.2210000000000001E-5,"MED"]
[null,"11/11/2016","15:26:00","KI44","Rural Long","Weather",null,92,430.43478260869563,0.28094799999999998,6.5271000000000003E-4,"MED"]
[null,"11/11/2016","16:53:00","NL511B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1840,178.31793478260872,0.53950100000000001,3.0255E-3,"MED"]
[null,"11/11/2016","17:46:00","ST42","Rural Long","Unknown","Unknown",1,1069,7.5839999999999996E-3,7.0899999999999999E-6,"MED"]
[null,"11/11/2016","18:23:00","BM44","Rural Short","Weather",null,950,1086.7168421052631,8.3328100000000003,7.6678800000000002E-3,"MED"]
[null,"12/11/2016","07:36:00","MV63","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",4.0000010000000001,319,1.0299000000000001E-2,3.2289999999999997E-5]
[null,"12/11/2016","07:59:10","ST44","Rural Long","Asset failure","LV",2,813,1.1535999999999999E-2,1.419E-5]
[null,"12/11/2016","16:10:00","SD481","Rural Short","Unknown","Unknown",629,129.78696343402228,0.65892099999999998,5.0769400000000003E-3]
[null,"13/11/2016","10:25:17","NL544B","Urban","Vegetation","Grow-in - NSP responsibility",1,337.00000000000006,5.5400000000000002E-4,1.64E-6]
[null,"13/11/2016","17:27:00","G36","Rural Long","Asset failure","HV",35,1195.3714285714286,0.29682599999999998,2.4831000000000001E-4]
[null,"14/11/2016","07:25:00","AP351B","Urban","Unknown","Unknown",6.0000030000000004,134,1.322E-3,9.8700000000000004E-6]
[null,"14/11/2016","16:19:22","HH429B","Urban","Asset failure","LV",57,112.99999999999999,1.0591E-2,9.3720000000000004E-5]
[null,"15/11/2016","10:25:00","GA39","Rural Long","Planned",null,1,61,4.3300000000000001E-4,7.0899999999999999E-6]
[null,"15/11/2016","22:30:42","SM216C","Urban","Overloads",null,1,212,3.4900000000000003E-4,1.64E-6]
[null,"16/11/2016","11:01:08","NL760C","Urban","Planned",null,29,166,7.9159999999999994E-3,4.7679999999999998E-5]
[null,"17/11/2016","09:28:00","MV62","Rural Short","Planned",null,110,147,0.13051499999999999,8.8785999999999997E-4]
[null,"18/11/2016","08:46:53","CD03","Rural Short","Asset failure","LV",2,84,1.356E-3,1.6140000000000001E-5]
[null,"18/11/2016","09:10:00","PA24","Rural Long","Planned",null,1,133,9.4399999999999996E-4,7.0899999999999999E-6]
[null,"19/11/2016","22:02:00","NA01","Rural Long","Planned",null,8,467.99999999999994,2.6561999999999999E-2,5.6759999999999999E-5]
[null,"20/11/2016","20:33:00","EL01Q","Urban","Planned",null,196,11.071428571428571,3.568E-3,3.2227999999999998E-4]
[null,"21/11/2016","09:02:26","HH102D","Urban","Planned",null,22,382.99999999999994,1.3854999999999999E-2,3.6170000000000001E-5]
[null,"21/11/2016","15:44:00","CM11","Rural Long","Weather",null,15,382.8,4.0737000000000002E-2,1.0642E-4]
[null,"22/11/2016","08:30:26","SA14","Urban","Planned",null,43,127,8.9789999999999991E-3,7.0699999999999997E-5]
[null,"22/11/2016","11:14:00","GA36","Rural Long","Planned",null,2,44,6.2399999999999999E-4,1.419E-5]
[null,"24/11/2016","08:11:30","HH428A","Urban","Planned",null,78,165,2.1162E-2,1.2825E-4]
[null,"24/11/2016","10:31:35","EL20","Urban","Asset failure","LV",1,180,2.9599999999999998E-4,1.64E-6]
[null,"26/11/2016","17:23:00","BT34","Rural Long","Third Party","Vehicle impact",58,441.99999999999994,0.18187800000000001,4.1148999999999998E-4]
[null,"28/11/2016","03:10:00","ST51","Rural Short","Unknown","Unknown",154,229.94155844155841,0.28581800000000002,1.243E-3]
[null,"28/11/2016","07:57:19","PA03","Urban","Planned",null,24,370.00000000000006,1.4600999999999999E-2,3.9459999999999998E-5]
[null,"29/11/2016","08:27:57","HH102C","Urban","Planned",null,118,403.99999999999994,7.8386999999999998E-2,1.9403000000000001E-4]
[null,"30/11/2016","00:14:00","EL21","Urban","Planned",null,3,256,1.263E-3,4.9300000000000002E-6]
[null,"30/11/2016","09:07:00","ST11","Rural Short","Planned",null,107,300,0.25909300000000002,8.6364000000000005E-4]
[null,"1/12/2016","07:42:49","EL01N","Urban","Planned",null,81,199,2.6504E-2,1.3318999999999999E-4]
[null,"1/12/2016","13:59:03","AP344D","Urban","Planned",null,1,15.000000000000002,2.5000000000000001E-5,1.64E-6]
[null,"2/12/2016","13:57:57","SM179A","Urban","Asset failure","LV",16.999983,44,1.23E-3,2.7949999999999998E-5]
[null,"4/12/2016","09:09:00","SA19","Urban","Unknown","Unknown",39.333353000000002,131,8.4729999999999996E-3,6.4679999999999997E-5]
[null,"5/12/2016","14:34:00","MV14","Rural Short","Planned",null,2,27,4.3600000000000003E-4,1.6140000000000001E-5]
[null,"6/12/2016","10:27:00","HK05","Rural Long","Planned",null,1,52,3.6900000000000002E-4,7.0899999999999999E-6]
[null,"7/12/2016","09:52:58","AP149A","Urban","Planned",null,1,84.000000000000014,1.3799999999999999E-4,1.64E-6]
[null,"7/12/2016","21:10:00","CV28","Rural Long","Weather",null,80,916.94999999999993,0.52043399999999995,5.6756999999999999E-4]
[null,"8/12/2016","00:10:00","MG32","Rural Long","Asset failure","HV",245,178.26530612244898,0.30985800000000002,1.7381899999999999E-3]
[null,"8/12/2016","09:58:00","SD371","Rural Long","Planned",null,1,115,8.1599999999999999E-4,7.0899999999999999E-6]
[null,"8/12/2016","14:44:02","MB71","Rural Long","Asset failure","LV",2,253,3.5899999999999999E-3,1.419E-5]
[null,"9/12/2016","09:27:00","SM137C","Urban","Planned",null,165,230.00000000000003,6.2400999999999998E-2,2.7130999999999998E-4]
[null,"11/12/2016","09:36:00","ME347D","Urban","Planned",null,38,21.94736842105263,1.371E-3,6.2479999999999998E-5]
[null,"12/12/2016","08:27:11","VH23","Rural Short","Planned",null,33,282,7.5112999999999999E-2,2.6635999999999999E-4]
[null,"12/12/2016","15:55:00","CBD366E","Urban","Unknown","Unknown",62,25,2.5490000000000001E-3,1.0195E-4]
[null,"13/12/2016","13:28:03","PP10","Urban","Asset failure","LV",1,113,1.8599999999999999E-4,1.64E-6]
[null,"14/12/2016","11:39:47","SA14","Urban","Planned",null,51,30.000000000000004,2.516E-3,8.386E-5]
[null,"15/12/2016","08:42:00","SD344","Rural Long","Planned",null,617,20.254457050243111,8.8662000000000005E-2,4.3773900000000001E-3]
[null,"16/12/2016","02:02:00","HH177B","Urban","Asset failure","HV",1,634,1.042E-3,1.64E-6]
[null,"17/12/2016","09:04:00","CBD366E","Urban","Planned",null,83,450.00000000000006,6.1414000000000003E-2,1.3647999999999999E-4]
[null,"18/12/2016","06:41:00","MV15","Rural Short","Planned",null,19,106.47368421052632,1.6329E-2,1.5336000000000001E-4]
[null,"19/12/2016","08:28:00","NL451A","Urban","Planned",null,511,13.017612524461839,1.0938E-2,8.4022999999999997E-4]
[null,"19/12/2016","22:58:13","EL16","Urban","Unknown","Unknown",2,262,8.6200000000000003E-4,3.2899999999999998E-6]
[null,"21/12/2016","08:40:49","NU14","Rural Long","Asset failure","LV",2,149,2.114E-3,1.419E-5]
[null,"22/12/2016","09:15:00","MTB14","Rural Short","Planned",null,54,315,0.137295,4.3585999999999999E-4]
[null,"22/12/2016","18:03:59","NL451E","Urban","Asset failure","LV",1,130,2.14E-4,1.64E-6]
[null,"23/12/2016","18:58:38","SA19","Urban","Asset failure","LV",1,146,2.4000000000000001E-4,1.64E-6,"MED"]
[null,"25/12/2016","07:42:29","NL544B","Urban","Asset failure","LV",17.666649,247,7.175E-3,2.9050000000000001E-5]
[null,"25/12/2016","18:20:20","PP04","Rural Short","Overloads",null,1,88,7.1000000000000002E-4,8.0700000000000007E-6]
[null,"26/12/2016","19:07:02","R18","Rural Long","Third Party","Vehicle impact",1,161,1.142E-3,7.0899999999999999E-6]
[null,"27/12/2016","10:29:03","SA40","Urban","Asset failure","LV",14.666651999999999,174,4.1960000000000001E-3,2.4119999999999999E-5,"MED"]
[null,"27/12/2016","21:11:00","SD311","Rural Long","Asset failure","Subtransmission",943,2169.3001060445386,14.513147999999999,6.6902400000000001E-3,"MED"]
[null,"27/12/2016","23:56:00","R01","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",19,909,0.122532,1.348E-4,"MED"]
[null,"28/12/2016","01:02:00","ST35","Rural Long","Unknown","Unknown",31,4023,0.88479399999999997,2.1992999999999999E-4,"MED"]
[null,"28/12/2016","02:07:00","VH15","Rural Short","Unknown","Unknown",27,493,0.10743900000000001,2.1793E-4,"MED"]
[null,"28/12/2016","02:57:00","SG13","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",922,14.148590021691975,0.105292,7.4418799999999997E-3,"MED"]
[null,"28/12/2016","03:29:47","SM126B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,391,6.4300000000000002E-4,1.64E-6,"MED"]
[null,"28/12/2016","04:19:00","HH428C","Urban","Unknown","Unknown",35,2134,0.122812,5.7550000000000003E-5,"MED"]
[null,"28/12/2016","04:45:00","MTB14","Rural Short","Weather",null,null,1,5.8900000000000001E-4,0,"MED"]
[null,"28/12/2016","05:44:00","ST35","Rural Long","Unknown","Unknown",null,2,1.575E-3,0,"MED"]
[null,"28/12/2016","07:04:00","BT06","Rural Long","Unknown","Unknown",52,455.76923076923077,0.16814299999999999,3.6892000000000001E-4,"MED"]
[null,"28/12/2016","08:01:43","HH121A","Urban","Asset failure","LV",1,2210,3.6340000000000001E-3,1.64E-6,"MED"]
[null,"28/12/2016","10:12:32","NL210D","Urban","Unknown","Unknown",1,500,8.2200000000000003E-4,1.64E-6,"MED"]
[null,"28/12/2016","12:23:50","ME200A","Urban","Unknown","Unknown",8.6666709999999991,594.00000000000011,8.4650000000000003E-3,1.4250000000000001E-5,"MED"]
[null,"28/12/2016","17:50:00","SD371","Rural Long","Asset failure","Subtransmission",583,15.780445969125214,6.5270999999999996E-2,4.1361699999999998E-3,"MED"]
[null,"28/12/2016","20:01:10","HH130D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,3041.0000000000005,5.0000000000000001E-3,1.64E-6,"MED"]
[null,"29/12/2016","03:07:24","SA36","Urban","Asset failure","LV",42,2463,0.170096,6.9060000000000006E-5]
[null,"29/12/2016","09:19:01","HH522B","Urban","Vegetation","Grow-in - NSP responsibility",13.999986,616,1.418E-2,2.302E-5]
[null,"29/12/2016","15:40:45","PP06","Rural Long","Asset failure","LV",26.333319000000007,1671,0.31218499999999999,1.8683E-4]
[null,"29/12/2016","23:33:56","NL210C","Urban","Asset failure","HV",76,162,2.0244999999999999E-2,1.2496999999999999E-4]
[null,"30/12/2016","09:32:00","PP04","Rural Short","Asset failure","HV",287,130,0.30114600000000002,2.3165099999999999E-3]
[null,"31/12/2016","02:11:58","SA11","Urban","Asset failure","LV",69,110.00000000000001,1.248E-2,1.1346E-4]
[null,"31/12/2016","17:29:37","MTB33","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",3,1219.0000000000002,2.9517000000000002E-2,2.421E-5]
[null,"31/12/2016","19:14:13","SG12","Rural Short","Vegetation","Blow-in/Fall-in - NSP responsibility",10,1318,0.106382,8.0710000000000005E-5]
[null,"1/01/2017","22:47:00","SM126A","Urban","Asset failure","HV",33,47,2.5500000000000002E-3,5.4259999999999999E-5]
[null,"3/01/2017","16:52:00","HH386A","Urban","Animal","Animal impact",1,382.00000000000006,6.2799999999999998E-4,1.64E-6]
[null,"4/01/2017","14:03:57","KA02","Rural Short","Asset failure","LV",16.999983,24,3.2929999999999999E-3,1.3721E-4]
[null,"5/01/2017","01:39:54","SA17","Urban","Asset failure","LV",15.333318,506,1.2758E-2,2.5210000000000001E-5]
[null,"5/01/2017","18:10:14","MB43","Rural Long","Asset failure","LV",2,401.99999999999994,5.7039999999999999E-3,1.419E-5]
[null,"6/01/2017","01:44:00","HK04","Rural Long","Weather",null,29,1054.0689655172412,0.21686900000000001,2.0573999999999999E-4]
[null,"6/01/2017","19:42:51","HH107B","Urban","Unknown","Unknown",30.666636,145.00000000000003,7.3119999999999999E-3,5.0420000000000002E-5]
[null,"7/01/2017","16:24:00","SB17","Rural Long","Weather",null,81,277.22222222222223,0.15931000000000001,5.7467E-4]
[null,"9/01/2017","08:23:28","BM15","Rural Short","Planned",null,1,288,2.3249999999999998E-3,8.0700000000000007E-6]
[null,"10/01/2017","07:23:38","PA13","Rural Long","Animal","Animal impact",1,118,8.3699999999999996E-4,7.0899999999999999E-6]
[null,"10/01/2017","08:22:20","HH496G","Urban","Planned",null,10,242.99999999999997,3.9960000000000004E-3,1.6439999999999998E-5]
[null,"11/01/2017","09:58:00","GU31","Rural Long","Planned",null,117,154.00000000000003,0.127831,8.3007000000000003E-4]
[null,"12/01/2017","07:28:13","SA36","Urban","Asset failure","HV",2.0000010000000001,247,8.12E-4,3.2899999999999998E-6]
[null,"12/01/2017","22:45:00","SA36","Urban","Asset failure","Distribution substation",2,195.00000000000003,6.4099999999999997E-4,3.2899999999999998E-6]
[null,"13/01/2017","14:33:24","PA13","Rural Long","Asset failure","LV",1,155,1.1000000000000001E-3,7.0899999999999999E-6]
[null,"15/01/2017","09:28:00","MTB12","Rural Short","Unknown","Unknown",5,135.99999999999997,5.489E-3,4.036E-5]
[null,"16/01/2017","19:30:21","SA31","Urban","Asset failure","LV",1,160.00000000000003,2.63E-4,1.64E-6]
[null,"17/01/2017","08:45:00","KA25","Rural Long","Planned",null,16,217,2.4632999999999999E-2,1.1351E-4]
[null,"18/01/2017","01:00:32","HH522C","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",16.666650000000001,5,1.37E-4,2.7399999999999999E-5]
[null,"19/01/2017","08:45:00","EL18","Urban","Planned",null,33,245,1.3294E-2,5.4259999999999999E-5,"MED"]
[null,"19/01/2017","17:52:00","CV22","Rural Long","Weather",null,42,1086.6666666666667,0.323799,2.9796999999999999E-4,"MED"]
[null,"19/01/2017","19:55:00","R29","Rural Long","Weather",null,81,367.19753086419757,0.21101600000000001,5.7467E-4,"MED"]
[null,"19/01/2017","20:33:00","HH145A","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1805,1,2.9680000000000002E-3,2.96795E-3,"MED"]
[null,"19/01/2017","21:08:37","SM402B","Urban","Unknown","Unknown",38.000019000000002,351.00000000000006,2.1932E-2,6.2479999999999998E-5,"MED"]
[null,"19/01/2017","21:24:28","EL10","Urban","Vegetation","Grow-in - NSP responsibility",71,373,4.3546000000000001E-2,1.1674E-4,"MED"]
[null,"19/01/2017","21:50:06","AP146B","Urban","Unknown","Unknown",60.000030000000002,421.00000000000006,4.1535000000000002E-2,9.8659999999999994E-5,"MED"]
[null,"20/01/2017","04:32:03","SA31","Urban","Asset failure","LV",24.000012000000002,463,1.8270999999999999E-2,3.9459999999999998E-5]
[null,"20/01/2017","05:19:14","NL234D","Urban","Vegetation","Grow-in - NSP responsibility",37.333351999999998,253.00000000000006,1.5531E-2,6.1389999999999993E-5]
[null,"20/01/2017","13:47:55","AP125A","Urban","Asset failure","LV",1,1151,1.8929999999999999E-3,1.64E-6]
[null,"21/01/2017","07:44:10","SM374E","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",21.999977999999999,67,2.4239999999999999E-3,3.6170000000000001E-5]
[null,"22/01/2017","09:43:49","NL210B","Urban","Asset failure","LV",0.99999899999999997,246.99999999999997,4.06E-4,1.64E-6]
[null,"23/01/2017","09:31:34","NL451C","Urban","Planned",null,48,40.000000000000007,3.1570000000000001E-3,7.8930000000000005E-5]
[null,"23/01/2017","20:20:34","AP146B","Urban","Asset failure","LV",68,77,8.6099999999999996E-3,1.1181E-4]
[null,"24/01/2017","08:51:00","LC02","Rural Long","Asset failure","HV",83,487.37349397590356,0.28699200000000002,5.8885999999999997E-4]
[null,"24/01/2017","20:13:57","MT19","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",2,1000,1.4189E-2,1.419E-5]
[null,"25/01/2017","13:45:18","MT18","Rural Long","Animal","Animal impact",1,110,7.7999999999999999E-4,7.0899999999999999E-6]
[null,"27/01/2017","13:49:58","AP425D","Urban","Asset failure","LV",2,70,2.3000000000000001E-4,3.2899999999999998E-6]
[null,"30/01/2017","05:41:52","EL01P","Urban","Asset failure","LV",11.666655,231.99999999999997,4.4510000000000001E-3,1.9179999999999999E-5]
[null,"30/01/2017","11:22:00","PL24","Rural Long","Planned",null,2,61,8.6600000000000002E-4,1.419E-5]
[null,"31/01/2017","12:54:00","M93","Rural Long","Unknown","Unknown",2,13,1.84E-4,1.419E-5]
[null,"1/02/2017","09:04:28","EL23","Urban","Planned",null,10,245.99999999999997,4.045E-3,1.6439999999999998E-5]
[null,"2/02/2017","09:09:00","SD54302","Rural Long","Planned",null,4,295,8.3719999999999992E-3,2.8379999999999999E-5]
[null,"2/02/2017","14:30:51","GA01","Urban","Third Party","Vehicle impact",0.99999899999999997,119,1.9599999999999999E-4,1.64E-6]
[null,"3/02/2017","17:15:18","HH432E","Urban","Asset failure","LV",1,99.000000000000014,1.63E-4,1.64E-6]
[null,"5/02/2017","19:35:10","AP365C","Urban","Asset failure","LV",1,33,5.3999999999999998E-5,1.64E-6]
[null,"6/02/2017","09:07:00","NL451A","Urban","Planned",null,841,4.4827586206896548,6.1989999999999996E-3,1.3828499999999999E-3]
[null,"6/02/2017","17:16:26","CBD103C","Urban","Asset failure","LV",25,80,3.2889999999999998E-3,4.1109999999999998E-5]
[null,"8/02/2017","00:20:45","HH496C","Urban","Unknown","Unknown",13.333320000000001,67,1.469E-3,2.192E-5]
[null,"8/02/2017","18:18:05","HH409C","Urban","Unknown","Unknown",22.999977000000001,147,5.5589999999999997E-3,3.782E-5]
[null,"8/02/2017","20:09:48","AP355F","Urban","Overloads",null,35.666631000000002,146,8.5620000000000002E-3,5.8650000000000003E-5]
[null,"8/02/2017","22:14:01","HH107A","Urban","Overloads",null,25.999974000000002,182.99999999999997,7.8239999999999994E-3,4.2750000000000002E-5]
[null,"9/02/2017","08:01:50","AP529E","Urban","Overloads",null,32.666634000000002,106.99999999999999,5.7470000000000004E-3,5.3709999999999999E-5]
[null,"9/02/2017","14:01:40","EL17","Urban","Unknown","Unknown",1,36,5.8999999999999998E-5,1.64E-6]
[null,"9/02/2017","18:07:05","HH102C","Urban","Asset failure","LV",15.666651,86,2.215E-3,2.5760000000000001E-5]
[null,"9/02/2017","22:33:19","HH409F","Urban","Unknown","Unknown",18.999980999999998,34,1.062E-3,3.1239999999999999E-5]
[null,"10/02/2017","08:15:00","BM31","Rural Short","Animal","Animal impact",442,84,0.29967700000000003,3.5675799999999999E-3]
[null,"10/02/2017","18:51:00","HH409D","Urban","Overloads",null,24.333309,97,3.8809999999999999E-3,4.0009999999999998E-5]
[null,"11/02/2017","16:44:48","HH118D","Urban","Asset failure","LV",1,436,7.1699999999999997E-4,1.64E-6]
[null,"13/02/2017","08:56:29","AP424B","Urban","Planned",null,32,337.00000000000006,1.7732000000000001E-2,5.2620000000000001E-5]
[null,"14/02/2017","09:15:00","MB26","Rural Long","Planned",null,31,165.00000000000003,3.6289000000000002E-2,2.1992999999999999E-4]
[null,"14/02/2017","12:53:00","AP125D","Urban","Asset failure","LV",15.333318,38,9.5799999999999998E-4,2.5210000000000001E-5]
[null,"15/02/2017","14:37:39","AP227D","Urban","Asset failure","LV",13.333320000000001,42,9.2100000000000005E-4,2.192E-5]
[null,"16/02/2017","09:01:00","WK51","Rural Short","Planned",null,17,294,4.0341000000000002E-2,1.3721E-4]
[null,"16/02/2017","18:05:50","NL234C","Urban","Asset failure","LV",1,173,2.8400000000000002E-4,1.64E-6]
[null,"17/02/2017","15:19:00","YK30","Rural Long","Asset failure","HV",109,171.00000000000003,0.13223699999999999,7.7331999999999998E-4]
[null,"19/02/2017","09:10:56","ME116C","Urban","Planned",null,120,22.999999999999996,4.5380000000000004E-3,1.9731999999999999E-4]
[null,"20/02/2017","09:06:00","MB81","Rural Long","Planned",null,5,45.999999999999993,1.632E-3,3.5469999999999998E-5]
[null,"21/02/2017","08:22:51","VH10","Rural Short","Planned",null,55,390.00000000000006,0.17313300000000001,4.4392999999999999E-4]
[null,"22/02/2017","15:07:00","NU02","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1641,49,0.57047300000000001,1.16423E-2]
[null,"23/02/2017","10:00:00","MB25","Rural Long","Planned",null,2,86,1.2199999999999999E-3,1.419E-5]
[null,"24/02/2017","06:24:00","BM54","Rural Short","Planned",null,2,4,6.4999999999999994E-5,1.6140000000000001E-5]
[null,"25/02/2017","06:44:57","HH145B","Urban","Asset failure","LV",1,309,5.0799999999999999E-4,1.64E-6]
[null,"27/02/2017","09:24:00","W04","Rural Long","Planned",null,21,60,8.9390000000000008E-3,1.4898999999999999E-4]
[null,"28/02/2017","01:19:00","NL210D","Urban","Unknown","Unknown",567,43.380952380952387,4.0445000000000002E-2,9.3232000000000005E-4]
[null,"1/03/2017","08:38:49","NL111P","Urban","Planned",null,86,120.99999999999999,1.7111000000000001E-2,1.4140999999999999E-4]
[null,"1/03/2017","09:33:29","ME231F","Urban","Asset failure","LV",1,692,1.1379999999999999E-3,1.64E-6]
[null,"2/03/2017","08:56:29","PP02","Urban","Planned",null,16,459,1.2076E-2,2.6310000000000001E-5]
[null,"3/03/2017","07:36:10","HH148D","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",1,134,2.2000000000000001E-4,1.64E-6]
[null,"3/03/2017","08:37:52","AP424A","Urban","Planned",null,37,288,1.7521999999999999E-2,6.084E-5]
[null,"4/03/2017","16:45:50","BU09","Rural Long","Vegetation","Blow-in/Fall-in - NSP responsibility",1,278,1.9719999999999998E-3,7.0899999999999999E-6]
[null,"6/03/2017","09:05:00","PL10","Rural Long","Planned",null,7,268,1.3310000000000001E-2,4.9660000000000002E-5]
[null,"6/03/2017","17:24:54","HH177E","Urban","Asset failure","LV",66,42,4.5580000000000004E-3,1.0852E-4]
[null,"8/03/2017","06:35:00","HH177E","Urban","Planned",null,1,108,1.7799999999999999E-4,1.64E-6]
[null,"8/03/2017","12:52:03","CBD412M","Urban","Asset failure","LV",19.666647000000001,144,4.6569999999999997E-3,3.2339999999999999E-5]
[null,"9/03/2017","08:42:00","VH23","Rural Short","Planned",null,26,314,6.5894999999999995E-2,2.0986E-4]
[null,"9/03/2017","19:41:31","MTB51","Rural Long","Asset failure","LV",1,184,1.305E-3,7.0899999999999999E-6]
[null,"11/03/2017","01:25:00","PL01","Urban","Asset failure","HV",1099,56.41310282074614,0.10194300000000001,1.80708E-3]
[null,"12/03/2017","18:34:41","HH341E","Urban","Vegetation","Grow-in - NSP responsibility",1.6666650000000001,187.99999999999997,5.1500000000000005E-4,2.74E-6]
[null,"14/03/2017","05:41:41","HH145D","Urban","Overloads",null,1,292,4.8000000000000001E-4,1.64E-6]
[null,"14/03/2017","10:32:00","MV34","Rural Short","Planned",null,31,2,5.0000000000000001E-4,2.5021E-4]
[null,"15/03/2017","08:16:58","MI03","Rural Long","Overloads",null,1,173,1.227E-3,7.0899999999999999E-6]
[null,"16/03/2017","09:32:12","MTB10","Urban","Planned",null,44,335.99999999999994,2.4309000000000001E-2,7.2349999999999997E-5]
[null,"16/03/2017","21:09:38","AP146C","Urban","Planned",null,29,408,1.9455E-2,4.7679999999999998E-5]
[null,"17/03/2017","20:48:26","SM126B","Urban","Asset failure","LV",27.999972,100,4.6039999999999996E-3,4.604E-5]
[null,"19/03/2017","15:26:16","GA745B","Rural Short","Animal","Animal impact",1,195,1.5740000000000001E-3,8.0700000000000007E-6]
[null,"20/03/2017","00:01:00","MTB14","Rural Short","Animal","Animal impact",289,113.02076124567476,0.26363799999999998,2.3326499999999999E-3]
[null,"20/03/2017","18:51:14","EL14","Urban","Asset failure","LV",1,122.00000000000001,2.0100000000000001E-4,1.64E-6]
[null,"21/03/2017","10:09:00","SA36","Urban","Planned",null,15,270,6.659E-3,2.4660000000000001E-5]
[null,"22/03/2017","09:09:00","GU32","Rural Long","Planned",null,31,333,7.3237999999999998E-2,2.1992999999999999E-4]
[null,"22/03/2017","10:21:39","HH428F","Urban","Planned",null,126,109,2.2582999999999999E-2,2.0718000000000001E-4]
[null,"23/03/2017","10:49:00","G22","Rural Long","Planned",null,3,107,2.2769999999999999E-3,2.128E-5]
[null,"24/03/2017","11:04:00","R25","Rural Long","Asset failure","HV",3,21,4.4700000000000002E-4,2.128E-5]
[null,"25/03/2017","11:15:00","HH130A","Urban","Unknown","Unknown",115,60.000000000000007,1.1346E-2,1.8908999999999999E-4]
[null,"27/03/2017","03:31:00","NU20","Rural Long","Unknown","Unknown",953,79.115424973767048,0.534914,6.7611900000000003E-3]
[null,"27/03/2017","11:25:00","PA11","Rural Long","Planned",null,1,16,1.1400000000000001E-4,7.0899999999999999E-6]
[null,"28/03/2017","09:35:00","MI15","Rural Long","Planned",null,131,297,0.27603100000000003,9.2940000000000004E-4]
[null,"28/03/2017","09:51:18","SA35","Urban","Planned",null,34,151,8.4419999999999999E-3,5.5909999999999998E-5]
[null,"30/03/2017","04:49:00","CN73","Rural Long","Asset failure","HV",105,1234.9333333333334,0.91994799999999999,7.4494000000000003E-4]
[null,"30/03/2017","10:27:00","G09","Rural Long","Planned",null,2,86,1.2199999999999999E-3,1.419E-5]
[null,"31/03/2017","13:53:00","NU12","Rural Long","Planned",null,1,29,2.0599999999999999E-4,7.0899999999999999E-6]
[null,"1/04/2017","09:56:26","HH341H","Urban","Vegetation","Grow-in - NSP responsibility",5.6666610000000004,16,1.4899999999999999E-4,9.3200000000000006E-6]
[null,"2/04/2017","20:56:12","SA20","Urban","Third Party","Vehicle impact",1,144,2.3699999999999999E-4,1.64E-6]
[null,"3/04/2017","16:45:15","GA01","Urban","Third Party","Vehicle impact",7.9999919999999998,83.999999999999986,1.1050000000000001E-3,1.3149999999999999E-5]
[null,"4/04/2017","11:26:26","EL14","Urban","Planned",null,9,79.999999999999986,1.1839999999999999E-3,1.4800000000000001E-5]
[null,"5/04/2017","09:55:00","R02","Rural Long","Planned",null,15,155.00000000000003,1.6494999999999999E-2,1.0642E-4]
[null,"6/04/2017","13:49:03","SM349F","Urban","Asset failure","LV",75,297.00000000000006,3.6627E-2,1.2332000000000001E-4]
[null,"8/04/2017","10:03:58","AP146B","Urban","Other",null,1,73,1.2E-4,1.64E-6]
[null,"8/04/2017","13:43:00","BM12","Rural Short","Weather",null,460,211.38260869565218,0.78483499999999995,3.7128700000000001E-3]
[null,"9/04/2017","11:34:31","AP149E","Urban","Asset failure","LV",1,358.00000000000006,5.8900000000000001E-4,1.64E-6]
[null,"10/04/2017","09:25:00","HH341C","Urban","Planned",null,122,271,5.4364000000000003E-2,2.006E-4]
[null,"11/04/2017","08:07:31","VH23","Rural Short","Planned",null,37,431.99999999999994,0.12901399999999999,2.9863999999999997E-4]
[null,"11/04/2017","13:29:00","PL12","Rural Long","Planned",null,2,70,9.9299999999999996E-4,1.419E-5]
[null,"12/04/2017","16:36:24","AP146B","Urban","Asset failure","LV",36.333297000000002,109,6.5120000000000004E-3,5.9740000000000001E-5]
[null,"13/04/2017","10:09:30","WK42","Rural Short","Planned",null,3,139,3.3660000000000001E-3,2.421E-5]
[null,"14/04/2017","20:10:00","HH102D","Urban","Unknown","Unknown",31,134,6.8300000000000001E-3,5.0970000000000002E-5]
[null,"17/04/2017","15:29:00","LX53","Rural Short","Animal","Animal impact",6,213,1.0315E-2,4.8430000000000002E-5]
[null,"19/04/2017","10:42:00","SD413","Rural Short","Planned",null,4,130,4.1970000000000002E-3,3.2289999999999997E-5]
[null,"20/04/2017","01:54:00","PA22","Rural Long","Unknown","Unknown",68,773.63235294117646,0.373228,4.8244E-4]
[null,"20/04/2017","12:40:00","NL544B","Urban","Asset failure","HV",1638,51.395604395604394,0.13842699999999999,2.6933500000000002E-3]
[null,"21/04/2017","03:01:51","MI02","Rural Short","Asset failure","HV",1,211,1.7030000000000001E-3,8.0700000000000007E-6]
[null,"22/04/2017","10:08:30","BM41","Urban","Asset failure","LV",1,178,2.9300000000000002E-4,1.64E-6]
[null,"23/04/2017","09:27:00","SD38100","Rural Long","Planned",null,3,128,2.7239999999999999E-3,2.128E-5]
[null,"24/04/2017","12:33:00","EL17","Urban","Animal","Animal impact",7,183,2.1059999999999998E-3,1.151E-5]
[null,"26/04/2017","05:41:00","CN27","Rural Long","Unknown","Unknown",65,456.53846153846155,0.210533,4.6115000000000001E-4]
[null,"26/04/2017","10:30:44","SM410D","Urban","Planned",null,1,284,4.6700000000000002E-4,1.64E-6]
[null,"27/04/2017","10:05:25","HH102B","Urban","Planned",null,79,126,1.6367E-2,1.2990000000000001E-4]
[null,"28/04/2017","10:03:21","HH148D","Urban","Asset failure","LV",1,259,4.26E-4,1.64E-6]
[null,"30/04/2017","11:30:00","NA09","Rural Long","Planned",null,1,50,3.5500000000000001E-4,7.0899999999999999E-6]
[null,"1/05/2017","11:39:00","CV23","Rural Long","Planned",null,2,103,1.4610000000000001E-3,1.419E-5]
[null,"2/05/2017","08:54:51","GA25","Rural Short","Planned",null,18,307,4.4602999999999997E-2,1.4529000000000001E-4]
[null,"3/05/2017","08:31:35","SM179A","Urban","Planned",null,43,59,4.1720000000000004E-3,7.0699999999999997E-5]
[null,"3/05/2017","09:16:00","NU15","Rural Long","Planned",null,2,347,4.9240000000000004E-3,1.419E-5]
[null,"4/05/2017","08:52:42","HH341H","Urban","Planned",null,55,163,1.4741000000000001E-2,9.0439999999999995E-5]
[null,"4/05/2017","18:05:06","SM172A","Urban","Network business","Switching and protection error",4,156.00000000000003,1.026E-3,6.5799999999999997E-6]
[null,"5/05/2017","10:51:00","CV30","Rural Long","Third Party","Vehicle impact",86,74.999999999999986,4.5760000000000002E-2,6.1014000000000001E-4]
[null,"6/05/2017","11:36:00","BT02","Rural Long","Unknown","Unknown",91,206,0.132996,6.4561000000000002E-4]
[null,"7/05/2017","14:07:00","GA745C","Rural Short","Unknown","Unknown",457,132.64989059080963,0.48929899999999998,3.6886499999999999E-3]
[null,"9/05/2017","10:00:11","HH121A","Urban","Unknown","Unknown",7,6,6.8999999999999997E-5,1.151E-5]
[null,"10/05/2017","06:53:30","WHY10","Urban","Asset failure","LV",1,135,2.22E-4,1.64E-6]
[null,"11/05/2017","05:39:13","PL07","Urban","Overloads",null,19.333342999999999,759.99999999999989,2.4160000000000001E-2,3.1789999999999999E-5]
[null,"11/05/2017","21:54:00","HH403A","Urban","Overloads",null,1,205.00000000000003,3.3700000000000001E-4,1.64E-6]
[null,"12/05/2017","19:41:53","HH107D","Urban","Asset failure","LV",13.999986,81,1.8649999999999999E-3,2.302E-5]
[null,"15/05/2017","09:23:00","PL29","Rural Long","Planned",null,1,29.999999999999996,2.13E-4,7.0899999999999999E-6]
[null,"15/05/2017","10:59:44","CBD103C","Urban","Planned",null,73,103,1.2363000000000001E-2,1.2003E-4]
[null,"16/05/2017","14:34:00","CM03","Rural Long","Unknown","Unknown",4,227.99999999999997,6.4700000000000001E-3,2.8379999999999999E-5]
[null,"18/05/2017","01:40:59","HH386B","Urban","Vegetation","Blow-in/Fall-in - NSP responsibility",21.333311999999999,433.00000000000006,1.5188999999999999E-2,3.5080000000000003E-5]
[null,"18/05/2017","08:54:00","PL30","Rural Long","Planned",null,36,205,5.2358000000000002E-2,2.5541000000000002E-4]
[null,"19/05/2017","08:40:19","KA03","Rural Long","Asset failure","LV",2,141,2.0010000000000002E-3,1.419E-5]
[null,"21/05/2017","03:45:00","NL234A","Urban","Planned",null,114,219,4.1050999999999997E-2,1.8745E-4]
[null,"22/05/2017","11:11:00","NL115D","Urban","Planned",null,118,207,4.0163999999999998E-2,1.9403000000000001E-4]
[null,"23/05/2017","09:52:59","KA03","Rural Long","Asset failure","LV",1,147,1.0430000000000001E-3,7.0899999999999999E-6]
[null,"24/05/2017","07:07:34","NU21","Rural Long","Asset failure","LV",1,209.99999999999997,1.49E-3,7.0899999999999999E-6]
[null,"24/05/2017","11:13:24","BM15","Rural Short","Asset failure","LV",3,214,5.182E-3,2.421E-5]
[null,"25/05/2017","09:28:00","VH45","Rural Short","Planned",null,10,422,3.4062000000000002E-2,8.0710000000000005E-5]
[null,"26/05/2017","09:25:00","MTB13","Rural Short","Planned",null,7,180,1.017E-2,5.6499999999999998E-5]
[null,"27/05/2017","14:34:51","MV64","Rural Short","Asset failure","LV",1,244,1.9689999999999998E-3,8.0700000000000007E-6]
[null,"29/05/2017","08:13:47","EL260A","Urban","Animal","Animal impact",1,98,1.6100000000000001E-4,1.64E-6]
[null,"29/05/2017","15:06:07","HH121C","Urban","Asset failure","LV",1,155,2.5500000000000002E-4,1.64E-6]
[null,"30/05/2017","07:50:12","KA04","Rural Long","Asset failure","LV",1,172,1.2199999999999999E-3,7.0899999999999999E-6]
[null,"30/05/2017","10:28:25","EL01Q","Urban","Asset failure","LV",1,105.00000000000001,1.73E-4,1.64E-6]
[null,"31/05/2017","08:16:56","M14","Rural Long","Unknown","Unknown",2,5,7.1000000000000005E-5,1.419E-5]
[null,"1/06/2017","08:39:33","NL115C","Urban","Planned",null,72,235,2.7820999999999999E-2,1.1839E-4]
[null,"1/06/2017","17:49:51","AP149E","Urban","Asset failure","LV",31.666634999999999,138.00000000000003,7.1859999999999997E-3,5.2070000000000001E-5]
[null,"2/06/2017","10:44:20","NL115A","Urban","Unknown","Unknown",28.666681000000001,177,8.3429999999999997E-3,4.7139999999999999E-5]
[null,"2/06/2017","13:24:00","MG27","Rural Long","Planned",null,1,26,1.84E-4,7.0899999999999999E-6]
[null,"4/06/2017","10:16:19","SG04","Rural Short","Asset failure","LV",1,290,2.3410000000000002E-3,8.0700000000000007E-6]
[null,"5/06/2017","09:04:00","YK08","Rural Long","Planned",null,1,59.999999999999993,4.26E-4,7.0899999999999999E-6]
[null,"5/06/2017","09:50:00","BM56","Rural Short","Planned",null,39,50,1.5739E-2,3.1479000000000001E-4]
[null,"6/06/2017","09:32:56","NL111C","Urban","Asset failure","LV",1,111,1.83E-4,1.64E-6]
[null,"7/06/2017","08:52:17","NL544B","Urban","Planned",null,31,374,1.9064000000000001E-2,5.0970000000000002E-5]
[null,"7/06/2017","20:33:59","AP424E","Urban","Asset failure","LV",1,134,2.2000000000000001E-4,1.64E-6]
[null,"8/06/2017","15:06:00","HH496D","Urban","Unknown","Unknown",2623,115.74227983225315,0.499195,4.3129800000000001E-3]
[null,"9/06/2017","10:58:57","CM20","Rural Long","Planned",null,18,135.00000000000003,1.7239999999999998E-2,1.2769999999999999E-4]
[null,"11/06/2017","19:24:21","MB12","Rural Long","Third Party","Vehicle impact",88,367,0.229128,6.2432999999999998E-4]
[null,"13/06/2017","11:30:00","PP13","Rural Long","Unknown","Unknown",2,29.999999999999996,4.26E-4,1.419E-5]
[null,"14/06/2017","09:40:00","HH409E","Urban","Planned",null,62,195.99999999999997,1.9980999999999999E-2,1.0195E-4]
[null,"15/06/2017","08:14:39","HH102D","Urban","Planned",null,37,126,7.6660000000000001E-3,6.084E-5]
[null,"15/06/2017","12:55:25","AP424D","Urban","Overloads",null,1,347,5.71E-4,1.64E-6]
[null,"16/06/2017","09:19:48","AP214A","Urban","Planned",null,88,348,5.0354999999999997E-2,1.4469999999999999E-4]
[null,"16/06/2017","20:19:57","GA53","Rural Short","Asset failure","LV",1,160,1.291E-3,8.0700000000000007E-6]
[null,"19/06/2017","05:57:54","NU21","Rural Long","Asset failure","LV",10,218,1.5466000000000001E-2,7.0950000000000003E-5]
[null,"19/06/2017","09:59:00","AP139D","Urban","Planned",null,58,305,2.9087999999999999E-2,9.5370000000000003E-5]
[null,"20/06/2017","09:22:19","AP226D","Urban","Planned",null,54,163,1.4473E-2,8.8789999999999995E-5]
[null,"22/06/2017","07:38:35","PL803A","Urban","Planned",null,56,470,4.3277999999999997E-2,9.2079999999999999E-5]
[null,"23/06/2017","08:22:08","HH496G","Urban","Planned",null,55,313,2.8306999999999999E-2,9.0439999999999995E-5]
[null,"23/06/2017","20:23:53","AP149E","Urban","Unknown","Unknown",17.999981999999999,118,3.4919999999999999E-3,2.9600000000000001E-5]
[null,"25/06/2017","08:07:58","SM411E","Urban","Unknown","Unknown",43,6,4.2400000000000001E-4,7.0699999999999997E-5]
[null,"26/06/2017","10:37:00","BU10","Rural Long","Planned",null,12,33,2.8089999999999999E-3,8.5140000000000001E-5]
[null,"26/06/2017","17:48:29","HH341A","Urban","Asset failure","LV",1.6666650000000001,158.00000000000003,4.3300000000000001E-4,2.74E-6]
[null,"27/06/2017","19:16:02","AP214D","Urban","Asset failure","LV",25.333307999999999,199.00000000000006,8.2889999999999995E-3,4.1659999999999998E-5]
[null,"28/06/2017","12:17:13","CBD103C","Urban","Planned",null,66,196,2.1271000000000002E-2,1.0852E-4]
[null,"29/06/2017","08:24:00","SB02","Rural Long","Planned",null,2,147,2.0860000000000002E-3,1.419E-5]
[null,"29/06/2017","18:04:29","HH496G","Urban","Asset failure","LV",12.999987000000001,282,6.0280000000000004E-3,2.1379999999999999E-5]
[null,"30/06/2017","09:50:00","SM410D","Urban","Planned",null,32,252,1.3259999999999999E-2,5.2620000000000001E-5]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]
[null,null,null,null,null,null," "]

{"sheet":"Amendments","index":25,"n_rows":3,"n_cols":4,"rows_kept":3,"cut":false,"hidden":false,"merged":[[1,1,1,3]]}
[null,"This sheet may be used to identify amendments made to data resubmitted to the AER."]
[null,"NSP data amendments"]
[null,"Worksheet","Table","Comments"]