## Instructions
Electricity Distribution Network Service Provider
Annual Reporting RIN
This template is to be used by SA Power Networks to fulfil its reporting obligations to the AER.
INSTRUCTIONS
GENERAL | Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting.
CONFIDENTIAL INFORMATION | Please use the macro at the top of each worksheet to identify confidential information in the confidential workbook.
-Do this by selecting the cell or cells that contain confidential information and then run the Mark selection as CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential. -To reverse this, select the cell or cells and run the Return selection to NON-CONFIDENTIAL macro.
RESPONSES | Please return four (4) files to the AER: 1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 2. An actual and an estimate version with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 3. A public version with confidential information either removed completely or aggregated in some form together with writtten consent to disclose the public version of the response. Use the drop down box on the Business and other details worksheet to identify the file as either confidential ('consolidated') or public.
AMENDMENTS | If an NSP wishes to correct data previously submitted to the AER it should resubmit that data using the original completed submission as the starting point. Please make any necessary changes to the data. Data that is not being amended should be left unchanged. NSPs must identify the reason for the amendments in the Amendment Reason box on the Business and other details worksheet. NSPs may provide further details regarding any amendments in the Amendments worksheet. .
NSP may use Amended Data macro to highlight cells that contain amended data. NB: if data is also CONFIDENTIAL, re-apply the Confidentiality macro after applying the Amended macro
Please resubmit two (2) files - a confidential version and a public version of the amended submission to the AER
UNITS OF MEASURE | All amounts are to be unrounded and reported on a one for one basis: that is 1000 is to be entered as '1000'. Applicable units of measure may be identified in the table column headings or row descriptors.
INPUT / NON-INPUT CELLS
Yellow = Input cell (mandatory)
Darker yellow = input cell (mandatory)
Orange = input cell (if data available)
Grey = Not applicable/No inputs required
PLEASE DO NOT ENTER TEXT into cells that are to contain numeric data.
NAVIGATION | Many tables in the worksheets have been "grouped" to allow for easy navigation. To ungroup or group data use the outline symbols in the left margin (for Row groupings) or above the columns (for column groupings).

## Contents
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
CONTENTS
| 1. Business details | 2. Expenditure
| 4. Alternative control services | 5. Network information | 6. Service & quality
Business & other details
2.1 Expenditure summary & reconciliation
2.3 Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.10 Overheads
2.6 Non-network
4.3 Ancillary services - Fee-based services
4.4 Ancillary services - Quoted services
4.1 Public lighting
4.2 Metering
5.4 Maximum demand & utilisation - Spatial
5.2 Asset age profile
5.3 Maximum demand - network level
6.3 Sustained interruptions
2.11 Labour
2.12 Input tables
2.3 (b) Augex data
2.1 Expenditure summary & reconciliation
2.3 (a) Augex project data
2.5 Connections
2.2 Repex
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency response
2.6 Non-network
2.3 (b) Augex data

## Business & other details
CATEGORY ANALYSIS
SA Power Networks
2018-19
BUSINESS & OTHER DETAILS
INSTRUCTIONS
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEET
ENTITY DETAILS
Business Name
| Short name |  |  | SA Power Networks
| ACN/ABN |  |  | 13332330749
| Business Address | [9 empty] | Postal Address
| Address 1 |  |  | 1 Anzac Highway |  |  |  |  | Address 1 |  | GPO Box 77
| Address 2 | [7 empty] | Address 2
| Suburb |  |  | KESWICK |  |  |  |  | Suburb |  | ADELAIDE
| State |  |  | SA |  | Post code |  |  | State |  | SA |  | Post code
`
Contact Names
Name
Phone
Email
REGULATORY CONTROL PERIODS
|  |  | Forthcoming period | 2020-21 | 2021-22 |  |  | 2022-23 |  | 2023-24 |  | 2024-25
|  |  |  | 2025-26 | 2026-27 |  |  | 2027-28 |  | 2028-29 |  | 2029-30
|  |  |  | 2030-31 | 2031-32 |  |  | 2032-33 |  | 2033-34 |  | 2034-35
|  | RESETS | Current period | 2015-16 | 2016-17 |  |  | 2017-18 |  | 2018-19 |  | 2019-20
|  |  |  | 2020-21 | 2021-22 |  |  | 2022-23 |  | 2023-24 |  | 2024-25
|  |  |  | 2025-26 | 2026-27 |  |  | 2027-28 |  | 2028-29 |  | 2029-30
|  |  | Previous period | 2010-11 | 2011-12 |  |  | 2012-13 |  | 2013-14 |  | 2014-15
|  |  |  | 2015-16 | 2016-17 |  |  | 2017-18 |  | 2018-19 |  | 2019-20
|  |  |  | 2020-21 | 2021-22 |  |  | 2022-23 |  | 2023-24 |  | 2024-25
|  |  | Commencing year | 2018-19
ANNUAL RINS
|  |  | Final year | 2018-19
SUBMISSION DETAILS
|  |  | RIN type | Category Analysis
|  |  | Source | Reporting
|  | THIS FILE | Data Quality | Consolidated
|  |  | Confidentiality Status | Public
|  |  | Amended RIN Amendment Reason | .
|  |  | Submission Date | 2019-10-31
Contents
Instructions

## 2.1 Expenditure summary
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.1 EXPENDITURE SUMMARY & RECONCILIATION
There are SIX tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.1.1 - STANDARD CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2018-19
Replacement expenditure | 148766797.76
Connections | 82263012.31
Augmentation Expenditure | 80506156.01
Non-network | 112801628.28
Capitalised network overheads | 4531405.78
Capitalised corporate overheads | -6271515.89
Metering | 0
Public Lighting | 0
balancing item | -7078279.28
capcons (included in the above) | 40866775.23
TOTAL GROSS CAPEX (including capcons) | 415519204.97
2.1.2 - STANDARD CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2018-19
Vegetation management | 33543575.03
Maintenance | 33511338.63
Emergency response | 40823594.43
Non-network | 40886776.81
Network overheads | 82520278.36
Corporate overheads | 78563015.57
Metering | 0
Public Lighting | 0
balancing item | -45404643.56
TOTAL OPEX | 264443935.27
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
EXPENDITURE ($0's)
2018-19
Connections | 0
Capitalised network overheads | 0
Capitalised corporate overheads | 0
Metering | 0
Public lighting | 0
Fee and quoted | 0
balancing item | 0
TOTAL CAPEX | 0
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
EXPENDITURE ($0's)
2018-19
Connections | 0
Network overheads | 2316229.03
Corporate overheads | 800506.79
Metering | 5274074.45
Public lighting | 0
Fee and quoted | 0
balancing item | 0
TOTAL OPEX | 8390810.27
2.1.5 - DUAL FUNCTION ASSETS CAPEX
EXPENDITURE ($0's)
2018-19
Replacement expenditure | 0
Connections | 0
Augmentation Expenditure | 0
Non-network | 0
Capitalised network overheads | 0
Capitalised corporate overheads | 0
balancing item | 0
capcons (included in the above) | 0
TOTAL GROSS CAPEX (including capcons) | 0
2.1.6 - DUAL FUNCTION ASSETS OPEX
EXPENDITURE ($0's)
2018-19
Vegetation management | 0
Maintenance | 0
Emergency response | 0
Non-network | 0
Network overheads | 0
Corporate overheads | 0
balancing item | 0
TOTAL OPEX | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.2 Repex
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.2 REPEX
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | EXPENDITURE ($0's) | ASSET REPLACEMENTS (0's) | ASSET FAILURES (0's)
ASSET GROUP | ASSET CATEGORY |  | 2018-19 | 2018-19 | 2018-19
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole
˂ = 1 kV; Wood
> 1 kV & < = 11 kV; Wood
˃ 11 kV & < = 22 kV; Wood
> 22 kV & < = 66 kV; Wood
> 66 kV & < = 132 kV; Wood
> 132 kV; Wood
˂ = 1 kV; Concrete
> 1 kV & < = 11 kV; Concrete
˃ 11 kV & < = 22 kV; Concrete
> 22 kV & < = 66 kV; Concrete
> 66 kV & < = 132 kV; Concrete
> 132 kV; Concrete
˂ = 1 kV; Steel
> 1 kV & < = 11 kV; Steel
˃ 11 kV & < = 22 kV; Steel
> 22 kV & < = 66 kV; Steel
> 66 kV & < = 132 kV; Steel
> 132 kV; Steel
Other
POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 6623820.8469 | 6851 | 3012
| > 1 kV & < = 11 kV |  | 22774794.1258 | 15000 | 1096
| ˃ 11 kV & < = 22 kV |  | 3942755.928 | 1821 | 603
| > 22 kV & < = 66 kV |  | 2264964.8611 | 681 | 132
| > 66 kV & < = 132 kV |  | 0
| > 132 kV |  | 0
| Other |  | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV |  | 1467241.5652 | 28.15 | 1009
| > 1 kV & < = 11 kV |  | 2646986.7095 | 64.354 | 185
| ˃ 11 kV & < = 22 kV ; SWER |  | 397931.0608 | 3.63 | 118
| ˃ 11 kV & < = 22 kV ; Single-Phase |  | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase |  | 0
| > 22 kV & < = 66 kV |  | 35088.448 | 0.53 | 4
| > 66 kV & < = 132 kV |  | 0
| > 132 kV |  | 0
| Other |  | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 7086550.181 | 4.84 | 465
| > 1 kV & < = 11 kV |  | 3630146.1577 | 2.708 | 117
| > 11 kV & < = 22 kV |  | 61960.8227 | 0.09 | 10
| > 22 kV & < = 33 kV |  | 430782.3713 | 0.12 | 12
| > 33 kV & < = 66 kV |  | 720393.4674 | 0.001
| > 66 kV & < = 132 kV |  | 0
| > 132 kV |  | 0
| Other |  | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type |  | 10703551.0817 | 20309 | 6102.73
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type |  | 0
| ˂ = 11 kV ; Residential ; Complex Type |  | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type |  | 1189283.4535 | 2251 | 754.27
| ˂ = 11 kV ; Subdivision ; Complex Type |  | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial |  | 0
| > 11 kV & < = 22 kV ; Subdivision |  | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial |  | 0
| > 22 kV & < = 33 kV ; Subdivision |  | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial |  | 0
| > 33 kV & < = 66 kV ; Subdivision |  | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial |  | 0
| > 66 kV & < = 132 kV ; Subdivision |  | 0
| > 132 kV ; Commercial & Industrial |  | 0
| > 132 kV ; Subdivision |  | 0
| Other |  | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 3543232.8174 | 278 | 142
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 76849.159 | 4 | 1
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 673950.1598 | 47 | 21
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 1659760.067 | 110 | 51
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 389458.1486 | 14 | 6
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 7101.7639 | 1
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase |  | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase |  | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase |  | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA |  | 238855.2148 | 2 | 2
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA |  | 363860.0682 | -
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA |  | 5625461.949 | 1 | 1
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA |  | 0
| Other |  | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; FUSE |  | 0
| ˂ = 11 kV ; Switch |  | 109869.555 | 0 | 0
| ˂ = 11 kV ; Circuit Breaker |  | 8023255.2358 | 15 | 0
| > 11 kV & < = 22 kV ; Switch |  | 0
| > 11 kV & < = 22 kV ; Circuit Breaker |  | 0
| > 22 kV & < = 33 kV ; Switch |  | 199695.0964 | 4 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker |  | 3008020.8458 | 15 | 0
| > 33 kV & < = 66 kV ; Switch |  | 261670.853 | 14 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker |  | 2139524.5579 | 7
| > 66 kV & < = 132 kV ; Switch |  | 0
| > 66 kV & < = 132 kV ; Circuit Breaker |  | 0
| > 132 kV ; Switch |  | 0
| > 132 kV ; Circuit Breaker |  | 0
| Other |  | 0
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road |  | 0
| Luminaires ; Minor Road |  | 0
| Brackets ; Major Road |  | 0
| Brackets ; Minor Road |  | 0
| Lamps ; Major Road |  | 0
| Lamps ; Minor Road |  | 0
| Poles / Columns ; Major Road |  | 0
| Poles / Columns ; Minor Road |  | 0
| Other |  | 0
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices |  | 5677490.4719 | 116 | 38
| Local Network Wiring Assets |  | 0
| Communications Network Assets |  | 6065006.3838 | 17 | 0
| Master Station Assets |  | 0
| Communications Site Infrastructure |  | 0
| Communications Linear Assets |  | 274982.6915 | 0 | 0
| AFLC |  | 0
| Other |  | 0
OTHER BY: DNSP DEFINED | ˂ = 1 kV; stobie pole |  | 3076895.0412 | 418 | 116
| > 1 kV & < = 11 kV; stobie pole |  | 17300464.8142 | 1704 | 135
| ˃ 11 kV & < = 22 kV; stobie pole |  | 1685641.0332 | 198 | 39
| > 22 kV & < = 66 kV; stobie pole |  | 785413.5664 | 50 | 2
| > 66 kV & < = 132 kV; stobie pole |  | 0
| > 132 kV; stobie pole |  | 0
| Pole REFURBISHED; STOBIE Pole |  | 4293851.6394 | 2818
| Pole Mounted ;> = 22 kV & < = 33 kV ; < = 60kVA |  | 209665.1607 | 13 | 8
| Pole Mounted ;> = 22 kV & < = 33 kV ; > 60 KVA AND < = 600 KVA |  | 122948.4833 | 5 | 4
| Kiosk Mounted; > = 22 kV & < = 33 kV ; |  | 0
| Recloser ;SWITCHGEAR |  | 2255629.9591 | 56 | 47
| Sectionalizer ;SWITCHGEAR |  | 7862.2459 | 0 | 3
| >= 11 kV & < ≈ 22 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR |  | 4542668.3942 | 71 | 3
| > 22 kV & < ≈ 33 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR |  | 0
| OTHER - Non Category Substation asset replacement/refurbishment |  | 5296776.5672 | 68 | 3
| Pipework Bus Substation Replacements |  | 1974801.3118 | 1
| ˂ = 11 kV ; Circuit Breaker REFURBISHED |  | 1104727.3063 | 69
| > 22 kV & < = 33 kV ; Circuit Breaker REFURBISHED |  | 103553.4869 | 2
| > 33 kV & < = 66 kV ; Circuit Breaker REFURBISHED |  | 320174.1219 | 5
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase REFURBISHED |  | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA REFURBISHED |  | 923883.4279 | 6
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA REFURBISHED |  | 1350295.1354 | 5
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA REFURBISHED |  | 711788.6638 | 3
| Northfield GIS |  | 385461.6495
2.2.2 - SELECTED ASSET CHARACTERISTICS
|  |  | ASSET VOLUMES CURRENTLY IN COMMISSION | ASSET REPLACEMENTS (0's)
ASSET GROUP | METRIC | UNITS | 2018-19 | 2018-19
TOTAL POLES BY: FEEDER TYPE | Total CBD poles | Number | 250 | 9
| Total urban poles | Number | 202457 | 1180
| Total rural long poles | Number | 343638 | 664
| Total rural short poles | Number | 100287 | 517
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Conductors CBD | KM | 60.0631 | 0.2
| Conductors urban | KM | 54941.8505 | 31.69
| Conductors rural long | KM | 87973.5714 | 44.744
| Conductors rural short | KM | 31256.5144 | 20.03
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE | OH conductor LV ABC | KM | 8143.8068
| OH conductor steel | KM | 41610.6116 | 9.86
| OH conductor ACSR | KM | 38922.1035 | 17.5
| OH conductor AAAC | KM | 6228.6567 | 32.244
| OH conductor AAC | KM | 33953.7443 | 21.62
| OH conductor HDBC | KM | 45373.0765 | 15.44
| Other | KM
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE | Cable CBD | KM | 275.4018 | 0.25
| Cable urban | KM | 11037.8084 | 6.439
| Cable rural long | KM | 3228.7382 | 0.64
| Cable rural short | KM | 3522.0515 | 0.43
TRANSFORMERS BY: TOTAL MVA | Total MVA replaced | MVA | 63.9
| Total MVA disposed of | MVA | 91.6
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(a) Augex
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.3 AUGEX PROJECT DATA
There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped. See the Instructions sheet on how to group or ungroup tables.
2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
SUBSTATION ID | SUBSTATION TYPE (drop down) | PROJECT ID | PROJECT TYPE (drop down) | PROJECT TRIGGER (drop down) | VOLTAGE (KV) | SUBSTATION RATING NORMAL CYCLIC (MVA) |  | SUBSTATION RATING N-1 EMERGENCY (MVA) |  | TRANSFORMERS |  |  | SWITCHGEAR |  | CAPACITORS |  |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | PRE | POST | PRE | POST | UNITS ADDED | MVA ADDED | EXPENDITURE ($0's) | UNITS ADDED | EXPENDITURE ($0's) | MVAR ADDED | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
|  | Non material projects - [actual] | [21 empty] | 21764472.1917
AUG232_1 | AUG232_2 | AUG232_3 | AUG232_4 | AUG232_5 | AUG232_6 | ED_AUG232_00001 | ED_AUG232_00002 | ED_AUG232_00003 | ED_AUG232_00004 | ED_AUG232_00005 | ED_AUG232_00006 | ED_AUG232_00007 | ED_AUG232_00008 | ED_AUG232_00009 | ED_AUG232_00010 | ED_AUG232_00011 | ED_AUG232_00012 | ED_AUG232_00013 | ED_AUG232_00014 | ED_AUG232_00015 | ED_AUG232_00016 | ED_AUG232_00017 | ED_AUG232_00018 | ED_AUG232_00019 | ED_AUG232_00020 | ED_AUG232_00021
2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE ($0's) | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
LINE ID | PROJECT ID | PROJECT TYPE | PROJECT TRIGGER |  | VOLTAGE (KV) | ROUTE LINE LENGTH ADDED |  |  |  | POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS) |  |  | OVERHEAD LINES |  |  | UNDERGROUND CABLES |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | KM ADDED |  |  |  | POLES/TOWERS ADDED | POLES/TOWERS UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE ($0's) | EXPENDITURE ($0's) | VOLUME | EXPENDITURE ($0's) | EXPENDITURE ($0's) |  |  |  | EXPENDITURE ($0's) |  |  | EXPENDITURE ($0's)
[24 empty] | 0 | [6 empty] | New line on new route - single circuit
[24 empty] | 0 | [6 empty] | New line on new route - dual circuit
[24 empty] | 0 | [6 empty] | New line on new route - other
[24 empty] | 0 | [6 empty] | Line rebuild over existing route - single circuit
[24 empty] | 0 | [6 empty] | Line rebuild over existing route - dual circuit
[24 empty] | 0 | [6 empty] | Reconductor - Single circuit
[24 empty] | 0 | [6 empty] | Reconductor - Dual circuit
[24 empty] | 0 | [6 empty] | Reconductor - Other
[24 empty] | 0 | [6 empty] | Line upgrade - raising/retensoring
[24 empty] | 0 | [6 empty] | Line upgrade - voltage upgrade
[24 empty] | 0 | [6 empty] | Line upgrade - capacity
[24 empty] | 0 | [6 empty] | String spare circuit
[24 empty] | 0 | [6 empty] | Other
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| Non material projects - [actual] | [22 empty] | 6316440.6285
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.3(b) Augex
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.3 AUGEX DATA
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS.
DESCRIPTOR METRICS
PROJECT TYPE |  | UNITS ADDED (0's) | UNITS UPGRADED (0's)
| UNITS | 2018-19 | 2018-19
HV Feeder Augmentations - Overhead Lines | Circuit line length in km | 2.03 | 0
HV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.38 | 0
LV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.11 | 12.419
LV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.08 | 0.16
Distribution Substation Augmentations - Pole Mounted | Number | 61 | 122
Distribution Substation Augmentations - Ground Mounted | Number | 1 | 3
Distribution Substation Augmentations - Indoor | Number | 0 | 0
COST METRICS
TOTAL DIRECT EXPENDITURE - Project Type |  | EXPENDITURE ($0's)
2018-19
HV Feeder Augmentations - Overhead Lines |  | 0
HV Feeder Augmentations - Underground Cables |  | 0
HV Feeder Non-Material Projects |  | 33564012.8567
LV Feeder Augmentations - Overhead Lines |  | 1305799.4782
LV Feeder Augmentations - Underground Cables |  | 0
LV Feeder Non-Material Projects |  | 2369692.6623
Distribution Substation Augmentations - Pole Mounted |  | 2464450.4156
Distribution Substation Augmentations - Ground Mounted |  | 183617.8982
Distribution Substation Augmentations - Indoor |  | 0
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
AUGMENTATION CAPEX (As incurred) |  | EXPENDITURE ($0's)
2018-19
Subtransmission Substations, Switching Stations, Zone Substations |  | 23394107.3109
Subtransmission Lines |  | 16975486.2277
HV Feeders |  | 33564012.8567
HV Feeders - Land Purchases and Easements |  | 0
Distribution Substations |  | 2648068.3137
Distribution Substations - Land Purchases And Easements |  | 0
LV Feeders |  | 3675492.1405
LV Feeders - Land Purchases And Easements |  | 0
Other Assets |  | 248989.3565
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.5 Connections
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.5 CONNECTIONS
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.5.1 - DESCRIPTOR METRICS
<<<GROUP-ROW>>>
VOLUMES AND EXPENDITURE
CONNECTION SUBCATEGORY | DESCRIPTOR METRIC | UNITS | 2018-19
RESIDENTIAL | Underground connections | 0's | 8587
| Overhead connections | 0's | 227
| Distribution substation installed | MVA added | 3.211
| Distribution substations installed | 0's | 66
| Distribution substation installed | total spend $0s | 1418679.103
| Augmentation HV | net circuit km added | 2.105
| Augmentation HV | total spend $0s | 329395.0674
| Augmentation LV | net circuit km added | 2.462
| Augmentation LV | total spend $0s | 442858.9414
| Mean days to connect residential customer with LV single phase connection | 0's | 11
| Volume of GSL breaches for residential customers | 0's | 229
| Volume of customer complaints relating to connection services | 0's | 120
| GSL payments | $0s | 64035.8287
COMMERCIAL/INDUSTRIAL | Underground connections | 0's | 815
| Overhead connections | 0's | 297
| Distribution substation installed | MVA added | 110.096
| Distribution substations installed | 0's | 206
| Distribution substation installed | total spend $0s | 11535167.2168
| Augmentation HV | net circuit km added | 28.699
| Augmentation HV | total spend $0s | 5631086.912
| Augmentation LV | net circuit km added | 4.156
| Augmentation LV | total spend $0s | 1467056.5556
SUBDIVISION | Underground connections | 0's | 275
| Overhead connections | 0's | 218
| Distribution substation installed | MVA added | 26.642
| Distribution substations installed | 0's | 79
| Distribution substation installed | total spend $0s | 4031326.6458
| Augmentation HV | net circuit km added | 13.858
| Augmentation HV | total spend $0s | 2540362.6044
| Augmentation LV | net circuit km added | 23.835
| Augmentation LV | total spend $0s | 6819423.7408
| Cost per lot ($) | $0s | 1417.6606
EMBEDDED GENERATION | Underground connections | 0's | 219.1412
| Overhead connections | 0's | 79.8588
| Distribution substation installed | MVA added | 7.1
| Distribution substations installed | 0's | 11
| Distribution substation installed | total spend $0s | 631739.8308
| Augmentation HV | net circuit km added | 2.054
| Augmentation HV | total spend $0s | 403028.2729
| Augmentation LV | net circuit km added | 0.025
| Augmentation LV | total spend $0s | 8824.9447
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  | EXPENDITURE ($0's) | VOLUMES (0's)
CONNECTION SUBCATEGORY | CONNECTION CLASSIFICATION | 2018-19 | 2018-19
RESIDENTIAL | Simple connection LV | 13657928.8133 | 8598
| Complex connection LV | 3897060.5998 | 216
| Complex connection HV | 0 | 0
COMMERCIAL/INDUSTRIAL | Simple connection LV | 1052779.2657 | 664
| Complex connection HV (customer connected at LV, minor HV works) | 23685716.1779 | 387
| Complex connection HV (customer connected at LV, upstream asset works) | 14197044.1998 | 61
| Complex connection HV (customer connected at HV) | 3912500.1123 | 3
Complex connection sub-transmission
SUBDIVISION | Complex connection LV | 1861968.205 | 278
| Complex connection HV (no upstream asset works) | 3597503.608 | 143
| Complex connection HV (with upstream asset works) | 3377036.2481 | 72
EMBEDDED GENERATION | Simple connection LV | 6060.5685 | 0
| Complex connection HV (small capacity) | 1403814.795 | 254
| Complex connection HV (large capacity) | 3687055.8858 | 45
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.6 Non-network
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.6 NON NETWORK EXPENDITURE
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.6.1 - NON-NETWORK EXPENDITURE
EXPENDITURE ($0's)
SERVICE SUBCATEGORY | ASSET CATEGORY |  |  | 2018-19
OPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 1606535
| Recurrent expenditure |  |  | 17663846
| Non-recurrent expenditure |  |  | 819791
MOTOR VEHICLES | Car |  |  | 318486.6934
| Light commercial vehicle |  |  | 4249333.5823
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 5817909.446
| Heavy commercial vehicle |  |  | 1176068.349
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 4159849
OTHER | Other expenditure |  |  | 5074956.5026
OTHER - DNSP nominated | TEC Vehicles |  |  | 488580.4556
| Cranes |  |  | 985979.157
| Trailers |  |  | 692457.9772
| Other Commercial Vehicles |  |  | 170276.9127
| Network Telephony |  |  | 2737662
CAPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 5221291
| Recurrent expenditure |  |  | 28232521
| Non-recurrent expenditure |  |  | 31651767
MOTOR VEHICLES | Car |  |  | 1059168.36
| Light commercial vehicle |  |  | 6755447.73
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 5064374.5
| Heavy commercial vehicle |  |  | 4114777.61
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 9097987
OTHER | Other expenditure |  |  | 21604293.66
OTHER - DNSP nominated | TEC Vehicles |  |  | 1528268.3
| Cranes |  |  | 443791.54
| Trailers |  |  | 725358.54
| Other Commercial Vehicles |  |  | 954351.28
| ADMS |  |  | 4908363
| OMS |  |  | 916653
| V&V rollout |  |  | 1763015
| Low Voltage Model |  |  | 1431352
| Other Network Strategic |  |  | 4691013
| Non-Network Telecommuniations |  |  | 553684
| Non-Network Plant and Tools |  |  | 3688444
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
VOLUMES (0's)
NON-NETWORK CATEGORY | DESCRIPTOR METRIC |  |  | 2018-19
IT & COMMUNICATIONS | Employee numbers |  |  | 1731.8583
| User numbers |  |  | 2557
| Number of devices |  |  | 6046
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
VOLUMES / %
NON-NETWORK CATEGORY | ASSET CATEGORY | DESCRIPTOR METRIC | UNITS | 2018-19
MOTOR VEHICLES | CAR | Average kilometres travelled | 0's | 10675.642
|  | Number purchased | 0's | 3
|  | Number leased | 0's | 1
|  | Number in fleet | 0's | 67
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 94.22%
| LIGHT COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 17893.926
|  | Number purchased | 0's | 100
|  | Number leased | 0's | 34
|  | Number in fleet | 0's | 418
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 90.71%
| ELEVATED WORK PLATFORM (LCV) | Average kilometres travelled | 0's | 0
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 0
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 0%
| ELEVATED WORK PLATFORM (HCV) | Average kilometres travelled | 0's | 12199.497
|  | Number purchased | 0's | 23
|  | Number leased | 0's | 2
|  | Number in fleet | 0's | 128
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 87.58%
| HEAVY COMMERCIAL VEHICLE | Average kilometres travelled | 0's | 3015.295
|  | Number purchased | 0's | 5
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 66
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 94.43%
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.7 Vegetation management
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.7 VEGETATION MANAGEMENT
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Please enter a description for each Zone in table 2.7.1 - Urban and CBD. The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2.
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
URBAN AND CBD
2018-19
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
RURAL
2018-19
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
2.7.2 - EXPENDITURE METRICS BY ZONE
EXPENDITURE ($0's)
| ZONES | SERVICE SUBCATEGORY |  | 2018-19
| ZONE 1 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 2 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 3 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 4 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 5 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 6 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 7 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 8 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 9 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 10 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 11 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 12 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 13 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 14 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 15 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 16 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 17 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 18 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
VOLUMES (0's)
| DESCRIPTOR METRIC |  |  | 2018-19
Number of fire starts caused by vegetation grow-ins (NSP responsibility)
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) |  |  | 4
Number of fire starts caused by vegetation grow-ins (other party responsibility)
| Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility) |  |  | 5
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.8 Maintenance
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.8 MAINTENANCE
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  |  | ASSET QUANTITY (0's) |  | AVERAGE AGE OF ASSET GROUP | INSPECTION CYCLE (YEARS) | MAINTENANCE CYCLE (YEARS)
|  |  |  | AT YEAR END | INSPECTED / MAINTAINED
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2018-19 | 2018-19 | 2018-19
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 646632 | 120070 | 47.8 | 5 | 0
| Service lines | Number of customers | Number | 805563 | 0 | 27.7 | 10 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 646632 | 120070 | 47.8 | 5 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 65204 | 50070 | 52.9 | 5 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 17876 | 710 | 25 | 0 | 0
| 33 KV and above | Length (KM) | KM | 189 | 3 | 29.9 | 0.5 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 275 | 11.54 | 29.9 | 0 | 0
| Non-CBD | Length (KM) | KM | 17789 | 701 | 25 | 0 | 0
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 76049 | 14122 | 27.88 | 5 | 0
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 9750 | 1223 | 13.19 | 1 | 0
| Distribution substation - other equipment | Earth mat | Number | 0 | 0 | 0 | 0 | 0
| Distribution substation - property | Number of distribution substation properties maintained | Number | 664 | 96 | 35.5 | 0 | 0
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 742 | 747 | 32 | 0.5 | 6
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 366 | 0 | 19 | 0.5 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0 | 0 | 0 | 0
| Zone substation - other equipment | <DNSP to nominate> | Number | 352 | 371 | 6 | 0.5 | 10
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 413 | 1760 | 42 | 0.5 | 4.5
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 0 | 0 | 0 | 0 | 0
| Major roads | Number of public lights maintained | Number | 0 | 0 | 0 | 0 | 0
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 380 | 0 | 10 | 0 | 0
Protection systems maintenance | Protection systems | Number of systems | Number | 6322 | 1586 | 33 | 0.5 | 4.5
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | <DNSP to nominate> | Number | 0 | 0 | 0 | 0 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 6166 | 477 | 12 | 1.5 | 1.5
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0 | 0 | 0 | 0
Other | < DNSP to nominate > | (1) Substation asset inspection | No. of sites | 405 | 398 | 42 | 0.5 | 0
|  | (2) Zone substation equipment maintenance (switchgear) | No. of CBs and disconnectors | 5952 | 1171 | 33 | 0.5 | 4.5
|  | (3) Numbers of signages and IDs replaced | No. of sites | 76049 | 1227 | 0 | 0 | 0
|  | (4) Power Station Maintenance, Asset Records Feeder Diagram Maintenance, Compliance Auditing, Asset Location Services, Customer Service Penalties | Units not quoted as various UOM | 0 | 0 | 0 | 0 | 0
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
EXPENDITURE ($0'S)
|  |  |  | ROUTINE MAINTENANCE | NON-ROUTINE MAINTENANCE
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2018-19 | 2018-19
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 145944.3719 | 2031282.1287
| Service lines | Number of customers | Number | 0 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 6859691.2665 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 5408285.585 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 587624.6291 | 375712.6392
| 33 KV and above | Length (KM) | KM | 118323.9326 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 705948.5617 | 375712.6392
| Non-CBD | Length (KM) | KM
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 28359.1072 | 1036256.6774
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 289045.6148 | 62576.2905
| Distribution substation - other equipment | Earth mat | Number
| Distribution substation - property | Number of distribution substation properties maintained | Number |  | 80714.687
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 1278652.0791 | 1589137.0197
| Transformers - distribution | Number of distribution transformers within zone substation | Number
| Transformers - HV | Number of HV transformers | Number
| Zone substation - other equipment | <DNSP to nominate> | Number | 855314.4235 | 512651.4203
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 1139348.6867 | 921851.563
Public lighting maintenance | Minor roads | Number of public lights maintained | Number
| Major roads | Number of public lights maintained | Number
SCADA & network control maintenance | SCADA & network control | Number of systems | Number |  | 523598.295
Protection systems maintenance | Protection systems | Number of systems | Number | 692916.8111 | 152527.4201
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets | <DNSP to nominate> | Number
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 676526.44 | 3841340.31
Ground clearance - access tracks | Access tracks | Number | Number
Other | < DNSP to nominate > | (1) Substation asset inspection |  | 1077119.369 | 0
|  | (2) Zone substation equipment maintenance (switchgear) |  | 977111.4906 | 588861.7277
|  | (3) Numbers of signages and IDs replaced |  | 0 | 830418.0226
|  | (4) Power Station Maintenance, Asset Records Feeder Diagram Maintenance, Compliance Auditing, Asset Location Services, Customer Service Penalties |  | 830146.6198 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.9 Emergency Response
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.9 EMERGENCY RESPONSE
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
EXPENDITURE ($0's)
2018-19
(A) TOTAL EMERGENCY RESPONSE EXPENDITURE
Total Expenditure | 40823594.43
(B) MAJOR EVENTS O&M EXPENDITURE
(C) MAJOR EVENT DAYS O&M EXPENDITURE
2018-10-15 | 471131.7266
2018-11-02 | 547938.375
2018-11-21 | 84401.5082
2018-11-22 | 723563.1397
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10 Overheads
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.10 OVERHEADS
Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. SA Power Networks is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If SA Power Networks is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. SA Power Networks is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN. |  | Choose Response drop down selection
Worksheet 2.10A
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
Instructions Please enter a description for each expenditure category as currently reported under SA Power Networks's annual RIN.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
NETWORK OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED NETWORK OVERHEADS
Standard Control Services
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
CORPORATE OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED CORPORATE OVERHEADS
Standard Control Services
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.10(A) Overheads
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.10(A) OVERHEADS
This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options.
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
OPEX
Standard Control Services | Total | 82520278.36
Alternative Control Services | Total | 2316229.03
CAPEX
Standard Control Services | Total | 4531405.78
Alternative Control Services | Total | 0
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 433946.22
Unregulated Services | Total | 0
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE ($0's)
2018-19
OPEX
Standard Control Services | Total | 78563015.57
Alternative Control Services | Total | 800506.79
CAPEX
Standard Control Services | Total | -6271515.89
Alternative Control Services | Total | 0
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 7774953.58
Unregulated Services | Total | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.11 Labour
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.11 LABOUR
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.11.1 - COST METRICS PER ANNUM
|  | ASL (0's) | TOTAL LABOUR EXPENDITURE ($0's) | AVERAGE PRODUCTIVE WORK HOURS PER ASL (0's) | STAND-DOWN OCCURENCES PER ASL (0's)
|  | 2018-19 | 2018-19 | 2018-19 | 2018-19
INTERNAL LABOUR EXPENDITURE
CORPORATE OVERHEADS | Executive manager | 24.9214 | 10243.9183 | 1932.8662 | 0
| Senior manager | 18.917 | 3854.4781 | 1779.4753 | -0.39647
| Manager | 12.2888 | 2130.0573 | 1624.8373 | 0
| Professional | 23.3944 | 4288.3274 | 1703.5453 | 1.0095
| Semi professional | 96.7714 | 15700.3081 | 1632.4287 | 0.38144
| Support staff | 117.2007 | 16593.6265 | 1611.5208 | 0.2605
| Intern, junior staff, apprentice | 2.2177 | 190.8167 | 1588.669 | 0
NETWORK OVERHEADS | Executive manager | 14.1178 | 5531.1944 | 1946.6591 | 0
| Senior manager | 36.7482 | 8270.0824 | 1824.2136 | 0
| Manager | 67.2318 | 12945.8068 | 1707.8086 | 2.7413
| Professional | 115.7311 | 16701.3607 | 1646.1742 | 5.0083
| Semi professional | 337.693 | 54515.1546 | 1700.4537 | 6.1372
| Support staff | 185.0026 | 24929.4914 | 1709.1947 | 3.0651
| Intern, junior staff, apprentice | 6.6853 | 151.997 | 1673.1115 | 0
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 535.011 | 84032.4235 | 1889.4724 | 84.5647
| Skilled non electical worker | 18.6538 | 2289.1205 | 1770.8791 | 17.2301
| Apprentice | 65.6432 | 3992.2797 | 1663.7564 | 28.1324
| Unskilled worker | 53.6291 | 5453.3173 | 1745.2343 | 25.5139
2.11.2 - DESCRIPTOR METRICS
|  | ORDINARY TIME (0's) |  | OVERTIME (0's)
|  | PER ASL | HOURLY RATE PER ASL | PER ASL | HOURLY RATE PER ASL
|  | 2018-19 | 2018-19 | 2018-19 | 2018-19
AVERAGE PRODUCTIVE WORK HOURS PER ASL
CORPORATE OVERHEADS | Executive manager | 1932.8662 | 212.663 | 0 | 0
| Senior manager | 1773.3067 | 114.3431 | 6.1685 | 160.8514
| Manager | 1622.1072 | 106.6278 | 2.7301 | 135.9748
| Professional | 1663.0162 | 106.7454 | 40.5292 | 140.943
| Semi professional | 1615.2319 | 99.0921 | 17.1968 | 120.4596
| Support staff | 1602.0546 | 87.8953 | 9.4662 | 109.6981
| Intern, junior staff, apprentice | 1588.669 | 54.1602 | 0 | 0
NETWORK OVERHEADS | Executive manager | 1946.6591 | 201.2623 | 0 | 0
| Senior manager | 1821.4142 | 123.2596 | 2.7993 | 193.064
| Manager | 1593.6255 | 109.0195 | 114.1831 | 164.8098
| Professional | 1621.3668 | 87.3949 | 24.8073 | 121.3229
| Semi professional | 1619.8815 | 93.0575 | 80.5722 | 135.7007
| Support staff | 1656.2749 | 78.2114 | 52.9198 | 106.9989
| Intern, junior staff, apprentice | 1670.9267 | 13.9988 | 2.1849 | 17.7438
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker | 1599.6376 | 74.1575 | 289.8348 | 132.2471
| Skilled non electical worker | 1617.0114 | 66.0722 | 153.8677 | 101.9876
| Apprentice | 1554.4306 | 34.5025 | 109.3258 | 49.763
| Unskilled worker | 1648.4267 | 57.3032 | 96.8076 | 83.2656
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 2.12 Input tables
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
2.12 INPUT TABLES
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
2.12.1 - INPUT TABLES
|  | DIRECT MATERIAL EXPENDITURE | DIRECT LABOUR EXPENDITURE | CONTRACT EXPENDITURE | OTHER EXPENDITURE | RELATED PARTY CONTRACT EXPENDITURE | RELATED PARTY CONTRACT MARGIN EXPENDITURE
EXPENDITURE ($0's)
|  | 2018-19 | 2018-19 | 2018-19 | 2018-19 | 2018-19 | 2018-19
VEGETATION MANAGEMENT | ZONE 1
ZONE 2
ZONE 3
ZONE 4
ZONE 5
ZONE 6
ZONE 7
ZONE 8
ZONE 9
ZONE 10
ZONE 11
ZONE 12
ZONE 13
ZONE 14
ZONE 15
ZONE 16
ZONE 17
ZONE 18
ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 3550.3548 | 106231.885 | 29937.5707 | 4403.344
| Pole inspection and treatment | 2119.16 | 123777.005 | 6345880.242 | 1870.5803
| Overhead asset inspection | 33860.4753 | 1534168.8129 | 3612483.0298 | 8012.0433
| Network underground cable maintenance | 20512.1393 | 362454.3348 | 282421.0866 | 23380.241
| Distribution substation equipment & property maintenance | 2506.1381 | 274505.2343 | 33535.4626 | 4817.796
| Zone substation equipment maintenance | 228198.6604 | 1097099.5408 | 700435.1272 | 65623.014
| Zone substation property maintenance | 27139.4292 | 206173.8509 | 833024.2724 | 22335.067
| Public lighting maintenance | 0 | 0 | 0 | 0
| Scada & network control maintenance | 0 | 0 | 0 | 0
| Protection systems maintenance | 590.2485 | 584409.3584 | 52513.8438 | 52208.7415
| Subtransmission asset maintenance - for dnsps with dual function assets | 0 | 0 | 0 | 0
| Other | 157656.0842 | 2088870.5816 | 1141177.6277 | 103777.406
NON-ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 135942.372 | 544319.786 | 1178913.2294 | 100388.9196
| Pole inspection and treatment | 0 | 0 | 0 | 0
| Overhead asset inspection | 0 | 0 | 0 | 0
| Network underground cable maintenance | 28492.1253 | 168108.7815 | 154333.1254 | 15389.9301
| Distribution substation equipment & property maintenance | 28517.8728 | 309999.5568 | 755020.59 | 40078.8316
| Zone substation equipment maintenance | 132667.2653 | 1419420.4671 | 436606.3701 | 86533.8943
| Zone substation property maintenance | 14009.6339 | 96556.8654 | 758588.7032 | 6548.4948
| Public lighting maintenance | 0 | 0 | 0 | 0
| SCADA & network control maintenance | 10617.7265 | 193228.6339 | 282950.5599 | 19588.4048
| Protection systems maintenance | 7301.2115 | 114211.4817 | 16863.7215 | 13125.1204
| Subtransmission asset maintenance - for DNSP with dual function assets | 0 | 0 | 0 | 0
| Other | 136566.6179 | 1472303.7316 | 3299513.1948 | 151514.45
OVERHEADS | Network overheads | 2261599.6508 | 37876235.8792 | 10655791.1069 | 22122239.8392
| Corporate overheads | 6474092.9642 | 45318865.787 | 2277529.7713 | 18961207.7745
AUGMENTATION | Subtransmission substations, switching stations, zone substations | 3763692.8289 | 11750168.8586 | 6117628.401 | 1069729.3239
| Subtransmission lines | 5008937.7642 | 5130256.8116 | 5642734.3265 | 554456.3415
| HV feeders | 8503124.6003 | 11351702.1943 | 10500622.5896 | 2019253.8507
| Distribution substations | 830302.3077 | 1106499.0707 | 420626.2539 | 243000.1871
| LV feeders | 1571526.7035 | 1266884.7016 | 535141.1907 | 241328.9893
| Other assets | 61228.0857 | 106620.0756 | 605.1176 | 80467.5415
CONNECTIONS | Simple and complex customer connections | 20843314.5421 | 42447426.2607 | 16027786.862 | 2390576.8952
EMERGENCY RESPONSE | Major storms | 1718377.8292 | 22402562.3722 | 13007310.2822 | 2996747.4906
Major event days
PUBLIC LIGHTING | All public lighting services
METERING | All metering services | 25557.8541 | 293269.3605 | 3456765.4069 | 31393.0327
FEE-BASED SERVICES | All fee-based services
QUOTED SERVICES | All quoted services
REPLACEMENT | Poles | 3447721.1042 | 6910231.7869 | 13208299.1504 | 1418102.0611
| Pole top structures | 4574041.6511 | 12853516.8899 | 13620408.7848 | 2333127.8418
| Overhead conductors | 571307.955 | 2676718.0259 | 709106.7341 | 474264.4274
| Underground cables | 500046.1321 | 2786593.4373 | 7113840.9 | 367125.9066
| Service lines | 457075.849 | 6132306.346 | 3582733.8466 | 1135387.6919
| Transformers | 7085153.3217 | 4999220.0843 | 2822283.8995 | 529360.9739
| Switchgear | 5801683.5868 | 8538041.4882 | 4979467.2167 | 800943.338
Public lighting
| SCADA network control and protection systems | 2326174.6761 | 4904721.1964 | 3906894.4299 | 241397.48
| Other | 2761566.6222 | 3706305.3179 | 1927229.7898 | 90069.0046
NON-NETWORK EXPENDITURE | IT and communications | 17812488 | 17904520 | 4333487.1582 | 42851533
| Motor vehicles | 24446775 | 3872996 | 444906 | 5779955
| Buildings and property | 664506 | 1334830 | 1220678.02 | 8516723
| Other | 2131344 | 4248651 | 5532351 | 8777842
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.1 Public lighting
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
4.1 PUBLIC LIGHTING
There are THREE tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.1.1 - DESCRIPTOR METRICS OVER YEAR
VOLUME (0's)
| LIGHT TYPE |  | 2018-19
POPULATION OF LIGHTS
4.1.2 - DESCRIPTOR METRICS ANNUALLY
VOLUMES & EXPENDITURE
SERVICE/SERVICE QUALITY | DESCRIPTOR METRIC | UNITS | 2018-19
LIGHT INSTALLATION | Major road light installation | 0's
| Minor road light installation | 0's
| Number of poles installed | 0's
| Total cost | $0s
LIGHT REPLACEMENT | Major road light replacement | 0's
| Minor road light replacement | 0's
| Number of poles replaced | 0's
| Total cost | $0s
LIGHT MAINTENANCE | Major road light maintenance | 0's
| Minor road light maintenance | 0's
| Number of poles installed | 0's
| Total cost | $0s
QUALITY OF SUPPLY | Mean days to rectify/replace public lighting assets | days
| GSO breaches | 0's
| GSL payments | $0s
| Customer complaints | 0's
4.1.3 - COST METRICS
AVERAGE UNIT COST ($)
ACTIVITY TYPE | LIGHT TYPE |  | 2018-19
LIGHT INSTALLATION
LIGHT REPLACEMENT
LIGHT MAINTENANCE
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.2 Metering
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
4.2 METERING
There are TWO tables on this worksheet. Each has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup tables.
4.2.1 - METERING DESCRIPTOR METRIC
VOLUMES (0's)
Asset Category | Asset Subcategory | 2018-19
Meter Type 4 | Single phase meter population | 0
| Multi phase meter population | 178
| Current transformer connected meter population | 174
| Direct connect meter population | 4
Meter Type 5 | Single phase meter population | 349
| Multi phase meter population | 8539
| Current transformer connected meter population | 4431
| Direct connect meter population | 4457
Meter Type 6 | Single phase meter population | 774027
| Multi phase meter population | 169592
| Current transformer connected meter population | 105
| Direct connect meter population | 943514
4.2.2 - COST METRICS
|  | VOLUMES (0's) | EXPENDITURE ($0's)
Service Subcategory | Meter Type | 2018-19 | 2018-19
Meter purchase | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter testing | Meter Type 4 | 11 | 18126.0651
| Meter Type 5 | 332 | 221647.913
| Meter Type 6 | 3267 | 871916.8365
Meter investigation | Meter Type 4 | 25 | 119217.1155
| Meter Type 5 | 67 | 14658.2596
| Meter Type 6 | 3498 | 358252.4497
Scheduled meter reading | Meter Type 4
Meter Type 5
Meter Type 6
Special meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
New meter installation | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter replacement | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter maintenance | Meter Type 4 | 1269 | 189821.2782
| Meter Type 5 | 223 | 67443.2765
| Meter Type 6 | 0 | 0
Remote meter reading | Meter Type 4 |  | 0
Remote meter re-configuration | Meter Type 4 | 0 | 0
Other metering | Meter Type 4 |  | 0
| Meter Type 5 |  | 0
| Meter Type 6 |  | 0
| Meter Type 7 |  | 0
IT infrastructure capex | Meter Type 4 |  | 0
IT infrastructure opex | Meter Type 4 |  | 0
Communications infrastructure capex | Meter Type 4 |  | 0
Communications infrastructure opex | Meter Type 4 |  | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.3 Fee-based services
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
4.3 ANCILLARY SERVICES - FEE BASED SERVICES
4.3.1 - COST METRICS FOR FEE-BASED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2018-19 |  | 2018-19
Common Fee-Based Services | Energisation |  | ED_FEE431_00001
| De-energisation |  | ED_FEE431_00002
| Re-energisation |  | ED_FEE431_00003
Miscellaneous Fee-Based Services | < Enter description for service > |  | ED_FEE431_00004
ED_FEE431_00005
ED_FEE431_00006
ED_FEE431_00007
ED_FEE431_00008
ED_FEE431_00009
ED_FEE431_00010
ED_FEE431_00011
ED_FEE431_00012
ED_FEE431_00013
ED_FEE431_00014
ED_FEE431_00015
ED_FEE431_00016
ED_FEE431_00017
ED_FEE431_00018
ED_FEE431_00019
ED_FEE431_00020
ED_FEE431_00021
ED_FEE431_00022
ED_FEE431_00023
ED_FEE431_00024
ED_FEE431_00025
ED_FEE431_00026
ED_FEE431_00027
ED_FEE431_00028
ED_FEE431_00029
ED_FEE431_00030
ED_FEE431_00031
ED_FEE431_00032
ED_FEE431_00033
ED_FEE431_00034
ED_FEE431_00035
ED_FEE431_00036
ED_FEE431_00037
ED_FEE431_00038
ED_FEE431_00039
ED_FEE431_00040
ED_FEE431_00041
ED_FEE431_00042
ED_FEE431_00043
ED_FEE431_00044
ED_FEE431_00045
ED_FEE431_00046
ED_FEE431_00047
ED_FEE431_00048
ED_FEE431_00049
ED_FEE431_00050
ED_FEE431_00051
ED_FEE431_00052
ED_FEE431_00053
ED_FEE431_00054
ED_FEE431_00055
ED_FEE431_00056
ED_FEE431_00057
ED_FEE431_00058
ED_FEE431_00059
ED_FEE431_00060
ED_FEE431_00061
ED_FEE431_00062
ED_FEE431_00063
ED_FEE431_00064
ED_FEE431_00065
ED_FEE431_00066
ED_FEE431_00067
ED_FEE431_00068
ED_FEE431_00069
ED_FEE431_00070
ED_FEE431_00071
ED_FEE431_00072
ED_FEE431_00073
ED_FEE431_00074
ED_FEE431_00075
ED_FEE431_00076
ED_FEE431_00077
ED_FEE431_00078
ED_FEE431_00079
ED_FEE431_00080
ED_FEE431_00081
ED_FEE431_00082
ED_FEE431_00083
ED_FEE431_00084
ED_FEE431_00085
ED_FEE431_00086
ED_FEE431_00087
ED_FEE431_00088
ED_FEE431_00089
ED_FEE431_00090
ED_FEE431_00091
ED_FEE431_00092
ED_FEE431_00093
ED_FEE431_00094
ED_FEE431_00095
ED_FEE431_00096
ED_FEE431_00097
ED_FEE431_00098
ED_FEE431_00099
ED_FEE431_00100
ED_FEE431_00101
ED_FEE431_00102
ED_FEE431_00103
ED_FEE431_00104
ED_FEE431_00105
ED_FEE431_00106
ED_FEE431_00107
ED_FEE431_00108
ED_FEE431_00109
ED_FEE431_00110
ED_FEE431_00111
ED_FEE431_00112
ED_FEE431_00113
ED_FEE431_00114
ED_FEE431_00115
ED_FEE431_00116
ED_FEE431_00117
ED_FEE431_00118
ED_FEE431_00119
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00164
ED_FEE431_00165
ED_FEE431_00166
ED_FEE431_00167
ED_FEE431_00168
ED_FEE431_00169
ED_FEE431_00170
ED_FEE431_00171
ED_FEE431_00172
ED_FEE431_00173
ED_FEE431_00174
ED_FEE431_00175
ED_FEE431_00176
ED_FEE431_00177
ED_FEE431_00178
ED_FEE431_00179
ED_FEE431_00180
ED_FEE431_00181
ED_FEE431_00182
ED_FEE431_00183
ED_FEE431_00184
ED_FEE431_00185
ED_FEE431_00186
ED_FEE431_00187
ED_FEE431_00188
ED_FEE431_00189
ED_FEE431_00190
ED_FEE431_00191
ED_FEE431_00192
ED_FEE431_00193
ED_FEE431_00194
ED_FEE431_00195
ED_FEE431_00196
ED_FEE431_00197
ED_FEE431_00198
ED_FEE431_00199
ED_FEE431_00200
ED_FEE431_00201
ED_FEE431_00202
ED_FEE431_00203
ED_FEE431_00204
ED_FEE431_00205
ED_FEE431_00206
ED_FEE431_00207
ED_FEE431_00208
ED_FEE431_00209
ED_FEE431_00210
ED_FEE431_00211
ED_FEE431_00212
ED_FEE431_00213
ED_FEE431_00214
ED_FEE431_00215
ED_FEE431_00216
ED_FEE431_00217
ED_FEE431_00218
ED_FEE431_00219
ED_FEE431_00220
ED_FEE431_00221
ED_FEE431_00222
ED_FEE431_00223
ED_FEE431_00224
ED_FEE431_00225
ED_FEE431_00226
ED_FEE431_00227
ED_FEE431_00228
ED_FEE431_00229
ED_FEE431_00230
ED_FEE431_00231
ED_FEE431_00232
ED_FEE431_00233
ED_FEE431_00234
ED_FEE431_00235
ED_FEE431_00236
ED_FEE431_00237
ED_FEE431_00238
ED_FEE431_00239
ED_FEE431_00240
ED_FEE431_00241
ED_FEE431_00242
ED_FEE431_00243
ED_FEE431_00244
ED_FEE431_00245
ED_FEE431_00246
ED_FEE431_00247
ED_FEE431_00248
ED_FEE431_00249
ED_FEE431_00250
ED_FEE431_00251
ED_FEE431_00252
ED_FEE431_00253
ED_FEE431_00254
ED_FEE431_00255
ED_FEE431_00256
ED_FEE431_00257
ED_FEE431_00258
ED_FEE431_00259
ED_FEE431_00260
ED_FEE431_00261
ED_FEE431_00262
ED_FEE431_00263
ED_FEE431_00264
ED_FEE431_00265
ED_FEE431_00266
ED_FEE431_00267
ED_FEE431_00268
ED_FEE431_00269
ED_FEE431_00270
ED_FEE431_00271
ED_FEE431_00272
ED_FEE431_00273
ED_FEE431_00274
ED_FEE431_00275
ED_FEE431_00276
ED_FEE431_00277
ED_FEE431_00278
ED_FEE431_00279
ED_FEE431_00280
ED_FEE431_00281
ED_FEE431_00282
ED_FEE431_00283
ED_FEE431_00284
ED_FEE431_00285
ED_FEE431_00286
ED_FEE431_00287
ED_FEE431_00288
ED_FEE431_00289
ED_FEE431_00290
ED_FEE431_00291
ED_FEE431_00292
ED_FEE431_00293
ED_FEE431_00294
ED_FEE431_00295
ED_FEE431_00296
ED_FEE431_00297
ED_FEE431_00298
ED_FEE431_00299
ED_FEE431_00300
ED_FEE431_00301
ED_FEE431_00302
ED_FEE431_00303
ED_FEE431_00304
ED_FEE431_00305
ED_FEE431_00306
ED_FEE431_00307
ED_FEE431_00308
ED_FEE431_00309
ED_FEE431_00310
ED_FEE431_00311
ED_FEE431_00312
ED_FEE431_00313
ED_FEE431_00314
ED_FEE431_00315
ED_FEE431_00316
ED_FEE431_00317
ED_FEE431_00318
ED_FEE431_00319
ED_FEE431_00320
ED_FEE431_00321
ED_FEE431_00322
ED_FEE431_00323
ED_FEE431_00324
ED_FEE431_00325
ED_FEE431_00326
ED_FEE431_00327
ED_FEE431_00328
ED_FEE431_00329
ED_FEE431_00330
ED_FEE431_00331
ED_FEE431_00332
ED_FEE431_00333
ED_FEE431_00334
ED_FEE431_00335
ED_FEE431_00336
ED_FEE431_00337
ED_FEE431_00338
ED_FEE431_00339
ED_FEE431_00340
ED_FEE431_00341
ED_FEE431_00342
ED_FEE431_00343
ED_FEE431_00344
ED_FEE431_00345
ED_FEE431_00346
ED_FEE431_00347
ED_FEE431_00348
ED_FEE431_00349
ED_FEE431_00350
ED_FEE431_00351
ED_FEE431_00352
ED_FEE431_00353
ED_FEE431_00354
ED_FEE431_00355
ED_FEE431_00356
ED_FEE431_00357
ED_FEE431_00358
ED_FEE431_00359
ED_FEE431_00360
ED_FEE431_00361
ED_FEE431_00362
ED_FEE431_00363
ED_FEE431_00364
ED_FEE431_00365
ED_FEE431_00366
ED_FEE431_00367
ED_FEE431_00368
ED_FEE431_00369
ED_FEE431_00370
ED_FEE431_00371
ED_FEE431_00372
ED_FEE431_00373
ED_FEE431_00374
ED_FEE431_00375
ED_FEE431_00376
ED_FEE431_00377
ED_FEE431_00378
ED_FEE431_00379
ED_FEE431_00380
ED_FEE431_00381
ED_FEE431_00382
ED_FEE431_00383
ED_FEE431_00384
ED_FEE431_00385
ED_FEE431_00386
ED_FEE431_00387
ED_FEE431_00388
ED_FEE431_00389
ED_FEE431_00390
ED_FEE431_00391
ED_FEE431_00392
ED_FEE431_00393
ED_FEE431_00394
ED_FEE431_00395
ED_FEE431_00396
ED_FEE431_00397
ED_FEE431_00398
ED_FEE431_00399
ED_FEE431_00400
ED_FEE431_00401
ED_FEE431_00402
ED_FEE431_00403
ED_FEE431_00404
ED_FEE431_00405
ED_FEE431_00406
ED_FEE431_00407
ED_FEE431_00408
ED_FEE431_00409
ED_FEE431_00410
ED_FEE431_00411
ED_FEE431_00412
ED_FEE431_00413
ED_FEE431_00414
ED_FEE431_00415
ED_FEE431_00416
ED_FEE431_00417
ED_FEE431_00418
ED_FEE431_00419
ED_FEE431_00420
ED_FEE431_00421
ED_FEE431_00422
ED_FEE431_00423
ED_FEE431_00424
ED_FEE431_00425
ED_FEE431_00426
ED_FEE431_00427
ED_FEE431_00428
ED_FEE431_00429
ED_FEE431_00430
ED_FEE431_00431
ED_FEE431_00432
ED_FEE431_00433
ED_FEE431_00434
ED_FEE431_00435
ED_FEE431_00436
ED_FEE431_00437
ED_FEE431_00438
ED_FEE431_00439
ED_FEE431_00440
ED_FEE431_00441
ED_FEE431_00442
ED_FEE431_00443
ED_FEE431_00444
ED_FEE431_00445
ED_FEE431_00446
ED_FEE431_00447
ED_FEE431_00448
ED_FEE431_00449
ED_FEE431_00450
ED_FEE431_00451
ED_FEE431_00452
ED_FEE431_00453
ED_FEE431_00454
ED_FEE431_00455
ED_FEE431_00456
ED_FEE431_00457
ED_FEE431_00458
ED_FEE431_00459
ED_FEE431_00460
ED_FEE431_00461
ED_FEE431_00462
ED_FEE431_00463
ED_FEE431_00464
ED_FEE431_00465
ED_FEE431_00466
ED_FEE431_00467
ED_FEE431_00468
ED_FEE431_00469
ED_FEE431_00470
ED_FEE431_00471
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 4.4 Quoted services
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
4.4 ANCILLARY SERVICES - QUOTED SERVICES
4.4.1 - COST METRICS FOR QUOTED SERVICES
|  | EXPENDITURE ($0's) |  | VOLUMES (0's)
SERVICE | SERVICE SUBCATEGORY | 2018-19 |  | 2018-19
Quoted Services | < Enter description for service subcategory > |  | ED_QUO441_00001
ED_QUO441_00002
ED_QUO441_00003
ED_QUO441_00004
ED_QUO441_00005
ED_QUO441_00006
ED_QUO441_00007
ED_QUO441_00008
ED_QUO441_00009
ED_QUO441_00010
ED_QUO441_00011
ED_QUO441_00012
ED_QUO441_00013
ED_QUO441_00014
ED_QUO441_00015
ED_QUO441_00016
ED_QUO441_00017
ED_QUO441_00018
ED_QUO441_00019
ED_QUO441_00020
ED_QUO441_00021
ED_QUO441_00022
ED_QUO441_00023
ED_QUO441_00024
ED_QUO441_00025
ED_QUO441_00026
ED_QUO441_00027
ED_QUO441_00028
ED_QUO441_00029
ED_QUO441_00030
ED_QUO441_00031
ED_QUO441_00032
ED_QUO441_00033
ED_QUO441_00034
ED_QUO441_00035
ED_QUO441_00036
ED_QUO441_00037
ED_QUO441_00038
ED_QUO441_00039
ED_QUO441_00040
ED_QUO441_00041
ED_QUO441_00042
ED_QUO441_00043
ED_QUO441_00044
ED_QUO441_00045
ED_QUO441_00046
ED_QUO441_00047
ED_QUO441_00048
ED_QUO441_00049
ED_QUO441_00050
ED_QUO441_00051
ED_QUO441_00052
ED_QUO441_00053
ED_QUO441_00054
ED_QUO441_00055
ED_QUO441_00056
ED_QUO441_00057
ED_QUO441_00058
ED_QUO441_00059
ED_QUO441_00060
ED_QUO441_00061
ED_QUO441_00062
ED_QUO441_00063
ED_QUO441_00064
ED_QUO441_00065
ED_QUO441_00066
ED_QUO441_00067
ED_QUO441_00068
ED_QUO441_00069
ED_QUO441_00070
ED_QUO441_00071
ED_QUO441_00072
ED_QUO441_00073
ED_QUO441_00074
ED_QUO441_00075
ED_QUO441_00076
ED_QUO441_00077
ED_QUO441_00078
ED_QUO441_00079
ED_QUO441_00080
ED_QUO441_00081
ED_QUO441_00082
ED_QUO441_00083
ED_QUO441_00084
ED_QUO441_00085
ED_QUO441_00086
ED_QUO441_00087
ED_QUO441_00088
ED_QUO441_00089
ED_QUO441_00090
ED_QUO441_00091
ED_QUO441_00092
ED_QUO441_00093
ED_QUO441_00094
ED_QUO441_00095
ED_QUO441_00096
ED_QUO441_00097
ED_QUO441_00098
ED_QUO441_00099
ED_QUO441_00100
ED_QUO441_00101
ED_QUO441_00102
ED_QUO441_00103
ED_QUO441_00104
ED_QUO441_00105
ED_QUO441_00106
ED_QUO441_00107
ED_QUO441_00108
ED_QUO441_00109
ED_QUO441_00110
ED_QUO441_00111
ED_QUO441_00112
ED_QUO441_00113
ED_QUO441_00114
ED_QUO441_00115
ED_QUO441_00116
ED_QUO441_00117
ED_QUO441_00118
ED_QUO441_00119
ED_QUO441_00120
ED_QUO441_00121
ED_QUO441_00122
ED_QUO441_00123
ED_QUO441_00124
ED_QUO441_00125
ED_QUO441_00126
ED_QUO441_00127
ED_QUO441_00128
ED_QUO441_00129
ED_QUO441_00130
ED_QUO441_00131
ED_QUO441_00132
ED_QUO441_00133
ED_QUO441_00134
ED_QUO441_00135
ED_QUO441_00136
ED_QUO441_00137
ED_QUO441_00138
ED_QUO441_00139
ED_QUO441_00140
ED_QUO441_00141
ED_QUO441_00142
ED_QUO441_00143
ED_QUO441_00144
ED_QUO441_00145
ED_QUO441_00146
ED_QUO441_00147
ED_QUO441_00148
ED_QUO441_00149
ED_QUO441_00150
ED_QUO441_00151
ED_QUO441_00152
ED_QUO441_00153
ED_QUO441_00154
ED_QUO441_00155
ED_QUO441_00156
ED_QUO441_00157
ED_QUO441_00158
ED_QUO441_00159
ED_QUO441_00160
ED_QUO441_00161
ED_QUO441_00162
ED_QUO441_00163
ED_QUO441_00164
ED_QUO441_00165
ED_QUO441_00166
ED_QUO441_00167
ED_QUO441_00168
ED_QUO441_00169
ED_QUO441_00170
ED_QUO441_00171
ED_QUO441_00172
ED_QUO441_00173
ED_QUO441_00174
ED_QUO441_00175
ED_QUO441_00176
ED_QUO441_00177
ED_QUO441_00178
ED_QUO441_00179
ED_QUO441_00180
ED_QUO441_00181
ED_QUO441_00182
ED_QUO441_00183
ED_QUO441_00184
ED_QUO441_00185
ED_QUO441_00186
ED_QUO441_00187
ED_QUO441_00188
ED_QUO441_00189
ED_QUO441_00190
ED_QUO441_00191
ED_QUO441_00192
ED_QUO441_00193
ED_QUO441_00194
ED_QUO441_00195
ED_QUO441_00196
ED_QUO441_00197
ED_QUO441_00198
ED_QUO441_00199
ED_QUO441_00200
ED_QUO441_00201
ED_QUO441_00202
ED_QUO441_00203
ED_QUO441_00204
ED_QUO441_00205
ED_QUO441_00206
ED_QUO441_00207
ED_QUO441_00208
ED_QUO441_00209
ED_QUO441_00210
ED_QUO441_00211
ED_QUO441_00212
ED_QUO441_00213
ED_QUO441_00214
ED_QUO441_00215
ED_QUO441_00216
ED_QUO441_00217
ED_QUO441_00218
ED_QUO441_00219
ED_QUO441_00220
ED_QUO441_00221
ED_QUO441_00222
ED_QUO441_00223
ED_QUO441_00224
ED_QUO441_00225
ED_QUO441_00226
ED_QUO441_00227
ED_QUO441_00228
ED_QUO441_00229
ED_QUO441_00230
ED_QUO441_00231
ED_QUO441_00232
ED_QUO441_00233
ED_QUO441_00234
ED_QUO441_00235
ED_QUO441_00236
ED_QUO441_00237
ED_QUO441_00238
ED_QUO441_00239
ED_QUO441_00240
ED_QUO441_00241
ED_QUO441_00242
ED_QUO441_00243
ED_QUO441_00244
ED_QUO441_00245
ED_QUO441_00246
ED_QUO441_00247
ED_QUO441_00248
ED_QUO441_00249
ED_QUO441_00250
ED_QUO441_00251
ED_QUO441_00252
ED_QUO441_00253
ED_QUO441_00254
ED_QUO441_00255
ED_QUO441_00256
ED_QUO441_00257
ED_QUO441_00258
ED_QUO441_00259
ED_QUO441_00260
ED_QUO441_00261
ED_QUO441_00262
ED_QUO441_00263
ED_QUO441_00264
ED_QUO441_00265
ED_QUO441_00266
ED_QUO441_00267
ED_QUO441_00268
ED_QUO441_00269
ED_QUO441_00270
ED_QUO441_00271
ED_QUO441_00272
ED_QUO441_00273
ED_QUO441_00274
ED_QUO441_00275
ED_QUO441_00276
ED_QUO441_00277
ED_QUO441_00278
ED_QUO441_00279
ED_QUO441_00280
ED_QUO441_00281
ED_QUO441_00282
ED_QUO441_00283
ED_QUO441_00284
ED_QUO441_00285
ED_QUO441_00286
ED_QUO441_00287
ED_QUO441_00288
ED_QUO441_00289
ED_QUO441_00290
ED_QUO441_00291
ED_QUO441_00292
ED_QUO441_00293
ED_QUO441_00294
ED_QUO441_00295
ED_QUO441_00296
ED_QUO441_00297
ED_QUO441_00298
ED_QUO441_00299
ED_QUO441_00300
ED_QUO441_00301
ED_QUO441_00302
ED_QUO441_00303
ED_QUO441_00304
ED_QUO441_00305
ED_QUO441_00306
ED_QUO441_00307
ED_QUO441_00308
ED_QUO441_00309
ED_QUO441_00310
ED_QUO441_00311
ED_QUO441_00312
ED_QUO441_00313
ED_QUO441_00314
ED_QUO441_00315
ED_QUO441_00316
ED_QUO441_00317
ED_QUO441_00318
ED_QUO441_00319
ED_QUO441_00320
ED_QUO441_00321
ED_QUO441_00322
ED_QUO441_00323
ED_QUO441_00324
ED_QUO441_00325
ED_QUO441_00326
ED_QUO441_00327
ED_QUO441_00328
ED_QUO441_00329
ED_QUO441_00330
ED_QUO441_00331
ED_QUO441_00332
ED_QUO441_00333
ED_QUO441_00334
ED_QUO441_00335
ED_QUO441_00336
ED_QUO441_00337
ED_QUO441_00338
ED_QUO441_00339
ED_QUO441_00340
ED_QUO441_00341
ED_QUO441_00342
ED_QUO441_00343
ED_QUO441_00344
ED_QUO441_00345
ED_QUO441_00346
ED_QUO441_00347
ED_QUO441_00348
ED_QUO441_00349
ED_QUO441_00350
ED_QUO441_00351
ED_QUO441_00352
ED_QUO441_00353
ED_QUO441_00354
ED_QUO441_00355
ED_QUO441_00356
ED_QUO441_00357
ED_QUO441_00358
ED_QUO441_00359
ED_QUO441_00360
ED_QUO441_00361
ED_QUO441_00362
ED_QUO441_00363
ED_QUO441_00364
ED_QUO441_00365
ED_QUO441_00366
ED_QUO441_00367
ED_QUO441_00368
ED_QUO441_00369
ED_QUO441_00370
ED_QUO441_00371
ED_QUO441_00372
ED_QUO441_00373
ED_QUO441_00374
ED_QUO441_00375
ED_QUO441_00376
ED_QUO441_00377
ED_QUO441_00378
ED_QUO441_00379
ED_QUO441_00380
ED_QUO441_00381
ED_QUO441_00382
ED_QUO441_00383
ED_QUO441_00384
ED_QUO441_00385
ED_QUO441_00386
ED_QUO441_00387
ED_QUO441_00388
ED_QUO441_00389
ED_QUO441_00390
ED_QUO441_00391
ED_QUO441_00392
ED_QUO441_00393
ED_QUO441_00394
ED_QUO441_00395
ED_QUO441_00396
ED_QUO441_00397
ED_QUO441_00398
ED_QUO441_00399
ED_QUO441_00400
ED_QUO441_00401
ED_QUO441_00402
ED_QUO441_00403
ED_QUO441_00404
ED_QUO441_00405
ED_QUO441_00406
ED_QUO441_00407
ED_QUO441_00408
ED_QUO441_00409
ED_QUO441_00410
ED_QUO441_00411
ED_QUO441_00412
ED_QUO441_00413
ED_QUO441_00414
ED_QUO441_00415
ED_QUO441_00416
ED_QUO441_00417
ED_QUO441_00418
ED_QUO441_00419
ED_QUO441_00420
ED_QUO441_00421
ED_QUO441_00422
ED_QUO441_00423
ED_QUO441_00424
ED_QUO441_00425
ED_QUO441_00426
ED_QUO441_00427
ED_QUO441_00428
ED_QUO441_00429
ED_QUO441_00430
ED_QUO441_00431
ED_QUO441_00432
ED_QUO441_00433
ED_QUO441_00434
ED_QUO441_00435
ED_QUO441_00436
ED_QUO441_00437
ED_QUO441_00438
ED_QUO441_00439
ED_QUO441_00440
ED_QUO441_00441
ED_QUO441_00442
ED_QUO441_00443
ED_QUO441_00444
ED_QUO441_00445
ED_QUO441_00446
ED_QUO441_00447
ED_QUO441_00448
ED_QUO441_00449
ED_QUO441_00450
ED_QUO441_00451
ED_QUO441_00452
ED_QUO441_00453
ED_QUO441_00454
ED_QUO441_00455
ED_QUO441_00456
ED_QUO441_00457
ED_QUO441_00458
ED_QUO441_00459
ED_QUO441_00460
ED_QUO441_00461
ED_QUO441_00462
ED_QUO441_00463
ED_QUO441_00464
ED_QUO441_00465
ED_QUO441_00466
ED_QUO441_00467
ED_QUO441_00468
ED_QUO441_00469
ED_QUO441_00470
ED_QUO441_00471
ED_QUO441_00472
ED_QUO441_00473
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.2 Asset Age Profile
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
5.2 ASSET AGE PROFILE
There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data.
5.2.1 - ASSET AGE PROFILE
|  | ECONOMIC LIFE (YEARS) |  | INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR
ASSET GROUP | ASSET CATEGORY | MEAN | STANDARD DEVIATION | 2018-19 | 2017-18 | 2016-17 | 2015-16 | 2014-15 | 2013-14 | 2012-13 | 2011-12 | 2010-11 | 2009-10 | 2008-09 | 2007-08 | 2006-07 | 2005-06 | 2004-05 | 2003-04 | 2002-03 | 2001-02 | 2000-01 | 1999-00 | 1998-99 | 1997-98 | 1996-97 | 1995-96 | 1994-95 | 1993-94 | 1992-93 | 1991-92 | 1990-91 | 1989-90 | 1988-89 | 1987-88 | 1986-87 | 1985-86 | 1984-85 | 1983-84 | 1982-83 | 1981-82 | 1980-81 | 1979-80 | 1978-79 | 1977-78 | 1976-77 | 1975-76 | 1974-75 | 1973-74 | 1972-73 | 1971-72 | 1970-71 | 1969-70 | 1968-69 | 1967-68 | 1966-67 | 1965-66 | 1964-65 | 1963-64 | 1962-63 | 1961-62 | 1960-61 | 1959-60 | 1958-59 | 1957-58 | 1956-57 | 1955-56 | 1954-55 | 1953-54 | 1952-53 | 1951-52 | 1950-51 | 1949-50 | 1948-49 | 1947-48 | 1946-47 | 1945-46 | 1944-45 | 1943-44 | 1942-43 | 1941-42 | 1940-41 | 1939-40 | 1938-39 | 1937-38 | 1936-37 | 1935-36 | 1934-35 | 1933-34 | 1932-33 | 1931-32 | 1930-31 | 1929-30 | 1928-29 | 1927-28 | 1926-27 | 1925-26 | 1924-25 | 1923-24 | 1922-23 | 1921-22 | 1920-21 | 1919-20 | 1918-19 | 1917-18 | 1916-17 | 1915-16 | 1914-15 | 1913-14 | 1912-13 | 1911-12 | 1910-11
POLES BY: HIGHEST OPERATING VOLTAGE ; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole
˂ = 1 kV; Wood
> 1 kV & < = 11 kV; Wood
˃ 11 kV & < = 22 kV; Wood
> 22 kV & < = 66 kV; Wood
> 66 kV & < = 132 kV; Wood
> 132 kV; Wood
˂ = 1 kV; Concrete
> 1 kV & < = 11 kV; Concrete
˃ 11 kV & < = 22 kV; Concrete
> 22 kV & < = 66 kV; Concrete
> 66 kV & < = 132 kV; Concrete
> 132 kV; Concrete
˂ = 1 kV; Steel
> 1 kV & < = 11 kV; Steel
˃ 11 kV & < = 22 kV; Steel
> 22 kV & < = 66 kV; Steel
> 66 kV & < = 132 kV; Steel
> 132 kV; Steel
Other
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV | 54.9077 | 7.41 | 31.329 | 44.4218 | 21.1375 | 20.3686 | 42.9191 | 151.2584 | 205.1067 | 188.2689 | 93.9507 | 89.4432 | 96.4786 | 105.3742 | 38.1751 | 91.0369 | 59.7736 | 46.3651 | 51.7339 | 45.2754 | 67.456 | 143.2744 | 9.4739 | 90.1981 | 5.063 | 157.7934 | 88.3965 | 117.5089 | 4.155 | 362.1175 | 246.4495 | 256.1897 | 283.8418 | 155.0754 | 273.0344 | 404.6866 | 315.5376 | 424.9519 | 392.8485 | 311.8454 | 454.4356 | 563.2142 | 639.5879 | 425.4848 | 821.9294 | 938.6629 | 1181.5248 | 1329.8165 | 1486.8691 | 1127.22 | 2373.3956 | 2420.208 | 1844.4268 | 3666.1906 | 1854.8468 | 3231.7895 | 4075.993 | 4147.5251 | 3984.5852 | 3624.0606 | 4310.0402 | 3057.4466 | 2650.2318 | 3492.214 | 2340.9854 | 1702.2232 | 5020.5552 | 2321.7593 | 1188.2659 | 478.4736 | 18.0389 | 54.1691 | 10.4522 | 21.4465 | 145.6053 | 103.8632 | 127.9065 | 51.7495 | 56.3551 | 102.1224 | 97.5843 | 583.0583 | 302.3665 | 256.624 | 262.7998 | 221.9392 | 312.8995 | 85.9402 | 24.659 | 15.1048 | 0.98811 | 4.1027 | 0.11732 | 0.21656 | 0.21152 | 0 | 0.35285 | 1.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 51.172 | 7.1535 | 70.444 | 42.526 | 32.7086 | 11.1893 | 39.2306 | 114.8467 | 102.339 | 134.7883 | 164.2859 | 74.3682 | 142.1637 | 157.0144 | 41.3272 | 108.9928 | 57.2188 | 34.1774 | 60.1804 | 46.0254 | 54.3894 | 209.4042 | 4.7509 | 278.0444 | 8.3828 | 348.382 | 119.838 | 193.6234 | 22.637 | 534.6468 | 243.0073 | 364.12 | 352.6211 | 234.7186 | 323.49 | 497.999 | 390.6977 | 327.8495 | 285.0056 | 281.9461 | 529.1798 | 704.1772 | 852.7977 | 409.5403 | 1137.3557 | 983.0187 | 815.9169 | 1215.8943 | 1687.9642 | 1614.0931 | 2248.9213 | 2245.0953 | 2222.889 | 3811.783 | 1354.874 | 2332.9418 | 2304.7051 | 1805.058 | 2315.1188 | 2159.2599 | 2382.774 | 1546.8489 | 1055.7711 | 1183.09 | 1126.1637 | 1461.7045 | 3035.14 | 1073.5316 | 533.9152 | 183.5045 | 10.6662 | 67.8284 | 1.3354 | 9.4276 | 85.1319 | 26.3295 | 37.8539 | 20.9784 | 15.2268 | 27.9857 | 14.4973 | 147.4902 | 51.1312 | 61.8608 | 80.0104 | 59.6732 | 64.7238 | 28.7616 | 5.9644 | 2.9867 | 1.4867 | 2.0057 | 0 | 0 | 0.1695 | 0 | 0 | 0.4759 | 0 | 0 | 0.59073 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; SWER | 51.9359 | 7.2067 | 3.63 | 2.1926 | 5.4367 | 21.7529 | 7.1472 | 70.8215 | 3.6019 | 9.024 | 21.7241 | 35.7203 | 14.2225 | 23.5905 | 12.1495 | 26.4922 | 26.2957 | 12.5199 | 16.7405 | 9.5692 | 24.686 | 51.6026 | 0.24304 | 54.0871 | 0.71481 | 58.8187 | 61.2137 | 64.5679 | 0.81265 | 100.7426 | 61.62 | 191.1402 | 89.4645 | 120.2218 | 168.4957 | 99.9317 | 69.5858 | 69.771 | 57.2198 | 187.6579 | 135.5144 | 341.8082 | 120.5009 | 240.6623 | 412.1737 | 524.335 | 1011.0681 | 754.2204 | 862.182 | 554.3448 | 1102.843 | 1751.3748 | 1121.8589 | 2496.2462 | 771.0841 | 2233.1429 | 2025.8595 | 2010.4699 | 1709.4464 | 1716.7811 | 1461.7149 | 1072.7294 | 989.0691 | 1020.3889 | 206.0462 | 219.7313 | 212.3831 | 74.0973 | 41.5655 | 10.8125 | 1.3168 | 6.5359 | 0.34627 | 3.6575 | 4.858 | 0.29588 | 7.0614 | 0.47851 | 5.0622 | 7.7481 | 2.5609 | 7.4385 | 1.588 | 8.7932 | 2.9231 | 0.59197 | 1.3804 | 1.2913 | 0.9206 | 0 | 0 | 1.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58117
˃ 11 kV & < = 22 kV ; Single-Phase
˃ 11 kV & < = 22 kV ; Multiple-Phase
| > 22 kV & < = 66 kV | 51.1787 | 7.1539 | 0.53 | 0.81169 | 10.435 | 10.4807 | 13.605 | 39.9651 | 20.2347 | 17.4653 | 30.7498 | 26.776 | 28.1089 | 34.9548 | 32.1442 | 11.2374 | 15.7625 | 53.1987 | 16.5873 | 14.8609 | 12.7619 | 145.7164 | 1.4492 | 143.4832 | 197.3632 | 19.1411 | 14.8036 | 73.4082 | 0.19219 | 111.6687 | 72.6996 | 86.63 | 245.6039 | 86.6817 | 90.056 | 86.6227 | 115.6324 | 82.3422 | 57.0005 | 8.1695 | 132.3723 | 86.4393 | 101.689 | 543.5909 | 426.693 | 730.2269 | 255.427 | 219.8387 | 676.3628 | 128.8037 | 554.084 | 593.3591 | 362.6881 | 749.4228 | 250.0361 | 724.1639 | 1055.2083 | 789.2068 | 1109.986 | 405.3603 | 811.4876 | 506.8567 | 238.5319 | 350.2612 | 477.5671 | 276.9485 | 655.0711 | 239.6395 | 168.5549 | 96.0093 | 4.0215 | 29.8996 | 0 | 5.9889 | 15.7205 | 101.1738 | 35.4697 | 20.4849 | 73.6573 | 45.5473 | 20.9426 | 44.5462 | 22.2089 | 24.5184 | 24.7616 | 4.118 | 8.7136 | 60.1311 | 2.4321 | 0.26626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17655 | 0 | 0 | 0 | 0 | 0 | 0 | 0
> 66 kV & < = 132 kV
> 132 kV
Other
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV | 25.0712 | 5.0071 | 5.08 | 6.9136 | 0 | 5.041 | 38.0034 | 184.0337 | 189.2808 | 257.7063 | 322.2762 | 457.2984 | 493.1859 | 450.1926 | 494.6283 | 454.9874 | 501.5416 | 471.082 | 401.683 | 442.547 | 306.9803 | 235.8954 | 255.1191 | 219.6691 | 240.6409 | 195.5954 | 331.8889 | 501.1819 | 451.5707 | 327.6992 | 466.1292 | 396.8109 | 400.5094 | 271.5477 | 339.9704 | 459.8503 | 435.6477 | 277.1682 | 151.2221 | 157.006 | 126.9192 | 102.6215 | 160.3039 | 261.1827 | 277.4419 | 261.8243 | 181.3415 | 118.986 | 63.1621 | 53.1421 | 38.4488 | 387.0975 | 0.2116 | 0.92959 | 0 | 0.03919 | 0 | 0.12873 | 0 | 0 | 0.46375 | 0 | 0 | 0 | 0.3151 | 40.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 24.6013 | 4.96 | 3.088 | 3.5776 | 0 | 1.5448 | 16.6469 | 66.666 | 92.3385 | 113.4767 | 129.1121 | 157.7478 | 164.4171 | 163.9938 | 139.3206 | 128.945 | 122.1862 | 105.8971 | 114.7067 | 110.0408 | 78.0801 | 82.0043 | 80.3608 | 76.3354 | 66.1872 | 47.1981 | 104.744 | 116.8073 | 98.3118 | 89.1553 | 128.6709 | 115.7171 | 122.0236 | 91.5954 | 122.537 | 169.3436 | 136.5836 | 83.0021 | 43.3853 | 57.9625 | 34.9536 | 34.6929 | 48.0549 | 57.6404 | 86.4645 | 81.9548 | 42.2865 | 55.0075 | 19.3763 | 16.6368 | 24.5641 | 60.8156 | 0.55666 | 0.57924 | 1.6207 | 1.0752 | 0.43894 | 0.80301 | 0 | 0.31431 | 0.26605 | 30.1872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV | 26.2853 | 5.1269 | 0.09 | 0.01997 | 0.38232 | 0.032971 | 0.34464 | 1.0583 | 0.60547 | 2.9335 | 0.26361 | 0.75849 | 0.71586 | 1.0341 | 2.0402 | 1.6466 | 3.42 | 1.1983 | 3.9489 | 0.86176 | 0.76563 | 2.7218 | 0.61412 | 0.99342 | 2.4851 | 0.071365 | 1.9049 | 0.21353 | 0.91249 | 0.11054 | 4.4549 | 1.3915 | 1.2244 | 3.4972 | 1.0226 | 2.0862 | 0.32169 | 2.5321 | 1.0264 | 0.0397 | 0.34833 | 3.6894 | 0 | 0 | 0.77868 | 0.098316 | 0.13129 | 0.077593 | 0 | 0 | 0.61604 | 4.7262 | 0 | 0 | 0 | 0.064172 | 0.11807 | 0 | 0.11729 | 0.38044 | 0.10948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV | 28.6695 | 5.3544 | 0.12 | 0.030197 | 0.078919 | 1.7376 | 2.1788 | 8.1556 | 1.7097 | 3.0963 | 5.2404 | 5.9794 | 3.5902 | 16.0093 | 3.5667 | 2.3084 | 0.67652 | 2.0179 | 1.1958 | 0.9565 | 0.45946 | 0.68561 | 4.112 | 0.63924 | 1.9089 | 1.6851 | 4.1271 | 0.17473 | 0.62466 | 3.004 | 0.44511 | 0.37041 | 0.30062 | 0.27826 | 18.5284 | 2.4795 | 0.12034 | 0.17261 | 0.14275 | 0.0096575 | 0.15609 | 0.42291 | 0.55001 | 0.066046 | 1.2445 | 0 | 0 | 0 | 0 | 0.55607 | 9.9728 | 0.098859 | 0 | 0 | 0 | 0 | 0.15435 | 0 | 0.24036 | 0 | 0.4685 | 0.42265 | 1.7889 | 0.069795 | 2.5977 | 1.2922 | 15.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | 33.0603 | 5.7498 | 0.001 | 0.079999 | 0 | 1.4033 | 0 | 4.068 | 0.05458 | 0 | 6.3262 | 1.5765 | 0.9963 | 0 | 0 | 0.047287 | 0 | 0 | 0.75154 | 0.40634 | 2.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6125 | 3.2711 | 0.12552 | 0 | 4.7393 | 0 | 1.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8731 | 4.9166 | 1.0832 | 1.9834 | 1.8243 | 0.65687 | 0.14387 | 3.3971 | 2.0015 | 1.3763 | 0.56737 | 0 | 0.40948 | 0 | 0.23005 | 0 | 0 | 0.080057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
> 132 kV
Other
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type | 28.5488 | 5.3431 | 28821 | 22773 | 18846 | 18759 | 13148 | 13315 | 5803 | 6454 | 7928 | 8539 | 8756 | 8607 | 8302 | 8357 | 8631 | 9607 | 11477 | 13145 | 14986 | 14238 | 11711 | 10625 | 10196 | 11618 | 14504 | 15997 | 16273 | 16491 | 15826 | 15392 | 15612 | 16043 | 16566 | 16276 | 16247 | 15054 | 12707 | 11648 | 10039 | 7843 | 6923 | 7564 | 11936 | 15690 | 15583 | 17652 | 14908 | 15049 | 10068 | 8741 | 8708 | 9871 | 9873 | 9841 | 5661 | 2773 | 2774 | 6989 | 5649 | 1085 | 1083 | 540 | 540 | 124 | 124 | 44 | 44 | 37 | 37 | 22 | 22 | 10 | 10 | 3 | 3 | 1 | 1 | 5 | 5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
˂ = 11 kV ; Commercial & Industrial ; Simple Type
˂ = 11 kV ; Residential ; Complex Type
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 26.8028 | 5.1771 | 3235 | 2658 | 2087 | 2160 | 1958 | 1709 | 901 | 864 | 844 | 831 | 868 | 891 | 909 | 956 | 922 | 1349 | 1740 | 2211 | 2454 | 2137 | 2025 | 1860 | 2012 | 2191 | 2126 | 1954 | 1909 | 1980 | 2048 | 2354 | 2413 | 2354 | 2505 | 2251 | 1849 | 1836 | 1854 | 1736 | 1608 | 1305 | 1070 | 1020 | 1111 | 1213 | 1197 | 1320 | 1181 | 1402 | 933 | 943 | 937 | 1043 | 1045 | 1175 | 351 | 125 | 125 | 155 | 102 | 28 | 28 | 14 | 14 | 5 | 5 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | - | - | 1 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
˂ = 11 kV ; Subdivision ; Complex Type
> 11 kV & < = 22 kV ; Commercial & Industrial
> 11 kV & < = 22 kV ; Subdivision
> 22 kV & < = 33 kV ; Commercial & Industrial
> 22 kV & < = 33 kV ; Subdivision
> 33 kV & < = 66 kV ; Commercial & Industrial
> 33 kV & < = 66 kV ; Subdivision
> 66 kV & < = 132 kV ; Commercial & Industrial
> 66 kV & < = 132 kV ; Subdivision
> 132 kV ; Commercial & Industrial
> 132 kV ; Subdivision
Other
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE ; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 30.4676 | 5.5197 | 278 | 575.9094 | 244.6608 | 221.5036 | 221.5036 | 525.5677 | 485.2943 | 502.4105 | 642.3605 | 563.8274 | 570.8752 | 424.8842 | 533.6224 | 510.4652 | 533.6224 | 480.2601 | 483.2806 | 593.0256 | 477.2396 | 592.0188 | 554.7659 | 418.8432 | 539.6634 | 549.7317 | 761.167 | 1138.73 | 731.9688 | 675.586 | 949.4451 | 1068.2515 | 763.1806 | 793.3857 | 793.3857 | 777.2763 | 823.5907 | 747.0713 | 893.0623 | 779.29 | 751.0986 | 684.6475 | 678.6065 | 581.9504 | 491.3353 | 542.6839 | 720.8936 | 503.4173 | 434.9526 | 449.0482 | 428.9116 | 693.7091 | 487.308 | 371.522 | 308.0914 | 371.522 | 388.6382 | 330.2418 | 351.3853 | 442.0004 | 220.4968 | 211.4353 | 167.1345 | 16.1094 | 7.0478 | 1.0068 | 3.0205 | 3.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 22.2731 | 4.7194 | 7 | 17.0754 | 11.0274 | 7.0343 | 8.0548 | 9.0617 | 12.0411 | 29.1096 | 15.0685 | 12.048 | 19.0959 | 10.0685 | 9.0343 | 12.0685 | 15.1028 | 8.048 | 8.048 | 10.0548 | 21.048 | 9.0617 | 11.0754 | 4.0274 | 6.0411 | 5.0343 | 1.0069 | 23.1576 | 3.0206 | 3.0206 | 8.0548 | 8.0548 | 6.0411 | 8.0411 | 10.0685 | 11.0754 | 8.0548 | 7.048 | 6.0411 | 6.0411 | 9.0617 | 3.0206 | 3.0206 | 3.0206 | 3.0206 | 5.0343 | 8.0548 | 4.0274 | 3.0206 | 1.0069 | 4.0274 | 2.0137 | 4.0274 | 6.0411 | 2.0137 | 2.0137 | 2.0137 | 2.0137 | 4.0274 | 1.0069 | 0 | 2.0137 | 2.0137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 32.0956 | 5.6653 | 47 | 102.6949 | 35.2384 | 21.1431 | 30.2044 | 49.3338 | 58.3951 | 65.4428 | 81.5518 | 59.4019 | 92.6267 | 74.5041 | 78.5314 | 106.7221 | 93.6335 | 95.6472 | 100.6812 | 110.7493 | 176.1921 | 248.6826 | 212.4374 | 197.3352 | 175.1853 | 178.2058 | 250.6963 | 276.8734 | 269.8257 | 266.8053 | 322.1799 | 405.7453 | 297.0096 | 230.56 | 264.7916 | 244.6554 | 274.8597 | 253.7167 | 234.5873 | 322.1799 | 290.9687 | 258.7508 | 216.4646 | 207.4033 | 176.1921 | 212.4374 | 229.5532 | 177.199 | 183.2398 | 118.8038 | 128.872 | 149.0082 | 141.9605 | 97.6608 | 76.5177 | 77.5245 | 75.5109 | 62.4224 | 49.3338 | 28.1907 | 16.109 | 13.0886 | 7.0477 | 5.0341 | 12.0817 | 15.1022 | 7.0477 | 2.0136 | 1.0068 | 1.0068 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 23.4495 | 4.8425 | 110 | 375.5452 | 82.5595 | 54.3685 | 88.6005 | 326.2109 | 401.7226 | 483.2754 | 581.9441 | 757.1314 | 616.1761 | 589.9987 | 561.8076 | 597.0464 | 545.6984 | 515.4937 | 507.4391 | 342.32 | 783.3088 | 351.3815 | 275.8697 | 244.6581 | 229.5558 | 134.9144 | 254.7264 | 272.8492 | 271.8424 | 237.6104 | 263.7878 | 353.3951 | 307.0812 | 303.0539 | 333.2586 | 281.9106 | 351.3815 | 337.2859 | 346.3473 | 361.4497 | 248.6854 | 252.7127 | 211.433 | 221.5012 | 189.2828 | 170.1532 | 195.3238 | 161.0918 | 148.0031 | 119.812 | 134.9144 | 96.6551 | 112.7642 | 96.6551 | 90.6141 | 77.5254 | 84.5732 | 59.4026 | 45.3071 | 14.0955 | 4.0273 | 4.0273 | 7.0478 | 4.0273 | 4.0273 | 6.0409 | 7.0478 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 27.45 | 5.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0136 | 2.0136 | 1.0068 | 2.0136 | 1.0068 | 1.0068 | 0 | 0 | 0 | 0 | 1.0068 | 2.0136 | 0 | 0 | 0 | 2.0136 | 1.0068 | 1.0068 | 2.0136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 27.4493 | 5.2392 | 0 | 1.0068 | 0 | 1.0068 | 0 | 0 | 3.0203 | 2.0136 | 4.0271 | 0 | 3.0203 | 10.0678 | 7.0474 | 10.0678 | 6.0407 | 4.0271 | 7.0474 | 8.0542 | 2.0136 | 4.0271 | 13.0881 | 5.0339 | 10.0678 | 9.061 | 13.0881 | 12.0813 | 18.122 | 11.0746 | 26.1762 | 15.1017 | 16.1085 | 18.122 | 44.2982 | 37.2508 | 12.0813 | 15.1017 | 4.0271 | 1.0068 | 2.0136 | 1.0068 | 3.0203 | 1.0068 | 0 | 0 | 1.0068 | 1.0068 | 1.0068 | 0 | 1.0068 | 1.0068 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 27.3333 | 5.2281 | 0 | 14.0949 | 0 | 0 | 0 | 2.0136 | 2.0136 | 0 | 2.0136 | 8.0542 | 0 | 0 | 2.0136 | 0 | 1.0068 | 1.0068 | 0 | 0 | 2.0136 | 2.0136 | 1.0068 | 1.0068 | 2.0136 | 0 | 1.0068 | 2.0136 | 0 | 2.0136 | 6.0407 | 0 | 1.0068 | 2.0136 | 0 | 4.0271 | 26.1762 | 19.1288 | 4.0271 | 12.0813 | 0 | 2.0136 | 6.0407 | 1.0068 | 0 | 0 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 25.2381 | 5.0238 | 0 | 0 | 1.0068 | 0 | 0 | 1.0068 | 1.0068 | 5.0339 | 1.0068 | 1.0068 | 0 | 2.0136 | 1.0068 | 3.0203 | 3.0203 | 0 | 2.0136 | 1.0068 | 0 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 2.0136 | 3.0203 | 1.0068 | 1.0068 | 3.0203 | 1.0068 | 10.0678 | 8.0542 | 3.0203 | 2.0136 | 1.0068 | 1.0068 | 0 | 0 | 1.0068 | 0 | 0 | 1.0068 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 24.8203 | 4.982 | 14 | 70.4751 | 8.0543 | 11.0747 | 52.3529 | 223.5066 | 268.812 | 306.0631 | 353.3821 | 419.83 | 418.8232 | 378.5517 | 300.0224 | 328.2124 | 317.1377 | 295.9952 | 273.8459 | 273.8459 | 172.1605 | 185.2487 | 163.0994 | 193.303 | 164.1062 | 139.9433 | 265.7916 | 331.2328 | 284.9206 | 274.8527 | 377.5449 | 371.5042 | 416.8096 | 303.0427 | 358.416 | 463.1218 | 405.735 | 271.8324 | 167.1266 | 176.1876 | 143.9705 | 140.9501 | 146.9908 | 230.5541 | 250.6898 | 216.4591 | 175.1809 | 105.7126 | 62.4208 | 28.19 | 22.1493 | 7.0475 | 1.0068 | 4.0271 | 5.0339 | 10.0679 | 11.0747 | 4.0271 | 21.1425 | 1.0068 | 5.0339 | 1.0068 | 0 | 1.0068 | 0 | 6.0407 | 35.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 19.9754 | 4.4694 | 1 | 11.0746 | 2.0136 | 2.0136 | 5.0339 | 25.1696 | 77.5222 | 80.5426 | 75.5087 | 79.5358 | 65.4408 | 90.6104 | 76.5154 | 74.5019 | 72.4883 | 65.4408 | 72.4883 | 54.3662 | 51.3459 | 57.3866 | 60.4069 | 55.373 | 35.2374 | 25.1696 | 37.2509 | 35.2374 | 40.2713 | 16.1085 | 37.2509 | 45.3052 | 39.2645 | 34.2306 | 36.2442 | 44.2984 | 31.2102 | 11.0746 | 19.1289 | 23.156 | 7.0475 | 12.0814 | 14.0949 | 7.0475 | 10.0678 | 0 | 3.0203 | 4.0271 | 1.0068 | 1.0068 | 2.0136 | 1.0068 | 4.0271 | 1.0068 | 0 | 3.0203 | 2.0136 | 0 | 1.0068 | 0 | 3.0203 | 0 | 0 | 0 | 0 | 3.0203 | 6.0407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 30.3333 | 5.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase
Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 54.75 | 7.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 41.8933 | 6.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 4 | 2 | 0 | 8 | 0 | 4 | 1 | 2 | 1 | 2 | 2 | 4 | 0 | 2 | 2 | 1 | 0 | 10 | 4 | 1 | 1 | 5 | 2 | 2 | 5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 32.8356 | 5.7302 | 1 | 8 | 7 | 7 | 6 | 2 | 7 | 11 | 7 | 7 | 4 | 2 | 4 | 2 | 2 | 5 | 3 | 10 | 8 | 0 | 1 | 2 | 0 | 2 | 0 | 1 | 0 | 13 | 2 | 3 | 0 | 24 | 0 | 7 | 0 | 9 | 14 | 0 | 0 | 1 | 3 | 0 | 5 | 5 | 11 | 0 | 3 | 0 | 3 | 17 | 2 | 1 | 13 | 7 | 0 | 5 | 7 | 4 | 3 | 0 | 2 | 6 | 5 | 6 | 2 | 2 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 21.4 | 4.626 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 45.3694 | 6.7357 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 4 | 3 | 0 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 1 | 2 | 5 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 9 | 7 | 5 | 7 | 5 | 4 | 18 | 5 | 12 | 5 | 0 | 2 | 5 | 0 | 2 | 4 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 25.2787 | 5.0278 | 1 | 2 | 0 | 0 | 3 | 5 | 1 | 11 | 4 | 4 | 4 | 2 | 4 | 2 | 5 | 2 | 5 | 4 | 4 | 0 | 1 | 0 | 0 | 2 | 0 | 3 | 0 | 1 | 5 | 1 | 3 | 0 | 1 | 4 | 0 | 2 | 3 | 2 | 0 | 4 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 3 | 6 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA
Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA
Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA
Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA
Other
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; Fuse
| ˂ = 11 kV ; Switch | 42.69 | 6.5338 | 30 | 10 | 22 | 14 | 0 | 21 | 39 | 20 | 6 | 11 | 18 | 13 | 4 | 14 | 4 | 4 | 0 | 4 | 1 | 0 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 5 | 11 | 1 | 7 | 3 | 15 | 0 | 8 | 25 | 20 | 11 | 28 | 20 | 3 | 44 | 22 | 25 | 6 | 6 | 67 | 32 | 105 | 144 | 81 | 77 | 106 | 144 | 34 | 38 | 8 | 12 | 0 | 3 | 5 | 55 | 3 | 18 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Circuit Breaker | 28.9856 | 5.3838 | 9 | 49 | 7 | 20 | 27 | 27 | 64 | 135 | 35 | 20 | 32 | 12 | 32 | 13 | 14 | 17 | 30 | 31 | 8 | 4 | 32 | 11 | 10 | 0 | 0 | 6 | 4 | 9 | 20 | 28 | 0 | 26 | 0 | 31 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 38 | 41 | 43 | 36 | 12 | 78 | 67 | 2 | 73 | 12 | 16 | 15 | 0 | 0 | 29 | 1 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Switch | 51 | 7.1414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
> 11 kV & < = 22 kV ; Circuit Breaker
| > 22 kV & < = 33 kV ; Switch | 32.4278 | 5.6945 | 43 | 6 | 20 | 19 | 9 | 57 | 49 | 32 | 34 | 40 | 20 | 1 | 9 | 36 | 19 | 16 | 6 | 7 | 12 | 4 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 27 | 15 | 4 | 5 | 0 | 10 | 3 | 4 | 10 | 3 | 3 | 11 | 21 | 13 | 3 | 5 | 9 | 2 | 16 | 43 | 8 | 6 | 15 | 76 | 39 | 65 | 55 | 25 | 16 | 4 | 3 | 0 | 0 | 0 | 21 | 24 | 27 | 8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker | 27.1401 | 5.2096 | 13 | 9 | 0 | 11 | 1 | 11 | 20 | 20 | 14 | 8 | 5 | 5 | 7 | 7 | 11 | 7 | 7 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 0 | 1 | 2 | 0 | 9 | 0 | 3 | 24 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch | 34.4409 | 5.8686 | 2 | 7 | 1 | 19 | 35 | 58 | 70 | 76 | 80 | 66 | 25 | 24 | 18 | 22 | 13 | 7 | 20 | 20 | 12 | 3 | 2 | 13 | 1 | 12 | 0 | 0 | 0 | 17 | 11 | 0 | 2 | 25 | 9 | 4 | 0 | 0 | 5 | 6 | 0 | 8 | 4 | 10 | 18 | 6 | 3 | 0 | 12 | 14 | 85 | 74 | 57 | 48 | 31 | 72 | 34 | 65 | 22 | 24 | 19 | 0 | 30 | 33 | 0 | 37 | 14 | 10 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker | 23.4098 | 4.8384 | 6 | 4 | 9 | 9 | 10 | 11 | 14 | 40 | 40 | 30 | 15 | 23 | 16 | 19 | 12 | 2 | 14 | 12 | 7 | 5 | 2 | 6 | 1 | 2 | 1 | 0 | 0 | 2 | 8 | 0 | 0 | 6 | 4 | 2 | 12 | 11 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 10 | 24 | 6 | 5 | 3 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 3 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
> 66 kV & < = 132 kV ; Switch
> 66 kV & < = 132 kV ; Circuit Breaker
> 132 kV ; Switch
> 132 kV ; Circuit Breaker
Other
PUBLIC LIGHTING BY: ASSET TYPE ; LIGHTING OBLIGATION | Luminaires ; Major Road
Luminaires ; Minor Road
Brackets ; Major Road
Brackets ; Minor Road
Lamps ; Major Road
Lamps ; Minor Road
Poles / Columns ; Major Road
Poles / Columns ; Minor Road
Other
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices | 26.8262 | 5.1794 | 213 | 194 | 171 | 172 | 192 | 214 | 227 | 251 | 224 | 171 | 127 | 89 | 89 | 78 | 70 | 70 | 66 | 55 | 51 | 50 | 36 | 39 | 30 | 22 | 29 | 43 | 127 | 190 | 182 | 170 | 177 | 165 | 122 | 102 | 104 | 92 | 74 | 62 | 52 | 50 | 51 | 62 | 61 | 61 | 57 | 51 | 63 | 91 | 115 | 110 | 117 | 114 | 76 | 76 | 89 | 87 | 74 | 38 | 19 | 49 | 78 | 81 | 51 | 20 | 12 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Local Network Wiring Assets
| Communications Network Assets | 7.6323 | 2.7627 | 175 | 447 | 203 | 251 | 201 | 141 | 397 | 272 | 259 | 197 | 77 | 63 | 248 | 190 | 42 | 47 | 0 | 18 | 0 | 0 | 1 | 12 | 0 | 3 | 14 | 3 | 24 | 1 | 2 | 4 | 0 | 0 | 0 | 7 | 1 | 4 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master Station Assets | 10.4237 | 3.2286 | 30 | 10 | 9 | 12 | 33 | 23 | 22 | 14 | 8 | 18 | 18 | 16 | 24 | 34 | 29 | 28 | 14 | 22 | 0 | 16
| Communications Site Infrastructure | 24.6957 | 4.9695 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 7 | 1 | 5 | 8 | 5 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 4 | 1 | 7 | 0 | 3 | 1 | 1 | 0 | 0 | 6 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Linear Assets | 16.0858 | 4.0107 | 6.7 | 6.67 | 17.89 | 117.51 | 92.931 | 91.675 | 210.8 | 205.9 | 186.56 | 180.26 | 172.8 | 157.9 | 182 | 161.55 | 153.95 | 169.6 | 90.8 | 82.03 | 26.63 | 25.21 | 23.31 | 24.55 | 8.74 | 1.46 | 2.91 | 4.37 | 4.37 | 7.28 | 26.22 | 4.37 | 7.28 | 5.83 | 5.83 | 2.91 | 2.91 | 11.65 | 8.74 | 10.2 | 2.91 | 5.83 | 17.48 | 17.48 | 13.11 | 8.74 | 1.46 | 0 | 1.46 | 15.95 | 29.13 | 28.63 | 17.05 | 19.91 | 13.11 | 28.25 | 7.28 | 1.46 | 13.11 | 0 | 7.28 | 0 | 1.46 | 7.28 | 5.83 | 11.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AFLC
Other
OTHER BY: DNSP DEFINED | DNSP defined
| ˂ = 1 kV; stobie pole | 53.8857 | 7.3407 | 418 | 569 | 1074 | 68 | 65 | 90 | 99 | 44 | 84 | 64 | 56 | 669.4927 | 260.5937 | 584.7468 | 409.9584 | 254.2377 | 382.4159 | 311.4412 | 498.9416 | 1048.7307 | 52.9662 | 492.5856 | 24.3645 | 1103.8156 | 493.645 | 623.9418 | 20.1272 | 1710.8082 | 1449.1552 | 1192.7988 | 1372.8838 | 745.7641 | 1290.2566 | 1569.9181 | 1377.1211 | 1921.6137 | 1542.3757 | 1190.6801 | 1655.7233 | 2030.724 | 1994.707 | 1457.6298 | 2658.9031 | 2943.8613 | 3882.4223 | 3466.108 | 4153.6092 | 2427.9705 | 5893.0192 | 6229.8842 | 5129.2466 | 9551.9241 | 5426.9166 | 8598.5326 | 12440.7006 | 13365.4904 | 12115.4881 | 11554.0464 | 13984.1356 | 9076.2877 | 9369.7204 | 12657.862 | 7744.7174 | 4705.517 | 14829.4761 | 6297.6809 | 3484.1165 | 1247.8836 | 38.1357 | 92.1612 | 28.6017 | 68.8561 | 256.3564 | 252.1191 | 347.4583 | 130.2968 | 121.8223 | 252.1191 | 301.9073 | 1593.2232 | 844.2812 | 691.7385 | 718.2216 | 636.6537 | 917.3745 | 223.5174 | 61.4408 | 33.8984 | 3.178 | 8.4746 | 0 | 0 | 0 | 0 | 1.0593 | 3.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV; stobie pole | 46.8608 | 6.8455 | 1704 | 1037 | 677 | 1694 | 1824 | 1941 | 2124 | 882 | 456 | 352 | 436 | 1071.9381 | 396.2665 | 912.5816 | 588.5567 | 407.9527 | 470.6329 | 439.824 | 533.3131 | 1580.8166 | 60.5555 | 1574.4423 | 36.1208 | 1842.1613 | 900.8955 | 1350.2808 | 79.6783 | 3067.0816 | 1801.7909 | 2549.7042 | 2394.5972 | 1503.2631 | 2283.0476 | 3198.8163 | 2361.6635 | 2581.5755 | 2131.1277 | 1944.1494 | 2909.8499 | 3641.8274 | 3856.4275 | 2289.4219 | 5310.8213 | 4412.0506 | 3992.4118 | 5365.0025 | 6971.3161 | 6418.8802 | 9902.4135 | 8488.3901 | 7828.6541 | 14133.86 | 5713.4621 | 9901.3511 | 9174.6855 | 7364.3955 | 7906.2076 | 7057.3686 | 6954.3181 | 4967.6736 | 3283.8065 | 4213.3861 | 3067.0816 | 5446.8055 | 10478.2217 | 3042.647 | 1392.7759 | 589.6191 | 46.7446 | 169.9803 | 8.499 | 15.9357 | 282.5922 | 106.2377 | 131.7347 | 62.6802 | 62.6802 | 108.3624 | 70.1169 | 638.4884 | 231.5981 | 257.0952 | 314.4635 | 237.9724 | 294.2784 | 95.6139 | 29.7465 | 14.8733 | 3.1871 | 8.499 | 0 | 0 | 1.0624 | 0 | 0 | 2.1248 | 0 | 0 | 1.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; stobie pole | 49.463 | 7.033 | 198 | 321 | 282 | 227 | 232 | 178 | 179 | 99 | 57 | 60 | 74 | 231.0091 | 125.0416 | 207.6963 | 205.5769 | 126.1013 | 151.5335 | 100.6691 | 207.6963 | 416.4523 | 15.8951 | 387.841 | 18.0145 | 597.6567 | 516.0617 | 628.3872 | 10.5967 | 947.3494 | 659.1178 | 1156.1054 | 822.3078 | 601.8954 | 1071.3314 | 989.7364 | 699.3855 | 714.2209 | 533.0165 | 954.7671 | 813.8304 | 1571.4979 | 594.4776 | 1248.2971 | 1789.791 | 2501.8925 | 4053.2566 | 2860.0627 | 3260.6198 | 2252.8689 | 4751.5824 | 6354.8706 | 4068.0921 | 8982.8644 | 2501.8925 | 8007.9635 | 7239.6992 | 7051.077 | 5674.5593 | 5591.9046 | 4977.2932 | 3579.5819 | 3227.7699 | 3583.8206 | 592.3583 | 671.8339 | 559.5084 | 147.2948 | 70.9982 | 19.0741 | 2.1193 | 16.9548 | 1.0597 | 4.2387 | 7.4177 | 1.0597 | 11.6564 | 2.1193 | 5.2984 | 11.6564 | 4.2387 | 7.4177 | 3.179 | 13.7758 | 4.2387 | 1.0597 | 3.179 | 2.1193 | 2.1193 | 0 | 0 | 3.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0597 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV; stobie pole | 49.0701 | 7.005 | 50 | 52 | 36 | 15 | 36 | 35 | 26 | 108 | 39 | 17 | 29 | 139.8421 | 105.941 | 75.2181 | 75.2181 | 161.0303 | 78.3963 | 58.2676 | 88.9905 | 325.2389 | 7.4159 | 431.1799 | 375.0312 | 93.2281 | 75.2181 | 203.4067 | 5.2971 | 349.6053 | 378.2094 | 354.9024 | 559.3685 | 272.2684 | 332.6548 | 348.5459 | 453.4275 | 309.3478 | 139.8421 | 49.7923 | 342.1895 | 268.0308 | 262.7337 | 1493.7683 | 797.7358 | 1083.7766 | 494.7445 | 563.6062 | 1312.6091 | 295.5754 | 1032.9249 | 1251.1634 | 805.1517 | 1814.7695 | 851.7657 | 1660.0957 | 2299.9794 | 1512.8377 | 2306.3358 | 782.9041 | 1507.5406 | 885.6669 | 432.2393 | 671.666 | 656.8343 | 465.081 | 1310.4903 | 412.1105 | 326.2983 | 62.5052 | 12.7129 | 84.7528 | 0 | 18.01 | 23.307 | 141.961 | 50.8517 | 16.9506 | 80.5152 | 76.2775 | 46.614 | 77.3369 | 39.1982 | 29.6635 | 26.4853 | 5.2971 | 15.8912 | 60.3864 | 3.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
> 66 kV & < = 132 kV; stobie pole
> 132 kV; stobie pole
| Pole REFURBISHED; STOBIE Pole | 5.3441 | 2.3117 | 2818 | 6112 | 4102 | 2676 | 3717 | 2563 | 3210 | 3005 | 1811 | 917 | 1232 | 1027.9756 | 979.0244
| Pole Mounted ;> = 22 kV & < = 33 kV ; < = 60kVA | 27.743 | 5.2672 | 13 | 15.1027 | 4.0274 | 9.0616 | 6.0411 | 30.2054 | 19.1301 | 51.3492 | 44.3013 | 30.2054 | 32.2191 | 18.1233 | 20.137 | 33.226 | 26.178 | 20.137 | 19.1301 | 24.1644 | 18.1233 | 25.1712 | 26.178 | 23.1575 | 21.1438 | 33.226 | 43.2945 | 20.137 | 33.226 | 32.2191 | 23.1575 | 43.2945 | 30.2054 | 22.1507 | 42.2876 | 18.1233 | 27.1849 | 26.178 | 26.178 | 19.1301 | 23.1575 | 11.0753 | 16.1096 | 13.089 | 15.1027 | 20.137 | 10.0685 | 13.089 | 11.0753 | 8.0548 | 13.089 | 33.226 | 6.0411 | 17.1164 | 26.178 | 6.0411 | 10.0685 | 10.0685 | 17.1164 | 3.0205 | 4.0274 | 4.0274 | 0 | 5.0342 | 15.1027 | 1.0068 | 1.0068 | 0 | 1.0068 | 0 | 0
| Pole Mounted ;> = 22 kV & < = 33 kV ; > 60 KVA AND < = 600 KVA | 23.9741 | 4.8963 | 5 | 11.0752 | 3.0205 | 3.0205 | 4.0273 | 8.0547 | 26.1777 | 21.1435 | 31.2118 | 25.1708 | 20.1367 | 20.1367 | 16.1093 | 17.1162 | 10.0683 | 15.1025 | 17.1162 | 17.1162 | 14.0957 | 17.1162 | 9.0615 | 6.041 | 14.0957 | 12.082 | 22.1503 | 26.1777 | 16.1093 | 13.0888 | 11.0752 | 11.0752 | 21.1435 | 10.0683 | 5.0342 | 7.0478 | 12.082 | 11.0752 | 4.0273 | 13.0888 | 9.0615 | 8.0547 | 4.0273 | 6.041 | 4.0273 | 2.0137 | 4.0273 | 7.0478 | 2.0137 | 2.0137 | 5.0342 | 7.0478 | 3.0205 | 1.0068 | 1.0068 | 5.0342 | 6.041 | 11.0752 | 4.0273 | 2.0137 | 1.0068 | 0 | 1.0068 | 4.0273 | 1.0068 | 0 | 0 | 3.0205 | 0 | 0 | 0
| Pole Mounted ; > = 22 kV & < = 33 kV ; > 600 kVA | 20.8322 | 4.5642 | 1 | 0 | 0 | 0 | 1.0071 | 0 | 0 | 1.0071 | 2.0142 | 0 | 0 | 2.0142 | 0 | 0 | 0 | 0 | 3.0213 | 1.0071 | 0 | 2.0142 | 0 | 1.0071 | 1.0071 | 0 | 3.0213 | 0 | 0 | 0 | 0 | 1.0071 | 0 | 0 | 0 | 0 | 1.0071 | 1.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted; > = 22 kV & < = 33 kV ; | 16.6805 | 4.0842 | 1 | 1.0071 | 1.0071 | 0 | 0 | 4.0283 | 0 | 1.0071 | 0 | 3.0213 | 4.0283 | 4.0283 | 3.0213 | 5.0354 | 3.0213 | 2.0142 | 4.0283 | 1.0071 | 2.0142 | 5.0354 | 2.0142 | 5.0354 | 1.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0071 | 0 | 0 | 0
| Recloser ;SWITCHGEAR | 9.3646 | 3.0602 | 56 | 47 | 222 | 114 | 131 | 173 | 88 | 181 | 128 | 45 | 32 | 42 | 39 | 19 | 37 | 22 | 17 | 10 | 6 | 2 | 2 |  |  |  | 4 | 44 | 17 |  | 2 | 3 | 10 | [13 empty] | 45
| Sectionalizer ;SWITCHGEAR | 23.8816 | 4.8869 | 0 | 0 | 4 | 49 | 1 | 2 | 0 | 6 | 5 | 14 | 2 | 5 | 1 | 2 | 19 | 68 | 11 | 23 | 22 | 11 | 14 | 5 | 26 | 36 | 50 | 26 | 34 | 6 | 48 | 44 | 2 | 14 | 51 | 30 | 20 | 6 | 13 | 4 | 0 | 0 | 1 | 8 | 0 | 11 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| >= 11 kV & < ≈ 22 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR | 12.9554 | 3.5994 | 118 | 371 | 448 | 276 | 301 | 327 | 268 | 410 | 442 | 451 | 455 | 434 | 338 | 542 | 329 | 288 | 260 | 142 | 48 | 21 | 73 | 52 | 362 | 1 | 3 | 0 | 0 | 418 | 7 | 1 | 10 | 3 | 4 | 142 | 1 | 0 | 0 | 1 | 82 | 0 | 0 | 0 | 0 | 72 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
> 22 kV & < ≈ 33 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR
| Pipework Switchyard Substations | 52.0455 | 7.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 4 | 2 | 3 | 1 | 2 | 4 | 4 | 2 | 3 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.3 MD - Network level
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
5.3 MAXIMUM DEMAND AT NETWORK LEVEL
5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL (Summed at transmission connection point)
| UNIT | 2018-19
Raw network coincident MD | MW | 2963.164
Date MD occurred |  | 2019-01-24
Half hour time period MD occurred |  | 19:30
Winter/summer peaking |  | Summer
Embedded generation | MW | 333.835
Weather corrected (10% POE) network coincident MD | MW | 3053.314
Weather corrected (50% POE) network coincident MD | MW | 2755.899
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 5.4 MD & utilisation-Spatial
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL
There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data.
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2018-19
SUBTRANSMISSION SUBSTATION | Angas Creek 33kV | Substation Rating | MVA | Non-Coincident | 53.9
|  |  |  | Coincident | 53.9
|  | Raw Adjusted MD | MW | Non-Coincident | 20.486
|  |  |  | Coincident | 20.26
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.1929
|  |  |  | Coincident | 20.911
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.20297
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.4142
|  |  |  | Coincident | 21.178
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.1531
|  |  |  | Coincident | 21.8584
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.2852
|  |  |  | Coincident | 19.0725
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.9507
|  |  |  | Coincident | 19.6853
| Ardrossan West 33kV | Substation Rating | MVA | Non-Coincident | 62
|  |  |  | Coincident | 62
|  | Raw Adjusted MD | MW | Non-Coincident | 12.149
|  |  |  | Coincident | 12.064
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.3473
|  |  |  | Coincident | 12.2573
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.22837
|  |  |  | Coincident | 0.12617
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.4285
|  |  |  | Coincident | 10.3555
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.5987
|  |  |  | Coincident | 10.5214
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.2529
|  |  |  | Coincident | 9.1882
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.4039
|  |  |  | Coincident | 9.3353
| Baroota 33kV | Substation Rating | MVA | Non-Coincident | 11.8
|  |  |  | Coincident | 11.8
|  | Raw Adjusted MD | MW | Non-Coincident | 8.707
|  |  |  | Coincident | 8.688
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.752
|  |  |  | Coincident | 8.7311
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.096743
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.2612
|  |  |  | Coincident | 8.2432
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.3039
|  |  |  | Coincident | 8.284
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.5028
|  |  |  | Coincident | 7.4865
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.5416
|  |  |  | Coincident | 7.5236
| Berri 66kV | Substation Rating | MVA | Non-Coincident | 190
|  |  |  | Coincident | 190
|  | Raw Adjusted MD | MW | Non-Coincident | 89.032
|  |  |  | Coincident | 87.112
|  | Raw Adjusted MD | MVA | Non-Coincident | 91.4124
|  |  |  | Coincident | 89.1576
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.1267
|  |  |  | Coincident | 0.62248
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 94.3674
|  |  |  | Coincident | 92.3324
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 96.8904
|  |  |  | Coincident | 94.5006
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 86.9654
|  |  |  | Coincident | 85.09
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 89.2905
|  |  |  | Coincident | 87.0881
| Blanche 33kV | Substation Rating | MVA | Non-Coincident | 126.3
|  |  |  | Coincident | 126.3
|  | Raw Adjusted MD | MW | Non-Coincident | 33.005
|  |  |  | Coincident | 31.634
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.9024
|  |  |  | Coincident | 32.6065
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.256
|  |  |  | Coincident | 0.16286
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.5125
|  |  |  | Coincident | 34.9958
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.6115
|  |  |  | Coincident | 36.0717
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.5415
|  |  |  | Coincident | 32.1482
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.4697
|  |  |  | Coincident | 33.1365
| Brinkworth 33kV | Substation Rating | MVA | Non-Coincident | 24.6
|  |  |  | Coincident | 24.6
|  | Raw Adjusted MD | MW | Non-Coincident | 4.969
|  |  |  | Coincident | 4.935
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.9764
|  |  |  | Coincident | 4.943
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.055566
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.3548
|  |  |  | Coincident | 5.3181
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.3627
|  |  |  | Coincident | 5.3267
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.7991
|  |  |  | Coincident | 4.7663
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.8062
|  |  |  | Coincident | 4.774
| Clare North 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 13.037
|  |  |  | Coincident | 12.719
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.7928
|  |  |  | Coincident | 13.41
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.77168
|  |  |  | Coincident | 0.095217
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.5229
|  |  |  | Coincident | 13.193
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.3068
|  |  |  | Coincident | 13.9097
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.0539
|  |  |  | Coincident | 11.7599
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.7527
|  |  |  | Coincident | 12.3988
| Dalrymple 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 7.0869
|  |  |  | Coincident | 6.9783
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.0872
|  |  |  | Coincident | 6.9784
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.15167
|  |  |  | Coincident | 0.083796
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.7778
|  |  |  | Coincident | 7.6592
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.7778
|  |  |  | Coincident | 7.6594
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.7978
|  |  |  | Coincident | 6.6942
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.7978
|  |  |  | Coincident | 6.6943
| Davenport West 33kV | Substation Rating | MVA | Non-Coincident | 120
|  |  |  | Coincident | 120
|  | Raw Adjusted MD | MW | Non-Coincident | 31.334
|  |  |  | Coincident | 31.131
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.2873
|  |  |  | Coincident | 32.0266
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.20751
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.0257
|  |  |  | Coincident | 30.8247
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.9697
|  |  |  | Coincident | 31.7115
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.0125
|  |  |  | Coincident | 27.831
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.8648
|  |  |  | Coincident | 28.6317
| Dorrien 33kV | Substation Rating | MVA | Non-Coincident | 216
|  |  |  | Coincident | 216
|  | Raw Adjusted MD | MW | Non-Coincident | 57.2507
|  |  |  | Coincident | 56.4686
|  | Raw Adjusted MD | MVA | Non-Coincident | 59.4179
|  |  |  | Coincident | 58.5043
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.116
|  |  |  | Coincident | 0.41855
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 63.8443
|  |  |  | Coincident | 62.9722
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 82.0814
|  |  |  | Coincident | 78.3114
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 58.4361
|  |  |  | Coincident | 57.6379
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 75.1284
|  |  |  | Coincident | 71.6777
| Florieton SWER 19kV | Substation Rating | MVA | Non-Coincident | 0.15
|  |  |  | Coincident | 0.15
|  | Raw Adjusted MD | MW | Non-Coincident | 0.04
|  |  |  | Coincident | 0.017
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.0617
|  |  |  | Coincident | 0.054708
|  | Date MD occurred |  | Non-Coincident | 2018-12-05
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.043117
|  |  |  | Coincident | 0.038806
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.066527
|  |  |  | Coincident | 0.067291
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.04014
|  |  |  | Coincident | 0.036126
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.061933
|  |  |  | Coincident | 0.062644
| Hummocks 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 14.394
|  |  |  | Coincident | 14.394
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.7411
|  |  |  | Coincident | 14.7411
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.082765
|  |  |  | Coincident | 0.082765
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.8257
|  |  |  | Coincident | 14.8257
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.1832
|  |  |  | Coincident | 15.1832
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.8099
|  |  |  | Coincident | 13.8099
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.1429
|  |  |  | Coincident | 14.1429
| Kadina East 33kV | Substation Rating | MVA | Non-Coincident | 120
|  |  |  | Coincident | 120
|  | Raw Adjusted MD | MW | Non-Coincident | 28.05
|  |  |  | Coincident | 28.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.1942
|  |  |  | Coincident | 29.1942
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.25267
|  |  |  | Coincident | 0.25267
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.8475
|  |  |  | Coincident | 28.8475
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.0241
|  |  |  | Coincident | 30.0241
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.8772
|  |  |  | Coincident | 25.8772
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.9327
|  |  |  | Coincident | 26.9327
| Kanmantoo 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.776
|  |  |  | Coincident | 1.776
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.817
|  |  |  | Coincident | 1.817
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.019604
|  |  |  | Coincident | 0.019604
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7943
|  |  |  | Coincident | 1.7943
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.8358
|  |  |  | Coincident | 1.8358
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.574
|  |  |  | Coincident | 1.574
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6104
|  |  |  | Coincident | 1.6104
| Keith 33kV | Substation Rating | MVA | Non-Coincident | 58.9
|  |  |  | Coincident | 58.9
|  | Raw Adjusted MD | MW | Non-Coincident | 21.434
|  |  |  | Coincident | 20.776
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.5753
|  |  |  | Coincident | 20.973
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.1036
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.7609
|  |  |  | Coincident | 24.0741
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 27.6599
|  |  |  | Coincident | 24.6767
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.3091
|  |  |  | Coincident | 21.7828
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.0274
|  |  |  | Coincident | 22.3281
| Kincraig 33kV | Substation Rating | MVA | Non-Coincident | 51.6
|  |  |  | Coincident | 51.6
|  | Raw Adjusted MD | MW | Non-Coincident | 21.251
|  |  |  | Coincident | 21.219
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.1344
|  |  |  | Coincident | 22.0887
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.23797
|  |  |  | Coincident | 0.13147
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.1054
|  |  |  | Coincident | 24.0691
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.1075
|  |  |  | Coincident | 25.0556
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.66
|  |  |  | Coincident | 21.6274
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.5605
|  |  |  | Coincident | 22.5138
| Leigh Creek South 33kV | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 0.972
|  |  |  | Coincident | 0.758
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.97521
|  |  |  | Coincident | 0.76141
|  | Date MD occurred |  | Non-Coincident | 2019-01-30
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0065295
|  |  |  | Coincident | 0.0065295
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.1111
|  |  |  | Coincident | 0.86647
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.1148
|  |  |  | Coincident | 0.87037
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.0201
|  |  |  | Coincident | 0.79548
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.0234
|  |  |  | Coincident | 0.79906
| Mannum 33kV | Substation Rating | MVA | Non-Coincident | 40
|  |  |  | Coincident | 40
|  | Raw Adjusted MD | MW | Non-Coincident | 12.862
|  |  |  | Coincident | 12.641
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.2047
|  |  |  | Coincident | 12.9187
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.20015
|  |  |  | Coincident | 0.11058
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.7538
|  |  |  | Coincident | 13.5175
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.1203
|  |  |  | Coincident | 13.8144
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.3588
|  |  |  | Coincident | 12.1465
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.6882
|  |  |  | Coincident | 12.4133
| Mobilong 33kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 38.532
|  |  |  | Coincident | 38.167
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.0782
|  |  |  | Coincident | 39.6577
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.4716
|  |  |  | Coincident | 0.26055
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.2951
|  |  |  | Coincident | 38.9229
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.872
|  |  |  | Coincident | 40.4431
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.044
|  |  |  | Coincident | 34.712
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.4502
|  |  |  | Coincident | 36.0678
| Mount Barker 66kV | Substation Rating | MVA | Non-Coincident | 361.6
|  |  |  | Coincident | 361.6
|  | Raw Adjusted MD | MW | Non-Coincident | 107.793
|  |  |  | Coincident | 107.793
|  | Raw Adjusted MD | MVA | Non-Coincident | 113.149
|  |  |  | Coincident | 113.149
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.9787
|  |  |  | Coincident | 0.9787
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 100.6357
|  |  |  | Coincident | 100.6357
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 105.636
|  |  |  | Coincident | 105.636
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 89.0525
|  |  |  | Coincident | 89.0525
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 93.4773
|  |  |  | Coincident | 93.4773
| Mount Gambier 33kV | Substation Rating | MVA | Non-Coincident | 63.3
|  |  |  | Coincident | 63.3
|  | Raw Adjusted MD | MW | Non-Coincident | 21.776
|  |  |  | Coincident | 20.432
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.3353
|  |  |  | Coincident | 20.879
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.86753
|  |  |  | Coincident | 0.10704
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.8245
|  |  |  | Coincident | 21.4158
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.4108
|  |  |  | Coincident | 21.8843
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.0902
|  |  |  | Coincident | 19.7885
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.6319
|  |  |  | Coincident | 20.2214
| Mount Gunson 33kV | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 0.13
|  |  |  | Coincident | 0.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.20153
|  |  |  | Coincident | 0.20504
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.15822
|  |  |  | Coincident | 0.12171
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.24529
|  |  |  | Coincident | 0.24955
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.14465
|  |  |  | Coincident | 0.11127
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.22425
|  |  |  | Coincident | 0.22815
| Neuroodla 33kV | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 0.969
|  |  |  | Coincident | 0.921
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.97182
|  |  |  | Coincident | 0.92447
|  | Date MD occurred |  | Non-Coincident | 2019-01-15
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.010743
|  |  |  | Coincident | 0.0059351
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.95651
|  |  |  | Coincident | 0.90913
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.9593
|  |  |  | Coincident | 0.91256
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.87219
|  |  |  | Coincident | 0.82899
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.87473
|  |  |  | Coincident | 0.83211
| North West Bend 66kV | Substation Rating | MVA | Non-Coincident | 73.6
|  |  |  | Coincident | 73.6
|  | Raw Adjusted MD | MW | Non-Coincident | 24.974
|  |  |  | Coincident | 19.922
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.4539
|  |  |  | Coincident | 20.618
|  | Date MD occurred |  | Non-Coincident | 2019-01-25
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.16161
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.5899
|  |  |  | Coincident | 18.8179
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.9878
|  |  |  | Coincident | 19.4754
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.9713
|  |  |  | Coincident | 17.5267
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.2733
|  |  |  | Coincident | 18.1391
| Penola West 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 7.745
|  |  |  | Coincident | 5.595
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.26
|  |  |  | Coincident | 5.7556
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 22:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.031094
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.1312
|  |  |  | Coincident | 5.874
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.6719
|  |  |  | Coincident | 6.0426
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.2706
|  |  |  | Coincident | 5.2523
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.7541
|  |  |  | Coincident | 5.403
| Port Lincoln Terminal 33kV | Substation Rating | MVA | Non-Coincident | 101.4
|  |  |  | Coincident | 101.4
|  | Raw Adjusted MD | MW | Non-Coincident | 35.297
|  |  |  | Coincident | 33.975
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.9045
|  |  |  | Coincident | 34.6243
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.4285
|  |  |  | Coincident | 0.28257
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.9344
|  |  |  | Coincident | 30.7383
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.484
|  |  |  | Coincident | 31.3258
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.5065
|  |  |  | Coincident | 27.4388
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.9972
|  |  |  | Coincident | 27.9632
| Snuggery Industrial 33kV | Substation Rating | MVA | Non-Coincident | 86.4
|  |  |  | Coincident | 86.4
|  | Raw Adjusted MD | MW | Non-Coincident | 22.4399
|  |  |  | Coincident | -6.102
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.3352
|  |  |  | Coincident | 7.8077
|  | Date MD occurred |  | Non-Coincident | 2019-03-14
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.5255
|  |  |  | Coincident | 11.3152
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 82.4756
|  |  |  | Coincident | 11.3299
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.5889
|  |  |  | Coincident | 10.9437
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 79.7676
|  |  |  | Coincident | 10.9579
| Snuggery Rural 33kV | Substation Rating | MVA | Non-Coincident | 28.8
|  |  |  | Coincident | 28.8
|  | Raw Adjusted MD | MW | Non-Coincident | 14.868
|  |  |  | Coincident | 14.868
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.3066
|  |  |  | Coincident | 15.3066
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11977
|  |  |  | Coincident | 0.11977
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.0386
|  |  |  | Coincident | 14.0386
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.4527
|  |  |  | Coincident | 14.4527
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.4525
|  |  |  | Coincident | 12.4525
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.8199
|  |  |  | Coincident | 12.8199
| Stony Point 11kV | Substation Rating | MVA | Non-Coincident | 2.5
|  |  |  | Coincident | 2.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.132
|  |  |  | Coincident | 0.095
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.13274
|  |  |  | Coincident | 0.096177
|  | Date MD occurred |  | Non-Coincident | 2019-01-21
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 22:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0010523
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.14649
|  |  |  | Coincident | 0.10543
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.14731
|  |  |  | Coincident | 0.10673
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.13961
|  |  |  | Coincident | 0.10047
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.14039
|  |  |  | Coincident | 0.10172
| Tailem Bend 33kV | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 25.921
|  |  |  | Coincident | 25.339
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.4952
|  |  |  | Coincident | 25.7992
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.13379
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.4518
|  |  |  | Coincident | 26.8355
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.0599
|  |  |  | Coincident | 27.3228
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.9592
|  |  |  | Coincident | 24.3988
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.5121
|  |  |  | Coincident | 24.8419
| Templers 33kV | Substation Rating | MVA | Non-Coincident | 147.6
|  |  |  | Coincident | 147.6
|  | Raw Adjusted MD | MW | Non-Coincident | 31.609
|  |  |  | Coincident | 30.912
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.7397
|  |  |  | Coincident | 31.9914
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.25295
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.0286
|  |  |  | Coincident | 33.2783
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.2459
|  |  |  | Coincident | 34.4403
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.153
|  |  |  | Coincident | 30.4661
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.2674
|  |  |  | Coincident | 31.5299
| Waterloo 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 9.212
|  |  |  | Coincident | 9.212
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.3813
|  |  |  | Coincident | 9.3813
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.081774
|  |  |  | Coincident | 0.081774
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.2205
|  |  |  | Coincident | 10.2205
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.4082
|  |  |  | Coincident | 10.4082
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.1257
|  |  |  | Coincident | 9.1257
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.2933
|  |  |  | Coincident | 9.2933
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Whyalla Central 33kV | Substation Rating | MVA | Non-Coincident | 240
|  |  |  | Coincident | 240
|  | Raw Adjusted MD | MW | Non-Coincident | 71.464
|  |  |  | Coincident | 49.524
|  | Raw Adjusted MD | MVA | Non-Coincident | 77.4283
|  |  |  | Coincident | 52.8359
|  | Date MD occurred |  | Non-Coincident | 2019-03-14
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.35295
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 74.71
|  |  |  | Coincident | 51.7734
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 80.9452
|  |  |  | Coincident | 55.2357
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 70.0043
|  |  |  | Coincident | 48.5125
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 75.8468
|  |  |  | Coincident | 51.7567
| Wudinna 66kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 15.332
|  |  |  | Coincident | 11.61
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.3323
|  |  |  | Coincident | 11.7422
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.12397
|  |  |  | Coincident | 0.12397
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.8914
|  |  |  | Coincident | 12.0336
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.8916
|  |  |  | Coincident | 12.1706
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.0889
|  |  |  | Coincident | 10.6687
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.0892
|  |  |  | Coincident | 10.7902
| Yadnarie 66kV | Substation Rating | MVA | Non-Coincident | 46.4
|  |  |  | Coincident | 46.4
|  | Raw Adjusted MD | MW | Non-Coincident | 8.298
|  |  |  | Coincident | 8.278
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.5136
|  |  |  | Coincident | 8.4971
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.12262
|  |  |  | Coincident | 0.067743
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.303
|  |  |  | Coincident | 8.283
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.5188
|  |  |  | Coincident | 8.5022
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.407
|  |  |  | Coincident | 7.3892
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.5995
|  |  |  | Coincident | 7.5847
| Port Pirie Bungama 33kV | Substation Rating | MVA | Non-Coincident | 192
|  |  |  | Coincident | 192
|  | Raw Adjusted MD | MW | Non-Coincident | 67.311
|  |  |  | Coincident | 54.528
|  | Raw Adjusted MD | MVA | Non-Coincident | 69.6008
|  |  |  | Coincident | 58.497
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.41883
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 64.5029
|  |  |  | Coincident | 52.2532
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.6972
|  |  |  | Coincident | 56.0566
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 60.7169
|  |  |  | Coincident | 49.1862
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 62.7824
|  |  |  | Coincident | 52.7663
| Metro North 66kV | Substation Rating | MVA | Non-Coincident | 870
|  |  |  | Coincident | 870
|  | Raw Adjusted MD | MW | Non-Coincident | 331.56
|  |  |  | Coincident | 330.462
|  | Raw Adjusted MD | MVA | Non-Coincident | 335.5503
|  |  |  | Coincident | 333.677
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 1.9981
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 351.0664
|  |  |  | Coincident | 348.8541
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 396.8822
|  |  |  | Coincident | 386.9443
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 317.505
|  |  |  | Coincident | 315.5041
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 358.9409
|  |  |  | Coincident | 349.953
| Metro South 66kV | Substation Rating | MVA | Non-Coincident | 1527
|  |  |  | Coincident | 1527
|  | Raw Adjusted MD | MW | Non-Coincident | 729.2282
|  |  |  | Coincident | 729.2282
|  | Raw Adjusted MD | MVA | Non-Coincident | 734.3663
|  |  |  | Coincident | 734.3663
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.6017
|  |  |  | Coincident | 4.6017
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 682.9402
|  |  |  | Coincident | 682.9402
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 698.7852
|  |  |  | Coincident | 698.7852
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 599.4304
|  |  |  | Coincident | 599.4304
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 613.3378
|  |  |  | Coincident | 613.3378
| Metro East 66kV | Substation Rating | MVA | Non-Coincident | 1650
|  |  |  | Coincident | 1650
|  | Raw Adjusted MD | MW | Non-Coincident | 703.648
|  |  |  | Coincident | 703.648
|  | Raw Adjusted MD | MVA | Non-Coincident | 711.0055
|  |  |  | Coincident | 711.0055
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.3629
|  |  |  | Coincident | 3.3629
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 760.2591
|  |  |  | Coincident | 760.2591
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 768.6635
|  |  |  | Coincident | 768.6635
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 677.4983
|  |  |  | Coincident | 677.4983
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 684.9878
|  |  |  | Coincident | 684.9878
| Metro West 66kV | Substation Rating | MVA | Non-Coincident | 885
|  |  |  | Coincident | 885
|  | Raw Adjusted MD | MW | Non-Coincident | 443.08
|  |  |  | Coincident | 443.08
|  | Raw Adjusted MD | MVA | Non-Coincident | 443.661
|  |  |  | Coincident | 443.661
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.9723
|  |  |  | Coincident | 1.9723
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 431.5389
|  |  |  | Coincident | 424.0705
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 432.0759
|  |  |  | Coincident | 424.5982
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 389.4064
|  |  |  | Coincident | 382.6672
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 389.891
|  |  |  | Coincident | 383.1434
| ACR 66kV | Substation Rating | MVA | Non-Coincident | 525
|  |  |  | Coincident | 525
|  | Raw Adjusted MD | MW | Non-Coincident | 185.8979
|  |  |  | Coincident | 120.0431
|  | Raw Adjusted MD | MVA | Non-Coincident | 191.0102
|  |  |  | Coincident | 122.1755
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.7116
|  |  |  | Coincident | 0.071779
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 193.6621
|  |  |  | Coincident | 127.2165
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 198.9673
|  |  |  | Coincident | 129.2289
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 180.5188
|  |  |  | Coincident | 118.5827
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 185.4639
|  |  |  | Coincident | 120.4585
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2018-19
ZONE SUBSTATION |  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Aldgate 11kV | Substation Rating | MVA | Non-Coincident | 12.5808
|  |  |  | Coincident | 12.5808
|  | Raw Adjusted MD | MW | Non-Coincident | 7.4007
|  |  |  | Coincident | 7.2103
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.4179
|  |  |  | Coincident | 7.2261
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11318
|  |  |  | Coincident | 0.062529
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.528
|  |  |  | Coincident | 6.5149
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.5431
|  |  |  | Coincident | 6.5296
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.9758
|  |  |  | Coincident | 5.9639
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.9896
|  |  |  | Coincident | 5.9773
| Aldinga 11kV | Substation Rating | MVA | Non-Coincident | 33.2
|  |  |  | Coincident | 33.2
|  | Raw Adjusted MD | MW | Non-Coincident | 21.0235
|  |  |  | Coincident | 20.9341
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.5518
|  |  |  | Coincident | 21.4896
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.82722
|  |  |  | Coincident | 0.16363
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.4275
|  |  |  | Coincident | 20.384
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.9551
|  |  |  | Coincident | 20.9249
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.6605
|  |  |  | Coincident | 17.6229
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.1166
|  |  |  | Coincident | 18.0905
| Allendale East 11kV | Substation Rating | MVA | Non-Coincident | 6.8
|  |  |  | Coincident | 6.8
|  | Raw Adjusted MD | MW | Non-Coincident | 3.7744
|  |  |  | Coincident | 2.881
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.1477
|  |  |  | Coincident | 3.1659
|  | Date MD occurred |  | Non-Coincident | 2019-02-05
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.02061
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.6349
|  |  |  | Coincident | 3.3038
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.9944
|  |  |  | Coincident | 3.6306
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.4346
|  |  |  | Coincident | 3.1218
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.7743
|  |  |  | Coincident | 3.4305
| Alma 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.096153
|  |  |  | Coincident | 0.096153
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.099594
|  |  |  | Coincident | 0.099594
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 2.88e-05
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.096153
|  |  |  | Coincident | 0.096153
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.099594
|  |  |  | Coincident | 0.099594
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.088415
|  |  |  | Coincident | 0.088415
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.091579
|  |  |  | Coincident | 0.091579
| American River 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.484
|  |  |  | Coincident | 0.484
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.48947
|  |  |  | Coincident | 0.48947
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0081664
|  |  |  | Coincident | 0.0081664
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.46544
|  |  |  | Coincident | 0.44332
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.47085
|  |  |  | Coincident | 0.44885
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.40914
|  |  |  | Coincident | 0.38969
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.41389
|  |  |  | Coincident | 0.39455
| Angaston 11kV | Substation Rating | MVA | Non-Coincident | 28.956
|  |  |  | Coincident | 28.956
|  | Raw Adjusted MD | MW | Non-Coincident | 14.6018
|  |  |  | Coincident | 12.9958
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.6227
|  |  |  | Coincident | 13.0109
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.45896
|  |  |  | Coincident | 0.090783
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.7169
|  |  |  | Coincident | 13.2614
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.7317
|  |  |  | Coincident | 13.2733
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.8087
|  |  |  | Coincident | 12.443
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.8226
|  |  |  | Coincident | 12.4542
| Angle Vale 11kV | Substation Rating | MVA | Non-Coincident | 27.3493
|  |  |  | Coincident | 27.3493
|  | Raw Adjusted MD | MW | Non-Coincident | 18.985
|  |  |  | Coincident | 18.6913
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.866
|  |  |  | Coincident | 19.5371
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.17009
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.5598
|  |  |  | Coincident | 19.4162
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.4742
|  |  |  | Coincident | 20.306
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.0045
|  |  |  | Coincident | 17.8723
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.8462
|  |  |  | Coincident | 18.6913
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Ardrossan 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.404
|  |  |  | Coincident | 2.404
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.4725
|  |  |  | Coincident | 2.4716
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.038492
|  |  |  | Coincident | 0.021266
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.9689
|  |  |  | Coincident | 1.9448
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0247
|  |  |  | Coincident | 2.0016
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.7764
|  |  |  | Coincident | 1.7546
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8266
|  |  |  | Coincident | 1.8058
| Arno Bay 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.67188
|  |  |  | Coincident | 0.61384
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.72781
|  |  |  | Coincident | 0.66493
|  | Date MD occurred |  | Non-Coincident | 2018-12-07
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.1877
|  |  |  | Coincident | 0.0052956
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.67674
|  |  |  | Coincident | 0.67674
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.69449
|  |  |  | Coincident | 0.69449
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.58614
|  |  |  | Coincident | 0.58614
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.60151
|  |  |  | Coincident | 0.60151
| Ascot Park 11kV | Substation Rating | MVA | Non-Coincident | 27.025
|  |  |  | Coincident | 27.025
|  | Raw Adjusted MD | MW | Non-Coincident | 19.3917
|  |  |  | Coincident | 19.1534
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.6569
|  |  |  | Coincident | 19.4268
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.11208
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.645
|  |  |  | Coincident | 18.301
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.9098
|  |  |  | Coincident | 18.5563
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.1362
|  |  |  | Coincident | 15.8385
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.3654
|  |  |  | Coincident | 16.0595
| Athol Park 11kV | Substation Rating | MVA | Non-Coincident | 26.5066
|  |  |  | Coincident | 26.5066
|  | Raw Adjusted MD | MW | Non-Coincident | 17.2953
|  |  |  | Coincident | 16.5511
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.8345
|  |  |  | Coincident | 17.334
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.1109
|  |  |  | Coincident | 0.11263
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.5649
|  |  |  | Coincident | 18.1229
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.2111
|  |  |  | Coincident | 18.995
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.745
|  |  |  | Coincident | 16.3464
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.2299
|  |  |  | Coincident | 17.133
| Auburn 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 3
|  |  |  | Coincident | 2.821
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.1417
|  |  |  | Coincident | 2.966
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.23257
|  |  |  | Coincident | 0.028697
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.1454
|  |  |  | Coincident | 3.0486
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.304
|  |  |  | Coincident | 3.2091
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.8788
|  |  |  | Coincident | 2.7902
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.0239
|  |  |  | Coincident | 2.9371
| Balaklava 7.6kV | Substation Rating | MVA | Non-Coincident | 5
|  |  |  | Coincident | 5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.94
|  |  |  | Coincident | 2.94
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.0906
|  |  |  | Coincident | 3.0906
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.022391
|  |  |  | Coincident | 0.022391
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.9394
|  |  |  | Coincident | 2.9239
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0899
|  |  |  | Coincident | 3.0881
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.646
|  |  |  | Coincident | 2.6321
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.7815
|  |  |  | Coincident | 2.7799
| Balhannah 33kV | Substation Rating | MVA | Non-Coincident | 35.4
|  |  |  | Coincident | 35.4
|  | Raw Adjusted MD | MW | Non-Coincident | 24.3904
|  |  |  | Coincident | 24.3904
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.5778
|  |  |  | Coincident | 25.5778
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.24296
|  |  |  | Coincident | 0.24296
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.9277
|  |  |  | Coincident | 20.9277
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.9463
|  |  |  | Coincident | 21.9463
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.0876
|  |  |  | Coincident | 19.0876
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.0166
|  |  |  | Coincident | 20.0166
| Balhannah Filtration Plant 11kV | Substation Rating | MVA | Non-Coincident | 1.5
|  |  |  | Coincident | 1.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.25005
|  |  |  | Coincident | 0.042112
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.25321
|  |  |  | Coincident | 0.042446
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 3:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.26225
|  |  |  | Coincident | 0.032618
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.26557
|  |  |  | Coincident | 0.032865
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.23865
|  |  |  | Coincident | 0.029682
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.24166
|  |  |  | Coincident | 0.029908
| Baroota Town 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.26
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.2613
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 2019-03-30
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.6219e-05
|  |  |  | Coincident | 0.0010719
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.26605
|  |  |  | Coincident | 0.26605
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.26742
|  |  |  | Coincident | 0.26742
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.24161
|  |  |  | Coincident | 0.24161
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.24286
|  |  |  | Coincident | 0.24286
| Barossa South TF1 11kV | Substation Rating | MVA | Non-Coincident | 8.9062
|  |  |  | Coincident | 8.9062
|  | Raw Adjusted MD | MW | Non-Coincident | 2.6
|  |  |  | Coincident | 2.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.6161
|  |  |  | Coincident | 2.1719
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.017443
|  |  |  | Coincident | 0.015206
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.7244
|  |  |  | Coincident | 2.2624
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.737
|  |  |  | Coincident | 2.2644
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4884
|  |  |  | Coincident | 2.0665
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4999
|  |  |  | Coincident | 2.0683
| Barossa South TF2 11kV | Substation Rating | MVA | Non-Coincident | 8.1
|  |  |  | Coincident | 8.1
|  | Raw Adjusted MD | MW | Non-Coincident | 3.48
|  |  |  | Coincident | 2.23
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.8643
|  |  |  | Coincident | 2.4522
|  | Date MD occurred |  | Non-Coincident | 2019-02-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 23:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00084672
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.6966
|  |  |  | Coincident | 2.3204
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.0807
|  |  |  | Coincident | 2.5517
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.3893
|  |  |  | Coincident | 2.1275
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.7414
|  |  |  | Coincident | 2.3395
| Beachport 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.244
|  |  |  | Coincident | 1.244
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.2662
|  |  |  | Coincident | 1.2662
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.012821
|  |  |  | Coincident | 0.012821
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.2095
|  |  |  | Coincident | 1.1764
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.2311
|  |  |  | Coincident | 1.1997
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.0685
|  |  |  | Coincident | 1.0393
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.0876
|  |  |  | Coincident | 1.0598
| Belvedere Road 7.6kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.123
|  |  |  | Coincident | 0.096
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.13599
|  |  |  | Coincident | 0.10439
|  | Date MD occurred |  | Non-Coincident | 2018-12-06
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 5:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00015945
|  |  |  | Coincident | 0.00032868
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.16154
|  |  |  | Coincident | 0.095871
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.1786
|  |  |  | Coincident | 0.10521
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.1449
|  |  |  | Coincident | 0.085995
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.1602
|  |  |  | Coincident | 0.094374
| Berri 11kV | Substation Rating | MVA | Non-Coincident | 28
|  |  |  | Coincident | 28
|  | Raw Adjusted MD | MW | Non-Coincident | 11.2531
|  |  |  | Coincident | 11.1638
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.8411
|  |  |  | Coincident | 11.6178
|  | Date MD occurred |  | Non-Coincident | 2019-01-16
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.3866
|  |  |  | Coincident | 0.12204
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.6481
|  |  |  | Coincident | 10.6158
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.1214
|  |  |  | Coincident | 10.9991
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.4402
|  |  |  | Coincident | 9.5149
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.8644
|  |  |  | Coincident | 9.8584
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Binnies 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 0.906
|  |  |  | Coincident | 0.432
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.94538
|  |  |  | Coincident | 0.43732
|  | Date MD occurred |  | Non-Coincident | 2018-11-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.003468
|  |  |  | Coincident | 0.000108
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.9511
|  |  |  | Coincident | 0.45036
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.99229
|  |  |  | Coincident | 0.45851
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.86968
|  |  |  | Coincident | 0.4118
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.90734
|  |  |  | Coincident | 0.41926
| Birdwood 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.701
|  |  |  | Coincident | 2.629
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.8
|  |  |  | Coincident | 2.7274
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.16235
|  |  |  | Coincident | 0.032114
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.6012
|  |  |  | Coincident | 2.4837
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.6966
|  |  |  | Coincident | 2.5803
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4651
|  |  |  | Coincident | 2.3537
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.5554
|  |  |  | Coincident | 2.4452
| Black Point 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.41848
|  |  |  | Coincident | 0.41848
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.42531
|  |  |  | Coincident | 0.42531
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0060479
|  |  |  | Coincident | 0.0033413
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.41848
|  |  |  | Coincident | 0.41848
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.42531
|  |  |  | Coincident | 0.42531
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.38178
|  |  |  | Coincident | 0.38178
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.38801
|  |  |  | Coincident | 0.38801
| Blackpool 11kV | Substation Rating | MVA | Non-Coincident | 24
|  |  |  | Coincident | 24
|  | Raw Adjusted MD | MW | Non-Coincident | 16.0952
|  |  |  | Coincident | 16.0952
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.4929
|  |  |  | Coincident | 16.4929
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.10714
|  |  |  | Coincident | 0.10714
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.243
|  |  |  | Coincident | 16.243
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.612
|  |  |  | Coincident | 16.612
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.1218
|  |  |  | Coincident | 14.1218
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.4426
|  |  |  | Coincident | 14.4426
| Blackwood 11kV | Substation Rating | MVA | Non-Coincident | 57.8756
|  |  |  | Coincident | 57.8756
|  | Raw Adjusted MD | MW | Non-Coincident | 29.9368
|  |  |  | Coincident | 29.9368
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.53
|  |  |  | Coincident | 30.5776
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.40012
|  |  |  | Coincident | 0.22106
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.567
|  |  |  | Coincident | 29.567
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.1761
|  |  |  | Coincident | 30.1761
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.0433
|  |  |  | Coincident | 25.0433
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.5592
|  |  |  | Coincident | 25.5592
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Booleroo Centre 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.59713
|  |  |  | Coincident | 0.52271
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.64207
|  |  |  | Coincident | 0.56205
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.026876
|  |  |  | Coincident | 0.0053161
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.52021
|  |  |  | Coincident | 0.45753
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.55936
|  |  |  | Coincident | 0.49197
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.47329
|  |  |  | Coincident | 0.41626
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.50891
|  |  |  | Coincident | 0.4476
| Boothby 33kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.72743
|  |  |  | Coincident | 0.56091
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.79068
|  |  |  | Coincident | 0.60968
|  | Date MD occurred |  | Non-Coincident | 2018-12-08
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.25066
|  |  |  | Coincident | 0.0072175
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.81974
|  |  |  | Coincident | 0.81813
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.84498
|  |  |  | Coincident | 0.84499
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.73062
|  |  |  | Coincident | 0.72919
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.75312
|  |  |  | Coincident | 0.75313
| Booyoolie 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.022307
|  |  |  | Coincident | 0.022307
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.023065
|  |  |  | Coincident | 0.023065
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00014382
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.022307
|  |  |  | Coincident | 0.022307
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.023065
|  |  |  | Coincident | 0.023065
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.020797
|  |  |  | Coincident | 0.020797
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.021505
|  |  |  | Coincident | 0.021505
| Bordertown 11kV | Substation Rating | MVA | Non-Coincident | 13.4
|  |  |  | Coincident | 13.4
|  | Raw Adjusted MD | MW | Non-Coincident | 9.8889
|  |  |  | Coincident | 9.6471
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.1747
|  |  |  | Coincident | 9.9573
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11115
|  |  |  | Coincident | 0.061409
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.3575
|  |  |  | Coincident | 11.3557
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.6736
|  |  |  | Coincident | 11.8043
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.9192
|  |  |  | Coincident | 10.133
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.2013
|  |  |  | Coincident | 10.5332
| Brinkworth Town 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.884
|  |  |  | Coincident | 0.884
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.91949
|  |  |  | Coincident | 0.91949
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.013461
|  |  |  | Coincident | 0.0074371
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.85799
|  |  |  | Coincident | 0.8478
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.89244
|  |  |  | Coincident | 0.88013
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.78157
|  |  |  | Coincident | 0.77228
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.81295
|  |  |  | Coincident | 0.80173
| Brukunga 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.54
|  |  |  | Coincident | 0.54
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.54575
|  |  |  | Coincident | 0.54575
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.010462
|  |  |  | Coincident | 0.0057798
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.43505
|  |  |  | Coincident | 0.43505
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.43968
|  |  |  | Coincident | 0.43968
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.39622
|  |  |  | Coincident | 0.39622
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.40044
|  |  |  | Coincident | 0.40044
| Bungama Napperby 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.87708
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.9431
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.01739
|  |  |  | Coincident | 0.014688
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.99518
|  |  |  | Coincident | 0.96994
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.0217
|  |  |  | Coincident | 0.99355
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.93746
|  |  |  | Coincident | 0.91368
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.96245
|  |  |  | Coincident | 0.93592
| Burnside 11kV | Substation Rating | MVA | Non-Coincident | 31.2
|  |  |  | Coincident | 31.2
|  | Raw Adjusted MD | MW | Non-Coincident | 13.34
|  |  |  | Coincident | 13.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.6798
|  |  |  | Coincident | 13.6471
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.081637
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.3878
|  |  |  | Coincident | 12.3785
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.6977
|  |  |  | Coincident | 12.6825
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.1078
|  |  |  | Coincident | 11.0995
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.3856
|  |  |  | Coincident | 11.372
| Burra TF1 11kV | Substation Rating | MVA | Non-Coincident | 5.7
|  |  |  | Coincident | 5.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.2709
|  |  |  | Coincident | 1.0486
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.6371
|  |  |  | Coincident | 1.4235
|  | Date MD occurred |  | Non-Coincident | 2019-03-09
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 22:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7058
|  |  |  | Coincident | 1.2697
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.2223
|  |  |  | Coincident | 1.7945
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.5693
|  |  |  | Coincident | 1.1681
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.0445
|  |  |  | Coincident | 1.6509
| Burra TF2 11kV | Substation Rating | MVA | Non-Coincident | 5.7
|  |  |  | Coincident | 5.7
|  | Raw Adjusted MD | MW | Non-Coincident | 2.0805
|  |  |  | Coincident | 1.9721
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.0834
|  |  |  | Coincident | 1.9751
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.14643
|  |  |  | Coincident | 0.018068
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.0246
|  |  |  | Coincident | 2.0167
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0268
|  |  |  | Coincident | 2.0194
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.832
|  |  |  | Coincident | 1.8249
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.834
|  |  |  | Coincident | 1.8273
| Cadell 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.27
|  |  |  | Coincident | 0.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.3602
|  |  |  | Coincident | 0.96137
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 22:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.012996
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.201
|  |  |  | Coincident | 0.80367
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.2859
|  |  |  | Coincident | 0.84734
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.074
|  |  |  | Coincident | 0.71867
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.1499
|  |  |  | Coincident | 0.75772
| Caloote 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.5893
|  |  |  | Coincident | 1.4448
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.7465
|  |  |  | Coincident | 1.5877
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.015902
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.4429
|  |  |  | Coincident | 1.378
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.5856
|  |  |  | Coincident | 1.5143
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.3215
|  |  |  | Coincident | 1.2621
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.4522
|  |  |  | Coincident | 1.387
| Caltowie 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.10277
|  |  |  | Coincident | 0.101
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.1105
|  |  |  | Coincident | 0.1086
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0017899
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.092892
|  |  |  | Coincident | 0.083337
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.099788
|  |  |  | Coincident | 0.086215
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.088851
|  |  |  | Coincident | 0.079712
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.095448
|  |  |  | Coincident | 0.082465
| Cambrai 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.90464
|  |  |  | Coincident | 0.90464
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.92875
|  |  |  | Coincident | 0.92875
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015734
|  |  |  | Coincident | 0.0086924
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.90464
|  |  |  | Coincident | 0.90464
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.92875
|  |  |  | Coincident | 0.92875
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.81778
|  |  |  | Coincident | 0.81778
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.83957
|  |  |  | Coincident | 0.83957
| Campbell Park 11kV | Substation Rating | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.95
|  | Raw Adjusted MD | MW | Non-Coincident | 1.4286
|  |  |  | Coincident | 1.4286
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.4603
|  |  |  | Coincident | 1.4603
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0021037
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.4286
|  |  |  | Coincident | 1.4286
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.4603
|  |  |  | Coincident | 1.4603
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.3279
|  |  |  | Coincident | 1.3279
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.3573
|  |  |  | Coincident | 1.3573
| Campbelltown 11kV | Substation Rating | MVA | Non-Coincident | 73.6
|  |  |  | Coincident | 73.6
|  | Raw Adjusted MD | MW | Non-Coincident | 50.0473
|  |  |  | Coincident | 50.0473
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.4881
|  |  |  | Coincident | 51.4881
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.28483
|  |  |  | Coincident | 0.28483
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 48.4419
|  |  |  | Coincident | 48.1538
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.8491
|  |  |  | Coincident | 49.5607
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.4123
|  |  |  | Coincident | 43.1541
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.6734
|  |  |  | Coincident | 44.4149
| Cape Jervis 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.5792
|  |  |  | Coincident | 0.5792
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.5792
|  |  |  | Coincident | 0.5792
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0074956
|  |  |  | Coincident | 0.0074956
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.53864
|  |  |  | Coincident | 0.53291
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.54165
|  |  |  | Coincident | 0.53692
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.49034
|  |  |  | Coincident | 0.48512
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.49308
|  |  |  | Coincident | 0.48878
| Cape Jervis 33kV | Substation Rating | MVA | Non-Coincident | 40
|  |  |  | Coincident | 40
|  | Raw Adjusted MD | MW | Non-Coincident | 9.1041
|  |  |  | Coincident | 9.1041
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.0841
|  |  |  | Coincident | 13.0841
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.065956
|  |  |  | Coincident | 0.065956
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.8861
|  |  |  | Coincident | 9.0663
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.8979
|  |  |  | Coincident | 12.4868
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.7666
|  |  |  | Coincident | 8.1339
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.7772
|  |  |  | Coincident | 11.2027
| Caralue 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 2.1756
|  |  |  | Coincident | 2.1615
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.2803
|  |  |  | Coincident | 2.2586
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.058251
|  |  |  | Coincident | 0.011522
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.3922
|  |  |  | Coincident | 2.3767
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.5073
|  |  |  | Coincident | 2.4835
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.1753
|  |  |  | Coincident | 2.1612
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.28
|  |  |  | Coincident | 2.2583
| Cavan 11kV | Substation Rating | MVA | Non-Coincident | 58.2264
|  |  |  | Coincident | 58.2264
|  | Raw Adjusted MD | MW | Non-Coincident | 34.29
|  |  |  | Coincident | 33.68
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.7358
|  |  |  | Coincident | 35.5989
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.4259
|  |  |  | Coincident | 0.093011
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.94
|  |  |  | Coincident | 36.2824
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.6206
|  |  |  | Coincident | 38.3734
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.8561
|  |  |  | Coincident | 33.2534
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.313
|  |  |  | Coincident | 35.1699
| CBD 33kV | Substation Rating | MVA | Non-Coincident | 47.6
|  |  |  | Coincident | 47.6
|  | Raw Adjusted MD | MW | Non-Coincident | 17.378
|  |  |  | Coincident | 7.9539
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.9202
|  |  |  | Coincident | 8.0088
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.021593
|  |  |  | Coincident | 0.00057312
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.1342
|  |  |  | Coincident | 18.1342
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.6622
|  |  |  | Coincident | 18.6622
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.0417
|  |  |  | Coincident | 17.0417
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.5379
|  |  |  | Coincident | 17.5379
| Ceduna 11kV | Substation Rating | MVA | Non-Coincident | 14.2
|  |  |  | Coincident | 14.2
|  | Raw Adjusted MD | MW | Non-Coincident | 6.6964
|  |  |  | Coincident | 4.8262
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.882
|  |  |  | Coincident | 4.9727
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.58861
|  |  |  | Coincident | 0.048379
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.4062
|  |  |  | Coincident | 6.4062
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.5838
|  |  |  | Coincident | 6.5838
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.895
|  |  |  | Coincident | 5.895
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.0584
|  |  |  | Coincident | 6.0584
| Chain of Ponds 11kV | Substation Rating | MVA | Non-Coincident | 0.6175
|  |  |  | Coincident | 0.6175
|  | Raw Adjusted MD | MW | Non-Coincident | 0.48605
|  |  |  | Coincident | 0.41582
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.50108
|  |  |  | Coincident | 0.42868
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.047059
|  |  |  | Coincident | 0.0038678
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.47386
|  |  |  | Coincident | 0.43468
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.48857
|  |  |  | Coincident | 0.44916
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.44401
|  |  |  | Coincident | 0.4073
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.4578
|  |  |  | Coincident | 0.42086
| Cheltenham 11kV | Substation Rating | MVA | Non-Coincident | 29.9
|  |  |  | Coincident | 29.9
|  | Raw Adjusted MD | MW | Non-Coincident | 10.55
|  |  |  | Coincident | 10.38
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.6691
|  |  |  | Coincident | 10.4951
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.063097
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.1605
|  |  |  | Coincident | 10.0783
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.2732
|  |  |  | Coincident | 10.1891
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.8391
|  |  |  | Coincident | 8.7676
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.9372
|  |  |  | Coincident | 8.864
| Cheltenham 33kV | Substation Rating | MVA | Non-Coincident | 19
|  |  |  | Coincident | 19
|  | Raw Adjusted MD | MW | Non-Coincident | 3.3487
|  |  |  | Coincident | 0.7155
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.8383
|  |  |  | Coincident | 0.78129
|  | Date MD occurred |  | Non-Coincident | 2019-03-18
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 11:00
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0498
|  |  |  | Coincident | 0.0018
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.2948
|  |  |  | Coincident | 0.95239
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.8403
|  |  |  | Coincident | 1.06
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.1451
|  |  |  | Coincident | 0.90912
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.6658
|  |  |  | Coincident | 1.0118
| Clare 11kV | Substation Rating | MVA | Non-Coincident | 12.6
|  |  |  | Coincident | 12.6
|  | Raw Adjusted MD | MW | Non-Coincident | 9.9438
|  |  |  | Coincident | 9.6342
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.3813
|  |  |  | Coincident | 10.0816
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30
|  |  |  | Coincident | 20:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.62502
|  |  |  | Coincident | 0.077122
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.6111
|  |  |  | Coincident | 9.6111
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.0808
|  |  |  | Coincident | 10.0808
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.6982
|  |  |  | Coincident | 8.6982
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.1233
|  |  |  | Coincident | 9.1233
| Clarence Gardens 11kV | Substation Rating | MVA | Non-Coincident | 35.9
|  |  |  | Coincident | 35.9
|  | Raw Adjusted MD | MW | Non-Coincident | 19.29
|  |  |  | Coincident | 19.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.6627
|  |  |  | Coincident | 19.4985
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.11974
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.7744
|  |  |  | Coincident | 18.6765
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.142
|  |  |  | Coincident | 19.0086
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.4349
|  |  |  | Coincident | 16.3492
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.7567
|  |  |  | Coincident | 16.6399
| Clarendon 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 3.2594
|  |  |  | Coincident | 3.1701
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.3469
|  |  |  | Coincident | 3.26
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.062119
|  |  |  | Coincident | 0.034319
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.1336
|  |  |  | Coincident | 3.1336
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.2151
|  |  |  | Coincident | 3.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.6903
|  |  |  | Coincident | 2.6903
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.7603
|  |  |  | Coincident | 2.7645
| Clearview 11kV | Substation Rating | MVA | Non-Coincident | 26.5973
|  |  |  | Coincident | 26.5973
|  | Raw Adjusted MD | MW | Non-Coincident | 24.9877
|  |  |  | Coincident | 24.3279
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.4466
|  |  |  | Coincident | 24.7371
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.16325
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.3513
|  |  |  | Coincident | 22.2851
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.7801
|  |  |  | Coincident | 22.6727
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.8511
|  |  |  | Coincident | 19.8991
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.2339
|  |  |  | Coincident | 20.2452
| Cleve 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.6293
|  |  |  | Coincident | 2.5061
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.7223
|  |  |  | Coincident | 2.5881
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.1263
|  |  |  | Coincident | 0.024981
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.6289
|  |  |  | Coincident | 2.5579
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.7275
|  |  |  | Coincident | 2.6419
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.2992
|  |  |  | Coincident | 2.2371
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.3854
|  |  |  | Coincident | 2.3106
| Cleve 33kV | Substation Rating | MVA | Non-Coincident | 17.8
|  |  |  | Coincident | 17.8
|  | Raw Adjusted MD | MW | Non-Coincident | 2.4
|  |  |  | Coincident | 2.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.4021
|  |  |  | Coincident | 2.4021
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.19114
|  |  |  | Coincident | 0.023585
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.4591
|  |  |  | Coincident | 2.4591
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.4613
|  |  |  | Coincident | 2.4613
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.1451
|  |  |  | Coincident | 2.1451
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.1469
|  |  |  | Coincident | 2.1469
| Coffin Bay 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.623
|  |  |  | Coincident | 0.937
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.6542
|  |  |  | Coincident | 0.97348
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.029062
|  |  |  | Coincident | 0.016056
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.2592
|  |  |  | Coincident | 0.84841
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.2843
|  |  |  | Coincident | 0.87445
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.1404
|  |  |  | Coincident | 0.76836
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.1631
|  |  |  | Coincident | 0.79194
| Collinsfield 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 0.31286
|  |  |  | Coincident | 0.29449
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.32933
|  |  |  | Coincident | 0.30999
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.025178
|  |  |  | Coincident | 0.0049802
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.34614
|  |  |  | Coincident | 0.33598
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.36436
|  |  |  | Coincident | 0.35366
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.32659
|  |  |  | Coincident | 0.317
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.34378
|  |  |  | Coincident | 0.33368
| Coomandook 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.404
|  |  |  | Coincident | 0.391
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.40661
|  |  |  | Coincident | 0.39381
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0051187
|  |  |  | Coincident | 0.002828
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.37379
|  |  |  | Coincident | 0.37285
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.37634
|  |  |  | Coincident | 0.37535
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.34533
|  |  |  | Coincident | 0.34447
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.34769
|  |  |  | Coincident | 0.34678
| Coonalpyn 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.404
|  |  |  | Coincident | 0.391
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.40661
|  |  |  | Coincident | 0.39381
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0067716
|  |  |  | Coincident | 0.0037411
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.38852
|  |  |  | Coincident | 0.38755
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.39117
|  |  |  | Coincident | 0.39015
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.35887
|  |  |  | Coincident | 0.35797
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.36132
|  |  |  | Coincident | 0.36037
| Coonawarra 11kV | Substation Rating | MVA | Non-Coincident | 13.4522
|  |  |  | Coincident | 13.4522
|  | Raw Adjusted MD | MW | Non-Coincident | 2.984
|  |  |  | Coincident | 1.539
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.545
|  |  |  | Coincident | 1.8616
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.89583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0075193
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.4432
|  |  |  | Coincident | 3.4432
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.0905
|  |  |  | Coincident | 4.0905
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.8897
|  |  |  | Coincident | 2.8897
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.433
|  |  |  | Coincident | 3.433
| Copley Nepabunna 33kV | Substation Rating | MVA | Non-Coincident | 0.3
|  |  |  | Coincident | 0.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.22634
|  |  |  | Coincident | 0.20748
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.22863
|  |  |  | Coincident | 0.20958
|  | Date MD occurred |  | Non-Coincident | 2018-10-31
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.29167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0045727
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.1255
|  |  |  | Coincident | 1.1255
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.1292
|  |  |  | Coincident | 1.1292
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.0377
|  |  |  | Coincident | 1.0377
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.0411
|  |  |  | Coincident | 1.0411
| Cordola 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.562
|  |  |  | Coincident | 0.929
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.6016
|  |  |  | Coincident | 0.96772
|  | Date MD occurred |  | Non-Coincident | 2018-12-28
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.042766
|  |  |  | Coincident | 0.0065565
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.021
|  |  |  | Coincident | 0.48565
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.0469
|  |  |  | Coincident | 0.50567
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.91497
|  |  |  | Coincident | 0.43523
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.93817
|  |  |  | Coincident | 0.45316
| Coromandel Place 11kV | Substation Rating | MVA | Non-Coincident | 93
|  |  |  | Coincident | 93
|  | Raw Adjusted MD | MW | Non-Coincident | 45.9962
|  |  |  | Coincident | 26.276
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.514
|  |  |  | Coincident | 26.7743
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.54167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.18023
|  |  |  | Coincident | 0.0047709
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.9278
|  |  |  | Coincident | 47.9278
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.4925
|  |  |  | Coincident | 49.4925
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 45.1472
|  |  |  | Coincident | 45.1472
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.6211
|  |  |  | Coincident | 46.6211
| Cowell 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.144
|  |  |  | Coincident | 2.144
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.1564
|  |  |  | Coincident | 2.1564
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.020436
|  |  |  | Coincident | 0.020436
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.0791
|  |  |  | Coincident | 2.0791
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0908
|  |  |  | Coincident | 2.0908
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.8261
|  |  |  | Coincident | 1.8261
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8364
|  |  |  | Coincident | 1.8364
| Croydon 11kV | Substation Rating | MVA | Non-Coincident | 48.4
|  |  |  | Coincident | 48.4
|  | Raw Adjusted MD | MW | Non-Coincident | 28.7175
|  |  |  | Coincident | 27.0495
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.7251
|  |  |  | Coincident | 27.0496
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.2771
|  |  |  | Coincident | 0.10496
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.5225
|  |  |  | Coincident | 27.6094
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.5319
|  |  |  | Coincident | 27.6094
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.4193
|  |  |  | Coincident | 24.6056
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.4277
|  |  |  | Coincident | 24.6056
| Croydon Park 11kV | Substation Rating | MVA | Non-Coincident | 26.4221
|  |  |  | Coincident | 26.4221
|  | Raw Adjusted MD | MW | Non-Coincident | 16.6106
|  |  |  | Coincident | 16.2386
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.0726
|  |  |  | Coincident | 16.7109
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.089555
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.8895
|  |  |  | Coincident | 17.697
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.3783
|  |  |  | Coincident | 18.2003
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.9816
|  |  |  | Coincident | 15.8097
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.4183
|  |  |  | Coincident | 16.2593
| Crystal Brook 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 2.044
|  |  |  | Coincident | 2.004
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.098
|  |  |  | Coincident | 2.0566
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.019216
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.9629
|  |  |  | Coincident | 1.8679
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0146
|  |  |  | Coincident | 1.9239
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.7824
|  |  |  | Coincident | 1.6961
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8293
|  |  |  | Coincident | 1.7469
| Cudmore Park 11kV | Substation Rating | MVA | Non-Coincident | 22.1309
|  |  |  | Coincident | 22.1309
|  | Raw Adjusted MD | MW | Non-Coincident | 13.8871
|  |  |  | Coincident | 10.6276
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.0632
|  |  |  | Coincident | 11.0249
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.45833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.1014
|  |  |  | Coincident | 0.062314
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.5523
|  |  |  | Coincident | 11.331
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.8421
|  |  |  | Coincident | 11.7802
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.9981
|  |  |  | Coincident | 10.1208
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.1501
|  |  |  | Coincident | 10.5221
| Cummins 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.4625
|  |  |  | Coincident | 2.4
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.553
|  |  |  | Coincident | 2.4883
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.13969
|  |  |  | Coincident | 0.027631
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.6475
|  |  |  | Coincident | 2.2651
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.6585
|  |  |  | Coincident | 2.2903
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4501
|  |  |  | Coincident | 2.0962
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4603
|  |  |  | Coincident | 2.1195
| Curramulka 7.6kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.1768
|  |  |  | Coincident | 0.1768
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.17968
|  |  |  | Coincident | 0.17968
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005007
|  |  |  | Coincident | 0.0027662
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.1768
|  |  |  | Coincident | 0.1768
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.17968
|  |  |  | Coincident | 0.17968
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.16317
|  |  |  | Coincident | 0.16317
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.16584
|  |  |  | Coincident | 0.16584
| Curramulka South 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.083507
|  |  |  | Coincident | 0.083507
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.08487
|  |  |  | Coincident | 0.08487
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00057146
|  |  |  | Coincident | 0.00031572
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.083507
|  |  |  | Coincident | 0.083507
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.08487
|  |  |  | Coincident | 0.08487
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.07577
|  |  |  | Coincident | 0.07577
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.077007
|  |  |  | Coincident | 0.077007
| Darke Peak 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.325
|  |  |  | Coincident | 0.319
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.34279
|  |  |  | Coincident | 0.33876
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0022669
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.37244
|  |  |  | Coincident | 0.3603
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.40274
|  |  |  | Coincident | 0.39199
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.34378
|  |  |  | Coincident | 0.33257
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.37175
|  |  |  | Coincident | 0.36183
| Deloraine 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.39169
|  |  |  | Coincident | 0.39169
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.40521
|  |  |  | Coincident | 0.40521
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.004376
|  |  |  | Coincident | 0.004376
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.39169
|  |  |  | Coincident | 0.39169
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.40521
|  |  |  | Coincident | 0.40521
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.3642
|  |  |  | Coincident | 0.3642
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.37677
|  |  |  | Coincident | 0.37677
| Desert Camp 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.068484
|  |  |  | Coincident | 0.068484
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.072132
|  |  |  | Coincident | 0.072132
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00041616
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.068484
|  |  |  | Coincident | 0.068484
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.072132
|  |  |  | Coincident | 0.072132
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.061878
|  |  |  | Coincident | 0.061878
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.065173
|  |  |  | Coincident | 0.065173
| Direk 11kV | Substation Rating | MVA | Non-Coincident | 56.4
|  |  |  | Coincident | 56.4
|  | Raw Adjusted MD | MW | Non-Coincident | 23.14
|  |  |  | Coincident | 22.46
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.9153
|  |  |  | Coincident | 23.2736
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.11994
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.5649
|  |  |  | Coincident | 22.232
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.3267
|  |  |  | Coincident | 23.0124
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.1114
|  |  |  | Coincident | 20.8
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.8242
|  |  |  | Coincident | 21.5302
| Dorrien TF4 11kV | Substation Rating | MVA | Non-Coincident | 13.6
|  |  |  | Coincident | 13.6
|  | Raw Adjusted MD | MW | Non-Coincident | 8.2135
|  |  |  | Coincident | 7.6516
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.6356
|  |  |  | Coincident | 7.8745
|  | Date MD occurred |  | Non-Coincident | 2019-02-28
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.55356
|  |  |  | Coincident | 0.056391
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.4733
|  |  |  | Coincident | 8.1734
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.9027
|  |  |  | Coincident | 8.4471
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.7185
|  |  |  | Coincident | 7.4453
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.1097
|  |  |  | Coincident | 7.6946
| Dorrien TF5 11kV | Substation Rating | MVA | Non-Coincident | 13.6
|  |  |  | Coincident | 13.6
|  | Raw Adjusted MD | MW | Non-Coincident | 3.8978
|  |  |  | Coincident | 3.0921
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.227
|  |  |  | Coincident | 3.2091
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.085663
|  |  |  | Coincident | 0.031791
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.0423
|  |  |  | Coincident | 3.3104
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.4146
|  |  |  | Coincident | 3.4544
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.6871
|  |  |  | Coincident | 3.0194
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.0266
|  |  |  | Coincident | 3.1508
| Dowlingville 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.097767
|  |  |  | Coincident | 0.097767
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.10012
|  |  |  | Coincident | 0.10012
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00044064
|  |  |  | Coincident | 0.00044064
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.097767
|  |  |  | Coincident | 0.097767
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.10012
|  |  |  | Coincident | 0.10012
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.091374
|  |  |  | Coincident | 0.091374
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.093577
|  |  |  | Coincident | 0.093577
| East Terrace 11kV | Substation Rating | MVA | Non-Coincident | 62.2394
|  |  |  | Coincident | 62.2394
|  | Raw Adjusted MD | MW | Non-Coincident | 34.7981
|  |  |  | Coincident | 23.9738
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.6442
|  |  |  | Coincident | 24.9319
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5625
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.014
|  |  |  | Coincident | 0.026914
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.4878
|  |  |  | Coincident | 36.4878
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.4299
|  |  |  | Coincident | 38.4299
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.5788
|  |  |  | Coincident | 33.5788
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.366
|  |  |  | Coincident | 35.366
| Edinburgh 11kV | Substation Rating | MVA | Non-Coincident | 57.058
|  |  |  | Coincident | 57.058
|  | Raw Adjusted MD | MW | Non-Coincident | 13.8066
|  |  |  | Coincident | 11.388
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.4773
|  |  |  | Coincident | 11.6052
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.2961
|  |  |  | Coincident | 0.039947
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.6069
|  |  |  | Coincident | 12.0052
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.3124
|  |  |  | Coincident | 12.2403
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.4835
|  |  |  | Coincident | 11.0819
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.1348
|  |  |  | Coincident | 11.2989
| Edinburgh ISS 11kV | Substation Rating | MVA | Non-Coincident | -
|  |  |  | Coincident | -
|  | Raw Adjusted MD | MW | Non-Coincident | 9.5
|  |  |  | Coincident | 6.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.7985
|  |  |  | Coincident | 6.364
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5625
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.9604
|  |  |  | Coincident | 6.4796
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.2478
|  |  |  | Coincident | 6.5292
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.2042
|  |  |  | Coincident | 5.9877
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.4698
|  |  |  | Coincident | 6.0335
| Edithburgh 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.2042
|  |  |  | Coincident | 1.2042
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.2676
|  |  |  | Coincident | 1.2676
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.018037
|  |  |  | Coincident | 0.018037
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.1203
|  |  |  | Coincident | 1.1124
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.1793
|  |  |  | Coincident | 1.1709
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.0666
|  |  |  | Coincident | 1.059
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.1227
|  |  |  | Coincident | 1.1148
| Elizabeth Downs 11kV | Substation Rating | MVA | Non-Coincident | 59.6
|  |  |  | Coincident | 59.6
|  | Raw Adjusted MD | MW | Non-Coincident | 46.2521
|  |  |  | Coincident | 45.88
|  | Raw Adjusted MD | MVA | Non-Coincident | 47.1352
|  |  |  | Coincident | 46.7557
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.26842
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.4593
|  |  |  | Coincident | 45.2763
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.3216
|  |  |  | Coincident | 46.135
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.0189
|  |  |  | Coincident | 40.8538
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.797
|  |  |  | Coincident | 41.6286
| Elizabeth Heights 11kV | Substation Rating | MVA | Non-Coincident | 27.5654
|  |  |  | Coincident | 27.5654
|  | Raw Adjusted MD | MW | Non-Coincident | 18.8794
|  |  |  | Coincident | 18.8794
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.2576
|  |  |  | Coincident | 19.2576
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.13497
|  |  |  | Coincident | 0.13497
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.2407
|  |  |  | Coincident | 19.2407
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.6352
|  |  |  | Coincident | 19.6352
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.4296
|  |  |  | Coincident | 17.4296
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.787
|  |  |  | Coincident | 17.787
| Elizabeth South 11kV | Substation Rating | MVA | Non-Coincident | 28.4301
|  |  |  | Coincident | 28.4301
|  | Raw Adjusted MD | MW | Non-Coincident | 9.7694
|  |  |  | Coincident | 9.6392
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.9218
|  |  |  | Coincident | 9.8106
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.071753
|  |  |  | Coincident | 0.039642
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.725
|  |  |  | Coincident | 9.6673
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.8764
|  |  |  | Coincident | 9.8351
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.9681
|  |  |  | Coincident | 8.9149
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.1077
|  |  |  | Coincident | 9.0697
| Eudunda 11kV | Substation Rating | MVA | Non-Coincident | 2.4
|  |  |  | Coincident | 2.4
|  | Raw Adjusted MD | MW | Non-Coincident | 1.8744
|  |  |  | Coincident | 1.7941
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.9731
|  |  |  | Coincident | 1.8885
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.021897
|  |  |  | Coincident | 0.012098
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.8476
|  |  |  | Coincident | 1.8349
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.9448
|  |  |  | Coincident | 1.9315
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.6967
|  |  |  | Coincident | 1.685
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.786
|  |  |  | Coincident | 1.7737
| Evanston 11kV | Substation Rating | MVA | Non-Coincident | 57.6602
|  |  |  | Coincident | 57.6602
|  | Raw Adjusted MD | MW | Non-Coincident | 38.3682
|  |  |  | Coincident | 37.9512
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.9345
|  |  |  | Coincident | 38.4834
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.744
|  |  |  | Coincident | 1.0047
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.1133
|  |  |  | Coincident | 40.1133
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.7124
|  |  |  | Coincident | 40.7124
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.1529
|  |  |  | Coincident | 36.1529
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.6928
|  |  |  | Coincident | 36.6928
| Evanston 33kV | Substation Rating | MVA | Non-Coincident | 11.875
|  |  |  | Coincident | 11.875
|  | Raw Adjusted MD | MW | Non-Coincident | 0.021356
|  |  |  | Coincident | 0.021356
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.030202
|  |  |  | Coincident | 0.030202
|  | Date MD occurred |  | Non-Coincident | 2018-11-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.020833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.021356
|  |  |  | Coincident | 0.021356
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.030202
|  |  |  | Coincident | 0.030202
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.019143
|  |  |  | Coincident | 0.019143
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.027072
|  |  |  | Coincident | 0.027072
| Findon 11kV | Substation Rating | MVA | Non-Coincident | 24.8215
|  |  |  | Coincident | 24.8215
|  | Raw Adjusted MD | MW | Non-Coincident | 18.311
|  |  |  | Coincident | 18.311
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.8357
|  |  |  | Coincident | 18.8357
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.075722
|  |  |  | Coincident | 0.075722
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.986
|  |  |  | Coincident | 16.986
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.4666
|  |  |  | Coincident | 17.4666
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.9833
|  |  |  | Coincident | 14.9833
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.4073
|  |  |  | Coincident | 15.4073
| Flinders Park 11kV | Substation Rating | MVA | Non-Coincident | 30
|  |  |  | Coincident | 30
|  | Raw Adjusted MD | MW | Non-Coincident | 20.7524
|  |  |  | Coincident | 20.3684
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.4096
|  |  |  | Coincident | 21.0099
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.097874
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.4556
|  |  |  | Coincident | 20.2664
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.1034
|  |  |  | Coincident | 20.9064
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.7354
|  |  |  | Coincident | 17.5714
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.2971
|  |  |  | Coincident | 18.1263
| Forreston 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.93514
|  |  |  | Coincident | 0.64683
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.96406
|  |  |  | Coincident | 0.66684
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.010328
|  |  |  | Coincident | 0.0089527
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.87798
|  |  |  | Coincident | 0.60914
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.89821
|  |  |  | Coincident | 0.62943
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.80604
|  |  |  | Coincident | 0.55923
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.82461
|  |  |  | Coincident | 0.57785
| Freeling 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.37648
|  |  |  | Coincident | 0.37648
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.38994
|  |  |  | Coincident | 0.38994
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0058163
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.37648
|  |  |  | Coincident | 0.37648
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.38994
|  |  |  | Coincident | 0.38994
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.35037
|  |  |  | Coincident | 0.35037
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.36291
|  |  |  | Coincident | 0.36291
| Freeling North 11kV | Substation Rating | MVA | Non-Coincident | 4.3
|  |  |  | Coincident | 4.3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.87
|  |  |  | Coincident | 2.836
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.9134
|  |  |  | Coincident | 2.877
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.026698
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.0317
|  |  |  | Coincident | 3.0137
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0775
|  |  |  | Coincident | 3.0583
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.7824
|  |  |  | Coincident | 2.7659
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.8245
|  |  |  | Coincident | 2.8068
| Fulham Gardens 11kV | Substation Rating | MVA | Non-Coincident | 48.9986
|  |  |  | Coincident | 48.9986
|  | Raw Adjusted MD | MW | Non-Coincident | 44.2199
|  |  |  | Coincident | 43.32
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.7295
|  |  |  | Coincident | 44.8888
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.43097
|  |  |  | Coincident | 0.2381
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.7447
|  |  |  | Coincident | 42.902
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.2826
|  |  |  | Coincident | 44.479
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.3544
|  |  |  | Coincident | 37.6155
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 39.7028
|  |  |  | Coincident | 38.9982
| Fullerville 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.025922
|  |  |  | Coincident | 0.025922
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.026056
|  |  |  | Coincident | 0.026056
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.025922
|  |  |  | Coincident | 0.025922
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.026056
|  |  |  | Coincident | 0.026056
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.023698
|  |  |  | Coincident | 0.023698
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.02382
|  |  |  | Coincident | 0.02382
| Gawler Belt TF1 11kV | Substation Rating | MVA | Non-Coincident | 14.6
|  |  |  | Coincident | 14.6
|  | Raw Adjusted MD | MW | Non-Coincident | 4.1923
|  |  |  | Coincident | 4.1402
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.4489
|  |  |  | Coincident | 4.3402
|  | Date MD occurred |  | Non-Coincident | 2019-01-16
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.6015
|  |  |  | Coincident | 0.043877
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.0085
|  |  |  | Coincident | 4.9495
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.3067
|  |  |  | Coincident | 5.1761
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.6197
|  |  |  | Coincident | 4.5652
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.8947
|  |  |  | Coincident | 4.7742
| Gawler Belt TF2 11kV | Substation Rating | MVA | Non-Coincident | 14.6
|  |  |  | Coincident | 14.6
|  | Raw Adjusted MD | MW | Non-Coincident | 5.045
|  |  |  | Coincident | 4.9194
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.1973
|  |  |  | Coincident | 5.0607
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.045422
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.1971
|  |  |  | Coincident | 5.1971
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.3523
|  |  |  | Coincident | 5.3523
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.6627
|  |  |  | Coincident | 4.6627
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.8019
|  |  |  | Coincident | 4.8019
| Georgetown 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.161
|  |  |  | Coincident | 0.157
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.1652
|  |  |  | Coincident | 0.16085
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0014659
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.15722
|  |  |  | Coincident | 0.15624
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.16159
|  |  |  | Coincident | 0.16019
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.14299
|  |  |  | Coincident | 0.1421
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.14697
|  |  |  | Coincident | 0.14569
| Geranium 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.092
|  |  |  | Coincident | 0.092
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.095603
|  |  |  | Coincident | 0.095603
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00070056
|  |  |  | Coincident | 0.00070056
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.089577
|  |  |  | Coincident | 0.075877
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.095901
|  |  |  | Coincident | 0.079187
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.081246
|  |  |  | Coincident | 0.06882
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.086983
|  |  |  | Coincident | 0.071823
| Gladstone 11kV | Substation Rating | MVA | Non-Coincident | 4.8
|  |  |  | Coincident | 4.8
|  | Raw Adjusted MD | MW | Non-Coincident | 2.352
|  |  |  | Coincident | 2.198
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.4789
|  |  |  | Coincident | 2.3132
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11961
|  |  |  | Coincident | 0.02366
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.5596
|  |  |  | Coincident | 2.4193
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.6707
|  |  |  | Coincident | 2.5156
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.3392
|  |  |  | Coincident | 2.2109
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4407
|  |  |  | Coincident | 2.299
| Glanville 7.6kV | Substation Rating | MVA | Non-Coincident | 20.3597
|  |  |  | Coincident | 20.3597
|  | Raw Adjusted MD | MW | Non-Coincident | 11.0834
|  |  |  | Coincident | 11.0834
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.2624
|  |  |  | Coincident | 11.2624
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.083763
|  |  |  | Coincident | 0.083763
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.7266
|  |  |  | Coincident | 10.7266
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.9003
|  |  |  | Coincident | 10.9003
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.4104
|  |  |  | Coincident | 9.4104
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.5628
|  |  |  | Coincident | 9.5628
| Glencoe 11kV | Substation Rating | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.95
|  | Raw Adjusted MD | MW | Non-Coincident | 0.998
|  |  |  | Coincident | 0.926
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.0637
|  |  |  | Coincident | 0.99497
|  | Date MD occurred |  | Non-Coincident | 2018-11-18
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.0625
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0088733
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.95464
|  |  |  | Coincident | 0.57489
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.0175
|  |  |  | Coincident | 0.63503
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.90333
|  |  |  | Coincident | 0.54399
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.96279
|  |  |  | Coincident | 0.6009
| Glenelg North 11kV | Substation Rating | MVA | Non-Coincident | 27.9125
|  |  |  | Coincident | 27.9125
|  | Raw Adjusted MD | MW | Non-Coincident | 21.726
|  |  |  | Coincident | 21.7222
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.5884
|  |  |  | Coincident | 22.5564
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.086294
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.1928
|  |  |  | Coincident | 20.191
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.9813
|  |  |  | Coincident | 20.9857
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.5641
|  |  |  | Coincident | 17.5626
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.25
|  |  |  | Coincident | 18.2538
| Glossop 11kV | Substation Rating | MVA | Non-Coincident | 15.3526
|  |  |  | Coincident | 15.3526
|  | Raw Adjusted MD | MW | Non-Coincident | 9.2434
|  |  |  | Coincident | 6.9377
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.6029
|  |  |  | Coincident | 7.1028
|  | Date MD occurred |  | Non-Coincident | 2019-03-04
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.041667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.047716
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.2264
|  |  |  | Coincident | 7.4634
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.7091
|  |  |  | Coincident | 7.6217
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.2671
|  |  |  | Coincident | 6.8257
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.7086
|  |  |  | Coincident | 6.9705
| Golden Grove 11kV | Substation Rating | MVA | Non-Coincident | 84.6321
|  |  |  | Coincident | 84.6321
|  | Raw Adjusted MD | MW | Non-Coincident | 47.693
|  |  |  | Coincident | 47.683
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.9601
|  |  |  | Coincident | 48.8643
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.36089
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.9955
|  |  |  | Coincident | 47.7806
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 49.2272
|  |  |  | Coincident | 48.991
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 43.3316
|  |  |  | Coincident | 43.1376
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 44.4436
|  |  |  | Coincident | 44.2304
| Gomersal North 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.2353
|  |  |  | Coincident | 0.17497
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.24768
|  |  |  | Coincident | 0.18417
|  | Date MD occurred |  | Non-Coincident | 2019-01-10
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.97917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.2261
|  |  |  | Coincident | 0.17392
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.238
|  |  |  | Coincident | 0.18308
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.19144
|  |  |  | Coincident | 0.14726
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.20151
|  |  |  | Coincident | 0.15501
| Goolwa 11kV | Substation Rating | MVA | Non-Coincident | 33.4
|  |  |  | Coincident | 33.4
|  | Raw Adjusted MD | MW | Non-Coincident | 16.7583
|  |  |  | Coincident | 16.7583
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.7594
|  |  |  | Coincident | 16.7594
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.16797
|  |  |  | Coincident | 0.16797
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.8895
|  |  |  | Coincident | 14.8895
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.8902
|  |  |  | Coincident | 14.8902
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.8509
|  |  |  | Coincident | 12.8509
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.8515
|  |  |  | Coincident | 12.8515
| Gulnare 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.090336
|  |  |  | Coincident | 0.090336
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.09047
|  |  |  | Coincident | 0.09047
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00032364
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.090336
|  |  |  | Coincident | 0.090336
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.09047
|  |  |  | Coincident | 0.09047
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.082704
|  |  |  | Coincident | 0.082704
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.082826
|  |  |  | Coincident | 0.082826
| Gumeracha 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.30135
|  |  |  | Coincident | 0.30135
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.31175
|  |  |  | Coincident | 0.31175
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0036149
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.30135
|  |  |  | Coincident | 0.30135
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.31175
|  |  |  | Coincident | 0.31175
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.28025
|  |  |  | Coincident | 0.28025
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.28993
|  |  |  | Coincident | 0.28993
| Gumeracha Weir 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.26599
|  |  |  | Coincident | 0.26599
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.27517
|  |  |  | Coincident | 0.27517
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0013095
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.26599
|  |  |  | Coincident | 0.26599
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.27517
|  |  |  | Coincident | 0.27517
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.24772
|  |  |  | Coincident | 0.24772
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.25627
|  |  |  | Coincident | 0.25627
| Gumhaven 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.088547
|  |  |  | Coincident | 0.088547
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.091604
|  |  |  | Coincident | 0.091604
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00033552
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.088547
|  |  |  | Coincident | 0.088547
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.091604
|  |  |  | Coincident | 0.091604
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.082427
|  |  |  | Coincident | 0.082427
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.085272
|  |  |  | Coincident | 0.085272
| Hackham 11kV | Substation Rating | MVA | Non-Coincident | 31.6
|  |  |  | Coincident | 31.6
|  | Raw Adjusted MD | MW | Non-Coincident | 15.12
|  |  |  | Coincident | 14.93
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.3453
|  |  |  | Coincident | 15.1496
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.67062
|  |  |  | Coincident | 0.13265
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.7592
|  |  |  | Coincident | 14.6659
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.9819
|  |  |  | Coincident | 14.8858
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.7943
|  |  |  | Coincident | 12.7134
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.9874
|  |  |  | Coincident | 12.9041
| Hahndorf 11kV | Substation Rating | MVA | Non-Coincident | 6.8
|  |  |  | Coincident | 6.8
|  | Raw Adjusted MD | MW | Non-Coincident | 5.4983
|  |  |  | Coincident | 5.4983
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.7103
|  |  |  | Coincident | 5.7103
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.047626
|  |  |  | Coincident | 0.047626
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.0429
|  |  |  | Coincident | 5.0262
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.2337
|  |  |  | Coincident | 5.2111
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.6239
|  |  |  | Coincident | 4.6085
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.7988
|  |  |  | Coincident | 4.7781
| Halbury 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.096993
|  |  |  | Coincident | 0.096993
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.097137
|  |  |  | Coincident | 0.097137
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0009972
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.096993
|  |  |  | Coincident | 0.096993
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.097137
|  |  |  | Coincident | 0.097137
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.088764
|  |  |  | Coincident | 0.088764
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.088895
|  |  |  | Coincident | 0.088895
| Hamley Bridge 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.296
|  |  |  | Coincident | 2.285
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.396
|  |  |  | Coincident | 2.3875
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.014127
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.3424
|  |  |  | Coincident | 2.3424
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.446
|  |  |  | Coincident | 2.446
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.1629
|  |  |  | Coincident | 2.1629
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.2585
|  |  |  | Coincident | 2.2585
| Happy Valley 11kV | Substation Rating | MVA | Non-Coincident | 59.8
|  |  |  | Coincident | 59.8
|  | Raw Adjusted MD | MW | Non-Coincident | 35.2257
|  |  |  | Coincident | 35.2257
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.0858
|  |  |  | Coincident | 36.0858
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.28789
|  |  |  | Coincident | 0.28789
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.0045
|  |  |  | Coincident | 35.0045
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.8639
|  |  |  | Coincident | 35.8639
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.2231
|  |  |  | Coincident | 30.2231
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.9651
|  |  |  | Coincident | 30.9651
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Harrow 11kV | Substation Rating | MVA | Non-Coincident | 28.3147
|  |  |  | Coincident | 28.3147
|  | Raw Adjusted MD | MW | Non-Coincident | 20.0172
|  |  |  | Coincident | 20.0172
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.7189
|  |  |  | Coincident | 20.7074
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.2072
|  |  |  | Coincident | 0.11447
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.5742
|  |  |  | Coincident | 18.5742
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.2199
|  |  |  | Coincident | 19.2199
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.5203
|  |  |  | Coincident | 16.5203
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.0947
|  |  |  | Coincident | 17.0947
| Hatherleigh 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.059847
|  |  |  | Coincident | 0.059847
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.061611
|  |  |  | Coincident | 0.061611
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00063324
|  |  |  | Coincident | 0.00063324
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.059847
|  |  |  | Coincident | 0.059847
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.061611
|  |  |  | Coincident | 0.061611
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.05396
|  |  |  | Coincident | 0.05396
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.055551
|  |  |  | Coincident | 0.055551
| Hawker 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.902
|  |  |  | Coincident | 0.864
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.90202
|  |  |  | Coincident | 0.86415
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.030005
|  |  |  | Coincident | 0.0059351
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.91911
|  |  |  | Coincident | 0.9028
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.91922
|  |  |  | Coincident | 0.90286
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.84491
|  |  |  | Coincident | 0.82992
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.84501
|  |  |  | Coincident | 0.82997
| Hay Flat 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.070652
|  |  |  | Coincident | 0.06081
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.070778
|  |  |  | Coincident | 0.061013
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00030042
|  |  |  | Coincident | 0.00030042
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.070652
|  |  |  | Coincident | 0.06081
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.070778
|  |  |  | Coincident | 0.061013
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.065357
|  |  |  | Coincident | 0.056253
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.065473
|  |  |  | Coincident | 0.056441
| Henley South 11kV | Substation Rating | MVA | Non-Coincident | 55.7251
|  |  |  | Coincident | 55.7251
|  | Raw Adjusted MD | MW | Non-Coincident | 37.0244
|  |  |  | Coincident | 37.0244
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.2183
|  |  |  | Coincident | 38.2183
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.1851
|  |  |  | Coincident | 0.1851
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.0323
|  |  |  | Coincident | 35.0323
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.1797
|  |  |  | Coincident | 36.1797
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.4076
|  |  |  | Coincident | 30.4076
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.4035
|  |  |  | Coincident | 31.4035
| Hermitage 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.14998
|  |  |  | Coincident | 0.13901
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.15623
|  |  |  | Coincident | 0.1448
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0025888
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.16685
|  |  |  | Coincident | 0.16362
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.1727
|  |  |  | Coincident | 0.16908
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.15738
|  |  |  | Coincident | 0.15433
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.16289
|  |  |  | Coincident | 0.15948
| Hillcrest 11kV | Substation Rating | MVA | Non-Coincident | 61.6816
|  |  |  | Coincident | 61.6816
|  | Raw Adjusted MD | MW | Non-Coincident | 37.69
|  |  |  | Coincident | 35.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.9966
|  |  |  | Coincident | 36.0228
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.1622
|  |  |  | Coincident | 0.20028
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.2654
|  |  |  | Coincident | 35.443
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.6474
|  |  |  | Coincident | 36.1768
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.7246
|  |  |  | Coincident | 32.0753
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.9753
|  |  |  | Coincident | 32.7394
| Hindley Street 11kV | Substation Rating | MVA | Non-Coincident | 77.124
|  |  |  | Coincident | 77.124
|  | Raw Adjusted MD | MW | Non-Coincident | 42.1826
|  |  |  | Coincident | 29.3747
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.479
|  |  |  | Coincident | 29.6067
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.58333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.43543
|  |  |  | Coincident | 0.011929
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.1633
|  |  |  | Coincident | 43.8817
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 44.4908
|  |  |  | Coincident | 44.2037
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.3596
|  |  |  | Coincident | 41.0959
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.6664
|  |  |  | Coincident | 41.3975
| Holden Hill 11kV | Substation Rating | MVA | Non-Coincident | 46.713
|  |  |  | Coincident | 46.713
|  | Raw Adjusted MD | MW | Non-Coincident | 37.8357
|  |  |  | Coincident | 37.8357
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.9679
|  |  |  | Coincident | 38.9679
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.21073
|  |  |  | Coincident | 0.21073
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.0506
|  |  |  | Coincident | 37.0506
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.1811
|  |  |  | Coincident | 38.1811
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.4836
|  |  |  | Coincident | 33.4836
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.5053
|  |  |  | Coincident | 34.5053
| Hope Valley 11kV | Substation Rating | MVA | Non-Coincident | 31.2
|  |  |  | Coincident | 31.2
|  | Raw Adjusted MD | MW | Non-Coincident | 19.47
|  |  |  | Coincident | 19.47
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.9413
|  |  |  | Coincident | 19.9413
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.14897
|  |  |  | Coincident | 0.14897
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.6772
|  |  |  | Coincident | 25.6772
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.0543
|  |  |  | Coincident | 28.0543
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.1669
|  |  |  | Coincident | 23.1669
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.3116
|  |  |  | Coincident | 25.3116
| Houghton 7.6kV | Substation Rating | MVA | Non-Coincident | 3.6
|  |  |  | Coincident | 3.6
|  | Raw Adjusted MD | MW | Non-Coincident | 2.22
|  |  |  | Coincident | 1.927
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.3143
|  |  |  | Coincident | 2.0359
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.032867
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.1117
|  |  |  | Coincident | 1.9035
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.2103
|  |  |  | Coincident | 2.0075
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.9603
|  |  |  | Coincident | 1.7671
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.0518
|  |  |  | Coincident | 1.8636
| Hoyleton 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.095
|  |  |  | Coincident | 0.085
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.095525
|  |  |  | Coincident | 0.085586
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00092412
|  |  |  | Coincident | 0.00092412
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.09032
|  |  |  | Coincident | 0.080813
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.090819
|  |  |  | Coincident | 0.08137
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.082601
|  |  |  | Coincident | 0.073906
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.083058
|  |  |  | Coincident | 0.074416
| Ingle Farm 11kV | Substation Rating | MVA | Non-Coincident | 51.7129
|  |  |  | Coincident | 51.7129
|  | Raw Adjusted MD | MW | Non-Coincident | 37.3594
|  |  |  | Coincident | 37.1733
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.4124
|  |  |  | Coincident | 38.0327
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.2399
|  |  |  | Coincident | 0.24525
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.0726
|  |  |  | Coincident | 37.5415
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.1292
|  |  |  | Coincident | 38.4381
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.4511
|  |  |  | Coincident | 33.9705
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.4072
|  |  |  | Coincident | 34.7818
| Inverness 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.701
|  |  |  | Coincident | 0.075
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.82765
|  |  |  | Coincident | 0.091837
|  | Date MD occurred |  | Non-Coincident | 2018-11-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.16667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.1742
|  |  |  | Coincident | 0.014549
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.20412
|  |  |  | Coincident | 0.017942
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.15461
|  |  |  | Coincident | 0.012912
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.18117
|  |  |  | Coincident | 0.015924
| Jabuk 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.076536
|  |  |  | Coincident | 0.076536
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.078233
|  |  |  | Coincident | 0.078233
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.000162
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.076536
|  |  |  | Coincident | 0.076536
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.078233
|  |  |  | Coincident | 0.078233
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.071113
|  |  |  | Coincident | 0.071113
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.072689
|  |  |  | Coincident | 0.072689
| James Well 7.6kV | Substation Rating | MVA | Non-Coincident | 0.91
|  |  |  | Coincident | 0.91
|  | Raw Adjusted MD | MW | Non-Coincident | 0.4237
|  |  |  | Coincident | 0.4237
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.43062
|  |  |  | Coincident | 0.43062
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0049695
|  |  |  | Coincident | 0.0027455
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.4237
|  |  |  | Coincident | 0.4237
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.43062
|  |  |  | Coincident | 0.43062
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.38487
|  |  |  | Coincident | 0.38487
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.39115
|  |  |  | Coincident | 0.39115
| Jamestown 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.614
|  |  |  | Coincident | 2.389
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.696
|  |  |  | Coincident | 2.4637
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.3358
|  |  |  | Coincident | 0.0276
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.5552
|  |  |  | Coincident | 2.2591
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.6502
|  |  |  | Coincident | 2.3526
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.329
|  |  |  | Coincident | 2.0591
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4156
|  |  |  | Coincident | 2.1443
| Jervois 11kV | Substation Rating | MVA | Non-Coincident | 4.6
|  |  |  | Coincident | 4.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.991
|  |  |  | Coincident | 1.445
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.187
|  |  |  | Coincident | 1.5673
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.23351
|  |  |  | Coincident | 0.011941
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.3154
|  |  |  | Coincident | 1.7762
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.5733
|  |  |  | Coincident | 1.9281
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.1336
|  |  |  | Coincident | 1.6368
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.3713
|  |  |  | Coincident | 1.7768
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Kadina 11kV | Substation Rating | MVA | Non-Coincident | 16
|  |  |  | Coincident | 16
|  | Raw Adjusted MD | MW | Non-Coincident | 9.4833
|  |  |  | Coincident | 9.4833
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.7188
|  |  |  | Coincident | 9.7188
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.15246
|  |  |  | Coincident | 0.084231
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.8073
|  |  |  | Coincident | 8.8073
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.0259
|  |  |  | Coincident | 9.0259
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.962
|  |  |  | Coincident | 7.962
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.1597
|  |  |  | Coincident | 8.1597
| Kalangadoo 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.52223
|  |  |  | Coincident | 0.52223
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.53763
|  |  |  | Coincident | 0.53763
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0036805
|  |  |  | Coincident | 0.0036805
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.52223
|  |  |  | Coincident | 0.52223
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.53763
|  |  |  | Coincident | 0.53763
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.45817
|  |  |  | Coincident | 0.45817
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.47169
|  |  |  | Coincident | 0.47169
| Kalangadoo West 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.798
|  |  |  | Coincident | 0.718
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.85682
|  |  |  | Coincident | 0.75897
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0018589
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.82035
|  |  |  | Coincident | 0.75432
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.87888
|  |  |  | Coincident | 0.79529
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.72927
|  |  |  | Coincident | 0.67057
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.7813
|  |  |  | Coincident | 0.707
| Kapunda TF1 11kV | Substation Rating | MVA | Non-Coincident | 14.8
|  |  |  | Coincident | 14.8
|  | Raw Adjusted MD | MW | Non-Coincident | 3.9977
|  |  |  | Coincident | 1.9674
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.2848
|  |  |  | Coincident | 1.9994
|  | Date MD occurred |  | Non-Coincident | 2019-01-22
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.1409
|  |  |  | Coincident | 0.017386
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.0786
|  |  |  | Coincident | 2.0183
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.3606
|  |  |  | Coincident | 2.0495
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.806
|  |  |  | Coincident | 1.8834
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.0691
|  |  |  | Coincident | 1.9125
| Kapunda TF2 11kV | Substation Rating | MVA | Non-Coincident | 17.4
|  |  |  | Coincident | 17.4
|  | Raw Adjusted MD | MW | Non-Coincident | 2.8223
|  |  |  | Coincident | 2.7727
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.854
|  |  |  | Coincident | 2.8049
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.04494
|  |  |  | Coincident | 0.024828
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.8488
|  |  |  | Coincident | 2.7561
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.8813
|  |  |  | Coincident | 2.7897
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.5785
|  |  |  | Coincident | 2.4946
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.6079
|  |  |  | Coincident | 2.525
| Karoonda 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.79783
|  |  |  | Coincident | 0.79783
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.8155
|  |  |  | Coincident | 0.8155
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0078275
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.79783
|  |  |  | Coincident | 0.79783
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.8155
|  |  |  | Coincident | 0.8155
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.74156
|  |  |  | Coincident | 0.74156
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.75799
|  |  |  | Coincident | 0.75799
| Keith 11kV | Substation Rating | MVA | Non-Coincident | 16.5904
|  |  |  | Coincident | 16.5904
|  | Raw Adjusted MD | MW | Non-Coincident | 5.3891
|  |  |  | Coincident | 5.3669
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.4225
|  |  |  | Coincident | 5.4083
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.023211
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.7032
|  |  |  | Coincident | 4.8059
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.7427
|  |  |  | Coincident | 4.8308
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.1139
|  |  |  | Coincident | 4.3093
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.1494
|  |  |  | Coincident | 4.3317
| Kent Town 11kV | Substation Rating | MVA | Non-Coincident | 59.1822
|  |  |  | Coincident | 59.1822
|  | Raw Adjusted MD | MW | Non-Coincident | 29.51
|  |  |  | Coincident | 24.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.1232
|  |  |  | Coincident | 25.5067
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.9124
|  |  |  | Coincident | 0.081416
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.8138
|  |  |  | Coincident | 25.1715
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.4195
|  |  |  | Coincident | 26.0975
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.8383
|  |  |  | Coincident | 22.6593
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.2838
|  |  |  | Coincident | 23.4929
| Kersbrook 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.551
|  |  |  | Coincident | 0.532
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.56567
|  |  |  | Coincident | 0.54515
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.033764
|  |  |  | Coincident | 0.0066785
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.50895
|  |  |  | Coincident | 0.48427
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.52241
|  |  |  | Coincident | 0.49817
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.46132
|  |  |  | Coincident | 0.43895
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.47352
|  |  |  | Coincident | 0.45155
| Keswick 11kV | Substation Rating | MVA | Non-Coincident | 49.0691
|  |  |  | Coincident | 49.0691
|  | Raw Adjusted MD | MW | Non-Coincident | 31.8733
|  |  |  | Coincident | 26.4097
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.9877
|  |  |  | Coincident | 27.5157
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.60417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.6531
|  |  |  | Coincident | 0.076161
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.0602
|  |  |  | Coincident | 27.4715
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.2504
|  |  |  | Coincident | 28.637
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.3715
|  |  |  | Coincident | 25.2373
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.3835
|  |  |  | Coincident | 26.308
| Ki Ki 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.10489
|  |  |  | Coincident | 0.10489
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.10722
|  |  |  | Coincident | 0.10722
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.000261
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.10489
|  |  |  | Coincident | 0.10489
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.10722
|  |  |  | Coincident | 0.10722
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.09749
|  |  |  | Coincident | 0.09749
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.09965
|  |  |  | Coincident | 0.09965
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Kilburn 11kV | Substation Rating | MVA | Non-Coincident | 76.1707
|  |  |  | Coincident | 76.1707
|  | Raw Adjusted MD | MW | Non-Coincident | 41.3825
|  |  |  | Coincident | 19.7828
|  | Raw Adjusted MD | MVA | Non-Coincident | 45.4719
|  |  |  | Coincident | 21.3341
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.39583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.2791
|  |  |  | Coincident | 1.4456
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 43.7443
|  |  |  | Coincident | 20.8885
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 48.7768
|  |  |  | Coincident | 23.0542
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.3157
|  |  |  | Coincident | 19.7288
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 46.0688
|  |  |  | Coincident | 21.7742
| Kilburn South 11kV | Substation Rating | MVA | Non-Coincident | 36.195
|  |  |  | Coincident | 36.195
|  | Raw Adjusted MD | MW | Non-Coincident | 14.65
|  |  |  | Coincident | 14.65
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.0062
|  |  |  | Coincident | 14.9641
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.10774
|  |  |  | Coincident | 0.059522
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.2361
|  |  |  | Coincident | 14.2361
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.5615
|  |  |  | Coincident | 14.5615
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.0171
|  |  |  | Coincident | 13.0171
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.3146
|  |  |  | Coincident | 13.3146
| Kilkenny 11kV | Substation Rating | MVA | Non-Coincident | 55.9052
|  |  |  | Coincident | 55.9052
|  | Raw Adjusted MD | MW | Non-Coincident | 20.1692
|  |  |  | Coincident | 19.8343
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.8983
|  |  |  | Coincident | 20.4519
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.5696
|  |  |  | Coincident | 0.066822
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.489
|  |  |  | Coincident | 20.1106
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.1303
|  |  |  | Coincident | 20.7265
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.0446
|  |  |  | Coincident | 18.6929
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.6407
|  |  |  | Coincident | 19.2654
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Kingscote 11kV | Substation Rating | MVA | Non-Coincident | 8
|  |  |  | Coincident | 8
|  | Raw Adjusted MD | MW | Non-Coincident | 3.4419
|  |  |  | Coincident | 3.4419
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.5676
|  |  |  | Coincident | 3.5676
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.028477
|  |  |  | Coincident | 0.028477
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.329
|  |  |  | Coincident | 3.329
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.4573
|  |  |  | Coincident | 3.4573
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.9923
|  |  |  | Coincident | 2.9923
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.1076
|  |  |  | Coincident | 3.1076
| Kingston SE 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 3.526
|  |  |  | Coincident | 3.377
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.5264
|  |  |  | Coincident | 3.3774
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.057913
|  |  |  | Coincident | 0.031996
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.3394
|  |  |  | Coincident | 3.3147
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.3398
|  |  |  | Coincident | 3.3151
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.0282
|  |  |  | Coincident | 3.0058
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.0286
|  |  |  | Coincident | 3.0062
| Kingswood 11kV | Substation Rating | MVA | Non-Coincident | 71.2
|  |  |  | Coincident | 71.2
|  | Raw Adjusted MD | MW | Non-Coincident | 49.1194
|  |  |  | Coincident | 48.9706
|  | Raw Adjusted MD | MVA | Non-Coincident | 51.0742
|  |  |  | Coincident | 50.9929
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.44416
|  |  |  | Coincident | 0.24539
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.0992
|  |  |  | Coincident | 45.0992
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 46.9276
|  |  |  | Coincident | 46.9276
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.4156
|  |  |  | Coincident | 40.4156
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.0541
|  |  |  | Coincident | 42.0541
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Kongorong 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.791
|  |  |  | Coincident | 0.607
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.81688
|  |  |  | Coincident | 0.6309
|  | Date MD occurred |  | Non-Coincident | 2019-01-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.020833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0040397
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.65879
|  |  |  | Coincident | 0.32398
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.68035
|  |  |  | Coincident | 0.33646
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.61282
|  |  |  | Coincident | 0.30138
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.63288
|  |  |  | Coincident | 0.31298
| Kumorna 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.543
|  |  |  | Coincident | 0.28
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.63079
|  |  |  | Coincident | 0.32004
|  | Date MD occurred |  | Non-Coincident | 2019-01-12
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.58567
|  |  |  | Coincident | 0.40825
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.67926
|  |  |  | Coincident | 0.4811
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.50748
|  |  |  | Coincident | 0.35374
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.58858
|  |  |  | Coincident | 0.41687
| Kybunga 11kV | Substation Rating | MVA | Non-Coincident | 0.13
|  |  |  | Coincident | 0.13
|  | Raw Adjusted MD | MW | Non-Coincident | 0.048
|  |  |  | Coincident | 0.027
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.050922
|  |  |  | Coincident | 0.027893
|  | Date MD occurred |  | Non-Coincident | 2018-12-28
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0045791
|  |  |  | Coincident | 0.00045288
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.045483
|  |  |  | Coincident | 0.025584
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.048251
|  |  |  | Coincident | 0.02643
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.040983
|  |  |  | Coincident | 0.023053
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.043478
|  |  |  | Coincident | 0.023815
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Lameroo 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.3347
|  |  |  | Coincident | 1.3347
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.3643
|  |  |  | Coincident | 1.3643
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.01031
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.3347
|  |  |  | Coincident | 1.3347
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.3643
|  |  |  | Coincident | 1.3643
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.2386
|  |  |  | Coincident | 1.2386
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.266
|  |  |  | Coincident | 1.266
| Langhorne Creek 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 3.845
|  |  |  | Coincident | 3.6805
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.1674
|  |  |  | Coincident | 3.998
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.053872
|  |  |  | Coincident | 0.018929
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.8875
|  |  |  | Coincident | 3.7551
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.2182
|  |  |  | Coincident | 4.0882
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.5536
|  |  |  | Coincident | 3.4325
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.8559
|  |  |  | Coincident | 3.7371
| Largs North 7.6kV | Substation Rating | MVA | Non-Coincident | 27.4987
|  |  |  | Coincident | 27.4987
|  | Raw Adjusted MD | MW | Non-Coincident | 16.2948
|  |  |  | Coincident | 16.2948
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.7559
|  |  |  | Coincident | 16.7559
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.10944
|  |  |  | Coincident | 0.10944
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.3349
|  |  |  | Coincident | 16.3349
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.797
|  |  |  | Coincident | 16.797
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.4842
|  |  |  | Coincident | 14.4842
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.8939
|  |  |  | Coincident | 14.8939
| Lefevre 11kV | Substation Rating | MVA | Non-Coincident | 72.1769
|  |  |  | Coincident | 72.1769
|  | Raw Adjusted MD | MW | Non-Coincident | 9.17
|  |  |  | Coincident | 6.12
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.4639
|  |  |  | Coincident | 6.4416
|  | Date MD occurred |  | Non-Coincident | 2018-11-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.39583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.071317
|  |  |  | Coincident | 0.002772
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.2051
|  |  |  | Coincident | 6.3599
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.7135
|  |  |  | Coincident | 6.6919
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.7186
|  |  |  | Coincident | 6.0238
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.2002
|  |  |  | Coincident | 6.3382
| Leigh Creek South 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.972
|  |  |  | Coincident | 0.758
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.97521
|  |  |  | Coincident | 0.76141
|  | Date MD occurred |  | Non-Coincident | 2019-01-30
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0019568
|  |  |  | Coincident | 0.0019568
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.24148
|  |  |  | Coincident | 0.22056
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.24152
|  |  |  | Coincident | 0.22142
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.23455
|  |  |  | Coincident | 0.21424
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.23459
|  |  |  | Coincident | 0.21507
| Linden Park 11kV | Substation Rating | MVA | Non-Coincident | 55.6587
|  |  |  | Coincident | 55.6587
|  | Raw Adjusted MD | MW | Non-Coincident | 40.6896
|  |  |  | Coincident | 40.6896
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.1098
|  |  |  | Coincident | 42.1098
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.20955
|  |  |  | Coincident | 0.20955
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 37.8938
|  |  |  | Coincident | 37.8938
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.2375
|  |  |  | Coincident | 39.2375
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.832
|  |  |  | Coincident | 33.832
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.0317
|  |  |  | Coincident | 35.0317
| Little Swamp 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.26982
|  |  |  | Coincident | 0.11458
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.27817
|  |  |  | Coincident | 0.11813
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.029813
|  |  |  | Coincident | 0.0036787
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.18902
|  |  |  | Coincident | 0.13375
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.19237
|  |  |  | Coincident | 0.13608
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.17802
|  |  |  | Coincident | 0.12597
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.18117
|  |  |  | Coincident | 0.12815
| Lobethal 11kV | Substation Rating | MVA | Non-Coincident | 12.8
|  |  |  | Coincident | 12.8
|  | Raw Adjusted MD | MW | Non-Coincident | 7.8908
|  |  |  | Coincident | 7.8773
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.1167
|  |  |  | Coincident | 8.1036
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.3281
|  |  |  | Coincident | 0.064899
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.6595
|  |  |  | Coincident | 7.6595
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.8795
|  |  |  | Coincident | 7.8795
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.209
|  |  |  | Coincident | 7.209
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.4161
|  |  |  | Coincident | 7.4161
| Lock 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.676
|  |  |  | Coincident | 0.659
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.69159
|  |  |  | Coincident | 0.67653
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.052829
|  |  |  | Coincident | 0.0043421
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.79381
|  |  |  | Coincident | 0.79321
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.81586
|  |  |  | Coincident | 0.81419
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.73069
|  |  |  | Coincident | 0.73014
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.751
|  |  |  | Coincident | 0.74945
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Loveday 11kV | Substation Rating | MVA | Non-Coincident | 20.3622
|  |  |  | Coincident | 20.3622
|  | Raw Adjusted MD | MW | Non-Coincident | 12.5692
|  |  |  | Coincident | 12.3983
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.6337
|  |  |  | Coincident | 12.4812
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.9375
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.093382
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.877
|  |  |  | Coincident | 12.4841
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.9425
|  |  |  | Coincident | 12.5724
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.7234
|  |  |  | Coincident | 11.3657
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.783
|  |  |  | Coincident | 11.446
| Lower Mitcham 11kV | Substation Rating | MVA | Non-Coincident | 28.2171
|  |  |  | Coincident | 28.2171
|  | Raw Adjusted MD | MW | Non-Coincident | 19.6224
|  |  |  | Coincident | 19.6224
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.0948
|  |  |  | Coincident | 20.0948
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.1166
|  |  |  | Coincident | 0.1166
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.7282
|  |  |  | Coincident | 19.7282
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.2043
|  |  |  | Coincident | 20.2043
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.1642
|  |  |  | Coincident | 17.1642
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.5784
|  |  |  | Coincident | 17.5784
| Loxton 11kV | Substation Rating | MVA | Non-Coincident | 19.9052
|  |  |  | Coincident | 19.9052
|  | Raw Adjusted MD | MW | Non-Coincident | 12.6458
|  |  |  | Coincident | 11.8583
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.5132
|  |  |  | Coincident | 12.298
|  | Date MD occurred |  | Non-Coincident | 2019-01-25
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.375
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.359
|  |  |  | Coincident | 0.061462
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.3295
|  |  |  | Coincident | 13.173
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.9488
|  |  |  | Coincident | 13.6301
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.4431
|  |  |  | Coincident | 12.297
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.0212
|  |  |  | Coincident | 12.7237
| Lucindale 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.375
|  |  |  | Coincident | 1.375
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.4164
|  |  |  | Coincident | 1.4164
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.007951
|  |  |  | Coincident | 0.007951
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.4525
|  |  |  | Coincident | 1.4005
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.4942
|  |  |  | Coincident | 1.4379
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.3194
|  |  |  | Coincident | 1.2721
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.3573
|  |  |  | Coincident | 1.3062
| Lyndoch 11kV | Substation Rating | MVA | Non-Coincident | 4.3
|  |  |  | Coincident | 4.3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.748
|  |  |  | Coincident | 2.748
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.8449
|  |  |  | Coincident | 2.8387
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.43653
|  |  |  | Coincident | 0.027648
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.9032
|  |  |  | Coincident | 2.9032
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0056
|  |  |  | Coincident | 2.9923
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.6421
|  |  |  | Coincident | 2.6421
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.7352
|  |  |  | Coincident | 2.7232
| Lyndoch South 7.6kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.32514
|  |  |  | Coincident | 0.30013
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.34225
|  |  |  | Coincident | 0.31593
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0075743
|  |  |  | Coincident | 0.0019202
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.29336
|  |  |  | Coincident | 0.26117
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.30879
|  |  |  | Coincident | 0.27492
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.27103
|  |  |  | Coincident | 0.2413
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.2853
|  |  |  | Coincident | 0.254
| Lyrup 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 4.1736
|  |  |  | Coincident | 2.9658
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.3501
|  |  |  | Coincident | 3.1344
|  | Date MD occurred |  | Non-Coincident | 2018-12-07
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.91667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.020626
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.2661
|  |  |  | Coincident | 3.2896
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.4516
|  |  |  | Coincident | 3.5397
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.9038
|  |  |  | Coincident | 3.0103
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.0736
|  |  |  | Coincident | 3.2391
| MacGillivray 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.944
|  |  |  | Coincident | 1.929
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.954
|  |  |  | Coincident | 1.9402
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.030446
|  |  |  | Coincident | 0.016821
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.8391
|  |  |  | Coincident | 1.8391
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.8491
|  |  |  | Coincident | 1.8491
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.6419
|  |  |  | Coincident | 1.6419
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6508
|  |  |  | Coincident | 1.6508
| Maitland 11kV | Substation Rating | MVA | Non-Coincident | 7.125
|  |  |  | Coincident | 7.125
|  | Raw Adjusted MD | MW | Non-Coincident | 3.8734
|  |  |  | Coincident | 3.8734
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.0772
|  |  |  | Coincident | 4.0772
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.21848
|  |  |  | Coincident | 0.043216
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.539
|  |  |  | Coincident | 3.539
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.7252
|  |  |  | Coincident | 3.7252
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.2396
|  |  |  | Coincident | 3.2396
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.4101
|  |  |  | Coincident | 3.4101
| Mallala 11kV | Substation Rating | MVA | Non-Coincident | 7.8
|  |  |  | Coincident | 7.8
|  | Raw Adjusted MD | MW | Non-Coincident | 4.385
|  |  |  | Coincident | 4.287
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.5677
|  |  |  | Coincident | 4.4686
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.035197
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.8905
|  |  |  | Coincident | 3.8905
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.0553
|  |  |  | Coincident | 4.0553
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.5781
|  |  |  | Coincident | 3.5781
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.7296
|  |  |  | Coincident | 3.7296
| Mannum Town 7.6kV | Substation Rating | MVA | Non-Coincident | 7.8
|  |  |  | Coincident | 7.8
|  | Raw Adjusted MD | MW | Non-Coincident | 4.334
|  |  |  | Coincident | 4.334
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.4759
|  |  |  | Coincident | 4.4714
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.19358
|  |  |  | Coincident | 0.038291
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.2871
|  |  |  | Coincident | 3.7653
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.4274
|  |  |  | Coincident | 3.8856
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.8158
|  |  |  | Coincident | 3.3514
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.9408
|  |  |  | Coincident | 3.4585
| Marion Bay 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.475
|  |  |  | Coincident | 0.453
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.47636
|  |  |  | Coincident | 0.45917
|  | Date MD occurred |  | Non-Coincident | 2019-01-04
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.020833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.005099
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.45881
|  |  |  | Coincident | 0.41992
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.46049
|  |  |  | Coincident | 0.42724
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.42064
|  |  |  | Coincident | 0.38498
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.42219
|  |  |  | Coincident | 0.3917
| Marrabel 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 0.953
|  |  |  | Coincident | 0.908
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.96129
|  |  |  | Coincident | 0.91576
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.058816
|  |  |  | Coincident | 0.011634
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.97721
|  |  |  | Coincident | 0.86646
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.98571
|  |  |  | Coincident | 0.87325
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.88843
|  |  |  | Coincident | 0.78775
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.89616
|  |  |  | Coincident | 0.79392
| McLaren Flat TF1 11kV | Substation Rating | MVA | Non-Coincident | 15.5
|  |  |  | Coincident | 15.5
|  | Raw Adjusted MD | MW | Non-Coincident | 7.38
|  |  |  | Coincident | 3.45
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.11
|  |  |  | Coincident | 3.79
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.599
|  |  |  | Coincident | 0.065525
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.2734
|  |  |  | Coincident | 8.3232
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.2734
|  |  |  | Coincident | 8.3232
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.193
|  |  |  | Coincident | 7.3534
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.193
|  |  |  | Coincident | 7.3534
| McLaren Flat TF2 11kV | Substation Rating | MVA | Non-Coincident | 15.2
|  |  |  | Coincident | 15.2
|  | Raw Adjusted MD | MW | Non-Coincident | 2.56
|  |  |  | Coincident | 1.06
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.67
|  |  |  | Coincident | 1.1
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11795
|  |  |  | Coincident | 0.018848
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.5206
|  |  |  | Coincident | 2.2628
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.7047
|  |  |  | Coincident | 2.3625
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.2582
|  |  |  | Coincident | 2.0272
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4231
|  |  |  | Coincident | 2.1165
| McLaren Vale 11kV | Substation Rating | MVA | Non-Coincident | 5.4
|  |  |  | Coincident | 5.4
|  | Raw Adjusted MD | MW | Non-Coincident | 2.6372
|  |  |  | Coincident | 2.458
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.7188
|  |  |  | Coincident | 2.534
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.12301
|  |  |  | Coincident | 0.024331
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.7273
|  |  |  | Coincident | 2.6355
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.8257
|  |  |  | Coincident | 2.7297
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.3677
|  |  |  | Coincident | 2.288
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4532
|  |  |  | Coincident | 2.3698
| McLaren Vale Vineyard 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.19419
|  |  |  | Coincident | 0.17782
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.19457
|  |  |  | Coincident | 0.17913
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.19419
|  |  |  | Coincident | 0.17782
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.19457
|  |  |  | Coincident | 0.17913
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.17187
|  |  |  | Coincident | 0.15738
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.17221
|  |  |  | Coincident | 0.15854
| Meadows 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 6.6489
|  |  |  | Coincident | 6.4948
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.9512
|  |  |  | Coincident | 6.8092
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.15559
|  |  |  | Coincident | 0.085958
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.9046
|  |  |  | Coincident | 5.9046
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.1816
|  |  |  | Coincident | 6.1816
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.4712
|  |  |  | Coincident | 5.4712
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.7278
|  |  |  | Coincident | 5.7278
| Melrose 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.31132
|  |  |  | Coincident | 0.24073
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.3277
|  |  |  | Coincident | 0.2534
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.018557
|  |  |  | Coincident | 0.0036706
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.34286
|  |  |  | Coincident | 0.26915
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.34402
|  |  |  | Coincident | 0.27051
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.31312
|  |  |  | Coincident | 0.24581
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.31419
|  |  |  | Coincident | 0.24705
| Meningie 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.2026
|  |  |  | Coincident | 2.2026
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.2626
|  |  |  | Coincident | 2.2542
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.095298
|  |  |  | Coincident | 0.01885
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.9937
|  |  |  | Coincident | 1.9937
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0442
|  |  |  | Coincident | 2.0374
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.8628
|  |  |  | Coincident | 1.8628
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.91
|  |  |  | Coincident | 1.9036
| Milang 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 3.9335
|  |  |  | Coincident | 3.6248
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.1508
|  |  |  | Coincident | 3.7624
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.18255
|  |  |  | Coincident | 0.030412
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.4362
|  |  |  | Coincident | 3.2279
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.6363
|  |  |  | Coincident | 3.3503
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.1417
|  |  |  | Coincident | 2.9512
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.3245
|  |  |  | Coincident | 3.0631
| Millicent 11kV | Substation Rating | MVA | Non-Coincident | 13.2
|  |  |  | Coincident | 13.2
|  | Raw Adjusted MD | MW | Non-Coincident | 5.7489
|  |  |  | Coincident | 5.7489
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.9729
|  |  |  | Coincident | 5.9729
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.29725
|  |  |  | Coincident | 0.058797
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.0801
|  |  |  | Coincident | 6.0801
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.317
|  |  |  | Coincident | 6.317
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.5305
|  |  |  | Coincident | 5.5305
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.746
|  |  |  | Coincident | 5.746
| Minlaton 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.8528
|  |  |  | Coincident | 1.7907
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.9503
|  |  |  | Coincident | 1.8849
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.040478
|  |  |  | Coincident | 0.022363
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.6879
|  |  |  | Coincident | 1.603
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.7767
|  |  |  | Coincident | 1.6873
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.5981
|  |  |  | Coincident | 1.5177
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6822
|  |  |  | Coincident | 1.5975
| Monarto Central 11kV | Substation Rating | MVA | Non-Coincident | 8.1
|  |  |  | Coincident | 8.1
|  | Raw Adjusted MD | MW | Non-Coincident | 2.467
|  |  |  | Coincident | 1.339
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.6189
|  |  |  | Coincident | 1.366
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.41667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0123
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.5223
|  |  |  | Coincident | 1.3891
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.6426
|  |  |  | Coincident | 1.4159
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4363
|  |  |  | Coincident | 1.3417
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.5525
|  |  |  | Coincident | 1.3677
| Monarto South 11kV | Substation Rating | MVA | Non-Coincident | 14.5
|  |  |  | Coincident | 14.5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.8838
|  |  |  | Coincident | 2.8838
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.3533
|  |  |  | Coincident | 3.3533
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015725
|  |  |  | Coincident | 0.015725
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.6949
|  |  |  | Coincident | 2.6717
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.1336
|  |  |  | Coincident | 3.1066
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4474
|  |  |  | Coincident | 2.4264
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.8459
|  |  |  | Coincident | 2.8213
| Moonta 11kV | Substation Rating | MVA | Non-Coincident | 12.8
|  |  |  | Coincident | 12.8
|  | Raw Adjusted MD | MW | Non-Coincident | 9.0681
|  |  |  | Coincident | 9.0681
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.5453
|  |  |  | Coincident | 9.5453
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.17101
|  |  |  | Coincident | 0.094481
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.3813
|  |  |  | Coincident | 8.3813
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.8224
|  |  |  | Coincident | 8.8224
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.6472
|  |  |  | Coincident | 7.6472
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.0497
|  |  |  | Coincident | 8.0497
| Moorkitabie 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.692
|  |  |  | Coincident | 0.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.69514
|  |  |  | Coincident | 0.50001
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0095725
|  |  |  | Coincident | 0.0052886
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.59329
|  |  |  | Coincident | 0.49699
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.59572
|  |  |  | Coincident | 0.49795
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.54412
|  |  |  | Coincident | 0.4558
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.54635
|  |  |  | Coincident | 0.45668
| Morgan 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.144
|  |  |  | Coincident | 0.931
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.1743
|  |  |  | Coincident | 0.95851
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.035378
|  |  |  | Coincident | 0.009162
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.9975
|  |  |  | Coincident | 0.55232
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.0254
|  |  |  | Coincident | 0.57541
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.87883
|  |  |  | Coincident | 0.48661
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.90338
|  |  |  | Coincident | 0.50695
| Morphett Vale East 11kV | Substation Rating | MVA | Non-Coincident | 57.3425
|  |  |  | Coincident | 57.3425
|  | Raw Adjusted MD | MW | Non-Coincident | 35.8047
|  |  |  | Coincident | 35.8047
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.368
|  |  |  | Coincident | 36.368
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.30572
|  |  |  | Coincident | 0.30572
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.5758
|  |  |  | Coincident | 36.3622
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.1599
|  |  |  | Coincident | 36.9019
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.8324
|  |  |  | Coincident | 31.6465
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.3408
|  |  |  | Coincident | 32.1162
| Morphettville 11kV | Substation Rating | MVA | Non-Coincident | 27.9874
|  |  |  | Coincident | 27.9874
|  | Raw Adjusted MD | MW | Non-Coincident | 24.7295
|  |  |  | Coincident | 24.7295
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.4164
|  |  |  | Coincident | 25.4164
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11084
|  |  |  | Coincident | 0.11084
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.9428
|  |  |  | Coincident | 22.9428
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.5667
|  |  |  | Coincident | 23.5667
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.9326
|  |  |  | Coincident | 19.9326
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.4746
|  |  |  | Coincident | 20.4746
| Mount Barker 11kV | Substation Rating | MVA | Non-Coincident | 72.39
|  |  |  | Coincident | 72.39
|  | Raw Adjusted MD | MW | Non-Coincident | 28.21
|  |  |  | Coincident | 28.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.278
|  |  |  | Coincident | 28.278
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.23677
|  |  |  | Coincident | 0.23677
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.6165
|  |  |  | Coincident | 24.6165
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.6849
|  |  |  | Coincident | 24.6849
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.1476
|  |  |  | Coincident | 22.1476
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.2091
|  |  |  | Coincident | 22.2091
| Mount Burr 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.32655
|  |  |  | Coincident | 0.32655
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.33619
|  |  |  | Coincident | 0.33619
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0032162
|  |  |  | Coincident | 0.0032162
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.32655
|  |  |  | Coincident | 0.32655
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.33619
|  |  |  | Coincident | 0.33619
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.28748
|  |  |  | Coincident | 0.28748
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.29596
|  |  |  | Coincident | 0.29596
| Mount Gambier 11kV | Substation Rating | MVA | Non-Coincident | 25.4441
|  |  |  | Coincident | 25.4441
|  | Raw Adjusted MD | MW | Non-Coincident | 13.6204
|  |  |  | Coincident | 13.0264
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.6224
|  |  |  | Coincident | 13.0265
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.5194
|  |  |  | Coincident | 0.10274
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.1432
|  |  |  | Coincident | 13.8651
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.1452
|  |  |  | Coincident | 13.8688
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.4981
|  |  |  | Coincident | 12.2523
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.4998
|  |  |  | Coincident | 12.2556
| Mount Gambier North 11kV | Substation Rating | MVA | Non-Coincident | 17
|  |  |  | Coincident | 17
|  | Raw Adjusted MD | MW | Non-Coincident | 9.6452
|  |  |  | Coincident | 9.1757
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.047
|  |  |  | Coincident | 9.558
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.76782
|  |  |  | Coincident | 0.048631
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.659
|  |  |  | Coincident | 7.8029
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.0614
|  |  |  | Coincident | 8.1281
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.7629
|  |  |  | Coincident | 7.079
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.128
|  |  |  | Coincident | 7.374
| Mount Gambier West 11kV | Substation Rating | MVA | Non-Coincident | 25.636
|  |  |  | Coincident | 25.636
|  | Raw Adjusted MD | MW | Non-Coincident | 15.7177
|  |  |  | Coincident | 12.8303
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.7867
|  |  |  | Coincident | 12.8304
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.6224
|  |  |  | Coincident | 0.069067
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.7332
|  |  |  | Coincident | 13.9632
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.8297
|  |  |  | Coincident | 14.0131
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.0212
|  |  |  | Coincident | 12.5346
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.1078
|  |  |  | Coincident | 12.5794
| Mount Pleasant 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 2.6558
|  |  |  | Coincident | 2.471
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.7664
|  |  |  | Coincident | 2.574
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.024219
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.2891
|  |  |  | Coincident | 2.2744
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.363
|  |  |  | Coincident | 2.3502
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.1034
|  |  |  | Coincident | 2.0899
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.1713
|  |  |  | Coincident | 2.1596
| Mount Schank 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.638
|  |  |  | Coincident | 1.361
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.0233
|  |  |  | Coincident | 1.5078
|  | Date MD occurred |  | Non-Coincident | 2019-02-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.29167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.014767
|  |  |  | Coincident | 0.0037971
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.7468
|  |  |  | Coincident | 1.9741
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.1862
|  |  |  | Coincident | 2.2551
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.5233
|  |  |  | Coincident | 1.8134
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.9269
|  |  |  | Coincident | 2.0717
| Murray Bridge North 11kV | Substation Rating | MVA | Non-Coincident | 26.0138
|  |  |  | Coincident | 26.0138
|  | Raw Adjusted MD | MW | Non-Coincident | 13.9238
|  |  |  | Coincident | 13.8783
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.0149
|  |  |  | Coincident | 13.935
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.9509
|  |  |  | Coincident | 0.09976
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.9097
|  |  |  | Coincident | 12.8936
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.9575
|  |  |  | Coincident | 12.9437
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.6839
|  |  |  | Coincident | 11.6693
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.7271
|  |  |  | Coincident | 11.7146
| Murray Bridge South 11kV | Substation Rating | MVA | Non-Coincident | 28.5
|  |  |  | Coincident | 28.5
|  | Raw Adjusted MD | MW | Non-Coincident | 16.1324
|  |  |  | Coincident | 16.0741
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.7474
|  |  |  | Coincident | 16.4862
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.4805
|  |  |  | Coincident | 0.12684
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.4657
|  |  |  | Coincident | 15.2156
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.0294
|  |  |  | Coincident | 15.6662
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.8143
|  |  |  | Coincident | 13.5909
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.3178
|  |  |  | Coincident | 13.9934
| Mylor 11kV | Substation Rating | MVA | Non-Coincident | 4.6
|  |  |  | Coincident | 4.6
|  | Raw Adjusted MD | MW | Non-Coincident | 2.657
|  |  |  | Coincident | 2.657
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.7063
|  |  |  | Coincident | 2.7063
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.039927
|  |  |  | Coincident | 0.039927
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.3432
|  |  |  | Coincident | 2.2726
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.3892
|  |  |  | Coincident | 2.3196
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.1915
|  |  |  | Coincident | 2.1255
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.2346
|  |  |  | Coincident | 2.1694
| Mypolonga 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 2.611
|  |  |  | Coincident | 2.345
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.7136
|  |  |  | Coincident | 2.4383
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.018219
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.6484
|  |  |  | Coincident | 2.2742
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.7541
|  |  |  | Coincident | 2.363
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.3997
|  |  |  | Coincident | 2.0607
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4955
|  |  |  | Coincident | 2.1411
| Myponga 11kV | Substation Rating | MVA | Non-Coincident | 14.102
|  |  |  | Coincident | 14.102
|  | Raw Adjusted MD | MW | Non-Coincident | 6.0586
|  |  |  | Coincident | 6.0545
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.3233
|  |  |  | Coincident | 6.2887
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.055277
|  |  |  | Coincident | 0.046017
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.8739
|  |  |  | Coincident | 6.8739
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.1389
|  |  |  | Coincident | 7.1389
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.1978
|  |  |  | Coincident | 6.1978
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.4368
|  |  |  | Coincident | 6.4368
| Nairne 11kV | Substation Rating | MVA | Non-Coincident | 9.2
|  |  |  | Coincident | 9.2
|  | Raw Adjusted MD | MW | Non-Coincident | 7.764
|  |  |  | Coincident | 7.682
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.0308
|  |  |  | Coincident | 7.9393
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.089617
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.5689
|  |  |  | Coincident | 6.4995
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.7947
|  |  |  | Coincident | 6.7173
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.9982
|  |  |  | Coincident | 5.9348
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.2043
|  |  |  | Coincident | 6.1336
| Nangwarry 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.821
|  |  |  | Coincident | 0.651
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.92912
|  |  |  | Coincident | 0.67283
|  | Date MD occurred |  | Non-Coincident | 2018-11-08
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.29167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.035269
|  |  |  | Coincident | 0.0042145
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.91226
|  |  |  | Coincident | 0.72932
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.9441
|  |  |  | Coincident | 0.7586
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.8101
|  |  |  | Coincident | 0.64765
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.83838
|  |  |  | Coincident | 0.67365
| Naracoorte 11kV | Substation Rating | MVA | Non-Coincident | 27.8
|  |  |  | Coincident | 27.8
|  | Raw Adjusted MD | MW | Non-Coincident | 10.6549
|  |  |  | Coincident | 10.2009
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.1769
|  |  |  | Coincident | 10.7992
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.4115
|  |  |  | Coincident | 0.081396
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.3034
|  |  |  | Coincident | 12.2679
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.9413
|  |  |  | Coincident | 12.9013
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.9221
|  |  |  | Coincident | 10.8906
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.4884
|  |  |  | Coincident | 11.4529
| Naracoorte East 11kV | Substation Rating | MVA | Non-Coincident | 17.2
|  |  |  | Coincident | 17.2
|  | Raw Adjusted MD | MW | Non-Coincident | 5.0641
|  |  |  | Coincident | 4.2509
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.755
|  |  |  | Coincident | 4.6552
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.47917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.29829
|  |  |  | Coincident | 0.0081221
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.0567
|  |  |  | Coincident | 4.3731
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.7444
|  |  |  | Coincident | 4.9157
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.7912
|  |  |  | Coincident | 4.1434
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.4427
|  |  |  | Coincident | 4.6576
| Narrung 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.3713
|  |  |  | Coincident | 0.55628
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.4137
|  |  |  | Coincident | 0.57348
|  | Date MD occurred |  | Non-Coincident | 2018-12-10
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.026393
|  |  |  | Coincident | 0.0009387
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.2979
|  |  |  | Coincident | 1.0372
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.338
|  |  |  | Coincident | 1.0693
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.2181
|  |  |  | Coincident | 0.97342
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.2557
|  |  |  | Coincident | 1.0035
| New Osborne 11kV | Substation Rating | MVA | Non-Coincident | 9.5
|  |  |  | Coincident | 9.5
|  | Raw Adjusted MD | MW | Non-Coincident | 1.6563
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.7108
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.47917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.1591
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.2305
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.8093
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8691
|  |  |  | Coincident | 0
| New Richmond 11kV | Substation Rating | MVA | Non-Coincident | 51.1293
|  |  |  | Coincident | 51.1293
|  | Raw Adjusted MD | MW | Non-Coincident | 32.6474
|  |  |  | Coincident | 32.6474
|  | Raw Adjusted MD | MVA | Non-Coincident | 34.0025
|  |  |  | Coincident | 34.0025
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.13327
|  |  |  | Coincident | 0.13327
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.9507
|  |  |  | Coincident | 33.9507
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.3329
|  |  |  | Coincident | 35.3329
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.18
|  |  |  | Coincident | 30.18
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.4087
|  |  |  | Coincident | 31.4087
| Nildottie 11kV | Substation Rating | MVA | Non-Coincident | 4.94
|  |  |  | Coincident | 4.94
|  | Raw Adjusted MD | MW | Non-Coincident | 1.926
|  |  |  | Coincident | 1.493
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.9381
|  |  |  | Coincident | 1.4938
|  | Date MD occurred |  | Non-Coincident | 2019-01-13
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.036047
|  |  |  | Coincident | 0.0071302
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.1083
|  |  |  | Coincident | 1.8894
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.1215
|  |  |  | Coincident | 1.8952
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.9171
|  |  |  | Coincident | 1.718
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.9291
|  |  |  | Coincident | 1.7233
| Ninnes 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.84625
|  |  |  | Coincident | 0.84625
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.86666
|  |  |  | Coincident | 0.86666
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.010222
|  |  |  | Coincident | 0.010222
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.84625
|  |  |  | Coincident | 0.84625
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.86666
|  |  |  | Coincident | 0.86666
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.79139
|  |  |  | Coincident | 0.79139
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.81047
|  |  |  | Coincident | 0.81047
| Noarlunga Centre 11kV | Substation Rating | MVA | Non-Coincident | 28.2723
|  |  |  | Coincident | 28.2723
|  | Raw Adjusted MD | MW | Non-Coincident | 19.2829
|  |  |  | Coincident | 18.7769
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.2598
|  |  |  | Coincident | 19.3922
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.4219
|  |  |  | Coincident | 0.060532
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.3488
|  |  |  | Coincident | 19.8558
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.373
|  |  |  | Coincident | 20.5224
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.3812
|  |  |  | Coincident | 17.9359
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.3064
|  |  |  | Coincident | 18.5381
| North Adelaide 11kV | Substation Rating | MVA | Non-Coincident | 72.104
|  |  |  | Coincident | 72.104
|  | Raw Adjusted MD | MW | Non-Coincident | 20.89
|  |  |  | Coincident | 19.96
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.4078
|  |  |  | Coincident | 20.3092
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.5163
|  |  |  | Coincident | 0.064552
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.2919
|  |  |  | Coincident | 19.7374
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.8053
|  |  |  | Coincident | 20.1079
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.3316
|  |  |  | Coincident | 17.8307
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.7954
|  |  |  | Coincident | 18.1654
| North Unley 11kV | Substation Rating | MVA | Non-Coincident | 25.3934
|  |  |  | Coincident | 25.3934
|  | Raw Adjusted MD | MW | Non-Coincident | 16.7893
|  |  |  | Coincident | 15.7474
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.5969
|  |  |  | Coincident | 16.234
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.5123
|  |  |  | Coincident | 0.064381
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.7225
|  |  |  | Coincident | 16.6688
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.5796
|  |  |  | Coincident | 17.1936
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.5758
|  |  |  | Coincident | 14.6498
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.3291
|  |  |  | Coincident | 15.111
| Northfield 11kV | Substation Rating | MVA | Non-Coincident | 26.5321
|  |  |  | Coincident | 26.5321
|  | Raw Adjusted MD | MW | Non-Coincident | 20.5475
|  |  |  | Coincident | 20.5475
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.4647
|  |  |  | Coincident | 21.4647
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.14754
|  |  |  | Coincident | 0.14754
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.3693
|  |  |  | Coincident | 20.1771
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.2964
|  |  |  | Coincident | 21.0878
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.3264
|  |  |  | Coincident | 18.1535
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.1605
|  |  |  | Coincident | 18.9728
| Norwood 11kV | Substation Rating | MVA | Non-Coincident | 73.7958
|  |  |  | Coincident | 73.7958
|  | Raw Adjusted MD | MW | Non-Coincident | 58.2201
|  |  |  | Coincident | 58.2201
|  | Raw Adjusted MD | MVA | Non-Coincident | 58.2956
|  |  |  | Coincident | 58.2956
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.29626
|  |  |  | Coincident | 0.29626
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 55.5757
|  |  |  | Coincident | 55.5757
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 55.6488
|  |  |  | Coincident | 55.6488
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 49.6027
|  |  |  | Coincident | 49.6027
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 49.6679
|  |  |  | Coincident | 49.6679
| Nuriootpa 11kV | Substation Rating | MVA | Non-Coincident | 13.4
|  |  |  | Coincident | 13.4
|  | Raw Adjusted MD | MW | Non-Coincident | 12.0904
|  |  |  | Coincident | 12.0086
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.5987
|  |  |  | Coincident | 12.4113
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.6877
|  |  |  | Coincident | 0.086305
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.8622
|  |  |  | Coincident | 11.8269
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.2505
|  |  |  | Coincident | 12.2189
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.8158
|  |  |  | Coincident | 10.7836
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.1699
|  |  |  | Coincident | 11.1411
| Oaklands 11kV | Substation Rating | MVA | Non-Coincident | 57.4996
|  |  |  | Coincident | 57.4996
|  | Raw Adjusted MD | MW | Non-Coincident | 48.0009
|  |  |  | Coincident | 48.0009
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.397
|  |  |  | Coincident | 48.397
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.2146
|  |  |  | Coincident | 0.2146
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 45.5116
|  |  |  | Coincident | 45.4585
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.8841
|  |  |  | Coincident | 45.8269
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 40.3362
|  |  |  | Coincident | 40.2891
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.6663
|  |  |  | Coincident | 40.6156
| Orroroo 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.372
|  |  |  | Coincident | 1.372
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.3791
|  |  |  | Coincident | 1.3791
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.015937
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.372
|  |  |  | Coincident | 1.372
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.3791
|  |  |  | Coincident | 1.3791
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.2558
|  |  |  | Coincident | 1.2558
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.2623
|  |  |  | Coincident | 1.2623
| Padthaway 11kV | Substation Rating | MVA | Non-Coincident | 13.8
|  |  |  | Coincident | 13.8
|  | Raw Adjusted MD | MW | Non-Coincident | 3.7509
|  |  |  | Coincident | 2.9271
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.8956
|  |  |  | Coincident | 3.0336
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0096685
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.9633
|  |  |  | Coincident | 3.1882
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.1227
|  |  |  | Coincident | 3.3043
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.5832
|  |  |  | Coincident | 2.8824
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.7273
|  |  |  | Coincident | 2.9874
| Palmer 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.032624
|  |  |  | Coincident | 0.032624
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.033495
|  |  |  | Coincident | 0.033495
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0023621
|  |  |  | Coincident | 0.001305
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.032624
|  |  |  | Coincident | 0.032624
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.033495
|  |  |  | Coincident | 0.033495
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.028022
|  |  |  | Coincident | 0.028022
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.028769
|  |  |  | Coincident | 0.028769
| Panorama 11kV | Substation Rating | MVA | Non-Coincident | 58.2
|  |  |  | Coincident | 58.2
|  | Raw Adjusted MD | MW | Non-Coincident | 25.51
|  |  |  | Coincident | 25.51
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.9375
|  |  |  | Coincident | 25.9375
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.15252
|  |  |  | Coincident | 0.15252
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.6653
|  |  |  | Coincident | 25.6653
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.1019
|  |  |  | Coincident | 26.1019
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.3739
|  |  |  | Coincident | 22.3739
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.7544
|  |  |  | Coincident | 22.7544
| Parafield Gardens 11kV | Substation Rating | MVA | Non-Coincident | 70.2
|  |  |  | Coincident | 70.2
|  | Raw Adjusted MD | MW | Non-Coincident | 28.8
|  |  |  | Coincident | 28.53
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.2223
|  |  |  | Coincident | 28.9683
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.23885
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.503
|  |  |  | Coincident | 28.4137
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.9222
|  |  |  | Coincident | 28.8402
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.6317
|  |  |  | Coincident | 25.5515
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.0087
|  |  |  | Coincident | 25.935
| Paralowie 11kV | Substation Rating | MVA | Non-Coincident | 27.4831
|  |  |  | Coincident | 27.4831
|  | Raw Adjusted MD | MW | Non-Coincident | 18.7109
|  |  |  | Coincident | 17.7273
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.7334
|  |  |  | Coincident | 17.8642
|  | Date MD occurred |  | Non-Coincident | 2018-12-19
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11786
|  |  |  | Coincident | 0.10382
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.3058
|  |  |  | Coincident | 18.3764
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.3284
|  |  |  | Coincident | 18.531
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.8809
|  |  |  | Coincident | 17.0201
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.9018
|  |  |  | Coincident | 17.1633
| Parilla 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.66957
|  |  |  | Coincident | 0.5572
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.70481
|  |  |  | Coincident | 0.58653
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0085936
|  |  |  | Coincident | 0.00070632
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.76981
|  |  |  | Coincident | 0.64062
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.81033
|  |  |  | Coincident | 0.67433
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.70568
|  |  |  | Coincident | 0.58725
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.74282
|  |  |  | Coincident | 0.61816
| Paringa 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 2.4994
|  |  |  | Coincident | 2.3176
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.5814
|  |  |  | Coincident | 2.3936
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015286
|  |  |  | Coincident | 0.023412
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.6684
|  |  |  | Coincident | 2.6163
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.7568
|  |  |  | Coincident | 2.7029
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.4108
|  |  |  | Coincident | 2.3637
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.4906
|  |  |  | Coincident | 2.4419
| Paringa 33kV | Substation Rating | MVA | Non-Coincident | 36.575
|  |  |  | Coincident | 36.575
|  | Raw Adjusted MD | MW | Non-Coincident | 15.2278
|  |  |  | Coincident | 8.1321
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.8098
|  |  |  | Coincident | 8.4718
|  | Date MD occurred |  | Non-Coincident | 2019-01-25
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.3125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.47146
|  |  |  | Coincident | 0.045211
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.2619
|  |  |  | Coincident | 11.3139
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.946
|  |  |  | Coincident | 11.7965
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.018
|  |  |  | Coincident | 10.4485
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.6498
|  |  |  | Coincident | 10.8942
| Paskeville 11kV | Substation Rating | MVA | Non-Coincident | 1.235
|  |  |  | Coincident | 1.235
|  | Raw Adjusted MD | MW | Non-Coincident | 0.31269
|  |  |  | Coincident | 0.31269
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.32023
|  |  |  | Coincident | 0.32023
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0045536
|  |  |  | Coincident | 0.0045536
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.31269
|  |  |  | Coincident | 0.31269
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.32023
|  |  |  | Coincident | 0.32023
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.29286
|  |  |  | Coincident | 0.29286
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.29992
|  |  |  | Coincident | 0.29992
| Peake 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.17096
|  |  |  | Coincident | 0.17096
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.17475
|  |  |  | Coincident | 0.17475
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0015552
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.17096
|  |  |  | Coincident | 0.17096
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.17475
|  |  |  | Coincident | 0.17475
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.15885
|  |  |  | Coincident | 0.15885
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.16237
|  |  |  | Coincident | 0.16237
| Pellaring Flat 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.089031
|  |  |  | Coincident | 0.089031
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.091402
|  |  |  | Coincident | 0.091402
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00092008
|  |  |  | Coincident | 0.00050832
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.089031
|  |  |  | Coincident | 0.089031
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.091402
|  |  |  | Coincident | 0.091402
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.081306
|  |  |  | Coincident | 0.081306
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.083471
|  |  |  | Coincident | 0.083471
| Penfield 11kV | Substation Rating | MVA | Non-Coincident | 51.3624
|  |  |  | Coincident | 51.3624
|  | Raw Adjusted MD | MW | Non-Coincident | 20.71
|  |  |  | Coincident | 18.18
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.7271
|  |  |  | Coincident | 18.8524
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.60417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.0103
|  |  |  | Coincident | 0.057709
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.831
|  |  |  | Coincident | 19.5219
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.2114
|  |  |  | Coincident | 20.2417
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.8716
|  |  |  | Coincident | 17.7698
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.1281
|  |  |  | Coincident | 18.425
| Penneshaw 11kV | Substation Rating | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.95
|  | Raw Adjusted MD | MW | Non-Coincident | 0.81545
|  |  |  | Coincident | 0.79259
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.81545
|  |  |  | Coincident | 0.79259
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.011417
|  |  |  | Coincident | 0.0063076
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.79175
|  |  |  | Coincident | 0.78455
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.79796
|  |  |  | Coincident | 0.79047
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.707
|  |  |  | Coincident | 0.70058
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.71255
|  |  |  | Coincident | 0.70586
| Penola 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.681
|  |  |  | Coincident | 2.566
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.7813
|  |  |  | Coincident | 2.6878
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.097264
|  |  |  | Coincident | 0.019239
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.9213
|  |  |  | Coincident | 2.4597
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0445
|  |  |  | Coincident | 2.5649
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.5976
|  |  |  | Coincident | 2.1872
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.7072
|  |  |  | Coincident | 2.2808
| Peterborough 11kV | Substation Rating | MVA | Non-Coincident | 6.2
|  |  |  | Coincident | 6.2
|  | Raw Adjusted MD | MW | Non-Coincident | 1.6751
|  |  |  | Coincident | 1.25
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.7313
|  |  |  | Coincident | 1.3532
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.32303
|  |  |  | Coincident | 0.02046
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.948
|  |  |  | Coincident | 1.7151
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0109
|  |  |  | Coincident | 1.7692
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.7751
|  |  |  | Coincident | 1.5629
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8325
|  |  |  | Coincident | 1.6122
| Piccadilly 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.787
|  |  |  | Coincident | 1.787
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.8096
|  |  |  | Coincident | 1.8096
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.017892
|  |  |  | Coincident | 0.017892
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7529
|  |  |  | Coincident | 1.7342
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.7759
|  |  |  | Coincident | 1.7581
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.637
|  |  |  | Coincident | 1.6195
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6584
|  |  |  | Coincident | 1.6418
| Pinnaroo 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.6909
|  |  |  | Coincident | 1.6909
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.7967
|  |  |  | Coincident | 1.7967
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0096687
|  |  |  | Coincident | 0.0096687
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7142
|  |  |  | Coincident | 1.6841
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.8214
|  |  |  | Coincident | 1.7894
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.5758
|  |  |  | Coincident | 1.5481
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6743
|  |  |  | Coincident | 1.6449
| Pinnaroo South 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.027
|  |  |  | Coincident | 0.008
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.027893
|  |  |  | Coincident | 0.008
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 9.36e-05
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.026548
|  |  |  | Coincident | 0.014686
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.028044
|  |  |  | Coincident | 0.014859
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.0246
|  |  |  | Coincident | 0.013609
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.025986
|  |  |  | Coincident | 0.013769
| Plympton 11kV | Substation Rating | MVA | Non-Coincident | 28.4291
|  |  |  | Coincident | 28.4291
|  | Raw Adjusted MD | MW | Non-Coincident | 21.9835
|  |  |  | Coincident | 20.897
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.7486
|  |  |  | Coincident | 21.5331
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.094546
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.5083
|  |  |  | Coincident | 22.8219
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.2823
|  |  |  | Coincident | 23.5235
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.1029
|  |  |  | Coincident | 20.4868
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.7977
|  |  |  | Coincident | 21.1166
| Point Boston 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.072
|  |  |  | Coincident | 1.054
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.1199
|  |  |  | Coincident | 1.1181
|  | Date MD occurred |  | Non-Coincident | 2019-03-11
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0006195
|  |  |  | Coincident | 0.000423
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.2303
|  |  |  | Coincident | 1.2056
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.2852
|  |  |  | Coincident | 1.2793
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.1791
|  |  |  | Coincident | 1.1554
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.2317
|  |  |  | Coincident | 1.2261
| Polda 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.874
|  |  |  | Coincident | 0.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.87483
|  |  |  | Coincident | 0.48001
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0095146
|  |  |  | Coincident | 0.0095146
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.74055
|  |  |  | Coincident | 0.67192
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.74171
|  |  |  | Coincident | 0.67218
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.68314
|  |  |  | Coincident | 0.61983
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.68421
|  |  |  | Coincident | 0.62007
| Poonindie 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.65341
|  |  |  | Coincident | 0.61721
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.6878
|  |  |  | Coincident | 0.64969
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.024349
|  |  |  | Coincident | 0.0048163
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.45767
|  |  |  | Coincident | 0.45378
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.46519
|  |  |  | Coincident | 0.46164
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.42587
|  |  |  | Coincident | 0.42225
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.43287
|  |  |  | Coincident | 0.42957
| Port Adelaide 11kV | Substation Rating | MVA | Non-Coincident | 24.5
|  |  |  | Coincident | 24.5
|  | Raw Adjusted MD | MW | Non-Coincident | 11.4629
|  |  |  | Coincident | 9.2914
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.3175
|  |  |  | Coincident | 9.8145
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.71608
|  |  |  | Coincident | 0.051739
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.1138
|  |  |  | Coincident | 10.7324
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.1157
|  |  |  | Coincident | 11.3366
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.5762
|  |  |  | Coincident | 9.4741
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.4607
|  |  |  | Coincident | 10.0075
| Port Adelaide North 11kV | Substation Rating | MVA | Non-Coincident | 47.1921
|  |  |  | Coincident | 47.1921
|  | Raw Adjusted MD | MW | Non-Coincident | 20.3825
|  |  |  | Coincident | 11.1986
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.7992
|  |  |  | Coincident | 11.6105
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.47917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.412
|  |  |  | Coincident | 1.1174
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.439
|  |  |  | Coincident | 12.5092
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.2037
|  |  |  | Coincident | 13.2114
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.0175
|  |  |  | Coincident | 11.6798
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.6651
|  |  |  | Coincident | 12.3354
| Port Augusta 11kV | Substation Rating | MVA | Non-Coincident | 28.4
|  |  |  | Coincident | 28.4
|  | Raw Adjusted MD | MW | Non-Coincident | 13.64
|  |  |  | Coincident | 13.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.1408
|  |  |  | Coincident | 13.8425
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.7138
|  |  |  | Coincident | 0.072961
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.5525
|  |  |  | Coincident | 13.5525
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.9173
|  |  |  | Coincident | 13.9173
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.2732
|  |  |  | Coincident | 12.2732
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.6035
|  |  |  | Coincident | 12.6035
| Port Augusta West TF1 11kV | Substation Rating | MVA | Non-Coincident | 14.8
|  |  |  | Coincident | 14.8
|  | Raw Adjusted MD | MW | Non-Coincident | 6.5996
|  |  |  | Coincident | 5.6214
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.7233
|  |  |  | Coincident | 5.7295
|  | Date MD occurred |  | Non-Coincident | 2018-11-19
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.25316
|  |  |  | Coincident | 0.032619
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.0741
|  |  |  | Coincident | 5.1738
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.1879
|  |  |  | Coincident | 5.2733
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.4317
|  |  |  | Coincident | 4.6266
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.5334
|  |  |  | Coincident | 4.7155
| Port Augusta West TF2 11kV | Substation Rating | MVA | Non-Coincident | 14.8
|  |  |  | Coincident | 14.8
|  | Raw Adjusted MD | MW | Non-Coincident | 2.0001
|  |  |  | Coincident | 2.0001
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.0397
|  |  |  | Coincident | 2.0397
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.034344
|  |  |  | Coincident | 0.034344
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7751
|  |  |  | Coincident | 1.7751
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.8102
|  |  |  | Coincident | 1.8102
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.6142
|  |  |  | Coincident | 1.6142
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6462
|  |  |  | Coincident | 1.6462
| Port Broughton 11kV | Substation Rating | MVA | Non-Coincident | 5.4
|  |  |  | Coincident | 5.4
|  | Raw Adjusted MD | MW | Non-Coincident | 2.7432
|  |  |  | Coincident | 2.7432
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.9817
|  |  |  | Coincident | 2.9817
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.062419
|  |  |  | Coincident | 0.034485
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.8655
|  |  |  | Coincident | 2.6223
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.922
|  |  |  | Coincident | 2.7128
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.6353
|  |  |  | Coincident | 2.4116
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.6872
|  |  |  | Coincident | 2.4949
| Port Clinton 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.41268
|  |  |  | Coincident | 0.41077
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.4344
|  |  |  | Coincident | 0.43239
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0070049
|  |  |  | Coincident | 0.0070049
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.4471
|  |  |  | Coincident | 0.4471
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.47063
|  |  |  | Coincident | 0.47063
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.41756
|  |  |  | Coincident | 0.41756
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.43953
|  |  |  | Coincident | 0.43953
| Port Germein 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.884
|  |  |  | Coincident | 0.867
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.88964
|  |  |  | Coincident | 0.87096
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.89583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.012191
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.69213
|  |  |  | Coincident | 0.68962
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.69944
|  |  |  | Coincident | 0.69541
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.62276
|  |  |  | Coincident | 0.6205
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.62934
|  |  |  | Coincident | 0.62571
| Port Giles 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 1.3792
|  |  |  | Coincident | 0.22625
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.4518
|  |  |  | Coincident | 0.23816
|  | Date MD occurred |  | Non-Coincident | 2018-12-13
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.037972
|  |  |  | Coincident | 0.0037555
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.6342
|  |  |  | Coincident | 0.2768
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.7202
|  |  |  | Coincident | 0.29137
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.4715
|  |  |  | Coincident | 0.24925
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.549
|  |  |  | Coincident | 0.26237
| Port Julia 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.33002
|  |  |  | Coincident | 0.27693
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.34739
|  |  |  | Coincident | 0.2915
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.030501
|  |  |  | Coincident | 0.0046762
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.28521
|  |  |  | Coincident | 0.2437
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.30022
|  |  |  | Coincident | 0.25653
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.27461
|  |  |  | Coincident | 0.23464
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.28906
|  |  |  | Coincident | 0.24699
| Port Lincoln City 11kV | Substation Rating | MVA | Non-Coincident | 29
|  |  |  | Coincident | 29
|  | Raw Adjusted MD | MW | Non-Coincident | 13.4383
|  |  |  | Coincident | 13.0925
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.4566
|  |  |  | Coincident | 13.1141
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.8778
|  |  |  | Coincident | 0.11893
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.6933
|  |  |  | Coincident | 10.2313
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.7075
|  |  |  | Coincident | 10.2473
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.9172
|  |  |  | Coincident | 9.4887
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.9304
|  |  |  | Coincident | 9.5035
| Port Lincoln Docks 11kV | Substation Rating | MVA | Non-Coincident | 12.3
|  |  |  | Coincident | 12.3
|  | Raw Adjusted MD | MW | Non-Coincident | 6.2188
|  |  |  | Coincident | 4.7828
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.684
|  |  |  | Coincident | 4.9405
|  | Date MD occurred |  | Non-Coincident | 2019-01-22
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.68587
|  |  |  | Coincident | 0.0228
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.0792
|  |  |  | Coincident | 4.6003
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.5326
|  |  |  | Coincident | 4.7851
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.6207
|  |  |  | Coincident | 4.2533
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.0399
|  |  |  | Coincident | 4.4242
| Port Lincoln Marina 11kV | Substation Rating | MVA | Non-Coincident | 16.8
|  |  |  | Coincident | 16.8
|  | Raw Adjusted MD | MW | Non-Coincident | 6.5439
|  |  |  | Coincident | 5.7905
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.782
|  |  |  | Coincident | 5.9791
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.47286
|  |  |  | Coincident | 0.038866
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.5501
|  |  |  | Coincident | 5.3485
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.7689
|  |  |  | Coincident | 5.5672
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.1638
|  |  |  | Coincident | 4.9763
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.3675
|  |  |  | Coincident | 5.1797
| Port Noarlunga 11kV | Substation Rating | MVA | Non-Coincident | 63.0903
|  |  |  | Coincident | 63.0903
|  | Raw Adjusted MD | MW | Non-Coincident | 31.55
|  |  |  | Coincident | 31.55
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.936
|  |  |  | Coincident | 31.9071
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.39723
|  |  |  | Coincident | 0.21946
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.1411
|  |  |  | Coincident | 33.1411
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.5312
|  |  |  | Coincident | 33.5312
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.2801
|  |  |  | Coincident | 29.2801
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.6247
|  |  |  | Coincident | 29.6247
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Port Pirie South 11kV | Substation Rating | MVA | Non-Coincident | 40.5097
|  |  |  | Coincident | 40.5097
|  | Raw Adjusted MD | MW | Non-Coincident | 23.2257
|  |  |  | Coincident | 23.2257
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.9425
|  |  |  | Coincident | 23.9425
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.33794
|  |  |  | Coincident | 0.1867
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.7946
|  |  |  | Coincident | 20.2402
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.4673
|  |  |  | Coincident | 20.9097
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.8158
|  |  |  | Coincident | 18.4025
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.4274
|  |  |  | Coincident | 19.0113
| Port Stanvac 11kV | Substation Rating | MVA | Non-Coincident | 88.6
|  |  |  | Coincident | 88.6
|  | Raw Adjusted MD | MW | Non-Coincident | 30.5118
|  |  |  | Coincident | 13.9095
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.8441
|  |  |  | Coincident | 14.3996
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 6.4869
|  |  |  | Coincident | 18.3756
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.4248
|  |  |  | Coincident | 34.514
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 101.5637
|  |  |  | Coincident | 429.3442
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.0683
|  |  |  | Coincident | 30.6009
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 90.0486
|  |  |  | Coincident | 380.6661
| Port Vincent 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 0.87445
|  |  |  | Coincident | 0.87445
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.92047
|  |  |  | Coincident | 0.92047
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.013889
|  |  |  | Coincident | 0.013889
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.68599
|  |  |  | Coincident | 0.68119
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.7221
|  |  |  | Coincident | 0.71704
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.64309
|  |  |  | Coincident | 0.63859
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.67694
|  |  |  | Coincident | 0.6722
| Portee 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.63651
|  |  |  | Coincident | 0.16893
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.67001
|  |  |  | Coincident | 0.17782
|  | Date MD occurred |  | Non-Coincident | 2019-03-02
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.00080964
|  |  |  | Coincident | 0.00031032
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.67484
|  |  |  | Coincident | 0.16021
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.71036
|  |  |  | Coincident | 0.16864
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.60538
|  |  |  | Coincident | 0.14372
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.63725
|  |  |  | Coincident | 0.15129
| Prospect 11kV | Substation Rating | MVA | Non-Coincident | 49.4207
|  |  |  | Coincident | 49.4207
|  | Raw Adjusted MD | MW | Non-Coincident | 28.4476
|  |  |  | Coincident | 28.3284
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.507
|  |  |  | Coincident | 29.3372
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.6776
|  |  |  | Coincident | 1.5168
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.301
|  |  |  | Coincident | 32.301
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.1514
|  |  |  | Coincident | 34.1514
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.6851
|  |  |  | Coincident | 29.6851
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.3857
|  |  |  | Coincident | 31.3857
| Punyelroo 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.448
|  |  |  | Coincident | 0.216
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.46131
|  |  |  | Coincident | 0.22339
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.039448
|  |  |  | Coincident | 0.0028377
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.26716
|  |  |  | Coincident | 0.20037
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.27509
|  |  |  | Coincident | 0.20689
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.24202
|  |  |  | Coincident | 0.18152
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.24921
|  |  |  | Coincident | 0.18743
| Pyap 11kV | Substation Rating | MVA | Non-Coincident | 15.1699
|  |  |  | Coincident | 15.1699
|  | Raw Adjusted MD | MW | Non-Coincident | 7.7198
|  |  |  | Coincident | 7.6402
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.8133
|  |  |  | Coincident | 7.6728
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.95833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.065334
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.8087
|  |  |  | Coincident | 8.3426
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.9031
|  |  |  | Coincident | 8.3782
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.8988
|  |  |  | Coincident | 7.4808
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.9834
|  |  |  | Coincident | 7.5127
| Qualco 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 2.8304
|  |  |  | Coincident | 2.8304
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.9982
|  |  |  | Coincident | 2.9982
|  | Date MD occurred |  | Non-Coincident | 2019-01-25
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.020833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0026534
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.8304
|  |  |  | Coincident | 2.8304
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.9982
|  |  |  | Coincident | 2.9982
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.6465
|  |  |  | Coincident | 2.6465
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.8033
|  |  |  | Coincident | 2.8033
| Queenstown 7.6kV | Substation Rating | MVA | Non-Coincident | 22.7006
|  |  |  | Coincident | 22.7006
|  | Raw Adjusted MD | MW | Non-Coincident | 10.4678
|  |  |  | Coincident | 10.2217
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.835
|  |  |  | Coincident | 10.5799
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.091022
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.0448
|  |  |  | Coincident | 10.9267
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.43
|  |  |  | Coincident | 11.3098
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.8968
|  |  |  | Coincident | 9.791
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.242
|  |  |  | Coincident | 10.1343
| Quorn 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.931
|  |  |  | Coincident | 1.899
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.9736
|  |  |  | Coincident | 1.9312
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.019682
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7439
|  |  |  | Coincident | 1.7439
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.7778
|  |  |  | Coincident | 1.7778
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.5806
|  |  |  | Coincident | 1.5806
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6114
|  |  |  | Coincident | 1.6114
| Ramco 11kV | Substation Rating | MVA | Non-Coincident | 8.4
|  |  |  | Coincident | 8.4
|  | Raw Adjusted MD | MW | Non-Coincident | 6.08
|  |  |  | Coincident | 4.51
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.5842
|  |  |  | Coincident | 4.8831
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.91667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.046747
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.7347
|  |  |  | Coincident | 5.254
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.2133
|  |  |  | Coincident | 5.6969
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.3035
|  |  |  | Coincident | 4.859
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.7461
|  |  |  | Coincident | 5.2686
| Rapid Bay 11kV | Substation Rating | MVA | Non-Coincident | 0.4095
|  |  |  | Coincident | 0.4095
|  | Raw Adjusted MD | MW | Non-Coincident | 0.041
|  |  |  | Coincident | 0.029
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.0416
|  |  |  | Coincident | 0.0294
|  | Date MD occurred |  | Non-Coincident | 2018-12-29
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002059
|  |  |  | Coincident | 0.000522
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.040881
|  |  |  | Coincident | 0.018289
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.041778
|  |  |  | Coincident | 0.019222
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.038049
|  |  |  | Coincident | 0.017022
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.038883
|  |  |  | Coincident | 0.017891
| Renmark 11kV | Substation Rating | MVA | Non-Coincident | 28.5
|  |  |  | Coincident | 28.5
|  | Raw Adjusted MD | MW | Non-Coincident | 20.3474
|  |  |  | Coincident | 20.3474
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.4242
|  |  |  | Coincident | 20.4242
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.16209
|  |  |  | Coincident | 0.16209
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.589
|  |  |  | Coincident | 20.3947
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.6745
|  |  |  | Coincident | 20.4881
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.5244
|  |  |  | Coincident | 18.4442
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.6016
|  |  |  | Coincident | 18.5287
| Riverton 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.731
|  |  |  | Coincident | 1.731
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.7839
|  |  |  | Coincident | 1.7839
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.01711
|  |  |  | Coincident | 0.01711
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.8621
|  |  |  | Coincident | 1.79
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.919
|  |  |  | Coincident | 1.8491
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.6905
|  |  |  | Coincident | 1.6251
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.7422
|  |  |  | Coincident | 1.6787
| Robe 7.6kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.993
|  |  |  | Coincident | 2.892
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.0226
|  |  |  | Coincident | 2.9201
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.036918
|  |  |  | Coincident | 0.020396
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.0077
|  |  |  | Coincident | 3.0077
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0372
|  |  |  | Coincident | 3.0372
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.646
|  |  |  | Coincident | 2.646
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.672
|  |  |  | Coincident | 2.672
| Robertstown 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.84391
|  |  |  | Coincident | 0.84391
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.85942
|  |  |  | Coincident | 0.85942
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0071759
|  |  |  | Coincident | 0.0071759
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.84391
|  |  |  | Coincident | 0.84391
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.85942
|  |  |  | Coincident | 0.85942
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.77413
|  |  |  | Coincident | 0.77413
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.78835
|  |  |  | Coincident | 0.78835
| Roonka 11kV | Substation Rating | MVA | Non-Coincident | 8.1
|  |  |  | Coincident | 8.1
|  | Raw Adjusted MD | MW | Non-Coincident | 2.8085
|  |  |  | Coincident | 2.1801
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.1072
|  |  |  | Coincident | 2.3063
|  | Date MD occurred |  | Non-Coincident | 2019-01-17
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.14689
|  |  |  | Coincident | 0.018124
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.9331
|  |  |  | Coincident | 2.3696
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.2565
|  |  |  | Coincident | 2.6685
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.6698
|  |  |  | Coincident | 2.1569
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.9642
|  |  |  | Coincident | 2.4289
| Royal Adelaide Hospital 11kV | Substation Rating | MVA | Non-Coincident | -
|  |  |  | Coincident | -
|  | Raw Adjusted MD | MW | Non-Coincident | 7.98
|  |  |  | Coincident | 5.89
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.0142
|  |  |  | Coincident | 5.9022
|  | Date MD occurred |  | Non-Coincident | 2019-01-15
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.45833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.5892
|  |  |  | Coincident | 41.3072
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 43.241
|  |  |  | Coincident | 42.8348
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.5408
|  |  |  | Coincident | 38.2796
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 40.0716
|  |  |  | Coincident | 39.6952
| Rudall 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.741
|  |  |  | Coincident | 0.39879
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.82194
|  |  |  | Coincident | 0.4091
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0018929
|  |  |  | Coincident | 0.0010458
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.741
|  |  |  | Coincident | 0.39879
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.82194
|  |  |  | Coincident | 0.4091
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.68253
|  |  |  | Coincident | 0.36732
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.75708
|  |  |  | Coincident | 0.37682
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Salisbury 11kV | Substation Rating | MVA | Non-Coincident | 72.5812
|  |  |  | Coincident | 72.5812
|  | Raw Adjusted MD | MW | Non-Coincident | 56.8632
|  |  |  | Coincident | 56.8632
|  | Raw Adjusted MD | MVA | Non-Coincident | 56.944
|  |  |  | Coincident | 56.944
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.32832
|  |  |  | Coincident | 0.32832
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 59.1351
|  |  |  | Coincident | 59.1351
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.2209
|  |  |  | Coincident | 59.2209
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 53.9911
|  |  |  | Coincident | 53.9911
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 54.0694
|  |  |  | Coincident | 54.0694
| Salt Cliffs 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.12516
|  |  |  | Coincident | 0.10772
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.12539
|  |  |  | Coincident | 0.10808
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0024516
|  |  |  | Coincident | 0.0024516
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.12516
|  |  |  | Coincident | 0.10772
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.12539
|  |  |  | Coincident | 0.10808
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.10967
|  |  |  | Coincident | 0.094388
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.10986
|  |  |  | Coincident | 0.094704
| Sandy Creek 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.378
|  |  |  | Coincident | 2.345
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.4778
|  |  |  | Coincident | 2.4334
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.32119
|  |  |  | Coincident | 0.026399
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.429
|  |  |  | Coincident | 2.3549
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.5308
|  |  |  | Coincident | 2.452
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.2116
|  |  |  | Coincident | 2.1442
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.3044
|  |  |  | Coincident | 2.2326
| Seacombe 11kV | Substation Rating | MVA | Non-Coincident | 59.2
|  |  |  | Coincident | 59.2
|  | Raw Adjusted MD | MW | Non-Coincident | 44.5033
|  |  |  | Coincident | 44.5033
|  | Raw Adjusted MD | MVA | Non-Coincident | 44.6079
|  |  |  | Coincident | 44.6079
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.27505
|  |  |  | Coincident | 0.27505
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.3195
|  |  |  | Coincident | 47.0615
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.4343
|  |  |  | Coincident | 47.1634
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.7895
|  |  |  | Coincident | 41.5616
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 41.8908
|  |  |  | Coincident | 41.6516
| Seaford 11kV | Substation Rating | MVA | Non-Coincident | 15.8
|  |  |  | Coincident | 15.8
|  | Raw Adjusted MD | MW | Non-Coincident | 10.1036
|  |  |  | Coincident | 10.1036
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.2499
|  |  |  | Coincident | 10.2499
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.091485
|  |  |  | Coincident | 0.091485
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.7011
|  |  |  | Coincident | 10.5683
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.8718
|  |  |  | Coincident | 10.725
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.378
|  |  |  | Coincident | 9.2617
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.5276
|  |  |  | Coincident | 9.399
| Second Valley 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.235
|  |  |  | Coincident | 0.228
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.247
|  |  |  | Coincident | 0.24
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0068954
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.23231
|  |  |  | Coincident | 0.22283
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.23398
|  |  |  | Coincident | 0.22451
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.2207
|  |  |  | Coincident | 0.2117
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.22229
|  |  |  | Coincident | 0.21329
| Sheidow Park 11kV | Substation Rating | MVA | Non-Coincident | 35
|  |  |  | Coincident | 35
|  | Raw Adjusted MD | MW | Non-Coincident | 26.5698
|  |  |  | Coincident | 26.5698
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.7051
|  |  |  | Coincident | 26.7051
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.22039
|  |  |  | Coincident | 0.22039
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.258
|  |  |  | Coincident | 27.9726
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.4154
|  |  |  | Coincident | 28.1156
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.9469
|  |  |  | Coincident | 24.6949
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.0858
|  |  |  | Coincident | 24.8212
| Sherlock 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.030907
|  |  |  | Coincident | 0.030907
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.031592
|  |  |  | Coincident | 0.031592
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00069228
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.030907
|  |  |  | Coincident | 0.030907
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.031592
|  |  |  | Coincident | 0.031592
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.028938
|  |  |  | Coincident | 0.028938
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.029579
|  |  |  | Coincident | 0.029579
| Smithfield West 11kV | Substation Rating | MVA | Non-Coincident | 36.195
|  |  |  | Coincident | 36.195
|  | Raw Adjusted MD | MW | Non-Coincident | 18.74
|  |  |  | Coincident | 18.19
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.8331
|  |  |  | Coincident | 18.2879
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.10924
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.8253
|  |  |  | Coincident | 18.5428
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.9258
|  |  |  | Coincident | 18.6396
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.8579
|  |  |  | Coincident | 16.6049
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.9479
|  |  |  | Coincident | 16.6916
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| South End 11kV | Substation Rating | MVA | Non-Coincident | 0.78
|  |  |  | Coincident | 0.78
|  | Raw Adjusted MD | MW | Non-Coincident | 0.45
|  |  |  | Coincident | 0.433
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.48429
|  |  |  | Coincident | 0.45857
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0071752
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.40465
|  |  |  | Coincident | 0.38936
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.43548
|  |  |  | Coincident | 0.41236
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.37252
|  |  |  | Coincident | 0.35844
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.40091
|  |  |  | Coincident | 0.37961
| Spalding 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.005
|  |  |  | Coincident | 0.967
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.0061
|  |  |  | Coincident | 0.96787
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0093074
|  |  |  | Coincident | 0.0093074
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.0399
|  |  |  | Coincident | 0.99332
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.041
|  |  |  | Coincident | 0.99429
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.96252
|  |  |  | Coincident | 0.91943
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.96358
|  |  |  | Coincident | 0.92033
| Square Water Hole 11kV | Substation Rating | MVA | Non-Coincident | 7.125
|  |  |  | Coincident | 7.125
|  | Raw Adjusted MD | MW | Non-Coincident | 4.4654
|  |  |  | Coincident | 4.4014
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.7544
|  |  |  | Coincident | 4.7243
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.24313
|  |  |  | Coincident | 0.048092
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.2731
|  |  |  | Coincident | 4.2423
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.5581
|  |  |  | Coincident | 4.5435
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.8574
|  |  |  | Coincident | 3.8296
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.1147
|  |  |  | Coincident | 4.1015
| Stansbury 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.2561
|  |  |  | Coincident | 1.1644
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.3222
|  |  |  | Coincident | 1.2257
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.02315
|  |  |  | Coincident | 0.01279
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.96555
|  |  |  | Coincident | 0.96555
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.0164
|  |  |  | Coincident | 1.0164
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.89441
|  |  |  | Coincident | 0.89441
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.94148
|  |  |  | Coincident | 0.94148
| Stirling East 11kV | Substation Rating | MVA | Non-Coincident | 17.2
|  |  |  | Coincident | 17.2
|  | Raw Adjusted MD | MW | Non-Coincident | 8.4598
|  |  |  | Coincident | 8.1482
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.669
|  |  |  | Coincident | 8.3589
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.49236
|  |  |  | Coincident | 0.060753
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.4591
|  |  |  | Coincident | 7.3208
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.643
|  |  |  | Coincident | 7.5068
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.872
|  |  |  | Coincident | 6.7446
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.0414
|  |  |  | Coincident | 6.916
| Stirling North 1 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 1.8393
|  |  |  | Coincident | 1.5576
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.0901
|  |  |  | Coincident | 1.77
|  | Date MD occurred |  | Non-Coincident | 2018-11-19
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.15388
|  |  |  | Coincident | 0.02004
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.8675
|  |  |  | Coincident | 1.516
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.9313
|  |  |  | Coincident | 1.5609
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.7103
|  |  |  | Coincident | 1.3884
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.7687
|  |  |  | Coincident | 1.4295
| Stirling North 2 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.798
|  |  |  | Coincident | 1.73
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.8448
|  |  |  | Coincident | 1.7683
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.017974
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.7514
|  |  |  | Coincident | 1.7183
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.797
|  |  |  | Coincident | 1.7597
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.5729
|  |  |  | Coincident | 1.5432
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.6139
|  |  |  | Coincident | 1.5804
| Stockwell TF1 11kV | Substation Rating | MVA | Non-Coincident | 8.9062
|  |  |  | Coincident | 8.9062
|  | Raw Adjusted MD | MW | Non-Coincident | 2.33
|  |  |  | Coincident | 2.33
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.3468
|  |  |  | Coincident | 2.3456
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.12426
|  |  |  | Coincident | 0.02458
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.1183
|  |  |  | Coincident | 2.0817
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.132
|  |  |  | Coincident | 2.0958
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.9278
|  |  |  | Coincident | 1.8946
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.9403
|  |  |  | Coincident | 1.9073
| Stockwell TF2 11kV | Substation Rating | MVA | Non-Coincident | 7.9
|  |  |  | Coincident | 7.9
|  | Raw Adjusted MD | MW | Non-Coincident | 4.65
|  |  |  | Coincident | 2.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.8798
|  |  |  | Coincident | 2.6315
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.10417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.01121
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.6876
|  |  |  | Coincident | 3.0804
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.923
|  |  |  | Coincident | 3.2581
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.3271
|  |  |  | Coincident | 2.8435
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.5444
|  |  |  | Coincident | 3.0075
| Strathalbyn 11kV | Substation Rating | MVA | Non-Coincident | 16.7
|  |  |  | Coincident | 16.7
|  | Raw Adjusted MD | MW | Non-Coincident | 11.1813
|  |  |  | Coincident | 11.0681
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.2553
|  |  |  | Coincident | 11.1497
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.10853
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.5749
|  |  |  | Coincident | 9.4898
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.6418
|  |  |  | Coincident | 9.5653
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.6727
|  |  |  | Coincident | 8.5957
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.7333
|  |  |  | Coincident | 8.664
| Strathalbyn East 11kV | Substation Rating | MVA | Non-Coincident | 9.5
|  |  |  | Coincident | 9.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 2018-11-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.020833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
| Streaky Bay 11kV | Substation Rating | MVA | Non-Coincident | 6.5
|  |  |  | Coincident | 6.5
|  | Raw Adjusted MD | MW | Non-Coincident | 3.269
|  |  |  | Coincident | 2.426
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.3002
|  |  |  | Coincident | 2.443
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.03677
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.8867
|  |  |  | Coincident | 2.8867
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.9496
|  |  |  | Coincident | 2.9496
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.6456
|  |  |  | Coincident | 2.6456
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.7032
|  |  |  | Coincident | 2.7032
| Swan Reach 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.424
|  |  |  | Coincident | 1.211
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.5222
|  |  |  | Coincident | 1.2919
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.045487
|  |  |  | Coincident | 0.0070925
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.5626
|  |  |  | Coincident | 1.0968
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.6704
|  |  |  | Coincident | 1.1834
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.3963
|  |  |  | Coincident | 0.98009
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.4927
|  |  |  | Coincident | 1.0575
| Swan Reach 33kV | Substation Rating | MVA | Non-Coincident | 10.69
|  |  |  | Coincident | 10.69
|  | Raw Adjusted MD | MW | Non-Coincident | 1.361
|  |  |  | Coincident | 1.112
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.4598
|  |  |  | Coincident | 1.2057
|  | Date MD occurred |  | Non-Coincident | 2018-12-27
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.027643
|  |  |  | Coincident | 0.0071269
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.8247
|  |  |  | Coincident | 1.5267
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0131
|  |  |  | Coincident | 1.695
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.6771
|  |  |  | Coincident | 1.4032
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8502
|  |  |  | Coincident | 1.5579
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Tailem Bend Town 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 3.0328
|  |  |  | Coincident | 2.9647
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.1
|  |  |  | Coincident | 3.0186
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.031552
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.2324
|  |  |  | Coincident | 3.2324
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.304
|  |  |  | Coincident | 3.304
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.9313
|  |  |  | Coincident | 2.9313
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.9962
|  |  |  | Coincident | 2.9962
| Tantanoola 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.55
|  |  |  | Coincident | 0.413
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.57778
|  |  |  | Coincident | 0.44291
|  | Date MD occurred |  | Non-Coincident | 2019-03-05
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.3125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.01741
|  |  |  | Coincident | 0.0037462
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.64842
|  |  |  | Coincident | 0.50032
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.77741
|  |  |  | Coincident | 0.53867
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.59572
|  |  |  | Coincident | 0.45966
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.71423
|  |  |  | Coincident | 0.49489
| Tarlton 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.533
|  |  |  | Coincident | 0.533
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.56687
|  |  |  | Coincident | 0.57738
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.05136
|  |  |  | Coincident | 0.0042214
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.47906
|  |  |  | Coincident | 0.46109
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.5095
|  |  |  | Coincident | 0.49994
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.44173
|  |  |  | Coincident | 0.42516
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.4698
|  |  |  | Coincident | 0.46099
| Tarpeena South 11kV | Substation Rating | MVA | Non-Coincident | 17.2
|  |  |  | Coincident | 17.2
|  | Raw Adjusted MD | MW | Non-Coincident | 5.1081
|  |  |  | Coincident | 4.0907
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.3769
|  |  |  | Coincident | 4.306
|  | Date MD occurred |  | Non-Coincident | 2018-11-09
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.27083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.020076
|  |  |  | Coincident | 0.0043065
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.6153
|  |  |  | Coincident | 5.3167
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.9634
|  |  |  | Coincident | 5.5965
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.1409
|  |  |  | Coincident | 4.9354
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.4641
|  |  |  | Coincident | 5.1952
| Tea Tree Gully 11kV | Substation Rating | MVA | Non-Coincident | 49.0682
|  |  |  | Coincident | 49.0682
|  | Raw Adjusted MD | MW | Non-Coincident | 34.288
|  |  |  | Coincident | 34.288
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.1219
|  |  |  | Coincident | 35.1219
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.23382
|  |  |  | Coincident | 0.23382
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.3198
|  |  |  | Coincident | 33.3198
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.152
|  |  |  | Coincident | 34.152
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.9908
|  |  |  | Coincident | 29.9908
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.7399
|  |  |  | Coincident | 30.7399
| Teal Flat 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.9928
|  |  |  | Coincident | 2.9928
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.0725
|  |  |  | Coincident | 3.0725
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.025954
|  |  |  | Coincident | 0.014339
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.9928
|  |  |  | Coincident | 2.9928
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0725
|  |  |  | Coincident | 3.0725
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.73
|  |  |  | Coincident | 2.73
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.8027
|  |  |  | Coincident | 2.8027
| Telowie 11kV | Substation Rating | MVA | Non-Coincident | 1
|  |  |  | Coincident | 1
|  | Raw Adjusted MD | MW | Non-Coincident | 0.604
|  |  |  | Coincident | 0.604
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.61127
|  |  |  | Coincident | 0.61127
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0089564
|  |  |  | Coincident | 0.0089564
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.60223
|  |  |  | Coincident | 0.60223
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.60948
|  |  |  | Coincident | 0.60948
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.54565
|  |  |  | Coincident | 0.54565
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.55222
|  |  |  | Coincident | 0.55222
| Thebarton 11kV | Substation Rating | MVA | Non-Coincident | 49
|  |  |  | Coincident | 49
|  | Raw Adjusted MD | MW | Non-Coincident | 22.4624
|  |  |  | Coincident | 19.2456
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.4854
|  |  |  | Coincident | 19.2943
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.1249
|  |  |  | Coincident | 0.096447
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.6711
|  |  |  | Coincident | 21.166
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.6935
|  |  |  | Coincident | 21.2196
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.139
|  |  |  | Coincident | 18.9937
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.1592
|  |  |  | Coincident | 19.0418
| Tintinara 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.3892
|  |  |  | Coincident | 1.3892
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.4632
|  |  |  | Coincident | 1.4632
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0067921
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.3892
|  |  |  | Coincident | 1.3892
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.4632
|  |  |  | Coincident | 1.4632
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.2564
|  |  |  | Coincident | 1.2564
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.3233
|  |  |  | Coincident | 1.3233
| Tonsley Park 11kV | Substation Rating | MVA | Non-Coincident | 40.0554
|  |  |  | Coincident | 40.0554
|  | Raw Adjusted MD | MW | Non-Coincident | 18.184
|  |  |  | Coincident | 15.9924
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.9793
|  |  |  | Coincident | 16.3548
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.66667
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.7148
|  |  |  | Coincident | 0.064173
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.2863
|  |  |  | Coincident | 17.1861
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.0627
|  |  |  | Coincident | 17.5827
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.3158
|  |  |  | Coincident | 15.4302
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.0129
|  |  |  | Coincident | 15.7863
| Tumby Bay 11kV | Substation Rating | MVA | Non-Coincident | 5.4
|  |  |  | Coincident | 5.4
|  | Raw Adjusted MD | MW | Non-Coincident | 3.047
|  |  |  | Coincident | 3.029
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.075
|  |  |  | Coincident | 3.0611
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.75
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.44718
|  |  |  | Coincident | 0.036754
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.4759
|  |  |  | Coincident | 2.4759
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.4998
|  |  |  | Coincident | 2.5008
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.275
|  |  |  | Coincident | 2.275
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.2968
|  |  |  | Coincident | 2.2978
| Two Wells 11kV | Substation Rating | MVA | Non-Coincident | 16.6
|  |  |  | Coincident | 16.6
|  | Raw Adjusted MD | MW | Non-Coincident | 4.2491
|  |  |  | Coincident | 4.2394
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.3034
|  |  |  | Coincident | 4.2923
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.035635
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.0878
|  |  |  | Coincident | 4.0878
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.1395
|  |  |  | Coincident | 4.1395
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.6966
|  |  |  | Coincident | 3.6966
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.7433
|  |  |  | Coincident | 3.7433
| Uley 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.26333
|  |  |  | Coincident | 0.26333
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.26786
|  |  |  | Coincident | 0.26786
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.013673
|  |  |  | Coincident | 0.0027045
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.26333
|  |  |  | Coincident | 0.26333
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.26786
|  |  |  | Coincident | 0.26786
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.24508
|  |  |  | Coincident | 0.24508
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.2493
|  |  |  | Coincident | 0.2493
| Uley South 11kV | Substation Rating | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.95
|  | Raw Adjusted MD | MW | Non-Coincident | 0.46942
|  |  |  | Coincident | 0.15524
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.48393
|  |  |  | Coincident | 0.16004
|  | Date MD occurred |  | Non-Coincident | 2018-11-26
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.49243
|  |  |  | Coincident | 0.1409
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.50114
|  |  |  | Coincident | 0.14334
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.46873
|  |  |  | Coincident | 0.13412
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.47701
|  |  |  | Coincident | 0.13644
| Uraidla 11kV | Substation Rating | MVA | Non-Coincident | 17.2
|  |  |  | Coincident | 17.2
|  | Raw Adjusted MD | MW | Non-Coincident | 5.0825
|  |  |  | Coincident | 5.0613
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.2763
|  |  |  | Coincident | 5.2305
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.12008
|  |  |  | Coincident | 0.066342
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.9599
|  |  |  | Coincident | 4.9599
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.1372
|  |  |  | Coincident | 5.1372
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.572
|  |  |  | Coincident | 4.572
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.7354
|  |  |  | Coincident | 4.7354
| Uraidla 33kV | Substation Rating | MVA | Non-Coincident | 31.4
|  |  |  | Coincident | 31.4
|  | Raw Adjusted MD | MW | Non-Coincident | 18.39
|  |  |  | Coincident | 18.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.9067
|  |  |  | Coincident | 18.5316
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.77083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.1441
|  |  |  | Coincident | 0.14117
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.9341
|  |  |  | Coincident | 15.7991
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.3852
|  |  |  | Coincident | 16.2257
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.6353
|  |  |  | Coincident | 14.5113
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.0496
|  |  |  | Coincident | 14.9031
| Verdun 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.267
|  |  |  | Coincident | 1.267
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.3007
|  |  |  | Coincident | 1.3007
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.017626
|  |  |  | Coincident | 0.017626
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.241
|  |  |  | Coincident | 1.2278
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.2747
|  |  |  | Coincident | 1.2625
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.1453
|  |  |  | Coincident | 1.1331
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.1765
|  |  |  | Coincident | 1.1652
| Victor Harbor 11kV | Substation Rating | MVA | Non-Coincident | 62.7333
|  |  |  | Coincident | 62.7333
|  | Raw Adjusted MD | MW | Non-Coincident | 28.82
|  |  |  | Coincident | 28.66
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.8622
|  |  |  | Coincident | 28.7092
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.3931
|  |  |  | Coincident | 0.27556
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 24.7348
|  |  |  | Coincident | 24.6659
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.7738
|  |  |  | Coincident | 24.708
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.4216
|  |  |  | Coincident | 21.362
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.4554
|  |  |  | Coincident | 21.3985
| Virginia 11kV | Substation Rating | MVA | Non-Coincident | 14.9
|  |  |  | Coincident | 14.9
|  | Raw Adjusted MD | MW | Non-Coincident | 6.3233
|  |  |  | Coincident | 6.3117
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.9669
|  |  |  | Coincident | 6.9542
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.049705
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.377
|  |  |  | Coincident | 6.3712
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.0261
|  |  |  | Coincident | 7.0197
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.9123
|  |  |  | Coincident | 5.9069
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.514
|  |  |  | Coincident | 6.5081
| Waikerie 11kV | Substation Rating | MVA | Non-Coincident | 12.0467
|  |  |  | Coincident | 12.0467
|  | Raw Adjusted MD | MW | Non-Coincident | 7.3137
|  |  |  | Coincident | 7.0896
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.3882
|  |  |  | Coincident | 7.1349
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.057935
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.656
|  |  |  | Coincident | 6.941
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.7372
|  |  |  | Coincident | 7.0639
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.0092
|  |  |  | Coincident | 6.3546
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.0836
|  |  |  | Coincident | 6.4672
| Walker Flat 11kV | Substation Rating | MVA | Non-Coincident | 2
|  |  |  | Coincident | 2
|  | Raw Adjusted MD | MW | Non-Coincident | 1.192
|  |  |  | Coincident | 0.617
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.2437
|  |  |  | Coincident | 0.63055
|  | Date MD occurred |  | Non-Coincident | 2018-12-28
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.625
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.25655
|  |  |  | Coincident | 0.0087991
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.1329
|  |  |  | Coincident | 0.78503
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.1898
|  |  |  | Coincident | 0.80508
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.0447
|  |  |  | Coincident | 0.72393
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.0972
|  |  |  | Coincident | 0.74242
| Wallaroo 11kV | Substation Rating | MVA | Non-Coincident | 16.2
|  |  |  | Coincident | 16.2
|  | Raw Adjusted MD | MW | Non-Coincident | 7.999
|  |  |  | Coincident | 7.999
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.42
|  |  |  | Coincident | 8.42
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.071554
|  |  |  | Coincident | 0.071554
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.529
|  |  |  | Coincident | 7.4634
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.9253
|  |  |  | Coincident | 7.8562
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.8541
|  |  |  | Coincident | 6.7944
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.2149
|  |  |  | Coincident | 7.152
| Warooka 11kV | Substation Rating | MVA | Non-Coincident | 5.4
|  |  |  | Coincident | 5.4
|  | Raw Adjusted MD | MW | Non-Coincident | 2.132
|  |  |  | Coincident | 1.789
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.1841
|  |  |  | Coincident | 1.8474
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.8125
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.039677
|  |  |  | Coincident | 0.02192
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.0002
|  |  |  | Coincident | 1.5977
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.0514
|  |  |  | Coincident | 1.6474
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.8221
|  |  |  | Coincident | 1.4554
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8687
|  |  |  | Coincident | 1.5007
| Wasleys 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.681
|  |  |  | Coincident | 1.607
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.699
|  |  |  | Coincident | 1.6219
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.016245
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.5674
|  |  |  | Coincident | 1.5674
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.5843
|  |  |  | Coincident | 1.5843
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.4305
|  |  |  | Coincident | 1.4305
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.4459
|  |  |  | Coincident | 1.4459
| Waterloo Town 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.38734
|  |  |  | Coincident | 0.3807
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.40772
|  |  |  | Coincident | 0.40074
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015344
|  |  |  | Coincident | 0.00097182
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.38831
|  |  |  | Coincident | 0.37631
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.40874
|  |  |  | Coincident | 0.39612
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.35766
|  |  |  | Coincident | 0.34661
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.37648
|  |  |  | Coincident | 0.36485
| White Sands 11kV | Substation Rating | MVA | Non-Coincident | 8.1
|  |  |  | Coincident | 8.1
|  | Raw Adjusted MD | MW | Non-Coincident | 3.347
|  |  |  | Coincident | 2.007
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.6417
|  |  |  | Coincident | 2.1951
|  | Date MD occurred |  | Non-Coincident | 2019-02-08
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.7981
|  |  |  | Coincident | 4.0014
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.2917
|  |  |  | Coincident | 4.354
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.9867
|  |  |  | Coincident | 3.4414
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.4112
|  |  |  | Coincident | 3.7447
| Whitmore Square 11kV | Substation Rating | MVA | Non-Coincident | 72.4102
|  |  |  | Coincident | 72.4102
|  | Raw Adjusted MD | MW | Non-Coincident | 39.8594
|  |  |  | Coincident | 26.5747
|  | Raw Adjusted MD | MVA | Non-Coincident | 41.5192
|  |  |  | Coincident | 27.1843
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.52083
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.0478
|  |  |  | Coincident | 0.027591
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.2346
|  |  |  | Coincident | 7.1906
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.2712
|  |  |  | Coincident | 7.2039
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.4922
|  |  |  | Coincident | 6.5423
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.5255
|  |  |  | Coincident | 6.5544
| Whyalla City 11kV | Substation Rating | MVA | Non-Coincident | 28.5
|  |  |  | Coincident | 28.5
|  | Raw Adjusted MD | MW | Non-Coincident | 23.1537
|  |  |  | Coincident | 23.0785
|  | Raw Adjusted MD | MVA | Non-Coincident | 23.2534
|  |  |  | Coincident | 23.1394
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.72917
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.2253
|  |  |  | Coincident | 0.14094
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.1526
|  |  |  | Coincident | 5.9296
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.2316
|  |  |  | Coincident | 5.9662
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.2517
|  |  |  | Coincident | 5.3411
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.3228
|  |  |  | Coincident | 5.374
| Whyalla North 11kV | Substation Rating | MVA | Non-Coincident | 2.9
|  |  |  | Coincident | 2.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.411
|  |  |  | Coincident | 0.368
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.45491
|  |  |  | Coincident | 0.40922
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0015295
|  |  |  | Coincident | 0.0015295
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.63639
|  |  |  | Coincident | 0.4862
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.70438
|  |  |  | Coincident | 0.54852
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.56079
|  |  |  | Coincident | 0.42844
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.6207
|  |  |  | Coincident | 0.48335
| Whyalla Stuart 11kV | Substation Rating | MVA | Non-Coincident | 31
|  |  |  | Coincident | 31
|  | Raw Adjusted MD | MW | Non-Coincident | 14.1079
|  |  |  | Coincident | 13.1582
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.3803
|  |  |  | Coincident | 13.3562
|  | Date MD occurred |  | Non-Coincident | 2018-12-28
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.64583
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.078
|  |  |  | Coincident | 0.11328
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.0836
|  |  |  | Coincident | 5.8688
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.4212
|  |  |  | Coincident | 5.8717
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.5051
|  |  |  | Coincident | 5.2928
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.8095
|  |  |  | Coincident | 5.2955
| Williamstown 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.7976
|  |  |  | Coincident | 0.74813
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.83958
|  |  |  | Coincident | 0.78751
|  | Date MD occurred |  | Non-Coincident | 2019-02-25
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.024915
|  |  |  | Coincident | 0.0080084
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.85946
|  |  |  | Coincident | 0.76291
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.90469
|  |  |  | Coincident | 0.80307
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.77969
|  |  |  | Coincident | 0.69211
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.82073
|  |  |  | Coincident | 0.72854
| Williamstown South 11kV | Substation Rating | MVA | Non-Coincident | 4.3
|  |  |  | Coincident | 4.3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.262
|  |  |  | Coincident | 2.19
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.2935
|  |  |  | Coincident | 2.2226
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.13844
|  |  |  | Coincident | 0.027383
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.2375
|  |  |  | Coincident | 2.2138
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.2687
|  |  |  | Coincident | 2.2453
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.0223
|  |  |  | Coincident | 2.0009
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.0505
|  |  |  | Coincident | 2.0294
| Willunga 11kV | Substation Rating | MVA | Non-Coincident | 6.7
|  |  |  | Coincident | 6.7
|  | Raw Adjusted MD | MW | Non-Coincident | 4.9271
|  |  |  | Coincident | 4.7707
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.1832
|  |  |  | Coincident | 5.0086
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.26769
|  |  |  | Coincident | 0.05295
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.8689
|  |  |  | Coincident | 4.7905
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.1164
|  |  |  | Coincident | 5.0288
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.1584
|  |  |  | Coincident | 4.0914
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.3697
|  |  |  | Coincident | 4.2949
| Willunga 33kV | Substation Rating | MVA | Non-Coincident | 10.6
|  |  |  | Coincident | 10.6
|  | Raw Adjusted MD | MW | Non-Coincident | 3.047
|  |  |  | Coincident | 2.8663
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.1515
|  |  |  | Coincident | 2.9621
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.12996
|  |  |  | Coincident | 0.025706
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.9272
|  |  |  | Coincident | 2.8386
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.0327
|  |  |  | Coincident | 2.9399
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.5001
|  |  |  | Coincident | 2.4244
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.5902
|  |  |  | Coincident | 2.5109
| Wilmington 11kV | Substation Rating | MVA | Non-Coincident | 2
|  |  |  | Coincident | 2
|  | Raw Adjusted MD | MW | Non-Coincident | 0.794
|  |  |  | Coincident | 0.76
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.80091
|  |  |  | Coincident | 0.76708
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0096451
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.78143
|  |  |  | Coincident | 0.78143
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.79144
|  |  |  | Coincident | 0.79144
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.71529
|  |  |  | Coincident | 0.71529
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.72445
|  |  |  | Coincident | 0.72445
| Wirrabara Forest 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.31894
|  |  |  | Coincident | 0.31894
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.34295
|  |  |  | Coincident | 0.34295
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0019739
|  |  |  | Coincident | 0.0019739
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.44711
|  |  |  | Coincident | 0.43145
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.44929
|  |  |  | Coincident | 0.43363
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.41772
|  |  |  | Coincident | 0.40309
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.41976
|  |  |  | Coincident | 0.40513
| Wirrabara South 11kV | Substation Rating | MVA | Non-Coincident | 0.13
|  |  |  | Coincident | 0.13
|  | Raw Adjusted MD | MW | Non-Coincident | 0.043204
|  |  |  | Coincident | 0.043204
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.043428
|  |  |  | Coincident | 0.043428
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 5.472e-05
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.043204
|  |  |  | Coincident | 0.043204
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.043428
|  |  |  | Coincident | 0.043428
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.039497
|  |  |  | Coincident | 0.039497
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.039702
|  |  |  | Coincident | 0.039702
| Wirrina Cove 11kV | Substation Rating | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.95
|  | Raw Adjusted MD | MW | Non-Coincident | 0.6497
|  |  |  | Coincident | 0.55917
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.65086
|  |  |  | Coincident | 0.56103
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.0014252
|  |  |  | Coincident | 0.0014252
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.6497
|  |  |  | Coincident | 0.55917
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.65086
|  |  |  | Coincident | 0.56103
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.58133
|  |  |  | Coincident | 0.50032
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.58236
|  |  |  | Coincident | 0.50199
| Wongyarra 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.086571
|  |  |  | Coincident | 0.086571
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.087018
|  |  |  | Coincident | 0.087018
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.00033948
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.086571
|  |  |  | Coincident | 0.086571
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.087018
|  |  |  | Coincident | 0.087018
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.079148
|  |  |  | Coincident | 0.079148
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.079557
|  |  |  | Coincident | 0.079557
| Woodforde 11kV | Substation Rating | MVA | Non-Coincident | 50.476
|  |  |  | Coincident | 50.476
|  | Raw Adjusted MD | MW | Non-Coincident | 40.779
|  |  |  | Coincident | 40.779
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.2581
|  |  |  | Coincident | 42.2581
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.25132
|  |  |  | Coincident | 0.25132
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.5178
|  |  |  | Coincident | 38.1943
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 39.9445
|  |  |  | Coincident | 39.5621
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.11
|  |  |  | Coincident | 33.8234
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.3734
|  |  |  | Coincident | 35.0348
| Woods Point 11kV | Substation Rating | MVA | Non-Coincident | 8.1
|  |  |  | Coincident | 8.1
|  | Raw Adjusted MD | MW | Non-Coincident | 3.7183
|  |  |  | Coincident | 1.5068
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.0485
|  |  |  | Coincident | 1.5504
|  | Date MD occurred |  | Non-Coincident | 2018-12-08
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.70833
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.2335
|  |  |  | Coincident | 0.01344
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.3284
|  |  |  | Coincident | 1.5308
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.6302
|  |  |  | Coincident | 1.5738
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.8278
|  |  |  | Coincident | 1.3538
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.0946
|  |  |  | Coincident | 1.3918
| Woodside 11kV | Substation Rating | MVA | Non-Coincident | 13
|  |  |  | Coincident | 13
|  | Raw Adjusted MD | MW | Non-Coincident | 9.1237
|  |  |  | Coincident | 9.1237
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.6127
|  |  |  | Coincident | 9.6127
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.089027
|  |  |  | Coincident | 0.089027
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.2944
|  |  |  | Coincident | 8.2944
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.7373
|  |  |  | Coincident | 8.7373
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.6259
|  |  |  | Coincident | 7.6259
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.0332
|  |  |  | Coincident | 8.0332
| Woodville 11kV | Substation Rating | MVA | Non-Coincident | 28.2
|  |  |  | Coincident | 28.2
|  | Raw Adjusted MD | MW | Non-Coincident | 14.5143
|  |  |  | Coincident | 14.2944
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.223
|  |  |  | Coincident | 14.8926
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.6875
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.88742
|  |  |  | Coincident | 0.037779
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.1677
|  |  |  | Coincident | 14.154
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.8749
|  |  |  | Coincident | 14.7463
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.4709
|  |  |  | Coincident | 12.4589
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.0934
|  |  |  | Coincident | 12.9803
| Woodville 33kV | Substation Rating | MVA | Non-Coincident | 37.89
|  |  |  | Coincident | 37.89
|  | Raw Adjusted MD | MW | Non-Coincident | 0.605
|  |  |  | Coincident | 0.4041
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.63818
|  |  |  | Coincident | 0.40997
|  | Date MD occurred |  | Non-Coincident | 2019-01-14
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.5625
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.65807
|  |  |  | Coincident | 0.43955
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.69416
|  |  |  | Coincident | 0.44593
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.63035
|  |  |  | Coincident | 0.42104
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.66493
|  |  |  | Coincident | 0.42715
| Woolpunda 11kV | Substation Rating | MVA | Non-Coincident | 18.8
|  |  |  | Coincident | 18.8
|  | Raw Adjusted MD | MW | Non-Coincident | 6.4829
|  |  |  | Coincident | 4.2141
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.9283
|  |  |  | Coincident | 4.5049
|  | Date MD occurred |  | Non-Coincident | 2019-03-01
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.9375
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0046193
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.8393
|  |  |  | Coincident | 6.2748
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.2794
|  |  |  | Coincident | 6.6584
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.3367
|  |  |  | Coincident | 5.8137
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.7445
|  |  |  | Coincident | 6.1691
| Wudinna 11kV | Substation Rating | MVA | Non-Coincident | 5.2
|  |  |  | Coincident | 5.2
|  | Raw Adjusted MD | MW | Non-Coincident | 1.998
|  |  |  | Coincident | 1.998
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.9983
|  |  |  | Coincident | 1.9983
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.019798
|  |  |  | Coincident | 0.019798
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.9719
|  |  |  | Coincident | 1.9057
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.972
|  |  |  | Coincident | 1.9058
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.8092
|  |  |  | Coincident | 1.7485
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.8093
|  |  |  | Coincident | 1.7486
| Yankalilla 11kV | Substation Rating | MVA | Non-Coincident | 16.6
|  |  |  | Coincident | 16.6
|  | Raw Adjusted MD | MW | Non-Coincident | 7.3101
|  |  |  | Coincident | 7.0237
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.4979
|  |  |  | Coincident | 7.201
|  | Date MD occurred |  | Non-Coincident | 2019-01-03
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.3461
|  |  |  | Coincident | 0.06846
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.9047
|  |  |  | Coincident | 7.6995
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.103
|  |  |  | Coincident | 7.8932
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.8358
|  |  |  | Coincident | 6.6584
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.0073
|  |  |  | Coincident | 6.8259
| Yankalilla 33kV | Substation Rating | MVA | Non-Coincident | 17.6
|  |  |  | Coincident | 17.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.2247
|  |  |  | Coincident | 1.0894
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.229
|  |  |  | Coincident | 1.0943
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.059136
|  |  |  | Coincident | 0.011697
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.2479
|  |  |  | Coincident | 1.113
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.2524
|  |  |  | Coincident | 1.1179
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.1239
|  |  |  | Coincident | 1.0023
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.1279
|  |  |  | Coincident | 1.0068
| Yankalilla Hill 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.12425
|  |  |  | Coincident | 0.10694
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.12447
|  |  |  | Coincident | 0.10729
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.83333
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.12425
|  |  |  | Coincident | 0.10694
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.12447
|  |  |  | Coincident | 0.10729
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.10939
|  |  |  | Coincident | 0.094152
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.10959
|  |  |  | Coincident | 0.094467
| Yongala 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.098796
|  |  |  | Coincident | 0.098796
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.10216
|  |  |  | Coincident | 0.10216
|  | Date MD occurred |  | Non-Coincident | 2019-01-23
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.85417
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.0011689
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.098796
|  |  |  | Coincident | 0.098796
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.10216
|  |  |  | Coincident | 0.10216
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.09236
|  |  |  | Coincident | 0.09236
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.095501
|  |  |  | Coincident | 0.095501
| Yorketown 11kV | Substation Rating | MVA | Non-Coincident | 2.6
|  |  |  | Coincident | 2.6
|  | Raw Adjusted MD | MW | Non-Coincident | 1.4951
|  |  |  | Coincident | 1.4341
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.5737
|  |  |  | Coincident | 1.5096
|  | Date MD occurred |  | Non-Coincident | 2019-01-24
|  |  |  | Coincident | 2019-01-24
|  | Half hour time period MD occurred |  | Non-Coincident | 0.79167
|  |  |  | Coincident | 0.83333
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.091557
|  |  |  | Coincident | 0.01811
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.2752
|  |  |  | Coincident | 1.2752
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.3423
|  |  |  | Coincident | 1.3423
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.1792
|  |  |  | Coincident | 1.1792
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.2413
|  |  |  | Coincident | 1.2413
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## 6.3 Sustained interruptions
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2018-19
6.3 SUSTAINED INTERRUPTIONS TO SUPPLY
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2018-19)
There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data.
Definitions:
Feeder classification definitions (column E) |  |  |  |  | Average duration of sustained customer interruption (column I) |  | Effect on unplanned SAIDI (column J) |  | Effect on unplanned SAIFI (column K)
CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km. Short rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km. Long rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km. |  |  |  |  | The average duration of an interruption experienced by an affected customer. |  | The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less). |  | The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
Date of event | Time of interruption | Asset ID | Feeder classification | Reason for interruption | Detailed reason for interruption | Number of customers affected by the interruption | Average duration of sustained customer interruption | Effect on unplanned SAIDI | Effect on unplanned SAIFI | MED
(DD/MM/YYYY) | (HH:MM) | (eg. feeder ID) | (drop down) | (select from options in drop-down box) | (select from options in column 'O' that correspond with reason in column 'F') |  | (minutes)
1/07/2018 | 00:17:14 | SG14 | Rural Short | Asset failure | LV | 15 | 237 | 0.026485 | 0.00011175 | No
1/07/2018 | 04:41:00 | SM349A | Urban | Third Party | Vehicle impact | 89 | 209 | 0.029737 | 0.00014228 | No
1/07/2018 | 09:19:00 | AP344A | Urban | Planned |  | 16 | 313 | 0.0080062 | 2.558e-05 | No
1/07/2018 | 09:34:00 | WK73 | Rural Short | Animal | Animal impact | 23 | 134 | 0.022961 | 0.00017135 | No
1/07/2018 | 13:52:05 | SM349A | Urban | Third Party | Vehicle impact | 89 | 276 | 0.03927 | 0.00014228 | No
1/07/2018 | 15:59:49 | AP529A | Urban | Overloads |  | 1 | 246 | 0.00039327 | 1.6e-06 | No
1/07/2018 | 18:44:59 | PL07 | Urban | Asset failure | LV | 19.3333 | 78 | 0.0024108 | 3.091e-05 | No
1/07/2018 | 21:16:43 | HH107B | Urban | Asset failure | LV | 40.3333 | 68 | 0.0043846 | 6.448e-05 | No
2/07/2018 | 07:10:36 | KA02 | Rural Short | Asset failure | LV | 17.3333 | 146 | 0.018854 | 0.00012914 | No
2/07/2018 | 08:16:00 | MTB32 | Rural Long | Planned |  | 109 | 306 | 0.24343 | 0.00079552 | No
2/07/2018 | 08:48:27 | HH121D | Urban | Asset failure | LV | 1 | 200 | 0.00031974 | 1.6e-06 | No
2/07/2018 | 08:57:00 | BM55 | Rural Short | Planned |  | 1 | 141 | 0.0010505 | 7.45e-06 | No
2/07/2018 | 09:02:00 | EL12 | Urban | Planned |  | 28 | 279 | 0.012489 | 4.476e-05 | No
2/07/2018 | 09:03:00 | AP227A | Urban | Planned |  | 463 | 281 | 0.20799 | 0.00074019 | No
2/07/2018 | 09:07:00 | PL02 | Urban | Planned |  | 2 | 5795 | 0.018529 | 3.2e-06 | No
2/07/2018 | 09:09:23 | MTB21 | Rural Short | Asset failure | LV | 1 | 143 | 0.0010654 | 7.45e-06 | No
2/07/2018 | 09:13:00 | HH386C | Urban | Planned |  | 97 | 154 | 0.023881 | 0.00015507 | No
2/07/2018 | 09:27:00 | MV53 | Rural Short | Planned |  | 63 | 293 | 0.13752 | 0.00046936 | No
2/07/2018 | 09:42:00 | ST13 | Rural Short | Planned |  | 5 | 322 | 0.011995 | 3.725e-05 | No
2/07/2018 | 09:47:00 | MV42 | Rural Short | Planned |  | 3 | 83 | 0.0018551 | 2.235e-05 | No
2/07/2018 | 10:22:32 | HH386F | Urban | Asset failure | LV | 30 | 187 | 0.0089686 | 4.796e-05 | No
2/07/2018 | 10:39:58 | HH386B | Urban | Planned |  | 4 | 56 | 0.0003581 | 6.39e-06 | No
2/07/2018 | 10:50:00 | GA21 | Rural Long | Unknown | Unknown | 1 | 30 | 0.00021895 | 7.3e-06 | No
2/07/2018 | 11:04:22 | LM61 | Rural Long | Weather |  | 1 | 457 | 0.0033353 | 7.3e-06 | No
2/07/2018 | 11:26:00 | GU43 | Rural Long | Planned |  | 36 | 36 | 0.0094587 | 0.00026274 | No
2/07/2018 | 11:26:36 | NL234B | Urban | Asset failure | LV | 1 | 296 | 0.00047321 | 1.6e-06 | No
2/07/2018 | 11:33:00 | SB16 | Rural Long | Planned |  | 1 | 21 | 0.00015327 | 7.3e-06 | No
2/07/2018 | 12:07:00 | YK12 | Rural Long | Planned |  | 78 | 179 | 0.1019 | 0.00056927 | No
2/07/2018 | 12:57:20 | BM21 | Rural Short | Asset failure | LV | 1 | 100 | 0.00074501 | 7.45e-06 | No
2/07/2018 | 12:58:00 | SD371 | Rural Long | Unknown | Unknown | 2534 | 73.165 | 1.3531 | 0.018494 | No
2/07/2018 | 14:19:28 | NL760C | Urban | Overloads |  | 1 | 194 | 0.00031014 | 1.6e-06 | No
2/07/2018 | 17:53:08 | NL115A | Urban | Overloads |  | 1 | 334 | 0.00053396 | 1.6e-06 | No
2/07/2018 | 18:48:41 | VH15 | Rural Short | Asset failure | LV | 1 | 231 | 0.001721 | 7.45e-06 | No
2/07/2018 | 19:30:29 | HH118A | Urban | Asset failure | LV | 1 | 194 | 0.00031014 | 1.6e-06 | No
2/07/2018 | 20:29:16 | AP355B | Urban | Asset failure | LV | 1 | 125 | 0.00019983 | 1.6e-06 | No
2/07/2018 | 22:02:50 | SA33 | Urban | Asset failure | LV | 1 | 163 | 0.00026058 | 1.6e-06 | No
2/07/2018 | 22:19:07 | HH522C | Urban | Asset failure | LV | 19.6666 | 63 | 0.0019808 | 3.144e-05 | No
3/07/2018 | 00:32:32 | MB11 | Rural Short | Asset failure | LV | 1 | 137 | 0.0010207 | 7.45e-06 | No
3/07/2018 | 00:35:48 | GA800A | Rural Short | Asset failure | LV | 5 | 193 | 0.0071894 | 3.725e-05 | No
3/07/2018 | 02:25:00 | CBD412A | CBD | 7 - STPIS Exclusion (3.3)(a) |  | 182 | 1291.0769 | 45.6131 | 0.03533 | No
3/07/2018 | 02:25:00 | CBD412A | Urban | 7 - STPIS Exclusion (3.3)(a) |  | 202 | 5 | 0.0016147 | 0.00032293 | No
3/07/2018 | 02:31:00 | HH386B | Urban | Animal | Animal impact | 1615 | 59.2557 | 0.15299 | 0.0025819 | No
3/07/2018 | 08:39:00 | KI45 | Rural Long | Planned |  | 1 | 144 | 0.001051 | 7.3e-06 | No
3/07/2018 | 08:39:00 | SB18 | Rural Long | Planned |  | 22 | 227 | 0.036448 | 0.00016056 | No
3/07/2018 | 08:56:00 | MV22 | Rural Short | Planned |  | 4 | 279 | 0.0083144 | 2.98e-05 | No
3/07/2018 | 08:57:00 | MTB72 | Rural Short | Planned |  | 32 | 301 | 0.07176 | 0.0002384 | No
3/07/2018 | 08:57:00 | MTB72 | Rural Long | Planned |  | 122 | 323 | 0.2876 | 0.0008904 | No
3/07/2018 | 09:03:00 | MB82 | Rural Long | Planned |  | 13 | 284 | 0.026945 | 9.488e-05 | No
3/07/2018 | 09:12:00 | SA18 | Urban | Planned |  | 35 | 279 | 0.015611 | 5.595e-05 | No
3/07/2018 | 09:17:00 | YK16 | Rural Long | Planned |  | 14 | 354 | 0.036171 | 0.00010218 | No
3/07/2018 | 09:17:16 | GA03 | Rural Long | Asset failure | LV | 1 | 249 | 0.0018173 | 7.3e-06 | No
3/07/2018 | 09:41:00 | GU15 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 114 | 55.5351 | 0.046206 | 0.00083201 | No
3/07/2018 | 09:46:00 | G11 | Rural Long | Third Party | Vehicle impact | 52 | 239 | 0.090704 | 0.00037951 | No
3/07/2018 | 10:03:00 | HH121C | Urban | Planned |  | 117 | 132 | 0.02469 | 0.00018704 | No
3/07/2018 | 10:15:00 | HH121D | Urban | Planned |  | 242 | 206.686 | 0.079963 | 0.00038688 | No
3/07/2018 | 10:17:27 | AP529D | Urban | Vegetation | Grow-in - NSP responsibility | 31 | 80 | 0.0039647 | 4.956e-05 | No
3/07/2018 | 10:18:00 | ST36 | Rural Long | Planned |  | 34 | 181 | 0.044914 | 0.00024814 | No
3/07/2018 | 10:46:37 | HH121E | Urban | Planned |  | 1 | 69 | 0.00011031 | 1.6e-06 | No
3/07/2018 | 12:03:28 | AP529E | Urban | Asset failure | LV | 1 | 124 | 0.00019824 | 1.6e-06 | No
3/07/2018 | 12:04:31 | ME131B | Urban | Asset failure | LV | 1 | 198 | 0.00031654 | 1.6e-06 | No
3/07/2018 | 12:20:00 | ME200C | Urban | Unknown | Unknown | 1 | 2958 | 0.0047289 | 1.6e-06 | No
3/07/2018 | 13:42:00 | EL19 | Urban | Unknown | Unknown | 1 | 20 | 3.197e-05 | 1.6e-06 | No
3/07/2018 | 14:11:16 | HH107A | Urban | Asset failure | LV | 1 | 105 | 0.00016786 | 1.6e-06 | No
3/07/2018 | 15:31:14 | YK11 | Rural Long | Asset failure | LV | 1 | 299 | 0.0021822 | 7.3e-06 | No
3/07/2018 | 16:22:00 | SD312 | Rural Long | Unknown | Unknown | 21.6667 | 160 | 0.025301 | 0.00015813 | No
3/07/2018 | 16:24:09 | SA18 | Urban | Asset failure | LV | 11.6667 | 59 | 0.0011004 | 1.865e-05 | No
3/07/2018 | 16:33:21 | HH121D | Urban | Asset failure | LV | 1 | 166 | 0.00026538 | 1.6e-06 | No
3/07/2018 | 17:06:00 | PL10 | Rural Long | Unknown | Unknown | 43 | 102 | 0.032011 | 0.00031383 | No
3/07/2018 | 17:59:00 | HH177A | Urban | Third Party | Vehicle impact | 681 | 102.0132 | 0.11106 | 0.0010887 | No
3/07/2018 | 18:08:14 | HH341H | Urban | Asset failure | LV | 1 | 303 | 0.0004844 | 1.6e-06 | No
3/07/2018 | 19:29:42 | NL234C | Urban | Animal | Animal impact | 41 | 183 | 0.011995 | 6.555e-05 | No
4/07/2018 | 01:49:00 | SG03 | Rural Short | Vegetation | Grow-in - NSP responsibility | 40 | 691 | 0.20592 | 0.00029801 | No
4/07/2018 | 03:19:00 | MTB21 | Rural Short | Animal | Animal impact | 1240 | 136.0379 | 1.2567 | 0.0092382 | No
4/07/2018 | 06:12:00 | SSD714 | Rural Long | Unknown | Unknown | 1066 | 71 | 0.55238 | 0.00778 | No
4/07/2018 | 08:18:00 | ST44 | Rural Long | Planned |  | 6 | 236 | 0.010334 | 4.379e-05 | No
4/07/2018 | 08:19:00 | YK17 | Rural Long | Planned |  | 65 | 275 | 0.13046 | 0.00047439 | No
4/07/2018 | 08:36:00 | CL04 | Rural Long | Planned |  | 1 | 125 | 0.00091229 | 7.3e-06 | No
4/07/2018 | 08:36:00 | PL15 | Rural Long | Planned |  | 9 | 420.1111 | 0.027595 | 6.569e-05 | No
4/07/2018 | 09:06:26 | NL115C | Urban | Asset failure | LV | 40 | 145 | 0.0092723 | 6.395e-05 | No
4/07/2018 | 09:07:00 | KA02 | Rural Short | Planned |  | 649 | 386 | 1.8664 | 0.0048351 | No
4/07/2018 | 09:07:25 | NL115C | Urban | Asset failure | LV | 30 | 148 | 0.0070981 | 4.796e-05 | No
4/07/2018 | 09:10:00 | SA41 | Urban | Unknown | Unknown | 7 | 22 | 0.0002462 | 1.119e-05 | No
4/07/2018 | 09:12:03 | KI15 | Rural Long | Asset failure | HV | 1 | 274 | 0.0019997 | 7.3e-06 | No
4/07/2018 | 09:16:00 | MI10 | Rural Long | Planned |  | 48 | 286 | 0.10019 | 0.00035032 | No
4/07/2018 | 09:24:11 | HH496D | Urban | Overloads |  | 1 | 107 | 0.00017106 | 1.6e-06 | No
4/07/2018 | 09:50:00 | MV53 | Rural Short | Planned |  | 58 | 295 | 0.12747 | 0.00043211 | No
4/07/2018 | 10:02:00 | CN83 | Rural Long | Planned |  | 40 | 55 | 0.016056 | 0.00029193 | No
4/07/2018 | 10:03:00 | MTB32 | Rural Long | Planned |  | 72 | 251.8333 | 0.13233 | 0.00052548 | No
4/07/2018 | 10:07:00 | HH121D | Urban | Planned |  | 79 | 40 | 0.0050518 | 0.0001263 | No
4/07/2018 | 10:08:00 | ST36 | Rural Long | Planned |  | 130 | 250 | 0.2372 | 0.00094878 | No
4/07/2018 | 10:10:58 | HH121D | Urban | Planned |  | 7 | 85 | 0.00095121 | 1.119e-05 | No
4/07/2018 | 10:23:00 | G08 | Rural Long | Planned |  | 30 | 182 | 0.039849 | 0.00021895 | No
4/07/2018 | 11:31:56 | LX75 | Rural Long | Asset failure | LV | 2 | 132 | 0.0019268 | 1.46e-05 | No
4/07/2018 | 14:40:00 | CD02 | Rural Long | Unknown | Unknown | 1 | 60 | 0.0004379 | 7.3e-06 | No
4/07/2018 | 15:49:08 | NL115A | Urban | Other |  | 1 | 147 | 0.00023501 | 1.6e-06 | No
4/07/2018 | 16:22:00 | SSD475 | Rural Short | Animal | Animal nesting/burrowing, etc and other | 896 | 89.5748 | 0.59794 | 0.0066753 | No
4/07/2018 | 17:41:14 | AP365A | Urban | Overloads |  | 1 | 173 | 0.00027657 | 1.6e-06 | No
4/07/2018 | 18:33:47 | GU13 | Rural Long | Unknown | Unknown | 1 | 167 | 0.0012188 | 7.3e-06 | No
4/07/2018 | 19:46:11 | GA05 | Rural Short | Asset failure | LV | 1 | 131 | 0.00097597 | 7.45e-06 | No
5/07/2018 | 04:58:48 | SM350F | Urban | Asset failure | LV | 20.3333 | 124 | 0.0040308 | 3.251e-05 | No
5/07/2018 | 08:56:00 | NU16 | Rural Long | Planned |  | 96 | 358 | 0.25083 | 0.00070064 | No
5/07/2018 | 09:00:00 | SG04 | Rural Short | Planned |  | 53 | 242.6226 | 0.095801 | 0.00039486 | No
5/07/2018 | 09:10:00 | W17 | Rural Long | Planned |  | 7 | 131 | 0.0066926 | 5.109e-05 | No
5/07/2018 | 09:27:36 | AP424C | Urban | Planned |  | 1 | 137 | 0.00021902 | 1.6e-06 | No
5/07/2018 | 09:36:46 | AP424C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 116 | 0.00018545 | 1.6e-06 | No
5/07/2018 | 09:39:00 | SA14 | Urban | Planned |  | 53 | 182.1132 | 0.01543 | 8.473e-05 | No
5/07/2018 | 09:48:00 | CV03 | Rural Short | Planned |  | 17 | 193 | 0.024444 | 0.00012665 | No
5/07/2018 | 10:00:00 | CD20 | Rural Long | Planned |  | 1 | 86 | 0.00062766 | 7.3e-06 | No
5/07/2018 | 10:37:00 | EL15 | Urban | Planned |  | 81 | 141 | 0.018258 | 0.00012949 | No
5/07/2018 | 10:40:00 | KI53 | Rural Long | Planned |  | 3 | 60 | 0.0013137 | 2.19e-05 | No
5/07/2018 | 10:44:00 | G04 | Rural Long | Planned |  | 7 | 257 | 0.01313 | 5.109e-05 | No
5/07/2018 | 10:48:00 | VH17 | Rural Short | Unknown | Unknown | 17 | 139 | 0.017605 | 0.00012665 | No
5/07/2018 | 10:54:00 | YK04 | Rural Short | Planned |  | 4 | 93 | 0.0027715 | 2.98e-05 | No
5/07/2018 | 11:16:00 | KA07 | Rural Long | Asset failure | HV | 74 | 199.6486 | 0.10783 | 0.00054008 | No
5/07/2018 | 11:45:00 | CL12 | Rural Long | Planned |  | 2 | 49 | 0.00071524 | 1.46e-05 | No
5/07/2018 | 12:51:00 | R12 | Rural Long | Unknown | Unknown | 1 | 26 | 0.00018976 | 7.3e-06 | No
5/07/2018 | 13:18:38 | MV52 | Rural Short | Asset failure | LV | 1 | 65 | 0.00048426 | 7.45e-06 | No
5/07/2018 | 14:31:00 | BU02 | Rural Long | Asset failure | HV | 102 | 162.1176 | 0.12069 | 0.00074443 | No
5/07/2018 | 14:59:29 | HH341G | Urban | Asset failure | LV | 1 | 143 | 0.00022861 | 1.6e-06 | No
5/07/2018 | 15:06:39 | GU23 | Rural Long | Unknown | Unknown | 2 | 130 | 0.0018976 | 1.46e-05 | No
5/07/2018 | 15:40:00 | MTB21 | Rural Short | Unknown | Unknown | 23 | 152 | 0.026046 | 0.00017135 | No
5/07/2018 | 23:52:00 | HH496E | Urban | Asset failure | HV | 799 | 81.4468 | 0.10404 | 0.0012773 | No
5/07/2018 | 23:58:09 | HH107B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 580 | 0.00092723 | 1.6e-06 | No
6/07/2018 | 00:34:00 | KA07 | Rural Long | Asset failure | HV | 74 | 125.9459 | 0.068021 | 0.00054008 | No
6/07/2018 | 00:56:00 | NA09 | Rural Long | Unknown | Unknown | 807 | 166.8848 | 0.98291 | 0.0058898 | No
6/07/2018 | 06:13:04 | SG09 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 223 | 0.0016614 | 7.45e-06 | No
6/07/2018 | 06:24:00 | MV12 | Urban | Planned |  | 4 | 158 | 0.0010104 | 6.39e-06 | No
6/07/2018 | 06:42:00 | GU13 | Rural Long | Unknown | Unknown | 10 | 215 | 0.015691 | 7.298e-05 | No
6/07/2018 | 07:29:18 | SM349A | Urban | Asset failure | LV | 4 | 201 | 0.0012853 | 6.39e-06 | No
6/07/2018 | 08:06:00 | MV15 | Rural Short | Planned |  | 62 | 188 | 0.086839 | 0.00046191 | No
6/07/2018 | 08:18:00 | MG38 | Rural Short | Planned |  | 3 | 138 | 0.0030844 | 2.235e-05 | No
6/07/2018 | 08:24:31 | GU35 | Rural Long | Overloads |  | 2 | 172 | 0.0025106 | 1.46e-05 | No
6/07/2018 | 08:45:00 | SG09 | Rural Short | Planned |  | 85 | 362 | 0.22924 | 0.00063326 | No
6/07/2018 | 08:55:00 | SG04 | Rural Short | Planned |  | 11 | 77 | 0.0063103 | 8.195e-05 | No
6/07/2018 | 09:10:00 | VH45 | Rural Short | Planned |  | 2 | 54 | 0.00080462 | 1.49e-05 | No
6/07/2018 | 09:20:00 | MG09 | Rural Short | Planned |  | 9 | 150 | 0.010058 | 6.705e-05 | No
6/07/2018 | 09:25:00 | ST34 | Rural Long | Planned |  | 8 | 259 | 0.015122 | 5.839e-05 | No
6/07/2018 | 09:36:00 | WHY14 | Urban | Planned |  | 100 | 183 | 0.029256 | 0.00015987 | No
6/07/2018 | 09:43:00 | HH121F | Urban | Planned |  | 216 | 267 | 0.092199 | 0.00034531 | No
6/07/2018 | 09:52:00 | ST16 | Rural Short | Planned |  | 43 | 266 | 0.085215 | 0.00032036 | No
6/07/2018 | 10:10:00 | ME131B | Urban | Planned |  | 149 | 313 | 0.074557 | 0.0002382 | No
6/07/2018 | 10:12:00 | NL210C | Urban | Planned |  | 75 | 276 | 0.033093 | 0.0001199 | No
6/07/2018 | 10:32:00 | HH341G | Urban | Planned |  | 280 | 340 | 0.15219 | 0.00044763 | No
6/07/2018 | 11:21:51 | SA744D | Urban | Asset failure | LV | 1 | 88 | 0.00014068 | 1.6e-06 | No
6/07/2018 | 13:26:25 | MG11 | Rural Short | Asset failure | LV | 10.3333 | 101 | 0.0077755 | 7.698e-05 | No
6/07/2018 | 16:38:00 | SD444 | Rural Short | Asset failure | Subtransmission | 896 | 195.3158 | 1.3038 | 0.0066753 | No
6/07/2018 | 18:20:54 | AP125D | Urban | Asset failure | LV | 1 | 478 | 0.00076417 | 1.6e-06 | No
6/07/2018 | 20:31:00 | YK29 | Rural Long | Asset failure | Distribution substation | 146 | 109 | 0.11615 | 0.0010656 | No
6/07/2018 | 21:04:00 | MG04 | Rural Short | Weather |  | 1721 | 229.5851 | 2.9437 | 0.012822 | No
6/07/2018 | 21:04:00 | MG04 | Rural Short | Weather |  | 0 | 2.3719 | 0.040201 | 0 | No
6/07/2018 | 21:31:43 | SM172C | Urban | Asset failure | LV | 67.6666 | 418 | 0.045218 | 0.00010818 | No
6/07/2018 | 22:05:39 | R04 | Rural Long | Asset failure | LV | 2 | 137 | 0.0019997 | 1.46e-05 | No
6/07/2018 | 22:21:00 | NL115C | Urban | Weather |  | 2358 | 179.3533 | 0.6761 | 0.0037697 | No
6/07/2018 | 22:26:31 | NL115C | Urban | Asset failure | HV | 399 | 8 | 0.005103 | 0.00063787 | No
6/07/2018 | 22:59:00 | MI17 | Rural Long | Weather |  | 96 | 522.1771 | 0.36586 | 0.00070064 | No
6/07/2018 | 23:26:35 | HH429C | Urban | Vegetation | Grow-in - NSP responsibility | 44.3333 | 932 | 0.066055 | 7.087e-05 | No
7/07/2018 | 00:00:25 | HH522B | Urban | Asset failure | LV | 7 | 825 | 0.0092323 | 1.119e-05 | No
7/07/2018 | 00:34:00 | HH148B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 825 | 325 | 0.42864 | 0.0013189 | No
7/07/2018 | 01:48:00 | SM411D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 65 | 900 | 0.093522 | 0.00010391 | No
7/07/2018 | 01:54:00 | SM137A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1815 | 180 | 0.52229 | 0.0029016 | No
7/07/2018 | 01:56:00 | ME131D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 719 | 456 | 0.52415 | 0.0011494 | No
7/07/2018 | 01:57:00 | SG07 | Rural Short | Unknown | Unknown | 234 | 204 | 0.35564 | 0.0017433 | No
7/07/2018 | 01:58:00 | HH102B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1003 | 291.3988 | 0.46725 | 0.0016035 | No
7/07/2018 | 01:58:00 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 905 | 723 | 1.046 | 0.0014468 | No
7/07/2018 | 01:59:00 | HH341H | Urban | Weather |  | 1893 | 324.879 | 0.98318 | 0.0030263 | No
7/07/2018 | 02:00:00 | HH177A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 679 | 489 | 0.53081 | 0.0010855 | No
7/07/2018 | 02:04:11 | HH145E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 667 | 0.0010663 | 1.6e-06 | No
7/07/2018 | 02:04:27 | HH428C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 50 | 533 | 0.042605 | 7.993e-05 | No
7/07/2018 | 02:05:00 | SM410B | Urban | Unknown | Unknown | 1890 | 491 | 1.4836 | 0.0030215 | No
7/07/2018 | 02:11:03 | HH432F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 457 | 0.00073059 | 1.6e-06 | No
7/07/2018 | 02:11:57 | SA711C | Urban | Vegetation | Grow-in - NSP responsibility | 19 | 287 | 0.0087176 | 3.037e-05 | No
7/07/2018 | 02:14:46 | HH341C | Urban | Vegetation | Grow-in - NSP responsibility | 147 | 767 | 0.18025 | 0.00023501 | No
7/07/2018 | 02:16:00 | GA05 | Rural Short | Weather |  | 433 | 285 | 0.91939 | 0.0032259 | No
7/07/2018 | 02:16:33 | HH145C | Urban | Unknown | Unknown | 36.3333 | 775 | 0.045016 | 5.809e-05 | No
7/07/2018 | 02:21:23 | HH121F | Urban | Unknown | Unknown | 19.6666 | 569 | 0.01789 | 3.144e-05 | No
7/07/2018 | 02:41:01 | EL07 | Urban | Asset failure | LV | 28 | 679 | 0.030394 | 4.476e-05 | No
7/07/2018 | 02:43:38 | AP146C | Urban | Vegetation | Grow-in - NSP responsibility | 41.6666 | 767 | 0.051091 | 6.661e-05 | No
7/07/2018 | 03:27:00 | AP373G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 120 | 728.225 | 0.1397 | 0.00019184 | No
7/07/2018 | 03:27:00 | HH107C | Urban | Unknown | Unknown | 2416 | 18.7355 | 0.072364 | 0.0038624 | No
7/07/2018 | 03:34:00 | AP373E | Urban | Asset failure | HV | 223 | 1082.9193 | 0.38607 | 0.0003565 | No
7/07/2018 | 03:34:00 | AP373E | Urban | Asset failure | HV | 0 | 43 | 0.01313 | 0 | No
7/07/2018 | 03:43:00 | NU31 | Rural Long | Asset failure | HV | 195.6667 | 311.9114 | 0.44542 | 0.001428 | No
7/07/2018 | 03:45:43 | AP424E | Urban | Asset failure | LV | 139 | 698 | 0.15511 | 0.00022222 | No
7/07/2018 | 03:49:16 | HH177C | Urban | Unknown | Unknown | 16.3333 | 430 | 0.011228 | 2.611e-05 | No
7/07/2018 | 05:19:17 | HH107A | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 554 | 0.0088567 | 1.599e-05 | No
7/07/2018 | 07:18:45 | AP424A | Urban | Overloads |  | 83 | 652 | 0.086514 | 0.00013269 | No
7/07/2018 | 07:23:16 | HH341E | Urban | Asset failure | LV | 48 | 465 | 0.035682 | 7.674e-05 | No
7/07/2018 | 07:32:04 | HH102A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 175 | 0.00027977 | 1.6e-06 | No
7/07/2018 | 07:32:57 | SA711C | Urban | Weather |  | 19 | 191 | 0.0058016 | 3.037e-05 | No
7/07/2018 | 08:01:58 | MG34 | Rural Long | Weather |  | 2 | 599 | 0.0087434 | 1.46e-05 | No
7/07/2018 | 08:02:31 | ST22 | Rural Short | Third Party | Vehicle impact | 1 | 136 | 0.0010132 | 7.45e-06 | No
7/07/2018 | 08:07:59 | AP351E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 636 | 0.0010168 | 1.6e-06 | No
7/07/2018 | 08:42:47 | KI32 | Rural Short | Asset failure | LV | 1 | 207 | 0.0015422 | 7.45e-06 | No
7/07/2018 | 08:53:19 | MG17 | Rural Long | Overloads |  | 1 | 76 | 0.00055467 | 7.3e-06 | No
7/07/2018 | 09:40:45 | MT06 | Rural Long | Asset failure | LV | 1 | 168 | 0.0012261 | 7.3e-06 | No
7/07/2018 | 09:55:00 | M04 | Rural Long | Unknown | Unknown | 69 | 30 | 0.015108 | 0.00050359 | No
7/07/2018 | 10:09:51 | HH429C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 329 | 0.00052596 | 1.6e-06 | No
7/07/2018 | 10:24:33 | SM126C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 277 | 0.00044283 | 1.6e-06 | No
7/07/2018 | 10:29:24 | HH130A | Urban | Vegetation | Grow-in - NSP responsibility | 91 | 219 | 0.03186 | 0.00014548 | No
7/07/2018 | 10:34:00 | MG03 | Rural Short | Unknown | Unknown | 39 | 266 | 0.077288 | 0.00029056 | No
7/07/2018 | 10:45:33 | AP139B | Urban | Weather |  | 1 | 504 | 0.00080573 | 1.6e-06 | No
7/07/2018 | 10:54:08 | SM374E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 72 | 40 | 0.0046042 | 0.0001151 | No
7/07/2018 | 11:08:00 | CBD353B | Urban | Planned |  | 78 | 1716 | 0.21398 | 0.0001247 | No
7/07/2018 | 12:00:00 | BU08 | Rural Long | Asset failure | HV | 46 | 1329.9348 | 0.44649 | 0.00033572 | No
7/07/2018 | 12:01:07 | MI14 | Rural Long | Other |  | 1 | 27 | 0.00019706 | 7.3e-06 | No
7/07/2018 | 15:24:34 | HH341K | Urban | Vegetation | Grow-in - NSP responsibility | 18.6666 | 102 | 0.0030439 | 2.984e-05 | No
7/07/2018 | 15:33:00 | MG48 | Rural Long | Weather |  | 99 | 41 | 0.029624 | 0.00072254 | No
7/07/2018 | 15:40:56 | HH177E | Urban | Asset failure | LV | 58 | 67 | 0.0062124 | 9.272e-05 | No
7/07/2018 | 16:01:15 | AP529E | Urban | Weather |  | 62 | 76 | 0.007533 | 9.912e-05 | No
7/07/2018 | 17:10:00 | AP424E | Urban | Unknown | Unknown | 80 | 193 | 0.024684 | 0.00012789 | No
7/07/2018 | 17:10:14 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 75 | 66 | 0.0079134 | 0.0001199 | No
7/07/2018 | 17:19:48 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 29.3333 | 320 | 0.015006 | 4.689e-05 | No
7/07/2018 | 18:34:30 | BU08 | Rural Long | Asset failure | HV | 41 | 1123.8537 | 0.33629 | 0.00029923 | No
7/07/2018 | 18:39:30 | HH121E | Urban | Asset failure | LV | 1 | 114 | 0.00018225 | 1.6e-06 | No
7/07/2018 | 20:52:57 | HH177E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 473 | 0.00075617 | 1.6e-06 | No
7/07/2018 | 21:25:21 | MG17 | Rural Long | Unknown | Unknown | 2 | 281 | 0.0041017 | 1.46e-05 | No
8/07/2018 | 00:05:48 | SG14 | Rural Short | Asset failure | LV | 1 | 220 | 0.001639 | 7.45e-06 | No
8/07/2018 | 01:11:29 | MTB61 | Rural Short | Asset failure | LV | 25.6666 | 62 | 0.011856 | 0.00019122 | No
8/07/2018 | 03:16:30 | MV52 | Rural Short | Unknown | Unknown | 7.6667 | 414 | 0.023647 | 5.712e-05 | No
8/07/2018 | 06:53:52 | PP14 | Rural Long | Overloads |  | 2 | 411 | 0.0059992 | 1.46e-05 | No
8/07/2018 | 07:15:00 | ME200D | Urban | Planned |  | 11 | 275 | 0.004836 | 1.759e-05 | No
8/07/2018 | 07:23:07 | AP424C | Urban | Asset failure | LV | 1 | 271 | 0.00043324 | 1.6e-06 | No
8/07/2018 | 07:23:40 | GA02 | Rural Short | Overloads |  | 2 | 201 | 0.002995 | 1.49e-05 | No
8/07/2018 | 08:04:00 | SD406 | Rural Long | Planned |  | 2014 | 380.139 | 5.5876 | 0.014699 | No
8/07/2018 | 08:10:00 | AP373C | Urban | Planned |  | 1 | 39 | 6.235e-05 | 1.6e-06 | No
8/07/2018 | 08:10:00 | MG17 | Rural Long | Asset failure | HV | 356 | 142.3315 | 0.36981 | 0.0025982 | No
8/07/2018 | 09:13:00 | CV757A | Rural Long | Planned |  | 250 | 248 | 0.4525 | 0.0018246 | No
8/07/2018 | 09:18:00 | PL803C | Urban | Planned |  | 260 | 110 | 0.045722 | 0.00041566 | No
8/07/2018 | 09:36:00 | HH118B | Urban | Planned |  | 10 | 190 | 0.0030375 | 1.599e-05 | No
8/07/2018 | 11:45:00 | NA04 | Rural Long | Unknown | Unknown | 2 | 60 | 0.0008758 | 1.46e-05 | No
8/07/2018 | 12:49:31 | MV42 | Rural Short | Asset failure | LV | 2 | 498 | 0.0074204 | 1.49e-05 | No
8/07/2018 | 12:58:15 | SM137A | Urban | Asset failure | LV | 1 | 197 | 0.00031494 | 1.6e-06 | No
8/07/2018 | 14:14:49 | AP424F | Urban | Asset failure | LV | 1 | 134 | 0.00021422 | 1.6e-06 | No
8/07/2018 | 14:43:32 | WHY04 | Urban | Asset failure | LV | 1 | 148 | 0.0002366 | 1.6e-06 | No
8/07/2018 | 14:59:23 | MB24 | Rural Short | Asset failure | LV | 33 | 116 | 0.028519 | 0.00024585 | No
8/07/2018 | 15:32:48 | ME347B | Urban | Overloads |  | 1 | 1161 | 0.0018561 | 1.6e-06 | No
8/07/2018 | 16:01:30 | SA19 | Urban | Asset failure | LV | 57 | 88 | 0.008019 | 9.112e-05 | No
8/07/2018 | 17:19:45 | AP424F | Urban | Asset failure | LV | 1 | 364 | 0.00058192 | 1.6e-06 | No
8/07/2018 | 17:48:41 | NL210B | Urban | Asset failure | LV | 25.6666 | 270 | 0.011079 | 4.103e-05 | No
8/07/2018 | 17:56:00 | HH409A | Urban | Unknown | Unknown | 59.3334 | 192 | 0.018212 | 9.485e-05 | No
8/07/2018 | 19:21:59 | ME200F | Urban | Asset failure | LV | 1 | 245 | 0.00039168 | 1.6e-06 | No
8/07/2018 | 19:48:00 | MI17 | Rural Long | Asset failure | HV | 2 | 318 | 0.0046417 | 1.46e-05 | No
8/07/2018 | 20:26:21 | AP125D | Urban | Other |  | 15.3333 | 120 | 0.0029416 | 2.451e-05 | No
8/07/2018 | 20:28:10 | AP149D | Urban | Asset failure | LV | 58.9999 | 350 | 0.033013 | 9.432e-05 | No
8/07/2018 | 22:46:00 | AP373C | Urban | Planned |  | 21 | 348 | 0.011683 | 3.357e-05 | No
9/07/2018 | 08:32:00 | MV14 | Rural Short | Planned |  | 84 | 195.7738 | 0.12252 | 0.00062581 | No
9/07/2018 | 08:43:22 | HH130F | Urban | Asset failure | LV | 19 | 47 | 0.0014276 | 3.037e-05 | No
9/07/2018 | 09:07:00 | KI21 | Rural Long | Planned |  | 1 | 247 | 0.0018027 | 7.3e-06 | No
9/07/2018 | 09:09:00 | VH45 | Rural Short | Planned |  | 9 | 278.2222 | 0.018655 | 6.705e-05 | No
9/07/2018 | 09:15:00 | MTB13 | Rural Short | Planned |  | 30 | 144 | 0.032185 | 0.0002235 | No
9/07/2018 | 09:34:00 | MI32 | Rural Long | Unknown | Unknown | 1219 | 6.5726 | 0.058474 | 0.0088967 | No
9/07/2018 | 09:35:00 | HH148B | Urban | Planned |  | 1 | 143 | 0.00022861 | 1.6e-06 | No
9/07/2018 | 09:40:00 | MB24 | Rural Short | Planned |  | 19 | 147 | 0.020808 | 0.00014155 | No
9/07/2018 | 09:46:00 | HH107A | Urban | Planned |  | 1 | 40 | 6.395e-05 | 1.6e-06 | No
9/07/2018 | 10:49:30 | SM172F | Urban | Overloads |  | 1 | 106 | 0.00016946 | 1.6e-06 | No
9/07/2018 | 10:57:00 | PL754A | Rural Long | Planned |  | 2 | 170 | 0.0024814 | 1.46e-05 | No
9/07/2018 | 12:38:42 | CBD412B | Urban | Overloads |  | 1 | 32 | 5.116e-05 | 1.6e-06 | No
9/07/2018 | 13:30:00 | MG18 | Rural Long | Planned |  | 3 | 36 | 0.00078822 | 2.19e-05 | No
9/07/2018 | 14:06:00 | R36 | Rural Short | Unknown | Unknown | 17 | 50 | 0.0063326 | 0.00012665 | No
9/07/2018 | 16:06:11 | SA14 | Urban | Asset failure | LV | 1 | 370 | 0.00059151 | 1.6e-06 | No
9/07/2018 | 16:37:51 | EL11 | Urban | Asset failure | LV | 1 | 232 | 0.00037089 | 1.6e-06 | No
9/07/2018 | 18:01:16 | AP214B | Urban | Overloads |  | 20.3333 | 70 | 0.0022755 | 3.251e-05 | No
9/07/2018 | 19:17:55 | AP372D | Urban | Other |  | 8 | 213 | 0.0027241 | 1.279e-05 | No
9/07/2018 | 20:05:00 | CN53 | Rural Long | Unknown | Unknown | 7 | 10 | 0.00051088 | 5.109e-05 | No
9/07/2018 | 20:20:00 | HH177A | Urban | Planned |  | 2 | 56 | 0.00017905 | 3.2e-06 | No
10/07/2018 | 00:59:01 | MB13 | Rural Short | Asset failure | LV | 1 | 109 | 0.00081207 | 7.45e-06 | No
10/07/2018 | 01:37:28 | ST34 | Rural Long | Overloads |  | 11.3333 | 216 | 0.017866 | 8.271e-05 | No
10/07/2018 | 02:24:50 | CBD366E | Urban | Other |  | 1 | 367 | 0.00058671 | 1.6e-06 | No
10/07/2018 | 03:39:00 | CBD412A | CBD | Planned |  | 127 | 1 | 0.024653 | 0.024653 | No
10/07/2018 | 03:39:00 | CBD412A | Urban | Planned |  | 6 | 1 | 9.59e-06 | 9.59e-06 | No
10/07/2018 | 03:40:23 | CL16 | Rural Long | Third Party | Vehicle impact | 40 | 344 | 0.10043 | 0.00029193 | No
10/07/2018 | 07:03:57 | HH409D | Urban | Overloads |  | 1 | 261 | 0.00041725 | 1.6e-06 | No
10/07/2018 | 08:41:00 | KI21 | Rural Long | Planned |  | 4 | 167 | 0.0048753 | 2.919e-05 | No
10/07/2018 | 08:51:00 | NU21 | Rural Long | Planned |  | 25 | 329 | 0.060029 | 0.00018246 | No
10/07/2018 | 08:58:00 | NL760C | Urban | Planned |  | 171 | 284 | 0.077638 | 0.00027337 | No
10/07/2018 | 09:03:00 | CV22 | Rural Long | Planned |  | 16 | 302 | 0.035266 | 0.00011677 | No
10/07/2018 | 09:05:00 | EL16 | Urban | Planned |  | 65 | 97 | 0.01008 | 0.00010391 | No
10/07/2018 | 09:11:00 | ST42 | Rural Long | Unknown | Unknown | 154 | 6.7468 | 0.007583 | 0.0011239 | No
10/07/2018 | 09:15:00 | EL19 | Urban | Unknown | Unknown | 1 | 12 | 1.918e-05 | 1.6e-06 | No
10/07/2018 | 09:27:00 | R20 | Rural Long | Overloads |  | 1 | 213 | 0.0015546 | 7.3e-06 | No
10/07/2018 | 09:41:00 | SA17 | Urban | Planned |  | 188 | 275 | 0.082652 | 0.00030055 | No
10/07/2018 | 10:07:18 | VH44 | Rural Short | Planned |  | 35 | 277 | 0.072229 | 0.00026076 | No
10/07/2018 | 10:17:30 | SA17 | Urban | Planned |  | 1 | 183 | 0.00029256 | 1.6e-06 | No
10/07/2018 | 10:22:00 | SB02 | Rural Long | Planned |  | 2 | 99 | 0.0014451 | 1.46e-05 | No
10/07/2018 | 11:07:00 | MB65 | Rural Long | Planned |  | 1 | 67 | 0.00048899 | 7.3e-06 | No
10/07/2018 | 11:26:46 | SM349A | Urban | Asset failure | LV | 40 | 161 | 0.010295 | 6.395e-05 | No
10/07/2018 | 11:27:05 | HH432F | Urban | Asset failure | LV | 3 | 205 | 0.00098319 | 4.8e-06 | No
10/07/2018 | 11:56:31 | AP226E | Urban | Asset failure | LV | 1 | 293 | 0.00046841 | 1.6e-06 | No
10/07/2018 | 12:38:00 | HH341A | Urban | Unknown | Unknown | 97 | 103 | 0.015972 | 0.00015507 | No
10/07/2018 | 12:48:19 | WHY01 | Urban | Asset failure | LV | 1 | 183 | 0.00029256 | 1.6e-06 | No
10/07/2018 | 12:53:35 | EL01R | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
10/07/2018 | 14:06:12 | BM41 | Urban | Asset failure | LV | 2 | 63 | 0.00020143 | 3.2e-06 | No
10/07/2018 | 15:36:10 | ME427D | Urban | Weather |  | 101 | 155 | 0.025027 | 0.00016147 | No
10/07/2018 | 16:23:00 | YK30 | Rural Long | Unknown | Unknown | 26 | 6 | 0.0011385 | 0.00018976 | No
10/07/2018 | 17:28:22 | SG10 | Rural Short | Asset failure | LV | 1 | 313 | 0.0023319 | 7.45e-06 | No
10/07/2018 | 19:12:00 | CN25 | Rural Long | Unknown | Unknown | 3 | 1492 | 0.032667 | 2.19e-05 | No
10/07/2018 | 19:47:00 | PP05 | Rural Long | Unknown | Unknown | 79 | 225 | 0.12973 | 0.00057657 | No
10/07/2018 | 19:57:35 | SG13 | Rural Short | Unknown | Unknown | 8.3333 | 107 | 0.006643 | 6.208e-05 | No
10/07/2018 | 20:20:11 | SA744D | Urban | Asset failure | LV | 1 | 120 | 0.00019184 | 1.6e-06 | No
10/07/2018 | 20:24:55 | SM349H | Urban | Asset failure | LV | 1 | 182 | 0.00029096 | 1.6e-06 | No
10/07/2018 | 21:09:33 | SG14 | Rural Short | Asset failure | LV | 1 | 218 | 0.0016241 | 7.45e-06 | No
10/07/2018 | 23:09:00 | CBD412A | CBD | Planned |  | 14 | 2 | 0.0054353 | 0.0027177 | No
10/07/2018 | 23:09:00 | CBD412A | CBD | Planned |  | 0 | 2 | 0.0054353 | 0 | No
10/07/2018 | 23:30:49 | HH107B | Urban | Overloads |  | 1 | 84 | 0.00013429 | 1.6e-06 | No
11/07/2018 | 08:55:00 | KA16 | Rural Long | Planned |  | 9 | 147 | 0.0096557 | 6.569e-05 | No
11/07/2018 | 09:11:00 | KI21 | Rural Long | Planned |  | 1 | 121 | 0.0008831 | 7.3e-06 | No
11/07/2018 | 09:12:00 | LX24 | Rural Short | Planned |  | 2 | 101 | 0.0015049 | 1.49e-05 | No
11/07/2018 | 09:15:00 | NL111A | Urban | Planned |  | 34 | 282 | 0.015328 | 5.435e-05 | No
11/07/2018 | 09:16:00 | VH15 | Rural Short | Planned |  | 70 | 365 | 0.19035 | 0.00052151 | No
11/07/2018 | 09:33:14 | W01 | Rural Long | Asset failure | LV | 2 | 56 | 0.00081741 | 1.46e-05 | No
11/07/2018 | 09:41:00 | SA17 | Urban | Planned |  | 83 | 240 | 0.031846 | 0.00013269 | No
11/07/2018 | 10:10:00 | HH121C | Urban | Planned |  | 92 | 257 | 0.037799 | 0.00014708 | No
11/07/2018 | 10:18:00 | ST41 | Rural Long | Planned |  | 41 | 248 | 0.074209 | 0.00029923 | No
11/07/2018 | 10:23:00 | VH44 | Rural Short | Planned |  | 67 | 275 | 0.13727 | 0.00049916 | No
11/07/2018 | 10:36:04 | ST41 | Rural Long | Planned |  | 1 | 9 | 6.569e-05 | 7.3e-06 | No
11/07/2018 | 10:49:04 | HH121B | Urban | Asset failure | LV | 14 | 149 | 0.0033348 | 2.238e-05 | No
11/07/2018 | 10:52:00 | NU15 | Rural Long | Unknown | Unknown | 73 | 96 | 0.051147 | 0.00053278 | No
11/07/2018 | 11:13:07 | HH121C | Urban | Planned |  | 2 | 292 | 0.00093363 | 3.2e-06 | No
11/07/2018 | 11:48:00 | W26 | Rural Long | Unknown | Unknown | 4 | 21 | 0.00061306 | 2.919e-05 | No
11/07/2018 | 12:13:37 | VH15 | Rural Short | Asset failure | LV | 21 | 159 | 0.024876 | 0.00015645 | No
11/07/2018 | 12:46:00 | CD24 | Rural Long | Asset failure | HV | 8 | 172 | 0.010043 | 5.839e-05 | No
11/07/2018 | 13:38:11 | NU13 | Rural Long | Third Party | Vehicle impact | 2 | 117 | 0.0017078 | 1.46e-05 | No
11/07/2018 | 16:57:56 | AP424B | Urban | Asset failure | LV | 1 | 250 | 0.00039967 | 1.6e-06 | No
11/07/2018 | 18:19:59 | SM179B | Urban | Asset failure | LV | 16 | 80 | 0.0020463 | 2.558e-05 | No
11/07/2018 | 18:21:48 | HH409D | Urban | Other |  | 17 | 125 | 0.0033972 | 2.718e-05 | No
11/07/2018 | 18:31:22 | SM179B | Urban | Asset failure | LV | 1 | 68 | 0.00010871 | 1.6e-06 | No
11/07/2018 | 18:52:35 | MTB52 | Rural Long | Unknown | Unknown | 1 | 153 | 0.0011167 | 7.3e-06 | No
11/07/2018 | 18:58:10 | ME347C | Urban | Asset failure | LV | 19.6666 | 140 | 0.0044017 | 3.144e-05 | No
11/07/2018 | 19:03:30 | HH177B | Urban | Other |  | 1 | 158 | 0.00025259 | 1.6e-06 | No
11/07/2018 | 19:56:11 | AP424E | Urban | Asset failure | LV | 18.3333 | 50 | 0.0014655 | 2.931e-05 | No
11/07/2018 | 20:22:56 | HH386D | Urban | Other |  | 2 | 156 | 0.00049879 | 3.2e-06 | No
11/07/2018 | 21:34:00 | CBD367N | CBD | Animal | Animal impact | 15 | 102.6667 | 0.29894 | 0.0029118 | No
11/07/2018 | 21:34:00 | CBD367N | Urban | Animal | Animal impact | 36 | 107.7222 | 0.0061997 | 5.755e-05 | No
11/07/2018 | 21:45:00 | SM402D | Urban | Planned |  | 162 | 3 | 0.00077696 | 0.00025899 | No
11/07/2018 | 21:46:42 | HH148C | Urban | Overloads |  | 1 | 122 | 0.00019504 | 1.6e-06 | No
11/07/2018 | 22:23:56 | MTB52 | Rural Long | Asset failure | LV | 1 | 88 | 0.00064225 | 7.3e-06 | No
12/07/2018 | 00:26:31 | ST41 | Rural Long | Asset failure | LV | 2 | 528 | 0.007707 | 1.46e-05 | No
12/07/2018 | 04:27:17 | HH145E | Urban | Asset failure | LV | 94 | 145 | 0.02179 | 0.00015028 | No
12/07/2018 | 08:27:00 | SA19 | Urban | Planned |  | 213 | 293 | 0.099772 | 0.00034052 | No
12/07/2018 | 08:46:00 | GU41 | Rural Long | Planned |  | 6 | 351 | 0.01537 | 4.379e-05 | No
12/07/2018 | 08:53:00 | MTB32 | Rural Long | Planned |  | 51 | 382 | 0.14219 | 0.00037222 | No
12/07/2018 | 09:04:00 | HH145A | Urban | Planned |  | 51 | 348 | 0.028373 | 8.153e-05 | No
12/07/2018 | 09:19:00 | SD52300 | Rural Long | Planned |  | 25 | 275 | 0.050176 | 0.00018246 | No
12/07/2018 | 09:22:00 | AP373C | Urban | Planned |  | 115 | 61 | 0.011215 | 0.00018385 | No
12/07/2018 | 09:25:58 | HH432E | Urban | Planned |  | 14 | 297 | 0.0066473 | 2.238e-05 | No
12/07/2018 | 09:26:00 | MTB13 | Rural Short | Planned |  | 53 | 271 | 0.10701 | 0.00039486 | No
12/07/2018 | 09:30:00 | SD35403 | Rural Short | Planned |  | 15 | 272 | 0.030397 | 0.00011175 | No
12/07/2018 | 09:32:19 | GA03 | Rural Long | Planned |  | 5 | 308 | 0.011239 | 3.649e-05 | No
12/07/2018 | 09:34:00 | SSD212 | Rural Short | Planned |  | 5 | 258 | 0.0096107 | 3.725e-05 | No
12/07/2018 | 09:35:00 | HH341G | Urban | Planned |  | 2 | 245 | 0.00078335 | 3.2e-06 | No
12/07/2018 | 09:48:00 | MI06 | Rural Long | Planned |  | 9 | 200 | 0.013137 | 6.569e-05 | No
12/07/2018 | 10:10:00 | MT18 | Rural Long | Unknown | Unknown | 1 | 20 | 0.00014597 | 7.3e-06 | No
12/07/2018 | 10:26:00 | HH409E | Urban | Planned |  | 220 | 191 | 0.067176 | 0.00035171 | No
12/07/2018 | 10:31:20 | SM350F | Urban | Overloads |  | 1 | 152 | 0.000243 | 1.6e-06 | No
12/07/2018 | 11:00:00 | VH44 | Rural Short | Planned |  | 90 | 239 | 0.16025 | 0.00067051 | No
12/07/2018 | 11:30:00 | CD26 | Rural Long | Planned |  | 2 | 179 | 0.0026128 | 1.46e-05 | No
12/07/2018 | 11:34:41 | MG10 | Rural Long | Other |  | 1 | 182 | 0.0013283 | 7.3e-06 | No
12/07/2018 | 11:47:37 | G16 | Rural Long | Planned |  | 1 | 3 | 2.19e-05 | 7.3e-06 | No
12/07/2018 | 12:21:00 | G31 | Rural Long | Planned |  | 1 | 110 | 0.00080282 | 7.3e-06 | No
12/07/2018 | 13:28:00 | SM179C | Urban | Unknown | Unknown | 122.6667 | 58.1467 | 0.011403 | 0.0001961 | No
12/07/2018 | 13:43:18 | HH409C | Urban | Asset failure | LV | 1 | 76 | 0.0001215 | 1.6e-06 | No
12/07/2018 | 14:11:04 | AP372F | Urban | Asset failure | LV | 1 | 203 | 0.00032453 | 1.6e-06 | No
12/07/2018 | 14:31:27 | VH21 | Rural Short | Asset failure | LV | 1 | 69 | 0.00051406 | 7.45e-06 | No
12/07/2018 | 17:28:26 | GA800A | Rural Short | Asset failure | LV | 1 | 183 | 0.0013634 | 7.45e-06 | No
12/07/2018 | 17:35:00 | MT09 | Rural Long | Unknown | Unknown | 1 | 5 | 3.649e-05 | 7.3e-06 | No
12/07/2018 | 18:05:02 | AP125C | Urban | Asset failure | LV | 22 | 116 | 0.0040798 | 3.517e-05 | No
12/07/2018 | 19:33:12 | MG11 | Rural Short | Asset failure | LV | 1 | 80 | 0.00059601 | 7.45e-06 | No
12/07/2018 | 19:57:34 | MT08 | Rural Long | Asset failure | LV | 1 | 235 | 0.0017151 | 7.3e-06 | No
13/07/2018 | 08:40:00 | KI21 | Rural Long | Planned |  | 2 | 29 | 0.0004233 | 1.46e-05 | No
13/07/2018 | 08:45:00 | MTB52 | Rural Long | Planned |  | 68 | 263 | 0.13052 | 0.00049629 | No
13/07/2018 | 08:47:00 | MTB21 | Rural Short | Planned |  | 30 | 117 | 0.02615 | 0.0002235 | No
13/07/2018 | 08:48:00 | SD34201 | Rural Short | Planned |  | 47 | 284 | 0.099445 | 0.00035016 | No
13/07/2018 | 09:23:00 | M23 | Rural Long | Planned |  | 1 | 55 | 0.00040141 | 7.3e-06 | No
13/07/2018 | 09:24:00 | YK14 | Rural Long | Planned |  | 1 | 271 | 0.0019779 | 7.3e-06 | No
13/07/2018 | 09:46:00 | VH44 | Rural Short | Planned |  | 34 | 286 | 0.072445 | 0.00025331 | No
13/07/2018 | 09:48:38 | PL01 | Urban | Asset failure | LV | 1 | 146 | 0.00023341 | 1.6e-06 | No
13/07/2018 | 09:59:00 | AP132E | Urban | Unknown | Unknown | 88 | 105.9545 | 0.014906 | 0.00014068 | No
13/07/2018 | 10:00:00 | VH44 | Rural Short | Planned |  | 3 | 66 | 0.0014751 | 2.235e-05 | No
13/07/2018 | 10:03:00 | MV42 | Rural Short | Planned |  | 218 | 272 | 0.44176 | 0.0016241 | No
13/07/2018 | 10:10:09 | HH522C | Urban | Asset failure | LV | 1 | 60 | 9.592e-05 | 1.6e-06 | No
13/07/2018 | 10:15:00 | CN25 | Rural Long | Unknown | Unknown | 21 | 58 | 0.0088894 | 0.00015327 | No
13/07/2018 | 10:26:15 | NL111B | Urban | Asset failure | LV | 2 | 237 | 0.00075777 | 3.2e-06 | No
13/07/2018 | 10:41:00 | W24 | Rural Long | Planned |  | 27 | 126 | 0.024829 | 0.00019706 | No
13/07/2018 | 10:58:50 | CBD366E | Urban | Planned |  | 92 | 215 | 0.031622 | 0.00014708 | No
13/07/2018 | 10:58:53 | SM216C | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
13/07/2018 | 11:00:00 | MT14 | Rural Short | Planned |  | 1 | 20 | 0.000149 | 7.45e-06 | No
13/07/2018 | 11:44:00 | KI21 | Rural Long | Planned |  | 5 | 16 | 0.00058387 | 3.649e-05 | No
13/07/2018 | 14:26:36 | ME116D | Urban | Asset failure | LV | 1 | 367 | 0.00058671 | 1.6e-06 | No
13/07/2018 | 16:08:00 | NA34 | Rural Long | Unknown | Unknown | 3 | 12 | 0.00026274 | 2.19e-05 | No
13/07/2018 | 16:41:56 | HH428A | Urban | Asset failure | LV | 2 | 158 | 0.00050518 | 3.2e-06 | No
13/07/2018 | 18:45:47 | PP10 | Urban | Overloads |  | 1 | 205 | 0.00032773 | 1.6e-06 | No
13/07/2018 | 20:10:40 | MI15 | Rural Long | Asset failure | LV | 1 | 864 | 0.0063058 | 7.3e-06 | No
13/07/2018 | 20:35:23 | EL10 | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
13/07/2018 | 23:34:14 | AP424A | Urban | Asset failure | LV | 28.3333 | 27 | 0.001223 | 4.53e-05 | No
14/07/2018 | 00:06:00 | SD523 | Rural Long | Unknown | Unknown | 1 | 221 | 0.0016129 | 7.3e-06 | No
14/07/2018 | 08:40:29 | HH428B | Urban | Asset failure | LV | 15.6667 | 413 | 0.010344 | 2.505e-05 | No
14/07/2018 | 08:48:56 | AP424A | Urban | Asset failure | LV | 11.3333 | 245 | 0.004439 | 1.812e-05 | No
14/07/2018 | 09:39:39 | SA35 | Urban | Unknown | Unknown | 6.3333 | 256 | 0.002592 | 1.012e-05 | No
14/07/2018 | 10:13:38 | VH17 | Rural Short | Asset failure | LV | 1 | 97 | 0.00072266 | 7.45e-06 | No
14/07/2018 | 10:50:21 | AP146B | Urban | Overloads |  | 1 | 385 | 0.00061549 | 1.6e-06 | No
14/07/2018 | 11:08:34 | AP227A | Urban | Overloads |  | 1 | 467 | 0.00074658 | 1.6e-06 | No
14/07/2018 | 14:40:37 | NA06 | Rural Long | Overloads |  | 1 | 418 | 0.0030507 | 7.3e-06 | No
14/07/2018 | 15:14:29 | SM349D | Urban | Asset failure | LV | 1 | 92 | 0.00014708 | 1.6e-06 | No
14/07/2018 | 15:27:58 | CV29 | Rural Long | Overloads |  | 1 | 221 | 0.0016129 | 7.3e-06 | No
14/07/2018 | 16:19:08 | SM172F | Urban | Overloads |  | 1 | 230 | 0.0003677 | 1.6e-06 | No
14/07/2018 | 17:34:00 | CV29 | Rural Long | Unknown | Unknown | 1 | 26 | 0.00018976 | 7.3e-06 | No
14/07/2018 | 17:52:16 | HH177B | Urban | Unknown | Unknown | 19.6666 | 102 | 0.0032069 | 3.144e-05 | No
14/07/2018 | 17:58:27 | AP529E | Urban | Overloads |  | 18.6666 | 138 | 0.0041182 | 2.984e-05 | No
14/07/2018 | 18:02:24 | NL234A | Urban | Asset failure | LV | 1 | 129 | 0.00020623 | 1.6e-06 | No
14/07/2018 | 18:20:47 | NL234A | Urban | Asset failure | LV | 1 | 110 | 0.00017585 | 1.6e-06 | No
14/07/2018 | 18:46:15 | NL210C | Urban | Asset failure | LV | 1 | 67 | 0.00010711 | 1.6e-06 | No
14/07/2018 | 19:55:00 | SM172A | Urban | Asset failure | LV | 1 | 211 | 0.00033732 | 1.6e-06 | No
14/07/2018 | 21:25:00 | AP227A | Urban | Unknown | Unknown | 71 | 114 | 0.01294 | 0.00011351 | No
14/07/2018 | 22:16:27 | HH496A | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
15/07/2018 | 08:03:00 | MB23 | Rural Short | Planned |  | 1160 | 457.8224 | 3.9566 | 0.0086422 | No
15/07/2018 | 08:16:23 | BM51 | Urban | Asset failure | LV | 1 | 189 | 0.00030215 | 1.6e-06 | No
15/07/2018 | 09:17:00 | SM411B | Urban | Planned |  | 46 | 298 | 0.021915 | 7.354e-05 | No
15/07/2018 | 09:21:00 | CBD412F | Urban | Planned |  | 50 | 2 | 0.00015987 | 7.993e-05 | No
15/07/2018 | 09:44:00 | AP344D | Urban | Third Party | Vehicle impact | 53 | 525 | 0.044483 | 8.473e-05 | No
15/07/2018 | 09:49:00 | PL24 | Rural Long | Unknown | Unknown | 32 | 158 | 0.0369 | 0.00023355 | No
15/07/2018 | 10:13:00 | SA17 | Urban | Planned |  | 30 | 258 | 0.012374 | 4.796e-05 | No
15/07/2018 | 10:30:38 | G41 | Rural Long | Other |  | 1 | 446 | 0.0032551 | 7.3e-06 | No
15/07/2018 | 11:03:56 | SM216B | Urban | Asset failure | LV | 1 | 261 | 0.00041725 | 1.6e-06 | No
15/07/2018 | 11:07:00 | HH118A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1063 | 71 | 0.12066 | 0.0016994 | No
15/07/2018 | 11:33:24 | SG01 | Rural Short | Asset failure | LV | 1 | 190 | 0.0014155 | 7.45e-06 | No
15/07/2018 | 11:48:30 | MG48 | Rural Long | Asset failure | LV | 1 | 193 | 0.0014086 | 7.3e-06 | No
15/07/2018 | 12:51:00 | EL15 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 291 | 66 | 0.030704 | 0.00046521 | No
15/07/2018 | 14:19:57 | HH403B | Urban | Unknown | Unknown | 1 | 851 | 0.0013605 | 1.6e-06 | No
15/07/2018 | 14:59:01 | HH386B | Urban | Asset failure | LV | 7 | 398 | 0.0044539 | 1.119e-05 | No
15/07/2018 | 15:40:00 | HH496H | Urban | Asset failure | HV | 924 | 148.2262 | 0.21896 | 0.0014772 | No
15/07/2018 | 16:26:31 | BM52 | Urban | Asset failure | LV | 1 | 176 | 0.00028137 | 1.6e-06 | No
15/07/2018 | 16:46:36 | PP03 | Urban | Asset failure | LV | 1 | 190 | 0.00030375 | 1.6e-06 | No
15/07/2018 | 17:53:02 | AP125D | Urban | Asset failure | LV | 54 | 230 | 0.019856 | 8.633e-05 | No
15/07/2018 | 17:57:51 | HH145E | Urban | Asset failure | LV | 1 | 297 | 0.00047481 | 1.6e-06 | No
15/07/2018 | 21:54:00 | AP344A | Urban | Planned |  | 39 | 336 | 0.020949 | 6.235e-05 | No
15/07/2018 | 23:20:00 | GU31 | Rural Long | Planned |  | 367 | 772 | 2.0678 | 0.0026785 | No
16/07/2018 | 05:04:02 | SA19 | Urban | Other |  | 19.3333 | 339 | 0.010478 | 3.091e-05 | No
16/07/2018 | 06:36:00 | PL08 | Urban | Asset failure | HV | 8 | 343 | 0.0043868 | 1.279e-05 | No
16/07/2018 | 06:36:00 | KI52 | Rural Long | Asset failure | HV | 42 | 225 | 0.068969 | 0.00030653 | No
16/07/2018 | 06:36:00 | PL13 | Rural Long | Asset failure | HV | 19 | 383 | 0.05311 | 0.00013867 | No
16/07/2018 | 07:37:33 | BT04 | Rural Long | Asset failure | LV | 1 | 116 | 0.00084661 | 7.3e-06 | No
16/07/2018 | 07:48:18 | SB20 | Rural Long | Overloads |  | 1 | 169 | 0.0012334 | 7.3e-06 | No
16/07/2018 | 08:09:50 | SG08 | Rural Short | Asset failure | LV | 1 | 82 | 0.00061091 | 7.45e-06 | No
16/07/2018 | 08:26:00 | ST43 | Rural Long | Planned |  | 114 | 170 | 0.14144 | 0.00083201 | No
16/07/2018 | 08:57:00 | MV15 | Rural Short | Planned |  | 1 | 176 | 0.0013112 | 7.45e-06 | No
16/07/2018 | 09:05:00 | SM350B | Urban | Planned |  | 99 | 47 | 0.0074386 | 0.00015827 | No
16/07/2018 | 09:14:00 | HH341G | Urban | Planned |  | 91 | 337 | 0.049027 | 0.00014548 | No
16/07/2018 | 09:15:00 | MB65 | Rural Long | Planned |  | 1 | 79 | 0.00057657 | 7.3e-06 | No
16/07/2018 | 09:19:00 | VH22 | Rural Short | Planned |  | 116 | 292 | 0.25235 | 0.00086422 | No
16/07/2018 | 09:22:00 | ST13 | Rural Short | Planned |  | 7 | 288 | 0.015019 | 5.215e-05 | No
16/07/2018 | 09:33:00 | EL13 | Urban | Planned |  | 118 | 331 | 0.062441 | 0.00018864 | No
16/07/2018 | 09:35:00 | NL111C | Urban | Planned |  | 167 | 63 | 0.01682 | 0.00026698 | No
16/07/2018 | 09:50:22 | EL01M | Urban | Asset failure | LV | 2 | 133 | 0.00042525 | 3.2e-06 | No
16/07/2018 | 11:03:28 | KI52 | Rural Long | Asset failure | HV | 1 | 20 | 0.00014597 | 7.3e-06 | No
16/07/2018 | 11:06:00 | PA03 | Urban | Third Party | Vehicle impact | 1 | 364 | 0.00058192 | 1.6e-06 | No
16/07/2018 | 11:21:00 | BT15 | Rural Long | Planned |  | 5 | 139 | 0.0050723 | 3.649e-05 | No
16/07/2018 | 12:16:00 | CD16 | Rural Short | Planned |  | 1 | 21 | 0.00015645 | 7.45e-06 | No
16/07/2018 | 12:34:00 | EL10 | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
16/07/2018 | 12:35:20 | EL01M | Urban | Asset failure | LV | 1 | 238 | 0.00038048 | 1.6e-06 | No
16/07/2018 | 13:16:33 | SA17 | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
16/07/2018 | 13:42:00 | GU17 | Rural Long | Vegetation | Grow-in - NSP responsibility | 18 | 154 | 0.020231 | 0.00013137 | No
16/07/2018 | 13:52:00 | M23 | Rural Long | Planned |  | 1 | 70 | 0.00051088 | 7.3e-06 | No
16/07/2018 | 14:37:00 | SB21 | Rural Long | Unknown | Unknown | 1 | 12 | 8.758e-05 | 7.3e-06 | No
16/07/2018 | 15:13:09 | MG07 | Rural Short | Asset failure | LV | 1 | 137 | 0.0010207 | 7.45e-06 | No
16/07/2018 | 16:14:00 | HH496H | Urban | Planned |  | 60 | 14 | 0.0013429 | 9.592e-05 | No
16/07/2018 | 16:35:48 | ST21 | Rural Short | Asset failure | LV | 1 | 387 | 0.0028832 | 7.45e-06 | No
16/07/2018 | 16:39:07 | SM349C | Urban | Asset failure | LV | 2 | 97 | 0.00031014 | 3.2e-06 | No
16/07/2018 | 17:05:07 | HH403B | Urban | Asset failure | LV | 59 | 132 | 0.01245 | 9.432e-05 | No
16/07/2018 | 22:30:00 | NL760C | Urban | Planned |  | 237 | 309 | 0.11708 | 0.00037889 | No
17/07/2018 | 04:59:21 | SG09 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 247 | 0.014721 | 5.96e-05 | No
17/07/2018 | 05:51:00 | MTB52 | Rural Long | Unknown | Unknown | 975 | 25.9815 | 0.18488 | 0.0071159 | No
17/07/2018 | 06:28:38 | SG03 | Rural Short | Vegetation | Grow-in - NSP responsibility | 44 | 603 | 0.19767 | 0.00032781 | No
17/07/2018 | 06:53:13 | HH341K | Urban | Other |  | 10.3333 | 111 | 0.0018337 | 1.652e-05 | No
17/07/2018 | 07:22:00 | SD442 | Rural Short | Asset failure | Subtransmission | 646 | 196.918 | 0.94773 | 0.0048128 | No
17/07/2018 | 07:22:43 | VH12 | Rural Short | Third Party | Other | 7.6667 | 248 | 0.014165 | 5.712e-05 | No
17/07/2018 | 08:07:00 | YK19 | Rural Long | Unknown | Unknown | 54 | 234.3333 | 0.092353 | 0.00039411 | No
17/07/2018 | 08:15:04 | SG03 | Rural Short | Asset failure | LV | 1 | 165 | 0.0012293 | 7.45e-06 | No
17/07/2018 | 08:21:00 | SG06 | Rural Short | Asset failure | HV | 159 | 207 | 0.24521 | 0.0011846 | No
17/07/2018 | 08:28:00 | MV42 | Rural Short | Planned |  | 292 | 55.7534 | 0.12129 | 0.0021754 | No
17/07/2018 | 08:33:00 | ST41 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 371 | 93 | 0.25181 | 0.0027077 | No
17/07/2018 | 08:39:00 | HH341C | Urban | Vegetation | Grow-in - NSP responsibility | 2455 | 27 | 0.10597 | 0.0039248 | No
17/07/2018 | 08:48:19 | VH21 | Rural Short | Other |  | 1 | 499 | 0.0037176 | 7.45e-06 | No
17/07/2018 | 08:49:00 | KI11 | Rural Long | Asset failure | HV | 323 | 342.709 | 0.80789 | 0.0023574 | No
17/07/2018 | 08:56:00 | AP351D | Urban | Planned |  | 10 | 306 | 0.0048919 | 1.599e-05 | No
17/07/2018 | 09:00:00 | SSD507 | Rural Short | 5 - STPIS Exclusion (3.3)(a) |  | 843 | 9 | 0.056524 | 0.0062805 | No
17/07/2018 | 09:00:00 | SSD507 | Rural Long | 5 - STPIS Exclusion (3.3)(a) |  | 3565 | 9 | 0.23417 | 0.026019 | No
17/07/2018 | 09:03:00 | SD34201 | Rural Short | Planned |  | 347 | 227 | 0.58684 | 0.0025852 | No
17/07/2018 | 09:05:00 | NU02 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1651 | 121.808 | 1.4677 | 0.01205 | No
17/07/2018 | 09:12:00 | MV53 | Rural Short | Planned |  | 18 | 91 | 0.012203 | 0.0001341 | No
17/07/2018 | 09:15:00 | ME200G | Urban | Planned |  | 156 | 225 | 0.056113 | 0.00024939 | No
17/07/2018 | 09:18:00 | MV31 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 405 | 202.6494 | 0.61146 | 0.0030173 | No
17/07/2018 | 09:25:00 | MV11 | Rural Short | Unknown | Unknown | 258 | 48.7093 | 0.093626 | 0.0019221 | No
17/07/2018 | 09:28:00 | NL115B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1818 | 91.5099 | 0.26596 | 0.0029064 | No
17/07/2018 | 09:34:00 | BU02 | Rural Long | Unknown | Unknown | 102 | 137.2157 | 0.10215 | 0.00074443 | No
17/07/2018 | 09:41:34 | HH409E | Urban | Planned |  | 2 | 84 | 0.00026858 | 3.2e-06 | No
17/07/2018 | 09:43:22 | MB61 | Rural Long | Unknown | Unknown | 1 | 73 | 0.00053278 | 7.3e-06 | No
17/07/2018 | 09:44:45 | SM126B | Urban | Vegetation | Grow-in - NSP responsibility | 39 | 389 | 0.024254 | 6.235e-05 | No
17/07/2018 | 09:54:16 | AP227B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 60 | 9.592e-05 | 1.6e-06 | No
17/07/2018 | 09:55:00 | HH409E | Urban | Planned |  | 248 | 199 | 0.078898 | 0.00039647 | No
17/07/2018 | 10:12:00 | WK43 | Rural Short | Planned |  | 8 | 126 | 0.0075097 | 5.96e-05 | No
17/07/2018 | 10:20:25 | GU17 | Rural Long | Asset failure | LV | 1 | 181 | 0.001321 | 7.3e-06 | No
17/07/2018 | 10:21:07 | SM137A | Urban | Weather |  | 1 | 194 | 0.00031014 | 1.6e-06 | No
17/07/2018 | 10:28:00 | MG19 | Rural Long | Planned |  | 11 | 122 | 0.0097944 | 8.028e-05 | No
17/07/2018 | 10:36:00 | NU15 | Rural Long | Asset failure | HV | 482 | 97.2365 | 0.34206 | 0.0035178 | No
17/07/2018 | 10:36:00 | MTB61 | Rural Short | Asset failure | HV | 1259 | 79.494 | 0.74563 | 0.0093797 | No
17/07/2018 | 10:42:00 | MB44 | Rural Long | Asset failure | HV | 59 | 419.1864 | 0.1805 | 0.0004306 | No
17/07/2018 | 11:02:52 | NL234A | Urban | Asset failure | LV | 1 | 60 | 9.592e-05 | 1.6e-06 | No
17/07/2018 | 11:09:00 | GU41 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 320 | 79 | 0.1845 | 0.0023355 | No
17/07/2018 | 11:12:00 | MG43 | Rural Short | Third Party | Other | 1519 | 68.817 | 0.77879 | 0.011317 | No
17/07/2018 | 11:15:16 | AP351C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 28.6666 | 187 | 0.00857 | 4.583e-05 | No
17/07/2018 | 11:19:00 | NA02 | Rural Long | Asset failure | HV | 290 | 239 | 0.50585 | 0.0021165 | No
17/07/2018 | 11:24:57 | HH177C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 83 | 0.00013269 | 1.6e-06 | No
17/07/2018 | 11:34:39 | HH496A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 167 | 0.00026698 | 1.6e-06 | No
17/07/2018 | 11:37:06 | SM179C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 201 | 0.00032133 | 1.6e-06 | No
17/07/2018 | 11:37:21 | MV53 | Rural Short | Vegetation | Grow-in - NSP responsibility | 7 | 337 | 0.017575 | 5.215e-05 | No
17/07/2018 | 12:04:00 | BT18 | Rural Long | Vegetation | Grow-in - NSP responsibility | 67 | 300.7164 | 0.14705 | 0.00048899 | No
17/07/2018 | 12:11:33 | AP424C | Urban | Third Party | Vehicle impact | 63 | 169 | 0.017021 | 0.00010072 | No
17/07/2018 | 12:22:22 | GA800A | Rural Short | Unknown | Unknown | 2 | 146 | 0.0021754 | 1.49e-05 | No
17/07/2018 | 12:32:00 | AP139B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2092 | 54 | 0.1806 | 0.0033444 | No
17/07/2018 | 12:35:29 | WK41 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 60 | 0.0035761 | 5.96e-05 | No
17/07/2018 | 12:40:04 | NL760C | Urban | Asset failure | LV | 20.3333 | 233 | 0.007574 | 3.251e-05 | No
17/07/2018 | 12:41:55 | WHY12 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 24 | 3.837e-05 | 1.6e-06 | No
17/07/2018 | 12:46:00 | R14 | Rural Long | Asset failure | HV | 52 | 197 | 0.074764 | 0.00037951 | No
17/07/2018 | 12:54:14 | NL451C | Urban | Vegetation | Grow-in - NSP responsibility | 20.6666 | 119 | 0.0039317 | 3.304e-05 | No
17/07/2018 | 13:03:33 | VH15 | Rural Short | Asset failure | LV | 16.6667 | 236 | 0.029304 | 0.00012417 | No
17/07/2018 | 13:19:38 | AP227A | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
17/07/2018 | 13:34:24 | BM53 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 20.6667 | 170 | 0.026175 | 0.00015397 | No
17/07/2018 | 13:41:00 | SG12 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 161 | 82 | 0.098357 | 0.0011995 | No
17/07/2018 | 14:07:00 | BT02 | Rural Long | Asset failure | HV | 91 | 297.4505 | 0.19755 | 0.00066415 | No
17/07/2018 | 14:07:00 | BT02 | Rural Long | Asset failure | HV | 0 | 3 | 0.0019706 | 0 | No
17/07/2018 | 14:17:00 | BT12 | Rural Long | Asset failure | HV | 46 | 304.1957 | 0.10213 | 0.00033572 | No
17/07/2018 | 14:17:00 | BT12 | Rural Long | Asset failure | HV | 0 | 341 | 0.024887 | 0 | No
17/07/2018 | 14:17:07 | ST35 | Rural Long | Asset failure | LV | 1 | 1165 | 0.0085026 | 7.3e-06 | No
17/07/2018 | 14:57:11 | WK44 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.3333 | 2826.0002 | 0.028072 | 9.93e-06 | No
17/07/2018 | 16:49:11 | MTB61 | Rural Short | Asset failure | LV | 1 | 221 | 0.0016465 | 7.45e-06 | No
17/07/2018 | 17:19:00 | W23 | Rural Long | Unknown | Unknown | 1 | 90 | 0.00065685 | 7.3e-06 | No
17/07/2018 | 17:23:22 | LM64 | Rural Long | Asset failure | LV | 2 | 418 | 0.0061014 | 1.46e-05 | No
17/07/2018 | 17:43:00 | ST35 | Rural Long | Asset failure | HV | 58 | 96.3448 | 0.040783 | 0.0004233 | No
17/07/2018 | 18:03:16 | NL111C | Urban | Asset failure | LV | 1 | 226 | 0.0003613 | 1.6e-06 | No
17/07/2018 | 18:17:01 | AP214C | Urban | Overloads |  | 1 | 229 | 0.0003661 | 1.6e-06 | No
17/07/2018 | 20:21:00 | MT26 | Rural Long | Asset failure | HV | 5 | 195 | 0.0071159 | 3.649e-05 | No
17/07/2018 | 20:30:53 | MG32 | Rural Long | Asset failure | LV | 7 | 9 | 0.00045979 | 5.109e-05 | No
17/07/2018 | 21:20:54 | HH386F | Urban | Asset failure | LV | 1 | 151 | 0.0002414 | 1.6e-06 | No
18/07/2018 | 07:58:28 | SM126E | Urban | Asset failure | LV | 22 | 365 | 0.012837 | 3.517e-05 | No
18/07/2018 | 08:11:17 | HH409F | Urban | Other |  | 3 | 203 | 0.00097359 | 4.8e-06 | No
18/07/2018 | 08:48:00 | SA711C | Urban | Unknown | Unknown | 60 | 54 | 0.0051797 | 9.592e-05 | No
18/07/2018 | 08:52:00 | G29 | Rural Long | Planned |  | 77 | 207 | 0.11633 | 0.00056197 | No
18/07/2018 | 08:54:00 | MV62 | Rural Short | Planned |  | 34 | 260 | 0.065859 | 0.00025331 | No
18/07/2018 | 08:59:00 | LX24 | Rural Short | Planned |  | 1 | 189 | 0.0014081 | 7.45e-06 | No
18/07/2018 | 09:00:00 | HH130A | Urban | Planned |  | 35 | 279 | 0.015611 | 5.595e-05 | No
18/07/2018 | 09:01:00 | MG21 | Rural Long | Planned |  | 64 | 210 | 0.09809 | 0.00046709 | No
18/07/2018 | 09:24:00 | MB82 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 432 | 0.056752 | 0.00013137 | No
18/07/2018 | 09:24:00 | SM411F | Urban | Planned |  | 61 | 234 | 0.022819 | 9.752e-05 | No
18/07/2018 | 09:38:00 | VH44 | Rural Short | Planned |  | 46 | 363 | 0.1244 | 0.00034271 | No
18/07/2018 | 09:42:19 | NL760A | Urban | Asset failure | LV | 1 | 92 | 0.00014708 | 1.6e-06 | No
18/07/2018 | 09:51:00 | CBD103G | Urban | Planned |  | 90 | 284 | 0.040862 | 0.00014388 | No
18/07/2018 | 09:51:00 | SG03 | Rural Short | Planned |  | 38 | 315 | 0.089178 | 0.00028311 | No
18/07/2018 | 10:00:00 | CD02 | Rural Long | Planned |  | 52 | 253 | 0.096017 | 0.00037951 | No
18/07/2018 | 10:13:00 | PL07 | Urban | Planned |  | 25 | 10 | 0.00039967 | 3.997e-05 | No
18/07/2018 | 10:27:00 | MG10 | Rural Long | Planned |  | 9 | 141 | 0.0092616 | 6.569e-05 | No
18/07/2018 | 10:37:00 | MG34 | Rural Long | Asset failure | HV | 1 | 203 | 0.0014816 | 7.3e-06 | No
18/07/2018 | 10:57:20 | NU13 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 127 | 0.00092689 | 7.3e-06 | No
18/07/2018 | 11:30:13 | AP424C | Urban | Third Party | Other | 1 | 140 | 0.00022381 | 1.6e-06 | No
18/07/2018 | 11:46:00 | YK01 | Rural Long | Asset failure | HV | 2 | 98 | 0.0014305 | 1.46e-05 | No
18/07/2018 | 12:07:53 | AP424C | Urban | Third Party | Other | 1 | 86 | 0.00013749 | 1.6e-06 | No
18/07/2018 | 12:57:00 | NA02 | Rural Long | Asset failure | Distribution substation | 36 | 220.3333 | 0.05789 | 0.00026274 | No
18/07/2018 | 13:17:15 | AP372A | Urban | Asset failure | LV | 29.6666 | 247 | 0.011715 | 4.743e-05 | No
18/07/2018 | 13:29:32 | WK72 | Rural Short | Weather |  | 1 | 285 | 0.0021233 | 7.45e-06 | No
18/07/2018 | 14:19:38 | EL03 | Urban | Overloads |  | 1 | 239 | 0.00038208 | 1.6e-06 | No
18/07/2018 | 15:36:48 | HH428B | Urban | Asset failure | LV | 1 | 34 | 5.435e-05 | 1.6e-06 | No
18/07/2018 | 16:33:57 | CM02 | Rural Long | Asset failure | LV | 1 | 258 | 0.001883 | 7.3e-06 | No
18/07/2018 | 16:51:39 | ME347B | Urban | Asset failure | LV | 1 | 303 | 0.0004844 | 1.6e-06 | No
18/07/2018 | 16:58:32 | VH23 | Rural Short | Asset failure | LV | 19.6666 | 90 | 0.013187 | 0.00014652 | No
18/07/2018 | 18:57:14 | AP125C | Urban | Asset failure | LV | 23.6666 | 83 | 0.0031403 | 3.784e-05 | No
18/07/2018 | 20:37:51 | AP132D | Urban | Asset failure | LV | 84 | 77 | 0.01034 | 0.00013429 | No
18/07/2018 | 22:53:06 | HH409D | Urban | Asset failure | LV | 22 | 128 | 0.0045019 | 3.517e-05 | No
18/07/2018 | 23:45:00 | SD44301 | Rural Short | Planned |  | 1601 | 2 | 0.023855 | 0.011928 | No
18/07/2018 | 23:45:00 | SD44301 | Rural Long | Planned |  | 2281 | 2 | 0.033295 | 0.016648 | No
19/07/2018 | 01:38:00 | CBD412F | Urban | Planned |  | 50 | 2 | 0.00015987 | 7.993e-05 | No
19/07/2018 | 08:08:00 | HH177B | Urban | Third Party | Vehicle impact | 445 | 141.5528 | 0.1007 | 0.00071141 | No
19/07/2018 | 08:08:00 | HH177B | Urban | Third Party | Vehicle impact | 0 | 7.3829 | 0.0096784 | 0 | No
19/07/2018 | 08:41:34 | NA33 | Rural Long | Unknown | Unknown | 1 | 1493 | 0.010896 | 7.3e-06 | No
19/07/2018 | 08:42:00 | NU22 | Rural Long | Planned |  | 6 | 130 | 0.0056927 | 4.379e-05 | No
19/07/2018 | 08:45:00 | MG46 | Rural Short | Planned |  | 1 | 408 | 0.0030397 | 7.45e-06 | No
19/07/2018 | 08:51:00 | CV15 | Rural Long | Animal | Animal nesting/burrowing, etc and other | 58 | 290.4828 | 0.12296 | 0.0004233 | No
19/07/2018 | 09:03:00 | MTB11 | Rural Short | Planned |  | 100 | 270 | 0.20115 | 0.00074501 | No
19/07/2018 | 09:16:45 | HH403D | Urban | Asset failure | LV | 52 | 186 | 0.015462 | 8.313e-05 | No
19/07/2018 | 09:20:00 | KA17 | Rural Long | Planned |  | 1 | 11 | 8.028e-05 | 7.3e-06 | No
19/07/2018 | 09:47:59 | NL760C | Urban | Overloads |  | 1 | 107 | 0.00017106 | 1.6e-06 | No
19/07/2018 | 09:58:00 | NL111Q | Urban | Planned |  | 8 | 92 | 0.0011766 | 1.279e-05 | No
19/07/2018 | 09:59:00 | NL210D | Urban | Planned |  | 52 | 252 | 0.020949 | 8.313e-05 | No
19/07/2018 | 10:15:16 | HH177B | Urban | Third Party | Vehicle impact | 249 | 191 | 0.076031 | 0.00039807 | No
19/07/2018 | 10:24:00 | MV41 | Rural Short | Planned |  | 65 | 283.4615 | 0.13727 | 0.00048426 | No
19/07/2018 | 10:25:00 | HH121C | Urban | Planned |  | 162 | 243 | 0.062933 | 0.00025899 | No
19/07/2018 | 10:30:45 | PP06 | Rural Long | Asset failure | LV | 2 | 24 | 0.00035032 | 1.46e-05 | No
19/07/2018 | 10:45:06 | MV34 | Rural Short | Weather |  | 1 | 204 | 0.0015198 | 7.45e-06 | No
19/07/2018 | 12:47:40 | MV13 | Rural Short | Asset failure | LV | 2 | 270 | 0.0040231 | 1.49e-05 | No
19/07/2018 | 13:38:00 | M61 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 198 | 110 | 0.15896 | 0.0014451 | No
19/07/2018 | 13:54:32 | VH16 | Rural Short | Other |  | 1 | 61 | 0.00045446 | 7.45e-06 | No
19/07/2018 | 15:00:00 | VH45 | Rural Short | Unknown | Unknown | 246 | 53.5285 | 0.098104 | 0.0018327 | No
19/07/2018 | 16:50:00 | SD371 | Rural Long | Unknown | Unknown | 4 | 53 | 0.0015473 | 2.919e-05 | No
19/07/2018 | 17:09:00 | MV62 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 41.3333 | 82 | 0.025251 | 0.00030794 | No
19/07/2018 | 17:36:53 | AP146C | Urban | Asset failure | LV | 41.6666 | 83 | 0.0055287 | 6.661e-05 | No
19/07/2018 | 18:04:35 | HH341K | Urban | Vegetation | Grow-in - NSP responsibility | 49.3334 | 114 | 0.0089909 | 7.887e-05 | No
19/07/2018 | 18:51:27 | VH12 | Rural Short | Asset failure | LV | 1 | 483 | 0.0035984 | 7.45e-06 | No
19/07/2018 | 20:13:39 | HH386F | Urban | Unknown | Unknown | 23.6666 | 105 | 0.0039727 | 3.784e-05 | No
19/07/2018 | 21:09:24 | HH145B | Urban | Asset failure | LV | 1 | 173 | 0.00027657 | 1.6e-06 | No
19/07/2018 | 21:35:46 | YK12 | Rural Long | Asset failure | LV | 2 | 185 | 0.0027004 | 1.46e-05 | No
19/07/2018 | 22:10:00 | AP373K | Urban | Third Party | Vehicle impact | 3 | 348 | 0.001669 | 4.8e-06 | No
19/07/2018 | 22:31:00 | TSD04 | Rural Short | Planned |  | 1377 | 355.8562 | 3.6507 | 0.010259 | No
19/07/2018 | 22:31:00 | TSD04 | Rural Long | Planned |  | 864 | 359 | 2.2638 | 0.0063058 | No
19/07/2018 | 22:41:46 | EL01A | Urban | Unknown | Unknown | 1 | 191 | 0.00030535 | 1.6e-06 | No
19/07/2018 | 23:55:51 | AP226D | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
19/07/2018 | 23:57:00 | MI08 | Rural Long | Asset failure | HV | 769 | 154.0208 | 0.86443 | 0.0056124 | No
20/07/2018 | 00:26:32 | EL01A | Urban | Unknown | Unknown | 1 | 88 | 0.00014068 | 1.6e-06 | No
20/07/2018 | 05:44:00 | KA20 | Rural Long | Unknown | Unknown | 64 | 222 | 0.10369 | 0.00046709 | No
20/07/2018 | 06:23:34 | CN12 | Rural Long | Overloads |  | 1 | 225 | 0.0016421 | 7.3e-06 | No
20/07/2018 | 07:36:04 | SM126D | Urban | Asset failure | LV | 1 | 362 | 0.00057872 | 1.6e-06 | No
20/07/2018 | 07:45:00 | MG11 | Rural Short | Animal | Animal impact | 10 | 155 | 0.011548 | 7.45e-05 | No
20/07/2018 | 07:49:35 | HH102C | Urban | Asset failure | LV | 18 | 131 | 0.0037697 | 2.878e-05 | No
20/07/2018 | 08:05:00 | ME231E | Urban | Planned |  | 156 | 308.4744 | 0.076931 | 0.00024939 | No
20/07/2018 | 08:40:23 | G05 | Rural Long | Asset failure | LV | 1 | 226 | 0.0016494 | 7.3e-06 | No
20/07/2018 | 08:56:00 | BM56 | Rural Short | Planned |  | 18 | 155 | 0.020786 | 0.0001341 | No
20/07/2018 | 09:06:12 | AP149C | Urban | Overloads |  | 1 | 91 | 0.00014548 | 1.6e-06 | No
20/07/2018 | 09:12:00 | ME427F | Urban | Planned |  | 108 | 315 | 0.054387 | 0.00017266 | No
20/07/2018 | 09:15:00 | BT11 | Rural Long | Planned |  | 2 | 132 | 0.0019268 | 1.46e-05 | No
20/07/2018 | 09:18:00 | MV14 | Rural Short | Planned |  | 80 | 233 | 0.13887 | 0.00059601 | No
20/07/2018 | 09:23:00 | SD444 | Rural Short | Network business | Switching and protection error | 61 | 9 | 0.0040901 | 0.00045446 | No
20/07/2018 | 09:30:00 | MI17 | Rural Long | Planned |  | 1 | 113 | 0.00082471 | 7.3e-06 | No
20/07/2018 | 09:33:00 | VH34 | Rural Short | Planned |  | 6 | 202 | 0.0090296 | 4.47e-05 | No
20/07/2018 | 09:37:00 | SG07 | Rural Short | Planned |  | 12 | 176 | 0.015735 | 8.94e-05 | No
20/07/2018 | 09:37:05 | NU19 | Rural Long | Asset failure | LV | 7.6667 | 311 | 0.017402 | 5.595e-05 | No
20/07/2018 | 09:39:09 | HH409E | Urban | Planned |  | 42 | 83 | 0.005573 | 6.714e-05 | No
20/07/2018 | 09:40:00 | SM350B | Urban | Planned |  | 82 | 54 | 0.0070789 | 0.00013109 | No
20/07/2018 | 09:43:00 | M23 | Rural Long | Planned |  | 1 | 145 | 0.0010583 | 7.3e-06 | No
20/07/2018 | 09:55:00 | VH22 | Rural Short | Planned |  | 65 | 296.9077 | 0.14378 | 0.00048426 | No
20/07/2018 | 09:57:00 | KA20 | Rural Long | Asset failure | HV | 64 | 309.7188 | 0.14467 | 0.00046709 | No
20/07/2018 | 10:04:00 | HH409E | Urban | Planned |  | 133 | 152 | 0.032319 | 0.00021262 | No
20/07/2018 | 10:12:46 | ST41 | Rural Long | Unknown | Unknown | 1 | 106 | 0.00077362 | 7.3e-06 | No
20/07/2018 | 10:14:00 | SM350F | Urban | Planned |  | 95 | 260 | 0.039487 | 0.00015187 | No
20/07/2018 | 10:23:00 | CM01 | Rural Long | Planned |  | 256 | 1 | 0.0018684 | 0.0018684 | No
20/07/2018 | 10:26:00 | NA01 | Rural Long | Overloads |  | 1 | 203 | 0.0014816 | 7.3e-06 | No
20/07/2018 | 10:28:11 | ME116C | Urban | Third Party | Vehicle impact | 1 | 214 | 0.00034212 | 1.6e-06 | No
20/07/2018 | 11:04:00 | ME231E | Urban | Unknown | Unknown | 37.3334 | 15 | 0.00089526 | 5.968e-05 | No
20/07/2018 | 11:26:13 | CBD412F | Urban | Other |  | 1 | 209 | 0.00033412 | 1.6e-06 | No
20/07/2018 | 12:00:00 | W23 | Rural Long | Unknown | Unknown | 1 | 115 | 0.00083931 | 7.3e-06 | No
20/07/2018 | 12:39:32 | HH429C | Urban | Asset failure | LV | 41 | 76 | 0.0049815 | 6.555e-05 | No
20/07/2018 | 13:10:00 | PL15 | Rural Long | Unknown | Unknown | 11 | 67 | 0.0053789 | 8.028e-05 | No
20/07/2018 | 13:35:49 | EL14 | Urban | Asset failure | LV | 1 | 81 | 0.00012949 | 1.6e-06 | No
20/07/2018 | 13:55:39 | EL20 | Urban | Planned |  | 1 | 87 | 0.00013908 | 1.6e-06 | No
20/07/2018 | 13:56:00 | CN42 | Rural Long | Animal | Animal impact | 27 | 7 | 0.0013794 | 0.00019706 | No
20/07/2018 | 15:28:12 | HH409E | Urban | Asset failure | LV | 7.6667 | 44 | 0.00053929 | 1.226e-05 | No
20/07/2018 | 15:39:38 | BT26 | Rural Long | Unknown | Unknown | 1 | 142 | 0.0010364 | 7.3e-06 | No
20/07/2018 | 16:36:21 | ME427F | Urban | Asset failure | LV | 21.3333 | 204 | 0.0069574 | 3.411e-05 | No
20/07/2018 | 16:37:35 | MTB11 | Rural Short | Asset failure | LV | 1 | 114 | 0.00084932 | 7.45e-06 | No
20/07/2018 | 18:33:35 | SM172F | Urban | Asset failure | LV | 23.3333 | 123 | 0.0045882 | 3.73e-05 | No
20/07/2018 | 18:35:33 | SA13 | Urban | Asset failure | LV | 38 | 118 | 0.0071685 | 6.075e-05 | No
20/07/2018 | 20:06:58 | PP04 | Rural Short | Overloads |  | 1 | 211 | 0.001572 | 7.45e-06 | No
20/07/2018 | 21:06:58 | AP125D | Urban | Asset failure | LV | 89 | 78 | 0.011098 | 0.00014228 | No
20/07/2018 | 23:31:03 | LX53 | Rural Short | Asset failure | LV | 1 | 132 | 0.00098342 | 7.45e-06 | No
21/07/2018 | 02:27:00 | SM126D | Urban | Third Party | Vehicle impact | 56 | 271 | 0.024261 | 8.953e-05 | No
21/07/2018 | 07:01:11 | WK41 | Rural Short | Unknown | Unknown | 1 | 399 | 0.0029726 | 7.45e-06 | No
21/07/2018 | 07:35:55 | NA22 | Rural Long | Asset failure | HV | 2 | 101 | 0.0014743 | 1.46e-05 | No
21/07/2018 | 08:54:44 | MB15 | Rural Short | Asset failure | LV | 1 | 241 | 0.0017955 | 7.45e-06 | No
21/07/2018 | 09:03:08 | SA11 | Urban | Overloads |  | 1 | 209 | 0.00033412 | 1.6e-06 | No
21/07/2018 | 09:42:00 | MG45 | Urban | Animal | Animal impact | 1 | 226 | 0.0003613 | 1.6e-06 | No
21/07/2018 | 09:42:46 | EL14 | Urban | Planned |  | 1 | 234 | 0.00037409 | 1.6e-06 | No
21/07/2018 | 10:31:59 | EL14 | Urban | Planned |  | 1 | 185 | 0.00029575 | 1.6e-06 | No
21/07/2018 | 14:28:34 | HH130B | Urban | Asset failure | LV | 1 | 175 | 0.00027977 | 1.6e-06 | No
21/07/2018 | 15:42:46 | YK07 | Rural Long | Asset failure | LV | 16.3333 | 130 | 0.015497 | 0.00011921 | No
21/07/2018 | 19:22:00 | R16 | Rural Long | Asset failure | HV | 66 | 316.4091 | 0.15241 | 0.00048169 | No
21/07/2018 | 22:17:12 | AP424C | Urban | Asset failure | LV | 19.6666 | 314 | 0.0098723 | 3.144e-05 | No
22/07/2018 | 00:47:00 | MB22 | Rural Short | Planned |  | 34 | 236 | 0.05978 | 0.00025331 | No
22/07/2018 | 00:54:54 | MB11 | Rural Short | Planned |  | 1 | 300 | 0.002235 | 7.45e-06 | No
22/07/2018 | 01:33:00 | CBD412C | CBD | Asset failure | HV | 143 | 150.2587 | 4.171 | 0.027759 | No
22/07/2018 | 02:06:48 | NL234C | Urban | Unknown | Unknown | 29 | 145 | 0.0067224 | 4.636e-05 | No
22/07/2018 | 05:54:00 | CBD367V | CBD | Unknown | Unknown | 2 | 194 | 0.075318 | 0.00038824 | No
22/07/2018 | 06:18:00 | YK05 | Rural Long | Asset failure | HV | 21 | 335.0952 | 0.051358 | 0.00015327 | No
22/07/2018 | 08:59:00 | CM10 | Rural Long | Asset failure | HV | 82 | 274.9512 | 0.16455 | 0.00059846 | No
22/07/2018 | 09:03:00 | CL06 | Rural Long | Planned |  | 5 | 204 | 0.0074443 | 3.649e-05 | No
22/07/2018 | 09:44:00 | NA03 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 107 | 114 | 0.089025 | 0.00078092 | No
22/07/2018 | 09:47:12 | HH341E | Urban | Planned |  | 117 | 420 | 0.078559 | 0.00018704 | No
22/07/2018 | 10:03:00 | HH386G | Urban | Planned |  | 39 | 135 | 0.008417 | 6.235e-05 | No
22/07/2018 | 10:04:11 | NL111P | Urban | Asset failure | LV | 1 | 239 | 0.00038208 | 1.6e-06 | No
22/07/2018 | 10:31:11 | CM05 | Rural Long | Overloads |  | 1 | 414 | 0.0030215 | 7.3e-06 | No
22/07/2018 | 10:44:00 | WHY06 | Urban | Planned |  | 33 | 222 | 0.011712 | 5.276e-05 | No
22/07/2018 | 11:19:46 | HH121A | Urban | Asset failure | LV | 1 | 293 | 0.00046841 | 1.6e-06 | No
22/07/2018 | 11:25:25 | SM411B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 396 | 0.00063308 | 1.6e-06 | No
22/07/2018 | 11:33:00 | HH107A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 831 | 88 | 0.11691 | 0.0013285 | No
22/07/2018 | 12:17:00 | HH341C | Urban | Planned |  | 183 | 163 | 0.047687 | 0.00029256 | No
22/07/2018 | 13:18:56 | AP373A | Urban | Asset failure | LV | 29.6666 | 61 | 0.0028931 | 4.743e-05 | No
22/07/2018 | 13:23:28 | HH145A | Urban | Overloads |  | 1 | 243 | 0.00038848 | 1.6e-06 | No
22/07/2018 | 14:00:00 | CL09 | Rural Long | Unknown | Unknown | 30 | 70 | 0.015327 | 0.00021895 | No
22/07/2018 | 17:21:11 | HH341E | Urban | Asset failure | LV | 3.6667 | 153 | 0.00089686 | 5.86e-06 | No
22/07/2018 | 18:56:54 | SM349F | Urban | Asset failure | LV | 24.6666 | 72 | 0.0028392 | 3.943e-05 | No
22/07/2018 | 19:02:00 | ME231E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1257 | 69 | 0.13866 | 0.0020095 | No
22/07/2018 | 19:06:21 | HH522A | Urban | Asset failure | LV | 1 | 102 | 0.00016306 | 1.6e-06 | No
22/07/2018 | 19:52:00 | SM179C | Urban | Third Party | Other | 1297 | 61 | 0.12648 | 0.0020735 | No
22/07/2018 | 20:52:36 | NL451C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20.6666 | 114 | 0.0037665 | 3.304e-05 | No
22/07/2018 | 22:15:00 | AP344B | Urban | Planned |  | 68 | 163 | 0.01772 | 0.00010871 | No
22/07/2018 | 22:46:45 | AP132A | Urban | Planned |  | 2 | 412 | 0.0013173 | 3.2e-06 | No
22/07/2018 | 23:24:18 | SA42 | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
23/07/2018 | 02:39:00 | GA800A | Rural Short | Vegetation | Grow-in - NSP responsibility | 934 | 123.651 | 0.86042 | 0.0069584 | No
23/07/2018 | 06:11:00 | AP344B | Urban | Asset failure | LV | 1 | 143 | 0.00022861 | 1.6e-06 | No
23/07/2018 | 07:43:23 | AP344A | Urban | Asset failure | LV | 1 | 67 | 0.00010711 | 1.6e-06 | No
23/07/2018 | 08:17:32 | MV32 | Rural Short | Asset failure | LV | 1.3333 | 117 | 0.0011622 | 9.93e-06 | No
23/07/2018 | 08:23:02 | AP132A | Urban | Asset failure | LV | 2 | 27 | 8.633e-05 | 3.2e-06 | No
23/07/2018 | 09:01:00 | BM56 | Rural Short | Planned |  | 22 | 153 | 0.025077 | 0.0001639 | No
23/07/2018 | 09:12:00 | GA48 | Rural Short | Unknown | Unknown | 1 | 19 | 0.00014155 | 7.45e-06 | No
23/07/2018 | 09:21:00 | SG07 | Rural Short | Planned |  | 9 | 186 | 0.012472 | 6.705e-05 | No
23/07/2018 | 09:25:58 | NU20 | Rural Long | Vegetation | Grow-in - NSP responsibility | 14.3333 | 185 | 0.019353 | 0.00010461 | No
23/07/2018 | 09:28:00 | CBD103C | Urban | Planned |  | 59 | 35 | 0.0033013 | 9.432e-05 | No
23/07/2018 | 09:30:54 | EL01N | Urban | Asset failure | LV | 1 | 341 | 0.00054515 | 1.6e-06 | No
23/07/2018 | 09:32:21 | ST11 | Rural Short | Asset failure | LV | 2 | 4 | 5.96e-05 | 1.49e-05 | No
23/07/2018 | 09:42:00 | EL260B | Urban | Third Party | Vehicle impact | 2293 | 70 | 0.2566 | 0.0036658 | No
23/07/2018 | 09:52:00 | WHY04 | Urban | Unknown | Unknown | 1121 | 127.7368 | 0.22892 | 0.0017921 | No
23/07/2018 | 10:01:00 | BT02 | Rural Long | Planned |  | 8 | 288 | 0.016815 | 5.839e-05 | No
23/07/2018 | 10:03:00 | PA04 | Rural Short | Planned |  | 126 | 232 | 0.21778 | 0.00093872 | No
23/07/2018 | 10:04:00 | G04 | Rural Long | Planned |  | 73 | 128.0137 | 0.068203 | 0.00053278 | No
23/07/2018 | 10:05:00 | YK08 | Rural Long | Unknown | Unknown | 2 | 60 | 0.0008758 | 1.46e-05 | No
23/07/2018 | 10:29:00 | NL111A | Urban | Vegetation | Grow-in - NSP responsibility | 939 | 37 | 0.055543 | 0.0015012 | No
23/07/2018 | 10:29:00 | VH34 | Rural Short | Planned |  | 71 | 124 | 0.065591 | 0.00052896 | No
23/07/2018 | 10:37:00 | SG03 | Rural Short | Planned |  | 44 | 130 | 0.042615 | 0.00032781 | No
23/07/2018 | 10:40:00 | MV14 | Rural Short | Planned |  | 11 | 150 | 0.012293 | 8.195e-05 | No
23/07/2018 | 11:00:00 | YK11 | Rural Long | Planned |  | 82 | 199 | 0.11909 | 0.00059846 | No
23/07/2018 | 11:46:44 | SG07 | Rural Short | Planned |  | 1 | 114 | 0.00084932 | 7.45e-06 | No
23/07/2018 | 12:08:54 | GA01 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19.3333 | 520 | 0.016072 | 3.091e-05 | No
23/07/2018 | 12:18:56 | MT09 | Rural Long | Asset failure | LV | 2 | 78 | 0.0011385 | 1.46e-05 | No
23/07/2018 | 12:24:26 | WK65 | Rural Short | Unknown | Unknown | 1 | 268 | 0.0019966 | 7.45e-06 | No
23/07/2018 | 12:50:24 | AP529D | Urban | Asset failure | LV | 31 | 122 | 0.0060462 | 4.956e-05 | No
23/07/2018 | 12:51:35 | KA30 | Rural Short | Asset failure | HV | 2 | 29 | 0.00043211 | 1.49e-05 | No
23/07/2018 | 13:12:41 | KA06 | Rural Long | Asset failure | LV | 1 | 105 | 0.00076632 | 7.3e-06 | No
23/07/2018 | 13:13:37 | SA17 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 9.3333 | 50 | 0.00074605 | 1.492e-05 | No
23/07/2018 | 13:14:00 | HH177E | Urban | Asset failure | HV | 610 | 91 | 0.088742 | 0.00097519 | No
23/07/2018 | 13:17:27 | MG46 | Rural Short | Asset failure | LV | 1 | 46 | 0.00034271 | 7.45e-06 | No
23/07/2018 | 13:24:00 | NL21 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 609 | 39 | 0.03797 | 0.00097359 | No
23/07/2018 | 13:46:00 | BM41 | Urban | Unknown | Unknown | 67 | 8 | 0.00085689 | 0.00010711 | No
23/07/2018 | 13:49:10 | MG17 | Rural Long | Other |  | 1 | 87 | 0.00063496 | 7.3e-06 | No
23/07/2018 | 13:56:59 | NL760C | Urban | Asset failure | LV | 103 | 201 | 0.033097 | 0.00016466 | No
23/07/2018 | 14:06:23 | HH341D | Urban | Asset failure | LV | 1 | 236 | 0.00037729 | 1.6e-06 | No
23/07/2018 | 14:11:46 | VH21 | Rural Short | Asset failure | LV | 1 | 79 | 0.00058856 | 7.45e-06 | No
23/07/2018 | 14:12:15 | EL09 | Urban | Third Party | Other | 2 | 73 | 0.00023341 | 3.2e-06 | No
23/07/2018 | 14:32:48 | EL01N | Urban | Asset failure | LV | 1 | 197 | 0.00031494 | 1.6e-06 | No
23/07/2018 | 14:57:27 | SG02 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 117 | 0.0095883 | 8.195e-05 | No
23/07/2018 | 15:34:06 | NL210A | Urban | Asset failure | LV | 3.3333 | 186 | 0.00099118 | 5.33e-06 | No
23/07/2018 | 15:36:03 | CD01 | Rural Short | Asset failure | LV | 5 | 72 | 0.0026821 | 3.725e-05 | No
23/07/2018 | 15:50:36 | AP146D | Urban | Overloads |  | 1 | 156 | 0.00024939 | 1.6e-06 | No
23/07/2018 | 16:39:07 | HH341D | Urban | Asset failure | LV | 37 | 48 | 0.0028393 | 5.915e-05 | No
23/07/2018 | 18:47:26 | SM374A | Urban | Asset failure | LV | 22.6666 | 143 | 0.0051818 | 3.624e-05 | No
23/07/2018 | 20:41:05 | MV61 | Urban | Asset failure | LV | 1 | 190 | 0.00030375 | 1.6e-06 | No
23/07/2018 | 20:46:49 | SM216E | Urban | Asset failure | LV | 32.6666 | 97 | 0.0050657 | 5.222e-05 | No
23/07/2018 | 22:53:00 | CD15 | Rural Long | Asset failure | HV | 32 | 1065 | 0.24873 | 0.00023355 | No
23/07/2018 | 23:33:00 | VH22 | Rural Short | Asset failure | Distribution substation | 116 | 270.1379 | 0.23346 | 0.00086422 | No
24/07/2018 | 08:07:12 | MG43 | Rural Short | Other |  | 1 | 406 | 0.0030248 | 7.45e-06 | No
24/07/2018 | 08:13:00 | NL234C | Urban | Planned |  | 30 | 445 | 0.021342 | 4.796e-05 | No
24/07/2018 | 08:23:00 | ST11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 275 | 248.28 | 0.50867 | 0.0020488 | No
24/07/2018 | 08:37:00 | YK16 | Rural Long | Planned |  | 68 | 332 | 0.16477 | 0.00049629 | No
24/07/2018 | 08:58:00 | ST42 | Rural Long | Planned |  | 3 | 239 | 0.0052329 | 2.19e-05 | No
24/07/2018 | 09:07:00 | MB28 | Rural Short | Planned |  | 2 | 159 | 0.0023691 | 1.49e-05 | No
24/07/2018 | 09:10:00 | ST44 | Rural Long | Planned |  | 3 | 200 | 0.004379 | 2.19e-05 | No
24/07/2018 | 09:17:00 | SG14 | Rural Short | Planned |  | 118 | 325 | 0.28571 | 0.00087912 | No
24/07/2018 | 09:23:00 | GU41 | Rural Long | Planned |  | 7 | 221 | 0.011291 | 5.109e-05 | No
24/07/2018 | 09:24:00 | NL234A | Urban | Planned |  | 62 | 249 | 0.02468 | 9.912e-05 | No
24/07/2018 | 09:30:26 | NA02 | Rural Long | Asset failure | LV | 4 | 74 | 0.0021603 | 2.919e-05 | No
24/07/2018 | 09:31:00 | G20 | Rural Long | Planned |  | 87 | 393 | 0.24954 | 0.00063496 | No
24/07/2018 | 09:31:00 | HH496B | Urban | Planned |  | 14 | 274 | 0.0061325 | 2.238e-05 | No
24/07/2018 | 09:32:00 | LC02 | Rural Long | Planned |  | 15 | 303 | 0.033171 | 0.00010948 | No
24/07/2018 | 09:39:00 | BM56 | Rural Short | Unknown | Unknown | 45 | 121 | 0.040566 | 0.00033526 | No
24/07/2018 | 09:40:00 | CV19 | Rural Long | Planned |  | 18 | 292 | 0.03836 | 0.00013137 | No
24/07/2018 | 09:42:00 | HH177F | Urban | Planned |  | 4 | 118 | 0.00075457 | 6.39e-06 | No
24/07/2018 | 09:43:00 | NL210D | Urban | Planned |  | 137 | 291 | 0.063734 | 0.00021902 | No
24/07/2018 | 09:54:00 | AP132E | Urban | Planned |  | 1 | 226 | 0.0003613 | 1.6e-06 | No
24/07/2018 | 10:02:45 | MI14 | Rural Long | Asset failure | LV | 36.6667 | 159 | 0.042549 | 0.00026761 | No
24/07/2018 | 10:14:00 | MB44 | Rural Long | Planned |  | 1 | 44 | 0.00032113 | 7.3e-06 | No
24/07/2018 | 10:16:00 | LX63 | Rural Long | Planned |  | 1 | 88 | 0.00064225 | 7.3e-06 | No
24/07/2018 | 10:18:00 | HH386C | Urban | Planned |  | 34 | 245 | 0.013317 | 5.435e-05 | No
24/07/2018 | 10:34:00 | ST44 | Rural Long | Planned |  | 3 | 79 | 0.0017297 | 2.19e-05 | No
24/07/2018 | 10:38:19 | HH341J | Urban | Overloads |  | 18.6666 | 276 | 0.0082364 | 2.984e-05 | No
24/07/2018 | 10:56:35 | NU04 | Rural Short | Unknown | Unknown | 1 | 94 | 0.00070031 | 7.45e-06 | No
24/07/2018 | 11:25:00 | R32 | Rural Long | Planned |  | 3 | 63 | 0.0013794 | 2.19e-05 | No
24/07/2018 | 11:51:00 | MTB41 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 257 | 71 | 0.13594 | 0.0019147 | No
24/07/2018 | 12:35:00 | SG10 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1069 | 39.0262 | 0.31081 | 0.0079642 | No
24/07/2018 | 12:45:00 | NA13 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 164 | 190.4878 | 0.228 | 0.0011969 | No
24/07/2018 | 12:50:15 | MV61 | Urban | Weather |  | 1 | 298 | 0.00047641 | 1.6e-06 | No
24/07/2018 | 13:13:00 | NL115E | Urban | Asset failure | LV | 1 | 105 | 0.00016786 | 1.6e-06 | No
24/07/2018 | 13:57:00 | GU43 | Rural Long | Third Party | Other | 2 | 36 | 0.00052548 | 1.46e-05 | No
24/07/2018 | 14:15:00 | SG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 10.6667 | 83 | 0.0065959 | 7.947e-05 | No
24/07/2018 | 14:23:39 | HH102B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 130 | 0.00020783 | 1.6e-06 | No
24/07/2018 | 15:23:00 | SG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 210 | 119.3524 | 0.18673 | 0.0015645 | No
24/07/2018 | 16:37:47 | NL115E | Urban | Asset failure | LV | 1 | 210 | 0.00033572 | 1.6e-06 | No
24/07/2018 | 17:40:14 | MB11 | Rural Short | Asset failure | LV | 1 | 1518 | 0.011309 | 7.45e-06 | No
24/07/2018 | 17:40:58 | SD38200 | Rural Long | Asset failure | Subtransmission | 2 | 235 | 0.0034302 | 1.46e-05 | No
24/07/2018 | 17:43:02 | SG14 | Rural Short | Asset failure | LV | 16 | 208 | 0.024794 | 0.0001192 | No
24/07/2018 | 18:59:00 | ST24 | Rural Short | Asset failure | HV | 2 | 136 | 0.0020264 | 1.49e-05 | No
24/07/2018 | 21:55:28 | HH130A | Urban | Unknown | Unknown | 30.3333 | 23 | 0.0011153 | 4.849e-05 | No
25/07/2018 | 08:02:00 | YK17 | Rural Long | Planned |  | 65 | 390 | 0.18501 | 0.00047439 | No
25/07/2018 | 08:10:00 | SG04 | Rural Short | Planned |  | 15 | 373 | 0.041684 | 0.00011175 | No
25/07/2018 | 08:24:58 | SA744D | Urban | Asset failure | LV | 1 | 93 | 0.00014868 | 1.6e-06 | No
25/07/2018 | 08:42:00 | BM56 | Rural Short | Planned |  | 2 | 192 | 0.0028609 | 1.49e-05 | No
25/07/2018 | 08:44:00 | SG12 | Rural Short | Planned |  | 541 | 330 | 1.3301 | 0.0040305 | No
25/07/2018 | 08:45:00 | PL07 | Urban | Planned |  | 61 | 9 | 0.00087767 | 9.752e-05 | No
25/07/2018 | 08:48:00 | MV62 | Rural Short | Planned |  | 104 | 306 | 0.23709 | 0.00077482 | No
25/07/2018 | 09:02:00 | SM349F | Urban | Planned |  | 74 | 311 | 0.036792 | 0.0001183 | No
25/07/2018 | 09:14:00 | SD32400 | Rural Long | Planned |  | 16 | 119 | 0.013896 | 0.00011677 | No
25/07/2018 | 09:30:00 | SB15 | Rural Long | Planned |  | 12 | 118 | 0.010334 | 8.758e-05 | No
25/07/2018 | 09:42:00 | BM44 | Rural Short | Planned |  | 7 | 148 | 0.0077183 | 5.215e-05 | No
25/07/2018 | 09:47:00 | HH145A | Urban | Planned |  | 173 | 380 | 0.1051 | 0.00027657 | No
25/07/2018 | 09:52:00 | W31 | Rural Short | Planned |  | 30 | 191 | 0.042689 | 0.0002235 | No
25/07/2018 | 10:17:00 | KI53 | Rural Long | Planned |  | 1 | 99 | 0.00072254 | 7.3e-06 | No
25/07/2018 | 10:21:32 | MI17 | Rural Long | Asset failure | LV | 2 | 131 | 0.0019122 | 1.46e-05 | No
25/07/2018 | 10:50:00 | NU04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 459 | 64.3181 | 0.21994 | 0.0034196 | No
25/07/2018 | 11:07:00 | HH341G | Urban | Planned |  | 294 | 190 | 0.089302 | 0.00047001 | No
25/07/2018 | 11:17:00 | AP355A | Urban | Planned |  | 251 | 204 | 0.081859 | 0.00040127 | No
25/07/2018 | 11:18:00 | CD23 | Rural Long | Planned |  | 3 | 137 | 0.0029996 | 2.19e-05 | No
25/07/2018 | 11:22:03 | WK31 | Rural Short | Asset failure | LV | 2 | 194 | 0.0028907 | 1.49e-05 | No
25/07/2018 | 11:25:34 | MG17 | Rural Long | Other |  | 1 | 340 | 0.0024814 | 7.3e-06 | No
25/07/2018 | 12:09:44 | SM216C | Urban | Asset failure | LV | 1 | 226 | 0.0003613 | 1.6e-06 | No
25/07/2018 | 12:19:00 | VH33 | Rural Short | Unknown | Unknown | 17 | 168 | 0.021278 | 0.00012665 | No
25/07/2018 | 12:41:00 | VH45 | Rural Short | Unknown | Unknown | 6 | 53 | 0.0023691 | 4.47e-05 | No
25/07/2018 | 13:25:00 | NA09 | Rural Long | Animal | Animal impact | 270 | 69.7407 | 0.13743 | 0.0019706 | No
25/07/2018 | 13:29:05 | AP355F | Urban | Overloads |  | 1 | 332 | 0.00053076 | 1.6e-06 | No
25/07/2018 | 13:42:00 | CD17 | Rural Long | Third Party | Vehicle impact | 13 | 132.2308 | 0.012546 | 9.488e-05 | No
25/07/2018 | 15:42:15 | AP132D | Urban | Overloads |  | 29 | 55 | 0.0025499 | 4.636e-05 | No
25/07/2018 | 15:50:00 | CL10 | Rural Long | Unknown | Unknown | 2 | 75 | 0.0010948 | 1.46e-05 | No
25/07/2018 | 16:15:00 | ST16 | Rural Short | Unknown | Unknown | 4 | 40 | 0.001192 | 2.98e-05 | No
25/07/2018 | 16:43:00 | MV34 | Rural Short | Asset failure | Distribution substation | 1067 | 98.9925 | 0.78692 | 0.0079493 | No
25/07/2018 | 16:43:00 | MV34 | Rural Short | Asset failure | Distribution substation | 0 | 3 | 0.00049171 | 0 | No
25/07/2018 | 18:18:02 | HH341B | Urban | Asset failure | LV | 1 | 177 | 0.00028297 | 1.6e-06 | No
25/07/2018 | 19:12:19 | ME131B | Urban | Asset failure | LV | 30.3333 | 126 | 0.0061101 | 4.849e-05 | No
25/07/2018 | 19:15:00 | MG19 | Rural Long | Asset failure | Distribution substation | 212 | 159.1274 | 0.24621 | 0.0015473 | No
25/07/2018 | 22:20:00 | SM402E | Urban | Planned |  | 31 | 355 | 0.017593 | 4.956e-05 | No
26/07/2018 | 07:43:00 | NA04 | Rural Long | Unknown | Unknown | 44 | 165 | 0.052986 | 0.00032113 | No
26/07/2018 | 07:59:00 | AP227B | Urban | Asset failure | LV | 8 | 165 | 0.0021103 | 1.279e-05 | No
26/07/2018 | 08:03:24 | SG01 | Rural Short | Asset failure | LV | 1 | 122 | 0.00090892 | 7.45e-06 | No
26/07/2018 | 08:35:00 | YK16 | Rural Long | Planned |  | 14 | 167 | 0.017064 | 0.00010218 | No
26/07/2018 | 08:35:00 | ST41 | Rural Long | Planned |  | 1 | 397 | 0.0028974 | 7.3e-06 | No
26/07/2018 | 08:40:00 | WHY02 | Urban | Planned |  | 78 | 345 | 0.04302 | 0.0001247 | No
26/07/2018 | 08:54:00 | NU02 | Rural Long | Unknown | Unknown | 1 | 134 | 0.00097798 | 7.3e-06 | No
26/07/2018 | 08:55:00 | BM56 | Rural Short | Planned |  | 68 | 323 | 0.16364 | 0.00050661 | No
26/07/2018 | 08:56:00 | KA04 | Rural Long | Planned |  | 1 | 169 | 0.0012334 | 7.3e-06 | No
26/07/2018 | 09:22:00 | MB65 | Rural Long | Planned |  | 33 | 184 | 0.044316 | 0.00024085 | No
26/07/2018 | 09:32:00 | MTB52 | Rural Long | Planned |  | 53 | 307 | 0.11875 | 0.00038681 | No
26/07/2018 | 09:33:00 | HH432F | Urban | Planned |  | 44 | 340 | 0.023916 | 7.034e-05 | No
26/07/2018 | 09:42:00 | EL09 | Urban | Planned |  | 118 | 277 | 0.052254 | 0.00018864 | No
26/07/2018 | 09:51:00 | SG06 | Rural Short | Planned |  | 26 | 267 | 0.051719 | 0.0001937 | No
26/07/2018 | 10:05:00 | KI53 | Rural Long | Planned |  | 2 | 105 | 0.0015326 | 1.46e-05 | No
26/07/2018 | 10:10:00 | MI15 | Rural Long | Unknown | Unknown | 1 | 121 | 0.0008831 | 7.3e-06 | No
26/07/2018 | 10:12:00 | HH148D | Urban | Planned |  | 41 | 216 | 0.014158 | 6.555e-05 | No
26/07/2018 | 10:17:00 | MV62 | Rural Short | Planned |  | 59 | 160 | 0.070329 | 0.00043956 | No
26/07/2018 | 10:22:05 | CN33 | Rural Long | Asset failure | LV | 3 | 408 | 0.0089332 | 2.19e-05 | No
26/07/2018 | 10:32:00 | G23 | Rural Long | Planned |  | 110 | 224 | 0.17983 | 0.00080282 | No
26/07/2018 | 10:33:00 | G20 | Rural Long | Planned |  | 3 | 71 | 0.0015546 | 2.19e-05 | No
26/07/2018 | 10:38:00 | MT05 | Rural Long | Unknown | Unknown | 2 | 189 | 0.0027588 | 1.46e-05 | No
26/07/2018 | 10:50:02 | CD22 | Rural Long | Other |  | 1 | 172 | 0.0012553 | 7.3e-06 | No
26/07/2018 | 11:14:32 | NL760A | Urban | Asset failure | LV | 1 | 139 | 0.00022222 | 1.6e-06 | No
26/07/2018 | 11:48:40 | SG11 | Rural Short | Vegetation | Grow-in - NSP responsibility | 25.3333 | 208 | 0.039257 | 0.00018874 | No
26/07/2018 | 14:11:19 | SA17 | Urban | Overloads |  | 2 | 169 | 0.00054035 | 3.2e-06 | No
26/07/2018 | 16:04:40 | HH148C | Urban | Third Party | Vehicle impact | 1 | 106 | 0.00016946 | 1.6e-06 | No
26/07/2018 | 16:36:00 | SD482 | Rural Long | Asset failure | Subtransmission | 2259 | 290.0589 | 4.7822 | 0.016487 | No
26/07/2018 | 17:13:44 | SD35403 | Rural Short | Asset failure | Subtransmission | 2 | 108 | 0.0016092 | 1.49e-05 | No
26/07/2018 | 18:31:06 | EL25 | Urban | Asset failure | LV | 15.3333 | 65 | 0.0015933 | 2.451e-05 | No
26/07/2018 | 19:17:11 | KA04 | Rural Long | Asset failure | LV | 1 | 13 | 9.488e-05 | 7.3e-06 | No
26/07/2018 | 20:40:57 | AP125D | Urban | Asset failure | LV | 43 | 84 | 0.0057744 | 6.874e-05 | No
26/07/2018 | 22:24:09 | NL111A | Urban | Asset failure | LV | 4 | 98 | 0.00062668 | 6.39e-06 | No
27/07/2018 | 00:22:48 | MTB21 | Rural Short | Asset failure | LV | 9.3333 | 558 | 0.0388 | 6.953e-05 | No
27/07/2018 | 01:08:00 | AP344B | Urban | Planned |  | 68 | 57 | 0.0061965 | 0.00010871 | No
27/07/2018 | 04:35:53 | HH107B | Urban | Overloads |  | 1 | 243 | 0.00038848 | 1.6e-06 | No
27/07/2018 | 06:25:23 | HH177B | Urban | Overloads |  | 1 | 242 | 0.00038688 | 1.6e-06 | No
27/07/2018 | 07:26:32 | NA57 | Rural Long | Overloads |  | 3 | 378 | 0.0082763 | 2.19e-05 | No
27/07/2018 | 09:14:00 | CM03 | Rural Long | Planned |  | 278 | 306.8273 | 0.62253 | 0.0020289 | No
27/07/2018 | 09:26:00 | VH32 | Rural Short | Planned |  | 98 | 221 | 0.16136 | 0.00073011 | No
27/07/2018 | 09:27:00 | GA43 | Rural Short | Planned |  | 700 | 8 | 0.041721 | 0.0052151 | No
27/07/2018 | 09:29:00 | M01 | Rural Long | Planned |  | 13 | 175 | 0.016604 | 9.488e-05 | No
27/07/2018 | 09:32:00 | KI53 | Rural Long | Planned |  | 2 | 163 | 0.0023793 | 1.46e-05 | No
27/07/2018 | 09:40:00 | VH43 | Rural Short | Planned |  | 37 | 138.7027 | 0.038234 | 0.00027566 | No
27/07/2018 | 09:40:21 | HH386C | Urban | Planned |  | 2 | 463 | 0.0014804 | 3.2e-06 | No
27/07/2018 | 09:45:00 | ME427E | Urban | Planned |  | 97 | 254 | 0.039388 | 0.00015507 | No
27/07/2018 | 09:46:00 | HH121C | Urban | Planned |  | 157 | 207 | 0.051955 | 0.00025099 | No
27/07/2018 | 09:55:14 | HH386B | Urban | Planned |  | 4 | 520 | 0.0033252 | 6.39e-06 | No
27/07/2018 | 10:10:00 | VH23 | Rural Short | Planned |  | 144 | 286 | 0.30683 | 0.0010728 | No
27/07/2018 | 10:20:00 | BM56 | Rural Short | Planned |  | 7 | 136 | 0.0070925 | 5.215e-05 | No
27/07/2018 | 10:35:00 | SB17 | Rural Long | Planned |  | 83 | 120 | 0.072691 | 0.00060576 | No
27/07/2018 | 10:40:00 | HH386B | Urban | Planned |  | 160 | 175 | 0.044763 | 0.00025579 | No
27/07/2018 | 10:55:00 | SM411A | Urban | Planned |  | 2712 | 1 | 0.0043356 | 0.0043356 | No
27/07/2018 | 11:06:00 | HH102D | Urban | Planned |  | 103 | 102 | 0.016796 | 0.00016466 | No
27/07/2018 | 16:17:31 | AP125D | Urban | Asset failure | LV | 89 | 95 | 0.013517 | 0.00014228 | No
27/07/2018 | 17:35:32 | HH409A | Urban | Asset failure | LV | 1 | 454 | 0.0007258 | 1.6e-06 | No
28/07/2018 | 06:37:00 | ST13 | Rural Short | Animal | Animal impact | 260 | 84.3231 | 0.16334 | 0.001937 | No
28/07/2018 | 07:23:34 | EL14 | Urban | Asset failure | LV | 1 | 127 | 0.00020303 | 1.6e-06 | No
28/07/2018 | 08:51:13 | ST12 | Rural Short | Asset failure | LV | 1 | 101 | 0.00075247 | 7.45e-06 | No
28/07/2018 | 08:57:00 | HH177C | Urban | Animal | Animal impact | 2347 | 59 | 0.22137 | 0.0037521 | No
28/07/2018 | 09:57:00 | CV33 | Rural Long | Planned |  | 40 | 141.975 | 0.041447 | 0.00029193 | No
28/07/2018 | 10:29:50 | HH432B | Urban | Asset failure | LV | 23.6666 | 56 | 0.0021188 | 3.784e-05 | No
28/07/2018 | 10:50:05 | GU12 | Rural Long | Overloads |  | 3 | 159 | 0.0034813 | 2.189e-05 | No
28/07/2018 | 11:18:00 | NA52 | Rural Long | Unknown | Unknown | 441 | 88 | 0.28323 | 0.0032186 | No
28/07/2018 | 12:29:55 | HH409F | Urban | Asset failure | LV | 1 | 62 | 9.912e-05 | 1.6e-06 | No
28/07/2018 | 13:22:24 | NL115D | Urban | Asset failure | LV | 1 | 200 | 0.00031974 | 1.6e-06 | No
28/07/2018 | 13:32:48 | ST11 | Rural Short | Unknown | Unknown | 1 | 167 | 0.0012442 | 7.45e-06 | No
28/07/2018 | 15:50:31 | HH496G | Urban | Unknown | Unknown | 1 | 122 | 0.00019504 | 1.6e-06 | No
28/07/2018 | 17:05:09 | ME131B | Urban | Overloads |  | 1 | 163 | 0.00026058 | 1.6e-06 | No
28/07/2018 | 18:10:00 | GA52 | Rural Long | Unknown | Unknown | 1 | 80 | 0.00058387 | 7.3e-06 | No
28/07/2018 | 18:32:20 | SM216B | Urban | Asset failure | LV | 15.3333 | 143 | 0.0035054 | 2.451e-05 | No
28/07/2018 | 19:34:36 | NL234A | Urban | Asset failure | LV | 1 | 217 | 0.00034691 | 1.6e-06 | No
28/07/2018 | 21:35:21 | HH145A | Urban | Asset failure | LV | 1 | 290 | 0.00046362 | 1.6e-06 | No
28/07/2018 | 21:44:00 | NL234A | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
28/07/2018 | 21:52:08 | SM216C | Urban | Asset failure | LV | 22.3333 | 94 | 0.0033562 | 3.57e-05 | No
29/07/2018 | 01:50:18 | HH341K | Urban | Unknown | Unknown | 8 | 190 | 0.00243 | 1.279e-05 | No
29/07/2018 | 03:41:00 | HH341C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2455 | 128 | 0.50237 | 0.0039248 | No
29/07/2018 | 04:07:00 | NA09 | Rural Long | Vegetation | Grow-in - NSP responsibility | 110 | 258 | 0.20713 | 0.00080282 | No
29/07/2018 | 08:02:00 | KA01 | Rural Short | Planned |  | 17 | 47 | 0.0059527 | 0.00012665 | No
29/07/2018 | 08:11:00 | SD406 | Rural Long | Planned |  | 2014 | 368.501 | 5.4165 | 0.014699 | No
29/07/2018 | 08:39:00 | HH177A | Urban | Planned |  | 40 | 444 | 0.028392 | 6.395e-05 | No
29/07/2018 | 08:53:00 | SSD475 | Rural Short | Planned |  | 61 | 5 | 0.0022723 | 0.00045446 | No
29/07/2018 | 09:00:23 | HH341C | Urban | Planned |  | 1 | 57 | 9.112e-05 | 1.6e-06 | No
29/07/2018 | 09:04:00 | NA09 | Rural Long | Vegetation | Grow-in - NSP responsibility | 270 | 100.4444 | 0.19793 | 0.0019706 | No
29/07/2018 | 09:07:00 | SA17 | Urban | Planned |  | 179 | 271 | 0.07755 | 0.00028616 | No
29/07/2018 | 09:17:52 | GU32 | Rural Long | Asset failure | LV | 2 | 111 | 0.0016202 | 1.46e-05 | No
29/07/2018 | 09:18:00 | CM16 | Rural Long | Planned |  | 16 | 311 | 0.036317 | 0.00011677 | No
29/07/2018 | 11:38:07 | ME200G | Urban | Asset failure | LV | 18 | 134 | 0.003856 | 2.878e-05 | No
29/07/2018 | 12:06:41 | CD04 | Rural Short | Asset failure | LV | 1 | 422 | 0.003144 | 7.45e-06 | No
29/07/2018 | 14:10:54 | HH130F | Urban | Asset failure | LV | 21 | 49 | 0.001645 | 3.357e-05 | No
29/07/2018 | 16:58:19 | HH386G | Urban | Asset failure | LV | 54 | 89 | 0.0076832 | 8.633e-05 | No
29/07/2018 | 18:56:33 | NU07 | Rural Long | Asset failure | LV | 1 | 213 | 0.0015546 | 7.3e-06 | No
29/07/2018 | 19:39:49 | SG07 | Rural Short | Asset failure | LV | 18.3333 | 112 | 0.015298 | 0.00013659 | No
29/07/2018 | 19:57:25 | NA52 | Rural Long | Asset failure | LV | 22.3333 | 162 | 0.026405 | 0.000163 | No
29/07/2018 | 20:11:17 | EL09 | Urban | Overloads |  | 1 | 278 | 0.00044443 | 1.6e-06 | No
29/07/2018 | 21:22:25 | NL210E | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
29/07/2018 | 21:47:21 | HH341D | Urban | Overloads |  | 1 | 239 | 0.00038208 | 1.6e-06 | No
30/07/2018 | 03:01:49 | WK11 | Rural Short | Asset failure | LV | 1 | 159 | 0.0011846 | 7.45e-06 | No
30/07/2018 | 07:08:49 | NL234B | Urban | Unknown | Unknown | 1 | 105 | 0.00016786 | 1.6e-06 | No
30/07/2018 | 08:42:00 | CM20 | Rural Long | Planned |  | 277 | 327.0036 | 0.66108 | 0.0020216 | No
30/07/2018 | 08:50:00 | SB15 | Rural Long | Planned |  | 10 | 106 | 0.0077362 | 7.298e-05 | No
30/07/2018 | 08:51:00 | VH10 | Rural Short | Planned |  | 9 | 204 | 0.013678 | 6.705e-05 | No
30/07/2018 | 09:03:00 | ME427D | Urban | Planned |  | 4 | 1350 | 0.0086328 | 6.39e-06 | No
30/07/2018 | 09:12:00 | GA02 | Rural Short | Planned |  | 1 | 328 | 0.0024436 | 7.45e-06 | No
30/07/2018 | 09:14:00 | KI21 | Rural Long | Planned |  | 11 | 43 | 0.0034521 | 8.028e-05 | No
30/07/2018 | 09:17:00 | BT02 | Rural Long | Planned |  | 11 | 146 | 0.011721 | 8.028e-05 | No
30/07/2018 | 09:31:00 | MB81 | Rural Long | Planned |  | 3 | 331 | 0.0072473 | 2.19e-05 | No
30/07/2018 | 09:33:00 | SM350F | Urban | Planned |  | 111 | 149 | 0.02644 | 0.00017745 | No
30/07/2018 | 09:46:00 | MV62 | Rural Short | Planned |  | 37 | 279 | 0.076908 | 0.00027566 | No
30/07/2018 | 10:02:00 | NU10 | Rural Long | Planned |  | 75 | 230 | 0.1259 | 0.00054738 | No
30/07/2018 | 10:29:00 | HH341B | Urban | Planned |  | 23 | 253 | 0.0093027 | 3.677e-05 | No
30/07/2018 | 12:16:35 | HH148C | Urban | Asset failure | LV | 82 | 79 | 0.010356 | 0.00013109 | No
30/07/2018 | 13:00:08 | NL544B | Urban | Asset failure | LV | 21 | 231 | 0.0077552 | 3.357e-05 | No
30/07/2018 | 13:41:00 | GU32 | Rural Long | Asset failure | HV | 2 | 67 | 0.00097798 | 1.46e-05 | No
30/07/2018 | 15:33:00 | WHY07 | Urban | Asset failure | HV | 1 | 96 | 0.00015347 | 1.6e-06 | No
30/07/2018 | 16:20:53 | MTB12 | Rural Short | Third Party | Vehicle impact | 1 | 74 | 0.00055131 | 7.45e-06 | No
30/07/2018 | 16:36:58 | AP424D | Urban | Asset failure | LV | 74 | 74 | 0.0087543 | 0.0001183 | No
30/07/2018 | 20:20:00 | MI31 | Rural Long | Asset failure | HV | 45 | 225 | 0.073896 | 0.00032843 | No
30/07/2018 | 20:31:05 | HH107B | Urban | Asset failure | LV | 1 | 281 | 0.00044923 | 1.6e-06 | No
30/07/2018 | 21:11:31 | HH177B | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
30/07/2018 | 21:39:00 | SM411F | Urban | Unknown | Unknown | 822 | 42 | 0.055193 | 0.0013141 | No
30/07/2018 | 22:20:00 | SM410B | Urban | Planned |  | 48 | 261.3333 | 0.020054 | 7.674e-05 | No
30/07/2018 | 22:30:28 | EL07 | Urban | Asset failure | LV | 1 | 59 | 9.432e-05 | 1.6e-06 | No
30/07/2018 | 22:36:00 | NA34 | Rural Long | Animal | Animal nesting/burrowing, etc and other | 149 | 195 | 0.21205 | 0.0010875 | No
31/07/2018 | 03:00:00 | CBD353B | Urban | Planned |  | 12 | 63 | 0.0012086 | 1.918e-05 | No
31/07/2018 | 07:55:45 | SM216B | Urban | Asset failure | LV | 1 | 176 | 0.00028137 | 1.6e-06 | No
31/07/2018 | 08:36:59 | ME427D | Urban | Planned |  | 4 | 192 | 0.0012278 | 6.39e-06 | No
31/07/2018 | 08:54:00 | VH14 | Rural Short | Asset failure | HV | 2 | 212 | 0.0031589 | 1.49e-05 | No
31/07/2018 | 09:01:00 | LX21 | Rural Short | Planned |  | 1 | 182 | 0.0013559 | 7.45e-06 | No
31/07/2018 | 09:08:00 | VH31 | Rural Short | Planned |  | 29 | 302 | 0.065248 | 0.00021605 | No
31/07/2018 | 09:19:00 | CV33 | Rural Long | Planned |  | 23 | 375 | 0.062948 | 0.00016786 | No
31/07/2018 | 09:24:00 | HH409C | Urban | Planned |  | 34 | 314 | 0.017067 | 5.435e-05 | No
31/07/2018 | 09:30:00 | KI53 | Rural Long | Planned |  | 1 | 180 | 0.0013137 | 7.3e-06 | No
31/07/2018 | 09:30:00 | HH496C | Urban | Planned |  | 28 | 40 | 0.0017905 | 4.476e-05 | No
31/07/2018 | 09:33:00 | SG14 | Rural Short | Planned |  | 18 | 277 | 0.037146 | 0.0001341 | No
31/07/2018 | 09:37:00 | MV11 | Rural Short | Planned |  | 95 | 310 | 0.21941 | 0.00070776 | No
31/07/2018 | 09:45:00 | GA22 | Rural Short | Planned |  | 116 | 299 | 0.2584 | 0.00086422 | No
31/07/2018 | 09:47:00 | SM350F | Urban | Planned |  | 23 | 88 | 0.0032357 | 3.677e-05 | No
31/07/2018 | 09:54:08 | HH341F | Urban | Planned |  | 37 | 61 | 0.0036082 | 5.915e-05 | No
31/07/2018 | 09:58:00 | VH51 | Rural Short | Planned |  | 37 | 150 | 0.041348 | 0.00027566 | No
31/07/2018 | 10:00:00 | KA20 | Rural Long | Planned |  | 1 | 90 | 0.00065685 | 7.3e-06 | No
31/07/2018 | 10:14:15 | MTB62 | Rural Short | Unknown | Unknown | 2 | 223 | 0.0033228 | 1.49e-05 | No
31/07/2018 | 10:17:00 | SG04 | Rural Short | Asset failure | HV | 39.3333 | 165 | 0.048351 | 0.00029304 | No
31/07/2018 | 10:17:00 | CD16 | Rural Short | Planned |  | 1 | 311 | 0.002317 | 7.45e-06 | No
31/07/2018 | 10:24:00 | PP06 | Rural Long | Planned |  | 3 | 138 | 0.0030215 | 2.19e-05 | No
31/07/2018 | 10:26:00 | R32 | Rural Long | Planned |  | 1 | 22 | 0.00016056 | 7.3e-06 | No
31/07/2018 | 11:10:00 | MV13 | Rural Short | Planned |  | 47 | 155 | 0.054274 | 0.00035016 | No
31/07/2018 | 11:35:00 | EL25 | Urban | Third Party | Vehicle impact | 672 | 72 | 0.07735 | 0.0010743 | No
31/07/2018 | 12:31:00 | WHY07 | Urban | Unknown | Unknown | 169 | 107.7811 | 0.02912 | 0.00027018 | No
31/07/2018 | 13:18:59 | GA28 | Rural Long | Asset failure | LV | 7.6667 | 66 | 0.003693 | 5.595e-05 | No
31/07/2018 | 13:59:29 | CM16 | Rural Long | Planned |  | 1 | 13 | 9.488e-05 | 7.3e-06 | No
31/07/2018 | 14:01:53 | MT17 | Rural Short | Asset failure | LV | 16.6667 | 21 | 0.0026076 | 0.00012417 | No
31/07/2018 | 14:02:09 | AP132D | Urban | Overloads |  | 1 | 135 | 0.00021582 | 1.6e-06 | No
31/07/2018 | 14:04:00 | MT17 | Rural Short | Unknown | Unknown | 50 | 10 | 0.0037251 | 0.00037251 | No
31/07/2018 | 17:58:04 | EL01A | Urban | Asset failure | LV | 1 | 1350 | 0.0021582 | 1.6e-06 | No
31/07/2018 | 19:11:15 | AP214D | Urban | Overloads |  | 1 | 163 | 0.00026058 | 1.6e-06 | No
31/07/2018 | 19:23:14 | NL111P | Urban | Asset failure | LV | 16 | 36 | 0.00092084 | 2.558e-05 | No
31/07/2018 | 19:48:33 | HH145E | Urban | Overloads |  | 1 | 83 | 0.00013269 | 1.6e-06 | No
31/07/2018 | 21:47:54 | SA14 | Urban | Asset failure | LV | 1 | 149 | 0.0002382 | 1.6e-06 | No
1/08/2018 | 04:57:00 | SA711C | Urban | Unknown | Unknown | 1439 | 77.3502 | 0.17794 | 0.0023005 | No
1/08/2018 | 06:41:00 | SD363 | Rural Long | Asset failure | Subtransmission | 1449 | 181.8571 | 1.9232 | 0.010575 | No
1/08/2018 | 07:29:00 | VH61 | Rural Short | Planned |  | 36 | 83 | 0.022261 | 0.00026821 | No
1/08/2018 | 08:14:01 | MTB32 | Rural Long | Asset failure | LV | 1 | 69 | 0.00050359 | 7.3e-06 | No
1/08/2018 | 08:41:00 | VH13 | Rural Short | Planned |  | 4 | 292 | 0.0087018 | 2.98e-05 | No
1/08/2018 | 08:46:00 | BT37 | Rural Long | Planned |  | 2 | 118 | 0.0017224 | 1.46e-05 | No
1/08/2018 | 08:46:00 | BM56 | Rural Short | Planned |  | 2 | 203 | 0.0030248 | 1.49e-05 | No
1/08/2018 | 08:53:00 | MV13 | Rural Short | Planned |  | 18 | 235 | 0.031514 | 0.0001341 | No
1/08/2018 | 08:58:00 | BT04 | Rural Long | Unknown | Unknown | 2 | 212 | 0.0030945 | 1.46e-05 | No
1/08/2018 | 08:58:00 | EL20 | Urban | Planned |  | 25 | 311 | 0.01243 | 3.997e-05 | No
1/08/2018 | 08:59:00 | MG33 | Rural Long | Planned |  | 3 | 150 | 0.0032842 | 2.19e-05 | No
1/08/2018 | 09:05:00 | CM03 | Rural Long | Planned |  | 236 | 349.0678 | 0.60124 | 0.0017224 | No
1/08/2018 | 09:18:42 | SM216B | Urban | Asset failure | LV | 1 | 212 | 0.00033892 | 1.6e-06 | No
1/08/2018 | 09:36:00 | KI53 | Rural Long | Planned |  | 2 | 150 | 0.0021895 | 1.46e-05 | No
1/08/2018 | 09:54:00 | HH409A | Urban | Planned |  | 313 | 174 | 0.087067 | 0.00050039 | No
1/08/2018 | 10:00:00 | ME347C | Urban | Planned |  | 105 | 225 | 0.037769 | 0.00016786 | No
1/08/2018 | 10:07:00 | ST34 | Rural Long | Planned |  | 144 | 377 | 0.39621 | 0.001051 | No
1/08/2018 | 10:08:00 | SM410B | Urban | Asset failure | HV | 3187 | 74 | 0.37703 | 0.005095 | No
1/08/2018 | 11:31:00 | AP373C | Urban | Unknown | Unknown | 1 | 69 | 0.00011031 | 1.6e-06 | No
1/08/2018 | 13:11:00 | NA34 | Rural Long | Unknown | Unknown | 2 | 182 | 0.0026566 | 1.46e-05 | No
1/08/2018 | 13:41:44 | MG17 | Rural Long | Asset failure | LV | 4 | 46 | 0.0013429 | 2.919e-05 | No
1/08/2018 | 16:32:48 | KA01 | Rural Short | Asset failure | LV | 71 | 68 | 0.035969 | 0.00052896 | No
1/08/2018 | 17:05:06 | MG43 | Rural Short | Asset failure | LV | 1 | 35 | 0.00026076 | 7.45e-06 | No
1/08/2018 | 17:19:44 | SA32 | Urban | Overloads |  | 1 | 131 | 0.00020943 | 1.6e-06 | No
1/08/2018 | 20:12:00 | CN27 | Rural Long | Asset failure | HV | 3 | 13 | 0.00028464 | 2.19e-05 | No
1/08/2018 | 21:19:52 | NL234A | Urban | Asset failure | LV | 40.3333 | 126 | 0.0081245 | 6.448e-05 | No
1/08/2018 | 23:48:00 | GU32 | Rural Long | Unknown | Unknown | 40 | 178 | 0.051964 | 0.00029193 | No
1/08/2018 | 23:48:00 | GU32 | Rural Long | Unknown | Unknown | 574 | 3 | 0.012568 | 0.0041893 | No
2/08/2018 | 00:03:00 | SM411E | Urban | Planned |  | 60 | 46 | 0.0044123 | 9.592e-05 | No
2/08/2018 | 06:01:11 | HH145B | Urban | Asset failure | LV | 1 | 231 | 0.00036929 | 1.6e-06 | No
2/08/2018 | 07:14:05 | PL14 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 93 | 0.00014868 | 1.6e-06 | No
2/08/2018 | 07:34:00 | VH32 | Rural Short | Asset failure | HV | 2 | 265 | 0.0039486 | 1.49e-05 | No
2/08/2018 | 07:57:00 | NA59 | Rural Long | Planned |  | 3 | 126 | 0.0027588 | 2.19e-05 | No
2/08/2018 | 08:02:00 | CD25 | Rural Long | Planned |  | 10 | 237.5 | 0.017334 | 7.298e-05 | No
2/08/2018 | 08:06:17 | EL01M | Urban | Animal | Animal impact | 1 | 88 | 0.00014068 | 1.6e-06 | No
2/08/2018 | 08:28:00 | PL33 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 761 | 124 | 0.6887 | 0.005554 | No
2/08/2018 | 08:48:00 | VH10 | Rural Short | Planned |  | 7 | 229 | 0.011943 | 5.215e-05 | No
2/08/2018 | 08:52:52 | HH341D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 237 | 0.00037889 | 1.6e-06 | No
2/08/2018 | 08:57:32 | HH145D | Urban | Overloads |  | 1 | 271 | 0.00043324 | 1.6e-06 | No
2/08/2018 | 08:58:00 | AP125A | Urban | Planned |  | 6 | 354 | 0.0033956 | 9.59e-06 | No
2/08/2018 | 09:00:00 | MG03 | Rural Short | Planned |  | 30 | 279 | 0.062358 | 0.0002235 | No
2/08/2018 | 09:03:00 | MT14 | Rural Short | Planned |  | 5 | 116 | 0.0043211 | 3.725e-05 | No
2/08/2018 | 09:13:00 | VH10 | Rural Short | Planned |  | 13 | 99 | 0.0095883 | 9.685e-05 | No
2/08/2018 | 09:21:00 | ST44 | Rural Long | Unknown | Unknown | 4 | 113 | 0.0032988 | 2.919e-05 | No
2/08/2018 | 09:28:00 | MT17 | Rural Short | Planned |  | 117 | 292 | 0.25453 | 0.00087167 | No
2/08/2018 | 09:28:28 | HH429C | Urban | Planned |  | 2 | 59 | 0.00018864 | 3.2e-06 | No
2/08/2018 | 09:32:21 | SB17 | Rural Long | Asset failure | HV | 5 | 293 | 0.010692 | 3.649e-05 | No
2/08/2018 | 09:39:00 | SM350F | Urban | Planned |  | 69 | 60 | 0.0066185 | 0.00011031 | No
2/08/2018 | 09:43:00 | CL06 | Rural Long | Planned |  | 1 | 94 | 0.00068604 | 7.3e-06 | No
2/08/2018 | 10:05:00 | VH21 | Rural Short | Planned |  | 1749 | 380 | 4.9515 | 0.01303 | No
2/08/2018 | 11:06:30 | MT01 | Rural Long | Asset failure | LV | 2 | 297 | 0.0043352 | 1.46e-05 | No
2/08/2018 | 11:10:02 | HH496A | Urban | Asset failure | LV | 14.3333 | 51 | 0.0011686 | 2.291e-05 | No
2/08/2018 | 11:35:19 | MTB54 | Rural Long | Unknown | Unknown | 1 | 318 | 0.0023209 | 7.3e-06 | No
2/08/2018 | 11:57:56 | WHY07 | Urban | Asset failure | LV | 1 | 69 | 0.00011031 | 1.6e-06 | No
2/08/2018 | 11:59:00 | MB63 | Rural Long | Third Party | Other | 244 | 210.6148 | 0.37506 | 0.0017808 | No
2/08/2018 | 12:10:00 | GA800A | Rural Short | Planned |  | 1 | 20 | 0.000149 | 7.45e-06 | No
2/08/2018 | 12:24:06 | AP149F | Urban | Overloads |  | 1 | 137 | 0.00021902 | 1.6e-06 | No
2/08/2018 | 12:25:15 | NL111C | Urban | Asset failure | LV | 44 | 99 | 0.0069638 | 7.034e-05 | No
2/08/2018 | 12:40:00 | SD371 | Rural Long | Third Party | Vehicle impact | 588 | 5.7211 | 0.024552 | 0.0042914 | No
2/08/2018 | 12:40:00 | NL111C | Urban | Asset failure | LV | 51 | 85 | 0.0069303 | 8.153e-05 | No
2/08/2018 | 13:21:00 | SM216A | Urban | Unknown | Unknown | 2 | 208 | 0.00066505 | 3.2e-06 | No
2/08/2018 | 13:24:52 | NU02 | Rural Long | Third Party | Vehicle impact | 3 | 157 | 0.0034375 | 2.189e-05 | No
2/08/2018 | 13:58:59 | HH403D | Urban | Asset failure | LV | 103 | 30 | 0.0049399 | 0.00016466 | No
2/08/2018 | 14:18:00 | CM05 | Rural Long | Unknown | Unknown | 1044 | 95 | 0.72385 | 0.0076195 | No
2/08/2018 | 14:41:00 | KI52 | Rural Long | Unknown | Unknown | 20 | 86 | 0.012553 | 0.00014597 | No
2/08/2018 | 14:51:36 | MTB41 | Rural Short | Unknown | Unknown | 2 | 122 | 0.0018178 | 1.49e-05 | No
2/08/2018 | 14:57:00 | ST36 | Rural Long | Unknown | Unknown | 3.3333 | 334 | 0.0081255 | 2.433e-05 | No
2/08/2018 | 15:00:51 | HH121E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 47.6666 | 207 | 0.015774 | 7.62e-05 | No
2/08/2018 | 15:17:00 | CV23 | Rural Long | Asset failure | HV | 14 | 560 | 0.057219 | 0.00010218 | No
2/08/2018 | 15:22:00 | G23 | Rural Long | Third Party | Other | 2 | 208 | 0.0030361 | 1.46e-05 | No
2/08/2018 | 15:40:00 | SG12 | Rural Short | Asset failure | HV | 1 | 5690 | 0.042391 | 7.45e-06 | No
2/08/2018 | 17:38:00 | CL19 | Rural Long | Unknown | Unknown | 23 | 87 | 0.014604 | 0.00016786 | No
2/08/2018 | 18:14:00 | KI22 | Rural Long | Asset failure | HV | 14 | 271.2857 | 0.027719 | 0.00010218 | No
2/08/2018 | 18:39:27 | HH121E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 47.6666 | 71 | 0.0054104 | 7.62e-05 | No
2/08/2018 | 20:20:02 | SM349C | Urban | Asset failure | LV | 97 | 105 | 0.016283 | 0.00015507 | No
2/08/2018 | 20:36:37 | AP424C | Urban | Overloads |  | 1 | 143 | 0.00022861 | 1.6e-06 | No
2/08/2018 | 22:24:04 | NL210A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 167 | 0.00026698 | 1.6e-06 | No
2/08/2018 | 22:36:08 | HH428A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 312 | 0.00049879 | 1.6e-06 | No
2/08/2018 | 23:24:03 | HH177E | Urban | Asset failure | LV | 61 | 138 | 0.013458 | 9.752e-05 | No
3/08/2018 | 00:14:00 | AP424E | Urban | Asset failure | HV | 1238 | 93.4451 | 0.18494 | 0.0019792 | No
3/08/2018 | 00:15:15 | ME131C | Urban | Overloads |  | 1 | 175 | 0.00027977 | 1.6e-06 | No
3/08/2018 | 00:17:57 | HH177E | Urban | Asset failure | LV | 59 | 85 | 0.0080174 | 9.432e-05 | No
3/08/2018 | 05:16:12 | AP139A | Urban | Overloads |  | 1 | 715 | 0.0011431 | 1.6e-06 | No
3/08/2018 | 05:37:48 | AP365E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 134 | 0.00021422 | 1.6e-06 | No
3/08/2018 | 06:13:21 | KA06 | Rural Long | Overloads |  | 9 | 372 | 0.024435 | 6.568e-05 | No
3/08/2018 | 06:56:46 | AP529C | Urban | Asset failure | LV | 1 | 463 | 0.00074019 | 1.6e-06 | No
3/08/2018 | 07:08:00 | SA36 | Urban | Unknown | Unknown | 616.6669 | 6.0162 | 0.0059311 | 0.00098585 | No
3/08/2018 | 07:40:00 | WK44 | Rural Short | Unknown | Unknown | 6 | 220 | 0.0098342 | 4.47e-05 | No
3/08/2018 | 08:03:08 | MG43 | Rural Short | Asset failure | LV | 1 | 52 | 0.00038741 | 7.45e-06 | No
3/08/2018 | 08:16:44 | PP08 | Rural Long | Asset failure | LV | 1 | 85 | 0.00062036 | 7.3e-06 | No
3/08/2018 | 08:37:28 | MV61 | Urban | Other |  | 1 | 63 | 0.00010072 | 1.6e-06 | No
3/08/2018 | 08:43:32 | WHY09 | Urban | Weather |  | 80 | 29 | 0.0037089 | 0.00012789 | No
3/08/2018 | 08:49:17 | G13 | Rural Long | Asset failure | LV | 2 | 180 | 0.0026274 | 1.46e-05 | No
3/08/2018 | 08:54:00 | VH31 | Rural Short | Planned |  | 808 | 343 | 2.0648 | 0.0060197 | No
3/08/2018 | 09:04:00 | KA03 | Rural Long | Planned |  | 16 | 132 | 0.015414 | 0.00011677 | No
3/08/2018 | 09:06:40 | SA17 | Urban | Asset failure | LV | 16 | 310 | 0.0079294 | 2.558e-05 | No
3/08/2018 | 09:19:25 | AP214C | Urban | Overloads |  | 1 | 530 | 0.0008473 | 1.6e-06 | No
3/08/2018 | 09:32:00 | MV12 | Urban | Planned |  | 5 | 236 | 0.0018864 | 7.99e-06 | No
3/08/2018 | 09:52:00 | HH130A | Urban | Planned |  | 176 | 191 | 0.053741 | 0.00028137 | No
3/08/2018 | 10:06:00 | CV33 | Rural Long | Planned |  | 5 | 280 | 0.010218 | 3.649e-05 | No
3/08/2018 | 10:08:00 | CV33 | Rural Long | Planned |  | 9 | 305 | 0.020034 | 6.569e-05 | No
3/08/2018 | 10:16:24 | HH121A | Urban | Weather |  | 50 | 208 | 0.016626 | 7.993e-05 | No
3/08/2018 | 10:56:00 | MV11 | Rural Short | Planned |  | 284 | 164 | 0.347 | 0.0021158 | No
3/08/2018 | 11:08:00 | NU31 | Rural Long | Planned |  | 91 | 217 | 0.14412 | 0.00066415 | No
3/08/2018 | 11:16:19 | EL13 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 96 | 0.00015347 | 1.6e-06 | No
3/08/2018 | 11:22:00 | NA60 | Rural Long | Planned |  | 2 | 97 | 0.0014159 | 1.46e-05 | No
3/08/2018 | 11:31:00 | BM53 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1235 | 67.5215 | 0.62126 | 0.0092009 | No
3/08/2018 | 11:49:42 | YK23 | Rural Long | Unknown | Unknown | 2 | 107 | 0.0015618 | 1.46e-05 | No
3/08/2018 | 11:57:06 | NL544A | Urban | Asset failure | LV | 1 | 171 | 0.00027337 | 1.6e-06 | No
3/08/2018 | 12:41:00 | MG37 | Rural Long | Unknown | Unknown | 3 | 3 | 6.569e-05 | 2.19e-05 | No
3/08/2018 | 12:44:12 | NL115A | Urban | Other |  | 69 | 140 | 0.015443 | 0.00011031 | No
3/08/2018 | 13:16:00 | ST34 | Rural Long | Unknown | Unknown | 55 | 176 | 0.070648 | 0.00040141 | No
3/08/2018 | 13:20:00 | SA36 | Urban | Unknown | Unknown | 21.3333 | 378 | 0.012892 | 3.411e-05 | No
3/08/2018 | 13:25:09 | MG52 | Rural Short | Overloads |  | 1 | 96 | 0.00071521 | 7.45e-06 | No
3/08/2018 | 13:54:00 | MT23 | Rural Long | Planned |  | 2 | 12 | 0.00017516 | 1.46e-05 | No
3/08/2018 | 14:03:04 | SA18 | Urban | Asset failure | LV | 1 | 422 | 0.00067464 | 1.6e-06 | No
3/08/2018 | 14:08:30 | LM13 | Rural Long | Asset failure | LV | 2 | 175 | 0.0025544 | 1.46e-05 | No
3/08/2018 | 14:09:00 | BM56 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 71 | 76 | 0.040201 | 0.00052896 | No
3/08/2018 | 15:04:00 | W26 | Rural Long | Asset failure | HV | 1 | 319 | 0.0023282 | 7.3e-06 | No
3/08/2018 | 15:22:23 | SM350B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 251 | 0.00040127 | 1.6e-06 | No
3/08/2018 | 16:00:00 | PA13 | Rural Long | Unknown | Unknown | 1 | 5453 | 0.039798 | 7.3e-06 | No
3/08/2018 | 17:08:15 | MB12 | Rural Short | Other |  | 5.3333 | 135 | 0.0053641 | 3.973e-05 | No
3/08/2018 | 17:49:00 | PA13 | Rural Long | Unknown | Unknown | 1 | 81 | 0.00059117 | 7.3e-06 | No
3/08/2018 | 18:15:51 | HH496E | Urban | Unknown | Unknown | 13.6667 | 44 | 0.00096134 | 2.185e-05 | No
3/08/2018 | 19:21:15 | SA19 | Urban | Asset failure | LV | 1 | 220 | 0.00035171 | 1.6e-06 | No
3/08/2018 | 20:27:40 | SM172F | Urban | Overloads |  | 1 | 102 | 0.00016306 | 1.6e-06 | No
3/08/2018 | 20:41:24 | HH496E | Urban | Asset failure | LV | 1 | 174 | 0.00027817 | 1.6e-06 | No
3/08/2018 | 22:48:39 | NL115F | Urban | Asset failure | LV | 1 | 179 | 0.00028616 | 1.6e-06 | No
3/08/2018 | 23:13:17 | AP424B | Urban | Asset failure | LV | 77 | 180 | 0.022158 | 0.0001231 | No
3/08/2018 | 23:19:55 | AP424B | Urban | Asset failure | LV | 101 | 174 | 0.028095 | 0.00016147 | No
4/08/2018 | 00:05:00 | HH496E | Urban | Unknown | Unknown | 801 | 9.2921 | 0.011899 | 0.0012805 | No
4/08/2018 | 07:45:00 | SA520H | Urban | Planned |  | 2 | 4 | 1.279e-05 | 3.2e-06 | No
4/08/2018 | 08:20:29 | AP355H | Urban | Asset failure | LV | 3.3333 | 229 | 0.0012203 | 5.33e-06 | No
4/08/2018 | 09:05:00 | NL760C | Urban | Planned |  | 85 | 285 | 0.038728 | 0.00013589 | No
4/08/2018 | 10:05:00 | CD18 | Rural Long | Unknown | Unknown | 19 | 158 | 0.02191 | 0.00013867 | No
4/08/2018 | 10:23:36 | MV61 | Urban | Asset failure | LV | 14.3333 | 474 | 0.010861 | 2.291e-05 | No
4/08/2018 | 10:29:31 | HH145E | Urban | Overloads |  | 1 | 84 | 0.00013429 | 1.6e-06 | No
4/08/2018 | 11:29:00 | SM350H | Urban | Unknown | Unknown | 1907 | 62.9093 | 0.19179 | 0.0030487 | No
4/08/2018 | 11:56:00 | SM411C | Urban | Unknown | Unknown | 1396 | 115 | 0.25665 | 0.0022317 | No
4/08/2018 | 12:16:54 | NA01 | Rural Long | Overloads |  | 1 | 334 | 0.0024376 | 7.3e-06 | No
4/08/2018 | 12:21:06 | SM179B | Urban | Asset failure | LV | 51 | 264 | 0.021525 | 8.153e-05 | No
4/08/2018 | 12:29:00 | SG12 | Rural Short | Unknown | Unknown | 540 | 15.2056 | 0.061173 | 0.0040231 | No
4/08/2018 | 13:50:17 | MV42 | Rural Short | Asset failure | LV | 24.6666 | 148 | 0.027198 | 0.00018377 | No
4/08/2018 | 14:56:45 | SM411E | Urban | Asset failure | LV | 1 | 157 | 0.00025099 | 1.6e-06 | No
4/08/2018 | 16:30:00 | SG11 | Rural Short | Vegetation | Grow-in - NSP responsibility | 38.6667 | 173 | 0.049837 | 0.00028807 | No
4/08/2018 | 16:40:12 | HH386G | Urban | Weather |  | 41.3333 | 161 | 0.010639 | 6.608e-05 | No
4/08/2018 | 19:24:41 | AP149H | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
4/08/2018 | 20:22:00 | CBD27C | CBD | Planned |  | 22 | 213 | 0.90964 | 0.0042706 | No
4/08/2018 | 21:41:52 | NL115F | Urban | Overloads |  | 1 | 413 | 0.00066025 | 1.6e-06 | No
4/08/2018 | 22:00:22 | HH403C | Urban | Asset failure | LV | 1 | 58 | 9.272e-05 | 1.6e-06 | No
4/08/2018 | 23:12:36 | NL115E | Urban | Asset failure | LV | 60 | 27 | 0.0025898 | 9.592e-05 | No
4/08/2018 | 23:54:45 | NL115E | Urban | Asset failure | LV | 1 | 160 | 0.00025579 | 1.6e-06 | No
5/08/2018 | 00:07:01 | HH177C | Urban | Asset failure | LV | 1 | 198 | 0.00031654 | 1.6e-06 | No
5/08/2018 | 03:47:00 | CM01 | Rural Long | Weather |  | 531 | 287.5913 | 1.1145 | 0.0038754 | No
5/08/2018 | 06:19:00 | MV12 | Urban | Planned |  | 110 | 137 | 0.024092 | 0.00017585 | No
5/08/2018 | 06:48:54 | HH386B | Urban | Asset failure | LV | 1 | 369 | 0.00058991 | 1.6e-06 | No
5/08/2018 | 07:37:25 | MG17 | Rural Long | Asset failure | LV | 1 | 130 | 0.00094878 | 7.3e-06 | No
5/08/2018 | 08:22:00 | KI21 | Rural Long | Planned |  | 190 | 151 | 0.20939 | 0.0013867 | No
5/08/2018 | 08:30:00 | AP355F | Urban | Planned |  | 29 | 243 | 0.011266 | 4.636e-05 | No
5/08/2018 | 08:39:00 | CBD412B | Urban | Planned |  | 2 | 382 | 0.0012214 | 3.2e-06 | No
5/08/2018 | 09:01:37 | HH121G | Urban | Overloads |  | 1 | 182 | 0.00029096 | 1.6e-06 | No
5/08/2018 | 09:13:00 | SA744C | Urban | Planned |  | 27 | 225 | 0.009712 | 4.316e-05 | No
5/08/2018 | 09:27:00 | ME200A | Urban | Planned |  | 135 | 338 | 0.072948 | 0.00021582 | No
5/08/2018 | 09:47:48 | HH177G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20.6666 | 70 | 0.0023128 | 3.304e-05 | No
5/08/2018 | 10:57:00 | EL03 | Urban | Asset failure | HV | 33.3334 | 361 | 0.019237 | 5.329e-05 | No
5/08/2018 | 11:12:14 | NL115E | Urban | Overloads |  | 13.6667 | 298 | 0.0065109 | 2.185e-05 | No
5/08/2018 | 11:59:02 | EL01N | Urban | Asset failure | LV | 1 | 353 | 0.00056433 | 1.6e-06 | No
5/08/2018 | 12:11:12 | SM350D | Urban | Asset failure | LV | 1 | 475 | 0.00075937 | 1.6e-06 | No
5/08/2018 | 12:50:04 | EL09 | Urban | Unknown | Unknown | 1 | 417 | 0.00066665 | 1.6e-06 | No
5/08/2018 | 12:54:58 | HH121A | Urban | Overloads |  | 1 | 142 | 0.00022701 | 1.6e-06 | No
5/08/2018 | 13:17:55 | SA744C | Urban | Unknown | Unknown | 2 | 302 | 0.0009656 | 3.2e-06 | No
5/08/2018 | 13:50:00 | CD01 | Rural Short | Asset failure | HV | 19.3333 | 145 | 0.020885 | 0.00014404 | No
5/08/2018 | 14:08:29 | ME427E | Urban | Vegetation | Grow-in - NSP responsibility | 40.3333 | 122 | 0.0078665 | 6.448e-05 | No
5/08/2018 | 14:18:36 | GA800A | Rural Short | Unknown | Unknown | 2 | 160 | 0.002384 | 1.49e-05 | No
5/08/2018 | 14:26:35 | G40 | Rural Long | Third Party | Other | 14.3333 | 209 | 0.021863 | 0.00010461 | No
5/08/2018 | 15:03:26 | VH12 | Rural Short | Asset failure | LV | 1 | 294 | 0.0021903 | 7.45e-06 | No
5/08/2018 | 15:12:45 | AP424D | Urban | Asset failure | LV | 1 | 130 | 0.00020783 | 1.6e-06 | No
5/08/2018 | 15:17:00 | HH386A | Urban | Animal | Animal impact | 413 | 292 | 0.19279 | 0.00066025 | No
5/08/2018 | 15:37:00 | GU13 | Rural Long | Unknown | Unknown | 10 | 218 | 0.01591 | 7.298e-05 | No
5/08/2018 | 16:55:29 | SM410C | Urban | Asset failure | LV | 11 | 215 | 0.0037809 | 1.759e-05 | No
5/08/2018 | 17:02:45 | ME116B | Urban | Vegetation | Grow-in - NSP responsibility | 41.6666 | 136 | 0.0090592 | 6.661e-05 | No
5/08/2018 | 23:40:45 | NL115A | Urban | Asset failure | LV | 23 | 170 | 0.0062508 | 3.677e-05 | No
6/08/2018 | 00:08:44 | ME200G | Urban | Asset failure | LV | 32.6666 | 100 | 0.0052223 | 5.222e-05 | No
6/08/2018 | 00:28:31 | HH145A | Urban | Overloads |  | 1 | 114 | 0.00018225 | 1.6e-06 | No
6/08/2018 | 05:00:20 | NL115A | Urban | Unknown | Unknown | 23 | 321 | 0.011803 | 3.677e-05 | No
6/08/2018 | 06:22:36 | NU14 | Rural Long | Unknown | Unknown | 4 | 206 | 0.0060138 | 2.919e-05 | No
6/08/2018 | 06:36:54 | HH409D | Urban | Asset failure | LV | 6 | 376 | 0.0036066 | 9.59e-06 | No
6/08/2018 | 07:00:46 | SM350A | Urban | Asset failure | LV | 1 | 246 | 0.00039327 | 1.6e-06 | No
6/08/2018 | 08:06:45 | NL511A | Urban | Asset failure | LV | 22.3333 | 101 | 0.0036061 | 3.57e-05 | No
6/08/2018 | 08:25:29 | EL01L | Urban | Unknown | Unknown | 26 | 87 | 0.0036162 | 4.157e-05 | No
6/08/2018 | 08:39:58 | SA744C | Urban | Asset failure | LV | 5.3333 | 193 | 0.0016456 | 8.53e-06 | No
6/08/2018 | 08:49:35 | ME131B | Urban | Asset failure | LV | 88 | 160 | 0.022509 | 0.00014068 | No
6/08/2018 | 09:21:25 | HH341E | Urban | Overloads |  | 1 | 289 | 0.00046202 | 1.6e-06 | No
6/08/2018 | 09:28:29 | AP125C | Urban | Asset failure | HV | 942 | 55.8928 | 0.084172 | 0.001506 | No
6/08/2018 | 09:31:04 | HH409F | Urban | Asset failure | LV | 19.6666 | 330 | 0.010375 | 3.144e-05 | No
6/08/2018 | 09:44:14 | SM349E | Urban | Asset failure | LV | 82 | 322 | 0.042211 | 0.00013109 | No
6/08/2018 | 10:06:04 | HH130F | Urban | Third Party | Vehicle impact | 73 | 488 | 0.056951 | 0.0001167 | No
6/08/2018 | 10:18:45 | EL01L | Urban | Asset failure | LV | 26 | 301 | 0.012511 | 4.157e-05 | No
6/08/2018 | 10:33:55 | NL115A | Urban | Asset failure | LV | 23 | 232 | 0.0085305 | 3.677e-05 | No
6/08/2018 | 10:37:10 | HH130F | Urban | Third Party | Vehicle impact | 73 | 87 | 0.010153 | 0.0001167 | No
6/08/2018 | 10:40:05 | BT15 | Rural Long | Unknown | Unknown | 5 | 4 | 0.00014597 | 3.649e-05 | No
6/08/2018 | 11:31:00 | HH107C | Urban | Vegetation | Grow-in - NSP responsibility | 2439 | 48 | 0.18716 | 0.0038992 | No
6/08/2018 | 11:48:19 | HH429A | Urban | Unknown | Unknown | 3 | 339 | 0.0016259 | 4.8e-06 | No
6/08/2018 | 11:56:06 | AP344E | Urban | Asset failure | LV | 1 | 380 | 0.0006075 | 1.6e-06 | No
6/08/2018 | 11:59:07 | HH522A | Urban | Asset failure | LV | 8 | 261 | 0.003338 | 1.279e-05 | No
6/08/2018 | 12:18:11 | HH341B | Urban | Third Party | Vehicle impact | 35 | 529 | 0.029599 | 5.595e-05 | No
6/08/2018 | 12:55:33 | NU34 | Rural Long | Asset failure | LV | 68 | 194 | 0.09628 | 0.00049629 | No
6/08/2018 | 13:47:48 | GU43 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 4.3333 | 196 | 0.0061987 | 3.163e-05 | No
6/08/2018 | 14:16:29 | SM349E | Urban | Asset failure | HV | 82 | 2 | 0.00026218 | 0.00013109 | No
6/08/2018 | 14:19:00 | NL111C | Urban | Overloads |  | 1 | 176 | 0.00028137 | 1.6e-06 | No
6/08/2018 | 15:11:44 | HH107B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 207 | 0.00033093 | 1.6e-06 | No
6/08/2018 | 15:16:00 | SM126D | Urban | Unknown | Unknown | 2112 | 8.6122 | 0.029078 | 0.0033764 | No
6/08/2018 | 16:00:47 | NU14 | Rural Long | Planned |  | 4 | 24 | 0.00070064 | 2.919e-05 | No
6/08/2018 | 16:15:11 | ME347G | Urban | Asset failure | LV | 57 | 58 | 0.0052852 | 9.112e-05 | No
6/08/2018 | 17:05:03 | MV62 | Rural Short | Asset failure | Distribution substation | 376 | 247.7367 | 0.69397 | 0.0028013 | No
6/08/2018 | 17:56:30 | NL760B | Urban | Unknown | Unknown | 17.3333 | 497 | 0.013772 | 2.771e-05 | No
6/08/2018 | 17:56:55 | HH121G | Urban | Asset failure | LV | 27.6666 | 96 | 0.0042461 | 4.423e-05 | No
6/08/2018 | 18:07:00 | NL760B | Urban | Asset failure | LV | 1 | 547 | 0.00087448 | 1.6e-06 | No
6/08/2018 | 18:35:33 | NL451C | Urban | Unknown | Unknown | 20 | 275 | 0.0087927 | 3.197e-05 | No
6/08/2018 | 18:44:12 | HH522C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 304 | 0.000486 | 1.6e-06 | No
6/08/2018 | 18:52:02 | HH341D | Urban | Unknown | Unknown | 25.6666 | 207 | 0.0084937 | 4.103e-05 | No
6/08/2018 | 20:16:43 | PP04 | Rural Short | Other |  | 1 | 205 | 0.0015273 | 7.45e-06 | No
6/08/2018 | 21:29:56 | AP424F | Urban | Asset failure | LV | 27 | 140 | 0.006043 | 4.316e-05 | No
6/08/2018 | 21:52:23 | HH403A | Urban | Asset failure | LV | 1 | 195 | 0.00031174 | 1.6e-06 | No
6/08/2018 | 22:27:06 | AP149E | Urban | Asset failure | LV | 17.6666 | 83 | 0.0023442 | 2.824e-05 | No
6/08/2018 | 22:32:58 | AP365E | Urban | Asset failure | LV | 80 | 30 | 0.0038368 | 0.00012789 | No
6/08/2018 | 22:46:42 | HH121A | Urban | Asset failure | LV | 75 | 95 | 0.011391 | 0.0001199 | No
6/08/2018 | 23:26:40 | NL451C | Urban | Unknown | Unknown | 10 | 88 | 0.0014068 | 1.599e-05 | No
6/08/2018 | 23:42:09 | ME347G | Urban | Asset failure | LV | 51 | 613 | 0.049979 | 8.153e-05 | No
7/08/2018 | 00:59:46 | NL451C | Urban | Asset failure | LV | 1 | 527 | 0.0008425 | 1.6e-06 | No
7/08/2018 | 03:15:00 | GA800A | Rural Short | Asset failure | HV | 940 | 133.0362 | 0.93167 | 0.0070031 | No
7/08/2018 | 03:15:44 | GA800A | Rural Short | Asset failure | HV | 940 | 136.9383 | 0.959 | 0.0070031 | No
7/08/2018 | 05:08:57 | HH130D | Urban | Asset failure | LV | 23.3333 | 314 | 0.011713 | 3.73e-05 | No
7/08/2018 | 07:58:48 | WK65 | Rural Short | Asset failure | LV | 2 | 421 | 0.006273 | 1.49e-05 | No
7/08/2018 | 08:29:25 | NA62 | Rural Long | Planned |  | 2 | 110 | 0.0016056 | 1.46e-05 | No
7/08/2018 | 08:43:56 | BM44 | Rural Short | Third Party | Other | 210 | 93 | 0.1455 | 0.0015645 | No
7/08/2018 | 09:01:24 | W06 | Rural Long | Planned |  | 231 | 337 | 0.56815 | 0.0016859 | No
7/08/2018 | 09:48:39 | AP125A | Urban | Planned |  | 322 | 276.5497 | 0.14236 | 0.00051477 | No
7/08/2018 | 09:51:42 | HH121B | Urban | Asset failure | LV | 1.3333 | 394 | 0.00083984 | 2.13e-06 | No
7/08/2018 | 10:11:17 | VH23 | Rural Short | Planned |  | 144 | 368 | 0.3948 | 0.0010728 | No
7/08/2018 | 10:13:58 | MG41 | Urban | Overloads |  | 1 | 102 | 0.00016306 | 1.6e-06 | No
7/08/2018 | 10:26:00 | AP424B | Urban | Unknown | Unknown | 91 | 47 | 0.0068375 | 0.00014548 | No
7/08/2018 | 10:39:38 | NA62 | Rural Long | Planned |  | 4 | 128 | 0.0037368 | 2.919e-05 | No
7/08/2018 | 10:42:03 | G23 | Rural Long | Planned |  | 2 | 75 | 0.0010948 | 1.46e-05 | No
7/08/2018 | 12:18:13 | NA32 | Rural Long | Unknown | Unknown | 7 | 189 | 0.0096557 | 5.109e-05 | No
7/08/2018 | 12:29:25 | NL115A | Urban | Asset failure | LV | 1 | 208 | 0.00033252 | 1.6e-06 | No
7/08/2018 | 12:30:40 | ME131C | Urban | Asset failure | LV | 1 | 244 | 0.00039008 | 1.6e-06 | No
7/08/2018 | 12:34:00 | CV25 | Rural Long | Unknown | Unknown | 1 | 1 | 7.3e-06 | 7.3e-06 | No
7/08/2018 | 13:09:40 | CV25 | Rural Long | Planned |  | 1 | 40 | 0.00029193 | 7.3e-06 | No
7/08/2018 | 14:23:34 | NA09 | Rural Long | Unknown | Unknown | 2 | 87 | 0.0012699 | 1.46e-05 | No
7/08/2018 | 15:20:03 | AP425C | Urban | Asset failure | LV | 1 | 150 | 0.0002398 | 1.6e-06 | No
7/08/2018 | 15:53:09 | AP424B | Urban | Asset failure | LV | 1 | 208 | 0.00033252 | 1.6e-06 | No
7/08/2018 | 16:19:20 | SG08 | Rural Short | Asset failure | LV | 1 | 93 | 0.00069286 | 7.45e-06 | No
7/08/2018 | 16:46:51 | HH428D | Urban | Overloads |  | 1 | 208 | 0.00033252 | 1.6e-06 | No
7/08/2018 | 17:07:23 | HH496F | Urban | Unknown | Unknown | 12.6667 | 62 | 0.0012555 | 2.025e-05 | No
7/08/2018 | 17:18:35 | HH130D | Urban | Overloads |  | 1 | 272 | 0.00043484 | 1.6e-06 | No
7/08/2018 | 18:04:02 | MTB13 | Rural Short | Asset failure | LV | 1 | 67 | 0.00049916 | 7.45e-06 | No
7/08/2018 | 18:25:37 | SM411D | Urban | Overloads |  | 1 | 101 | 0.00016147 | 1.6e-06 | No
7/08/2018 | 18:37:07 | AP227A | Urban | Asset failure | LV | 1 | 228 | 0.0003645 | 1.6e-06 | No
7/08/2018 | 18:47:04 | AP529E | Urban | Asset failure | LV | 21 | 169 | 0.0056737 | 3.357e-05 | No
7/08/2018 | 19:02:50 | SA744D | Urban | Asset failure | LV | 1 | 295 | 0.00047161 | 1.6e-06 | No
7/08/2018 | 20:33:34 | EL01L | Urban | Unknown | Unknown | 32.6666 | 83 | 0.0043345 | 5.222e-05 | No
7/08/2018 | 20:58:04 | MT06 | Rural Long | Asset failure | LV | 20 | 123 | 0.017954 | 0.00014597 | No
8/08/2018 | 00:52:59 | HH403A | Urban | Asset failure | LV | 40 | 42 | 0.0026858 | 6.395e-05 | No
8/08/2018 | 03:38:08 | NA02 | Rural Long | Unknown | Unknown | 290 | 47.8069 | 0.10118 | 0.0021165 | No
8/08/2018 | 05:15:17 | GU32 | Rural Long | Asset failure | HV | 66 | 445 | 0.21435 | 0.00048169 | No
8/08/2018 | 06:28:35 | SA12 | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 149 | 0.0002382 | 1.6e-06 | No
8/08/2018 | 08:59:47 | BM56 | Rural Short | Planned |  | 8 | 127 | 0.0075693 | 5.96e-05 | No
8/08/2018 | 09:33:00 | MV61 | Urban | Unknown | Unknown | 14.3333 | 56 | 0.0012832 | 2.291e-05 | No
8/08/2018 | 09:36:04 | VH71 | Rural Short | Planned |  | 5 | 298 | 0.011101 | 3.725e-05 | No
8/08/2018 | 09:56:32 | MT19 | Rural Long | Planned |  | 2 | 834 | 0.012174 | 1.46e-05 | No
8/08/2018 | 10:04:30 | MV11 | Rural Short | Planned |  | 6 | 40 | 0.001788 | 4.47e-05 | No
8/08/2018 | 10:17:50 | HH130F | Urban | Planned |  | 5 | 297 | 0.002374 | 7.99e-06 | No
8/08/2018 | 10:27:14 | NA60 | Rural Long | Planned |  | 3 | 96 | 0.0021019 | 2.19e-05 | No
8/08/2018 | 10:55:08 | CD03 | Rural Short | Animal | Animal impact | 1 | 118 | 0.00087912 | 7.45e-06 | No
8/08/2018 | 11:11:47 | CM18 | Rural Long | Planned |  | 2 | 96 | 0.0014013 | 1.46e-05 | No
8/08/2018 | 11:49:12 | HH409C | Urban | Asset failure | LV | 79 | 45 | 0.0056833 | 0.0001263 | No
8/08/2018 | 12:35:56 | MB63 | Rural Long | Asset failure | HV | 206 | 70 | 0.10524 | 0.0015035 | No
8/08/2018 | 12:51:16 | CD03 | Rural Short | Unknown | Unknown | 1 | 1 | 7.45e-06 | 7.45e-06 | No
8/08/2018 | 13:15:33 | CN52 | Rural Long | Unknown | Unknown | 2 | 34 | 0.00049629 | 1.46e-05 | No
8/08/2018 | 13:30:44 | BM11 | Rural Short | Third Party | Vehicle impact | 9 | 175 | 0.011734 | 6.705e-05 | No
8/08/2018 | 13:53:13 | SG03 | Rural Short | Asset failure | LV | 18 | 117 | 0.01569 | 0.0001341 | No
8/08/2018 | 14:13:32 | MI33 | Rural Long | Asset failure | HV | 50 | 232.9 | 0.084989 | 0.00036492 | No
8/08/2018 | 14:34:12 | YK29 | Rural Long | Asset failure | LV | 2 | 75 | 0.0010948 | 1.46e-05 | No
8/08/2018 | 16:27:07 | BM31 | Rural Short | Unknown | Unknown | 1 | 35 | 0.00026076 | 7.45e-06 | No
8/08/2018 | 17:46:45 | SM137A | Urban | Other |  | 1 | 296 | 0.00047321 | 1.6e-06 | No
8/08/2018 | 17:49:28 | SA13 | Urban | Asset failure | LV | 31 | 77 | 0.003816 | 4.956e-05 | No
8/08/2018 | 18:44:42 | HH428D | Urban | Overloads |  | 1 | 135 | 0.00021582 | 1.6e-06 | No
8/08/2018 | 18:48:42 | SM216C | Urban | Overloads |  | 1 | 137 | 0.00021902 | 1.6e-06 | No
8/08/2018 | 19:16:27 | MT08 | Rural Long | Overloads |  | 1 | 191 | 0.001394 | 7.3e-06 | No
8/08/2018 | 19:28:29 | MV52 | Rural Short | Asset failure | LV | 13.6667 | 143 | 0.01456 | 0.00010182 | No
8/08/2018 | 22:18:05 | HH145B | Urban | Asset failure | LV | 1 | 116 | 0.00018545 | 1.6e-06 | No
8/08/2018 | 23:28:41 | HH341H | Urban | Overloads |  | 1 | 148 | 0.0002366 | 1.6e-06 | No
9/08/2018 | 01:49:45 | SD52300 | Rural Short | Animal | Animal impact | 572 | 125 | 0.53269 | 0.0042615 | No
9/08/2018 | 01:49:45 | SD52300 | Rural Long | Animal | Animal impact | 2912 | 124.6854 | 2.6499 | 0.021253 | No
9/08/2018 | 07:20:34 | AP146E | Urban | Unknown | Unknown | 44.6666 | 110 | 0.0078548 | 7.141e-05 | No
9/08/2018 | 07:37:04 | NA57 | Rural Long | Planned |  | 2 | 145 | 0.0021165 | 1.46e-05 | No
9/08/2018 | 08:29:30 | HH121F | Urban | Asset failure | LV | 19.6666 | 118 | 0.00371 | 3.144e-05 | No
9/08/2018 | 08:34:04 | HH177F | Urban | Asset failure | LV | 1 | 343 | 0.00054835 | 1.6e-06 | No
9/08/2018 | 08:45:10 | BT18 | Rural Long | Asset failure | HV | 25 | 334.68 | 0.061065 | 0.00018246 | No
9/08/2018 | 08:53:36 | HH409A | Urban | Asset failure | LV | 1 | 237 | 0.00037889 | 1.6e-06 | No
9/08/2018 | 08:54:56 | WK65 | Rural Short | Asset failure | LV | 2 | 369 | 0.0054982 | 1.49e-05 | No
9/08/2018 | 08:56:21 | MV62 | Rural Short | Asset failure | LV | 1 | 148 | 0.0011026 | 7.45e-06 | No
9/08/2018 | 09:16:32 | MV61 | Urban | Planned |  | 43 | 148 | 0.010174 | 6.874e-05 | No
9/08/2018 | 09:27:37 | SG04 | Rural Short | Planned |  | 69 | 301.1014 | 0.15478 | 0.00051406 | No
9/08/2018 | 09:53:55 | GA29 | Rural Long | Planned |  | 6 | 118 | 0.0051672 | 4.379e-05 | No
9/08/2018 | 10:10:19 | MV34 / MV62 | Rural Short | Planned |  | 1073 | 374.37 | 2.9927 | 0.007994 | No
9/08/2018 | 10:13:15 | GA28 | Rural Long | Planned |  | 206 | 223 | 0.33527 | 0.0015035 | No
9/08/2018 | 10:14:05 | GA34 | Rural Short | Planned |  | 41 | 155 | 0.047346 | 0.00030546 | No
9/08/2018 | 10:15:02 | KI54 | Rural Long | Unknown | Unknown | 1 | 67 | 0.00048899 | 7.3e-06 | No
9/08/2018 | 10:33:55 | SM350E | Urban | Planned |  | 62 | 197 | 0.019526 | 9.912e-05 | No
9/08/2018 | 11:45:08 | CD24 | Rural Long | Unknown | Unknown | 1 | 75 | 0.00054738 | 7.3e-06 | No
9/08/2018 | 11:46:00 | AP125A | Urban | Planned |  | 95 | 100.7368 | 0.015299 | 0.00015187 | No
9/08/2018 | 12:51:13 | NL451C | Urban | Asset failure | LV | 1 | 273 | 0.00043644 | 1.6e-06 | No
9/08/2018 | 13:12:07 | ME347F | Urban | Overloads |  | 1 | 49 | 7.834e-05 | 1.6e-06 | No
9/08/2018 | 13:35:37 | VH10 | Rural Short | Planned |  | 1 | 69 | 0.00051406 | 7.45e-06 | No
9/08/2018 | 13:43:47 | SM179B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 7 | 91 | 0.0010184 | 1.119e-05 | No
9/08/2018 | 14:04:01 | MI33 | Rural Long | Asset failure | HV | 49 | 2 | 0.00071524 | 0.00035762 | No
9/08/2018 | 15:10:07 | ST34 | Rural Long | Unknown | Unknown | 48.6667 | 78 | 0.027704 | 0.00035519 | No
9/08/2018 | 16:13:35 | GA50 | Urban | Asset failure | LV | 1 | 166 | 0.00026538 | 1.6e-06 | No
9/08/2018 | 16:54:32 | SG14 | Rural Short | Asset failure | LV | 1 | 1308 | 0.0097448 | 7.45e-06 | No
9/08/2018 | 18:01:41 | SA31 | Urban | Other |  | 1 | 138 | 0.00022062 | 1.6e-06 | No
9/08/2018 | 18:03:18 | HH177G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 50 | 60 | 0.004796 | 7.993e-05 | No
9/08/2018 | 18:09:59 | NL760B | Urban | Asset failure | LV | 29 | 57 | 0.0026426 | 4.636e-05 | No
9/08/2018 | 18:13:12 | MB22 | Rural Short | Asset failure | HV | 1148 | 107.7927 | 0.92193 | 0.0085528 | No
9/08/2018 | 20:46:00 | MG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 660 | 75.853 | 0.37298 | 0.0049171 | No
10/08/2018 | 00:24:00 | SG09 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 315 | 93 | 0.21825 | 0.0023468 | No
10/08/2018 | 01:36:00 | HH341A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1216 | 73 | 0.14191 | 0.001944 | No
10/08/2018 | 01:50:00 | MG05 | Rural Long | Asset failure | HV | 1186 | 82.7681 | 0.71643 | 0.0086558 | No
10/08/2018 | 02:39:00 | YK23 | Rural Long | Asset failure | HV | 807 | 87.7757 | 0.51698 | 0.0058898 | No
10/08/2018 | 02:49:33 | SM350G | Urban | Asset failure | LV | 99 | 752 | 0.11902 | 0.00015827 | No
10/08/2018 | 03:17:00 | MV42 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 762 | 175.29 | 0.99512 | 0.005677 | No
10/08/2018 | 03:28:09 | KI31 | Rural Short | Unknown | Unknown | 64 | 87 | 0.041482 | 0.00047681 | No
10/08/2018 | 05:56:12 | HH496A | Urban | Asset failure | LV | 1 | 501 | 0.00080094 | 1.6e-06 | No
10/08/2018 | 06:03:53 | SM349F | Urban | Asset failure | LV | 1 | 227 | 0.0003629 | 1.6e-06 | No
10/08/2018 | 06:21:00 | MTB32 | Rural Long | Unknown | Unknown | 60 | 200.9 | 0.087974 | 0.0004379 | No
10/08/2018 | 06:43:00 | HH148C | Urban | Unknown | Unknown | 119 | 102 | 0.019405 | 0.00019024 | No
10/08/2018 | 07:16:59 | VH10 | Rural Short | Unknown | Unknown | 16.6667 | 187 | 0.02322 | 0.00012417 | No
10/08/2018 | 07:56:16 | VH23 | Rural Short | Asset failure | LV | 25 | 67 | 0.012479 | 0.00018625 | No
10/08/2018 | 08:07:40 | HH432A | Urban | Unknown | Unknown | 1 | 46 | 7.354e-05 | 1.6e-06 | No
10/08/2018 | 08:31:00 | BT06 | Rural Long | Third Party | Vehicle impact | 1116 | 34.1989 | 0.27855 | 0.0081449 | No
10/08/2018 | 08:32:19 | VH21 | Rural Short | Asset failure | LV | 1 | 352 | 0.0026225 | 7.45e-06 | No
10/08/2018 | 08:49:47 | VH22 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 8 | 193 | 0.011503 | 5.96e-05 | No
10/08/2018 | 09:01:52 | NL115C | Urban | Planned |  | 465 | 367 | 0.27282 | 0.00074338 | No
10/08/2018 | 09:16:02 | NA60 | Rural Long | Planned |  | 2 | 126 | 0.0018392 | 1.46e-05 | No
10/08/2018 | 09:18:12 | ST34 | Rural Long | Vegetation | Grow-in - NSP responsibility | 1 | 217 | 0.0015837 | 7.3e-06 | No
10/08/2018 | 09:33:58 | HH148D | Urban | Asset failure | LV | 2 | 159 | 0.00050838 | 3.2e-06 | No
10/08/2018 | 09:54:07 | PA04 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 174 | 0.0012963 | 7.45e-06 | No
10/08/2018 | 10:07:41 | SA16 | Urban | Asset failure | LV | 41 | 60 | 0.0039327 | 6.555e-05 | No
10/08/2018 | 10:11:00 | HH341J | Urban | Planned |  | 311 | 280 | 0.13921 | 0.00049719 | No
10/08/2018 | 10:27:00 | SD49100 | Rural Long | Unknown | Unknown | 304 | 510.0888 | 1.1317 | 0.0022187 | No
10/08/2018 | 11:12:30 | CD02 | Rural Long | Overloads |  | 17 | 171 | 0.021216 | 0.00012407 | No
10/08/2018 | 11:46:11 | NA60 | Rural Long | Planned |  | 2 | 129 | 0.001883 | 1.46e-05 | No
10/08/2018 | 12:36:19 | VH15 | Rural Short | Asset failure | LV | 13.6667 | 122 | 0.012422 | 0.00010182 | No
10/08/2018 | 12:46:58 | GA800A | Rural Short | Asset failure | LV | 1 | 591 | 0.004403 | 7.45e-06 | No
10/08/2018 | 13:23:44 | G24 | Rural Long | Asset failure | HV | 46 | 45 | 0.015108 | 0.00033572 | No
10/08/2018 | 14:49:22 | CBD103C | Urban | Animal | Animal impact | 1 | 285 | 0.00045562 | 1.6e-06 | No
10/08/2018 | 15:11:03 | HH341E | Urban | Asset failure | LV | 1 | 335 | 0.00053556 | 1.6e-06 | No
10/08/2018 | 15:16:06 | SD54300 | Rural Long | Unknown | Unknown | 621.6669 | 49 | 0.22232 | 0.0045371 | No
10/08/2018 | 15:55:57 | MTB13 | Rural Short | Asset failure | HV | 457 | 75 | 0.25535 | 0.0034047 | No
10/08/2018 | 16:40:18 | HH145D | Urban | Asset failure | LV | 40 | 593 | 0.037921 | 6.395e-05 | No
10/08/2018 | 17:37:03 | HH403A | Urban | Asset failure | LV | 67 | 27 | 0.002892 | 0.00010711 | No
10/08/2018 | 18:32:49 | NL544B | Urban | Asset failure | LV | 1 | 173 | 0.00027657 | 1.6e-06 | No
10/08/2018 | 18:33:06 | HH341E | Urban | Asset failure | LV | 1 | 195 | 0.00031174 | 1.6e-06 | No
10/08/2018 | 18:44:26 | SA744D | Urban | Asset failure | LV | 1 | 356 | 0.00056913 | 1.6e-06 | No
10/08/2018 | 19:30:22 | MT07 | Rural Long | Asset failure | LV | 2 | 225 | 0.0032842 | 1.46e-05 | No
10/08/2018 | 22:29:55 | SD33200 | Rural Long | Unknown | Unknown | 1 | 132 | 0.00096338 | 7.3e-06 | No
11/08/2018 | 02:29:00 | SG07 | Rural Short | Unknown | Unknown | 235 | 151.5532 | 0.26534 | 0.0017508 | No
11/08/2018 | 07:37:07 | CBD103A | Urban | Asset failure | LV | 1 | 255 | 0.00040766 | 1.6e-06 | No
11/08/2018 | 09:24:10 | BT26 | Rural Long | Unknown | Unknown | 165 | 219 | 0.26373 | 0.0012042 | No
11/08/2018 | 11:17:11 | HH107D | Urban | Overloads |  | 1 | 229 | 0.0003661 | 1.6e-06 | No
11/08/2018 | 11:22:03 | SA20 | Urban | Asset failure | LV | 46 | 122 | 0.0089718 | 7.354e-05 | No
11/08/2018 | 11:35:46 | SA20 | Urban | Unknown | Unknown | 46 | 94 | 0.0069127 | 7.354e-05 | No
11/08/2018 | 12:13:45 | HH496B | Urban | Unknown | Unknown | 2 | 121 | 0.00038688 | 3.2e-06 | No
11/08/2018 | 12:33:28 | HH177B | Urban | Vegetation | Grow-in - NSP responsibility | 7.3333 | 75 | 0.00087927 | 1.172e-05 | No
11/08/2018 | 12:55:23 | HH145B | Urban | Asset failure | LV | 1 | 385 | 0.00061549 | 1.6e-06 | No
11/08/2018 | 13:24:41 | VH21 | Rural Short | Asset failure | LV | 83 | 129 | 0.079769 | 0.00061836 | No
11/08/2018 | 13:33:03 | MG34 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1699.0006 | 11.2727 | 0.13978 | 0.0124 | No
11/08/2018 | 13:50:51 | SM350G | Urban | Asset failure | LV | 99 | 77 | 0.012187 | 0.00015827 | No
11/08/2018 | 14:57:14 | BM13 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 70 | 0.00052151 | 7.45e-06 | No
11/08/2018 | 15:12:09 | BU09 | Rural Long | Asset failure | HV | 2 | 23 | 0.00033572 | 1.46e-05 | No
11/08/2018 | 15:51:56 | NL234C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 230 | 0.0003677 | 1.6e-06 | No
11/08/2018 | 16:00:00 | HH130F | Urban | Asset failure | Distribution substation | 1727 | 114.8222 | 0.31701 | 0.0027609 | No
11/08/2018 | 16:01:54 | HH130F | Urban | Asset failure | Distribution substation | 3 | 106 | 0.00050838 | 4.8e-06 | No
11/08/2018 | 16:08:27 | AP425C | Urban | Asset failure | LV | 29.3333 | 180 | 0.008441 | 4.689e-05 | No
11/08/2018 | 16:35:39 | SA33 | Urban | Asset failure | LV | 70 | 91 | 0.010184 | 0.00011191 | No
11/08/2018 | 17:24:43 | LX41 | Rural Short | Animal | Animal impact | 30.3333 | 57 | 0.012881 | 0.00022599 | No
11/08/2018 | 17:38:48 | SA31 | Urban | Asset failure | LV | 1 | 334 | 0.00053396 | 1.6e-06 | No
11/08/2018 | 17:52:08 | SM216B | Urban | Asset failure | LV | 15 | 209 | 0.0050118 | 2.398e-05 | No
11/08/2018 | 19:11:59 | SM349F | Urban | Asset failure | LV | 29.6666 | 100 | 0.0047427 | 4.743e-05 | No
11/08/2018 | 19:50:05 | SB01 | Rural Long | Asset failure | HV | 1 | 70 | 0.00051088 | 7.3e-06 | No
11/08/2018 | 21:26:25 | VH17 | Rural Short | Asset failure | LV | 1 | 147 | 0.0010952 | 7.45e-06 | No
11/08/2018 | 21:26:46 | AP424D | Urban | Overloads |  | 1 | 208 | 0.00033252 | 1.6e-06 | No
11/08/2018 | 21:56:00 | MV13 | Rural Short | Asset failure | HV | 681 | 291 | 1.4764 | 0.0050735 | No
11/08/2018 | 22:05:49 | NL210A | Urban | Asset failure | LV | 4 | 892 | 0.0057041 | 6.39e-06 | No
12/08/2018 | 00:02:59 | SM411C | Urban | Asset failure | LV | 1 | 559 | 0.00089366 | 1.6e-06 | No
12/08/2018 | 08:22:56 | AP424A | Urban | Asset failure | LV | 1 | 269 | 0.00043004 | 1.6e-06 | No
12/08/2018 | 08:26:26 | HH107C | Urban | Asset failure | LV | 1 | 173 | 0.00027657 | 1.6e-06 | No
12/08/2018 | 09:05:54 | SA31 | Urban | Asset failure | LV | 15 | 306 | 0.0073379 | 2.398e-05 | No
12/08/2018 | 09:20:59 | HH409F | Urban | Planned |  | 170 | 392 | 0.10654 | 0.00027177 | No
12/08/2018 | 09:22:31 | HH429C | Urban | Asset failure | LV | 1 | 135 | 0.00021582 | 1.6e-06 | No
12/08/2018 | 09:47:15 | NL115E | Urban | Asset failure | LV | 1 | 185 | 0.00029575 | 1.6e-06 | No
12/08/2018 | 09:54:53 | SA18 | Urban | Overloads |  | 1 | 311 | 0.00049719 | 1.6e-06 | No
12/08/2018 | 10:01:03 | EL14 | Urban | Vegetation | Grow-in - NSP responsibility | 16.6667 | 30 | 0.00079934 | 2.664e-05 | No
12/08/2018 | 10:04:36 | KA05 | Rural Long | Asset failure | LV | 1 | 417 | 0.0030434 | 7.3e-06 | No
12/08/2018 | 10:41:13 | HH121A | Urban | Planned |  | 250 | 219 | 0.087527 | 0.00039967 | No
12/08/2018 | 11:11:21 | PA02 | Urban | Asset failure | LV | 1 | 139 | 0.00022222 | 1.6e-06 | No
12/08/2018 | 11:31:11 | PP06 | Rural Long | Asset failure | LV | 1 | 277 | 0.0020216 | 7.3e-06 | No
12/08/2018 | 12:09:11 | NA60 | Rural Long | Asset failure | LV | 1 | 264 | 0.0019268 | 7.3e-06 | No
12/08/2018 | 12:55:08 | HH148D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 228 | 0.0003645 | 1.6e-06 | No
12/08/2018 | 15:48:59 | YK19 | Rural Long | Asset failure | LV | 1 | 1213 | 0.0088529 | 7.3e-06 | No
12/08/2018 | 20:21:03 | HH341E | Urban | Overloads |  | 1 | 121 | 0.00019344 | 1.6e-06 | No
12/08/2018 | 21:11:14 | SA17 | Urban | Asset failure | LV | 1 | 69 | 0.00011031 | 1.6e-06 | No
12/08/2018 | 21:49:01 | SA711C | Urban | Asset failure | LV | 1 | 94 | 0.00015028 | 1.6e-06 | No
12/08/2018 | 23:22:44 | SA40 | Urban | Third Party | Dig-in | 1 | 609 | 0.00097359 | 1.6e-06 | No
13/08/2018 | 05:13:18 | HH496D | Urban | Asset failure | LV | 1 | 340 | 0.00054355 | 1.6e-06 | No
13/08/2018 | 05:31:07 | MTB51 | Rural Long | Animal | Animal impact | 44 | 107 | 0.034361 | 0.00032113 | No
13/08/2018 | 07:30:59 | G13 | Rural Long | Asset failure | LV | 1 | 520 | 0.0037951 | 7.3e-06 | No
13/08/2018 | 07:46:37 | SA35 | Urban | Overloads |  | 1 | 161 | 0.00025739 | 1.6e-06 | No
13/08/2018 | 08:09:29 | GA53 | Rural Short | Overloads |  | 2 | 190 | 0.0028311 | 1.49e-05 | No
13/08/2018 | 09:14:06 | AP139D | Urban | Planned |  | 72 | 301 | 0.034646 | 0.0001151 | No
13/08/2018 | 09:31:07 | SA40 | Urban | Planned |  | 655 | 27.4458 | 0.028739 | 0.0010471 | No
13/08/2018 | 09:31:07 | SA40 | Urban | Planned |  | 0 | 36.942 | 0.038683 | 0 | No
13/08/2018 | 09:33:27 | AP139B | Urban | Asset failure | LV | 1 | 251 | 0.00040127 | 1.6e-06 | No
13/08/2018 | 09:39:10 | ME231E | Urban | Asset failure | LV | 1 | 111 | 0.00017745 | 1.6e-06 | No
13/08/2018 | 10:05:42 | ST34 | Rural Long | Planned |  | 257 | 240 | 0.45016 | 0.0018757 | No
13/08/2018 | 10:07:40 | SM350A | Urban | Planned |  | 101 | 255 | 0.041174 | 0.00016147 | No
13/08/2018 | 11:10:47 | HH409A | Urban | Planned |  | 2 | 64 | 0.00020463 | 3.2e-06 | No
13/08/2018 | 11:47:42 | HH102B | Urban | Asset failure | LV | 2 | 252 | 0.00080573 | 3.2e-06 | No
13/08/2018 | 12:45:23 | M92 | Rural Long | Unknown | Unknown | 9 | 55 | 0.0036127 | 6.569e-05 | No
13/08/2018 | 16:11:18 | SA17 | Urban | Asset failure | LV | 59 | 103 | 0.0097152 | 9.432e-05 | No
13/08/2018 | 16:11:38 | SA17 | Urban | Asset failure | LV | 46 | 103 | 0.0075745 | 7.354e-05 | No
13/08/2018 | 16:14:33 | SA14 | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
13/08/2018 | 16:39:19 | HH177D | Urban | Overloads |  | 1 | 58 | 9.272e-05 | 1.6e-06 | No
13/08/2018 | 18:14:28 | HH496G | Urban | Asset failure | LV | 1 | 80 | 0.00012789 | 1.6e-06 | No
13/08/2018 | 18:21:03 | HH386G | Urban | Asset failure | LV | 32.6666 | 146 | 0.0076246 | 5.222e-05 | No
13/08/2018 | 19:57:09 | HH118C | Urban | Asset failure | LV | 62 | 57 | 0.0056497 | 9.912e-05 | No
13/08/2018 | 22:04:19 | SM349F | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
13/08/2018 | 22:07:56 | SM349F | Urban | Asset failure | LV | 1 | 95 | 0.00015187 | 1.6e-06 | No
14/08/2018 | 05:55:24 | MG37 | Rural Long | Asset failure | LV | 1 | 163 | 0.0011896 | 7.3e-06 | No
14/08/2018 | 06:37:07 | HH386E | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
14/08/2018 | 07:13:16 | VH21 | Rural Short | Asset failure | LV | 48 | 95 | 0.033973 | 0.00035761 | No
14/08/2018 | 08:26:47 | PA06 | Rural Long | Planned |  | 27 | 262 | 0.051628 | 0.00019706 | No
14/08/2018 | 08:29:18 | YK17 | Rural Long | Planned |  | 598 | 10 | 0.043644 | 0.0043644 | No
14/08/2018 | 08:52:48 | MTB52 | Rural Long | Planned |  | 18 | 297 | 0.039017 | 0.00013137 | No
14/08/2018 | 09:35:00 | ST36 | Rural Long | Asset failure | HV | 421 | 123 | 0.37793 | 0.0030726 | No
14/08/2018 | 09:35:34 | SM216B | Urban | Asset failure | LV | 29.6666 | 138 | 0.006545 | 4.743e-05 | No
14/08/2018 | 09:50:37 | SG09 | Rural Short | Asset failure | LV | 1 | 575 | 0.0042838 | 7.45e-06 | No
14/08/2018 | 09:57:52 | SM350E | Urban | Asset failure | LV | 11 | 242 | 0.0042557 | 1.759e-05 | No
14/08/2018 | 09:59:36 | HH341K | Urban | Planned |  | 36 | 283 | 0.016287 | 5.755e-05 | No
14/08/2018 | 10:04:28 | MV15 | Rural Short | Planned |  | 4 | 285 | 0.0084932 | 2.98e-05 | No
14/08/2018 | 10:05:24 | PL07 | Urban | Planned |  | 8 | 20 | 0.00025579 | 1.279e-05 | No
14/08/2018 | 10:06:33 | AP132B | Urban | Third Party | Vehicle impact | 1 | 491 | 0.00078495 | 1.6e-06 | No
14/08/2018 | 10:11:19 | MV62 | Rural Short | Planned |  | 135 | 216 | 0.21725 | 0.0010058 | No
14/08/2018 | 10:17:10 | W23 | Rural Long | Planned |  | 47 | 211 | 0.072378 | 0.00034302 | No
14/08/2018 | 10:28:00 | SG08 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 200 | 128.67 | 0.19172 | 0.00149 | No
14/08/2018 | 10:30:23 | AP372B | Urban | Third Party | Vehicle impact | 111 | 460 | 0.081628 | 0.00017745 | No
14/08/2018 | 10:40:38 | BM34 | Rural Short | Asset failure | LV | 1 | 225 | 0.0016763 | 7.45e-06 | No
14/08/2018 | 12:11:05 | LX51 | Rural Short | Overloads |  | 1 | 201 | 0.0014975 | 7.45e-06 | No
14/08/2018 | 14:33:00 | SA520H | Urban | Asset failure | LV | 20 | 178 | 0.0056913 | 3.197e-05 | No
14/08/2018 | 15:36:52 | MG02 | Rural Long | Unknown | Unknown | 139 | 46.8561 | 0.047534 | 0.0010145 | No
14/08/2018 | 18:54:29 | HH429C | Urban | Asset failure | LV | 1 | 123 | 0.00019664 | 1.6e-06 | No
14/08/2018 | 19:19:04 | GA25 | Rural Short | Overloads |  | 1 | 189 | 0.0014081 | 7.45e-06 | No
14/08/2018 | 20:54:11 | MV11 | Rural Short | Unknown | Unknown | 92 | 226.3587 | 0.15515 | 0.00068541 | No
14/08/2018 | 22:26:57 | SA33 | Urban | Unknown | Unknown | 10.6667 | 37 | 0.00063094 | 1.705e-05 | No
14/08/2018 | 22:55:56 | AP365F | Urban | Asset failure | LV | 34.6666 | 69 | 0.003824 | 5.542e-05 | No
14/08/2018 | 23:42:23 | NL511A | Urban | Overloads |  | 1 | 188 | 0.00030055 | 1.6e-06 | No
15/08/2018 | 06:54:56 | SA33 | Urban | Unknown | Unknown | 10.6667 | 67 | 0.0011425 | 1.705e-05 | No
15/08/2018 | 06:56:03 | SM216C | Urban | Overloads |  | 1 | 118 | 0.00018864 | 1.6e-06 | No
15/08/2018 | 08:12:58 | YK17 | Rural Long | Planned |  | 474 | 312 | 1.0793 | 0.0034594 | No
15/08/2018 | 08:21:39 | NL111A / NL451A / SM349F | Urban | Planned |  | 698 | 319.8868 | 0.35695 | 0.0011159 | No
15/08/2018 | 08:55:00 | MTB52 | Rural Long | Planned |  | 49 | 284.0408 | 0.10158 | 0.00035762 | No
15/08/2018 | 08:55:42 | NU23 | Rural Long | Planned |  | 43 | 378 | 0.11863 | 0.00031383 | No
15/08/2018 | 08:57:12 | GA800A | Rural Short | Planned |  | 71 | 28 | 0.014811 | 0.00052896 | No
15/08/2018 | 09:04:29 | BM44 | Rural Short | Planned |  | 4 | 102 | 0.0030397 | 2.98e-05 | No
15/08/2018 | 09:05:56 | MB65 | Rural Long | Planned |  | 31 | 328 | 0.074209 | 0.00022625 | No
15/08/2018 | 09:09:53 | GA01 | Urban | Asset failure | LV | 20 | 49 | 0.0015667 | 3.197e-05 | No
15/08/2018 | 09:20:02 | KA04 | Rural Long | Planned |  | 165 | 297.1273 | 0.35781 | 0.0012042 | No
15/08/2018 | 09:39:38 | HH177F | Urban | Asset failure | LV | 32.6667 | 225 | 0.01175 | 5.222e-05 | No
15/08/2018 | 09:47:18 | HH341G | Urban | Planned |  | 231 | 141.7186 | 0.052336 | 0.00036929 | No
15/08/2018 | 09:48:42 | HH145C | Urban | Planned |  | 39 | 239 | 0.014901 | 6.235e-05 | No
15/08/2018 | 10:21:08 | BM15 | Rural Short | Planned |  | 1 | 117 | 0.00087167 | 7.45e-06 | No
15/08/2018 | 10:26:06 | SA14 | Urban | Asset failure | HV | 70 | 299 | 0.03346 | 0.00011191 | No
15/08/2018 | 10:28:07 | HH121F | Urban | Planned |  | 166 | 99 | 0.026273 | 0.00026538 | No
15/08/2018 | 11:00:57 | MB01 | Rural Long | Planned |  | 110 | 209 | 0.16779 | 0.00080282 | No
15/08/2018 | 12:01:19 | EL17 | Urban | Overloads |  | 8 | 33 | 0.00042205 | 1.279e-05 | No
15/08/2018 | 13:27:01 | BM53 | Rural Short | Unknown | Unknown | 1 | 13 | 9.685e-05 | 7.45e-06 | No
15/08/2018 | 13:40:09 | HH341A | Urban | Asset failure | LV | 2 | 166 | 0.00053076 | 3.2e-06 | No
15/08/2018 | 15:57:27 | MV64 | Urban | Asset failure | LV | 19.3333 | 138 | 0.0042653 | 3.091e-05 | No
15/08/2018 | 17:09:59 | NL451E | Urban | Asset failure | LV | 1 | 96 | 0.00015347 | 1.6e-06 | No
15/08/2018 | 17:14:21 | SA33 | Urban | Asset failure | LV | 32 | 297 | 0.015194 | 5.116e-05 | No
15/08/2018 | 18:04:23 | CBD412F | Urban | Other |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
15/08/2018 | 19:24:01 | HH341D | Urban | Overloads |  | 1 | 147 | 0.00023501 | 1.6e-06 | No
15/08/2018 | 20:16:39 | CL16 | Rural Long | Third Party | Vehicle impact | 202 | 88 | 0.12974 | 0.0014743 | No
15/08/2018 | 21:56:18 | AP425C | Urban | Overloads |  | 1 | 294 | 0.00047001 | 1.6e-06 | No
15/08/2018 | 22:53:01 | NL234A | Urban | Planned |  | 361 | 299 | 0.17256 | 0.00057712 | No
15/08/2018 | 22:58:03 | SM179D | Urban | Planned |  | 191 | 327.8063 | 0.10009 | 0.00030535 | No
15/08/2018 | 23:03:46 | NL511A | Urban | Planned |  | 45 | 313 | 0.022517 | 7.194e-05 | No
16/08/2018 | 00:13:12 | HH522C | Urban | Asset failure | LV | 37 | 42 | 0.0024843 | 5.915e-05 | No
16/08/2018 | 03:45:21 | SA14 | Urban | Asset failure | LV | 1 | 275 | 0.00043964 | 1.6e-06 | No
16/08/2018 | 06:35:20 | HH148C | Urban | Asset failure | HV | 119 | 240 | 0.045658 | 0.00019024 | No
16/08/2018 | 07:44:07 | NA30 | Rural Long | Unknown | Unknown | 36 | 233 | 0.061218 | 0.00026274 | No
16/08/2018 | 07:53:06 | SM411A | Urban | Asset failure | LV | 1 | 195 | 0.00031174 | 1.6e-06 | No
16/08/2018 | 08:07:00 | SM410D | Urban | Third Party | Dig-in | 1886 | 114.9565 | 0.34661 | 0.0030151 | No
16/08/2018 | 08:08:44 | SM410D | Urban | Third Party | Vehicle impact | 2 | 127.5 | 0.00040766 | 3.2e-06 | No
16/08/2018 | 08:52:17 | PA05 | Rural Long | Planned |  | 2 | 38 | 0.00055467 | 1.46e-05 | No
16/08/2018 | 08:58:33 | SB22 | Rural Long | Planned |  | 47 | 295 | 0.10119 | 0.00034302 | No
16/08/2018 | 09:00:16 | KI31 | Rural Short | Other |  | 1 | 90 | 0.00067051 | 7.45e-06 | No
16/08/2018 | 09:03:35 | MTB32 | Rural Long | Planned |  | 56 | 359 | 0.14673 | 0.00040871 | No
16/08/2018 | 09:33:42 | GA10 | Rural Long | Planned |  | 14 | 117 | 0.011955 | 0.00010218 | No
16/08/2018 | 09:40:09 | SA744D | Urban | Planned |  | 205 | 46.6585 | 0.015291 | 0.00032773 | No
16/08/2018 | 09:40:58 | MG03 | Rural Short | Planned |  | 8 | 229 | 0.013649 | 5.96e-05 | No
16/08/2018 | 09:44:58 | HH145A | Urban | Planned |  | 944 | 295.4163 | 0.44583 | 0.0015091 | No
16/08/2018 | 09:45:51 | AP424E | Urban | Planned |  | 32 | 248 | 0.012687 | 5.116e-05 | No
16/08/2018 | 09:51:14 | MV62 | Rural Short | Planned |  | 114 | 148 | 0.1257 | 0.00084932 | No
16/08/2018 | 09:54:10 | SA20 | Urban | Planned |  | 108 | 236 | 0.040747 | 0.00017266 | No
16/08/2018 | 10:00:28 | WK71 | Rural Short | Planned |  | 1 | 49 | 0.00036506 | 7.45e-06 | No
16/08/2018 | 10:07:38 | SA20 | Urban | Planned |  | 48 | 251 | 0.019261 | 7.674e-05 | No
16/08/2018 | 10:24:23 | GA21 | Rural Long | Planned |  | 44 | 242 | 0.077713 | 0.00032113 | No
16/08/2018 | 10:31:52 | GA33 | Rural Short | Asset failure | HV | 2 | 9 | 0.0001341 | 1.49e-05 | No
16/08/2018 | 10:32:07 | HH386A | Urban | Planned |  | 66 | 187 | 0.019731 | 0.00010551 | No
16/08/2018 | 11:10:41 | EL03 | Urban | Vegetation | Grow-in - NSP responsibility | 27.6666 | 66 | 0.0029192 | 4.423e-05 | No
16/08/2018 | 11:26:00 | MT24 | Rural Long | Planned |  | 74 | 5.5676 | 0.0030069 | 0.00054008 | No
16/08/2018 | 12:10:31 | AP214D | Urban | Asset failure | LV | 2 | 174 | 0.00055634 | 3.2e-06 | No
16/08/2018 | 12:57:33 | CM16 | Rural Long | Asset failure | LV | 2 | 296 | 0.0043206 | 1.46e-05 | No
16/08/2018 | 13:38:32 | GA08 | Rural Long | Unknown | Unknown | 2 | 54 | 0.00078822 | 1.46e-05 | No
16/08/2018 | 14:13:28 | HH121E | Urban | Asset failure | LV | 1 | 144 | 0.00023021 | 1.6e-06 | No
16/08/2018 | 15:31:30 | SM137B | Urban | Overloads |  | 1 | 532 | 0.0008505 | 1.6e-06 | No
16/08/2018 | 16:40:00 | WHY03 | Urban | Asset failure | HV | 968 | 231.4246 | 0.35813 | 0.0015475 | No
16/08/2018 | 16:46:00 | EL01Q | Urban | Animal | Animal impact | 1003 | 87.7926 | 0.14077 | 0.0016035 | No
16/08/2018 | 18:22:33 | SA16 | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | No
16/08/2018 | 19:36:23 | MV13 | Rural Short | Asset failure | LV | 1 | 368 | 0.0027416 | 7.45e-06 | No
16/08/2018 | 19:59:47 | SM411E | Urban | Overloads |  | 1 | 369 | 0.00058991 | 1.6e-06 | No
16/08/2018 | 20:30:24 | AP227A | Urban | Asset failure | LV | 1 | 76 | 0.0001215 | 1.6e-06 | No
16/08/2018 | 20:53:36 | MT10 | Rural Long | Asset failure | HV | 13 | 222 | 0.021063 | 9.488e-05 | No
16/08/2018 | 21:30:24 | SM126D | Urban | Asset failure | LV | 25 | 117 | 0.0046761 | 3.997e-05 | No
17/08/2018 | 03:07:28 | EL15 | Urban | Asset failure | LV | 8 | 91 | 0.0011638 | 1.279e-05 | No
17/08/2018 | 06:10:07 | MT02 | Rural Long | Overloads |  | 2 | 199 | 0.0029047 | 1.46e-05 | No
17/08/2018 | 07:07:00 | CL09 | Rural Long | Unknown | Unknown | 6 | 152 | 0.0066561 | 4.379e-05 | No
17/08/2018 | 07:35:30 | CBD103C | Urban | Asset failure | LV | 94 | 292 | 0.04388 | 0.00015028 | No
17/08/2018 | 08:33:22 | WK31 | Rural Short | Planned |  | 4 | 124 | 0.0036953 | 2.98e-05 | No
17/08/2018 | 08:48:09 | MV63 | Rural Short | Planned |  | 34 | 200.1765 | 0.050706 | 0.00025331 | No
17/08/2018 | 08:55:48 | AP373H | Urban | Planned |  | 1 | 4301 | 0.0068759 | 1.6e-06 | No
17/08/2018 | 09:07:31 | KI31 | Rural Short | Planned |  | 2 | 104 | 0.0015496 | 1.49e-05 | No
17/08/2018 | 09:07:58 | HH429B | Urban | Planned |  | 92 | 276 | 0.040594 | 0.00014708 | No
17/08/2018 | 09:10:46 | MB02 | Rural Long | Planned |  | 73 | 230 | 0.12254 | 0.00053278 | No
17/08/2018 | 09:23:21 | SM350G | Urban | Planned |  | 248 | 283 | 0.1122 | 0.00039647 | No
17/08/2018 | 09:31:23 | MB42 | Rural Long | Unknown | Unknown | 1 | 227 | 0.0016567 | 7.3e-06 | No
17/08/2018 | 09:41:00 | SA42 | Urban | Network business | Switching and protection error | 2741 | 38.1609 | 0.16722 | 0.004382 | No
17/08/2018 | 09:57:22 | HH432B | Urban | Planned |  | 126 | 168 | 0.033841 | 0.00020143 | No
17/08/2018 | 10:18:23 | MV15 | Rural Short | Unknown | Unknown | 76 | 25 | 0.014155 | 0.00056621 | No
17/08/2018 | 10:22:38 | SM349C | Urban | Planned |  | 178 | 241 | 0.06858 | 0.00028456 | No
17/08/2018 | 10:32:13 | SM374A | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
17/08/2018 | 10:34:40 | GA20 | Rural Long | Planned |  | 2 | 219 | 0.0031967 | 1.46e-05 | No
17/08/2018 | 10:44:01 | SM349C | Urban | Planned |  | 1 | 297 | 0.00047481 | 1.6e-06 | No
17/08/2018 | 10:49:50 | GU118 | Rural Long | Planned |  | 1 | 110 | 0.00080282 | 7.3e-06 | No
17/08/2018 | 10:52:55 | W29 | Rural Long | Asset failure | LV | 1 | 310 | 0.0022625 | 7.3e-06 | No
17/08/2018 | 11:08:34 | BT14 | Rural Long | Planned |  | 14 | 162 | 0.016553 | 0.00010218 | No
17/08/2018 | 12:09:06 | AP529D | Urban | Asset failure | LV | 1 | 217 | 0.00034691 | 1.6e-06 | No
17/08/2018 | 13:15:08 | M21 | Rural Long | Asset failure | LV | 1 | 231 | 0.0016859 | 7.3e-06 | No
17/08/2018 | 14:10:18 | R14 | Rural Long | Planned |  | 2 | 35 | 0.00051088 | 1.46e-05 | No
17/08/2018 | 14:18:54 | BM44 | Rural Short | Asset failure | LV | 2 | 72 | 0.0010728 | 1.49e-05 | No
17/08/2018 | 14:25:39 | AP344F | Urban | Asset failure | LV | 2 | 138 | 0.00044123 | 3.2e-06 | No
17/08/2018 | 14:54:49 | HH177C | Urban | Overloads |  | 1 | 126 | 0.00020143 | 1.6e-06 | No
17/08/2018 | 15:18:36 | SA20 / SA711C | Urban | Planned |  | 631 | 1 | 0.0010088 | 0.0010088 | No
17/08/2018 | 15:39:26 | HH496A | Urban | Asset failure | LV | 2 | 2622 | 0.0083835 | 3.2e-06 | No
17/08/2018 | 15:46:04 | HH145D | Urban | Asset failure | LV | 1 | 216 | 0.00034531 | 1.6e-06 | No
17/08/2018 | 15:49:25 | MI33 | Rural Long | Asset failure | HV | 50 | 1241.14 | 0.45291 | 0.00036492 | No
17/08/2018 | 18:31:53 | HH121A | Urban | Asset failure | LV | 1 | 383 | 0.00061229 | 1.6e-06 | No
17/08/2018 | 19:19:54 | HH428B | Urban | Overloads |  | 1 | 209 | 0.00033412 | 1.6e-06 | No
17/08/2018 | 20:21:22 | ME131A | Urban | Asset failure | LV | 1 | 172 | 0.00027497 | 1.6e-06 | No
17/08/2018 | 20:37:00 | NL234C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2608 | 64 | 0.26684 | 0.0041693 | No
17/08/2018 | 21:09:51 | ME116A | Urban | Overloads |  | 1 | 168 | 0.00026858 | 1.6e-06 | No
17/08/2018 | 21:17:12 | CM16 | Rural Long | Unknown | Unknown | 20 | 287.2 | 0.041922 | 0.00014597 | No
18/08/2018 | 05:13:16 | HH341E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2417 | 83.9144 | 0.32424 | 0.003864 | No
18/08/2018 | 05:18:56 | SG12 | Rural Short | Unknown | Unknown | 11.6667 | 107 | 0.0093003 | 8.692e-05 | No
18/08/2018 | 07:18:07 | AP226E | Urban | Weather |  | 1 | 230 | 0.0003677 | 1.6e-06 | No
18/08/2018 | 09:18:44 | HH428F | Urban | Asset failure | LV | 52.9999 | 119 | 0.010083 | 8.473e-05 | No
18/08/2018 | 09:20:05 | LX51 | Rural Short | Asset failure | LV | 1 | 175 | 0.0013038 | 7.45e-06 | No
18/08/2018 | 10:12:15 | CV08 | Rural Long | Asset failure | HV | 13 | 233 | 0.022107 | 9.488e-05 | No
18/08/2018 | 10:41:21 | HH522B | Urban | Asset failure | LV | 1 | 284 | 0.00045402 | 1.6e-06 | No
18/08/2018 | 10:47:57 | NL760B | Urban | Asset failure | LV | 1 | 167 | 0.00026698 | 1.6e-06 | No
18/08/2018 | 10:54:06 | SM349E | Urban | Vegetation | Grow-in - NSP responsibility | 41 | 72 | 0.0047193 | 6.555e-05 | No
18/08/2018 | 11:29:11 | HH130F | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 160 | 0.00051158 | 3.2e-06 | No
18/08/2018 | 11:40:08 | MB28 | Rural Short | Asset failure | LV | 1 | 209 | 0.0015571 | 7.45e-06 | No
18/08/2018 | 12:12:38 | NL760C | Urban | Asset failure | LV | 30.3333 | 35 | 0.0016973 | 4.849e-05 | No
18/08/2018 | 12:52:31 | HH121A | Urban | Asset failure | LV | 1 | 334 | 0.00053396 | 1.6e-06 | No
18/08/2018 | 13:17:07 | MG29 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 202.3774 | 0.078282 | 0.00038681 | No
18/08/2018 | 14:22:38 | NA09 | Rural Long | Asset failure | HV | 270 | 273.8889 | 0.53971 | 0.0019706 | No
18/08/2018 | 14:50:29 | AP226A | Urban | Asset failure | LV | 2 | 255 | 0.00081532 | 3.2e-06 | No
18/08/2018 | 16:05:00 | CV26 | Rural Long | Unknown | Unknown | 1 | 70 | 0.00051088 | 7.3e-06 | No
18/08/2018 | 17:01:51 | AP146C | Urban | Asset failure | LV | 26.6666 | 222 | 0.0094641 | 4.263e-05 | No
18/08/2018 | 17:31:40 | NL111P | Urban | Overloads |  | 1 | 271 | 0.00043324 | 1.6e-06 | No
18/08/2018 | 17:48:15 | NL210A | Urban | Asset failure | LV | 1 | 183 | 0.00029256 | 1.6e-06 | No
18/08/2018 | 17:54:35 | HH522A | Urban | Asset failure | LV | 1 | 265 | 0.00042365 | 1.6e-06 | No
18/08/2018 | 19:04:29 | HH107A | Urban | Third Party | Vehicle impact | 87 | 570 | 0.079278 | 0.00013908 | No
18/08/2018 | 19:47:07 | HH107A | Urban | Unknown | Unknown | 33 | 437 | 0.023054 | 5.276e-05 | No
18/08/2018 | 19:51:05 | SM350D | Urban | Overloads |  | 1 | 159 | 0.00025419 | 1.6e-06 | No
19/08/2018 | 01:54:43 | EL10 | Urban | Asset failure | LV | 1 | 534 | 0.00085369 | 1.6e-06 | No
19/08/2018 | 07:36:59 | KA02 | Rural Short | Asset failure | HV | 791 | 210 | 1.2375 | 0.0058931 | No
19/08/2018 | 07:46:58 | AP355D | Urban | Planned |  | 1 | 354 | 0.00056593 | 1.6e-06 | No
19/08/2018 | 07:52:17 | NL111Q | Urban | Overloads |  | 1 | 195 | 0.00031174 | 1.6e-06 | No
19/08/2018 | 08:43:34 | NU13 | Rural Long | Planned |  | 5 | 236 | 0.008612 | 3.649e-05 | No
19/08/2018 | 08:44:52 | AP146B | Urban | Planned |  | 79 | 410 | 0.051781 | 0.0001263 | No
19/08/2018 | 08:46:23 | AP146B | Urban | Planned |  | 1 | 22 | 3.517e-05 | 1.6e-06 | No
19/08/2018 | 09:09:26 | SA17 | Urban | Planned |  | 25 | 151 | 0.006035 | 3.997e-05 | No
19/08/2018 | 09:14:36 | MTB13 | Rural Short | Asset failure | HV | 1 | 345 | 0.0025703 | 7.45e-06 | No
19/08/2018 | 09:55:36 | W28 | Rural Long | Planned |  | 17 | 300 | 0.037222 | 0.00012407 | No
19/08/2018 | 12:33:56 | SM374B | Urban | Asset failure | LV | 92 | 205 | 0.030151 | 0.00014708 | No
19/08/2018 | 14:12:46 | G28 | Rural Long | Unknown | Unknown | 40 | 119 | 0.03474 | 0.00029193 | No
19/08/2018 | 16:07:29 | AP146B | Urban | Network business | Network error | 26.3333 | 125 | 0.0052623 | 4.21e-05 | No
19/08/2018 | 16:18:35 | BU05 | Rural Long | Unknown | Unknown | 1 | 21 | 0.00015327 | 7.3e-06 | No
19/08/2018 | 17:37:03 | MG38 | Rural Short | Vegetation | Grow-in - NSP responsibility | 20.3333 | 100 | 0.015149 | 0.00015149 | No
19/08/2018 | 18:55:11 | EL01Q | Urban | Asset failure | LV | 1 | 91 | 0.00014548 | 1.6e-06 | No
19/08/2018 | 19:42:20 | AP149C | Urban | Asset failure | LV | 29.6666 | 201 | 0.0095329 | 4.743e-05 | No
19/08/2018 | 23:19:10 | KI51 | Rural Long | Asset failure | HV | 39 | 1610.4872 | 0.4584 | 0.00028464 | No
20/08/2018 | 06:37:45 | HH121B | Urban | Planned |  | 155 | 109 | 0.02701 | 0.00024779 | No
20/08/2018 | 06:55:13 | AP139C | Urban | Asset failure | HV | 1 | 380 | 0.0006075 | 1.6e-06 | No
20/08/2018 | 07:25:40 | HH121B | Urban | Planned |  | 1 | 159 | 0.00025419 | 1.6e-06 | No
20/08/2018 | 08:18:04 | GU11 | Rural Long | Planned |  | 1 | 95 | 0.00069334 | 7.3e-06 | No
20/08/2018 | 08:36:44 | MV63 | Rural Short | Planned |  | 63 | 243 | 0.11405 | 0.00046936 | No
20/08/2018 | 08:46:24 | NL111B | Urban | Planned |  | 11 | 70 | 0.001231 | 1.759e-05 | No
20/08/2018 | 09:18:48 | MV14 | Rural Short | Planned |  | 9 | 271 | 0.018171 | 6.705e-05 | No
20/08/2018 | 09:40:50 | NU11 | Rural Long | Overloads |  | 1 | 124 | 0.00090499 | 7.3e-06 | No
20/08/2018 | 09:44:52 | PP10 | Urban | Asset failure | LV | 1 | 185 | 0.00029575 | 1.6e-06 | No
20/08/2018 | 09:58:40 | VH51 | Rural Short | Planned |  | 141 | 26 | 0.027312 | 0.0010505 | No
20/08/2018 | 10:09:34 | HH145C | Urban | Planned |  | 96 | 209 | 0.032076 | 0.00015347 | No
20/08/2018 | 10:22:51 | PL08 | Urban | Planned |  | 16 | 147 | 0.0037601 | 2.558e-05 | No
20/08/2018 | 10:44:06 | VH23 | Rural Short | Asset failure | LV | 12 | 135 | 0.012069 | 8.94e-05 | No
20/08/2018 | 11:28:41 | LX43 | Rural Short | Asset failure | LV | 1 | 116 | 0.00086422 | 7.45e-06 | No
20/08/2018 | 11:49:12 | HH496C | Urban | Asset failure | LV | 13 | 113 | 0.0023485 | 2.078e-05 | No
20/08/2018 | 12:26:09 | W28 | Rural Long | Unknown | Unknown | 2 | 228 | 0.003328 | 1.46e-05 | No
20/08/2018 | 12:27:52 | MI33 | Rural Long | Unknown | Unknown | 1 | 9 | 6.569e-05 | 7.3e-06 | No
20/08/2018 | 12:33:37 | LX51 | Rural Short | Asset failure | LV | 1 | 101 | 0.00075247 | 7.45e-06 | No
20/08/2018 | 13:40:01 | LX54 | Rural Short | Unknown | Unknown | 10 | 138 | 0.010281 | 7.45e-05 | No
20/08/2018 | 14:05:00 | KA04 | Rural Long | Third Party | Dig-in | 1892 | 67.1131 | 0.92673 | 0.013808 | No
20/08/2018 | 14:45:41 | SM374D | Urban | Animal | Animal impact | 39 | 160.9231 | 0.010033 | 6.235e-05 | No
20/08/2018 | 16:03:28 | ME347F | Urban | Third Party | Vehicle impact | 7 | 211 | 0.0023612 | 1.119e-05 | No
20/08/2018 | 17:16:52 | HH130B | Urban | Overloads |  | 1 | 343 | 0.00054835 | 1.6e-06 | No
20/08/2018 | 20:08:31 | HH177E | Urban | Vegetation | Grow-in - NSP responsibility | 19.6666 | 126 | 0.0039615 | 3.144e-05 | No
21/08/2018 | 01:09:25 | VH32 | Rural Short | Unknown | Unknown | 107 | 339.9159 | 0.27097 | 0.00079717 | No
21/08/2018 | 06:40:45 | MTB21 | Rural Short | Overloads |  | 1 | 178 | 0.0013261 | 7.45e-06 | No
21/08/2018 | 07:25:51 | LX73 | Rural Long | Unknown | Unknown | 8 | 203 | 0.011853 | 5.839e-05 | No
21/08/2018 | 08:05:28 | HH409F | Urban | Asset failure | LV | 47 | 80 | 0.006011 | 7.514e-05 | No
21/08/2018 | 08:12:18 | NL111C | Urban | Asset failure | LV | 102 | 74 | 0.012067 | 0.00016306 | No
21/08/2018 | 08:14:43 | ST41 | Rural Long | Planned |  | 10 | 116 | 0.0084661 | 7.298e-05 | No
21/08/2018 | 08:18:36 | ST41 | Rural Long | Planned |  | 2 | 20 | 0.00029193 | 1.46e-05 | No
21/08/2018 | 09:03:33 | ST41 | Rural Long | Planned |  | 13 | 147 | 0.013947 | 9.488e-05 | No
21/08/2018 | 09:03:52 | PP08 | Rural Long | Planned |  | 94 | 149 | 0.10222 | 0.00068604 | No
21/08/2018 | 09:05:57 | MV62 | Rural Short | Planned |  | 135 | 215 | 0.21624 | 0.0010058 | No
21/08/2018 | 09:22:14 | VH71 | Rural Short | Planned |  | 55 | 338 | 0.1385 | 0.00040976 | No
21/08/2018 | 09:28:43 | WHY02 | Urban | Other |  | 1.3333 | 104 | 0.00022168 | 2.13e-06 | No
21/08/2018 | 09:36:51 | CN81 | Rural Long | Asset failure | HV | 10 | 259.2 | 0.018917 | 7.298e-05 | No
21/08/2018 | 09:43:27 | MT25 | Rural Long | Planned |  | 24 | 111 | 0.019443 | 0.00017516 | No
21/08/2018 | 10:02:16 | HH432B | Urban | Planned |  | 64 | 168 | 0.017189 | 0.00010232 | No
21/08/2018 | 10:08:27 | SA17 | Urban | Unknown | Unknown | 17.3333 | 66 | 0.0018289 | 2.771e-05 | No
21/08/2018 | 10:32:25 | PA12 | Rural Long | Planned |  | 7 | 62 | 0.0031675 | 5.109e-05 | No
21/08/2018 | 10:50:00 | GA01 | Urban | Asset failure | LV | 1 | 194 | 0.00031014 | 1.6e-06 | No
21/08/2018 | 10:56:50 | HH386C | Urban | Planned |  | 158 | 123 | 0.031069 | 0.00025259 | No
21/08/2018 | 11:21:38 | ST41 | Rural Long | Asset failure | LV | 1.6667 | 187 | 0.0022747 | 1.216e-05 | No
21/08/2018 | 12:20:53 | GA26 | Urban | Asset failure | LV | 1 | 158 | 0.00025259 | 1.6e-06 | No
21/08/2018 | 12:56:43 | SA42 | Urban | Overloads |  | 6.6667 | 243 | 0.0025898 | 1.066e-05 | No
21/08/2018 | 13:09:07 | PA26 | Rural Long | Asset failure | LV | 1 | 44 | 0.00032113 | 7.3e-06 | No
21/08/2018 | 16:17:07 | HH409F | Urban | Asset failure | LV | 1 | 201 | 0.00032133 | 1.6e-06 | No
21/08/2018 | 16:19:53 | HH341G | Urban | Other |  | 2 | 256 | 0.00081852 | 3.2e-06 | No
21/08/2018 | 16:32:02 | AP529E | Urban | Asset failure | LV | 25 | 290 | 0.01159 | 3.997e-05 | No
21/08/2018 | 16:34:19 | HH432F | Urban | Asset failure | LV | 10 | 132 | 0.0021103 | 1.599e-05 | No
21/08/2018 | 17:41:27 | MI14 | Rural Long | Asset failure | HV | 690 | 47.6855 | 0.24014 | 0.0050358 | No
21/08/2018 | 18:46:20 | HH177C | Urban | Overloads |  | 1 | 169 | 0.00027018 | 1.6e-06 | No
21/08/2018 | 23:58:09 | HH145C | Urban | Asset failure | LV | 1 | 123 | 0.00019664 | 1.6e-06 | No
22/08/2018 | 03:38:40 | SG07 | Rural Short | Animal | Animal impact | 82 | 113 | 0.069033 | 0.00061091 | No
22/08/2018 | 08:31:57 | YK17 | Rural Long | Planned |  | 417 | 294 | 0.89476 | 0.0030434 | No
22/08/2018 | 09:00:04 | MT26 | Rural Long | Animal | Animal impact | 87 | 107 | 0.06794 | 0.00063496 | No
22/08/2018 | 09:09:43 | SA31 | Urban | Planned |  | 468 | 344 | 0.25737 | 0.00074818 | No
22/08/2018 | 09:11:22 | SA11 | Urban | Planned |  | 26 | 298 | 0.012387 | 4.157e-05 | No
22/08/2018 | 09:17:55 | NU02 | Rural Long | Planned |  | 45 | 16.4 | 0.0053862 | 0.00032843 | No
22/08/2018 | 09:19:01 | MB03 | Rural Long | Planned |  | 103 | 360 | 0.27062 | 0.00075173 | No
22/08/2018 | 09:28:29 | MT09 | Rural Long | Planned |  | 36 | 135 | 0.03547 | 0.00026274 | No
22/08/2018 | 09:31:35 | GA11 | Rural Short | Planned |  | 40 | 310 | 0.092382 | 0.00029801 | No
22/08/2018 | 10:06:31 | NU06 | Rural Long | Third Party | Other | 1 | 69 | 0.00050359 | 7.3e-06 | No
22/08/2018 | 10:24:02 | SD31100 | Rural Long | Planned |  | 93 | 160 | 0.1086 | 0.00067875 | No
22/08/2018 | 10:35:15 | SM374A / ME200F | Urban | Planned |  | 240 | 241 | 0.092467 | 0.00038368 | No
22/08/2018 | 10:43:35 | G16 | Rural Long | Planned |  | 1 | 780 | 0.0056927 | 7.3e-06 | No
22/08/2018 | 10:53:45 | VH15 | Rural Short | Planned |  | 315 | 338 | 0.79322 | 0.0023468 | No
22/08/2018 | 11:54:15 | PP04 | Rural Short | Asset failure | LV | 1 | 158 | 0.0011771 | 7.45e-06 | No
22/08/2018 | 14:28:59 | AP365A | Urban | Asset failure | LV | 30 | 161 | 0.0077216 | 4.796e-05 | No
22/08/2018 | 15:17:55 | HH177G | Urban | Other |  | 1 | 95 | 0.00015187 | 1.6e-06 | No
22/08/2018 | 15:18:13 | PL06 | Urban | Asset failure | LV | 1 | 207 | 0.00033093 | 1.6e-06 | No
22/08/2018 | 17:40:12 | LX71 | Rural Long | Unknown | Unknown | 14 | 35 | 0.0035762 | 0.00010218 | No
22/08/2018 | 17:41:05 | W21 | Rural Long | Asset failure | HV | 53 | 244 | 0.094382 | 0.00038681 | No
22/08/2018 | 17:59:51 | SD31200 | Rural Long | Weather |  | 544 | 5.3162 | 0.021107 | 0.0039703 | No
22/08/2018 | 18:57:12 | AP139C | Urban | Third Party | Vehicle impact | 38 | 362 | 0.021991 | 6.075e-05 | No
22/08/2018 | 20:03:10 | SG10 | Rural Short | Asset failure | LV | 22.3333 | 14 | 0.0023294 | 0.00016639 | No
22/08/2018 | 20:23:46 | HH428C | Urban | Asset failure | LV | 66 | 70 | 0.0073859 | 0.00010551 | No
22/08/2018 | 23:03:11 | HH522C | Urban | Unknown | Unknown | 11.6667 | 243 | 0.0045322 | 1.865e-05 | No
23/08/2018 | 04:33:34 | HH177B | Urban | Asset failure | LV | 1 | 354 | 0.00056593 | 1.6e-06 | No
23/08/2018 | 06:11:03 | HH118A | Urban | Overloads |  | 1 | 328 | 0.00052437 | 1.6e-06 | No
23/08/2018 | 07:09:49 | LX51 | Rural Short | Overloads |  | 1 | 465 | 0.0034643 | 7.45e-06 | No
23/08/2018 | 07:36:18 | HH386C | Urban | Third Party | Vehicle impact | 1 | 109 | 0.00017426 | 1.6e-06 | No
23/08/2018 | 07:46:56 | HH496A | Urban | Asset failure | LV | 27.6666 | 81 | 0.0035826 | 4.423e-05 | No
23/08/2018 | 08:16:32 | ST41 | Rural Long | Planned |  | 28 | 326 | 0.066619 | 0.00020435 | No
23/08/2018 | 08:21:35 | NL115E | Urban | Other |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
23/08/2018 | 08:26:08 | NL115E | Urban | Other |  | 1 | 91 | 0.00014548 | 1.6e-06 | No
23/08/2018 | 08:53:23 | MG52 | Rural Short | Planned |  | 5 | 225 | 0.0083814 | 3.725e-05 | No
23/08/2018 | 09:23:00 | NU08 | Rural Long | Planned |  | 99 | 341 | 0.24638 | 0.00072254 | No
23/08/2018 | 09:46:40 | VH31 | Rural Short | Planned |  | 808 | 271 | 1.6313 | 0.0060197 | No
23/08/2018 | 09:50:15 | SG14 | Rural Short | Planned |  | 118 | 279 | 0.24527 | 0.00087912 | No
23/08/2018 | 10:05:35 | NL511A | Urban | Planned |  | 53 | 14 | 0.0011862 | 8.473e-05 | No
23/08/2018 | 10:13:40 | HH177A | Urban | Planned |  | 106 | 273 | 0.046262 | 0.00016946 | No
23/08/2018 | 10:13:59 | MV62 | Rural Short | Planned |  | 159 | 203 | 0.24047 | 0.0011846 | No
23/08/2018 | 10:20:46 | MI14 | Rural Long | Planned |  | 125 | 254 | 0.23172 | 0.00091229 | No
23/08/2018 | 10:20:50 | ST41 | Rural Long | Planned |  | 1 | 350 | 0.0025544 | 7.3e-06 | No
23/08/2018 | 10:32:48 | AP373B | Urban | Planned |  | 1 | 247 | 0.00039487 | 1.6e-06 | No
23/08/2018 | 11:06:00 | MTB53 | Rural Long | Unknown | Unknown | 406 | 174.8325 | 0.51805 | 0.0029631 | No
23/08/2018 | 11:06:50 | CM17 | Rural Long | Planned |  | 12 | 140 | 0.012261 | 8.758e-05 | No
23/08/2018 | 11:44:34 | SM172B | Urban | Asset failure | LV | 1 | 92 | 0.00014708 | 1.6e-06 | No
23/08/2018 | 13:27:35 | AP425C | Urban | Asset failure | LV | 1 | 224 | 0.0003581 | 1.6e-06 | No
23/08/2018 | 13:55:25 | SD49500 | Rural Long | Animal | Animal impact | 685 | 212.7591 | 1.0637 | 0.0049994 | No
23/08/2018 | 15:08:40 | YK07 | Rural Long | Asset failure | LV | 2 | 195 | 0.0028464 | 1.46e-05 | No
23/08/2018 | 18:13:24 | EL18 | Urban | Asset failure | LV | 1 | 154 | 0.0002462 | 1.6e-06 | No
23/08/2018 | 20:55:20 | HH121C | Urban | Vegetation | Grow-in - NSP responsibility | 16.3333 | 84 | 0.0021934 | 2.611e-05 | No
23/08/2018 | 21:43:33 | AP351E | Urban | Planned |  | 251 | 316 | 0.1268 | 0.00040127 | No
23/08/2018 | 22:12:27 | CBD366A | CBD | Planned |  | 1 | 3 | 0.00058235 | 0.00019412 | No
23/08/2018 | 22:12:27 | CBD366A | CBD | Planned |  | 0 | 4621 | 0.89702 | 0 | No
24/08/2018 | 01:13:23 | ME347G | Urban | Asset failure | LV | 66 | 86 | 0.0090741 | 0.00010551 | No
24/08/2018 | 01:29:16 | AP373G | Urban | Asset failure | LV | 1 | 76 | 0.0001215 | 1.6e-06 | No
24/08/2018 | 04:56:15 | SD34201 | Rural Short | Asset failure | Subtransmission | 18.6667 | 377 | 0.052429 | 0.00013907 | No
24/08/2018 | 07:01:43 | NL111A | Urban | Planned |  | 11 | 66 | 0.0011606 | 1.759e-05 | No
24/08/2018 | 07:30:27 | MB23 | Rural Short | Asset failure | LV | 1 | 69 | 0.00051406 | 7.45e-06 | No
24/08/2018 | 08:23:07 | M92 | Rural Long | Planned |  | 42 | 127 | 0.038929 | 0.00030653 | No
24/08/2018 | 08:27:00 | MB92 | Rural Long | Planned |  | 13 | 137 | 0.012998 | 9.488e-05 | No
24/08/2018 | 08:29:10 | KI51 | Rural Long | Unknown | Unknown | 3 | 381 | 0.008342 | 2.19e-05 | No
24/08/2018 | 08:34:56 | EL13 | Urban | Asset failure | LV | 2 | 162 | 0.00051797 | 3.2e-06 | No
24/08/2018 | 08:42:39 | YK05 | Rural Long | Planned |  | 2 | 94 | 0.0013721 | 1.46e-05 | No
24/08/2018 | 08:43:25 | YK12 | Rural Long | Planned |  | 78 | 220 | 0.12524 | 0.00056927 | No
24/08/2018 | 08:59:37 | NL234A | Urban | Planned |  | 112 | 118 | 0.021128 | 0.00017905 | No
24/08/2018 | 09:05:14 | CV22 | Rural Long | Planned |  | 46 | 266 | 0.089302 | 0.00033572 | No
24/08/2018 | 09:12:10 | MTB32 | Rural Long | Planned |  | 27 | 319 | 0.062861 | 0.00019706 | No
24/08/2018 | 09:41:33 | HH386B | Urban | Planned |  | 227 | 241.8458 | 0.087766 | 0.0003629 | No
24/08/2018 | 09:45:21 | MTB32 | Rural Long | Planned |  | 4 | 71 | 0.0020727 | 2.919e-05 | No
24/08/2018 | 09:56:13 | SM179D | Urban | Asset failure | LV | 1 | 320 | 0.00051158 | 1.6e-06 | No
24/08/2018 | 10:29:18 | HH148B | Urban | Asset failure | LV | 28 | 139 | 0.006222 | 4.476e-05 | No
24/08/2018 | 10:29:59 | HH148B | Urban | Asset failure | LV | 68 | 138 | 0.015002 | 0.00010871 | No
24/08/2018 | 10:34:29 | HH341A | Urban | Planned |  | 1 | 45 | 7.194e-05 | 1.6e-06 | No
24/08/2018 | 11:02:32 | HH148B | Urban | Planned |  | 1 | 45 | 7.194e-05 | 1.6e-06 | No
24/08/2018 | 11:16:42 | HH148B | Urban | Planned |  | 76 | 86 | 0.010449 | 0.0001215 | No
24/08/2018 | 11:30:33 | NL451A | Urban | Asset failure | LV | 1 | 129 | 0.00020623 | 1.6e-06 | No
24/08/2018 | 11:58:41 | PL06 | Urban | Unknown | Unknown | 2 | 196 | 0.00062668 | 3.2e-06 | No
24/08/2018 | 12:53:11 | PL03 | Urban | Unknown | Unknown | 17.3333 | 146 | 0.0040457 | 2.771e-05 | No
24/08/2018 | 13:56:44 | NL451A | Urban | Asset failure | LV | 1 | 197 | 0.00031494 | 1.6e-06 | No
24/08/2018 | 18:53:34 | NL115D | Urban | Unknown | Unknown | 31.3333 | 206 | 0.010319 | 5.009e-05 | No
24/08/2018 | 20:46:20 | WHY01 | Urban | Overloads |  | 1 | 91 | 0.00014548 | 1.6e-06 | No
24/08/2018 | 21:46:08 | NL115D | Urban | Unknown | Unknown | 996.0005 | 1.0187 | 0.0016221 | 0.0015923 | No
25/08/2018 | 00:58:31 | NL115D | Urban | Animal | Animal impact | 1 | 521 | 0.00083291 | 1.6e-06 | No
25/08/2018 | 03:16:30 | AP424A | Urban | Asset failure | LV | 1 | 193 | 0.00030854 | 1.6e-06 | No
25/08/2018 | 03:34:00 | GU32 | Rural Long | Asset failure | HV | 1068 | 220.1798 | 1.7162 | 0.0077946 | No
25/08/2018 | 07:31:00 | SA43 | Urban | Planned |  | 1 | 449 | 0.00071781 | 1.6e-06 | No
25/08/2018 | 08:18:46 | CBD412F | Urban | Planned |  | 25 | 175 | 0.0069942 | 3.997e-05 | No
25/08/2018 | 08:56:36 | SA12 | Urban | Planned |  | 1 | 897 | 0.001434 | 1.6e-06 | No
25/08/2018 | 09:20:54 | BM31 | Rural Short | Asset failure | LV | 1 | 178 | 0.0013261 | 7.45e-06 | No
25/08/2018 | 09:32:41 | CBD412F | Urban | Planned |  | 2 | 213 | 0.00068104 | 3.2e-06 | No
25/08/2018 | 09:58:06 | HH522B | Urban | Asset failure | LV | 1 | 238 | 0.00038048 | 1.6e-06 | No
25/08/2018 | 12:08:24 | PL03 | Urban | Unknown | Unknown | 2 | 479 | 0.0015315 | 3.2e-06 | No
25/08/2018 | 12:23:51 | AP355F | Urban | Overloads |  | 1 | 140 | 0.00022381 | 1.6e-06 | No
25/08/2018 | 13:05:52 | HH496F | Urban | Asset failure | LV | 1 | 596 | 0.00095281 | 1.6e-06 | No
25/08/2018 | 14:02:00 | SB01 | Rural Long | Asset failure | HV | 8.6667 | 106.3077 | 0.0067242 | 6.325e-05 | No
25/08/2018 | 15:18:15 | HH107C | Urban | Asset failure | HV | 2439 | 211.0431 | 0.82289 | 0.0038992 | No
25/08/2018 | 15:19:23 | HH107C | Urban | Overloads |  | 7 | 328 | 0.0036706 | 1.119e-05 | No
25/08/2018 | 18:36:33 | SM349D | Urban | Asset failure | LV | 1 | 274 | 0.00043804 | 1.6e-06 | No
25/08/2018 | 19:29:44 | SA17 | Urban | Overloads |  | 1 | 281 | 0.00044923 | 1.6e-06 | No
25/08/2018 | 20:06:35 | SM349F | Urban | Asset failure | LV | 1 | 238 | 0.00038048 | 1.6e-06 | No
25/08/2018 | 20:27:52 | MI33 | Rural Long | Asset failure | HV | 2291 | 2.8581 | 0.04779 | 0.01672 | No
25/08/2018 | 21:03:57 | SM137B | Urban | Asset failure | LV | 1 | 241 | 0.00038528 | 1.6e-06 | No
25/08/2018 | 21:41:00 | MTB62 | Rural Short | Unknown | Unknown | 17 | 114 | 0.014438 | 0.00012665 | No
25/08/2018 | 23:32:57 | PL07 | Urban | Asset failure | LV | 19.3333 | 110 | 0.0033998 | 3.091e-05 | No
26/08/2018 | 04:46:49 | HH107A | Urban | Third Party | Vehicle impact | 502 | 110.7331 | 0.088867 | 0.00080253 | No
26/08/2018 | 05:38:33 | MG02 | Rural Long | Asset failure | HV | 20 | 15 | 0.0021895 | 0.00014597 | No
26/08/2018 | 08:03:07 | BM34 | Rural Short | Unknown | Unknown | 2.6667 | 60 | 0.001192 | 1.987e-05 | No
26/08/2018 | 08:12:13 | SG13 | Rural Short | Asset failure | LV | 1 | 281 | 0.0020935 | 7.45e-06 | No
26/08/2018 | 08:14:25 | YK17 | Rural Long | Planned |  | 1214 | 392.6194 | 3.4787 | 0.0088602 | No
26/08/2018 | 08:20:40 | EL16 | Urban | Planned |  | 16 | 431 | 0.011024 | 2.558e-05 | No
26/08/2018 | 08:40:02 | SM411F | Urban | Asset failure | LV | 19.6666 | 116 | 0.0036471 | 3.144e-05 | No
26/08/2018 | 09:30:30 | GA800A | Rural Short | Planned |  | 148 | 307 | 0.3385 | 0.0011026 | No
26/08/2018 | 10:57:42 | SD35200 | Rural Long | Overloads |  | 1 | 209 | 0.0015253 | 7.3e-06 | No
26/08/2018 | 12:10:03 | G36 | Rural Short | Unknown | Unknown | 1 | 46 | 0.00034271 | 7.45e-06 | No
26/08/2018 | 17:46:08 | KA05 | Rural Long | Asset failure | LV | 14 | 71 | 0.0072545 | 0.00010218 | No
26/08/2018 | 18:05:40 | HH432D | Urban | Asset failure | LV | 24 | 121 | 0.0046425 | 3.837e-05 | No
26/08/2018 | 20:46:59 | NL115A | Urban | Asset failure | HV | 12.6667 | 132 | 0.002673 | 2.025e-05 | No
27/08/2018 | 00:16:57 | MTB11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 101 | 164.5248 | 0.1238 | 0.00075247 | No
27/08/2018 | 07:25:36 | VH11 | Urban | Asset failure | LV | 1 | 138 | 0.00022062 | 1.6e-06 | No
27/08/2018 | 07:36:57 | EL10 | Urban | Asset failure | LV | 14.3333 | 213 | 0.0048807 | 2.291e-05 | No
27/08/2018 | 07:53:52 | NU35 | Rural Long | Asset failure | LV | 2 | 139 | 0.0020289 | 1.46e-05 | No
27/08/2018 | 08:10:01 | PL07 | Urban | Asset failure | LV | 19.3333 | 94 | 0.0029053 | 3.091e-05 | No
27/08/2018 | 08:42:51 | ST42 | Rural Long | Planned |  | 1 | 237 | 0.0017297 | 7.3e-06 | No
27/08/2018 | 08:53:00 | GA22 | Rural Short | Planned |  | 1 | 47 | 0.00035016 | 7.45e-06 | No
27/08/2018 | 09:05:44 | YK03 | Rural Long | Planned |  | 63 | 116 | 0.053336 | 0.0004598 | No
27/08/2018 | 09:09:28 | SG01 | Rural Short | Planned |  | 284 | 232.1972 | 0.49129 | 0.0021158 | No
27/08/2018 | 09:24:11 | CM28 | Rural Long | Planned |  | 2 | 40 | 0.00058387 | 1.46e-05 | No
27/08/2018 | 09:25:52 | VH44 | Rural Short | Planned |  | 3 | 129 | 0.0028832 | 2.235e-05 | No
27/08/2018 | 09:29:08 | SG10 | Rural Short | Unknown | Unknown | 1 | 111 | 0.00082697 | 7.45e-06 | No
27/08/2018 | 09:32:34 | ME131D | Urban | Planned |  | 1 | 261 | 0.00041725 | 1.6e-06 | No
27/08/2018 | 09:47:18 | SM402D | Urban | Planned |  | 97 | 304 | 0.047142 | 0.00015507 | No
27/08/2018 | 09:54:06 | GA25 | Rural Short | Planned |  | 202 | 148 | 0.22273 | 0.0015049 | No
27/08/2018 | 09:56:22 | NL111P | Urban | Planned |  | 55 | 83 | 0.007298 | 8.793e-05 | No
27/08/2018 | 10:19:30 | NL111P | Urban | Planned |  | 143 | 294 | 0.067211 | 0.00022861 | No
27/08/2018 | 10:24:09 | HH496D | Urban | Asset failure | LV | 19 | 226 | 0.0068647 | 3.037e-05 | No
27/08/2018 | 10:26:48 | LM13 | Rural Long | Planned |  | 81 | 226 | 0.1336 | 0.00059117 | No
27/08/2018 | 10:30:08 | M23 | Rural Long | Planned |  | 1 | 53 | 0.00038681 | 7.3e-06 | No
27/08/2018 | 10:36:31 | SD38100 | Rural Long | Planned |  | 44 | 194 | 0.062299 | 0.00032113 | No
27/08/2018 | 10:37:41 | LX75 | Rural Long | Planned |  | 8 | 182 | 0.010626 | 5.839e-05 | No
27/08/2018 | 10:53:41 | MV61 | Urban | Planned |  | 601 | 219 | 0.21042 | 0.0009608 | No
27/08/2018 | 11:49:51 | MI33 | Rural Long | Asset failure | HV | 1 | 112 | 0.00081741 | 7.3e-06 | No
27/08/2018 | 12:01:52 | EL20 | Urban | Overloads |  | 1 | 169 | 0.00027018 | 1.6e-06 | No
27/08/2018 | 12:38:58 | KA12 | Rural Long | Planned |  | 36 | 131 | 0.034419 | 0.00026274 | No
27/08/2018 | 12:41:39 | SM137B | Urban | Asset failure | LV | 14.3333 | 154 | 0.0035288 | 2.291e-05 | No
27/08/2018 | 14:09:57 | SM216D | Urban | Asset failure | LV | 42.6666 | 154 | 0.010504 | 6.821e-05 | No
27/08/2018 | 14:37:12 | NL760A | Urban | Animal | Animal impact | 1 | 577 | 0.00092244 | 1.6e-06 | No
27/08/2018 | 15:14:49 | NL115D | Urban | Overloads |  | 31.3333 | 193 | 0.0096677 | 5.009e-05 | No
27/08/2018 | 21:34:08 | NL451E | Urban | Asset failure | LV | 13.6667 | 189 | 0.0041294 | 2.185e-05 | No
27/08/2018 | 22:13:13 | AP351E | Urban | Planned |  | 4 | 276 | 0.0017649 | 6.39e-06 | No
28/08/2018 | 05:25:35 | SA33 | Urban | Overloads |  | 20.6666 | 205 | 0.0067731 | 3.304e-05 | No
28/08/2018 | 06:42:09 | HH403A | Urban | Overloads |  | 1 | 243 | 0.00038848 | 1.6e-06 | No
28/08/2018 | 08:20:44 | W28 | Rural Long | Planned |  | 17 | 384 | 0.047644 | 0.00012407 | No
28/08/2018 | 08:29:40 | EL10 | Urban | Overloads |  | 1 | 90 | 0.00014388 | 1.6e-06 | No
28/08/2018 | 08:55:16 | HH341D | Urban | Planned |  | 68 | 313 | 0.034026 | 0.00010871 | No
28/08/2018 | 09:45:16 | PP16 | Rural Short | Planned |  | 2 | 121 | 0.0018029 | 1.49e-05 | No
28/08/2018 | 09:46:26 | MTB54 | Rural Long | Planned |  | 62 | 284 | 0.12851 | 0.0004525 | No
28/08/2018 | 09:47:47 | VH16 | Rural Short | Planned |  | 45 | 333 | 0.11164 | 0.00033526 | No
28/08/2018 | 10:06:50 | MV51 | Rural Short | Planned |  | 64 | 82.125 | 0.039158 | 0.00047681 | No
28/08/2018 | 10:12:41 | KI53 | Rural Long | Planned |  | 1 | 93 | 0.00067875 | 7.3e-06 | No
28/08/2018 | 10:35:05 | MT02 | Rural Long | Planned |  | 133 | 115 | 0.11163 | 0.00097068 | No
28/08/2018 | 10:59:04 | ST15 | Rural Short | Planned |  | 87 | 290 | 0.18797 | 0.00064816 | No
28/08/2018 | 11:11:20 | NL111Q | Urban | Planned |  | 65 | 135 | 0.014028 | 0.00010391 | No
28/08/2018 | 11:45:49 | SM350H | Urban | Other |  | 65 | 120 | 0.01247 | 0.00010391 | No
28/08/2018 | 12:14:30 | SM350C | Urban | Planned |  | 104 | 137 | 0.022778 | 0.00016626 | No
28/08/2018 | 13:19:32 | MG17 | Rural Long | Asset failure | LV | 9 | 71 | 0.0046636 | 6.568e-05 | No
28/08/2018 | 15:35:33 | CD01 | Rural Short | Overloads |  | 1 | 50 | 0.00037251 | 7.45e-06 | No
28/08/2018 | 18:05:23 | MG26 | Rural Long | Unknown | Unknown | 11 | 157 | 0.012604 | 8.028e-05 | No
28/08/2018 | 18:09:07 | SM374C | Urban | Asset failure | LV | 1 | 179 | 0.00028616 | 1.6e-06 | No
28/08/2018 | 18:56:29 | VH11 | Urban | Asset failure | LV | 1 | 103 | 0.00016466 | 1.6e-06 | No
28/08/2018 | 19:01:01 | AP424A | Urban | Asset failure | LV | 1 | 185 | 0.00029575 | 1.6e-06 | No
28/08/2018 | 19:05:23 | HH121E | Urban | Asset failure | LV | 14.6667 | 219 | 0.0051349 | 2.345e-05 | No
28/08/2018 | 20:04:42 | SM410B | Urban | Asset failure | LV | 2 | 117 | 0.00037409 | 3.2e-06 | No
28/08/2018 | 22:52:33 | CBD353M | CBD | Planned |  | 37 | 4 | 0.02873 | 0.0071824 | No
28/08/2018 | 22:52:33 | CBD353M | CBD | Planned |  | 0 | 2 | 0.014365 | 0 | No
29/08/2018 | 04:05:28 | HH386D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 137 | 190 | 0.041614 | 0.00021902 | No
29/08/2018 | 06:29:17 | HH145E | Urban | Asset failure | LV | 1 | 358 | 0.00057233 | 1.6e-06 | No
29/08/2018 | 08:05:42 | SD32200 | Rural Long | Unknown | Unknown | 2 | 918 | 0.0134 | 1.46e-05 | No
29/08/2018 | 08:37:22 | GU32 | Rural Long | Asset failure | LV | 1 | 173 | 0.0012626 | 7.3e-06 | No
29/08/2018 | 08:38:38 | NL21 | Urban | Unknown | Unknown | 1 | 186 | 0.00029735 | 1.6e-06 | No
29/08/2018 | 08:46:42 | M13 | Rural Long | Asset failure | LV | 7 | 245 | 0.012517 | 5.109e-05 | No
29/08/2018 | 08:57:14 | NU02 | Rural Long | Planned |  | 7 | 152 | 0.0077654 | 5.109e-05 | No
29/08/2018 | 09:10:15 | GU118 | Rural Long | Planned |  | 2 | 59 | 0.0008612 | 1.46e-05 | No
29/08/2018 | 09:11:45 | ST16 | Rural Short | Planned |  | 51 | 256 | 0.097269 | 0.00037996 | No
29/08/2018 | 09:18:46 | SB19 | Rural Long | Planned |  | 55 | 303 | 0.12163 | 0.00040141 | No
29/08/2018 | 09:29:09 | HH130A | Urban | Planned |  | 1 | 250 | 0.00039967 | 1.6e-06 | No
29/08/2018 | 09:33:16 | BT37 | Rural Long | Planned |  | 6 | 264 | 0.011561 | 4.379e-05 | No
29/08/2018 | 10:14:09 | MV52 | Rural Short | Planned |  | 31 | 117 | 0.027022 | 0.00023095 | No
29/08/2018 | 10:18:23 | CL20 | Rural Long | Planned |  | 102 | 206 | 0.15335 | 0.00074443 | No
29/08/2018 | 10:38:46 | AP214A | Urban | Asset failure | LV | 38 | 112 | 0.006804 | 6.075e-05 | No
29/08/2018 | 10:39:19 | EL01N | Urban | Planned |  | 28 | 4 | 0.00017905 | 4.476e-05 | No
29/08/2018 | 11:44:18 | SD40101 | Rural Long | Planned |  | 1207 | 55.7796 | 0.49137 | 0.0088091 | No
29/08/2018 | 12:26:44 | NL111B | Urban | Asset failure | LV | 2 | 126 | 0.00040287 | 3.2e-06 | No
29/08/2018 | 14:45:12 | KA10 | Rural Long | Unknown | Unknown | 2 | 6 | 8.758e-05 | 1.46e-05 | No
29/08/2018 | 16:26:48 | WHY12 | Urban | Asset failure | LV | 14 | 55 | 0.001231 | 2.238e-05 | No
29/08/2018 | 16:42:27 | MV31 | Rural Short | Planned |  | 306 | 165 | 0.37616 | 0.0022798 | No
29/08/2018 | 16:46:00 | ST36 | Rural Long | Unknown | Unknown | 1 | 314 | 0.0022917 | 7.3e-06 | No
29/08/2018 | 18:16:12 | KA13 | Rural Long | Asset failure | HV | 54 | 201.037 | 0.079231 | 0.00039411 | No
29/08/2018 | 18:21:01 | SA19 | Urban | Overloads |  | 1 | 199 | 0.00031814 | 1.6e-06 | No
29/08/2018 | 18:27:35 | NL451C | Urban | Asset failure | LV | 1 | 123 | 0.00019664 | 1.6e-06 | No
29/08/2018 | 20:14:28 | R09 | Rural Long | Asset failure | LV | 1 | 171 | 0.001248 | 7.3e-06 | No
29/08/2018 | 23:39:19 | AP227A | Urban | Asset failure | LV | 30.3333 | 91 | 0.0044129 | 4.849e-05 | No
30/08/2018 | 01:11:05 | MV32 | Rural Short | Asset failure | HV | 13 | 289 | 0.02799 | 9.685e-05 | No
30/08/2018 | 01:50:18 | HH121C | Urban | Unknown | Unknown | 52.6667 | 126 | 0.010609 | 8.42e-05 | No
30/08/2018 | 02:29:20 | NL511A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 175 | 0.00027977 | 1.6e-06 | No
30/08/2018 | 03:05:52 | NL115F | Urban | Weather |  | 74 | 199 | 0.023542 | 0.0001183 | No
30/08/2018 | 03:41:59 | HH409D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1252 | 37 | 0.074057 | 0.0020015 | No
30/08/2018 | 03:56:21 | ME116C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1595 | 62 | 0.15809 | 0.0025499 | No
30/08/2018 | 06:37:39 | HH177E | Urban | Vegetation | Grow-in - NSP responsibility | 13.6667 | 141 | 0.0030806 | 2.185e-05 | No
30/08/2018 | 06:40:42 | AP373E | Urban | Unknown | Unknown | 2 | 186 | 0.00059471 | 3.2e-06 | No
30/08/2018 | 07:08:22 | HH496D | Urban | Asset failure | LV | 1 | 351 | 0.00056113 | 1.6e-06 | No
30/08/2018 | 07:29:51 | CV15 | Rural Long | Unknown | Unknown | 59 | 290.5763 | 0.12512 | 0.0004306 | No
30/08/2018 | 08:04:07 | CV07 | Rural Short | Unknown | Unknown | 13 | 219 | 0.021211 | 9.685e-05 | No
30/08/2018 | 08:17:41 | NL111P | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 135 | 0.00021582 | 1.6e-06 | No
30/08/2018 | 08:31:52 | YK25 | Rural Long | Planned |  | 325 | 166 | 0.39375 | 0.002372 | No
30/08/2018 | 08:51:20 | SD32301 | Rural Long | Planned |  | 1 | 417 | 0.0030434 | 7.3e-06 | No
30/08/2018 | 08:55:52 | VH21 | Rural Short | Asset failure | LV | 1 | 74 | 0.00055131 | 7.45e-06 | No
30/08/2018 | 08:56:00 | GA800A | Rural Short | Planned |  | 71 | 308 | 0.16292 | 0.00052896 | No
30/08/2018 | 09:14:51 | MI14 | Rural Long | Planned |  | 157 | 223 | 0.25552 | 0.0011458 | No
30/08/2018 | 09:17:31 | MTB32 | Rural Long | Planned |  | 222 | 372 | 0.60273 | 0.0016202 | No
30/08/2018 | 09:26:53 | AP372A | Urban | Planned |  | 1 | 102 | 0.00016306 | 1.6e-06 | No
30/08/2018 | 09:28:49 | MV13 | Rural Short | Planned |  | 2 | 74 | 0.0011026 | 1.49e-05 | No
30/08/2018 | 09:32:56 | MV62 | Rural Short | Asset failure | LV | 1 | 204 | 0.0015198 | 7.45e-06 | No
30/08/2018 | 09:38:07 | HH341C | Urban | Planned |  | 314 | 111 | 0.05572 | 0.00050198 | No
30/08/2018 | 09:40:58 | HH121G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 95 | 0.00030375 | 3.2e-06 | No
30/08/2018 | 09:52:16 | SD37102 | Rural Long | Planned |  | 1 | 15 | 0.00010948 | 7.3e-06 | No
30/08/2018 | 10:13:18 | PP12 | Rural Long | Asset failure | HV | 31 | 234 | 0.052942 | 0.00022625 | No
30/08/2018 | 10:18:47 | GU32 | Rural Long | Planned |  | 124 | 288 | 0.26064 | 0.00090499 | No
30/08/2018 | 10:21:10 | SM350C | Urban | Planned |  | 74 | 273 | 0.032296 | 0.0001183 | No
30/08/2018 | 10:28:24 | EL10 | Urban | Planned |  | 207 | 238 | 0.07876 | 0.00033093 | No
30/08/2018 | 10:33:25 | SM350H | Urban | Planned |  | 91 | 89 | 0.012948 | 0.00014548 | No
30/08/2018 | 10:46:24 | G41 | Rural Long | Unknown | Unknown | 4 | 424 | 0.012378 | 2.919e-05 | No
30/08/2018 | 10:53:00 | SG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 549 | 120 | 0.49082 | 0.0040901 | No
30/08/2018 | 10:54:12 | SA20 | Urban | Planned |  | 36 | 135 | 0.0077696 | 5.755e-05 | No
30/08/2018 | 10:59:17 | MTB54 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 465 | 2 | 0.0067875 | 0.0033937 | No
30/08/2018 | 11:00:22 | SM126E | Urban | Planned |  | 40 | 86 | 0.0054994 | 6.395e-05 | No
30/08/2018 | 11:01:00 | KA27 | Rural Long | Asset failure | HV | 242 | 274 | 0.48394 | 0.0017662 | No
30/08/2018 | 11:01:00 | HH118C | Urban | Unknown | Unknown | 187 | 104 | 0.031091 | 0.00029895 | No
30/08/2018 | 11:01:26 | GA27 | Rural Long | Asset failure | HV | 463 | 125.0691 | 0.42262 | 0.0033791 | No
30/08/2018 | 11:26:00 | EL15 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 292 | 406.4897 | 0.18975 | 0.00046681 | No
30/08/2018 | 11:27:01 | G15 | Rural Long | Third Party | Other | 1 | 265 | 0.0019341 | 7.3e-06 | No
30/08/2018 | 11:32:00 | HH130A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1953 | 120.1234 | 0.37505 | 0.0031222 | No
30/08/2018 | 11:36:18 | AP146B | Urban | Vegetation | Grow-in - NSP responsibility | 2381 | 120.827 | 0.45992 | 0.0038064 | No
30/08/2018 | 11:37:40 | HH409C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2477 | 63.8692 | 0.25292 | 0.0039599 | No
30/08/2018 | 11:38:48 | AP146B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 192 | 0.00030695 | 1.6e-06 | No
30/08/2018 | 11:39:00 | HH121B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 4077 | 127.1011 | 0.82842 | 0.0065178 | No
30/08/2018 | 11:40:21 | HH341B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 846 | 184.7683 | 0.2499 | 0.0013525 | No
30/08/2018 | 11:40:44 | SM126C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 18 | 59 | 0.0016978 | 2.878e-05 | No
30/08/2018 | 11:46:10 | AP146C | Urban | Unknown | Unknown | 26.6666 | 193 | 0.0082278 | 4.263e-05 | No
30/08/2018 | 11:47:00 | HH341K | Urban | Unknown | Unknown | 1945 | 467.0776 | 1.4523 | 0.0031094 | No
30/08/2018 | 11:56:38 | SM172B | Urban | Vegetation | Grow-in - NSP responsibility | 94 | 217 | 0.03261 | 0.00015028 | No
30/08/2018 | 11:57:00 | SM137A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1819 | 84.5201 | 0.24578 | 0.002908 | No
30/08/2018 | 11:58:31 | ME427A | Urban | Weather |  | 1 | 162 | 0.00025899 | 1.6e-06 | No
30/08/2018 | 11:58:33 | HH341J | Urban | Other |  | 15.3333 | 541 | 0.013262 | 2.451e-05 | No
30/08/2018 | 12:01:19 | HH341E | Urban | Weather |  | 3346 | 177.9474 | 0.95187 | 0.0053492 | No
30/08/2018 | 12:04:31 | MV13 | Rural Short | Third Party | Other | 473 | 95 | 0.33477 | 0.0035239 | No
30/08/2018 | 12:04:34 | SM137A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 87 | 0.00013908 | 1.6e-06 | No
30/08/2018 | 12:05:00 | SM172E | Urban | Weather |  | 1170 | 103.3333 | 0.19328 | 0.0018705 | No
30/08/2018 | 12:06:30 | SM350F | Urban | Unknown | Unknown | 57 | 306 | 0.027884 | 9.112e-05 | No
30/08/2018 | 12:07:59 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 145 | 110 | 0.11883 | 0.0010803 | No
30/08/2018 | 12:19:45 | SM349D | Urban | Vegetation | Grow-in - NSP responsibility | 54 | 178 | 0.015366 | 8.633e-05 | No
30/08/2018 | 12:26:17 | SM374A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 34.6666 | 283 | 0.015684 | 5.542e-05 | No
30/08/2018 | 12:27:25 | AP149F | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 352 | 0.00056273 | 1.6e-06 | No
30/08/2018 | 12:32:51 | AP226A | Urban | Unknown | Unknown | 17.3333 | 142 | 0.0039349 | 2.771e-05 | No
30/08/2018 | 12:33:07 | HH102A | Urban | Asset failure | LV | 26.3333 | 327 | 0.013766 | 4.21e-05 | No
30/08/2018 | 12:53:24 | HH432F | Urban | Asset failure | LV | 1 | 394 | 0.00062988 | 1.6e-06 | No
30/08/2018 | 12:54:24 | AP355H | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 254 | 0.00040606 | 1.6e-06 | No
30/08/2018 | 13:14:35 | CV15 | Rural Long | Unknown | Unknown | 59 | 174.4407 | 0.075114 | 0.0004306 | No
30/08/2018 | 13:16:21 | SD31300 | Rural Long | Unknown | Unknown | 7 | 284 | 0.014509 | 5.109e-05 | No
30/08/2018 | 13:20:43 | AP344D | Urban | Asset failure | LV | 1 | 53 | 8.473e-05 | 1.6e-06 | No
30/08/2018 | 13:34:40 | SA11 | Urban | Third Party | Other | 1 | 268 | 0.00042844 | 1.6e-06 | No
30/08/2018 | 13:40:09 | MB32 | Rural Long | Planned |  | 1 | 10 | 7.298e-05 | 7.3e-06 | No
30/08/2018 | 13:43:09 | WK41 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 547 | 58 | 0.23636 | 0.0040752 | No
30/08/2018 | 13:44:29 | NU21 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 2311 | 150.2518 | 2.5342 | 0.016866 | No
30/08/2018 | 13:45:04 | NU15 | Rural Long | Unknown | Unknown | 20.3333 | 214 | 0.031758 | 0.0001484 | No
30/08/2018 | 14:00:16 | HH102D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 25 | 527 | 0.021063 | 3.997e-05 | No
30/08/2018 | 14:16:00 | SM126D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 59 | 28 | 0.002641 | 9.432e-05 | No
30/08/2018 | 14:35:23 | KA13 | Rural Long | Asset failure | HV | 54 | 54.5185 | 0.021486 | 0.00039411 | No
30/08/2018 | 15:00:00 | NU04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 458 | 73.1703 | 0.24967 | 0.0034122 | No
30/08/2018 | 15:26:37 | WK33 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 315 | 0.0023468 | 7.45e-06 | No
30/08/2018 | 15:50:39 | VH23 | Rural Short | Animal | Animal impact | 1 | 224 | 0.0016688 | 7.45e-06 | No
30/08/2018 | 15:54:14 | CBD353L | Urban | Other |  | 6 | 171 | 0.0016402 | 9.59e-06 | No
30/08/2018 | 15:56:47 | NL544B | Urban | Third Party | Vehicle impact | 1696 | 65.0218 | 0.1763 | 0.0027113 | No
30/08/2018 | 15:58:47 | BM44 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 951 | 64 | 0.45345 | 0.0070851 | No
30/08/2018 | 16:10:33 | SA11 | Urban | Third Party | Other | 1 | 111 | 0.00017745 | 1.6e-06 | No
30/08/2018 | 16:25:50 | BM43 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 50 | 0.00074501 | 1.49e-05 | No
30/08/2018 | 16:35:15 | CBD103A | Urban | Asset failure | HV | 278 | 80.3237 | 0.035698 | 0.00044443 | No
30/08/2018 | 16:38:41 | HH121F | Urban | Asset failure | LV | 57 | 191 | 0.017405 | 9.112e-05 | No
30/08/2018 | 16:51:29 | AP132B | Urban | Asset failure | LV | 1 | 336 | 0.00053715 | 1.6e-06 | No
30/08/2018 | 17:13:11 | SM350F | Urban | Unknown | Unknown | 57 | 4 | 0.0003645 | 9.112e-05 | No
30/08/2018 | 17:21:01 | EL11 | Urban | Unknown | Unknown | 31 | 18 | 0.00089206 | 4.956e-05 | No
30/08/2018 | 17:36:50 | MG04 | Rural Short | Other |  | 2 | 352 | 0.0052449 | 1.49e-05 | No
30/08/2018 | 17:46:42 | HH121G | Urban | Weather |  | 21.3333 | 109 | 0.0037175 | 3.411e-05 | No
30/08/2018 | 18:05:32 | WK23 | Rural Short | Asset failure | LV | 1 | 213 | 0.0015869 | 7.45e-06 | No
30/08/2018 | 20:02:00 | G14 | Rural Long | Asset failure | HV | 11 | 324.1818 | 0.026026 | 8.028e-05 | No
30/08/2018 | 20:05:38 | CV15 | Rural Long | Unknown | Unknown | 59 | 336 | 0.14468 | 0.0004306 | No
30/08/2018 | 20:25:17 | EL260A | Urban | Weather |  | 2506 | 269.4425 | 1.0795 | 0.0040063 | No
30/08/2018 | 20:25:17 | EL260A | Urban | Weather |  | 0 | 100 | 0.14052 | 0 | No
30/08/2018 | 20:28:00 | MG04 | Rural Short | Asset failure | Distribution substation | 2 | 120 | 0.001788 | 1.49e-05 | No
30/08/2018 | 21:20:06 | SA33 | Urban | Asset failure | LV | 1 | 216 | 0.00034531 | 1.6e-06 | No
30/08/2018 | 23:35:50 | LX33 | Rural Short | Unknown | Unknown | 65 | 65.8 | 0.031864 | 0.00048426 | No
31/08/2018 | 06:43:36 | SG07 | Rural Short | Vegetation | Grow-in - NSP responsibility | 2 | 167 | 0.0024883 | 1.49e-05 | No
31/08/2018 | 07:59:00 | SM410A | Urban | Asset failure | LV | 1 | 140 | 0.00022381 | 1.6e-06 | No
31/08/2018 | 08:00:04 | KI31 | Rural Short | Planned |  | 2 | 44 | 0.00065561 | 1.49e-05 | No
31/08/2018 | 09:20:09 | NL111Q | Urban | Planned |  | 142 | 243 | 0.055164 | 0.00022701 | No
31/08/2018 | 09:25:00 | G14 | Rural Long | Unknown | Unknown | 97 | 472.9485 | 0.33482 | 0.00070794 | No
31/08/2018 | 09:30:26 | GU32 | Rural Long | Planned |  | 98 | 272 | 0.19454 | 0.00071524 | No
31/08/2018 | 09:34:55 | SA17 | Urban | Planned |  | 1 | 353 | 0.00056433 | 1.6e-06 | No
31/08/2018 | 09:47:06 | NU13 | Rural Long | Unknown | Unknown | 770 | 110.8571 | 0.62299 | 0.0056197 | No
31/08/2018 | 09:48:20 | MI14 | Rural Long | Planned |  | 61 | 258 | 0.11486 | 0.0004452 | No
31/08/2018 | 09:50:32 | MTB13 | Rural Short | Planned |  | 1 | 215 | 0.0016018 | 7.45e-06 | No
31/08/2018 | 09:55:00 | SA18 | Urban | Planned |  | 35 | 608 | 0.03402 | 5.595e-05 | No
31/08/2018 | 10:20:10 | HH386F | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 439 | 0.00070182 | 1.6e-06 | No
31/08/2018 | 10:34:36 | CBD366E | Urban | Animal | Animal impact | 7 | 271 | 0.0030327 | 1.119e-05 | No
31/08/2018 | 10:49:23 | HH341G | Urban | Planned |  | 274 | 272 | 0.11915 | 0.00043804 | No
31/08/2018 | 10:51:51 | MV63 | Rural Short | Planned |  | 38 | 203 | 0.05747 | 0.00028311 | No
31/08/2018 | 11:24:00 | CL08 | Rural Long | Planned |  | 77 | 721 | 0.40518 | 0.00056197 | No
31/08/2018 | 11:26:56 | WK41 | Rural Short | Planned |  | 5 | 86 | 0.0032036 | 3.725e-05 | No
31/08/2018 | 11:29:55 | EL01Q | Urban | Planned |  | 22 | 36 | 0.0012661 | 3.517e-05 | No
31/08/2018 | 11:50:06 | KI31 | Rural Short | Planned |  | 3 | 66 | 0.0014751 | 2.235e-05 | No
31/08/2018 | 12:07:33 | AP125D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 206 | 0.00032933 | 1.6e-06 | No
31/08/2018 | 12:12:47 | SA11 | Urban | Asset failure | LV | 10 | 57 | 0.00091124 | 1.599e-05 | No
31/08/2018 | 12:40:04 | NU04 | Rural Short | Unknown | Unknown | 458 | 72 | 0.24568 | 0.0034122 | No
31/08/2018 | 13:26:38 | ME347A | Urban | Asset failure | LV | 93 | 87 | 0.012935 | 0.00014868 | No
31/08/2018 | 15:22:28 | G41 | Rural Long | Overloads |  | 1 | 421 | 0.0030726 | 7.3e-06 | No
31/08/2018 | 15:40:18 | CBD366E | Urban | Animal | Animal impact | 14 | 201 | 0.0044987 | 2.238e-05 | No
31/08/2018 | 16:44:46 | HH428E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 1023 | 0.0016354 | 1.6e-06 | No
31/08/2018 | 16:46:53 | MI32 | Rural Long | Overloads |  | 1 | 280 | 0.0020435 | 7.3e-06 | No
31/08/2018 | 17:29:32 | CM05 | Rural Long | Asset failure | LV | 1 | 70 | 0.00051088 | 7.3e-06 | No
31/08/2018 | 17:49:49 | AP529D | Urban | Overloads |  | 1 | 168 | 0.00026858 | 1.6e-06 | No
31/08/2018 | 17:57:00 | MTB22 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 36 | 150 | 0.040231 | 0.00026821 | No
31/08/2018 | 18:36:45 | SG03 | Rural Short | Asset failure | LV | 1 | 292 | 0.0021754 | 7.45e-06 | No
31/08/2018 | 18:49:08 | R20 | Rural Long | Overloads |  | 1 | 282 | 0.0020581 | 7.3e-06 | No
31/08/2018 | 19:50:47 | ME427F | Urban | Asset failure | LV | 56 | 68 | 0.0060878 | 8.953e-05 | No
31/08/2018 | 22:55:22 | CD23 | Rural Long | Planned |  | 28 | 106.4286 | 0.021749 | 0.00020435 | No
31/08/2018 | 23:31:58 | AP125B | Urban | Asset failure | LV | 1 | 278 | 0.00044443 | 1.6e-06 | No
1/09/2018 | 07:27:00 | MB84 | Rural Long | Asset failure | HV | 6 | 486.5 | 0.021304 | 4.379e-05 | No
1/09/2018 | 07:39:21 | SM411D | Urban | Overloads |  | 4.6667 | 530 | 0.003954 | 7.46e-06 | No
1/09/2018 | 08:26:33 | LX32 | Rural Short | Asset failure | LV | 1 | 129 | 0.00096107 | 7.45e-06 | No
1/09/2018 | 08:40:15 | AP214B | Urban | Planned |  | 189 | 326 | 0.098501 | 0.00030215 | No
1/09/2018 | 09:22:40 | SB19 | Rural Long | Planned |  | 32 | 233 | 0.054416 | 0.00023355 | No
1/09/2018 | 09:39:01 | SA17 | Urban | Planned |  | 2 | 346 | 0.0011063 | 3.2e-06 | No
1/09/2018 | 09:45:54 | ME347F | Urban | Planned |  | 1 | 169 | 0.00027018 | 1.6e-06 | No
1/09/2018 | 09:46:09 | SG01 | Rural Short | Asset failure | LV | 1 | 251 | 0.00187 | 7.45e-06 | No
1/09/2018 | 09:56:24 | NL111A | Urban | Asset failure | LV | 1 | 172 | 0.00027497 | 1.6e-06 | No
1/09/2018 | 10:25:02 | NL111A | Urban | Asset failure | LV | 31.3333 | 483 | 0.024194 | 5.009e-05 | No
1/09/2018 | 10:39:55 | M21 | Rural Long | Third Party | Vehicle impact | 397 | 219 | 0.63454 | 0.0028974 | No
1/09/2018 | 11:35:31 | WK21 | Rural Short | Overloads |  | 3 | 448 | 0.010013 | 2.235e-05 | No
1/09/2018 | 11:46:16 | AP425A | Urban | Asset failure | LV | 1 | 303 | 0.0004844 | 1.6e-06 | No
1/09/2018 | 12:25:00 | W04 | Rural Long | Asset failure | HV | 367 | 205 | 0.54909 | 0.0026785 | No
1/09/2018 | 14:56:50 | EL01M | Urban | Asset failure | LV | 9.3333 | 245 | 0.0036556 | 1.492e-05 | No
1/09/2018 | 16:16:23 | HH107A | Urban | Asset failure | LV | 43 | 35 | 0.002406 | 6.874e-05 | No
1/09/2018 | 17:19:52 | ME131B | Urban | Overloads |  | 1 | 182 | 0.00029096 | 1.6e-06 | No
1/09/2018 | 18:55:33 | NU35 | Rural Long | Unknown | Unknown | 9 | 73 | 0.004795 | 6.569e-05 | No
1/09/2018 | 19:59:17 | HH409E | Urban | Unknown | Unknown | 2342 | 70.7626 | 0.26494 | 0.0037441 | No
1/09/2018 | 20:54:49 | SG04 | Rural Short | Asset failure | HV | 564 | 109.0284 | 0.45812 | 0.0042019 | No
2/09/2018 | 01:07:03 | NL111Q | Urban | Asset failure | LV | 1 | 498 | 0.00079614 | 1.6e-06 | No
2/09/2018 | 07:59:36 | ME131E | Urban | Planned |  | 1 | 246 | 0.00039327 | 1.6e-06 | No
2/09/2018 | 09:12:11 | CD17 | Rural Long | Planned |  | 31 | 281 | 0.063576 | 0.00022625 | No
2/09/2018 | 09:21:50 | R04 | Rural Long | Unknown | Unknown | 16 | 9 | 0.001051 | 0.00011677 | No
2/09/2018 | 10:10:32 | LX43 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 295 | 98 | 0.21538 | 0.0021978 | No
2/09/2018 | 12:28:16 | SM350B | Urban | Asset failure | LV | 1 | 272 | 0.00043484 | 1.6e-06 | No
2/09/2018 | 13:12:36 | G11 | Rural Long | Asset failure | LV | 2 | 402 | 0.0058679 | 1.46e-05 | No
2/09/2018 | 15:27:48 | SD34400 | Rural Short | Network business | Switching and protection error | 3116 | 6 | 0.13929 | 0.023215 | No
2/09/2018 | 15:27:48 | SD34400 | Rural Long | Network business | Switching and protection error | 7852 | 6 | 0.34384 | 0.057307 | No
2/09/2018 | 15:29:09 | HH148D | Urban | Asset failure | LV | 1 | 181 | 0.00028936 | 1.6e-06 | No
2/09/2018 | 16:00:40 | SM349E | Urban | Unknown | Unknown | 90 | 190 | 0.027337 | 0.00014388 | No
2/09/2018 | 17:52:59 | AP125D | Urban | Unknown | Unknown | 15.6667 | 95 | 0.0023794 | 2.505e-05 | No
2/09/2018 | 21:04:39 | NL115F | Urban | Asset failure | LV | 1 | 89 | 0.00014228 | 1.6e-06 | No
2/09/2018 | 21:40:33 | SM349E | Urban | Asset failure | LV | 90 | 275 | 0.039567 | 0.00014388 | No
2/09/2018 | 23:13:16 | AP344B | Urban | Planned |  | 47 | 260 | 0.019536 | 7.514e-05 | No
3/09/2018 | 07:56:29 | SM350B | Urban | Overloads |  | 33.6666 | 129 | 0.006943 | 5.382e-05 | No
3/09/2018 | 08:31:57 | HH496D | Urban | Asset failure | LV | 1 | 134 | 0.00021422 | 1.6e-06 | No
3/09/2018 | 08:39:28 | MT14 | Rural Short | Planned |  | 20 | 136 | 0.020264 | 0.000149 | No
3/09/2018 | 08:45:52 | KA28 | Rural Long | Planned |  | 2 | 56 | 0.00081741 | 1.46e-05 | No
3/09/2018 | 09:00:25 | HH432E | Urban | Animal | Animal impact | 396.3335 | 36 | 0.02281 | 0.00063361 | No
3/09/2018 | 09:16:51 | SD38200 | Rural Long | Planned |  | 7 | 311 | 0.015888 | 5.109e-05 | No
3/09/2018 | 09:34:25 | HH341C | Urban | Planned |  | 231 | 229 | 0.084568 | 0.00036929 | No
3/09/2018 | 09:38:19 | SB23 | Rural Long | Planned |  | 40 | 250 | 0.072983 | 0.00029193 | No
3/09/2018 | 10:04:36 | AP355A | Urban | Planned |  | 100 | 270 | 0.043164 | 0.00015987 | No
3/09/2018 | 10:05:42 | ST44 | Rural Long | Asset failure | LV | 2.3333 | 147 | 0.0025033 | 1.703e-05 | No
3/09/2018 | 10:16:42 | MV62 | Rural Short | Planned |  | 207 | 318 | 0.49041 | 0.0015422 | No
3/09/2018 | 10:47:24 | CM24 | Rural Long | Planned |  | 17 | 773 | 0.095907 | 0.00012407 | No
3/09/2018 | 11:12:52 | G42 | Rural Long | Planned |  | 44 | 79 | 0.025369 | 0.00032113 | No
3/09/2018 | 12:35:28 | VH45 | Rural Short | Planned |  | 2 | 4 | 5.96e-05 | 1.49e-05 | No
3/09/2018 | 14:13:56 | HH341B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 149 | 0.0002382 | 1.6e-06 | No
3/09/2018 | 14:52:05 | W04 | Rural Long | Other |  | 1 | 157 | 0.0011458 | 7.3e-06 | No
3/09/2018 | 17:17:03 | SA16 | Urban | Overloads |  | 1 | 122 | 0.00019504 | 1.6e-06 | No
3/09/2018 | 18:18:04 | HH145B | Urban | Vegetation | Grow-in - NSP responsibility | 15.6667 | 34 | 0.00085156 | 2.505e-05 | No
3/09/2018 | 21:55:27 | AP344B | Urban | Planned |  | 36 | 340 | 0.019568 | 5.755e-05 | No
4/09/2018 | 05:46:04 | EL01C | Urban | Asset failure | LV | 58.6667 | 471 | 0.044175 | 9.379e-05 | No
4/09/2018 | 07:12:11 | AP132D | Urban | Asset failure | LV | 2 | 121 | 0.00038688 | 3.2e-06 | No
4/09/2018 | 08:16:15 | ST12 | Rural Short | Planned |  | 383 | 387.0888 | 1.1045 | 0.0028534 | No
4/09/2018 | 08:26:49 | BM14 | Urban | Planned |  | 1 | 183 | 0.00029256 | 1.6e-06 | No
4/09/2018 | 08:50:20 | WHY08 | Urban | Planned |  | 270 | 378 | 0.16316 | 0.00043164 | No
4/09/2018 | 08:59:17 | ME347C | Urban | Planned |  | 4 | 226 | 0.0014452 | 6.39e-06 | No
4/09/2018 | 09:02:34 | NU02 | Rural Long | Planned |  | 6 | 447 | 0.019574 | 4.379e-05 | No
4/09/2018 | 09:07:31 | ST42 | Rural Long | Planned |  | 74 | 367 | 0.19821 | 0.00054008 | No
4/09/2018 | 09:15:23 | AP365A | Urban | Planned |  | 1 | 203 | 0.00032453 | 1.6e-06 | No
4/09/2018 | 09:17:53 | SM350H | Urban | Asset failure | LV | 4 | 581 | 0.0037153 | 6.39e-06 | No
4/09/2018 | 09:35:03 | AP425A | Urban | Overloads |  | 1 | 308 | 0.00049239 | 1.6e-06 | No
4/09/2018 | 09:43:34 | NL111Q | Urban | Planned |  | 44 | 204 | 0.01435 | 7.034e-05 | No
4/09/2018 | 10:00:33 | ST14 | Rural Short | Planned |  | 20 | 320 | 0.047681 | 0.000149 | No
4/09/2018 | 10:00:37 | EL01C | Urban | Unknown | Unknown | 298.0002 | 2 | 0.00095281 | 0.00047641 | No
4/09/2018 | 10:04:20 | HH522C | Urban | Planned |  | 81 | 265 | 0.034316 | 0.00012949 | No
4/09/2018 | 10:10:06 | KI12 | Rural Long | Planned |  | 1 | 114 | 0.00083201 | 7.3e-06 | No
4/09/2018 | 10:20:23 | CV19 | Rural Long | Planned |  | 9 | 246 | 0.016159 | 6.569e-05 | No
4/09/2018 | 10:25:39 | ME200A | Urban | Overloads |  | 1 | 165 | 0.00026378 | 1.6e-06 | No
4/09/2018 | 10:35:36 | SM126A | Urban | Planned |  | 4 | 250 | 0.0015987 | 6.39e-06 | No
4/09/2018 | 10:38:42 | SB19 | Rural Long | Planned |  | 25 | 226 | 0.041236 | 0.00018246 | No
4/09/2018 | 11:02:05 | EL01C | Urban | Unknown | Unknown | 298.0002 | 1 | 0.00047641 | 0.00047641 | No
4/09/2018 | 11:06:56 | NU34 | Rural Long | Asset failure | LV | 1 | 102 | 0.00074443 | 7.3e-06 | No
4/09/2018 | 11:12:38 | HH386A | Urban | Unknown | Unknown | 19.6666 | 79 | 0.0024838 | 3.144e-05 | No
4/09/2018 | 11:24:07 | SM402D | Urban | Asset failure | LV | 1 | 328 | 0.00052437 | 1.6e-06 | No
4/09/2018 | 11:42:29 | MI12 | Rural Long | Planned |  | 3 | 231 | 0.0050577 | 2.19e-05 | No
4/09/2018 | 12:53:12 | BU02 | Rural Long | Asset failure | HV | 102 | 18 | 0.0134 | 0.00074443 | No
4/09/2018 | 13:30:00 | NU02 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 11 | 290 | 0.023282 | 8.028e-05 | No
4/09/2018 | 14:08:27 | WHY04 | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
4/09/2018 | 14:20:55 | PP09 | Rural Long | Planned |  | 1 | 49 | 0.00035762 | 7.3e-06 | No
4/09/2018 | 14:27:25 | NU31 | Rural Long | Asset failure | LV | 1 | 415 | 0.0030288 | 7.3e-06 | No
4/09/2018 | 15:06:31 | PL803C | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
4/09/2018 | 16:18:51 | R25 | Rural Long | Unknown | Unknown | 2 | 25 | 0.00036492 | 1.46e-05 | No
4/09/2018 | 17:20:46 | SA17 | Urban | Unknown | Unknown | 31 | 150 | 0.0074338 | 4.956e-05 | No
4/09/2018 | 17:57:32 | MV34 | Rural Short | Asset failure | LV | 1 | 76 | 0.00056621 | 7.45e-06 | No
4/09/2018 | 18:10:53 | MI32 | Rural Long | Other |  | 18.3333 | 81 | 0.010838 | 0.0001338 | No
4/09/2018 | 19:18:12 | SA17 | Urban | Asset failure | LV | 47 | 135 | 0.010144 | 7.514e-05 | No
4/09/2018 | 19:56:11 | SM179C | Urban | Asset failure | LV | 79 | 96 | 0.012124 | 0.0001263 | No
4/09/2018 | 20:05:48 | M92 | Rural Long | Unknown | Unknown | 463 | 211 | 0.713 | 0.0033791 | No
4/09/2018 | 22:00:33 | HH341D | Urban | Overloads |  | 46 | 142 | 0.010443 | 7.354e-05 | No
5/09/2018 | 05:42:34 | GA22 | Rural Short | Asset failure | LV | 1 | 467 | 0.0034792 | 7.45e-06 | No
5/09/2018 | 07:35:21 | SA32 | Urban | Animal | Animal impact | 19 | 199 | 0.0060446 | 3.037e-05 | No
5/09/2018 | 08:30:16 | SG13 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 100 | 0.017135 | 0.00017135 | No
5/09/2018 | 08:30:33 | PL15 | Rural Long | Planned |  | 246 | 421.9024 | 0.75748 | 0.0017954 | No
5/09/2018 | 09:05:52 | MTB52 | Rural Long | Planned |  | 5 | 329 | 0.012006 | 3.649e-05 | No
5/09/2018 | 09:05:52 | SD31100 | Rural Long | Planned |  | 2 | 374 | 0.0054592 | 1.46e-05 | No
5/09/2018 | 09:14:01 | SA20 | Urban | Planned |  | 104 | 275 | 0.045722 | 0.00016626 | No
5/09/2018 | 09:29:11 | SG10 | Rural Short | Asset failure | LV | 1 | 23 | 0.00017135 | 7.45e-06 | No
5/09/2018 | 09:33:00 | HH177B | Urban | Planned |  | 25 | 324 | 0.012949 | 3.997e-05 | No
5/09/2018 | 09:34:52 | SA33 | Urban | Animal | Animal impact | 1 | 54 | 8.633e-05 | 1.6e-06 | No
5/09/2018 | 09:39:44 | AP125A | Urban | Planned |  | 287 | 248.2927 | 0.11392 | 0.00045882 | No
5/09/2018 | 09:39:52 | ST42 | Rural Long | Planned |  | 68 | 259 | 0.12854 | 0.00049629 | No
5/09/2018 | 09:42:19 | SA20 | Urban | Planned |  | 1 | 260 | 0.00041566 | 1.6e-06 | No
5/09/2018 | 09:45:31 | VH23 | Rural Short | Planned |  | 121 | 294 | 0.26503 | 0.00090147 | No
5/09/2018 | 09:51:53 | PA11 | Rural Long | Planned |  | 42 | 143 | 0.043834 | 0.00030653 | No
5/09/2018 | 10:20:42 | ME231C | Urban | Asset failure | LV | 1 | 412 | 0.00065865 | 1.6e-06 | No
5/09/2018 | 10:26:33 | VH12 | Rural Short | Asset failure | LV | 1 | 100 | 0.00074501 | 7.45e-06 | No
5/09/2018 | 10:47:03 | HH432B | Urban | Planned |  | 1 | 196 | 0.00031334 | 1.6e-06 | No
5/09/2018 | 11:50:00 | SD52300 | Rural Long | Asset failure | Subtransmission | 1 | 107 | 0.00078092 | 7.3e-06 | No
5/09/2018 | 12:29:59 | AP214C | Urban | Overloads |  | 1 | 239 | 0.00038208 | 1.6e-06 | No
5/09/2018 | 12:53:54 | G08 | Rural Long | Unknown | Unknown | 1 | 102 | 0.00074443 | 7.3e-06 | No
5/09/2018 | 15:20:53 | CD15 | Rural Long | Planned |  | 32 | 14 | 0.0032697 | 0.00023355 | No
5/09/2018 | 16:42:08 | MI04 | Rural Long | Asset failure | HV | 1 | 78 | 0.00056927 | 7.3e-06 | No
5/09/2018 | 17:33:48 | ST44 | Rural Long | Planned |  | 3 | 52 | 0.0011385 | 2.19e-05 | No
5/09/2018 | 18:19:50 | SM126E | Urban | Other |  | 1 | 149 | 0.0002382 | 1.6e-06 | No
5/09/2018 | 18:29:57 | NL760B | Urban | Asset failure | LV | 1 | 210 | 0.00033572 | 1.6e-06 | No
5/09/2018 | 18:57:57 | ME427D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 159 | 0.00025419 | 1.6e-06 | No
5/09/2018 | 20:04:43 | SM172F | Urban | Other |  | 1 | 82 | 0.00013109 | 1.6e-06 | No
5/09/2018 | 20:59:21 | VH23 | Rural Short | Asset failure | LV | 4.6667 | 80 | 0.0027814 | 3.477e-05 | No
5/09/2018 | 21:15:44 | MTB72 | Rural Long | Unknown | Unknown | 1 | 11 | 8.028e-05 | 7.3e-06 | No
5/09/2018 | 21:39:02 | AP425B | Urban | Asset failure | LV | 43 | 96 | 0.0065993 | 6.874e-05 | No
5/09/2018 | 21:48:02 | AP372B | Urban | Asset failure | LV | 45 | 87 | 0.0062588 | 7.194e-05 | No
5/09/2018 | 21:55:15 | NU13 | Rural Long | Weather |  | 4 | 113 | 0.0032988 | 2.919e-05 | No
5/09/2018 | 22:22:52 | HH145B | Urban | Asset failure | LV | 1 | 134 | 0.00021422 | 1.6e-06 | No
6/09/2018 | 07:07:08 | SD33100 | Rural Long | Unknown | Unknown | 5 | 210 | 0.0076632 | 3.649e-05 | No
6/09/2018 | 08:38:54 | YK12 | Rural Long | Planned |  | 20 | 290 | 0.04233 | 0.00014597 | No
6/09/2018 | 08:42:43 | VH44 | Rural Short | Planned |  | 105 | 360 | 0.28162 | 0.00078227 | No
6/09/2018 | 08:45:37 | HH341K | Urban | Planned |  | 1 | 239 | 0.00038208 | 1.6e-06 | No
6/09/2018 | 08:54:31 | HH341K / HH102C | Urban | Planned |  | 279 | 188.2581 | 0.083969 | 0.00044603 | No
6/09/2018 | 09:05:08 | AP227B | Urban | Asset failure | LV | 89 | 72 | 0.010244 | 0.00014228 | No
6/09/2018 | 09:13:06 | SB19 | Rural Long | Planned |  | 13 | 227 | 0.021537 | 9.488e-05 | No
6/09/2018 | 09:14:19 | HH102D | Urban | Planned |  | 3 | 211 | 0.001012 | 4.8e-06 | No
6/09/2018 | 09:16:39 | CD03 | Rural Short | Asset failure | LV | 1 | 150 | 0.0011175 | 7.45e-06 | No
6/09/2018 | 09:25:48 | NA01 | Rural Long | Planned |  | 32 | 414 | 0.096688 | 0.00023355 | No
6/09/2018 | 09:38:31 | VH22 | Rural Short | Planned |  | 53 | 191 | 0.075418 | 0.00039486 | No
6/09/2018 | 09:39:39 | W04 | Rural Long | Planned |  | 3 | 73 | 0.0015983 | 2.19e-05 | No
6/09/2018 | 09:45:09 | SM411D | Urban | Planned |  | 16 | 57 | 0.001458 | 2.558e-05 | No
6/09/2018 | 09:52:17 | MG19 | Rural Long | Third Party | Other | 1 | 110 | 0.00080282 | 7.3e-06 | No
6/09/2018 | 10:00:48 | SM172F | Urban | Planned |  | 50 | 268 | 0.021422 | 7.993e-05 | No
6/09/2018 | 10:05:44 | G11 | Rural Long | Planned |  | 5 | 297 | 0.010838 | 3.649e-05 | No
6/09/2018 | 10:08:30 | MTB52 | Rural Long | Planned |  | 4 | 122 | 0.0035616 | 2.919e-05 | No
6/09/2018 | 10:13:51 | PL27 | Rural Long | Planned |  | 48 | 202 | 0.070765 | 0.00035032 | No
6/09/2018 | 10:40:27 | HH428B | Urban | Asset failure | LV | 38 | 56 | 0.003402 | 6.075e-05 | No
6/09/2018 | 10:47:48 | GU32 | Rural Long | Planned |  | 1 | 11 | 8.028e-05 | 7.3e-06 | No
6/09/2018 | 11:01:09 | GA22 | Rural Short | Planned |  | 5 | 65 | 0.0024213 | 3.725e-05 | No
6/09/2018 | 12:00:57 | GA18 | Rural Long | Planned |  | 55 | 217 | 0.087106 | 0.00040141 | No
6/09/2018 | 14:06:24 | ST35 | Rural Long | Unknown | Unknown | 1 | 13 | 9.488e-05 | 7.3e-06 | No
6/09/2018 | 14:38:00 | SG04 | Rural Short | Unknown | Unknown | 38.3333 | 143 | 0.040839 | 0.00028559 | No
6/09/2018 | 19:29:09 | MG17 | Rural Long | Asset failure | LV | 1 | 110 | 0.00080282 | 7.3e-06 | No
6/09/2018 | 21:07:14 | ST22 | Rural Short | Unknown | Unknown | 8 | 30 | 0.001788 | 5.96e-05 | No
7/09/2018 | 08:47:08 | NL511B | Urban | Planned |  | 144 | 288 | 0.0663 | 0.00023021 | No
7/09/2018 | 08:53:41 | EL18 | Urban | Planned |  | 22 | 54 | 0.0018992 | 3.517e-05 | No
7/09/2018 | 09:08:46 | EL08G | Urban | Asset failure | LV | 37.3334 | 160 | 0.0095494 | 5.968e-05 | No
7/09/2018 | 09:09:17 | GA47 | Rural Long | Planned |  | 33 | 88 | 0.021194 | 0.00024085 | No
7/09/2018 | 09:10:40 | PL04 | Urban | Planned |  | 3 | 98 | 0.00047001 | 4.8e-06 | No
7/09/2018 | 09:12:11 | G11 | Rural Long | Asset failure | LV | 2 | 274 | 0.0039995 | 1.46e-05 | No
7/09/2018 | 09:17:03 | ST41 | Rural Long | Planned |  | 73 | 193 | 0.10283 | 0.00053278 | No
7/09/2018 | 09:18:33 | PA02 | Urban | Planned |  | 37 | 20 | 0.001183 | 5.915e-05 | No
7/09/2018 | 09:32:52 | HH121C | Urban | Unknown | Unknown | 2241 | 55 | 0.19704 | 0.0035826 | No
7/09/2018 | 09:50:02 | MV34 | Rural Short | Planned |  | 377 | 257 | 0.72184 | 0.0028087 | No
7/09/2018 | 09:58:43 | CD24 | Rural Long | Planned |  | 8 | 176 | 0.010276 | 5.839e-05 | No
7/09/2018 | 10:10:31 | MT01 | Rural Long | Planned |  | 230 | 176 | 0.29544 | 0.0016786 | No
7/09/2018 | 10:22:02 | MTB72 | Rural Long | Unknown | Unknown | 1 | 64 | 0.00046709 | 7.3e-06 | No
7/09/2018 | 10:26:10 | ST41 | Rural Long | Planned |  | 1 | 23 | 0.00016786 | 7.3e-06 | No
7/09/2018 | 10:26:11 | BT18 | Rural Long | Planned |  | 2 | 65 | 0.00094878 | 1.46e-05 | No
7/09/2018 | 10:50:43 | CN73 | Rural Long | Planned |  | 27 | 195 | 0.038426 | 0.00019706 | No
7/09/2018 | 11:56:06 | ST41 | Rural Long | Planned |  | 1 | 32 | 0.00023355 | 7.3e-06 | No
7/09/2018 | 12:51:27 | BT15 | Rural Long | Planned |  | 4 | 21 | 0.00061306 | 2.919e-05 | No
7/09/2018 | 13:21:38 | ST12 | Rural Short | Planned |  | 4 | 56 | 0.0016688 | 2.98e-05 | No
7/09/2018 | 13:23:19 | HH341E | Urban | Asset failure | LV | 56 | 92 | 0.0082364 | 8.953e-05 | No
7/09/2018 | 13:23:26 | HH341E | Urban | Asset failure | LV | 60 | 97 | 0.0093043 | 9.592e-05 | No
7/09/2018 | 13:51:19 | LX34 | Rural Short | Asset failure | LV | 3 | 228 | 0.0050959 | 2.235e-05 | No
7/09/2018 | 18:23:25 | CV24 | Rural Long | Unknown | Unknown | 1 | 122 | 0.0008904 | 7.3e-06 | No
7/09/2018 | 19:58:08 | MV22 | Rural Short | Third Party | Vehicle impact | 183 | 436.9344 | 0.59571 | 0.0013634 | No
7/09/2018 | 19:58:08 | MV22 | Rural Short | Third Party | Vehicle impact | 0 | 100 | 0.061836 | 0 | No
7/09/2018 | 20:12:55 | MG03 | Rural Short | Unknown | Unknown | 39 | 27 | 0.007845 | 0.00029056 | No
7/09/2018 | 20:33:00 | SD44300 | Rural Short | Unknown | Unknown | 1583 | 4 | 0.047174 | 0.011794 | No
7/09/2018 | 20:33:00 | SD44300 | Rural Short | Unknown | Unknown | 0 | 15 | 0.1769 | 0 | No
7/09/2018 | 20:33:00 | SD44300 | Rural Long | Unknown | Unknown | 2252 | 47.0488 | 0.77329 | 0.016436 | No
7/09/2018 | 20:33:00 | SD44300 | Rural Long | Unknown | Unknown | 0 | 12.3619 | 0.20318 | 0 | No
7/09/2018 | 21:19:14 | MT21 | Rural Long | Asset failure | LV | 6.6667 | 143 | 0.0069577 | 4.866e-05 | No
8/09/2018 | 08:07:00 | SM216C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2954 | 101 | 0.47697 | 0.0047225 | No
8/09/2018 | 09:11:04 | GA53 | Rural Short | Asset failure | LV | 1 | 323 | 0.0024064 | 7.45e-06 | No
8/09/2018 | 09:49:28 | VH45 | Rural Short | Planned |  | 10 | 199 | 0.014826 | 7.45e-05 | No
8/09/2018 | 09:50:58 | W26 | Rural Long | Planned |  | 92 | 303 | 0.20345 | 0.00067145 | No
8/09/2018 | 10:12:28 | HH496C | Urban | Asset failure | LV | 1 | 176 | 0.00028137 | 1.6e-06 | No
8/09/2018 | 10:14:06 | SA20 | Urban | Asset failure | LV | 1 | 80 | 0.00012789 | 1.6e-06 | No
8/09/2018 | 10:25:00 | VH45 | Rural Short | Planned |  | 3 | 2 | 4.47e-05 | 2.235e-05 | No
8/09/2018 | 11:20:14 | KA04 | Rural Long | Unknown | Unknown | 41 | 5 | 0.0014962 | 0.00029923 | No
8/09/2018 | 11:34:02 | HH107A | Urban | Asset failure | LV | 70 | 25 | 0.0027977 | 0.00011191 | No
8/09/2018 | 11:42:02 | R29 | Rural Long | Asset failure | LV | 1 | 476 | 0.003474 | 7.3e-06 | No
8/09/2018 | 14:46:03 | NL234A | Urban | Overloads |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
8/09/2018 | 16:04:11 | W26 | Rural Long | Unknown | Unknown | 2 | 131 | 0.0019122 | 1.46e-05 | No
8/09/2018 | 16:07:42 | NL210A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19.3333 | 238 | 0.007356 | 3.091e-05 | No
8/09/2018 | 16:45:41 | MTB14 | Rural Short | Weather |  | 308 | 1 | 0.0022947 | 0.0022947 | No
8/09/2018 | 18:57:51 | EL260A | Urban | Third Party | Vehicle impact | 2 | 57 | 0.00018225 | 3.2e-06 | No
8/09/2018 | 19:03:30 | NU04 | Rural Short | Asset failure | HV | 305 | 123.2951 | 0.28016 | 0.0022723 | No
8/09/2018 | 19:03:30 | NU02 | Rural Long | Asset failure | HV | 1638 | 229 | 2.7376 | 0.011955 | No
8/09/2018 | 23:13:37 | NU02 | Rural Long | Overloads |  | 1 | 63 | 0.0004598 | 7.3e-06 | No
9/09/2018 | 08:17:38 | NU19 | Rural Long | Planned |  | 77 | 230 | 0.12925 | 0.00056197 | No
9/09/2018 | 09:04:57 | HH409A | Urban | Planned |  | 197 | 41.4315 | 0.013048 | 0.00031494 | No
9/09/2018 | 09:09:34 | VH44 | Rural Short | Planned |  | 13 | 228 | 0.022082 | 9.685e-05 | No
9/09/2018 | 09:11:44 | NL111A | Urban | Planned |  | 48 | 273 | 0.020949 | 7.674e-05 | No
9/09/2018 | 09:28:24 | AP132E | Urban | Planned |  | 1 | 296 | 0.00047321 | 1.6e-06 | No
9/09/2018 | 09:31:05 | HH341C | Urban | Third Party | Vehicle impact | 73 | 493.5342 | 0.057597 | 0.0001167 | No
9/09/2018 | 09:41:29 | SA20 | Urban | Planned |  | 129 | 196 | 0.040421 | 0.00020623 | No
9/09/2018 | 09:52:24 | MTB52 | Rural Long | Asset failure | LV | 2 | 120 | 0.0017516 | 1.46e-05 | No
9/09/2018 | 11:04:08 | GA50 | Urban | Asset failure | LV | 1 | 217 | 0.00034691 | 1.6e-06 | No
9/09/2018 | 11:34:50 | EL03 | Urban | Overloads |  | 1 | 91 | 0.00014548 | 1.6e-06 | No
9/09/2018 | 12:07:00 | HH496F | Urban | Unknown | Unknown | 1 | 230 | 0.0003677 | 1.6e-06 | No
9/09/2018 | 15:33:01 | SM350F | Urban | Asset failure | LV | 20.3333 | 128 | 0.0041608 | 3.251e-05 | No
9/09/2018 | 16:20:14 | AP425A | Urban | Planned |  | 6 | 128 | 0.0012278 | 9.59e-06 | No
9/09/2018 | 16:31:17 | MTB11 | Rural Short | Asset failure | LV | 1 | 122 | 0.00090892 | 7.45e-06 | No
9/09/2018 | 19:33:48 | SM374A | Urban | Asset failure | LV | 11 | 63 | 0.0011079 | 1.759e-05 | No
9/09/2018 | 20:23:46 | GA15 | Rural Short | Asset failure | LV | 1 | 119 | 0.00088657 | 7.45e-06 | No
10/09/2018 | 00:32:23 | AP344B | Urban | Planned |  | 14 | 134 | 0.0029991 | 2.238e-05 | No
10/09/2018 | 05:53:14 | SD33100 | Rural Long | Asset failure | Subtransmission | 9 | 178 | 0.011692 | 6.568e-05 | No
10/09/2018 | 06:03:59 | HH148C | Urban | Unknown | Unknown | 914 | 27.43 | 0.04008 | 0.0014612 | No
10/09/2018 | 06:17:48 | KA01 | Rural Short | Overloads |  | 1 | 274 | 0.0020413 | 7.45e-06 | No
10/09/2018 | 08:15:48 | CL05 | Rural Long | Planned |  | 11 | 368 | 0.029544 | 8.028e-05 | No
10/09/2018 | 08:44:57 | YK29 | Rural Long | Planned |  | 158 | 160 | 0.1845 | 0.0011531 | No
10/09/2018 | 08:45:31 | HH522C | Urban | Overloads |  | 2.6667 | 43 | 0.00018331 | 4.26e-06 | No
10/09/2018 | 08:58:12 | MTB33 | Rural Short | Planned |  | 55 | 224 | 0.091786 | 0.00040976 | No
10/09/2018 | 08:59:50 | BT02 | Rural Long | Planned |  | 12 | 340 | 0.029777 | 8.758e-05 | No
10/09/2018 | 09:00:03 | CD16 | Rural Short | Planned |  | 56 | 265 | 0.11056 | 0.00041721 | No
10/09/2018 | 09:00:40 | KA05 | Rural Long | Planned |  | 3 | 12 | 0.00026274 | 2.19e-05 | No
10/09/2018 | 09:05:24 | VH34 | Rural Short | Planned |  | 43 | 403 | 0.1291 | 0.00032036 | No
10/09/2018 | 09:10:52 | W33 | Rural Short | Planned |  | 13 | 56 | 0.0054237 | 9.685e-05 | No
10/09/2018 | 09:11:56 | SG01 | Rural Short | Planned |  | 148 | 276 | 0.30432 | 0.0011026 | No
10/09/2018 | 09:18:34 | SD38100 | Rural Long | Planned |  | 6 | 346 | 0.015151 | 4.379e-05 | No
10/09/2018 | 09:23:12 | SA31 | Urban | Planned |  | 180 | 75 | 0.021582 | 0.00028776 | No
10/09/2018 | 09:26:51 | KA03 | Rural Long | Planned |  | 4 | 312 | 0.0091083 | 2.919e-05 | No
10/09/2018 | 09:36:10 | AP424E | Urban | Planned |  | 137 | 132 | 0.02891 | 0.00021902 | No
10/09/2018 | 09:37:56 | M22 | Rural Long | Planned |  | 9 | 60 | 0.0039411 | 6.569e-05 | No
10/09/2018 | 09:50:15 | LX21 | Rural Short | Planned |  | 3 | 274 | 0.006124 | 2.235e-05 | No
10/09/2018 | 10:27:08 | G14 | Rural Long | Planned |  | 6 | 58 | 0.0025398 | 4.379e-05 | No
10/09/2018 | 10:29:18 | LX51 | Rural Short | Planned |  | 2 | 23 | 0.00034271 | 1.49e-05 | No
10/09/2018 | 10:46:00 | MB43 | Rural Long | Planned |  | 27 | 151 | 0.029755 | 0.00019706 | No
10/09/2018 | 12:07:00 | LX53 | Rural Short | Planned |  | 2 | 118 | 0.0017582 | 1.49e-05 | No
10/09/2018 | 12:30:13 | MB43 | Rural Long | Planned |  | 1 | 27 | 0.00019706 | 7.3e-06 | No
10/09/2018 | 12:54:15 | HH428D | Urban | Third Party | Vehicle impact | 35.6666 | 89 | 0.0050747 | 5.702e-05 | No
10/09/2018 | 14:29:50 | LX53 | Rural Short | Asset failure | HV | 4.6667 | 130 | 0.0045198 | 3.477e-05 | No
10/09/2018 | 16:06:12 | SM411F | Urban | Asset failure | LV | 1 | 202 | 0.00032293 | 1.6e-06 | No
10/09/2018 | 16:38:24 | MV34 | Rural Short | Asset failure | LV | 12 | 187 | 0.016718 | 8.94e-05 | No
10/09/2018 | 21:41:15 | SG03 | Rural Short | Animal | Animal impact | 995 | 164.1307 | 1.2167 | 0.0074129 | No
11/09/2018 | 00:56:18 | CBD366E | Urban | Planned |  | 44 | 252 | 0.017726 | 7.034e-05 | No
11/09/2018 | 08:01:52 | SM349H | Urban | Overloads |  | 1 | 219 | 0.00035011 | 1.6e-06 | No
11/09/2018 | 08:09:44 | ST16 | Rural Short | Planned |  | 107 | 349.2336 | 0.2784 | 0.00079717 | No
11/09/2018 | 08:23:37 | SA33 | Urban | Planned |  | 26 | 276 | 0.011472 | 4.157e-05 | No
11/09/2018 | 08:56:22 | MB51 | Rural Long | Planned |  | 16 | 45 | 0.0052548 | 0.00011677 | No
11/09/2018 | 09:02:00 | W29 | Rural Long | Planned |  | 33 | 140 | 0.033718 | 0.00024085 | No
11/09/2018 | 09:02:34 | NL111Q | Urban | Planned |  | 88 | 355 | 0.049943 | 0.00014068 | No
11/09/2018 | 09:06:48 | MB41 | Rural Long | Planned |  | 2 | 60 | 0.0008758 | 1.46e-05 | No
11/09/2018 | 09:08:27 | HH121C | Urban | Planned |  | 134 | 196 | 0.041988 | 0.00021422 | No
11/09/2018 | 09:09:31 | NU13 | Rural Long | Planned |  | 3 | 159 | 0.0034813 | 2.19e-05 | No
11/09/2018 | 09:26:00 | ST11 | Rural Short | Planned |  | 12 | 246 | 0.021993 | 8.94e-05 | No
11/09/2018 | 09:30:32 | G05 | Rural Long | Planned |  | 1 | 344 | 0.0025106 | 7.3e-06 | No
11/09/2018 | 09:40:08 | MI32 | Rural Long | Asset failure | LV | 1 | 342 | 0.002496 | 7.3e-06 | No
11/09/2018 | 09:53:34 | MV62 | Rural Short | Planned |  | 66 | 138 | 0.067856 | 0.00049171 | No
11/09/2018 | 10:00:02 | SG12 | Rural Short | Unknown | Unknown | 15 | 72 | 0.0080462 | 0.00011175 | No
11/09/2018 | 10:03:40 | HH386B | Urban | Planned |  | 1 | 128 | 0.00020463 | 1.6e-06 | No
11/09/2018 | 10:04:04 | GA28 | Rural Long | Planned |  | 1 | 70 | 0.00051088 | 7.3e-06 | No
11/09/2018 | 10:08:00 | CD26 | Rural Long | Planned |  | 5 | 141 | 0.0051453 | 3.649e-05 | No
11/09/2018 | 10:08:05 | SD40102 | Rural Long | Planned |  | 2 | 149 | 0.0021749 | 1.46e-05 | No
11/09/2018 | 10:25:29 | MV63 | Rural Short | Unknown | Unknown | 187 | 98 | 0.13653 | 0.0013932 | No
11/09/2018 | 10:52:00 | CM28 | Rural Long | Unknown | Unknown | 60 | 1704.9667 | 0.74661 | 0.0004379 | No
11/09/2018 | 10:52:00 | CM28 | Rural Long | Unknown | Unknown | 469 | 7 | 0.02396 | 0.0034229 | No
11/09/2018 | 11:11:35 | G41 | Rural Long | Unknown | Unknown | 7.3333 | 287 | 0.015361 | 5.352e-05 | No
11/09/2018 | 11:15:38 | SA744C | Urban | Vegetation | Grow-in - NSP responsibility | 3.6667 | 181 | 0.001061 | 5.86e-06 | No
11/09/2018 | 11:35:25 | SA36 | Urban | Asset failure | HV | 161 | 32.5528 | 0.0083787 | 0.00025739 | No
11/09/2018 | 11:37:09 | SA18 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 31 | 128 | 0.0063435 | 4.956e-05 | No
11/09/2018 | 11:37:52 | MG44 | Urban | Planned |  | 135 | 148 | 0.031942 | 0.00021582 | No
11/09/2018 | 11:45:13 | W29 | Rural Long | Planned |  | 35 | 86 | 0.021968 | 0.00025544 | No
11/09/2018 | 11:50:48 | GA800A | Rural Short | Unknown | Unknown | 2 | 154 | 0.0022946 | 1.49e-05 | No
11/09/2018 | 11:55:00 | LM64 | Rural Long | Planned |  | 2 | 18 | 0.00026274 | 1.46e-05 | No
11/09/2018 | 12:04:00 | GU14 | Rural Long | Asset failure | HV | 13 | 147.4615 | 0.013991 | 9.488e-05 | No
11/09/2018 | 12:18:42 | SA36 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 7.6667 | 59 | 0.00072313 | 1.226e-05 | No
11/09/2018 | 12:19:37 | GA26 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 188 | 0.00030055 | 1.6e-06 | No
11/09/2018 | 12:20:37 | CD15 | Rural Long | Asset failure | LV | 1 | 198 | 0.0014451 | 7.3e-06 | No
11/09/2018 | 12:21:11 | GA25 | Rural Short | Vegetation | Grow-in - NSP responsibility | 2422 | 96 | 1.7322 | 0.018044 | No
11/09/2018 | 13:15:50 | NU20 | Rural Long | Unknown | Unknown | 18.3333 | 106 | 0.014183 | 0.0001338 | No
11/09/2018 | 13:15:58 | CV30 | Rural Long | Planned |  | 3 | 28 | 0.00061306 | 2.19e-05 | No
11/09/2018 | 13:24:21 | HH145B | Urban | Asset failure | LV | 1 | 30 | 4.796e-05 | 1.6e-06 | No
11/09/2018 | 14:45:26 | YK08 | Rural Long | Unknown | Unknown | 50 | 144.16 | 0.052606 | 0.00036492 | No
11/09/2018 | 14:50:06 | GA800A | Rural Short | Asset failure | LV | 2 | 216 | 0.0032185 | 1.49e-05 | No
11/09/2018 | 15:02:35 | NL111C | Urban | Asset failure | LV | 1 | 376 | 0.0006011 | 1.6e-06 | No
11/09/2018 | 15:04:58 | MG44 | Urban | Asset failure | LV | 28 | 36 | 0.0016115 | 4.476e-05 | No
11/09/2018 | 15:29:17 | BM31 | Rural Short | Unknown | Unknown | 284 | 50 | 0.10579 | 0.0021158 | No
11/09/2018 | 15:38:15 | HH177G | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 166 | 0.00026538 | 1.6e-06 | No
11/09/2018 | 15:43:48 | HH177C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 191 | 0.00030535 | 1.6e-06 | No
11/09/2018 | 15:54:34 | NL111Q | Urban | Asset failure | LV | 21.6666 | 47 | 0.001628 | 3.464e-05 | No
11/09/2018 | 16:02:46 | SM137A | Urban | Asset failure | LV | 1 | 300 | 0.0004796 | 1.6e-06 | No
11/09/2018 | 16:12:46 | NL760B | Urban | Asset failure | LV | 1 | 282 | 0.00045083 | 1.6e-06 | No
11/09/2018 | 16:16:31 | HH177G | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 127 | 0.00020303 | 1.6e-06 | No
11/09/2018 | 16:26:58 | EL23 | Urban | Asset failure | LV | 8 | 74 | 0.00094642 | 1.279e-05 | No
11/09/2018 | 16:45:00 | NL451C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2704 | 72.0673 | 0.31153 | 0.0043228 | No
11/09/2018 | 17:00:52 | AP149B | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
11/09/2018 | 17:50:14 | MB72 | Rural Long | Other |  | 1 | 146 | 0.0010656 | 7.3e-06 | No
11/09/2018 | 17:56:19 | WHY06 | Urban | Asset failure | LV | 1 | 325 | 0.00051957 | 1.6e-06 | No
11/09/2018 | 18:20:40 | NL111Q | Urban | Asset failure | LV | 57 | 92 | 0.0083835 | 9.112e-05 | No
11/09/2018 | 18:46:44 | GA15 | Rural Short | Asset failure | LV | 2 | 340 | 0.0050661 | 1.49e-05 | No
11/09/2018 | 19:10:42 | PA01 | Urban | Asset failure | LV | 47 | 149 | 0.011196 | 7.514e-05 | No
11/09/2018 | 20:31:10 | EL10 | Urban | Asset failure | LV | 71 | 56 | 0.0063563 | 0.00011351 | No
11/09/2018 | 21:32:37 | SD37301 | Rural Short | Animal | Animal impact | 3 | 5 | 0.00011175 | 2.235e-05 | No
11/09/2018 | 22:39:20 | MI16 | Rural Long | Asset failure | LV | 2 | 363 | 0.0052986 | 1.46e-05 | No
12/09/2018 | 01:22:21 | GA25 | Rural Short | Unknown | Unknown | 18 | 59 | 0.0079121 | 0.0001341 | No
12/09/2018 | 06:52:32 | AP424C | Urban | Overloads |  | 1 | 184 | 0.00029416 | 1.6e-06 | No
12/09/2018 | 07:29:15 | SM350D | Urban | Asset failure | LV | 21.6666 | 143 | 0.0049532 | 3.464e-05 | No
12/09/2018 | 07:41:07 | MG17 | Rural Long | Asset failure | LV | 1 | 306 | 0.0022333 | 7.3e-06 | No
12/09/2018 | 08:44:00 | SG10 | Rural Short | Asset failure | LV | 1 | 51 | 0.00037996 | 7.45e-06 | No
12/09/2018 | 08:46:12 | GU43 | Rural Long | Planned |  | 57 | 310 | 0.12896 | 0.00041601 | No
12/09/2018 | 08:51:57 | PL803C | Urban | Asset failure | LV | 1 | 55 | 8.793e-05 | 1.6e-06 | No
12/09/2018 | 09:01:48 | YK08 | Rural Long | Planned |  | 48 | 104 | 0.036433 | 0.00035032 | No
12/09/2018 | 09:06:29 | AP146C | Urban | Planned |  | 163 | 336 | 0.087556 | 0.00026058 | No
12/09/2018 | 09:07:56 | GU13 | Rural Long | Planned |  | 322 | 328 | 0.77082 | 0.0023501 | No
12/09/2018 | 09:09:51 | HH341G | Urban | Planned |  | 2 | 76 | 0.000243 | 3.2e-06 | No
12/09/2018 | 09:14:39 | CN52 | Rural Long | Unknown | Unknown | 88 | 83 | 0.053307 | 0.00064225 | No
12/09/2018 | 09:22:10 | W20 | Rural Long | Planned |  | 5 | 157 | 0.0057292 | 3.649e-05 | No
12/09/2018 | 09:25:11 | BM31 | Rural Short | Planned |  | 49 | 222 | 0.081043 | 0.00036506 | No
12/09/2018 | 09:25:35 | VH16 | Rural Short | Planned |  | 1 | 26 | 0.0001937 | 7.45e-06 | No
12/09/2018 | 09:35:29 | SA19 | Urban | Planned |  | 21 | 91 | 0.0030551 | 3.357e-05 | No
12/09/2018 | 09:47:17 | GU43 | Rural Long | Planned |  | 147 | 328 | 0.3519 | 0.0010729 | No
12/09/2018 | 09:49:56 | MV13 | Rural Short | Planned |  | 32 | 294 | 0.070091 | 0.0002384 | No
12/09/2018 | 10:02:24 | HH341G | Urban | Planned |  | 1 | 34 | 5.435e-05 | 1.6e-06 | No
12/09/2018 | 10:04:04 | HH341G | Urban | Planned |  | 257 | 247 | 0.10148 | 0.00041086 | No
12/09/2018 | 10:04:07 | MTB32 | Rural Long | Unknown | Unknown | 1 | 134 | 0.00097798 | 7.3e-06 | No
12/09/2018 | 10:37:43 | LM51 | Rural Long | Planned |  | 103 | 211 | 0.15861 | 0.00075173 | No
12/09/2018 | 10:39:27 | VH16 | Rural Short | Planned |  | 1 | 28 | 0.0002086 | 7.45e-06 | No
12/09/2018 | 10:45:00 | CD16 | Rural Short | Planned |  | 3 | 232.6667 | 0.0052002 | 2.235e-05 | No
12/09/2018 | 10:58:22 | PA28 | Rural Long | Planned |  | 4 | 17 | 0.00049629 | 2.919e-05 | No
12/09/2018 | 11:05:36 | R17 | Rural Long | Planned |  | 39 | 206 | 0.058635 | 0.00028464 | No
12/09/2018 | 11:36:00 | LM52 | Rural Long | Planned |  | 45 | 209 | 0.068641 | 0.00032843 | No
12/09/2018 | 12:13:13 | MG19 | Rural Long | Asset failure | LV | 1 | 151 | 0.0011021 | 7.3e-06 | No
12/09/2018 | 13:19:00 | MV14 | Rural Short | Planned |  | 32 | 47.6875 | 0.011369 | 0.0002384 | No
12/09/2018 | 14:05:00 | M23 | Rural Long | Unknown | Unknown | 26 | 36 | 0.0068312 | 0.00018976 | No
12/09/2018 | 14:32:17 | SA17 | Urban | Asset failure | LV | 16 | 120 | 0.0030695 | 2.558e-05 | No
12/09/2018 | 15:54:37 | MB14 | Rural Short | Unknown | Unknown | 61 | 12 | 0.0054535 | 0.00045446 | No
12/09/2018 | 16:44:42 | SA17 | Urban | Asset failure | LV | 2.6667 | 146 | 0.00062242 | 4.26e-06 | No
12/09/2018 | 18:34:37 | MI09 | Rural Long | Asset failure | HV | 52 | 293.4615 | 0.11137 | 0.00037951 | No
12/09/2018 | 21:23:58 | HH130F | Urban | Asset failure | LV | 1 | 82 | 0.00013109 | 1.6e-06 | No
12/09/2018 | 23:22:02 | SB01 | Rural Long | Other |  | 19.3333 | 175 | 0.024693 | 0.0001411 | No
13/09/2018 | 08:32:45 | NU33 | Rural Long | Planned |  | 17 | 386 | 0.047892 | 0.00012407 | No
13/09/2018 | 08:37:57 | PL07 | Urban | Planned |  | 4 | 103 | 0.00065865 | 6.39e-06 | No
13/09/2018 | 08:51:13 | MT01 | Rural Long | Planned |  | 98 | 313 | 0.22387 | 0.00071524 | No
13/09/2018 | 08:52:01 | PA24 | Rural Long | Planned |  | 26 | 199 | 0.037762 | 0.00018976 | No
13/09/2018 | 08:53:19 | ST42 | Rural Long | Planned |  | 19 | 249 | 0.034528 | 0.00013867 | No
13/09/2018 | 08:57:39 | MI17 | Rural Long | Asset failure | HV | 2 | 63 | 0.00091959 | 1.46e-05 | No
13/09/2018 | 09:02:30 | BT02 | Rural Long | Planned |  | 15 | 201 | 0.022004 | 0.00010948 | No
13/09/2018 | 09:10:52 | SG14 | Rural Short | Planned |  | 19 | 334 | 0.047279 | 0.00014155 | No
13/09/2018 | 09:12:02 | AP125A | Urban | Overloads |  | 58 | 148 | 0.013723 | 9.272e-05 | No
13/09/2018 | 09:24:52 | HH429C | Urban | Planned |  | 50 | 304 | 0.0243 | 7.993e-05 | No
13/09/2018 | 09:30:52 | MTB22 | Rural Short | Unknown | Unknown | 35 | 138 | 0.035984 | 0.00026076 | No
13/09/2018 | 09:32:10 | NL760B | Urban | Planned |  | 72 | 181 | 0.020834 | 0.0001151 | No
13/09/2018 | 09:48:11 | NL760A | Urban | Planned |  | 4 | 342 | 0.002187 | 6.39e-06 | No
13/09/2018 | 09:51:31 | MV63 | Rural Short | Planned |  | 30 | 148 | 0.033079 | 0.0002235 | No
13/09/2018 | 10:00:01 | YK19 | Rural Long | Planned |  | 16 | 166 | 0.019384 | 0.00011677 | No
13/09/2018 | 10:00:31 | KI53 | Rural Long | Planned |  | 1 | 89 | 0.00064955 | 7.3e-06 | No
13/09/2018 | 10:05:43 | NU15 | Rural Long | Planned |  | 1 | 242 | 0.0017662 | 7.3e-06 | No
13/09/2018 | 10:19:00 | AP424E | Urban | Planned |  | 256 | 148.5469 | 0.060794 | 0.00040926 | No
13/09/2018 | 10:31:47 | CBD412A | CBD | Planned |  | 6 | 102 | 0.1188 | 0.0011647 | No
13/09/2018 | 10:44:07 | CD25 | Rural Long | Planned |  | 9 | 66 | 0.0043352 | 6.569e-05 | No
13/09/2018 | 11:23:00 | CM18 | Rural Long | Planned |  | 33 | 54 | 0.013006 | 0.00024085 | No
13/09/2018 | 11:39:28 | NA61 | Rural Long | Planned |  | 69 | 2 | 0.0010072 | 0.00050359 | No
13/09/2018 | 11:49:55 | SA711E | Urban | Network business | Switching and protection error | 1 | 49 | 7.834e-05 | 1.6e-06 | No
13/09/2018 | 14:05:16 | ME200C | Urban | Other |  | 2 | 74 | 0.0002366 | 3.2e-06 | No
13/09/2018 | 14:42:35 | W15 | Rural Long | Planned |  | 1 | 22 | 0.00016056 | 7.3e-06 | No
13/09/2018 | 15:04:31 | ME200A | Urban | Asset failure | HV | 6 | 4 | 3.837e-05 | 9.59e-06 | No
13/09/2018 | 17:30:52 | AP125D | Urban | Overloads |  | 15.6667 | 38 | 0.00095174 | 2.505e-05 | No
13/09/2018 | 17:40:06 | PP10 | Urban | Unknown | Unknown | 105 | 28 | 0.0047001 | 0.00016786 | No
14/09/2018 | 05:15:30 | G13 | Rural Long | Animal | Animal impact | 106 | 244 | 0.18876 | 0.00077362 | No
14/09/2018 | 05:15:55 | NU13 | Rural Long | Third Party | Other | 1 | 176 | 0.0012845 | 7.3e-06 | No
14/09/2018 | 07:35:35 | NA29 | Rural Long | Asset failure | HV | 2 | 112 | 0.0016348 | 1.46e-05 | No
14/09/2018 | 08:34:40 | MV53 | Rural Short | Planned |  | 187 | 250.4492 | 0.34892 | 0.0013932 | No
14/09/2018 | 08:47:04 | HH107A | Urban | Asset failure | LV | 77 | 102 | 0.012556 | 0.0001231 | No
14/09/2018 | 08:47:27 | HH107A | Urban | Asset failure | LV | 105 | 99 | 0.016618 | 0.00016786 | No
14/09/2018 | 08:55:26 | GA43 | Rural Short | Planned |  | 137 | 413 | 0.42154 | 0.0010207 | No
14/09/2018 | 09:01:17 | HH429C | Urban | Planned |  | 1 | 97 | 0.00015507 | 1.6e-06 | No
14/09/2018 | 09:05:06 | HH341G | Urban | Planned |  | 104 | 339 | 0.056363 | 0.00016626 | No
14/09/2018 | 09:16:55 | BM31 | Rural Short | Planned |  | 16 | 325 | 0.038741 | 0.0001192 | No
14/09/2018 | 09:24:00 | AP125A | Urban | Planned |  | 296 | 297 | 0.14054 | 0.00047321 | No
14/09/2018 | 09:24:58 | AP373E | Urban | Planned |  | 40 | 195 | 0.01247 | 6.395e-05 | No
14/09/2018 | 09:36:30 | AP373E | Urban | Planned |  | 2 | 91 | 0.00029096 | 3.2e-06 | No
14/09/2018 | 09:37:16 | MB11 | Rural Short | Unknown | Unknown | 1 | 85 | 0.00063326 | 7.45e-06 | No
14/09/2018 | 09:48:19 | HH341J | Urban | Planned |  | 78 | 142 | 0.017707 | 0.0001247 | No
14/09/2018 | 09:54:08 | AP146C | Urban | Planned |  | 101 | 274 | 0.044242 | 0.00016147 | No
14/09/2018 | 09:58:35 | EL12 | Urban | Planned |  | 93 | 283 | 0.042076 | 0.00014868 | No
14/09/2018 | 09:59:05 | HH429C | Urban | Planned |  | 1 | 39 | 6.235e-05 | 1.6e-06 | No
14/09/2018 | 10:42:16 | GU23 | Rural Long | Asset failure | LV | 3 | 269 | 0.0058898 | 2.19e-05 | No
14/09/2018 | 10:54:49 | MTB71 | Rural Short | Planned |  | 1 | 3 | 2.235e-05 | 7.45e-06 | No
14/09/2018 | 11:13:16 | HH107C | Urban | Asset failure | LV | 57 | 78 | 0.0071077 | 9.112e-05 | No
14/09/2018 | 11:18:01 | M21 | Rural Long | Planned |  | 39 | 17 | 0.0048388 | 0.00028464 | No
14/09/2018 | 12:09:41 | WK21 | Rural Short | Asset failure | LV | 1 | 14 | 0.0001043 | 7.45e-06 | No
14/09/2018 | 12:56:00 | MV63 | Rural Short | Asset failure | HV | 187 | 112.4492 | 0.15666 | 0.0013932 | No
14/09/2018 | 16:08:39 | VH32 | Rural Short | Unknown | Unknown | 1 | 41 | 0.00030546 | 7.45e-06 | No
14/09/2018 | 16:27:14 | MTB22 | Rural Short | Asset failure | LV | 3 | 19 | 0.00042466 | 2.235e-05 | No
14/09/2018 | 19:35:33 | KA29 | Rural Long | Overloads |  | 1 | 161 | 0.001175 | 7.3e-06 | No
14/09/2018 | 21:35:13 | SB21 | Rural Long | Asset failure | HV | 1 | 113 | 0.00082471 | 7.3e-06 | No
15/09/2018 | 02:57:00 | ST15 | Rural Short | Unknown | Unknown | 86 | 235 | 0.15057 | 0.00064071 | No
15/09/2018 | 03:01:00 | ST22 | Rural Short | Asset failure | HV | 208.0001 | 115.6538 | 0.17922 | 0.0015496 | No
15/09/2018 | 03:10:04 | M92 | Rural Long | Unknown | Unknown | 454 | 214 | 0.70908 | 0.0033134 | No
15/09/2018 | 03:13:10 | HH177D | Urban | Vegetation | Grow-in - NSP responsibility | 47.3334 | 382 | 0.028906 | 7.567e-05 | No
15/09/2018 | 03:39:47 | MI28 | Rural Long | Unknown | Unknown | 51 | 206 | 0.076676 | 0.00037222 | No
15/09/2018 | 04:07:20 | SM374B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 118 | 0.00018864 | 1.6e-06 | No
15/09/2018 | 04:28:22 | R16 | Rural Long | Asset failure | HV | 89 | 212.2697 | 0.13788 | 0.00064955 | No
15/09/2018 | 05:22:16 | ME200A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 964 | 56 | 0.086303 | 0.0015411 | No
15/09/2018 | 05:53:55 | AP149E | Urban | Asset failure | LV | 26 | 203 | 0.0084378 | 4.157e-05 | No
15/09/2018 | 06:21:19 | NU05 | Rural Short | Unknown | Unknown | 499 | 117 | 0.43496 | 0.0037176 | No
15/09/2018 | 06:30:55 | HH107B | Urban | Asset failure | LV | 29.6666 | 300 | 0.014228 | 4.743e-05 | No
15/09/2018 | 06:32:17 | AP125C | Urban | Weather |  | 69 | 306 | 0.033754 | 0.00011031 | No
15/09/2018 | 06:32:37 | HH409D | Urban | Asset failure | HV | 774 | 189.5323 | 0.23452 | 0.0012374 | No
15/09/2018 | 06:34:59 | HH409D | Urban | Asset failure | HV | 1 | 275 | 0.00043964 | 1.6e-06 | No
15/09/2018 | 06:40:45 | HH130F | Urban | Vegetation | Grow-in - NSP responsibility | 29.3333 | 371 | 0.017398 | 4.689e-05 | No
15/09/2018 | 07:01:40 | SM350E | Urban | Unknown | Unknown | 62 | 16 | 0.0015859 | 9.912e-05 | No
15/09/2018 | 07:01:51 | HH429B | Urban | Weather |  | 32 | 216 | 0.01105 | 5.116e-05 | No
15/09/2018 | 07:08:04 | HH428F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 6.3333 | 224 | 0.002268 | 1.012e-05 | No
15/09/2018 | 07:56:59 | GA08 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 331 | 0.038652 | 0.00011677 | No
15/09/2018 | 08:05:09 | SG11 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1.3333 | 330 | 0.0032781 | 9.93e-06 | No
15/09/2018 | 08:11:45 | VH12 | Rural Short | Asset failure | LV | 1 | 199 | 0.0014826 | 7.45e-06 | No
15/09/2018 | 08:57:00 | HH177B | Urban | Vegetation | Grow-in - NSP responsibility | 602 | 105 | 0.10105 | 0.0009624 | No
15/09/2018 | 08:59:30 | HH432C | Urban | Weather |  | 22.6666 | 159 | 0.0057616 | 3.624e-05 | No
15/09/2018 | 08:59:59 | M92 | Rural Long | Unknown | Unknown | 454 | 223.0176 | 0.73896 | 0.0033134 | No
15/09/2018 | 09:56:41 | BT03 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 167 | 153 | 0.18648 | 0.0012188 | No
15/09/2018 | 10:14:12 | PL07 | Urban | Asset failure | LV | 1 | 99 | 0.00015827 | 1.6e-06 | No
15/09/2018 | 11:08:01 | MI23 | Rural Long | Asset failure | HV | 92 | 226.3043 | 0.15195 | 0.00067145 | No
15/09/2018 | 11:20:36 | HH428F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 50 | 7.993e-05 | 1.6e-06 | No
15/09/2018 | 12:05:06 | VH12 | Rural Short | Weather |  | 32 | 125 | 0.029801 | 0.0002384 | No
15/09/2018 | 13:03:49 | NA05 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 127 | 138.2677 | 0.12816 | 0.00092689 | No
15/09/2018 | 13:04:54 | MB12 | Rural Short | Unknown | Unknown | 1974 | 10.9899 | 0.16162 | 0.014707 | No
15/09/2018 | 13:39:12 | HH121C | Urban | Unknown | Unknown | 32 | 136 | 0.0069574 | 5.116e-05 | No
15/09/2018 | 14:02:41 | G06 | Rural Long | Asset failure | HV | 62 | 299 | 0.1353 | 0.0004525 | No
15/09/2018 | 14:14:38 | ST34 | Rural Long | Unknown | Unknown | 55 | 172 | 0.069042 | 0.00040141 | No
15/09/2018 | 15:28:00 | HH496D | Urban | Asset failure | LV | 2 | 77 | 0.0002462 | 3.2e-06 | No
15/09/2018 | 16:11:04 | LM43 | Rural Long | Asset failure | HV | 1 | 584 | 0.0042622 | 7.3e-06 | No
15/09/2018 | 17:28:56 | AP424E | Urban | Asset failure | LV | 34.3333 | 215 | 0.011801 | 5.489e-05 | No
15/09/2018 | 17:50:51 | ME131D | Urban | Asset failure | LV | 86 | 72 | 0.009899 | 0.00013749 | No
15/09/2018 | 17:58:49 | NL451C | Urban | Asset failure | LV | 1 | 86 | 0.00013749 | 1.6e-06 | No
15/09/2018 | 18:06:53 | GA745B | Rural Short | Asset failure | LV | 28 | 232 | 0.048396 | 0.0002086 | No
15/09/2018 | 18:51:51 | NL115B | Urban | Unknown | Unknown | 26 | 117 | 0.0048632 | 4.157e-05 | No
15/09/2018 | 23:58:49 | SM349H | Urban | Asset failure | LV | 1 | 207 | 0.00033093 | 1.6e-06 | No
16/09/2018 | 05:33:44 | WHY07 | Urban | Unknown | Unknown | 154 | 216 | 0.053178 | 0.0002462 | No
16/09/2018 | 06:30:39 | GA02 | Rural Short | Planned |  | 22 | 571 | 0.093589 | 0.0001639 | No
16/09/2018 | 06:35:00 | R17 | Rural Long | Asset failure | HV | 71 | 133.4225 | 0.069137 | 0.00051818 | No
16/09/2018 | 07:49:29 | AP373E | Urban | Planned |  | 6 | 212 | 0.0020335 | 9.59e-06 | No
16/09/2018 | 08:03:39 | NL760C | Urban | Asset failure | LV | 18.3333 | 86 | 0.0025206 | 2.931e-05 | No
16/09/2018 | 08:36:37 | YK17 | Rural Long | Planned |  | 1186 | 411 | 3.5575 | 0.0086558 | No
16/09/2018 | 08:39:57 | AP373C | Urban | Planned |  | 1 | 44 | 7.034e-05 | 1.6e-06 | No
16/09/2018 | 09:10:26 | GA800A | Rural Short | Planned |  | 16 | 319 | 0.038026 | 0.0001192 | No
16/09/2018 | 09:12:08 | HH177A | Urban | Planned |  | 21 | 189 | 0.0063451 | 3.357e-05 | No
16/09/2018 | 09:30:41 | HH341G | Urban | Asset failure | LV | 33 | 164 | 0.008652 | 5.276e-05 | No
16/09/2018 | 10:41:22 | ST15 | Rural Short | Asset failure | HV | 86 | 252.1628 | 0.16156 | 0.00064071 | No
16/09/2018 | 13:08:00 | MG27 | Rural Long | Asset failure | HV | 3 | 204.6667 | 0.0044812 | 2.19e-05 | No
16/09/2018 | 17:23:38 | AP355B | Urban | Asset failure | LV | 1 | 203 | 0.00032453 | 1.6e-06 | No
16/09/2018 | 17:40:28 | MB23 | Rural Short | Asset failure | LV | 27.3333 | 97 | 0.019753 | 0.00020364 | No
16/09/2018 | 17:56:01 | CN41 | Rural Long | Unknown | Unknown | 1 | 11 | 8.028e-05 | 7.3e-06 | No
16/09/2018 | 18:38:39 | NL451C | Urban | Planned |  | 2427 | 1 | 0.00388 | 0.00388 | No
17/09/2018 | 00:36:20 | SM172B | Urban | Planned |  | 1 | 146 | 0.00023341 | 1.6e-06 | No
17/09/2018 | 01:38:00 | SD49200 | Rural Long | Unknown | Unknown | 6480 | 131.6102 | 6.2243 | 0.047293 | No
17/09/2018 | 07:56:25 | HH118D | Urban | Asset failure | LV | 16 | 216 | 0.005525 | 2.558e-05 | No
17/09/2018 | 08:35:26 | MG05 | Rural Long | Planned |  | 19 | 220 | 0.030507 | 0.00013867 | No
17/09/2018 | 08:37:10 | ST43 | Rural Long | Planned |  | 39 | 197 | 0.056073 | 0.00028464 | No
17/09/2018 | 08:37:29 | BM34 | Rural Short | Planned |  | 1 | 58 | 0.00043211 | 7.45e-06 | No
17/09/2018 | 09:22:21 | W27 | Rural Long | Planned |  | 7 | 143 | 0.0073056 | 5.109e-05 | No
17/09/2018 | 09:31:16 | MB32 | Rural Long | Planned |  | 6 | 201 | 0.0088018 | 4.379e-05 | No
17/09/2018 | 09:34:52 | MV64 | Urban | Planned |  | 26 | 113 | 0.0046969 | 4.157e-05 | No
17/09/2018 | 09:36:56 | HH341C | Urban | Planned |  | 1 | 326 | 0.00052117 | 1.6e-06 | No
17/09/2018 | 09:50:00 | MV14 | Rural Short | Planned |  | 11 | 109 | 0.0089327 | 8.195e-05 | No
17/09/2018 | 09:51:49 | HH341E | Urban | Planned |  | 6 | 312 | 0.0029927 | 9.59e-06 | No
17/09/2018 | 09:53:07 | VH32 | Rural Short | Planned |  | 16 | 219 | 0.026105 | 0.0001192 | No
17/09/2018 | 09:55:35 | MTB15 | Urban | Unknown | Unknown | 21 | 45 | 0.0015107 | 3.357e-05 | No
17/09/2018 | 10:05:43 | MI14 | Rural Long | Unknown | Unknown | 2 | 59 | 0.0008612 | 1.46e-05 | No
17/09/2018 | 10:05:51 | HH341J | Urban | Planned |  | 247 | 41 | 0.01619 | 0.00039487 | No
17/09/2018 | 10:13:08 | AP365A | Urban | Third Party | Vehicle impact | 2647 | 129.7185 | 0.54893 | 0.0042317 | No
17/09/2018 | 10:38:47 | G32 | Rural Long | Planned |  | 10 | 51 | 0.0037222 | 7.298e-05 | No
17/09/2018 | 10:45:36 | KI53 | Rural Long | Planned |  | 2 | 119 | 0.001737 | 1.46e-05 | No
17/09/2018 | 11:19:09 | HH496D | Urban | Asset failure | LV | 1 | 344 | 0.00054994 | 1.6e-06 | No
17/09/2018 | 11:27:29 | ST36 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 420 | 266.3143 | 0.81633 | 0.0030653 | No
17/09/2018 | 11:58:56 | BU09 | Rural Long | Asset failure | LV | 2 | 207 | 0.0030215 | 1.46e-05 | No
17/09/2018 | 12:14:14 | SM216E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 110 | 0.00017585 | 1.6e-06 | No
17/09/2018 | 12:41:26 | ST43 | Rural Long | Unknown | Unknown | 15 | 28.6667 | 0.0031383 | 0.00010948 | No
17/09/2018 | 13:33:00 | SD38200 | Rural Long | Planned |  | 498 | 7.4438 | 0.027055 | 0.0036346 | No
17/09/2018 | 13:51:24 | MG34 | Rural Long | Unknown | Unknown | 249 | 80 | 0.14538 | 0.0018173 | No
17/09/2018 | 14:53:21 | HH130F | Urban | Planned |  | 14 | 1783 | 0.039906 | 2.238e-05 | No
17/09/2018 | 17:28:23 | HH130B | Urban | Asset failure | LV | 28 | 37 | 0.0016562 | 4.476e-05 | No
17/09/2018 | 20:41:15 | EL01N | Urban | Third Party | Other | 1 | 47 | 7.514e-05 | 1.6e-06 | No
17/09/2018 | 22:40:58 | HH409D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 5.3333 | 299 | 0.0025494 | 8.53e-06 | No
18/09/2018 | 06:45:40 | NL511A | Urban | Asset failure | LV | 1 | 159 | 0.00025419 | 1.6e-06 | No
18/09/2018 | 08:45:37 | HH341F | Urban | Planned |  | 124 | 62 | 0.012291 | 0.00019824 | No
18/09/2018 | 09:04:18 | MV62 | Rural Short | Planned |  | 313 | 294 | 0.68558 | 0.0023319 | No
18/09/2018 | 09:42:06 | VH23 | Rural Short | Planned |  | 186 | 329 | 0.4559 | 0.0013857 | No
18/09/2018 | 09:52:06 | ST13 | Rural Short | Planned |  | 216 | 297 | 0.47794 | 0.0016092 | No
18/09/2018 | 10:03:58 | NU02 | Rural Long | Planned |  | 1 | 10 | 7.298e-05 | 7.3e-06 | No
18/09/2018 | 10:14:55 | BT22 | Rural Long | Unknown | Unknown | 3 | 431 | 0.0094368 | 2.19e-05 | No
18/09/2018 | 10:29:47 | ST21 | Rural Short | Planned |  | 126 | 177 | 0.16615 | 0.00093872 | No
18/09/2018 | 10:30:31 | CM28 | Rural Long | Planned |  | 1 | 783 | 0.0057146 | 7.3e-06 | No
18/09/2018 | 10:30:51 | KI53 | Rural Long | Planned |  | 2 | 175 | 0.0025544 | 1.46e-05 | No
18/09/2018 | 11:02:53 | KI55 | Rural Long | Asset failure | LV | 2 | 175 | 0.0025544 | 1.46e-05 | No
18/09/2018 | 11:30:56 | HH118A | Urban | Third Party | Vehicle impact | 1 | 130 | 0.00020783 | 1.6e-06 | No
18/09/2018 | 12:14:56 | CM28 | Rural Long | Planned |  | 7 | 71 | 0.0036273 | 5.109e-05 | No
18/09/2018 | 12:16:51 | HH145C | Urban | Overloads |  | 1 | 91 | 0.00014548 | 1.6e-06 | No
18/09/2018 | 12:18:08 | GA05 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 128 | 0.040052 | 0.00031291 | No
18/09/2018 | 12:35:36 | CM15 | Rural Long | Planned |  | 68 | 99 | 0.049132 | 0.00049629 | No
18/09/2018 | 14:07:50 | MI21 | Rural Long | Unknown | Unknown | 2 | 5 | 7.298e-05 | 1.46e-05 | No
18/09/2018 | 14:19:12 | SA14 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 45 | 58 | 0.0041725 | 7.194e-05 | No
18/09/2018 | 14:27:54 | EL260C | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
18/09/2018 | 14:29:13 | AP344D | Urban | Asset failure | LV | 1 | 228 | 0.0003645 | 1.6e-06 | No
18/09/2018 | 14:54:38 | SA11 | Urban | Asset failure | LV | 2 | 142 | 0.00045402 | 3.2e-06 | No
18/09/2018 | 16:05:07 | NL111C | Urban | Asset failure | LV | 69 | 77 | 0.0084938 | 0.00011031 | No
18/09/2018 | 18:20:20 | HH432B | Urban | Asset failure | LV | 27 | 41 | 0.0017697 | 4.316e-05 | No
18/09/2018 | 19:26:31 | YK03 | Rural Long | Asset failure | LV | 1 | 55 | 0.00040141 | 7.3e-06 | No
18/09/2018 | 20:45:24 | CBD367M | CBD | Planned |  | 1 | 409 | 0.079394 | 0.00019412 | No
18/09/2018 | 22:35:45 | SM374A | Urban | Other |  | 34 | 68 | 0.0036961 | 5.435e-05 | No
18/09/2018 | 22:59:17 | SM411E | Urban | Asset failure | LV | 71 | 119 | 0.013507 | 0.00011351 | No
19/09/2018 | 00:27:00 | AP125A | Urban | Planned |  | 59 | 89 | 0.0083946 | 9.432e-05 | No
19/09/2018 | 02:25:01 | CN52 | Rural Long | Unknown | Unknown | 88 | 274.0114 | 0.17598 | 0.00064225 | No
19/09/2018 | 05:56:11 | SA520E | Urban | Overloads |  | 1 | 333 | 0.00053236 | 1.6e-06 | No
19/09/2018 | 07:36:34 | NL111C | Urban | Overloads |  | 26.3333 | 84 | 0.0035363 | 4.21e-05 | No
19/09/2018 | 08:21:23 | KA03 | Rural Long | Planned |  | 163 | 315 | 0.37473 | 0.0011896 | No
19/09/2018 | 08:48:41 | ME427B | Urban | Asset failure | LV | 42 | 176 | 0.011817 | 6.714e-05 | No
19/09/2018 | 09:03:53 | G13 | Rural Long | Planned |  | 21 | 316 | 0.048432 | 0.00015327 | No
19/09/2018 | 09:05:37 | SA744D | Urban | Vegetation | Grow-in - NSP responsibility | 22.6667 | 79 | 0.0028627 | 3.624e-05 | No
19/09/2018 | 09:07:37 | HH341A | Urban | Planned |  | 22 | 46 | 0.0016179 | 3.517e-05 | No
19/09/2018 | 09:20:18 | HH107B | Urban | Planned |  | 1 | 67 | 0.00010711 | 1.6e-06 | No
19/09/2018 | 09:20:40 | MI03 | Rural Long | Planned |  | 16 | 350 | 0.040871 | 0.00011677 | No
19/09/2018 | 09:40:01 | VH23 | Rural Short | Planned |  | 232 | 279 | 0.48223 | 0.0017284 | No
19/09/2018 | 09:46:05 | SA14 | Urban | Planned |  | 52 | 245 | 0.020367 | 8.313e-05 | No
19/09/2018 | 09:52:57 | MV13 | Rural Short | Planned |  | 43 | 171 | 0.054781 | 0.00032036 | No
19/09/2018 | 09:55:04 | HH121C | Urban | Planned |  | 44 | 264 | 0.01857 | 7.034e-05 | No
19/09/2018 | 10:39:33 | CV19 | Rural Long | Planned |  | 54 | 224 | 0.088281 | 0.00039411 | No
19/09/2018 | 10:45:10 | HH341G | Urban | Planned |  | 54 | 278 | 0.023999 | 8.633e-05 | No
19/09/2018 | 10:52:33 | W29 | Rural Long | Planned |  | 33 | 66 | 0.015896 | 0.00024085 | No
19/09/2018 | 11:03:08 | LX33 | Rural Short | Animal | Animal impact | 2 | 86 | 0.0012814 | 1.49e-05 | No
19/09/2018 | 11:44:19 | MI01 | Rural Long | Asset failure | LV | 1 | 160 | 0.0011677 | 7.3e-06 | No
19/09/2018 | 12:01:42 | NL760C | Urban | Asset failure | LV | 40 | 1 | 6.395e-05 | 6.395e-05 | No
19/09/2018 | 13:59:16 | M22 | Rural Long | Planned |  | 66 | 36 | 0.017341 | 0.00048169 | No
19/09/2018 | 14:16:50 | SA41 | Urban | Unknown | Unknown | 13 | 49 | 0.0010184 | 2.078e-05 | No
19/09/2018 | 15:13:00 | HH341E | Urban | Third Party | Other | 951 | 46 | 0.069936 | 0.0015203 | No
19/09/2018 | 18:23:52 | SM410C | Urban | Other |  | 1.3333 | 212 | 0.00045189 | 2.13e-06 | No
19/09/2018 | 18:32:57 | HH522A | Urban | Asset failure | LV | 1 | 258 | 0.00041246 | 1.6e-06 | No
19/09/2018 | 18:33:07 | GA15 | Rural Short | Third Party | Vehicle impact | 1 | 185 | 0.0013783 | 7.45e-06 | No
19/09/2018 | 19:31:01 | HH428F | Urban | Unknown | Unknown | 6.3333 | 37 | 0.00037462 | 1.012e-05 | No
19/09/2018 | 21:23:13 | HH386G | Urban | Weather |  | 13.6667 | 150 | 0.0032773 | 2.185e-05 | No
20/09/2018 | 00:25:06 | SA17 | Urban | Asset failure | HV | 35.3334 | 152 | 0.008586 | 5.649e-05 | No
20/09/2018 | 00:25:35 | SA17 | Urban | Asset failure | HV | 41.3334 | 150 | 0.0099118 | 6.608e-05 | No
20/09/2018 | 06:56:56 | HH121B | Urban | Vegetation | Grow-in - NSP responsibility | 62 | 190 | 0.018832 | 9.912e-05 | No
20/09/2018 | 07:06:13 | HH341C | Urban | Asset failure | LV | 1 | 260 | 0.00041566 | 1.6e-06 | No
20/09/2018 | 08:41:12 | SD38200 | Rural Long | Planned |  | 228 | 67.4211 | 0.11219 | 0.001664 | No
20/09/2018 | 08:50:33 | WHY03 | Urban | Planned |  | 37 | 292 | 0.017272 | 5.915e-05 | No
20/09/2018 | 08:51:59 | SB15 | Rural Long | Planned |  | 43 | 318 | 0.099797 | 0.00031383 | No
20/09/2018 | 09:02:32 | KI56 | Rural Long | Planned |  | 69 | 263 | 0.13244 | 0.00050359 | No
20/09/2018 | 09:14:02 | W16 | Rural Long | Planned |  | 2 | 63 | 0.00091959 | 1.46e-05 | No
20/09/2018 | 09:14:32 | NL111Q | Urban | Planned |  | 512 | 286 | 0.2341 | 0.00081852 | No
20/09/2018 | 09:23:05 | GA15 | Rural Short | Planned |  | 23 | 252 | 0.043181 | 0.00017135 | No
20/09/2018 | 09:28:58 | MG45 | Urban | Asset failure | LV | 1 | 243 | 0.00038848 | 1.6e-06 | No
20/09/2018 | 09:29:23 | ST41 | Rural Long | Planned |  | 21 | 382 | 0.058547 | 0.00015327 | No
20/09/2018 | 09:34:14 | HH428F | Urban | Overloads |  | 1 | 216 | 0.00034531 | 1.6e-06 | No
20/09/2018 | 09:42:37 | EL01C | Urban | Asset failure | LV | 1 | 212 | 0.00033892 | 1.6e-06 | No
20/09/2018 | 10:11:37 | YK19 | Rural Long | Planned |  | 10 | 78 | 0.0056927 | 7.298e-05 | No
20/09/2018 | 10:43:40 | MI14 | Rural Long | Planned |  | 7 | 13 | 0.00066415 | 5.109e-05 | No
20/09/2018 | 10:47:00 | SM126A | Urban | Unknown | Unknown | 144 | 203 | 0.046732 | 0.00023021 | No
20/09/2018 | 11:03:57 | PL30 | Rural Long | Planned |  | 1 | 5759 | 0.042031 | 7.3e-06 | No
20/09/2018 | 11:42:31 | HH121B | Urban | Planned |  | 1 | 331 | 0.00052916 | 1.6e-06 | No
20/09/2018 | 13:31:53 | YK28 | Rural Long | Planned |  | 5 | 58 | 0.0021165 | 3.649e-05 | No
20/09/2018 | 14:30:18 | SM374A | Urban | Asset failure | LV | 1 | 8641 | 0.013814 | 1.6e-06 | No
20/09/2018 | 15:35:52 | SG03 | Rural Short | Overloads |  | 1 | 157 | 0.0011697 | 7.45e-06 | No
20/09/2018 | 15:44:44 | HH409D | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 118 | 0.00018864 | 1.6e-06 | No
20/09/2018 | 19:37:54 | SA12 | Urban | Asset failure | LV | 85 | 104 | 0.014132 | 0.00013589 | No
20/09/2018 | 19:54:43 | EL01C | Urban | Asset failure | LV | 1 | 767 | 0.0012262 | 1.6e-06 | No
20/09/2018 | 21:03:39 | ME347A | Urban | Asset failure | LV | 84 | 100 | 0.013429 | 0.00013429 | No
20/09/2018 | 21:55:25 | HH177G | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 162 | 0.00025899 | 1.6e-06 | No
21/09/2018 | 02:37:43 | CBD367N | CBD | Planned |  | 9 | 3 | 0.0052412 | 0.0017471 | No
21/09/2018 | 02:37:43 | CBD367N | Urban | Planned |  | 22 | 3 | 0.00010551 | 3.517e-05 | No
21/09/2018 | 08:15:24 | BM21 | Rural Short | Planned |  | 15 | 331 | 0.03699 | 0.00011175 | No
21/09/2018 | 08:21:05 | KI13 | Rural Long | Planned |  | 17 | 364 | 0.045162 | 0.00012407 | No
21/09/2018 | 08:29:44 | SB18 | Rural Long | Planned |  | 7 | 39 | 0.0019925 | 5.109e-05 | No
21/09/2018 | 08:41:35 | MTB52 | Rural Long | Planned |  | 30 | 181 | 0.03963 | 0.00021895 | No
21/09/2018 | 08:45:09 | VH12 | Rural Short | Planned |  | 90 | 335 | 0.22462 | 0.00067051 | No
21/09/2018 | 08:45:31 | SB22 | Rural Long | Planned |  | 3 | 57 | 0.001248 | 2.19e-05 | No
21/09/2018 | 08:45:44 | NL511A | Urban | Asset failure | LV | 1 | 282 | 0.00045083 | 1.6e-06 | No
21/09/2018 | 08:55:08 | AP529B | Urban | Planned |  | 52 | 315 | 0.026186 | 8.313e-05 | No
21/09/2018 | 08:58:59 | ME427E | Urban | Planned |  | 96 | 300 | 0.046042 | 0.00015347 | No
21/09/2018 | 08:59:13 | NU19 | Rural Long | Planned |  | 5 | 313 | 0.011422 | 3.649e-05 | No
21/09/2018 | 09:03:35 | ST44 | Rural Long | Planned |  | 117 | 346 | 0.29545 | 0.00085391 | No
21/09/2018 | 09:10:12 | MI18 | Rural Long | Planned |  | 31 | 23 | 0.0052037 | 0.00022625 | No
21/09/2018 | 09:15:37 | GU31 | Rural Long | Planned |  | 2 | 413 | 0.0060284 | 1.46e-05 | No
21/09/2018 | 09:26:26 | MV12 | Urban | Planned |  | 5 | 313 | 0.0025019 | 7.99e-06 | No
21/09/2018 | 09:34:37 | AP373A | Urban | Planned |  | 13 | 258 | 0.005362 | 2.078e-05 | No
21/09/2018 | 09:53:45 | MV31 | Rural Short | Planned |  | 4 | 88 | 0.0026225 | 2.98e-05 | No
21/09/2018 | 10:00:35 | G11 | Rural Long | Planned |  | 33 | 141 | 0.033959 | 0.00024085 | No
21/09/2018 | 10:03:33 | LM13 | Rural Long | Asset failure | HV | 80 | 197 | 0.11502 | 0.00058387 | No
21/09/2018 | 10:06:07 | CM02 | Rural Long | Planned |  | 2 | 158 | 0.0023063 | 1.46e-05 | No
21/09/2018 | 10:11:24 | GA37 | Rural Long | Planned |  | 22 | 288 | 0.046242 | 0.00016056 | No
21/09/2018 | 10:24:35 | M81 | Rural Long | Planned |  | 61 | 282 | 0.12555 | 0.0004452 | No
21/09/2018 | 10:39:54 | SA32 | Urban | Asset failure | LV | 1 | 162 | 0.00025899 | 1.6e-06 | No
21/09/2018 | 10:42:32 | CV18 | Rural Short | Planned |  | 17 | 130 | 0.016465 | 0.00012665 | No
21/09/2018 | 10:47:02 | GA52 | Rural Long | Planned |  | 58 | 195 | 0.082544 | 0.0004233 | No
21/09/2018 | 11:01:08 | BU02 | Rural Long | Planned |  | 1 | 64 | 0.00046709 | 7.3e-06 | No
21/09/2018 | 11:14:26 | VH23 | Rural Short | Planned |  | 686 | 241 | 1.2317 | 0.0051108 | No
21/09/2018 | 12:25:21 | AP226B | Urban | Planned |  | 12 | 1 | 1.918e-05 | 1.918e-05 | No
21/09/2018 | 12:32:18 | MV31 | Rural Short | Planned |  | 10 | 77 | 0.0057366 | 7.45e-05 | No
21/09/2018 | 13:05:39 | AP125D | Urban | Planned |  | 31 | 1 | 4.956e-05 | 4.956e-05 | No
21/09/2018 | 15:47:26 | MV64 | Urban | Asset failure | LV | 1 | 320 | 0.00051158 | 1.6e-06 | No
21/09/2018 | 15:51:00 | SD33200 | Rural Long | Animal | Animal impact | 3 | 61 | 0.0013356 | 2.19e-05 | No
21/09/2018 | 17:12:25 | EL11 | Urban | Third Party | Other | 25 | 38 | 0.0015187 | 3.997e-05 | No
21/09/2018 | 18:28:33 | VH31 | Rural Short | Asset failure | LV | 1 | 422 | 0.003144 | 7.45e-06 | No
21/09/2018 | 19:44:09 | AP227D | Urban | Overloads |  | 1 | 99 | 0.00015827 | 1.6e-06 | No
22/09/2018 | 05:13:37 | SA711C | Urban | Asset failure | LV | 1 | 253 | 0.00040446 | 1.6e-06 | No
22/09/2018 | 08:46:27 | AP146C | Urban | Asset failure | LV | 42.3333 | 103 | 0.0069708 | 6.768e-05 | No
22/09/2018 | 09:23:29 | NA33 | Rural Long | Unknown | Unknown | 232 | 83 | 0.14054 | 0.0016932 | No
22/09/2018 | 09:28:41 | VH72 | Rural Short | Planned |  | 40 | 333 | 0.099236 | 0.00029801 | No
22/09/2018 | 09:37:54 | VH44 | Rural Short | Planned |  | 26 | 1691 | 0.32755 | 0.0001937 | No
22/09/2018 | 10:07:45 | AP529A | Urban | Planned |  | 358 | 277 | 0.15853 | 0.00057233 | No
22/09/2018 | 11:26:00 | CN24 | Rural Long | Asset failure | HV | 105 | 204.0286 | 0.15635 | 0.00076633 | No
22/09/2018 | 12:56:22 | HH341B | Urban | Third Party | Vehicle impact | 25 | 405 | 0.016187 | 3.997e-05 | No
22/09/2018 | 14:33:47 | HH130A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 129 | 0.0041246 | 3.197e-05 | No
22/09/2018 | 16:17:29 | VH21 | Rural Short | Unknown | Unknown | 269 | 75 | 0.15031 | 0.0020041 | No
22/09/2018 | 17:12:51 | ME200F | Urban | Asset failure | LV | 6 | 162 | 0.0015539 | 9.59e-06 | No
22/09/2018 | 17:15:02 | HH130A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 88 | 0.0028137 | 3.197e-05 | No
22/09/2018 | 22:55:00 | HH121E | Urban | Unknown | Unknown | 18 | 171 | 0.0049207 | 2.878e-05 | No
22/09/2018 | 22:55:00 | HH121E | Urban | Unknown | Unknown | 500 | 3 | 0.002398 | 0.00079934 | No
22/09/2018 | 23:11:35 | SA711C | Urban | Asset failure | LV | 1 | 319 | 0.00050998 | 1.6e-06 | No
22/09/2018 | 23:20:53 | SM350A | Urban | Asset failure | LV | 63 | 110 | 0.011079 | 0.00010072 | No
23/09/2018 | 03:10:25 | SD59100 | Rural Long | Planned |  | 323 | 575 | 1.3555 | 0.0023574 | No
23/09/2018 | 04:09:00 | LC01 | Rural Short | Planned |  | 121 | 511 | 0.46065 | 0.00090147 | No
23/09/2018 | 04:09:00 | LC02 | Rural Long | Planned |  | 237 | 496 | 0.85793 | 0.0017297 | No
23/09/2018 | 05:54:22 | EL19 | Urban | Unknown | Unknown | 27 | 336 | 0.014503 | 4.316e-05 | No
23/09/2018 | 07:20:23 | SM126E | Urban | Third Party | Vehicle impact | 631 | 180 | 0.18158 | 0.0010088 | No
23/09/2018 | 08:35:46 | MG44 | Urban | Planned |  | 14 | 202 | 0.0045211 | 2.238e-05 | No
23/09/2018 | 08:40:57 | EL01N | Urban | Planned |  | 26 | 341 | 0.014174 | 4.157e-05 | No
23/09/2018 | 09:20:11 | VH44 | Rural Short | Planned |  | 3 | 41 | 0.00091637 | 2.235e-05 | No
23/09/2018 | 10:05:14 | AP373C | Urban | Planned |  | 17 | 346 | 0.0094034 | 2.718e-05 | No
23/09/2018 | 10:10:33 | NA33 | Rural Long | Asset failure | HV | 1 | 1504 | 0.010977 | 7.3e-06 | No
23/09/2018 | 10:15:24 | HH429C | Urban | Planned |  | 206 | 210 | 0.069159 | 0.00032933 | No
23/09/2018 | 10:26:30 | SM126E | Urban | Third Party | Vehicle impact | 42 | 361 | 0.024239 | 6.714e-05 | No
23/09/2018 | 10:26:52 | SM126E | Urban | Third Party | Vehicle impact | 40 | 438 | 0.028009 | 6.395e-05 | No
23/09/2018 | 15:48:02 | EL10 | Urban | Asset failure | LV | 18 | 164 | 0.0047193 | 2.878e-05 | No
24/09/2018 | 04:37:41 | HH177A | Urban | Unknown | Unknown | 42 | 117 | 0.0078559 | 6.714e-05 | No
24/09/2018 | 06:45:15 | SA17 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 152 | 0.010206 | 6.714e-05 | No
24/09/2018 | 08:58:17 | GA25 | Rural Short | Planned |  | 11 | 169 | 0.01385 | 8.195e-05 | No
24/09/2018 | 09:02:44 | GA22 | Rural Short | Planned |  | 36 | 254 | 0.068124 | 0.00026821 | No
24/09/2018 | 09:10:00 | KI31 | Rural Short | Planned |  | 2 | 125 | 0.0018625 | 1.49e-05 | No
24/09/2018 | 09:32:43 | MB63 | Rural Long | Planned |  | 18 | 154 | 0.020231 | 0.00013137 | No
24/09/2018 | 09:41:38 | GU33 | Rural Long | Planned |  | 77 | 349 | 0.19613 | 0.00056197 | No
24/09/2018 | 10:07:28 | MG06 | Rural Short | Unknown | Unknown | 145 | 58 | 0.062656 | 0.0010803 | No
24/09/2018 | 10:14:22 | NL111C | Urban | Asset failure | LV | 70 | 100 | 0.011191 | 0.00011191 | No
24/09/2018 | 10:22:14 | W28 | Rural Long | Planned |  | 3 | 257 | 0.005627 | 2.19e-05 | No
24/09/2018 | 10:33:36 | ST11 | Rural Short | Planned |  | 31 | 265 | 0.061203 | 0.00023095 | No
24/09/2018 | 10:39:00 | MV53 | Rural Short | Planned |  | 1 | 92 | 0.00068541 | 7.45e-06 | No
24/09/2018 | 10:47:24 | ME131C | Urban | Asset failure | HV | 92 | 204 | 0.030004 | 0.00014708 | No
24/09/2018 | 11:23:05 | PA02 | Urban | Planned |  | 1 | 74 | 0.0001183 | 1.6e-06 | No
24/09/2018 | 11:53:16 | HH409D | Urban | Asset failure | LV | 97 | 73 | 0.01132 | 0.00015507 | No
24/09/2018 | 12:01:14 | KI31 | Rural Short | Planned |  | 1 | 127 | 0.00094617 | 7.45e-06 | No
24/09/2018 | 12:04:07 | SA32 | Urban | Asset failure | LV | 39 | 160 | 0.0099757 | 6.235e-05 | No
24/09/2018 | 12:06:02 | VH36 | Rural Short | Planned |  | 4 | 50 | 0.00149 | 2.98e-05 | No
24/09/2018 | 13:14:37 | MV22 | Rural Short | Asset failure | LV | 2 | 23 | 0.00034271 | 1.49e-05 | No
24/09/2018 | 13:18:49 | HH341H | Urban | Planned |  | 1 | 95 | 0.00015187 | 1.6e-06 | No
24/09/2018 | 13:28:57 | HH522B | Urban | Asset failure | LV | 1 | 103 | 0.00016466 | 1.6e-06 | No
24/09/2018 | 14:02:48 | AP125D | Urban | Asset failure | LV | 1 | 140 | 0.00022381 | 1.6e-06 | No
24/09/2018 | 14:28:58 | SM216C | Urban | Asset failure | LV | 1 | 110 | 0.00017585 | 1.6e-06 | No
24/09/2018 | 14:31:22 | ST11 | Rural Short | Planned |  | 2 | 112 | 0.0016688 | 1.49e-05 | No
24/09/2018 | 14:44:24 | SA14 | Urban | Third Party | Dig-in | 3415 | 40 | 0.21838 | 0.0054595 | No
24/09/2018 | 14:45:32 | SA32 | Urban | Unknown | Unknown | 39 | 2 | 0.0001247 | 6.235e-05 | No
24/09/2018 | 16:07:06 | VH16 | Rural Short | Asset failure | LV | 1 | 76 | 0.00056621 | 7.45e-06 | No
24/09/2018 | 18:12:53 | CV25 | Rural Long | Unknown | Unknown | 1 | 44 | 0.00032113 | 7.3e-06 | No
24/09/2018 | 19:55:22 | CV25 | Rural Long | Unknown | Unknown | 55 | 4 | 0.0016056 | 0.00040141 | No
24/09/2018 | 20:08:28 | NL234C | Urban | Unknown | Unknown | 29.3333 | 65 | 0.0030481 | 4.689e-05 | No
24/09/2018 | 21:48:03 | AP125B | Urban | Asset failure | LV | 1 | 130 | 0.00020783 | 1.6e-06 | No
25/09/2018 | 00:28:26 | SA744D | Urban | Animal | Animal impact | 1452 | 92.6508 | 0.21507 | 0.0023213 | No
25/09/2018 | 03:26:59 | HH148A | Urban | Unknown | Unknown | 909 | 59.9934 | 0.087182 | 0.0014532 | No
25/09/2018 | 06:25:10 | HH148A | Urban | Animal | Animal impact | 38 | 207 | 0.012575 | 6.075e-05 | No
25/09/2018 | 07:12:27 | G09 | Rural Long | Asset failure | LV | 1 | 229 | 0.0016713 | 7.3e-06 | No
25/09/2018 | 07:14:12 | EL01L | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
25/09/2018 | 07:34:00 | HH107A | Urban | Third Party | Vehicle impact | 2416 | 102.1312 | 0.39447 | 0.0038624 | No
25/09/2018 | 07:58:00 | HH522B | Urban | Asset failure | LV | 1 | 374 | 0.0005979 | 1.6e-06 | No
25/09/2018 | 08:09:56 | ST21 | Rural Short | Planned |  | 482 | 372 | 1.3358 | 0.003591 | No
25/09/2018 | 08:38:26 | KA07 | Rural Long | Planned |  | 25 | 122 | 0.02226 | 0.00018246 | No
25/09/2018 | 08:56:37 | SG11 | Rural Short | Planned |  | 3 | 349 | 0.0078003 | 2.235e-05 | No
25/09/2018 | 09:11:20 | SM410D | Urban | Planned |  | 18 | 225 | 0.0064746 | 2.878e-05 | No
25/09/2018 | 09:13:03 | SG14 | Rural Short | Planned |  | 37 | 325 | 0.089588 | 0.00027566 | No
25/09/2018 | 09:32:48 | AP149F | Urban | Asset failure | LV | 1 | 205 | 0.00032773 | 1.6e-06 | No
25/09/2018 | 09:32:56 | MV15 | Rural Short | Planned |  | 44 | 203 | 0.066545 | 0.00032781 | No
25/09/2018 | 09:36:50 | VH45 | Rural Short | Planned |  | 1 | 353 | 0.0026299 | 7.45e-06 | No
25/09/2018 | 09:38:32 | AP125A | Urban | Planned |  | 236 | 237 | 0.089417 | 0.00037729 | No
25/09/2018 | 09:39:27 | VH22 | Rural Short | Planned |  | 1256 | 367.5279 | 3.4391 | 0.0093574 | No
25/09/2018 | 09:42:42 | HH177D | Urban | Planned |  | 2 | 116 | 0.00037089 | 3.2e-06 | No
25/09/2018 | 10:28:42 | W04 | Rural Long | Planned |  | 3 | 51 | 0.0011167 | 2.19e-05 | No
25/09/2018 | 10:44:06 | KA10 | Rural Long | Unknown | Unknown | 69 | 12 | 0.006043 | 0.00050359 | No
25/09/2018 | 10:47:29 | HH130A | Urban | Planned |  | 116 | 311 | 0.057674 | 0.00018545 | No
25/09/2018 | 11:00:58 | KA07 | Rural Long | Planned |  | 38 | 65 | 0.018027 | 0.00027734 | No
25/09/2018 | 11:01:37 | G02 | Rural Long | Asset failure | LV | 1 | 283 | 0.0020654 | 7.3e-06 | No
25/09/2018 | 11:31:00 | SA520E | Urban | Network business | Switching and protection error | 548 | 13 | 0.011389 | 0.00087607 | No
25/09/2018 | 11:53:17 | SB18 | Rural Long | Planned |  | 1 | 198 | 0.0014451 | 7.3e-06 | No
25/09/2018 | 12:24:08 | MV31 | Rural Short | Unknown | Unknown | 8 | 70 | 0.0041721 | 5.96e-05 | No
25/09/2018 | 13:17:00 | CL23 | Rural Long | Planned |  | 41 | 118 | 0.035309 | 0.00029923 | No
25/09/2018 | 14:29:31 | VH12 | Rural Short | Asset failure | LV | 32 | 51 | 0.012159 | 0.0002384 | No
25/09/2018 | 14:30:35 | MG39 | Rural Short | Other |  | 2 | 55 | 0.00081952 | 1.49e-05 | No
25/09/2018 | 14:36:03 | VH15 | Rural Short | Asset failure | LV | 1 | 49 | 0.00036506 | 7.45e-06 | No
25/09/2018 | 14:44:12 | BM44 | Rural Short | Third Party | Vehicle impact | 943 | 97.0456 | 0.68179 | 0.0070255 | No
25/09/2018 | 15:52:41 | LX61 | Rural Long | Unknown | Unknown | 4 | 6 | 0.00017516 | 2.919e-05 | No
25/09/2018 | 16:24:53 | NA34 | Rural Long | Unknown | Unknown | 2 | 51 | 0.00074443 | 1.46e-05 | No
25/09/2018 | 16:27:42 | W21 | Rural Long | Asset failure | HV | 39 | 198.3077 | 0.056445 | 0.00028464 | No
25/09/2018 | 17:41:01 | SM349B | Urban | Asset failure | LV | 126 | 79 | 0.015913 | 0.00020143 | No
26/09/2018 | 08:11:44 | MG46 | Rural Short | Asset failure | LV | 8.3333 | 38 | 0.0023592 | 6.208e-05 | No
26/09/2018 | 08:13:30 | MB22 | Rural Short | Third Party | Vehicle impact | 66 | 158 | 0.07769 | 0.00049171 | No
26/09/2018 | 08:14:33 | HH107B | Urban | Planned |  | 283 | 369 | 0.16694 | 0.00045243 | No
26/09/2018 | 08:41:28 | HH130F | Urban | Planned |  | 9 | 91 | 0.0013093 | 1.439e-05 | No
26/09/2018 | 08:55:14 | HH130F | Urban | Planned |  | 1 | 77 | 0.0001231 | 1.6e-06 | No
26/09/2018 | 08:58:50 | CD15 | Rural Long | Planned |  | 3 | 48 | 0.001051 | 2.19e-05 | No
26/09/2018 | 08:59:30 | BT02 | Rural Long | Planned |  | 12 | 279 | 0.024435 | 8.758e-05 | No
26/09/2018 | 09:03:18 | MTB13 | Rural Short | Planned |  | 66 | 312 | 0.15341 | 0.00049171 | No
26/09/2018 | 09:04:07 | HH130F | Urban | Planned |  | 85 | 152 | 0.020655 | 0.00013589 | No
26/09/2018 | 09:05:28 | YK17 | Rural Long | Planned |  | 489 | 248 | 0.88508 | 0.0035689 | No
26/09/2018 | 09:08:40 | GU43 | Rural Long | Planned |  | 136 | 371 | 0.36824 | 0.00099257 | No
26/09/2018 | 09:09:55 | MV63 | Rural Short | Planned |  | 7 | 116 | 0.0060495 | 5.215e-05 | No
26/09/2018 | 09:10:11 | NL760B | Urban | Planned |  | 6 | 34 | 0.00032613 | 9.59e-06 | No
26/09/2018 | 09:14:11 | YK30 | Rural Long | Planned |  | 62 | 33 | 0.014932 | 0.0004525 | No
26/09/2018 | 09:52:02 | MB63 | Rural Long | Planned |  | 1 | 105 | 0.00076633 | 7.3e-06 | No
26/09/2018 | 09:52:53 | MV54 | Rural Short | Planned |  | 1 | 207 | 0.0015422 | 7.45e-06 | No
26/09/2018 | 10:03:22 | VH33 | Rural Short | Planned |  | 135 | 261 | 0.26251 | 0.0010058 | No
26/09/2018 | 11:10:47 | R31 | Rural Long | Planned |  | 4 | 234 | 0.0068312 | 2.919e-05 | No
26/09/2018 | 11:21:16 | SA14 | Urban | Third Party | Vehicle impact | 3422 | 17 | 0.093001 | 0.0054707 | No
26/09/2018 | 11:55:00 | PA02 | Urban | Asset failure | HV | 1551 | 98.1231 | 0.2433 | 0.0024795 | No
26/09/2018 | 11:55:00 | PA07 | Rural Long | Asset failure | HV | 620 | 48 | 0.2172 | 0.004525 | No
26/09/2018 | 12:57:11 | G05 | Rural Long | Asset failure | LV | 1 | 237 | 0.0017297 | 7.3e-06 | No
26/09/2018 | 13:33:15 | MG04 | Rural Short | Overloads |  | 2 | 69 | 0.0010281 | 1.49e-05 | No
26/09/2018 | 13:39:31 | HH107D | Urban | Asset failure | LV | 90 | 56 | 0.0080573 | 0.00014388 | No
26/09/2018 | 14:10:33 | BU08 | Rural Long | Asset failure | HV | 14 | 147 | 0.01502 | 0.00010218 | No
26/09/2018 | 14:20:57 | YK07 | Rural Long | Asset failure | LV | 1 | 119 | 0.0008685 | 7.3e-06 | No
26/09/2018 | 14:50:50 | CV24 | Rural Long | Asset failure | HV | 2 | 46 | 0.00067145 | 1.46e-05 | No
26/09/2018 | 15:20:05 | GU43 | Rural Long | Animal | Animal impact | 136 | 260.2132 | 0.25828 | 0.00099257 | No
26/09/2018 | 15:20:05 | GU43 | Rural Long | Animal | Animal impact | 0 | 4 | 8.758e-05 | 0 | No
26/09/2018 | 15:55:21 | M51 | Rural Short | Asset failure | LV | 9.3333 | 279 | 0.0194 | 6.953e-05 | No
26/09/2018 | 17:35:48 | MT18 | Rural Long | Animal | Animal impact | 3 | 132 | 0.0028901 | 2.19e-05 | No
26/09/2018 | 20:39:44 | SM374B | Urban | Overloads |  | 1 | 114 | 0.00018225 | 1.6e-06 | No
26/09/2018 | 20:59:02 | AP214D | Urban | Asset failure | LV | 1 | 124 | 0.00019824 | 1.6e-06 | No
26/09/2018 | 22:29:35 | SM126A | Urban | Unknown | Unknown | 280 | 113 | 0.050582 | 0.00044763 | No
26/09/2018 | 23:19:36 | MTB61 | Rural Short | Overloads |  | 25 | 259 | 0.04824 | 0.00018625 | No
26/09/2018 | 23:59:38 | NL234C | Urban | Unknown | Unknown | 83 | 238 | 0.03158 | 0.00013269 | No
27/09/2018 | 02:37:15 | SD34201 | Rural Short | Asset failure | Subtransmission | 3 | 153.3333 | 0.0034271 | 2.235e-05 | No
27/09/2018 | 08:22:28 | KI31 | Rural Short | Planned |  | 14 | 123 | 0.012829 | 0.0001043 | No
27/09/2018 | 08:37:14 | MV14 | Rural Short | Planned |  | 83 | 302.2771 | 0.18692 | 0.00061836 | No
27/09/2018 | 08:39:28 | SM216D | Urban | Planned |  | 1 | 49 | 7.834e-05 | 1.6e-06 | No
27/09/2018 | 09:00:50 | LX51 | Rural Short | Planned |  | 38 | 189 | 0.053507 | 0.00028311 | No
27/09/2018 | 09:09:46 | NL111Q | Urban | Planned |  | 405 | 370 | 0.23956 | 0.00064746 | No
27/09/2018 | 09:15:15 | ST34 | Rural Long | Planned |  | 50 | 377 | 0.13757 | 0.00036492 | No
27/09/2018 | 09:17:56 | LX51 | Rural Short | Planned |  | 1 | 375 | 0.0027938 | 7.45e-06 | No
27/09/2018 | 09:19:28 | KI11 | Rural Long | Asset failure | LV | 1 | 233 | 0.0017005 | 7.3e-06 | No
27/09/2018 | 09:20:20 | NL210E | Urban | Planned |  | 25 | 341 | 0.013629 | 3.997e-05 | No
27/09/2018 | 09:34:02 | SA17 | Urban | Planned |  | 141 | 243 | 0.054775 | 0.00022541 | No
27/09/2018 | 09:50:11 | MB81 | Rural Long | Planned |  | 25 | 392 | 0.071524 | 0.00018246 | No
27/09/2018 | 10:00:58 | EL01R | Urban | Unknown | Unknown | 1 | 117 | 0.00018704 | 1.6e-06 | No
27/09/2018 | 11:01:02 | AP424E | Urban | Planned |  | 256 | 111.9961 | 0.045836 | 0.00040926 | No
27/09/2018 | 11:02:57 | EL01R | Urban | Unknown | Unknown | 1 | 56 | 8.953e-05 | 1.6e-06 | No
27/09/2018 | 11:03:14 | HH522B | Urban | Asset failure | LV | 7.6667 | 32 | 0.00039221 | 1.226e-05 | No
27/09/2018 | 13:41:00 | SD38100 | Rural Long | Asset failure | Subtransmission | 1281 | 143.6066 | 1.3426 | 0.0093492 | No
27/09/2018 | 19:00:29 | NL234C | Urban | Asset failure | LV | 24 | 225 | 0.0086328 | 3.837e-05 | No
27/09/2018 | 20:35:40 | AP355H | Urban | Asset failure | LV | 1 | 171 | 0.00027337 | 1.6e-06 | No
27/09/2018 | 21:56:24 | SM216A | Urban | Planned |  | 54 | 425 | 0.03669 | 8.633e-05 | No
27/09/2018 | 23:20:06 | CBD366N | CBD | Planned |  | 11 | 37 | 0.079006 | 0.0021353 | No
28/09/2018 | 00:46:12 | ME427F | Urban | Asset failure | LV | 1 | 51 | 8.153e-05 | 1.6e-06 | No
28/09/2018 | 02:04:00 | MV14 | Rural Short | Asset failure | HV | 542 | 284.8801 | 1.1503 | 0.004038 | No
28/09/2018 | 05:06:55 | MI32 | Rural Long | Asset failure | LV | 1 | 269 | 0.0019633 | 7.3e-06 | No
28/09/2018 | 07:58:31 | AP424B | Urban | Asset failure | LV | 42.3333 | 65 | 0.004399 | 6.768e-05 | No
28/09/2018 | 08:20:50 | NU22 | Rural Long | Asset failure | LV | 1 | 162 | 0.0011823 | 7.3e-06 | No
28/09/2018 | 08:47:11 | PL14 | Urban | Planned |  | 1 | 33 | 5.276e-05 | 1.6e-06 | No
28/09/2018 | 08:52:08 | GU14 | Rural Long | Planned |  | 13 | 348 | 0.033018 | 9.488e-05 | No
28/09/2018 | 09:00:58 | LX34 | Rural Short | Planned |  | 1 | 112 | 0.00083442 | 7.45e-06 | No
28/09/2018 | 09:06:53 | AP125A | Urban | Planned |  | 206 | 321 | 0.10571 | 0.00032933 | No
28/09/2018 | 09:08:42 | VH32 | Rural Short | Planned |  | 5 | 113 | 0.0042093 | 3.725e-05 | No
28/09/2018 | 09:11:08 | KI21 | Rural Long | Planned |  | 335 | 19.791 | 0.048388 | 0.0024449 | No
28/09/2018 | 09:29:01 | MB12 | Rural Short | Planned |  | 34 | 283 | 0.071685 | 0.00025331 | No
28/09/2018 | 09:35:11 | VH45 | Rural Short | Planned |  | 143 | 250 | 0.26634 | 0.0010654 | No
28/09/2018 | 09:44:24 | NA36 | Rural Long | Asset failure | LV | 2 | 510 | 0.0074443 | 1.46e-05 | No
28/09/2018 | 09:45:14 | HH386G | Urban | Planned |  | 39 | 291 | 0.018143 | 6.235e-05 | No
28/09/2018 | 09:48:45 | EL19 | Urban | Planned |  | 8 | 266 | 0.003402 | 1.279e-05 | No
28/09/2018 | 09:52:20 | VH43 | Rural Short | Planned |  | 102 | 193 | 0.14666 | 0.00075992 | No
28/09/2018 | 10:00:56 | EL01R | Urban | Unknown | Unknown | 1 | 98 | 0.00015667 | 1.6e-06 | No
28/09/2018 | 10:04:55 | AP373A | Urban | Planned |  | 36 | 232 | 0.013352 | 5.755e-05 | No
28/09/2018 | 10:05:43 | HH145C | Urban | Planned |  | 127 | 123 | 0.024973 | 0.00020303 | No
28/09/2018 | 10:18:24 | HH177D | Urban | Planned |  | 5 | 36 | 0.00028776 | 7.99e-06 | No
28/09/2018 | 10:22:37 | AP355H | Urban | Overloads |  | 1 | 43 | 6.874e-05 | 1.6e-06 | No
28/09/2018 | 10:27:27 | MTB32 | Rural Long | Planned |  | 30 | 177 | 0.038754 | 0.00021895 | No
28/09/2018 | 10:33:32 | NL760B | Urban | Planned |  | 659 | 207 | 0.21808 | 0.0010535 | No
28/09/2018 | 10:35:44 | HH341G | Urban | Planned |  | 337 | 198 | 0.10667 | 0.00053875 | No
28/09/2018 | 10:42:02 | SG10 | Rural Short | Unknown | Unknown | 4.3333 | 142 | 0.0045843 | 3.228e-05 | No
28/09/2018 | 10:45:44 | CD01 | Rural Short | Planned |  | 53 | 149 | 0.058834 | 0.00039486 | No
28/09/2018 | 11:56:55 | HH403D | Urban | Asset failure | LV | 1 | 464 | 0.00074179 | 1.6e-06 | No
28/09/2018 | 12:02:37 | EL01R | Urban | Unknown | Unknown | 1 | 327 | 0.00052277 | 1.6e-06 | No
28/09/2018 | 12:56:07 | EL01R | Urban | Unknown | Unknown | 1 | 273 | 0.00043644 | 1.6e-06 | No
28/09/2018 | 13:11:12 | ME200D | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
28/09/2018 | 13:40:35 | ME427E | Urban | Third Party | Vehicle impact | 1 | 19 | 3.037e-05 | 1.6e-06 | No
28/09/2018 | 13:52:43 | HH428F | Urban | Overloads |  | 1 | 282 | 0.00045083 | 1.6e-06 | No
28/09/2018 | 14:02:26 | NA04 | Rural Long | Asset failure | HV | 36.6667 | 100 | 0.026761 | 0.00026761 | No
28/09/2018 | 14:30:23 | MTB72 | Rural Long | Planned |  | 1 | 5 | 3.649e-05 | 7.3e-06 | No
28/09/2018 | 14:43:21 | NL451A | Urban | Animal | Animal impact | 16.3333 | 222 | 0.0057968 | 2.611e-05 | No
28/09/2018 | 15:12:10 | SG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 50 | 73 | 0.027193 | 0.00037251 | No
28/09/2018 | 15:12:57 | AP355C | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 267 | 0.00085369 | 3.2e-06 | No
28/09/2018 | 16:48:11 | NL760B | Urban | Asset failure | LV | 1 | 203 | 0.00032453 | 1.6e-06 | No
28/09/2018 | 20:09:03 | SM349E | Urban | Overloads |  | 1 | 135 | 0.00021582 | 1.6e-06 | No
28/09/2018 | 20:33:05 | HH107C | Urban | Asset failure | LV | 23.3333 | 181 | 0.0067517 | 3.73e-05 | No
28/09/2018 | 20:55:50 | HH403D | Urban | Asset failure | LV | 1 | 102 | 0.00016306 | 1.6e-06 | No
28/09/2018 | 23:40:51 | SM411D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 185 | 0.0050278 | 2.718e-05 | No
29/09/2018 | 00:10:18 | SM216E | Urban | Asset failure | HV | 2471 | 140.2477 | 0.55402 | 0.0039503 | No
29/09/2018 | 07:44:12 | LM13 | Rural Long | Unknown | Unknown | 31 | 152 | 0.03439 | 0.00022625 | No
29/09/2018 | 07:45:13 | HH130A | Urban | Overloads |  | 1 | 266 | 0.00042525 | 1.6e-06 | No
29/09/2018 | 08:02:21 | SA20 | Urban | Asset failure | LV | 1 | 217 | 0.00034691 | 1.6e-06 | No
29/09/2018 | 10:12:58 | ME131A | Urban | Asset failure | LV | 51 | 91 | 0.0074195 | 8.153e-05 | No
29/09/2018 | 14:44:39 | YK11 | Rural Long | Asset failure | LV | 1 | 246 | 0.0017954 | 7.3e-06 | No
29/09/2018 | 16:52:40 | MB03 | Rural Long | Unknown | Unknown | 32 | 173 | 0.040404 | 0.00023355 | No
29/09/2018 | 18:10:35 | HH403B | Urban | Overloads |  | 2 | 199 | 0.00063627 | 3.2e-06 | No
30/09/2018 | 06:54:00 | HH403A | Urban | Asset failure | LV | 28.6666 | 168 | 0.0076992 | 4.583e-05 | No
30/09/2018 | 08:12:38 | EL15 | Urban | Planned |  | 1 | 323 | 0.00051637 | 1.6e-06 | No
30/09/2018 | 09:33:50 | VH44 | Rural Short | Planned |  | 58 | 165 | 0.071298 | 0.00043211 | No
30/09/2018 | 16:01:12 | WHY07 | Urban | Asset failure | HV | 656.3336 | 94.5653 | 0.099224 | 0.0010493 | No
30/09/2018 | 17:05:22 | GU11 | Rural Long | Unknown | Unknown | 25.6667 | 223 | 0.041773 | 0.00018732 | No
30/09/2018 | 19:42:51 | NL234B | Urban | Unknown | Unknown | 1791 | 35.0826 | 0.10045 | 0.0028632 | No
1/10/2018 | 00:10:51 | G17 | Rural Long | Unknown | Unknown | 4 | 199 | 0.0058095 | 2.919e-05 | No
1/10/2018 | 06:12:47 | AP149H | Urban | Asset failure | LV | 17.3333 | 310 | 0.0085902 | 2.771e-05 | No
1/10/2018 | 10:25:13 | HH102A | Urban | Other |  | 1 | 89 | 0.00014228 | 1.6e-06 | No
1/10/2018 | 16:18:39 | WHY10 | Urban | Asset failure | LV | 4 | 110 | 0.00070342 | 6.39e-06 | No
2/10/2018 | 07:46:14 | HH428C | Urban | Planned |  | 64 | 290 | 0.029671 | 0.00010232 | No
2/10/2018 | 08:14:15 | NU31 | Rural Long | Animal | Animal impact | 1 | 187 | 0.0013648 | 7.3e-06 | No
2/10/2018 | 08:26:33 | HH522A | Urban | Planned |  | 1 | 660 | 0.0010551 | 1.6e-06 | No
2/10/2018 | 08:38:17 | NL210A | Urban | Weather |  | 3 | 1642 | 0.0078751 | 4.8e-06 | No
2/10/2018 | 09:00:34 | VH17 | Rural Short | Planned |  | 5 | 232 | 0.0086422 | 3.725e-05 | No
2/10/2018 | 09:00:39 | VH10 | Rural Short | Planned |  | 5 | 327 | 0.012181 | 3.725e-05 | No
2/10/2018 | 09:03:09 | SA18 | Urban | Planned |  | 87 | 210 | 0.029208 | 0.00013908 | No
2/10/2018 | 09:14:54 | MV14 | Rural Short | Planned |  | 5 | 261 | 0.0097224 | 3.725e-05 | No
2/10/2018 | 09:34:30 | MG41 | Urban | Planned |  | 75 | 842 | 0.10096 | 0.0001199 | No
2/10/2018 | 10:09:38 | ME231A | Urban | Planned |  | 56 | 126 | 0.01128 | 8.953e-05 | No
2/10/2018 | 10:48:00 | WK42 | Rural Short | Third Party | Vehicle impact | 365 | 295.3452 | 0.80313 | 0.0027193 | No
2/10/2018 | 10:52:44 | EL17 | Urban | Planned |  | 207 | 224 | 0.074127 | 0.00033093 | No
2/10/2018 | 11:49:16 | CD17 | Rural Long | Planned |  | 1 | 36 | 0.00026274 | 7.3e-06 | No
2/10/2018 | 12:35:03 | NA34 | Rural Long | Asset failure | HV | 1 | 40 | 0.00029193 | 7.3e-06 | No
2/10/2018 | 12:39:41 | CD17 | Rural Long | Planned |  | 1 | 11 | 8.028e-05 | 7.3e-06 | No
2/10/2018 | 12:46:17 | EL02 | Urban | Planned |  | 1 | 25 | 3.997e-05 | 1.6e-06 | No
2/10/2018 | 13:20:37 | HH432B | Urban | Asset failure | LV | 8 | 177 | 0.0022637 | 1.279e-05 | No
2/10/2018 | 14:11:46 | MB14 | Rural Short | Asset failure | HV | 17 | 8 | 0.0010132 | 0.00012665 | No
2/10/2018 | 15:02:59 | SM349D | Urban | Unknown | Unknown | 16 | 271 | 0.0069318 | 2.558e-05 | No
2/10/2018 | 15:04:11 | SA17 | Urban | Animal | Animal impact | 20.6666 | 97 | 0.0032048 | 3.304e-05 | No
2/10/2018 | 15:49:41 | CV31 | Rural Long | Unknown | Unknown | 58 | 370 | 0.15662 | 0.0004233 | No
2/10/2018 | 15:51:25 | CV32 | Rural Long | Weather |  | 68 | 1309 | 0.64964 | 0.00049629 | No
2/10/2018 | 16:26:23 | AP146C | Urban | Asset failure | LV | 26.3333 | 190 | 0.0079987 | 4.21e-05 | No
2/10/2018 | 16:30:15 | CV25 | Rural Long | Weather |  | 55 | 1492 | 0.5989 | 0.00040141 | No
2/10/2018 | 16:47:29 | PA02 | Urban | Asset failure | LV | 1 | 85 | 0.00013589 | 1.6e-06 | No
2/10/2018 | 16:50:18 | NL760C | Urban | Asset failure | HV | 1790.0009 | 40.4609 | 0.11578 | 0.0028616 | No
2/10/2018 | 17:24:21 | CV24 | Rural Long | Weather |  | 73 | 1116.1644 | 0.59467 | 0.00053278 | No
2/10/2018 | 17:24:21 | CV24 | Rural Long | Weather |  | 0 | 527.9852 | 0.52021 | 0 | No
2/10/2018 | 18:33:00 | KA10 | Rural Long | Weather |  | 32 | 653.8438 | 0.1527 | 0.00023355 | No
2/10/2018 | 18:33:00 | KA10 | Rural Long | Weather |  | 0 | 25 | 0.0018246 | 0 | No
2/10/2018 | 18:57:25 | SD35100 | Rural Long | Weather |  | 2113 | 223.513 | 3.4469 | 0.015421 | No
2/10/2018 | 19:14:52 | HH145C | Urban | Overloads |  | 7 | 169 | 0.0018912 | 1.119e-05 | No
2/10/2018 | 20:09:14 | SA38 | Urban | Weather |  | 33 | 66.8182 | 0.0035251 | 5.276e-05 | No
2/10/2018 | 20:10:48 | SD35200 | Rural Long | Weather |  | 3.3333 | 1089 | 0.026493 | 2.433e-05 | No
2/10/2018 | 20:16:58 | SA18 | Urban | Weather |  | 1297 | 6.7016 | 0.013896 | 0.0020735 | No
2/10/2018 | 20:27:13 | SM411E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1487 | 73 | 0.17354 | 0.0023772 | No
2/10/2018 | 20:27:59 | SM402D | Urban | Weather |  | 1597 | 244 | 0.62295 | 0.0025531 | No
2/10/2018 | 20:33:06 | ME347C | Urban | Asset failure | LV | 172 | 205 | 0.056369 | 0.00027497 | No
2/10/2018 | 20:36:01 | SG12 | Rural Short | Unknown | Unknown | 94 | 337.3404 | 0.23624 | 0.00070031 | No
2/10/2018 | 20:42:38 | MTB32 | Rural Long | Weather |  | 57 | 421 | 0.17514 | 0.00041601 | No
2/10/2018 | 20:42:38 | MTB32 | Rural Long | Weather |  | 196 | 198.2857 | 0.28364 | 0.0014305 | No
2/10/2018 | 20:54:22 | ST41 | Rural Long | Unknown | Unknown | 3 | 786 | 0.017209 | 2.19e-05 | No
2/10/2018 | 20:55:56 | MTB22 | Rural Short | Unknown | Unknown | 34.6667 | 779 | 0.20119 | 0.00025827 | No
2/10/2018 | 20:56:06 | ST22 | Rural Short | Unknown | Unknown | 291 | 723 | 1.5675 | 0.002168 | No
2/10/2018 | 21:00:05 | AP149C | Urban | Asset failure | LV | 1 | 158 | 0.00025259 | 1.6e-06 | No
2/10/2018 | 21:01:02 | ST34 | Rural Long | Unknown | Unknown | 55 | 811 | 0.32554 | 0.00040141 | No
2/10/2018 | 21:01:43 | ST34 | Rural Long | Unknown | Unknown | 69 | 432.4058 | 0.21775 | 0.00050359 | No
2/10/2018 | 21:03:00 | ST12 | Rural Short | Weather |  | 1773 | 143.8223 | 1.8998 | 0.013209 | No
2/10/2018 | 21:03:00 | ST12 | Rural Short | Weather |  | 0 | 2 | 0.013515 | 0 | No
2/10/2018 | 21:03:13 | ST41 | Rural Long | Weather |  | 122 | 669.1967 | 0.59585 | 0.0008904 | No
2/10/2018 | 21:04:17 | ST42 | Rural Long | Unknown | Unknown | 15 | 838 | 0.09174 | 0.00010948 | No
2/10/2018 | 21:04:17 | ST42 | Rural Long | Unknown | Unknown | 140 | 7 | 0.0071524 | 0.0010218 | No
2/10/2018 | 21:20:00 | ST41 | Rural Long | Unknown | Unknown | 5 | 839 | 0.030617 | 3.649e-05 | No
2/10/2018 | 21:22:00 | KA05 | Rural Long | Unknown | Unknown | 26.3333 | 162 | 0.031135 | 0.00019219 | No
2/10/2018 | 21:46:45 | MT15 | Rural Long | Weather |  | 46 | 150.8261 | 0.050636 | 0.00033572 | No
2/10/2018 | 21:52:06 | SD40300 | Rural Long | Weather |  | 75 | 193 | 0.10564 | 0.00054738 | No
2/10/2018 | 22:21:48 | SD34400 | Rural Long | Weather |  | 49 | 483 | 0.17273 | 0.00035762 | No
2/10/2018 | 23:12:00 | BT12 | Rural Long | Unknown | Unknown | 93 | 408.6667 | 0.27738 | 0.00067875 | No
2/10/2018 | 23:20:07 | CN12 | Rural Long | Weather |  | 52 | 503.9808 | 0.19127 | 0.00037951 | No
3/10/2018 | 00:48:56 | AP373E | Urban | Weather |  | 222 | 7.0135 | 0.0024891 | 0.00035491 | No
3/10/2018 | 01:48:17 | KA15 | Rural Long | Weather |  | 59 | 782.1356 | 0.33679 | 0.0004306 | No
3/10/2018 | 04:36:03 | CN03 | Rural Long | Weather |  | 51 | 499 | 0.18574 | 0.00037222 | No
3/10/2018 | 06:11:05 | SM402D | Urban | Weather |  | 40 | 304 | 0.01944 | 6.395e-05 | No
3/10/2018 | 06:38:58 | ST12 | Rural Short | Weather |  | 1 | 380 | 0.0028311 | 7.45e-06 | No
3/10/2018 | 06:48:00 | NA04 | Rural Long | Unknown | Unknown | 6 | 116 | 0.0050796 | 4.379e-05 | No
3/10/2018 | 07:11:00 | MT15 | Rural Long | Weather |  | 2 | 601 | 0.0087726 | 1.46e-05 | No
3/10/2018 | 07:21:54 | SM402D | Urban | Weather |  | 51.3334 | 246 | 0.020188 | 8.207e-05 | No
3/10/2018 | 07:51:40 | SM216G | Urban | Asset failure | LV | 29.3333 | 236 | 0.011067 | 4.689e-05 | No
3/10/2018 | 08:27:56 | AP214C | Urban | Weather |  | 3 | 192 | 0.00092084 | 4.8e-06 | No
3/10/2018 | 08:48:00 | SD38100 | Rural Long | Weather |  | 1285 | 108.7494 | 1.0199 | 0.0093784 | No
3/10/2018 | 08:51:41 | SM411A | Urban | Asset failure | LV | 130 | 51 | 0.010599 | 0.00020783 | No
3/10/2018 | 08:52:09 | SD38100 | Rural Long | Unknown | Unknown | 1 | 108 | 0.00078822 | 7.3e-06 | No
3/10/2018 | 09:02:48 | HH522B | Urban | Asset failure | LV | 1 | 239 | 0.00038208 | 1.6e-06 | No
3/10/2018 | 09:12:00 | GA22 | Rural Short | Planned |  | 121 | 96 | 0.086541 | 0.00090147 | No
3/10/2018 | 09:16:45 | KI31 | Rural Short | Planned |  | 56 | 203 | 0.084693 | 0.00041721 | No
3/10/2018 | 09:17:55 | ME131C | Urban | Planned |  | 182 | 371 | 0.10795 | 0.00029096 | No
3/10/2018 | 09:18:44 | GA35 | Rural Long | Planned |  | 1 | 148 | 0.0010801 | 7.3e-06 | No
3/10/2018 | 09:35:36 | MV14 | Rural Short | Planned |  | 24 | 141 | 0.025211 | 0.0001788 | No
3/10/2018 | 09:39:42 | CL23 | Rural Long | Planned |  | 72 | 216 | 0.1135 | 0.00052548 | No
3/10/2018 | 09:45:54 | HH341K | Urban | Planned |  | 321 | 250 | 0.12829 | 0.00051317 | No
3/10/2018 | 09:46:18 | CD02 | Rural Long | Planned |  | 99 | 292.5152 | 0.21135 | 0.00072254 | No
3/10/2018 | 09:51:36 | HH341K | Urban | Planned |  | 7 | 69 | 0.00077216 | 1.119e-05 | No
3/10/2018 | 09:55:46 | AP355A | Urban | Planned |  | 254 | 260 | 0.10558 | 0.00040606 | No
3/10/2018 | 09:56:51 | HH121C | Urban | Asset failure | LV | 32.6666 | 126 | 0.0065801 | 5.222e-05 | No
3/10/2018 | 10:20:26 | HH496C | Urban | Planned |  | 187 | 3034 | 0.90702 | 0.00029895 | No
3/10/2018 | 10:23:50 | AP125D | Urban | Planned |  | 313 | 240 | 0.12009 | 0.00050039 | No
3/10/2018 | 10:52:13 | ST35 | Rural Long | Asset failure | LV | 1 | 264 | 0.0019268 | 7.3e-06 | No
3/10/2018 | 11:06:04 | HH341K | Urban | Planned |  | 1 | 219 | 0.00035011 | 1.6e-06 | No
3/10/2018 | 11:54:40 | GA22 | Rural Short | Planned |  | 24 | 118 | 0.021099 | 0.0001788 | No
3/10/2018 | 12:04:24 | HH341G | Urban | Asset failure | LV | 14 | 111 | 0.0024843 | 2.238e-05 | No
3/10/2018 | 12:42:49 | NL115B | Urban | Planned |  | 13 | 120 | 0.0024939 | 2.078e-05 | No
3/10/2018 | 13:15:18 | MG19 | Rural Long | Weather |  | 9 | 94 | 0.0061744 | 6.569e-05 | No
3/10/2018 | 16:40:51 | CV34 | Rural Long | Weather |  | 6 | 1382 | 0.060518 | 4.379e-05 | No
3/10/2018 | 16:47:29 | ST12 | Rural Short | Unknown | Unknown | 2 | 134 | 0.0019966 | 1.49e-05 | No
3/10/2018 | 17:20:44 | NA23 | Rural Long | Unknown | Unknown | 29 | 14 | 0.0029631 | 0.00021165 | No
3/10/2018 | 18:07:35 | WK41 | Rural Short | Third Party | Vehicle impact | 189 | 96.9471 | 0.13651 | 0.0014081 | No
3/10/2018 | 21:09:56 | NU13 | Rural Long | Overloads |  | 1 | 85 | 0.00062036 | 7.3e-06 | No
3/10/2018 | 22:13:43 | SM216A | Urban | Planned |  | 62 | 400 | 0.039647 | 9.912e-05 | No
4/10/2018 | 00:11:19 | GA50 | Urban | Asset failure | LV | 1 | 118 | 0.00018864 | 1.6e-06 | No
4/10/2018 | 08:14:56 | ST22 | Rural Short | Planned |  | 131 | 363 | 0.35428 | 0.00097597 | No
4/10/2018 | 08:44:53 | PA02 | Urban | Planned |  | 55 | 126 | 0.011079 | 8.793e-05 | No
4/10/2018 | 09:03:21 | MV54 | Rural Short | Planned |  | 122 | 308 | 0.27995 | 0.00090892 | No
4/10/2018 | 09:10:47 | HH496D | Urban | Planned |  | 538 | 110.3234 | 0.094888 | 0.00086009 | No
4/10/2018 | 09:20:56 | KA03 | Rural Long | Planned |  | 70 | 291 | 0.14867 | 0.00051088 | No
4/10/2018 | 09:27:08 | SG14 | Rural Short | Planned |  | 149 | 318.2886 | 0.35332 | 0.0011101 | No
4/10/2018 | 09:36:25 | EL10 | Urban | Planned |  | 1 | 397 | 0.00063467 | 1.6e-06 | No
4/10/2018 | 09:45:53 | NU19 | Rural Long | Planned |  | 2 | 138 | 0.0020143 | 1.46e-05 | No
4/10/2018 | 10:05:56 | NL111P | Urban | Planned |  | 60 | 119 | 0.011415 | 9.592e-05 | No
4/10/2018 | 10:18:47 | HH121C | Urban | Planned |  | 222 | 271 | 0.096179 | 0.00035491 | No
4/10/2018 | 10:22:37 | ST36 | Rural Long | Planned |  | 107 | 249 | 0.19445 | 0.00078092 | No
4/10/2018 | 10:27:41 | SG03 | Rural Short | Planned |  | 113 | 261 | 0.21973 | 0.00084187 | No
4/10/2018 | 10:35:42 | HH121C | Urban | Planned |  | 2 | 338 | 0.0010807 | 3.2e-06 | No
4/10/2018 | 11:00:18 | SD35403 | Rural Short | Planned |  | 1 | 31 | 0.00023095 | 7.45e-06 | No
4/10/2018 | 11:30:19 | EL11 | Urban | Planned |  | 2 | 158 | 0.00050518 | 3.2e-06 | No
4/10/2018 | 11:42:52 | EL03 | Urban | Asset failure | LV | 1 | 202 | 0.00032293 | 1.6e-06 | No
4/10/2018 | 12:18:19 | HH107B | Urban | Third Party | Vehicle impact | 45 | 94 | 0.0067624 | 7.194e-05 | No
4/10/2018 | 12:22:00 | ME347A | Urban | Vegetation | Grow-in - NSP responsibility | 11.3333 | 67 | 0.0012139 | 1.812e-05 | No
4/10/2018 | 12:54:28 | G15 | Rural Long | Other |  | 2 | 218 | 0.0031821 | 1.46e-05 | No
4/10/2018 | 12:56:15 | CV24 | Rural Long | Unknown | Unknown | 2 | 126 | 0.0018392 | 1.46e-05 | No
4/10/2018 | 13:21:35 | NU19 | Rural Long | Planned |  | 3 | 63 | 0.0013794 | 2.19e-05 | No
4/10/2018 | 14:54:40 | ME427E | Urban | Other |  | 1 | 170 | 0.00027177 | 1.6e-06 | No
4/10/2018 | 15:20:20 | SM216E | Urban | Unknown | Unknown | 46 | 342 | 0.02515 | 7.354e-05 | No
4/10/2018 | 15:23:43 | SG14 | Rural Short | Overloads |  | 12.6667 | 202 | 0.019062 | 9.437e-05 | No
4/10/2018 | 15:44:28 | WHY08 | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
4/10/2018 | 15:52:43 | AP425A | Urban | Asset failure | LV | 20 | 45 | 0.0014388 | 3.197e-05 | No
4/10/2018 | 16:21:15 | CL10 | Rural Long | Asset failure | HV | 5 | 319 | 0.011641 | 3.649e-05 | No
4/10/2018 | 17:28:16 | BT02 | Rural Long | Asset failure | HV | 93 | 5 | 0.0033937 | 0.00067875 | No
4/10/2018 | 18:32:22 | MG11 | Rural Short | Third Party | Other | 1 | 88 | 0.00065561 | 7.45e-06 | No
4/10/2018 | 18:37:00 | SM350G | Urban | Asset failure | LV | 1 | 175 | 0.00027977 | 1.6e-06 | No
4/10/2018 | 18:45:14 | MG46 | Rural Short | Asset failure | LV | 1 | 104 | 0.00077482 | 7.45e-06 | No
4/10/2018 | 20:44:47 | AP125D | Urban | Asset failure | LV | 1 | 46 | 7.354e-05 | 1.6e-06 | No
5/10/2018 | 00:09:07 | HH107C | Urban | Asset failure | LV | 19.3333 | 78 | 0.0024108 | 3.091e-05 | No
5/10/2018 | 01:07:10 | ME347A | Urban | Asset failure | LV | 80 | 71 | 0.0090805 | 0.00012789 | No
5/10/2018 | 02:29:53 | ME116C | Urban | Asset failure | LV | 96 | 99 | 0.015194 | 0.00015347 | No
5/10/2018 | 07:42:00 | MG27 | Rural Long | Animal | Animal impact | 9 | 138 | 0.0090645 | 6.569e-05 | No
5/10/2018 | 08:28:08 | SM410D | Urban | Planned |  | 49 | 351 | 0.027496 | 7.834e-05 | No
5/10/2018 | 08:38:51 | MTB33 | Rural Short | Unknown | Unknown | 2 | 300 | 0.0044701 | 1.49e-05 | No
5/10/2018 | 08:42:35 | SD41300 | Rural Short | Planned |  | 2 | 80 | 0.001192 | 1.49e-05 | No
5/10/2018 | 08:55:21 | ST43 | Rural Long | Planned |  | 6 | 51 | 0.0022333 | 4.379e-05 | No
5/10/2018 | 09:00:07 | MTB21 | Rural Short | Planned |  | 75 | 364 | 0.20339 | 0.00055876 | No
5/10/2018 | 09:06:24 | ME231E | Urban | Planned |  | 43 | 61 | 0.0041933 | 6.874e-05 | No
5/10/2018 | 09:29:52 | GU51 | Urban | Planned |  | 16 | 314 | 0.0080317 | 2.558e-05 | No
5/10/2018 | 09:55:03 | G16 | Rural Long | Planned |  | 12 | 93 | 0.0081449 | 8.758e-05 | No
5/10/2018 | 10:11:57 | VH33 | Rural Short | Planned |  | 9 | 205 | 0.013746 | 6.705e-05 | No
5/10/2018 | 10:14:37 | GA21 | Rural Long | Planned |  | 21 | 45 | 0.0068969 | 0.00015327 | No
5/10/2018 | 10:16:22 | EL14 | Urban | Asset failure | LV | 1 | 98 | 0.00015667 | 1.6e-06 | No
5/10/2018 | 10:16:32 | VH71 | Rural Short | Planned |  | 1 | 125 | 0.00093127 | 7.45e-06 | No
5/10/2018 | 10:29:16 | BM56 | Rural Short | Planned |  | 1 | 119 | 0.00088657 | 7.45e-06 | No
5/10/2018 | 11:17:51 | PL33 | Rural Long | Planned |  | 19 | 33.0526 | 0.0045834 | 0.00013867 | No
5/10/2018 | 11:30:17 | VH71 | Rural Short | Asset failure | HV | 2 | 29 | 0.00043211 | 1.49e-05 | No
5/10/2018 | 12:37:15 | R25 | Rural Long | Other |  | 1 | 78 | 0.00056927 | 7.3e-06 | No
5/10/2018 | 13:01:17 | HH177C | Urban | Planned |  | 1 | 162 | 0.00025899 | 1.6e-06 | No
5/10/2018 | 13:05:31 | NL210A | Urban | Asset failure | HV | 93 | 548 | 0.081475 | 0.00014868 | No
5/10/2018 | 15:23:00 | BT02 | Rural Long | Asset failure | HV | 92 | 3 | 0.0020143 | 0.00067145 | No
5/10/2018 | 17:09:13 | NA03 | Rural Long | Asset failure | HV | 7 | 69.7143 | 0.0035616 | 5.109e-05 | No
5/10/2018 | 19:17:31 | SA14 | Urban | Third Party | Other | 3431 | 93 | 0.51011 | 0.005485 | No
5/10/2018 | 20:30:40 | HH341K | Urban | Asset failure | LV | 1 | 264 | 0.00042205 | 1.6e-06 | No
5/10/2018 | 21:56:30 | ST14 | Rural Short | Unknown | Unknown | 10 | 49 | 0.0036506 | 7.45e-05 | No
6/10/2018 | 00:13:22 | EL01L | Urban | Unknown | Unknown | 35.3333 | 112 | 0.0063265 | 5.649e-05 | No
6/10/2018 | 06:24:27 | LM13 | Rural Long | Unknown | Unknown | 81 | 171 | 0.10109 | 0.00059117 | No
6/10/2018 | 07:59:58 | SG14 | Rural Short | Asset failure | LV | 7.6667 | 188 | 0.010738 | 5.712e-05 | No
6/10/2018 | 09:07:05 | KA04 | Rural Long | Asset failure | HV | 28 | 1440.143 | 0.2943 | 0.00020435 | No
6/10/2018 | 09:07:05 | KA04 | Rural Long | Asset failure | HV | 0 | 28 | 0.0057219 | 0 | No
6/10/2018 | 09:36:46 | MV53 | Rural Short | Unknown | Unknown | 122 | 176 | 0.15997 | 0.00090892 | No
6/10/2018 | 10:44:03 | ST22 | Rural Short | Weather |  | 42 | 28 | 0.0087614 | 0.00031291 | No
6/10/2018 | 11:41:01 | KA04 | Rural Long | Asset failure | HV | 1 | 26 | 0.00018976 | 7.3e-06 | No
6/10/2018 | 19:32:04 | HH102B | Urban | Overloads |  | 1 | 131 | 0.00020943 | 1.6e-06 | No
6/10/2018 | 23:57:45 | SM374B | Urban | Third Party | Vehicle impact | 8 | 681 | 0.0087096 | 1.279e-05 | No
6/10/2018 | 23:57:45 | SM374B | Urban | Third Party | Vehicle impact | 40 | 465 | 0.029735 | 6.395e-05 | No
7/10/2018 | 07:24:41 | BT03 | Rural Long | Planned |  | 1 | 114 | 0.00083201 | 7.3e-06 | No
7/10/2018 | 07:41:48 | BM55 | Rural Short | Planned |  | 2 | 123 | 0.0018327 | 1.49e-05 | No
7/10/2018 | 08:48:44 | HH121C | Urban | Planned |  | 188 | 152 | 0.045684 | 0.00030055 | No
7/10/2018 | 09:17:19 | HH428B | Urban | Asset failure | LV | 1 | 114 | 0.00018225 | 1.6e-06 | No
7/10/2018 | 09:48:06 | BT03 | Rural Long | Planned |  | 2 | 82 | 0.0011969 | 1.46e-05 | No
7/10/2018 | 10:38:20 | HH177C | Urban | Asset failure | LV | 1 | 103 | 0.00016466 | 1.6e-06 | No
7/10/2018 | 10:50:37 | SM374B | Urban | Overloads |  | 1 | 190 | 0.00030375 | 1.6e-06 | No
7/10/2018 | 14:28:08 | ST21 | Rural Short | Overloads |  | 1 | 88 | 0.00065561 | 7.45e-06 | No
7/10/2018 | 15:08:10 | HH121E | Urban | Asset failure | LV | 1 | 112 | 0.00017905 | 1.6e-06 | No
7/10/2018 | 16:54:10 | SM410B | Urban | Asset failure | HV | 3207 | 91.6738 | 0.47001 | 0.0051269 | No
7/10/2018 | 17:09:51 | SA13 | Urban | Planned |  | 12 | 72.5 | 0.0013908 | 1.918e-05 | No
7/10/2018 | 18:34:38 | SM402E | Urban | Asset failure | HV | 461 | 9 | 0.0066329 | 0.00073699 | No
7/10/2018 | 21:21:59 | AP214C | Urban | Overloads |  | 1 | 220 | 0.00035171 | 1.6e-06 | No
7/10/2018 | 22:17:04 | AP424D | Urban | Planned |  | 31 | 173 | 0.0085737 | 4.956e-05 | No
8/10/2018 | 07:07:44 | LC03 | Rural Long | Planned |  | 25 | 410 | 0.074808 | 0.00018246 | No
8/10/2018 | 07:55:33 | KA28 | Rural Long | Planned |  | 2 | 86 | 0.0012553 | 1.46e-05 | No
8/10/2018 | 08:07:06 | CBD367H | CBD | Planned |  | 8 | 5720 | 8.8828 | 0.0015529 | No
8/10/2018 | 08:07:21 | SB16 | Rural Long | Planned |  | 18 | 54 | 0.007094 | 0.00013137 | No
8/10/2018 | 08:11:30 | AP125C | Urban | Planned |  | 130 | 341 | 0.070869 | 0.00020783 | No
8/10/2018 | 08:15:50 | AP344F | Urban | Planned |  | 28 | 528 | 0.023635 | 4.476e-05 | No
8/10/2018 | 08:15:54 | MG31 | Rural Long | Planned |  | 13 | 74 | 0.007021 | 9.488e-05 | No
8/10/2018 | 08:31:53 | VH71 | Rural Short | Planned |  | 6 | 199 | 0.0088955 | 4.47e-05 | No
8/10/2018 | 08:45:10 | SM349C | Urban | Planned |  | 60 | 442 | 0.042397 | 9.592e-05 | No
8/10/2018 | 08:57:11 | MV31 | Rural Short | Planned |  | 4 | 218 | 0.0064965 | 2.98e-05 | No
8/10/2018 | 09:03:52 | HH341E | Urban | Planned |  | 58 | 14 | 0.0012981 | 9.272e-05 | No
8/10/2018 | 09:10:27 | MI09 | Rural Long | Planned |  | 1 | 34 | 0.00024814 | 7.3e-06 | No
8/10/2018 | 09:29:47 | SM350B | Urban | Planned |  | 168 | 198 | 0.053178 | 0.00026858 | No
8/10/2018 | 10:15:01 | NU15 | Rural Long | Planned |  | 2 | 56 | 0.00081741 | 1.46e-05 | No
8/10/2018 | 10:17:22 | SM350B | Urban | Planned |  | 1 | 87 | 0.00013908 | 1.6e-06 | No
8/10/2018 | 10:58:31 | MV32 | Rural Short | Planned |  | 2 | 104 | 0.0015496 | 1.49e-05 | No
8/10/2018 | 11:51:55 | SA17 | Urban | Asset failure | LV | 66 | 76 | 0.008019 | 0.00010551 | No
8/10/2018 | 12:58:56 | SM350D | Urban | Asset failure | LV | 3.3333 | 62 | 0.00033039 | 5.33e-06 | No
8/10/2018 | 13:25:16 | SA17 | Urban | Asset failure | LV | 22 | 44 | 0.0015475 | 3.517e-05 | No
8/10/2018 | 13:41:20 | SM216A | Urban | Planned |  | 63 | 2 | 0.00020143 | 0.00010072 | No
8/10/2018 | 14:43:55 | BT04 | Rural Long | Overloads |  | 1 | 217 | 0.0015837 | 7.3e-06 | No
8/10/2018 | 16:53:19 | PA08 | Rural Long | Asset failure | LV | 7 | 107 | 0.0054665 | 5.109e-05 | No
8/10/2018 | 16:55:22 | ME116B | Urban | Asset failure | LV | 1 | 178 | 0.00028456 | 1.6e-06 | No
8/10/2018 | 17:44:27 | HH432C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 203 | 0.00032453 | 1.6e-06 | No
8/10/2018 | 18:17:05 | NA02 | Rural Long | Asset failure | HV | 6 | 453.3333 | 0.019851 | 4.379e-05 | No
8/10/2018 | 23:06:14 | NA02 | Rural Long | Unknown | Unknown | 6 | 649 | 0.02842 | 4.379e-05 | No
9/10/2018 | 05:13:50 | MTB61 | Rural Short | Asset failure | HV | 33 | 54 | 0.013276 | 0.00024585 | No
9/10/2018 | 05:45:01 | LX71 | Rural Long | Unknown | Unknown | 31 | 56.9677 | 0.012889 | 0.00022625 | No
9/10/2018 | 06:36:18 | SSD134 | Urban | Planned |  | 1 | 294 | 0.00047001 | 1.6e-06 | No
9/10/2018 | 07:27:34 | MG46 | Rural Short | Planned |  | 1 | 414 | 0.0030844 | 7.45e-06 | No
9/10/2018 | 08:22:00 | SG02 | Rural Short | Planned |  | 101 | 126 | 0.094811 | 0.00075247 | No
9/10/2018 | 08:25:54 | HH409E | Urban | Planned |  | 76 | 301 | 0.036571 | 0.0001215 | No
9/10/2018 | 08:30:39 | HH429B | Urban | Planned |  | 98 | 275 | 0.043084 | 0.00015667 | No
9/10/2018 | 08:38:19 | GA53 | Rural Short | Overloads |  | 1 | 154 | 0.0011473 | 7.45e-06 | No
9/10/2018 | 08:39:29 | MTB51 | Rural Long | Planned |  | 433 | 5 | 0.015801 | 0.0031602 | No
9/10/2018 | 08:40:06 | AP125D | Urban | Planned |  | 237 | 281 | 0.10647 | 0.00037889 | No
9/10/2018 | 08:42:00 | LC04 | Rural Long | Planned |  | 39 | 357 | 0.10161 | 0.00028464 | No
9/10/2018 | 08:53:18 | MV31 | Rural Short | Planned |  | 4 | 83 | 0.0024734 | 2.98e-05 | No
9/10/2018 | 08:53:37 | WHY02 | Urban | Planned |  | 2 | 181 | 0.00057872 | 3.2e-06 | No
9/10/2018 | 09:07:00 | MV62 | Rural Short | Planned |  | 258 | 341 | 0.65545 | 0.0019221 | No
9/10/2018 | 09:09:52 | ST36 | Rural Long | Planned |  | 22 | 261 | 0.041907 | 0.00016056 | No
9/10/2018 | 09:36:21 | AP125D | Urban | Planned |  | 43 | 336 | 0.023098 | 6.874e-05 | No
9/10/2018 | 09:38:17 | HH121D | Urban | Planned |  | 265 | 190 | 0.080493 | 0.00042365 | No
9/10/2018 | 09:57:36 | BT02 | Rural Long | Unknown | Unknown | 2 | 293 | 0.0042768 | 1.46e-05 | No
9/10/2018 | 10:04:34 | BM52 | Urban | Planned |  | 35 | 4381 | 0.24513 | 5.595e-05 | No
9/10/2018 | 10:10:47 | NA02 | Rural Long | Asset failure | HV | 2 | 206 | 0.0030069 | 1.46e-05 | No
9/10/2018 | 11:35:59 | G17 | Rural Long | Planned |  | 1 | 48 | 0.00035032 | 7.3e-06 | No
9/10/2018 | 12:44:15 | MV33 | Rural Short | Planned |  | 6 | 76 | 0.0033973 | 4.47e-05 | No
9/10/2018 | 12:47:16 | PA28 | Rural Long | Planned |  | 4 | 178 | 0.0051964 | 2.919e-05 | No
9/10/2018 | 12:49:17 | MG41 | Urban | Asset failure | LV | 15.6667 | 91 | 0.0022792 | 2.505e-05 | No
9/10/2018 | 13:19:52 | SG02 | Rural Short | Planned |  | 1 | 73 | 0.00054386 | 7.45e-06 | No
9/10/2018 | 13:31:29 | SM350F | Urban | Asset failure | LV | 1 | 517 | 0.00082651 | 1.6e-06 | No
9/10/2018 | 13:42:11 | HH121C | Urban | Planned |  | 1 | 45 | 7.194e-05 | 1.6e-06 | No
9/10/2018 | 14:11:39 | MV53 | Rural Short | Unknown | Unknown | 78.6667 | 251.7034 | 0.14752 | 0.00058608 | No
9/10/2018 | 14:45:08 | MG43 | Rural Short | Planned |  | 228 | 5 | 0.0084932 | 0.0016986 | No
9/10/2018 | 17:18:20 | SM410B | Urban | Asset failure | LV | 16.3333 | 97 | 0.0025328 | 2.611e-05 | No
9/10/2018 | 20:38:02 | M92 | Rural Long | Asset failure | HV | 460 | 38.3978 | 0.12891 | 0.0033572 | No
9/10/2018 | 20:38:02 | M92 | Rural Long | Asset failure | HV | 7 | 962 | 0.049147 | 5.109e-05 | No
9/10/2018 | 20:40:00 | LX71 | Rural Long | Unknown | Unknown | 10 | 280.6 | 0.020479 | 7.298e-05 | No
10/10/2018 | 03:07:36 | MB03 | Rural Long | Unknown | Unknown | 34 | 414 | 0.10273 | 0.00024814 | No
10/10/2018 | 05:24:43 | AP146E | Urban | Asset failure | LV | 21.6666 | 213 | 0.0073779 | 3.464e-05 | No
10/10/2018 | 08:10:32 | LC03 | Rural Long | Planned |  | 25 | 410 | 0.074808 | 0.00018246 | No
10/10/2018 | 08:49:52 | LX21 | Rural Short | Planned |  | 2 | 253 | 0.0037698 | 1.49e-05 | No
10/10/2018 | 09:01:11 | NU21 | Rural Long | Planned |  | 12 | 300 | 0.026274 | 8.758e-05 | No
10/10/2018 | 09:08:37 | EL01Z | Urban | Planned |  | 81 | 277 | 0.035869 | 0.00012949 | No
10/10/2018 | 09:16:51 | HH341K | Urban | Planned |  | 36 | 329 | 0.018935 | 5.755e-05 | No
10/10/2018 | 09:18:13 | CM11 | Rural Long | Planned |  | 66 | 142 | 0.0684 | 0.00048169 | No
10/10/2018 | 09:18:58 | GA02 | Rural Short | Planned |  | 264 | 284.803 | 0.56016 | 0.0019668 | No
10/10/2018 | 09:29:38 | VH43 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 102 | 59 | 0.044835 | 0.00075992 | No
10/10/2018 | 09:38:08 | HH145A | Urban | Planned |  | 56 | 310 | 0.027753 | 8.953e-05 | No
10/10/2018 | 10:00:33 | SM350B | Urban | Planned |  | 116 | 214 | 0.039686 | 0.00018545 | No
10/10/2018 | 10:15:57 | SD34201 | Rural Short | Planned |  | 31 | 4 | 0.00092382 | 0.00023095 | No
10/10/2018 | 10:25:41 | CN25 | Rural Long | Planned |  | 1 | 12 | 8.758e-05 | 7.3e-06 | No
10/10/2018 | 10:40:09 | HH177B | Urban | Planned |  | 225 | 215 | 0.077336 | 0.0003597 | No
10/10/2018 | 10:49:03 | CBD412A | Urban | Third Party | Vehicle impact | 1 | 45 | 7.194e-05 | 1.6e-06 | No
10/10/2018 | 12:02:49 | G28 | Rural Long | Planned |  | 102 | 160 | 0.11911 | 0.00074443 | No
10/10/2018 | 12:17:45 | R25 | Rural Long | Other |  | 1 | 193 | 0.0014086 | 7.3e-06 | No
10/10/2018 | 12:43:21 | NL234C | Urban | Asset failure | LV | 10.3333 | 295 | 0.0048733 | 1.652e-05 | No
10/10/2018 | 12:53:31 | NL760C | Urban | Third Party | Other | 1 | 150 | 0.0002398 | 1.6e-06 | No
10/10/2018 | 13:07:51 | MV13 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 118 | 0.00087912 | 7.45e-06 | No
10/10/2018 | 14:15:16 | SM179A | Urban | Planned |  | 1 | 2 | 3.2e-06 | 1.6e-06 | No
10/10/2018 | 14:19:26 | EL23 | Urban | Third Party | Other | 8.6667 | 163 | 0.0022584 | 1.386e-05 | No
10/10/2018 | 15:03:03 | NL234D | Urban | Unknown | Unknown | 40 | 96 | 0.0061389 | 6.395e-05 | No
10/10/2018 | 17:32:17 | AP355C | Urban | Unknown | Unknown | 2 | 211 | 0.00067464 | 3.2e-06 | No
10/10/2018 | 18:47:27 | HH107B | Urban | Unknown | Unknown | 73 | 47 | 0.005485 | 0.0001167 | No
10/10/2018 | 19:56:21 | HH121B | Urban | Asset failure | LV | 1 | 89 | 0.00014228 | 1.6e-06 | No
10/10/2018 | 20:55:44 | MV53 | Rural Short | Asset failure | LV | 1 | 176 | 0.0013112 | 7.45e-06 | No
10/10/2018 | 21:22:13 | NL115A | Urban | Planned |  | 803 | 1816.193 | 2.3315 | 0.0012837 | No
11/10/2018 | 06:39:40 | HH409D | Urban | Asset failure | LV | 22.6666 | 177 | 0.0064139 | 3.624e-05 | No
11/10/2018 | 07:39:41 | NL210D | Urban | Asset failure | LV | 20 | 359 | 0.011478 | 3.197e-05 | No
11/10/2018 | 08:01:43 | LC04 | Rural Long | Planned |  | 49 | 393 | 0.14054 | 0.00035762 | No
11/10/2018 | 08:19:34 | CD02 | Rural Long | Planned |  | 44 | 358 | 0.11496 | 0.00032113 | No
11/10/2018 | 08:28:19 | SD31100 | Rural Long | Unknown | Unknown | 2 | 435 | 0.0063495 | 1.46e-05 | No
11/10/2018 | 08:28:32 | WHY07 | Urban | Planned |  | 302 | 424 | 0.20471 | 0.0004828 | No
11/10/2018 | 08:35:36 | SM349B | Urban | Asset failure | LV | 137 | 102 | 0.02234 | 0.00021902 | No
11/10/2018 | 08:41:46 | PL754A | Rural Long | Planned |  | 24 | 252 | 0.04414 | 0.00017516 | No
11/10/2018 | 08:46:57 | YK29 | Rural Long | Planned |  | 2 | 12 | 0.00017516 | 1.46e-05 | No
11/10/2018 | 09:00:33 | EL25 | Urban | Planned |  | 664 | 297 | 0.31527 | 0.0010615 | No
11/10/2018 | 09:10:12 | SG09 | Rural Short | Planned |  | 6 | 200 | 0.0089402 | 4.47e-05 | No
11/10/2018 | 09:10:50 | MV63 | Rural Short | Planned |  | 16 | 189 | 0.022529 | 0.0001192 | No
11/10/2018 | 09:36:57 | HH107B | Urban | Planned |  | 41 | 51 | 0.0033428 | 6.555e-05 | No
11/10/2018 | 09:45:12 | HH107B | Urban | Planned |  | 1 | 55 | 8.793e-05 | 1.6e-06 | No
11/10/2018 | 09:53:28 | MB72 | Rural Long | Planned |  | 1 | 189 | 0.0013794 | 7.3e-06 | No
11/10/2018 | 09:53:33 | HH341C | Urban | Planned |  | 3 | 276 | 0.0013237 | 4.8e-06 | No
11/10/2018 | 10:01:55 | HH177B | Urban | Planned |  | 73 | 234 | 0.027309 | 0.0001167 | No
11/10/2018 | 10:06:19 | LX73 | Rural Long | Planned |  | 6 | 107 | 0.0046855 | 4.379e-05 | No
11/10/2018 | 10:35:21 | HH341C | Urban | Planned |  | 331 | 142 | 0.075141 | 0.00052916 | No
11/10/2018 | 10:46:47 | G13 | Rural Long | Planned |  | 2 | 53 | 0.00077362 | 1.46e-05 | No
11/10/2018 | 10:48:39 | HH121B | Urban | Asset failure | LV | 1 | 67 | 0.00010711 | 1.6e-06 | No
11/10/2018 | 10:52:07 | SG10 | Rural Short | Unknown | Unknown | 1 | 243 | 0.0018104 | 7.45e-06 | No
11/10/2018 | 10:53:26 | AP149D | Urban | Planned |  | 1 | 75 | 0.0001199 | 1.6e-06 | No
11/10/2018 | 11:58:36 | SD34300 | Rural Short | Planned |  | 99 | 1 | 0.00073756 | 0.00073756 | No
11/10/2018 | 12:18:07 | SD35200 | Rural Long | Asset failure | Subtransmission | 2 | 136 | 0.0019852 | 1.46e-05 | No
11/10/2018 | 13:26:55 | SG10 | Rural Short | Unknown | Unknown | 1 | 90 | 0.00067051 | 7.45e-06 | No
11/10/2018 | 13:49:09 | MG12 | Rural Long | Asset failure | LV | 2 | 67 | 0.00097798 | 1.46e-05 | No
11/10/2018 | 13:57:57 | W02 | Rural Long | Asset failure | LV | 1 | 135 | 0.00098528 | 7.3e-06 | No
11/10/2018 | 14:16:39 | CL17 | Rural Long | Planned |  | 223 | 60 | 0.097652 | 0.0016275 | No
11/10/2018 | 18:09:44 | NL111C | Urban | Asset failure | LV | 64 | 37 | 0.0037857 | 0.00010232 | No
11/10/2018 | 19:16:35 | PP08 | Rural Long | Other |  | 1 | 127 | 0.00092689 | 7.3e-06 | No
11/10/2018 | 21:22:23 | NL760B | Urban | Asset failure | LV | 17.3333 | 319 | 0.0088396 | 2.771e-05 | No
12/10/2018 | 07:29:29 | MG14 | Rural Long | Asset failure | LV | 2 | 169 | 0.0024668 | 1.46e-05 | No
12/10/2018 | 08:21:12 | EL15 | Urban | Unknown | Unknown | 2 | 110 | 0.00035171 | 3.2e-06 | No
12/10/2018 | 08:45:54 | NL115D | Urban | Planned |  | 52 | 75 | 0.0062348 | 8.313e-05 | No
12/10/2018 | 10:13:58 | GU43 | Rural Long | Third Party | Vehicle impact | 4 | 287 | 0.0083785 | 2.919e-05 | No
12/10/2018 | 11:02:47 | SG03 | Rural Short | Asset failure | LV | 2 | 370 | 0.0055131 | 1.49e-05 | No
12/10/2018 | 13:02:38 | GA15 | Rural Short | Planned |  | 89 | 70 | 0.046414 | 0.00066306 | No
12/10/2018 | 14:27:45 | SA17 | Urban | Asset failure | LV | 1 | 67 | 0.00010711 | 1.6e-06 | No
12/10/2018 | 15:50:56 | SM349F | Urban | Asset failure | LV | 52 | 151 | 0.012553 | 8.313e-05 | No
12/10/2018 | 16:04:03 | AP227B | Urban | Asset failure | LV | 65 | 123 | 0.012781 | 0.00010391 | No
12/10/2018 | 16:12:23 | MV64 | Urban | Asset failure | LV | 59 | 67 | 0.0063196 | 9.432e-05 | No
12/10/2018 | 16:13:01 | HH522C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 79 | 52 | 0.0065674 | 0.0001263 | No
12/10/2018 | 16:41:07 | NL511B | Urban | Asset failure | LV | 37.3334 | 170 | 0.010146 | 5.968e-05 | No
12/10/2018 | 19:00:29 | NL760C | Urban | Asset failure | LV | 1 | 203 | 0.00032453 | 1.6e-06 | No
13/10/2018 | 08:10:08 | AP132D | Urban | Planned |  | 10 | 1475 | 0.02358 | 1.599e-05 | No
13/10/2018 | 11:20:29 | SM402E | Urban | Asset failure | LV | 35 | 158 | 0.0088407 | 5.595e-05 | No
13/10/2018 | 14:39:17 | EL23 | Urban | Unknown | Unknown | 13 | 103 | 0.0021406 | 2.078e-05 | No
13/10/2018 | 14:57:39 | EL16 | Urban | Asset failure | HV | 15 | 336 | 0.0080573 | 2.398e-05 | No
13/10/2018 | 17:06:33 | EL23 | Urban | Unknown | Unknown | 7 | 215 | 0.002406 | 1.119e-05 | No
13/10/2018 | 19:02:59 | NL111B | Urban | Asset failure | LV | 81 | 77 | 0.0099709 | 0.00012949 | No
13/10/2018 | 19:07:56 | MG03 | Rural Short | Unknown | Unknown | 89 | 48 | 0.031827 | 0.00066306 | No
13/10/2018 | 19:18:19 | CV31 | Rural Long | Unknown | Unknown | 58 | 249.1552 | 0.10547 | 0.0004233 | No
13/10/2018 | 20:38:00 | HH432D | Urban | Overloads |  | 24.6666 | 121 | 0.0047715 | 3.943e-05 | No
13/10/2018 | 21:21:43 | KA04 | Rural Long | Asset failure | HV | 29.3333 | 76 | 0.01627 | 0.00021408 | No
14/10/2018 | 03:01:51 | HH107A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 849 | 61 | 0.082794 | 0.0013573 | No
14/10/2018 | 07:39:43 | MG26 | Rural Long | Unknown | Unknown | 11 | 131 | 0.010517 | 8.028e-05 | No
14/10/2018 | 08:05:11 | HH145C | Urban | Asset failure | LV | 12.6667 | 263 | 0.0053257 | 2.025e-05 | No
14/10/2018 | 08:32:33 | PA24 | Rural Long | Weather |  | 30 | 299 | 0.065466 | 0.00021895 | No
14/10/2018 | 09:00:45 | HH429C | Urban | Planned |  | 214 | 394 | 0.13479 | 0.00034212 | No
14/10/2018 | 09:26:56 | SA42 | Urban | Asset failure | LV | 1 | 184 | 0.00029416 | 1.6e-06 | No
14/10/2018 | 09:28:39 | HH121E | Urban | Planned |  | 16 | 402 | 0.010283 | 2.558e-05 | No
14/10/2018 | 09:36:23 | HH522C | Urban | Planned |  | 101 | 278.3267 | 0.04494 | 0.00016147 | No
14/10/2018 | 09:39:09 | CD25 | Rural Long | Planned |  | 99 | 256.697 | 0.18547 | 0.00072254 | No
14/10/2018 | 10:11:34 | G20 | Rural Long | Overloads |  | 56 | 745.8214 | 0.30482 | 0.00040871 | No
14/10/2018 | 10:22:26 | PP04 | Rural Short | Unknown | Unknown | 91 | 200 | 0.13559 | 0.00067796 | No
14/10/2018 | 10:34:41 | VH19 | Rural Short | Asset failure | LV | 2.3333 | 90 | 0.0015645 | 1.738e-05 | No
14/10/2018 | 10:49:52 | AP146B | Urban | Asset failure | LV | 84 | 358 | 0.048075 | 0.00013429 | No
14/10/2018 | 11:00:08 | SD32400 | Rural Long | Unknown | Unknown | 1 | 624 | 0.0045542 | 7.3e-06 | No
14/10/2018 | 11:02:00 | PP09 | Rural Long | Weather |  | 42 | 848.4524 | 0.26008 | 0.00030653 | No
14/10/2018 | 11:02:00 | PP09 | Rural Long | Weather |  | 0 | 2 | 0.00040871 | 0 | No
14/10/2018 | 11:04:55 | PP12 | Rural Long | Unknown | Unknown | 31 | 531 | 0.12014 | 0.00022625 | No
14/10/2018 | 11:34:45 | MT22 | Rural Long | Weather |  | 658 | 260 | 1.2486 | 0.0048023 | No
14/10/2018 | 11:50:06 | SM350B | Urban | Vegetation | Grow-in - NSP responsibility | 27 | 161 | 0.0069494 | 4.316e-05 | No
14/10/2018 | 11:56:28 | CL16 | Rural Long | Unknown | Unknown | 223 | 153 | 0.24901 | 0.0016275 | No
14/10/2018 | 12:07:00 | SD35100 | Rural Long | Weather |  | 2113 | 129.0033 | 1.9894 | 0.015421 | No
14/10/2018 | 12:07:00 | MT11 | Rural Long | Weather |  | 68 | 386.5 | 0.19181 | 0.00049629 | No
14/10/2018 | 12:28:02 | MT09 | Rural Long | Unknown | Unknown | 66 | 271 | 0.13054 | 0.00048169 | No
14/10/2018 | 13:12:38 | GA16 | Rural Long | Weather |  | 36 | 365.0278 | 0.095907 | 0.00026274 | No
14/10/2018 | 14:30:30 | MG03 | Rural Short | Unknown | Unknown | 4 | 175 | 0.0052151 | 2.98e-05 | No
14/10/2018 | 14:36:26 | PP16 | Rural Short | Unknown | Unknown | 74 | 207 | 0.11412 | 0.00055131 | No
14/10/2018 | 14:40:57 | MT02 | Rural Long | Weather |  | 133 | 420.5113 | 0.40818 | 0.00097068 | No
14/10/2018 | 15:02:34 | ST35 | Rural Long | Unknown | Unknown | 7 | 117 | 0.0059773 | 5.109e-05 | No
14/10/2018 | 15:40:58 | WK65 | Rural Short | Unknown | Unknown | 47 | 179 | 0.062678 | 0.00035016 | No
14/10/2018 | 16:10:04 | PA19 | Rural Long | Weather |  | 2 | 1364 | 0.01991 | 1.46e-05 | No
14/10/2018 | 16:27:17 | VH12 | Rural Short | Asset failure | LV | 98 | 182 | 0.13288 | 0.00073011 | No
14/10/2018 | 16:37:10 | HH341K | Urban | Overloads |  | 24.6666 | 68 | 0.0026815 | 3.943e-05 | No
14/10/2018 | 17:28:54 | SM402B | Urban | Overloads |  | 1 | 195 | 0.00031174 | 1.6e-06 | No
14/10/2018 | 18:07:58 | KA14 | Rural Long | Unknown | Unknown | 16 | 272 | 0.031762 | 0.00011677 | No
14/10/2018 | 19:09:31 | MB11 | Rural Short | Unknown | Unknown | 617 | 16 | 0.073548 | 0.0045967 | No
14/10/2018 | 19:25:43 | SM374B | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
14/10/2018 | 19:28:25 | CBD367G | CBD | Planned |  | 4 | 515.25 | 0.40008 | 0.00077647 | No
14/10/2018 | 20:13:33 | ME231E | Urban | Third Party | Vehicle impact | 113 | 402 | 0.072621 | 0.00018065 | No
14/10/2018 | 20:40:11 | HH145C | Urban | Planned |  | 1 | 491 | 0.00078495 | 1.6e-06 | No
14/10/2018 | 21:02:43 | MTB52 | Rural Long | Asset failure | LV | 2.3333 | 45 | 0.00076632 | 1.703e-05 | No
14/10/2018 | 21:11:35 | CV31 | Rural Long | Unknown | Unknown | 58 | 1016.5172 | 0.4303 | 0.0004233 | No
14/10/2018 | 21:30:51 | VH44 | Rural Short | Weather |  | 3 | 699 | 0.015623 | 2.235e-05 | No
14/10/2018 | 22:18:26 | CD03 | Rural Short | Asset failure | HV | 745 | 105.6121 | 0.58619 | 0.0055504 | No
14/10/2018 | 23:29:11 | MT01 | Rural Long | Weather |  | 11 | 723 | 0.058044 | 8.028e-05 | No
14/10/2018 | 23:39:43 | SB03 | Rural Long | Unknown | Unknown | 3 | 731 | 0.016005 | 2.19e-05 | No
15/10/2018 | 00:25:33 | HH130F | Urban | Unknown | Unknown | 19.6666 | 122 | 0.0038358 | 3.144e-05 | Yes
15/10/2018 | 00:27:31 | SM350D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 785 | 30 | 0.037649 | 0.001255 | Yes
15/10/2018 | 00:31:43 | PL11 | Rural Long | Unknown | Unknown | 68 | 521 | 0.25857 | 0.00049629 | Yes
15/10/2018 | 02:19:53 | ME131D | Urban | Asset failure | LV | 64 | 117 | 0.011971 | 0.00010232 | Yes
15/10/2018 | 02:29:59 | ME131E | Urban | Asset failure | LV | 87 | 100 | 0.013908 | 0.00013908 | Yes
15/10/2018 | 03:38:42 | CL09 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 683 | 214 | 1.0667 | 0.0049848 | Yes
15/10/2018 | 04:56:08 | HH409D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 22.6666 | 386 | 0.013987 | 3.624e-05 | Yes
15/10/2018 | 05:14:00 | SD1611 | Rural Short | Weather |  | 100 | 254 | 0.18923 | 0.00074501 | Yes
15/10/2018 | 05:14:00 | SD1611 | Rural Long | Weather |  | 330 | 254 | 0.61175 | 0.0024084 | Yes
15/10/2018 | 05:24:04 | PP10 | Urban | Weather |  | 67 | 564 | 0.060411 | 0.00010711 | Yes
15/10/2018 | 05:28:24 | PP18 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 221 | 318 | 0.51291 | 0.0016129 | Yes
15/10/2018 | 05:43:22 | PP04 | Rural Short | Weather |  | 48 | 297 | 0.10621 | 0.00035761 | Yes
15/10/2018 | 06:21:22 | NU13 | Rural Long | Weather |  | 2 | 301 | 0.0043936 | 1.46e-05 | Yes
15/10/2018 | 06:28:06 | CL24 | Rural Long | Weather |  | 49 | 232 | 0.082967 | 0.00035762 | Yes
15/10/2018 | 06:32:32 | BM11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 423 | 76.695 | 0.2417 | 0.0031514 | Yes
15/10/2018 | 06:35:10 | NA02 | Rural Long | Weather |  | 6 | 268 | 0.011736 | 4.379e-05 | Yes
15/10/2018 | 06:58:53 | NU15 | Rural Long | Unknown | Unknown | 9 | 92.7778 | 0.0060941 | 6.569e-05 | Yes
15/10/2018 | 07:00:42 | SB16 | Rural Long | Weather |  | 18 | 829.2778 | 0.10894 | 0.00013137 | Yes
15/10/2018 | 07:03:07 | PA22 | Rural Long | Weather |  | 9 | 707 | 0.046439 | 6.569e-05 | Yes
15/10/2018 | 07:11:00 | SM179C | Urban | Unknown | Unknown | 1307 | 150.6534 | 0.31479 | 0.0020895 | Yes
15/10/2018 | 07:14:11 | HH386G | Urban | Asset failure | LV | 21 | 540 | 0.018129 | 3.357e-05 | Yes
15/10/2018 | 07:17:10 | W29 | Rural Long | Weather |  | 83 | 649.5542 | 0.39348 | 0.00060576 | Yes
15/10/2018 | 07:20:16 | AP373D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 626 | 0.0010008 | 1.6e-06 | Yes
15/10/2018 | 07:22:00 | SSD403 | Urban | Unknown | Unknown | 15667 | 142.7742 | 3.576 | 0.025046 | Yes
15/10/2018 | 07:23:00 | HH409F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2015 | 114.5057 | 0.36886 | 0.0032213 | Yes
15/10/2018 | 07:28:11 | AP425B | Urban | Asset failure | LV | 1 | 423 | 0.00067624 | 1.6e-06 | Yes
15/10/2018 | 07:30:10 | LX51 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 6.6667 | 499 | 0.024784 | 4.967e-05 | Yes
15/10/2018 | 07:39:39 | SM402B | Urban | Asset failure | LV | 60 | 156 | 0.014964 | 9.592e-05 | Yes
15/10/2018 | 07:43:42 | SG04 | Rural Short | Unknown | Unknown | 141 | 108.4043 | 0.11388 | 0.0010505 | Yes
15/10/2018 | 07:46:00 | MG51 | Rural Long | Unknown | Unknown | 15 | 336 | 0.036784 | 0.00010948 | Yes
15/10/2018 | 07:47:13 | HH177C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 27 | 576 | 0.024863 | 4.316e-05 | Yes
15/10/2018 | 07:50:24 | NU15 | Rural Long | Weather |  | 73 | 80 | 0.042622 | 0.00053278 | Yes
15/10/2018 | 07:56:35 | CD04 | Rural Short | Weather |  | 126.6667 | 404 | 0.38125 | 0.00094369 | Yes
15/10/2018 | 07:56:53 | ME200E | Urban | Asset failure | LV | 22.6666 | 432 | 0.015654 | 3.624e-05 | Yes
15/10/2018 | 08:00:19 | HH409E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 77 | 564 | 0.069427 | 0.0001231 | Yes
15/10/2018 | 08:02:36 | HH522B | Urban | Unknown | Unknown | 248 | 564 | 0.22361 | 0.00039647 | Yes
15/10/2018 | 08:05:03 | CL12 | Rural Long | Weather |  | 93 | 318.043 | 0.21587 | 0.00067875 | Yes
15/10/2018 | 08:06:33 | KI21 | Rural Long | Unknown | Unknown | 15 | 123 | 0.013465 | 0.00010948 | Yes
15/10/2018 | 08:06:55 | HH432D | Urban | Unknown | Unknown | 17.6666 | 102 | 0.0028808 | 2.824e-05 | Yes
15/10/2018 | 08:08:28 | M73 | Rural Long | Weather |  | 74 | 368 | 0.19875 | 0.00054008 | Yes
15/10/2018 | 08:10:08 | R11 | Rural Long | Weather |  | 81 | 344.2963 | 0.20354 | 0.00059117 | Yes
15/10/2018 | 08:14:42 | SA14 | Urban | Vegetation | Grow-in - NSP responsibility | 8.6667 | 199 | 0.0027572 | 1.386e-05 | Yes
15/10/2018 | 08:16:06 | AP529B | Urban | Asset failure | HV | 26.6667 | 589 | 0.02511 | 4.263e-05 | Yes
15/10/2018 | 08:18:21 | HH121C | Urban | Vegetation | Grow-in - NSP responsibility | 28 | 773 | 0.034602 | 4.476e-05 | Yes
15/10/2018 | 08:19:37 | HH177B | Urban | Asset failure | LV | 1 | 559 | 0.00089366 | 1.6e-06 | Yes
15/10/2018 | 08:22:46 | HH177B | Urban | Vegetation | Grow-in - NSP responsibility | 14.6667 | 609 | 0.014279 | 2.345e-05 | Yes
15/10/2018 | 08:23:48 | HH177G | Urban | Vegetation | Grow-in - NSP responsibility | 20.3333 | 786 | 0.02555 | 3.251e-05 | Yes
15/10/2018 | 08:24:00 | SA16 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1877 | 132.8247 | 0.39857 | 0.0030007 | Yes
15/10/2018 | 08:29:01 | SM374A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 845 | 314 | 0.42418 | 0.0013509 | Yes
15/10/2018 | 08:30:00 | HH177F | Urban | Unknown | Unknown | 2118 | 128.4542 | 0.43495 | 0.003386 | Yes
15/10/2018 | 08:30:15 | MG11 | Rural Short | Asset failure | LV | 1 | 164 | 0.0012218 | 7.45e-06 | Yes
15/10/2018 | 08:31:43 | HH177C | Urban | Planned |  | 49 | 653 | 0.051153 | 7.834e-05 | Yes
15/10/2018 | 08:35:36 | HH177C | Urban | Unknown | Unknown | 27.3333 | 675 | 0.029496 | 4.37e-05 | Yes
15/10/2018 | 08:43:30 | SM402D | Urban | Asset failure | LV | 122 | 62 | 0.012092 | 0.00019504 | Yes
15/10/2018 | 08:43:57 | CV29 | Rural Long | Weather |  | 40 | 510.025 | 0.14889 | 0.00029193 | Yes
15/10/2018 | 08:44:18 | BM12 | Rural Short | Weather |  | 456 | 75.2412 | 0.25561 | 0.0033973 | Yes
15/10/2018 | 08:45:56 | CV26 | Rural Long | Weather |  | 66 | 545 | 0.26252 | 0.00048169 | Yes
15/10/2018 | 08:46:09 | SM411C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 42 | 84 | 0.0056401 | 6.714e-05 | Yes
15/10/2018 | 08:52:12 | AP132A | Urban | Asset failure | HV | 11.3333 | 136 | 0.0024641 | 1.812e-05 | Yes
15/10/2018 | 09:01:31 | HH177E | Urban | Asset failure | LV | 21 | 769 | 0.025817 | 3.357e-05 | Yes
15/10/2018 | 09:03:00 | HH121E | Urban | Asset failure | HV | 518 | 582.4402 | 0.48233 | 0.00082811 | Yes
15/10/2018 | 09:11:00 | AP344F | Urban | Vegetation | Grow-in - NSP responsibility | 494 | 111 | 0.087662 | 0.00078975 | Yes
15/10/2018 | 09:15:00 | SA33 | Urban | Weather |  | 2 | 309 | 0.00098798 | 3.2e-06 | Yes
15/10/2018 | 09:16:32 | PP04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 78 | 559 | 0.32484 | 0.00058111 | Yes
15/10/2018 | 09:17:38 | MB91 | Rural Long | Planned |  | 6 | 45 | 0.0019706 | 4.379e-05 | Yes
15/10/2018 | 09:20:04 | SM349A | Urban | Asset failure | LV | 21.3333 | 483 | 0.016473 | 3.411e-05 | Yes
15/10/2018 | 09:21:11 | AP373E | Urban | Asset failure | HV | 222 | 615 | 0.21827 | 0.00035491 | Yes
15/10/2018 | 09:21:21 | NL111B | Urban | Unknown | Unknown | 46 | 352 | 0.025886 | 7.354e-05 | Yes
15/10/2018 | 09:22:00 | LX41 | Rural Short | Weather |  | 26 | 162.9231 | 0.031559 | 0.0001937 | Yes
15/10/2018 | 09:22:23 | M91 | Rural Long | Unknown | Unknown | 36 | 220 | 0.057803 | 0.00026274 | Yes
15/10/2018 | 09:23:41 | SM410B | Urban | Asset failure | LV | 15.6667 | 89 | 0.0022291 | 2.505e-05 | Yes
15/10/2018 | 09:24:07 | SM216G | Urban | Unknown | Unknown | 29.3333 | 420 | 0.019696 | 4.689e-05 | Yes
15/10/2018 | 09:29:47 | AP227A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 70 | 228 | 0.025515 | 0.00011191 | Yes
15/10/2018 | 09:31:25 | MTB41 | Rural Short | Weather |  | 43 | 164 | 0.052538 | 0.00032036 | Yes
15/10/2018 | 09:36:00 | WK43 | Rural Short | Unknown | Unknown | 10 | 139 | 0.010356 | 7.45e-05 | Yes
15/10/2018 | 09:36:29 | AP425C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1617 | 7.2876 | 0.018839 | 0.0025851 | Yes
15/10/2018 | 09:36:35 | SM126A | Urban | Asset failure | HV | 423 | 343.6809 | 0.23241 | 0.00067624 | Yes
15/10/2018 | 09:39:26 | HH177C | Urban | Unknown | Unknown | 14.6667 | 585 | 0.013717 | 2.345e-05 | Yes
15/10/2018 | 09:41:37 | HH341D | Urban | Asset failure | LV | 12 | 739 | 0.014177 | 1.918e-05 | Yes
15/10/2018 | 09:46:32 | PA03 | Urban | Asset failure | LV | 1 | 503 | 0.00080413 | 1.6e-06 | Yes
15/10/2018 | 09:53:54 | VH22 | Rural Short | Planned |  | 123 | 123 | 0.11271 | 0.00091637 | Yes
15/10/2018 | 09:54:52 | ST22 | Rural Short | Planned |  | 42 | 290 | 0.090743 | 0.00031291 | Yes
15/10/2018 | 09:56:46 | AP132D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 197 | 0.00031494 | 1.6e-06 | Yes
15/10/2018 | 09:57:10 | HH148A | Urban | Unknown | Unknown | 910 | 190.9286 | 0.27776 | 0.0014548 | Yes
15/10/2018 | 09:57:53 | HH409F | Urban | Unknown | Unknown | 225 | 571 | 0.20539 | 0.0003597 | Yes
15/10/2018 | 09:57:57 | WK43 | Rural Short | Weather |  | 1 | 184 | 0.0013708 | 7.45e-06 | Yes
15/10/2018 | 09:59:35 | MB03 | Rural Long | Weather |  | 36 | 456 | 0.11981 | 0.00026274 | Yes
15/10/2018 | 10:03:26 | SM126D | Urban | Other |  | 1 | 336 | 0.00053715 | 1.6e-06 | Yes
15/10/2018 | 10:03:45 | ME200F | Urban | Asset failure | LV | 4 | 84 | 0.00053715 | 6.39e-06 | Yes
15/10/2018 | 10:06:51 | NU15 | Rural Long | Weather |  | 836 | 105.6962 | 0.6449 | 0.0061014 | Yes
15/10/2018 | 10:06:51 | NU15 | Rural Long | Weather |  | 3 | 267 | 0.005846 | 2.19e-05 | Yes
15/10/2018 | 10:09:30 | HH177G | Urban | Unknown | Unknown | 22.6666 | 604 | 0.021887 | 3.624e-05 | Yes
15/10/2018 | 10:10:57 | NL234D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1550 | 126.0555 | 0.31236 | 0.002478 | Yes
15/10/2018 | 10:11:38 | HH429A | Urban | Unknown | Unknown | 28 | 258 | 0.011549 | 4.476e-05 | Yes
15/10/2018 | 10:12:59 | AP132D | Urban | Asset failure | HV | 27 | 42 | 0.0018129 | 4.316e-05 | Yes
15/10/2018 | 10:17:05 | AP355A | Urban | Unknown | Unknown | 30.3333 | 501 | 0.024295 | 4.849e-05 | Yes
15/10/2018 | 10:17:07 | HH118D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21.3333 | 536 | 0.01828 | 3.411e-05 | Yes
15/10/2018 | 10:21:04 | MG11 | Rural Short | Unknown | Unknown | 1 | 59 | 0.00043956 | 7.45e-06 | Yes
15/10/2018 | 10:24:01 | SM179D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 834 | 401.4436 | 0.53524 | 0.0013333 | Yes
15/10/2018 | 10:25:37 | SM350E | Urban | Weather |  | 28 | 203 | 0.0090869 | 4.476e-05 | Yes
15/10/2018 | 10:29:15 | NL511B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 22.6666 | 247 | 0.0089504 | 3.624e-05 | Yes
15/10/2018 | 10:31:51 | NL210B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 929 | 264 | 0.39208 | 0.0014852 | Yes
15/10/2018 | 10:38:10 | HH409F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 40 | 20 | 0.0012789 | 6.395e-05 | Yes
15/10/2018 | 10:39:55 | HH148D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 537 | 0.00085849 | 1.6e-06 | Yes
15/10/2018 | 10:48:24 | HH148B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 745 | 0.001191 | 1.6e-06 | Yes
15/10/2018 | 10:48:41 | LM31 | Rural Long | Unknown | Unknown | 29 | 248 | 0.05249 | 0.00021165 | Yes
15/10/2018 | 10:49:36 | SM350A | Urban | Other |  | 2 | 572 | 0.0018289 | 3.2e-06 | Yes
15/10/2018 | 10:51:12 | CV20 | Rural Long | Weather |  | 34 | 889.6471 | 0.22076 | 0.00024814 | Yes
15/10/2018 | 10:52:25 | NU05 | Rural Short | Third Party | Other | 2 | 545 | 0.0081207 | 1.49e-05 | Yes
15/10/2018 | 10:54:01 | HH145A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 22.6666 | 537 | 0.019459 | 3.624e-05 | Yes
15/10/2018 | 11:08:48 | LX24 | Rural Short | Unknown | Unknown | 3 | 208 | 0.0046489 | 2.235e-05 | Yes
15/10/2018 | 11:13:30 | G42 | Rural Long | Weather |  | 18 | 1541 | 0.20244 | 0.00013137 | Yes
15/10/2018 | 11:13:41 | HH121F | Urban | Third Party | Other | 22 | 511 | 0.017972 | 3.517e-05 | Yes
15/10/2018 | 11:18:59 | GU32 | Rural Long | Unknown | Unknown | 12 | 186 | 0.01629 | 8.758e-05 | Yes
15/10/2018 | 11:20:11 | ME231D | Urban | Weather |  | 1 | 237 | 0.00037889 | 1.6e-06 | Yes
15/10/2018 | 11:30:57 | SM411C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 56 | 234 | 0.020949 | 8.953e-05 | Yes
15/10/2018 | 11:32:55 | SA32 | Urban | Weather |  | 12.6667 | 164 | 0.003321 | 2.025e-05 | Yes
15/10/2018 | 11:37:53 | ME231F | Urban | Other |  | 1 | 222 | 0.00035491 | 1.6e-06 | Yes
15/10/2018 | 11:38:09 | HH107A | Urban | Vegetation | Grow-in - NSP responsibility | 24.6666 | 726 | 0.028629 | 3.943e-05 | Yes
15/10/2018 | 11:46:53 | BT04 | Rural Long | Weather |  | 16 | 299.1875 | 0.034937 | 0.00011677 | Yes
15/10/2018 | 11:51:56 | CD03 | Rural Short | Weather |  | 745 | 140 | 0.77705 | 0.0055504 | Yes
15/10/2018 | 12:05:14 | LM12 | Rural Long | Unknown | Unknown | 24 | 125 | 0.021895 | 0.00017516 | Yes
15/10/2018 | 12:13:50 | BM34 | Rural Short | Weather |  | 113 | 102 | 0.08587 | 0.00084187 | Yes
15/10/2018 | 12:20:26 | HH102A | Urban | Vegetation | Grow-in - NSP responsibility | 28.6666 | 437 | 0.020027 | 4.583e-05 | Yes
15/10/2018 | 12:20:52 | BT04 | Rural Long | Unknown | Unknown | 55.3334 | 117 | 0.047249 | 0.00040384 | Yes
15/10/2018 | 12:31:42 | BT04 | Rural Long | Unknown | Unknown | 16 | 310.625 | 0.036273 | 0.00011677 | Yes
15/10/2018 | 12:37:42 | PP18 | Rural Long | Asset failure | LV | 1 | 381 | 0.0027807 | 7.3e-06 | Yes
15/10/2018 | 12:43:27 | AP344D | Urban | Unknown | Unknown | 1 | 322 | 0.00051477 | 1.6e-06 | Yes
15/10/2018 | 12:53:00 | ST51 | Rural Short | Unknown | Unknown | 29.3333 | 169 | 0.036933 | 0.00021854 | Yes
15/10/2018 | 12:53:35 | SA33 | Urban | Weather |  | 1 | 78 | 0.0001247 | 1.6e-06 | Yes
15/10/2018 | 13:12:48 | HH130A | Urban | Unknown | Unknown | 32.6667 | 447 | 0.023344 | 5.222e-05 | Yes
15/10/2018 | 13:33:03 | PP04 | Rural Short | Vegetation | Grow-in - NSP responsibility | 43 | 205 | 0.065673 | 0.00032036 | Yes
15/10/2018 | 13:52:33 | EL13 | Urban | Asset failure | LV | 19 | 110 | 0.0033412 | 3.037e-05 | Yes
15/10/2018 | 13:57:02 | AP227B | Urban | Asset failure | LV | 1 | 159 | 0.00025419 | 1.6e-06 | Yes
15/10/2018 | 14:11:59 | SM374B | Urban | Unknown | Unknown | 429 | 23.5897 | 0.016179 | 0.00068583 | Yes
15/10/2018 | 14:39:27 | HH107D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 705 | 0.0011271 | 1.6e-06 | Yes
15/10/2018 | 14:48:38 | ME231E | Urban | Asset failure | LV | 1 | 112 | 0.00017905 | 1.6e-06 | Yes
15/10/2018 | 14:54:42 | ME231E | Urban | Asset failure | LV | 19.3333 | 102 | 0.0031526 | 3.091e-05 | Yes
15/10/2018 | 14:55:11 | GA13 | Rural Long | Unknown | Unknown | 1 | 193 | 0.0014086 | 7.3e-06 | Yes
15/10/2018 | 15:05:00 | HH145C | Urban | Asset failure | LV | 21 | 300 | 0.010072 | 3.357e-05 | Yes
15/10/2018 | 15:05:07 | AP132A | Urban | Weather |  | 1.3333 | 254 | 0.00054142 | 2.13e-06 | Yes
15/10/2018 | 15:31:17 | NA15 | Rural Long | Unknown | Unknown | 4 | 261 | 0.0076195 | 2.919e-05 | Yes
15/10/2018 | 15:32:19 | BT03 | Rural Long | Weather |  | 29 | 232 | 0.049103 | 0.00021165 | Yes
15/10/2018 | 15:33:30 | HH177C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 311 | 0.00049719 | 1.6e-06 | Yes
15/10/2018 | 15:38:19 | HH432C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 110 | 0.00017585 | 1.6e-06 | Yes
15/10/2018 | 15:49:30 | SM411C | Urban | Asset failure | LV | 18.6666 | 253 | 0.00755 | 2.984e-05 | Yes
15/10/2018 | 16:20:19 | SM374B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 101 | 0.00016147 | 1.6e-06 | Yes
15/10/2018 | 16:48:33 | LX71 | Rural Long | Unknown | Unknown | 7 | 127 | 0.0064882 | 5.109e-05 | Yes
15/10/2018 | 17:15:44 | HH145B | Urban | Weather |  | 81 | 51 | 0.0066041 | 0.00012949 | Yes
15/10/2018 | 17:18:04 | LM13 | Rural Long | Unknown | Unknown | 81 | 127 | 0.075078 | 0.00059117 | Yes
15/10/2018 | 17:18:14 | MV31 | Rural Short | Unknown | Unknown | 52.3333 | 119 | 0.046397 | 0.00038989 | Yes
15/10/2018 | 17:21:35 | SM137A | Urban | Asset failure | LV | 45 | 38 | 0.0027337 | 7.194e-05 | Yes
15/10/2018 | 17:23:40 | BM15 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 203 | 114 | 0.17241 | 0.0015124 | Yes
15/10/2018 | 17:39:28 | SM349F | Urban | Asset failure | LV | 1 | 71 | 0.00011351 | 1.6e-06 | Yes
15/10/2018 | 17:40:17 | HH409E | Urban | Weather |  | 1 | 141 | 0.00022541 | 1.6e-06 | Yes
15/10/2018 | 17:47:47 | LM31 | Rural Long | Weather |  | 29 | 350.3448 | 0.074151 | 0.00021165 | Yes
15/10/2018 | 17:47:47 | LM31 | Rural Long | Weather |  | 0 | 17.5 | 0.0040871 | 0 | Yes
15/10/2018 | 17:49:16 | LX42 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 270 | 0.0020115 | 7.45e-06 | Yes
15/10/2018 | 18:02:50 | MI26 | Rural Long | Animal | Animal nesting/burrowing, etc and other | 71 | 228.7183 | 0.11852 | 0.00051818 | Yes
15/10/2018 | 18:08:36 | LX54 | Rural Short | Weather |  | 22 | 525 | 0.086049 | 0.0001639 | Yes
15/10/2018 | 18:15:55 | HH121D | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | Yes
15/10/2018 | 18:17:30 | CN76 | Rural Long | Weather |  | 39 | 1157.4359 | 0.32945 | 0.00028464 | Yes
15/10/2018 | 18:18:53 | HH386C | Urban | Vegetation | Grow-in - NSP responsibility | 8 | 126 | 0.0016115 | 1.279e-05 | Yes
15/10/2018 | 18:53:56 | LX71 | Rural Long | Asset failure | HV | 128 | 1030.3828 | 0.96257 | 0.00093419 | Yes
15/10/2018 | 19:03:19 | AP355A | Urban | Asset failure | LV | 1 | 269 | 0.00043004 | 1.6e-06 | Yes
15/10/2018 | 19:12:06 | AP132A | Urban | Weather |  | 3.3333 | 5 | 2.664e-05 | 5.33e-06 | Yes
15/10/2018 | 19:14:19 | BT23 | Rural Long | Weather |  | 50 | 1158 | 0.42257 | 0.00036492 | Yes
15/10/2018 | 19:14:52 | HH107C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 58 | 68 | 0.0063052 | 9.272e-05 | Yes
15/10/2018 | 19:23:44 | BM33 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 410 | 69 | 0.21076 | 0.0030546 | Yes
15/10/2018 | 19:34:10 | HH148A | Urban | Weather |  | 18 | 47 | 0.0013525 | 2.878e-05 | Yes
15/10/2018 | 19:48:59 | PL11 | Rural Long | Unknown | Unknown | 68 | 140 | 0.06948 | 0.00049629 | Yes
15/10/2018 | 20:01:00 | LX51 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 117 | 101 | 0.088038 | 0.00087167 | Yes
15/10/2018 | 20:06:05 | BM34 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 42 | 0.00062581 | 1.49e-05 | Yes
15/10/2018 | 20:38:10 | LM51 | Rural Long | Unknown | Unknown | 19 | 944 | 0.1309 | 0.00013867 | Yes
15/10/2018 | 20:44:13 | NA61 | Rural Long | Weather |  | 70 | 1262.5429 | 0.64501 | 0.00051088 | Yes
15/10/2018 | 20:44:13 | NA61 | Rural Long | Weather |  | 0 | 88 | 0.005138 | 0 | Yes
15/10/2018 | 20:47:40 | CBD412L | CBD | Planned |  | 1 | 1391 | 0.27002 | 0.00019412 | Yes
15/10/2018 | 20:59:26 | KA03 | Rural Long | Weather |  | 9.3333 | 74 | 0.0050407 | 6.812e-05 | Yes
15/10/2018 | 21:18:57 | NA22 | Rural Long | Unknown | Unknown | 2 | 48 | 0.00070064 | 1.46e-05 | Yes
15/10/2018 | 21:24:33 | BM12 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 1121 | 0.033406 | 2.98e-05 | Yes
15/10/2018 | 21:52:09 | NA09 | Rural Long | Unknown | Unknown | 10 | 120 | 0.008758 | 7.298e-05 | Yes
15/10/2018 | 21:55:21 | KA15 | Rural Long | Asset failure | Distribution substation | 59 | 130.0169 | 0.055986 | 0.0004306 | Yes
15/10/2018 | 22:27:02 | NA04 | Rural Long | Unknown | Unknown | 5 | 912 | 0.03328 | 3.649e-05 | Yes
15/10/2018 | 22:29:48 | KA03 | Rural Long | Weather |  | 9.3333 | 614 | 0.041824 | 6.812e-05 | Yes
15/10/2018 | 23:13:18 | BM21 | Rural Short | Unknown | Unknown | 13 | 829 | 0.08029 | 9.685e-05 | Yes
15/10/2018 | 23:13:47 | BM21 | Rural Short | Other |  | 1 | 833 | 0.006206 | 7.45e-06 | Yes
15/10/2018 | 23:14:52 | SM350G | Urban | Vegetation | Grow-in - NSP responsibility | 71 | 49 | 0.0055618 | 0.00011351 | Yes
15/10/2018 | 23:18:03 | HH341K | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1952 | 86.8438 | 0.27101 | 0.0031206 | Yes
16/10/2018 | 00:16:00 | PL11 | Rural Long | Unknown | Unknown | 99 | 429.8586 | 0.31059 | 0.00072254 | No
16/10/2018 | 00:25:57 | HH107D | Urban | Asset failure | LV | 89 | 90 | 0.012805 | 0.00014228 | No
16/10/2018 | 00:38:25 | SM374A | Urban | Asset failure | LV | 20 | 124 | 0.0039647 | 3.197e-05 | No
16/10/2018 | 02:31:20 | MTB52 | Rural Long | Weather |  | 972 | 154.4938 | 1.096 | 0.007094 | No
16/10/2018 | 02:57:01 | HH409D | Urban | Asset failure | LV | 1 | 101 | 0.00016147 | 1.6e-06 | No
16/10/2018 | 04:17:06 | HH409D | Urban | Asset failure | LV | 1 | 16 | 2.558e-05 | 1.6e-06 | No
16/10/2018 | 05:45:20 | NA05 | Rural Long | Weather |  | 1 | 608 | 0.0044374 | 7.3e-06 | No
16/10/2018 | 05:53:00 | MTB52 | Rural Long | Unknown | Unknown | 972 | 59.5021 | 0.42211 | 0.007094 | No
16/10/2018 | 05:58:28 | NA04 | Rural Long | Unknown | Unknown | 9 | 535 | 0.035141 | 6.569e-05 | No
16/10/2018 | 06:38:49 | SM126B | Urban | Weather |  | 13 | 243 | 0.0050502 | 2.078e-05 | No
16/10/2018 | 08:22:33 | SM126A | Urban | Weather |  | 423 | 330.5296 | 0.22352 | 0.00067624 | No
16/10/2018 | 08:24:13 | SM126A | Urban | Weather |  | 70 | 491 | 0.054946 | 0.00011191 | No
16/10/2018 | 08:44:58 | YK17 | Rural Long | Planned |  | 239 | 396 | 0.69074 | 0.0017443 | No
16/10/2018 | 09:24:51 | NA09 | Rural Long | Weather |  | 266 | 80.6053 | 0.15648 | 0.0019414 | No
16/10/2018 | 09:58:06 | ST41 | Rural Long | Planned |  | 50 | 282 | 0.10291 | 0.00036492 | No
16/10/2018 | 10:57:23 | HH107B | Urban | Planned |  | 156 | 266 | 0.066339 | 0.00024939 | No
16/10/2018 | 11:07:36 | GA800A | Rural Short | Third Party | Vehicle impact | 9 | 289 | 0.019378 | 6.705e-05 | No
16/10/2018 | 11:12:30 | AP146A | Urban | Asset failure | HV | 3 | 209 | 0.0010024 | 4.8e-06 | No
16/10/2018 | 12:03:37 | EL260C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 118 | 0.00018864 | 1.6e-06 | No
16/10/2018 | 12:35:29 | HH107B | Urban | Planned |  | 2 | 102 | 0.00032613 | 3.2e-06 | No
16/10/2018 | 12:49:23 | HH107A | Urban | Overloads |  | 24.6666 | 185 | 0.0072953 | 3.943e-05 | No
16/10/2018 | 13:26:47 | SD35200 | Rural Long | Weather |  | 6 | 79.5 | 0.0034813 | 4.379e-05 | No
16/10/2018 | 13:45:38 | SG07 | Rural Short | Asset failure | LV | 2.6667 | 14 | 0.00027814 | 1.987e-05 | No
16/10/2018 | 13:55:57 | ME200D | Urban | Other |  | 5.6667 | 112 | 0.0010146 | 9.06e-06 | No
16/10/2018 | 14:15:58 | HH107B | Urban | Planned |  | 1 | 18 | 2.878e-05 | 1.6e-06 | No
16/10/2018 | 14:33:48 | CM17 | Rural Long | Planned |  | 19 | 55 | 0.0076268 | 0.00013867 | No
16/10/2018 | 15:08:39 | SM411D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1554 | 41 | 0.10186 | 0.0024843 | No
16/10/2018 | 15:10:05 | EL16 | Urban | Unknown | Unknown | 1.6667 | 147 | 0.00039167 | 2.66e-06 | No
16/10/2018 | 16:00:56 | AP351C | Urban | Unknown | Unknown | 16.6667 | 134 | 0.0035704 | 2.664e-05 | No
16/10/2018 | 16:31:53 | BT04 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 101 | 137 | 0.10099 | 0.00073713 | No
16/10/2018 | 17:52:58 | HH121A | Urban | Asset failure | LV | 107 | 151 | 0.02583 | 0.00017106 | No
16/10/2018 | 18:00:49 | HH177E | Urban | Asset failure | LV | 1 | 298 | 0.00047641 | 1.6e-06 | No
16/10/2018 | 18:20:44 | HH177C | Urban | Asset failure | LV | 1 | 276 | 0.00044123 | 1.6e-06 | No
16/10/2018 | 19:36:54 | ME200G | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 367 | 0.00058671 | 1.6e-06 | No
16/10/2018 | 19:52:05 | NL511B | Urban | Asset failure | LV | 1 | 502 | 0.00080253 | 1.6e-06 | No
16/10/2018 | 20:08:05 | SM349C | Urban | Unknown | Unknown | 2 | 71 | 0.00022701 | 3.2e-06 | No
16/10/2018 | 20:09:57 | SM137D | Urban | Unknown | Unknown | 1 | 48 | 7.674e-05 | 1.6e-06 | No
16/10/2018 | 20:29:40 | HH409C | Urban | Asset failure | LV | 4.6667 | 189 | 0.00141 | 7.46e-06 | No
16/10/2018 | 20:32:57 | SG13 | Rural Short | Unknown | Unknown | 15.3333 | 108 | 0.012337 | 0.00011424 | No
16/10/2018 | 21:08:00 | CN53 | Rural Long | Unknown | Unknown | 3 | 232 | 0.0050796 | 2.19e-05 | No
16/10/2018 | 22:04:27 | HH386C | Urban | Asset failure | LV | 1 | 156 | 0.00024939 | 1.6e-06 | No
16/10/2018 | 22:55:27 | SG13 | Rural Short | Asset failure | LV | 15.3333 | 165 | 0.018849 | 0.00011424 | No
16/10/2018 | 23:58:09 | MV62 | Rural Short | Asset failure | LV | 3 | 29 | 0.00064816 | 2.235e-05 | No
17/10/2018 | 00:47:48 | HH386F | Urban | Asset failure | LV | 80 | 203 | 0.025962 | 0.00012789 | No
17/10/2018 | 01:55:31 | HH386F | Urban | Asset failure | HV | 27.3333 | 159 | 0.0069478 | 4.37e-05 | No
17/10/2018 | 02:29:55 | HH386F | Urban | Overloads |  | 32.6667 | 153 | 0.0079902 | 5.222e-05 | No
17/10/2018 | 06:09:55 | AP125A | Urban | Asset failure | LV | 1 | 292 | 0.00046681 | 1.6e-06 | No
17/10/2018 | 08:50:22 | AP125C | Urban | Planned |  | 257 | 291 | 0.11956 | 0.00041086 | No
17/10/2018 | 09:16:20 | SA18 | Urban | Planned |  | 102 | 130 | 0.021198 | 0.00016306 | No
17/10/2018 | 09:30:00 | MI23 | Rural Long | Planned |  | 64 | 214 | 0.099958 | 0.00046709 | No
17/10/2018 | 09:32:20 | EL16 | Urban | Planned |  | 10 | 189 | 0.0030215 | 1.599e-05 | No
17/10/2018 | 09:35:42 | BT14 | Rural Long | Planned |  | 8 | 272 | 0.015881 | 5.839e-05 | No
17/10/2018 | 10:16:16 | R20 | Rural Long | Weather |  | 1 | 336 | 0.0024522 | 7.3e-06 | No
17/10/2018 | 10:29:00 | BM44 | Rural Short | Planned |  | 36 | 210 | 0.056323 | 0.00026821 | No
17/10/2018 | 10:43:20 | PL14 | Urban | Planned |  | 1 | 42 | 6.714e-05 | 1.6e-06 | No
17/10/2018 | 10:44:54 | NL511B | Urban | Asset failure | LV | 1 | 229 | 0.0003661 | 1.6e-06 | No
17/10/2018 | 10:48:57 | SG08 | Rural Short | Planned |  | 16 | 132 | 0.015735 | 0.0001192 | No
17/10/2018 | 11:13:05 | SM137B | Urban | Asset failure | LV | 1 | 184 | 0.00029416 | 1.6e-06 | No
17/10/2018 | 11:28:17 | SA36 | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 203 | 0.00064906 | 3.2e-06 | No
17/10/2018 | 11:29:37 | HH177C | Urban | Planned |  | 67 | 55 | 0.0058911 | 0.00010711 | No
17/10/2018 | 12:24:35 | HH386C | Urban | Asset failure | LV | 2.3333 | 456 | 0.001701 | 3.73e-06 | No
17/10/2018 | 12:34:49 | BT06 | Rural Long | Overloads |  | 3 | 235 | 0.0051453 | 2.19e-05 | No
17/10/2018 | 12:50:35 | G17 | Rural Long | Unknown | Unknown | 3 | 3 | 6.569e-05 | 2.19e-05 | No
17/10/2018 | 13:34:09 | MG17 | Rural Long | Asset failure | LV | 1 | 94 | 0.00068604 | 7.3e-06 | No
17/10/2018 | 13:34:13 | MI33 | Rural Long | Unknown | Unknown | 1 | 44 | 0.00032113 | 7.3e-06 | No
17/10/2018 | 13:56:06 | W28 | Rural Long | Planned |  | 4 | 15 | 0.0004379 | 2.919e-05 | No
17/10/2018 | 13:59:11 | MTB22 | Rural Short | Unknown | Unknown | 1 | 111 | 0.00082697 | 7.45e-06 | No
17/10/2018 | 14:15:21 | HH177B | Urban | Third Party | Vehicle impact | 47.3334 | 197 | 0.014907 | 7.567e-05 | No
17/10/2018 | 14:19:27 | SM179B | Urban | Asset failure | LV | 52 | 227 | 0.018871 | 8.313e-05 | No
17/10/2018 | 16:49:48 | SSD384 | Urban | Planned |  | 1 | 1443 | 0.0023069 | 1.6e-06 | No
17/10/2018 | 17:12:43 | HH386B | Urban | Asset failure | LV | 1 | 176 | 0.00028137 | 1.6e-06 | No
17/10/2018 | 18:10:30 | MI05 | Rural Long | Unknown | Unknown | 3 | 17 | 0.00037222 | 2.19e-05 | No
17/10/2018 | 18:33:34 | HH386D | Urban | Asset failure | LV | 1 | 245 | 0.00039168 | 1.6e-06 | No
17/10/2018 | 18:58:28 | AP139B | Urban | Other |  | 1 | 312 | 0.00049879 | 1.6e-06 | No
17/10/2018 | 19:04:34 | HH145A | Urban | Asset failure | LV | 1 | 228 | 0.0003645 | 1.6e-06 | No
17/10/2018 | 20:26:15 | GA53 | Rural Short | Asset failure | LV | 2 | 168 | 0.0025032 | 1.49e-05 | No
17/10/2018 | 21:04:09 | EL25 | Urban | Asset failure | LV | 18 | 92 | 0.0026474 | 2.878e-05 | No
17/10/2018 | 21:54:28 | HH121F | Urban | Overloads |  | 1 | 102 | 0.00016306 | 1.6e-06 | No
17/10/2018 | 23:53:06 | EL25 | Urban | Overloads |  | 54 | 51 | 0.0044028 | 8.633e-05 | No
18/10/2018 | 00:10:36 | SM137B | Urban | Planned |  | 11 | 369.0909 | 0.0064906 | 1.759e-05 | No
18/10/2018 | 08:34:17 | YK17 | Rural Long | Planned |  | 148 | 329 | 0.35537 | 0.0010801 | No
18/10/2018 | 08:37:21 | MTB13 | Rural Short | Planned |  | 34 | 146 | 0.036983 | 0.00025331 | No
18/10/2018 | 08:50:12 | MG04 | Rural Short | Planned |  | 1 | 150 | 0.0011175 | 7.45e-06 | No
18/10/2018 | 08:59:39 | SA744D | Urban | Planned |  | 24 | 318 | 0.012201 | 3.837e-05 | No
18/10/2018 | 09:00:53 | KI53 | Rural Long | Planned |  | 85 | 306 | 0.18983 | 0.00062036 | No
18/10/2018 | 09:04:44 | AP355H | Urban | Planned |  | 111 | 327 | 0.058027 | 0.00017745 | No
18/10/2018 | 09:05:00 | ST42 | Rural Long | Planned |  | 4 | 56 | 0.0016348 | 2.919e-05 | No
18/10/2018 | 09:22:49 | ST41 | Rural Long | Planned |  | 2 | 81 | 0.0011823 | 1.46e-05 | No
18/10/2018 | 09:23:02 | MV64 | Urban | Planned |  | 653 | 166.5161 | 0.17383 | 0.0010439 | No
18/10/2018 | 09:25:25 | MB63 | Rural Long | Planned |  | 1 | 248 | 0.00181 | 7.3e-06 | No
18/10/2018 | 09:29:06 | WK51 | Rural Short | Planned |  | 2 | 100 | 0.00149 | 1.49e-05 | No
18/10/2018 | 09:30:19 | SM179B | Urban | Planned |  | 90 | 285 | 0.041006 | 0.00014388 | No
18/10/2018 | 09:59:44 | GA37 | Rural Long | Planned |  | 22 | 323 | 0.051862 | 0.00016056 | No
18/10/2018 | 10:09:22 | VH15 | Rural Short | Planned |  | 27 | 238 | 0.047875 | 0.00020115 | No
18/10/2018 | 10:31:29 | PL27 | Rural Long | Planned |  | 6 | 768 | 0.033631 | 4.379e-05 | No
18/10/2018 | 10:35:30 | CV31 | Rural Long | Planned |  | 13 | 74 | 0.007021 | 9.488e-05 | No
18/10/2018 | 10:52:47 | CD17 | Rural Long | Planned |  | 75 | 187 | 0.10236 | 0.00054738 | No
18/10/2018 | 11:15:46 | CN33 | Rural Long | Planned |  | 1 | 30 | 0.00021895 | 7.3e-06 | No
18/10/2018 | 11:55:06 | NU10 | Rural Long | Planned |  | 1 | 41 | 0.00029923 | 7.3e-06 | No
18/10/2018 | 12:13:48 | CV31 | Rural Long | Planned |  | 2 | 52 | 0.00075903 | 1.46e-05 | No
18/10/2018 | 12:30:01 | G20 | Rural Long | Planned |  | 2 | 194 | 0.0028318 | 1.46e-05 | No
18/10/2018 | 13:30:37 | WK51 | Rural Short | Planned |  | 1 | 36 | 0.00026821 | 7.45e-06 | No
18/10/2018 | 13:45:42 | HH102B | Urban | Asset failure | LV | 1 | 326 | 0.00052117 | 1.6e-06 | No
18/10/2018 | 14:55:15 | GA36 | Rural Long | Asset failure | LV | 1 | 131 | 0.00095608 | 7.3e-06 | No
18/10/2018 | 15:50:21 | SD32400 | Rural Long | Unknown | Unknown | 2 | 200 | 0.0029193 | 1.46e-05 | No
18/10/2018 | 16:14:05 | HH177G | Urban | Asset failure | LV | 49 | 72 | 0.0056401 | 7.834e-05 | No
18/10/2018 | 16:42:57 | NA04 | Rural Long | Unknown | Unknown | 9.6667 | 144 | 0.010159 | 7.055e-05 | No
18/10/2018 | 18:23:35 | AP365A | Urban | Unknown | Unknown | 211 | 497 | 0.16765 | 0.00033732 | No
18/10/2018 | 19:51:34 | SB18 | Rural Long | Asset failure | LV | 1 | 212 | 0.0015473 | 7.3e-06 | No
19/10/2018 | 02:15:25 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 910 | 199.1505 | 0.28972 | 0.0014548 | No
19/10/2018 | 06:21:48 | HH121C | Urban | Overloads |  | 1 | 143 | 0.00022861 | 1.6e-06 | No
19/10/2018 | 06:59:52 | MG43 | Rural Short | Unknown | Unknown | 1508 | 55 | 0.61792 | 0.011235 | No
19/10/2018 | 08:02:41 | CM03 | Rural Long | Animal | Animal impact | 1 | 230 | 0.0016786 | 7.3e-06 | No
19/10/2018 | 08:24:31 | CL09 | Rural Long | Planned |  | 1 | 48 | 0.00035032 | 7.3e-06 | No
19/10/2018 | 08:47:29 | MTB12 | Rural Short | Planned |  | 1 | 258 | 0.0019221 | 7.45e-06 | No
19/10/2018 | 08:53:13 | ST12 | Rural Short | Planned |  | 19 | 231 | 0.032699 | 0.00014155 | No
19/10/2018 | 09:00:08 | MB93 | Rural Long | Planned |  | 27 | 233 | 0.045914 | 0.00019706 | No
19/10/2018 | 09:03:17 | M22 | Rural Long | Planned |  | 35 | 242 | 0.061817 | 0.00025544 | No
19/10/2018 | 09:08:12 | CV19 | Rural Long | Planned |  | 55 | 107 | 0.042951 | 0.00040141 | No
19/10/2018 | 09:10:00 | MV63 | Rural Short | Planned |  | 3 | 307 | 0.0068616 | 2.235e-05 | No
19/10/2018 | 09:12:55 | KA01 | Rural Short | Planned |  | 17 | 164 | 0.020771 | 0.00012665 | No
19/10/2018 | 09:30:28 | ME347A | Urban | Planned |  | 4 | 46 | 0.00029416 | 6.39e-06 | No
19/10/2018 | 09:33:59 | MV34 | Rural Short | Planned |  | 309 | 215 | 0.49495 | 0.0023021 | No
19/10/2018 | 09:34:25 | VH11 | Urban | Overloads |  | 1 | 120 | 0.00019184 | 1.6e-06 | No
19/10/2018 | 09:44:08 | SG09 | Rural Short | Planned |  | 184 | 245 | 0.33585 | 0.0013708 | No
19/10/2018 | 09:47:08 | VH23 | Rural Short | Planned |  | 157 | 318 | 0.37196 | 0.0011697 | No
19/10/2018 | 09:59:10 | MG41 | Urban | Planned |  | 55 | 120 | 0.010551 | 8.793e-05 | No
19/10/2018 | 10:28:58 | BT12 | Rural Long | Planned |  | 11 | 185 | 0.014852 | 8.028e-05 | No
19/10/2018 | 10:35:48 | HH130A | Urban | Asset failure | LV | 7 | 145 | 0.0016227 | 1.119e-05 | No
19/10/2018 | 10:38:33 | G10 | Rural Long | Planned |  | 12 | 111 | 0.0097214 | 8.758e-05 | No
19/10/2018 | 10:51:57 | ST12 | Rural Short | Asset failure | LV | 1 | 77 | 0.00057366 | 7.45e-06 | No
19/10/2018 | 11:06:28 | SG13 | Rural Short | Planned |  | 28 | 47 | 0.0098044 | 0.0002086 | No
19/10/2018 | 11:07:40 | G08 | Rural Long | Planned |  | 31 | 63 | 0.014254 | 0.00022625 | No
19/10/2018 | 11:14:32 | ME347A | Urban | Vegetation | Grow-in - NSP responsibility | 11.3333 | 162 | 0.0029352 | 1.812e-05 | No
19/10/2018 | 11:47:26 | CV753A | Rural Long | Weather |  | 23.3333 | 402 | 0.068458 | 0.00017029 | No
19/10/2018 | 11:53:22 | LX32 | Rural Short | Planned |  | 4 | 41 | 0.0012218 | 2.98e-05 | No
19/10/2018 | 12:29:19 | AP344E | Urban | Planned |  | 18 | 20 | 0.00057552 | 2.878e-05 | No
19/10/2018 | 12:29:45 | GA36 | Rural Long | Third Party | Vehicle impact | 95 | 366.5368 | 0.25414 | 0.00069334 | No
19/10/2018 | 13:09:26 | VH14 | Rural Short | Unknown | Unknown | 4 | 45 | 0.001341 | 2.98e-05 | No
19/10/2018 | 13:09:30 | CV30 | Rural Long | Weather |  | 80 | 120.125 | 0.070137 | 0.00058387 | No
19/10/2018 | 13:48:34 | NL234D | Urban | Asset failure | LV | 1 | 70 | 0.00011191 | 1.6e-06 | No
19/10/2018 | 14:06:16 | CL20 | Rural Long | Asset failure | LV | 5 | 172 | 0.0062766 | 3.649e-05 | No
19/10/2018 | 15:42:32 | SD37102 | Rural Long | Unknown | Unknown | 121 | 137.4215 | 0.12136 | 0.0008831 | No
19/10/2018 | 16:31:55 | GA800A | Rural Short | Unknown | Unknown | 1 | 272 | 0.0020264 | 7.45e-06 | No
19/10/2018 | 16:41:57 | GA25 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1412 | 100 | 1.052 | 0.01052 | No
19/10/2018 | 16:45:01 | HH102C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 223 | 57 | 0.020321 | 0.0003565 | No
19/10/2018 | 16:46:56 | GU43 | Rural Long | Unknown | Unknown | 20 | 125 | 0.018246 | 0.00014597 | No
19/10/2018 | 18:24:54 | GA25 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 70 | 0.00052151 | 7.45e-06 | No
19/10/2018 | 19:35:11 | EL10 | Urban | Asset failure | LV | 14.3333 | 268 | 0.006141 | 2.291e-05 | No
19/10/2018 | 19:58:55 | MG11 | Rural Short | Unknown | Unknown | 17 | 203 | 0.02571 | 0.00012665 | No
19/10/2018 | 20:00:58 | HH177G | Urban | Asset failure | LV | 10.6667 | 159 | 0.0027113 | 1.705e-05 | No
19/10/2018 | 20:52:53 | SD33200 | Rural Long | Unknown | Unknown | 1 | 1073 | 0.0078311 | 7.3e-06 | No
20/10/2018 | 06:19:13 | SA42 | Urban | Asset failure | LV | 20 | 676 | 0.021614 | 3.197e-05 | No
20/10/2018 | 08:21:28 | AP425C | Urban | Third Party | Vehicle impact | 1 | 150 | 0.0002398 | 1.6e-06 | No
20/10/2018 | 10:16:29 | EL01M | Urban | Asset failure | LV | 1 | 472 | 0.00075457 | 1.6e-06 | No
20/10/2018 | 10:26:30 | R22 | Rural Long | Unknown | Unknown | 8 | 72 | 0.0042038 | 5.839e-05 | No
20/10/2018 | 12:42:30 | AP149F | Urban | Weather |  | 28 | 151 | 0.0067592 | 4.476e-05 | No
20/10/2018 | 13:00:23 | SA42 | Urban | Asset failure | HV | 20 | 155 | 0.0049559 | 3.197e-05 | No
20/10/2018 | 15:13:06 | GA745A | Rural Short | Asset failure | LV | 1 | 229 | 0.0017061 | 7.45e-06 | No
20/10/2018 | 15:24:37 | MTB22 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.6667 | 22 | 0.00027317 | 1.242e-05 | No
20/10/2018 | 22:02:15 | PL803C | Urban | Asset failure | LV | 2 | 81 | 0.00025899 | 3.2e-06 | No
21/10/2018 | 00:51:27 | SA11 | Urban | Asset failure | HV | 387 | 145.0672 | 0.089751 | 0.00061869 | No
21/10/2018 | 05:38:05 | HH121G | Urban | Planned |  | 158 | 216 | 0.05456 | 0.00025259 | No
21/10/2018 | 05:50:42 | KA15 | Rural Long | Unknown | Unknown | 59 | 222 | 0.095594 | 0.0004306 | No
21/10/2018 | 07:57:42 | MB81 | Rural Long | Planned |  | 1 | 221 | 0.0016129 | 7.3e-06 | No
21/10/2018 | 08:49:20 | AP132D | Urban | Planned |  | 13 | 360 | 0.0074818 | 2.078e-05 | No
21/10/2018 | 09:42:23 | AP146A | Urban | Planned |  | 10 | 388 | 0.0062029 | 1.599e-05 | No
21/10/2018 | 11:17:32 | EL10 | Urban | Asset failure | LV | 1 | 201 | 0.00032133 | 1.6e-06 | No
21/10/2018 | 12:12:15 | AP227B | Urban | Asset failure | LV | 1 | 113 | 0.00018065 | 1.6e-06 | No
21/10/2018 | 12:12:18 | AP227D | Urban | Asset failure | LV | 1 | 115 | 0.00018385 | 1.6e-06 | No
21/10/2018 | 15:07:12 | SD34400 | Rural Long | Animal | Animal impact | 74 | 108 | 0.058328 | 0.00054008 | No
21/10/2018 | 19:00:52 | EL01L | Urban | Unknown | Unknown | 35.3333 | 71 | 0.0040105 | 5.649e-05 | No
21/10/2018 | 22:30:27 | NL234C | Urban | Other |  | 1 | 135 | 0.00021582 | 1.6e-06 | No
22/10/2018 | 00:04:43 | VH15 | Rural Short | Planned |  | 3 | 820 | 0.018327 | 2.235e-05 | No
22/10/2018 | 05:56:26 | GA50 | Urban | Unknown | Unknown | 1188 | 187.0051 | 0.35516 | 0.0018992 | No
22/10/2018 | 07:56:42 | EL08G | Urban | Asset failure | LV | 2 | 545 | 0.0017426 | 3.2e-06 | No
22/10/2018 | 08:56:58 | SM349C | Urban | Planned |  | 94 | 263 | 0.039522 | 0.00015028 | No
22/10/2018 | 09:00:58 | ST41 | Rural Long | Planned |  | 84 | 161 | 0.098703 | 0.00061306 | No
22/10/2018 | 09:10:17 | SD38100 | Rural Long | Planned |  | 10 | 885 | 0.06459 | 7.298e-05 | No
22/10/2018 | 09:19:00 | MTB12 | Rural Short | Planned |  | 23 | 87 | 0.014908 | 0.00017135 | No
22/10/2018 | 09:20:18 | SG11 | Rural Short | Planned |  | 106 | 536 | 0.42329 | 0.00078972 | No
22/10/2018 | 09:33:28 | M23 | Rural Long | Planned |  | 124 | 308 | 0.27874 | 0.00090499 | No
22/10/2018 | 09:38:08 | ST42 | Rural Long | Planned |  | 2 | 59 | 0.0008612 | 1.46e-05 | No
22/10/2018 | 09:39:02 | HH121B | Urban | Planned |  | 101 | 249 | 0.040205 | 0.00016147 | No
22/10/2018 | 09:44:10 | M74 | Rural Long | Planned |  | 25 | 80 | 0.014597 | 0.00018246 | No
22/10/2018 | 09:46:56 | HH428C | Urban | Overloads |  | 1 | 302 | 0.0004828 | 1.6e-06 | No
22/10/2018 | 09:57:06 | AP125D | Urban | Planned |  | 259 | 290 | 0.12008 | 0.00041406 | No
22/10/2018 | 10:03:05 | NA21 | Rural Long | Asset failure | HV | 2 | 293 | 0.0042768 | 1.46e-05 | No
22/10/2018 | 10:09:31 | GA53 | Rural Short | Planned |  | 23 | 53 | 0.0090817 | 0.00017135 | No
22/10/2018 | 10:30:00 | SG05 | Rural Short | Planned |  | 45 | 124 | 0.041572 | 0.00033526 | No
22/10/2018 | 10:30:47 | NU14 | Rural Long | Planned |  | 1 | 139 | 0.0010145 | 7.3e-06 | No
22/10/2018 | 11:00:56 | CN01 | Rural Long | Planned |  | 62 | 222 | 0.10045 | 0.0004525 | No
22/10/2018 | 11:09:42 | AP425C | Urban | Asset failure | LV | 59 | 77 | 0.0072628 | 9.432e-05 | No
22/10/2018 | 11:55:58 | KA30 | Rural Short | Planned |  | 1 | 29 | 0.00021605 | 7.45e-06 | No
22/10/2018 | 12:05:17 | GA53 | Rural Short | Planned |  | 13 | 45 | 0.0043583 | 9.685e-05 | No
22/10/2018 | 16:02:23 | ME347A | Urban | Asset failure | LV | 30.6666 | 182 | 0.0089227 | 4.903e-05 | No
22/10/2018 | 16:06:08 | GA53 | Rural Short | Animal | Animal impact | 2 | 193 | 0.0028758 | 1.49e-05 | No
22/10/2018 | 16:14:09 | VH45 | Rural Short | Unknown | Unknown | 29 | 33 | 0.0071298 | 0.00021605 | No
22/10/2018 | 16:44:58 | ME116B | Urban | Asset failure | LV | 94 | 81 | 0.012172 | 0.00015028 | No
22/10/2018 | 17:07:09 | CL13 | Rural Long | Third Party | Vehicle impact | 56 | 91 | 0.037192 | 0.00040871 | No
22/10/2018 | 17:44:58 | HH102D | Urban | Asset failure | LV | 15 | 61 | 0.0014628 | 2.398e-05 | No
22/10/2018 | 18:42:37 | PP15 | Rural Long | Weather |  | 2 | 81 | 0.0011823 | 1.46e-05 | No
22/10/2018 | 22:06:34 | AP149C | Urban | Asset failure | LV | 49 | 51 | 0.0039951 | 7.834e-05 | No
22/10/2018 | 22:22:03 | AP125C | Urban | Asset failure | LV | 1 | 126 | 0.00020143 | 1.6e-06 | No
23/10/2018 | 01:32:21 | AP365A | Urban | Asset failure | Distribution substation | 138 | 158.7971 | 0.035033 | 0.00022062 | No
23/10/2018 | 08:00:40 | ST41 | Rural Long | Planned |  | 38 | 255 | 0.070721 | 0.00027734 | No
23/10/2018 | 08:22:03 | MV14 | Rural Short | Planned |  | 43 | 318 | 0.10187 | 0.00032036 | No
23/10/2018 | 08:35:06 | YK11 | Rural Long | Planned |  | 81 | 312 | 0.18444 | 0.00059117 | No
23/10/2018 | 08:36:00 | SA14 | Urban | Planned |  | 75 | 406 | 0.04868 | 0.0001199 | No
23/10/2018 | 08:44:03 | ST12 | Rural Short | Planned |  | 3 | 202 | 0.0045148 | 2.235e-05 | No
23/10/2018 | 09:09:19 | MV12 | Urban | Planned |  | 18 | 218 | 0.0062732 | 2.878e-05 | No
23/10/2018 | 09:11:51 | MI03 | Rural Long | Planned |  | 1 | 43 | 0.00031383 | 7.3e-06 | No
23/10/2018 | 09:26:34 | VH17 | Rural Short | Planned |  | 12 | 273 | 0.024407 | 8.94e-05 | No
23/10/2018 | 09:42:22 | SG07 | Rural Short | Planned |  | 13 | 272 | 0.026344 | 9.685e-05 | No
23/10/2018 | 09:46:44 | BT26 | Rural Long | Unknown | Unknown | 2 | 132 | 0.0019268 | 1.46e-05 | No
23/10/2018 | 09:46:49 | PP04 | Rural Short | Planned |  | 2 | 135 | 0.0020115 | 1.49e-05 | No
23/10/2018 | 10:13:38 | HH121C | Urban | Planned |  | 134 | 202 | 0.043273 | 0.00021422 | No
23/10/2018 | 10:28:57 | SM411E | Urban | Animal | Animal impact | 1487 | 212.5582 | 0.5053 | 0.0023772 | No
23/10/2018 | 10:28:58 | AP125C | Urban | Planned |  | 122 | 253 | 0.049345 | 0.00019504 | No
23/10/2018 | 10:39:44 | HH522B / HH121D | Urban | Planned |  | 150 | 201.8933 | 0.048414 | 0.0002398 | No
23/10/2018 | 10:48:10 | GU41 | Rural Long | Planned |  | 9 | 189 | 0.012414 | 6.569e-05 | No
23/10/2018 | 11:50:05 | EL03 | Urban | Asset failure | LV | 79 | 46 | 0.0058096 | 0.0001263 | No
23/10/2018 | 12:09:41 | AP149C | Urban | Asset failure | LV | 49 | 58 | 0.0045434 | 7.834e-05 | No
23/10/2018 | 12:23:39 | KI43 | Rural Long | Unknown | Unknown | 1 | 24 | 0.00017516 | 7.3e-06 | No
23/10/2018 | 12:38:09 | NL544B | Urban | Asset failure | HV | 1711 | 71.3103 | 0.19506 | 0.0027353 | No
23/10/2018 | 12:38:12 | HH177E | Urban | Planned |  | 38 | 64 | 0.003888 | 6.075e-05 | No
23/10/2018 | 14:18:47 | SA744D | Urban | Asset failure | LV | 36 | 46 | 0.0026474 | 5.755e-05 | No
23/10/2018 | 17:00:23 | SA33 | Urban | Asset failure | LV | 70 | 138 | 0.015443 | 0.00011191 | No
23/10/2018 | 17:00:58 | SA33 | Urban | Asset failure | LV | 50 | 137 | 0.010951 | 7.993e-05 | No
23/10/2018 | 23:23:14 | SA520D | Urban | Asset failure | LV | 1 | 71 | 0.00011351 | 1.6e-06 | No
24/10/2018 | 01:05:07 | AP146C | Urban | Planned |  | 164 | 187 | 0.049028 | 0.00026218 | No
24/10/2018 | 02:52:57 | MV31 | Rural Short | Asset failure | LV | 5.3333 | 251 | 0.0099733 | 3.973e-05 | No
24/10/2018 | 07:21:34 | HH121B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 29 | 176 | 0.0081596 | 4.636e-05 | No
24/10/2018 | 08:41:45 | YK17 | Rural Long | Planned |  | 68 | 142 | 0.070473 | 0.00049629 | No
24/10/2018 | 08:55:32 | MB34 | Rural Long | Planned |  | 22 | 122 | 0.019589 | 0.00016056 | No
24/10/2018 | 08:56:02 | SA17 | Urban | Planned |  | 8 | 211 | 0.0026986 | 1.279e-05 | No
24/10/2018 | 09:01:14 | WHY02 | Urban | Planned |  | 30 | 153 | 0.0073379 | 4.796e-05 | No
24/10/2018 | 09:03:56 | SD38200 | Rural Long | Planned |  | 1 | 119 | 0.0008685 | 7.3e-06 | No
24/10/2018 | 09:04:16 | GA18 | Rural Long | Planned |  | 51 | 99 | 0.036849 | 0.00037222 | No
24/10/2018 | 09:09:00 | SA18 | Urban | Planned |  | 161 | 164 | 0.042211 | 0.00025739 | No
24/10/2018 | 09:15:07 | SA14 | Urban | Planned |  | 8 | 310 | 0.0039647 | 1.279e-05 | No
24/10/2018 | 09:19:55 | W28 | Rural Long | Planned |  | 82 | 278 | 0.16637 | 0.00059846 | No
24/10/2018 | 09:25:12 | CN11 | Rural Long | Planned |  | 17 | 275 | 0.03412 | 0.00012407 | No
24/10/2018 | 09:43:42 | HH409D | Urban | Planned |  | 25 | 260 | 0.010391 | 3.997e-05 | No
24/10/2018 | 09:47:44 | MTB32 | Rural Long | Planned |  | 29 | 279 | 0.059051 | 0.00021165 | No
24/10/2018 | 09:52:45 | MB42 | Rural Long | Planned |  | 12 | 33 | 0.0028901 | 8.758e-05 | No
24/10/2018 | 10:20:44 | ST44 | Rural Long | Planned |  | 41 | 45 | 0.013465 | 0.00029923 | No
24/10/2018 | 10:48:01 | CV01 | Rural Short | Planned |  | 38 | 184 | 0.052091 | 0.00028311 | No
24/10/2018 | 10:51:06 | BT18 | Rural Long | Unknown | Unknown | 2 | 43 | 0.00062766 | 1.46e-05 | No
24/10/2018 | 11:17:44 | SA16 | Urban | Planned |  | 2 | 63 | 0.00020143 | 3.2e-06 | No
24/10/2018 | 11:20:03 | GA43 | Rural Short | Planned |  | 145 | 92 | 0.099385 | 0.0010803 | No
24/10/2018 | 11:48:54 | CN53 | Rural Long | Planned |  | 7 | 235 | 0.012006 | 5.109e-05 | No
24/10/2018 | 12:03:37 | SD38200 | Rural Long | Planned |  | 17 | 98 | 0.012159 | 0.00012407 | No
24/10/2018 | 12:14:41 | SA16 | Urban | Planned |  | 2 | 12 | 3.837e-05 | 3.2e-06 | No
24/10/2018 | 12:19:25 | CN75 | Rural Long | Planned |  | 2 | 17 | 0.00024814 | 1.46e-05 | No
24/10/2018 | 12:38:42 | NU07 | Rural Long | Planned |  | 11 | 94 | 0.0075465 | 8.028e-05 | No
24/10/2018 | 13:39:53 | AP226D | Urban | Asset failure | LV | 102 | 89 | 0.014513 | 0.00016306 | No
24/10/2018 | 15:21:18 | CD03 | Rural Short | Asset failure | HV | 534.3335 | 15 | 0.059713 | 0.0039809 | No
24/10/2018 | 16:34:58 | MB42 | Rural Long | Planned |  | 7 | 11 | 0.00056197 | 5.109e-05 | No
24/10/2018 | 17:13:02 | HH107A | Urban | Asset failure | LV | 106 | 67 | 0.011354 | 0.00016946 | No
24/10/2018 | 17:47:23 | HH130A | Urban | Overloads |  | 1 | 200 | 0.00031974 | 1.6e-06 | No
24/10/2018 | 18:39:32 | SG07 | Rural Short | Asset failure | LV | 18.3333 | 143 | 0.019532 | 0.00013659 | No
24/10/2018 | 18:40:33 | NL760C | Urban | Asset failure | LV | 51 | 88 | 0.0071748 | 8.153e-05 | No
24/10/2018 | 19:00:58 | BM12 | Rural Short | Animal | Animal impact | 50 | 93 | 0.034643 | 0.00037251 | No
24/10/2018 | 19:36:31 | M13 | Rural Long | Unknown | Unknown | 963 | 82 | 0.57632 | 0.0070283 | No
24/10/2018 | 22:59:49 | SM410B | Urban | Planned |  | 48 | 337 | 0.02586 | 7.674e-05 | No
24/10/2018 | 23:53:18 | SM374A | Urban | Animal | Animal impact | 93 | 117 | 0.017395 | 0.00014868 | No
25/10/2018 | 01:47:31 | VH23 | Rural Short | Planned |  | 335 | 207 | 0.51663 | 0.0024958 | No
25/10/2018 | 06:46:59 | GA800A | Rural Short | Animal | Animal impact | 219 | 114.6438 | 0.18705 | 0.0016316 | No
25/10/2018 | 07:08:59 | MI01 | Rural Long | Other |  | 1 | 258 | 0.001883 | 7.3e-06 | No
25/10/2018 | 07:14:51 | GU43 | Rural Long | Unknown | Unknown | 9 | 395 | 0.025946 | 6.569e-05 | No
25/10/2018 | 08:28:49 | CN03 | Rural Long | Planned |  | 51 | 222 | 0.082632 | 0.00037222 | No
25/10/2018 | 08:30:53 | MV15 | Rural Short | Planned |  | 3 | 89 | 0.0019892 | 2.235e-05 | No
25/10/2018 | 08:32:09 | NL234A | Urban | Planned |  | 114 | 332 | 0.060507 | 0.00018225 | No
25/10/2018 | 08:55:48 | CN42 | Rural Long | Planned |  | 105 | 215 | 0.16476 | 0.00076633 | No
25/10/2018 | 08:59:50 | GU21 | Rural Long | Planned |  | 27 | 159 | 0.031332 | 0.00019706 | No
25/10/2018 | 09:00:54 | MV14 | Rural Short | Planned |  | 33 | 344 | 0.084574 | 0.00024585 | No
25/10/2018 | 09:10:45 | MB72 | Rural Long | Planned |  | 21 | 171 | 0.026208 | 0.00015327 | No
25/10/2018 | 09:14:36 | MB14 | Rural Short | Planned |  | 1 | 150 | 0.0011175 | 7.45e-06 | No
25/10/2018 | 09:15:48 | GU14 | Rural Long | Planned |  | 12 | 225 | 0.019706 | 8.758e-05 | No
25/10/2018 | 09:20:19 | AP125D | Urban | Planned |  | 1 | 28 | 4.476e-05 | 1.6e-06 | No
25/10/2018 | 09:23:16 | R03 | Rural Long | Planned |  | 3 | 141 | 0.0030872 | 2.19e-05 | No
25/10/2018 | 09:24:08 | LX54 | Rural Short | Planned |  | 19 | 86 | 0.012174 | 0.00014155 | No
25/10/2018 | 09:26:59 | HH107B | Urban | Planned |  | 95 | 237 | 0.035994 | 0.00015187 | No
25/10/2018 | 09:27:06 | MV63 | Rural Short | Planned |  | 227 | 214.8899 | 0.36342 | 0.0016912 | No
25/10/2018 | 09:34:35 | BT26 | Rural Long | Planned |  | 9 | 156 | 0.010247 | 6.569e-05 | No
25/10/2018 | 09:37:31 | ST22 | Rural Short | Asset failure | HV | 2 | 99 | 0.0014751 | 1.49e-05 | No
25/10/2018 | 09:40:32 | SM172F | Urban | Planned |  | 60 | 25 | 0.002398 | 9.592e-05 | No
25/10/2018 | 09:41:04 | HH177G | Urban | Overloads |  | 1 | 191 | 0.00030535 | 1.6e-06 | No
25/10/2018 | 10:08:04 | GA27 | Rural Long | Planned |  | 24 | 256 | 0.044841 | 0.00017516 | No
25/10/2018 | 10:09:27 | SG13 | Rural Short | Planned |  | 148 | 289 | 0.31866 | 0.0011026 | No
25/10/2018 | 11:11:50 | MB01 | Rural Long | Planned |  | 1 | 15 | 0.00010948 | 7.3e-06 | No
25/10/2018 | 11:12:57 | HH177F | Urban | Planned |  | 55 | 203 | 0.017849 | 8.793e-05 | No
25/10/2018 | 13:48:06 | MB123 | Rural Long | Planned |  | 7 | 80 | 0.0040871 | 5.109e-05 | No
25/10/2018 | 17:15:52 | AP372F | Urban | Unknown | Unknown | 1 | 22 | 3.517e-05 | 1.6e-06 | No
25/10/2018 | 19:51:00 | HH386G | Urban | Unknown | Unknown | 60 | 94 | 0.0090165 | 9.592e-05 | No
25/10/2018 | 23:41:00 | SM172C | Urban | Asset failure | LV | 151 | 84 | 0.020278 | 0.0002414 | No
26/10/2018 | 00:33:29 | EL17 | Urban | Unknown | Unknown | 988 | 167.1093 | 0.26395 | 0.0015795 | No
26/10/2018 | 03:33:51 | NL115A | Urban | Asset failure | LV | 1 | 445 | 0.00071141 | 1.6e-06 | No
26/10/2018 | 04:31:55 | ST15 | Rural Short | Asset failure | HV | 41 | 348 | 0.1063 | 0.00030546 | No
26/10/2018 | 05:49:37 | CN71 | Rural Long | Planned |  | 228 | 60 | 0.099841 | 0.001664 | No
26/10/2018 | 08:01:17 | ST11 | Rural Short | Unknown | Unknown | 4 | 180 | 0.0053641 | 2.98e-05 | No
26/10/2018 | 08:04:00 | VH21 | Rural Short | Planned |  | 40 | 236 | 0.070329 | 0.00029801 | No
26/10/2018 | 08:16:27 | WHY10 | Urban | Asset failure | LV | 1 | 448 | 0.00071621 | 1.6e-06 | No
26/10/2018 | 08:28:15 | GU41 | Rural Long | Planned |  | 58 | 397 | 0.16805 | 0.0004233 | No
26/10/2018 | 08:58:11 | M04 | Rural Long | Planned |  | 109 | 186 | 0.14797 | 0.00079552 | No
26/10/2018 | 08:59:38 | MV53 | Rural Short | Planned |  | 11 | 154 | 0.012621 | 8.195e-05 | No
26/10/2018 | 09:12:07 | W17 | Rural Long | Planned |  | 7 | 184 | 0.0094003 | 5.109e-05 | No
26/10/2018 | 09:16:55 | MV53 | Rural Short | Planned |  | 17 | 118 | 0.014945 | 0.00012665 | No
26/10/2018 | 09:30:13 | MB02 | Rural Long | Planned |  | 14 | 108 | 0.011035 | 0.00010218 | No
26/10/2018 | 09:31:45 | SG04 | Rural Short | Planned |  | 81 | 298 | 0.17983 | 0.00060346 | No
26/10/2018 | 09:33:46 | MTB54 | Rural Long | Planned |  | 10 | 150 | 0.010948 | 7.298e-05 | No
26/10/2018 | 09:36:51 | SM410A | Urban | Planned |  | 53 | 327 | 0.027707 | 8.473e-05 | No
26/10/2018 | 09:55:00 | CN32 | Rural Long | Planned |  | 3 | 198 | 0.0043352 | 2.19e-05 | No
26/10/2018 | 09:55:05 | GA35 | Rural Long | Planned |  | 18 | 53 | 0.0069626 | 0.00013137 | No
26/10/2018 | 09:58:00 | MI06 | Rural Long | Planned |  | 40 | 183 | 0.053424 | 0.00029193 | No
26/10/2018 | 09:58:12 | HH102B | Urban | Planned |  | 279 | 271 | 0.12087 | 0.00044603 | No
26/10/2018 | 10:08:36 | PL07 | Urban | Planned |  | 90 | 271 | 0.038992 | 0.00014388 | No
26/10/2018 | 10:10:58 | WK51 | Rural Short | Unknown | Unknown | 1 | 249 | 0.0018551 | 7.45e-06 | No
26/10/2018 | 10:15:14 | CD23 | Rural Long | Planned |  | 3 | 54.6667 | 0.0011969 | 2.19e-05 | No
26/10/2018 | 10:15:14 | PP12 | Rural Long | Planned |  | 21 | 168 | 0.025749 | 0.00015327 | No
26/10/2018 | 10:21:00 | MG21 | Rural Long | Planned |  | 3 | 7179 | 0.15718 | 2.19e-05 | No
26/10/2018 | 10:41:06 | KI53 | Rural Long | Planned |  | 1 | 85 | 0.00062036 | 7.3e-06 | No
26/10/2018 | 10:42:00 | GA13 | Rural Long | Planned |  | 67 | 455 | 0.22249 | 0.00048899 | No
26/10/2018 | 11:11:01 | EL17 | Urban | Animal | Animal impact | 1 | 14 | 2.238e-05 | 1.6e-06 | No
26/10/2018 | 11:47:06 | MT07 | Rural Long | Unknown | Unknown | 1 | 220 | 0.0016056 | 7.3e-06 | No
26/10/2018 | 12:14:01 | M43 | Rural Long | Planned |  | 1 | 15 | 0.00010948 | 7.3e-06 | No
26/10/2018 | 13:43:44 | MB01 | Rural Long | Planned |  | 20 | 44 | 0.0064225 | 0.00014597 | No
26/10/2018 | 14:01:00 | MT05 | Rural Long | Asset failure | HV | 7 | 22 | 0.0011239 | 5.109e-05 | No
26/10/2018 | 15:08:00 | SG12 | Rural Short | Planned |  | 18 | 4 | 0.00053641 | 0.0001341 | No
26/10/2018 | 17:44:23 | HH121E | Urban | Overloads |  | 1 | 115 | 0.00018385 | 1.6e-06 | No
26/10/2018 | 19:39:06 | SM411A | Urban | Vegetation | Grow-in - NSP responsibility | 32 | 107 | 0.0054739 | 5.116e-05 | No
26/10/2018 | 20:09:25 | SM411B | Urban | Vegetation | Grow-in - NSP responsibility | 16.6667 | 78 | 0.0020783 | 2.664e-05 | No
27/10/2018 | 00:15:24 | SM216D | Urban | Asset failure | LV | 121 | 71 | 0.013734 | 0.00019344 | No
27/10/2018 | 08:42:50 | BT18 | Rural Long | Asset failure | LV | 1 | 406 | 0.0029631 | 7.3e-06 | No
27/10/2018 | 09:12:54 | HH121B | Urban | Asset failure | HV | 2604 | 1.8756 | 0.0078079 | 0.004163 | No
27/10/2018 | 09:39:31 | HH145B | Urban | Third Party | Vehicle impact | 1 | 432 | 0.00069063 | 1.6e-06 | No
27/10/2018 | 09:52:28 | SM126C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 179 | 204 | 0.058377 | 0.00028616 | No
27/10/2018 | 11:08:56 | VH21 | Rural Short | Asset failure | LV | 1 | 91 | 0.00067796 | 7.45e-06 | No
27/10/2018 | 12:08:20 | SM126E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 32.6667 | 67 | 0.003499 | 5.222e-05 | No
27/10/2018 | 12:29:35 | AP529D | Urban | Asset failure | LV | 1 | 160 | 0.00025579 | 1.6e-06 | No
27/10/2018 | 13:28:33 | SM126E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 52 | 8.313e-05 | 1.6e-06 | No
27/10/2018 | 14:11:37 | WK72 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 235 | 0.0017508 | 7.45e-06 | No
27/10/2018 | 16:38:23 | AP227B | Urban | Asset failure | LV | 80 | 174 | 0.022254 | 0.00012789 | No
27/10/2018 | 17:15:41 | HH130F | Urban | Asset failure | LV | 72 | 99 | 0.011395 | 0.0001151 | No
27/10/2018 | 18:06:35 | CN73 | Rural Long | Asset failure | HV | 103 | 399.0583 | 0.29998 | 0.00075173 | No
27/10/2018 | 22:45:22 | BM15 | Rural Short | Asset failure | HV | 203 | 238.202 | 0.36025 | 0.0015124 | No
27/10/2018 | 23:32:59 | AP529A | Urban | Asset failure | LV | 1 | 683 | 0.0010919 | 1.6e-06 | No
28/10/2018 | 07:06:46 | CBD353E | CBD | Planned |  | 4 | 143 | 0.11104 | 0.00077647 | No
28/10/2018 | 07:06:46 | CBD353E | Urban | Planned |  | 14 | 143 | 0.0032005 | 2.238e-05 | No
28/10/2018 | 08:00:19 | AP365D2 | Urban | Planned |  | 3 | 291 | 0.0013956 | 4.8e-06 | No
28/10/2018 | 08:35:55 | HH432D | Urban | Planned |  | 10 | 353 | 0.0056433 | 1.599e-05 | No
28/10/2018 | 09:07:43 | WK23 | Rural Short | Planned |  | 20 | 52 | 0.0077482 | 0.000149 | No
28/10/2018 | 09:20:36 | AP344D | Urban | Planned |  | 47 | 274 | 0.020588 | 7.514e-05 | No
28/10/2018 | 09:31:54 | MTB54 | Rural Long | Planned |  | 63 | 351 | 0.16139 | 0.0004598 | No
28/10/2018 | 09:36:50 | SA13 / SA14 | Urban | Planned |  | 89 | 369.8652 | 0.052625 | 0.00014228 | No
28/10/2018 | 10:33:16 | CBD366N | CBD | Planned |  | 14 | 386 | 1.049 | 0.0027177 | No
28/10/2018 | 11:01:05 | WK31 | Rural Short | Planned |  | 1 | 17 | 0.00012665 | 7.45e-06 | No
28/10/2018 | 12:07:42 | MI02 | Rural Short | Unknown | Unknown | 8 | 112 | 0.0066753 | 5.96e-05 | No
28/10/2018 | 14:29:55 | SM411C | Urban | Overloads |  | 1 | 142 | 0.00022701 | 1.6e-06 | No
28/10/2018 | 15:08:51 | BU11 | Rural Short | Animal | Animal impact | 1 | 466 | 0.0034718 | 7.45e-06 | No
28/10/2018 | 18:02:44 | AP424F | Urban | Asset failure | LV | 1 | 224 | 0.0003581 | 1.6e-06 | No
28/10/2018 | 19:59:57 | MTB41 | Rural Short | Unknown | Unknown | 43 | 165 | 0.052859 | 0.00032036 | No
28/10/2018 | 20:27:41 | BU11 | Rural Short | Unknown | Unknown | 1 | 30 | 0.0002235 | 7.45e-06 | No
28/10/2018 | 22:27:50 | SM410D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 223 | 0.0003565 | 1.6e-06 | No
28/10/2018 | 22:42:17 | SD54102 | Rural Long | Unknown | Unknown | 1009 | 72.8196 | 0.53625 | 0.007364 | No
29/10/2018 | 04:16:21 | CBD367G | CBD | Planned |  | 2 | 1 | 0.00038824 | 0.00038824 | No
29/10/2018 | 04:18:00 | CM16 | Rural Long | Unknown | Unknown | 38 | 326.0526 | 0.090426 | 0.00027734 | No
29/10/2018 | 04:49:03 | SD58200 | Rural Long | Asset failure | Subtransmission | 512 | 133.0938 | 0.49734 | 0.0037368 | No
29/10/2018 | 08:31:45 | KI31 | Rural Short | Overloads |  | 1 | 630 | 0.0046936 | 7.45e-06 | No
29/10/2018 | 08:45:23 | KI56 | Rural Long | Planned |  | 72 | 289 | 0.15186 | 0.00052548 | No
29/10/2018 | 08:45:57 | GA800A | Rural Short | Planned |  | 210 | 129 | 0.20182 | 0.0015645 | No
29/10/2018 | 08:53:56 | SM349H | Urban | Planned |  | 230 | 253 | 0.093027 | 0.0003677 | No
29/10/2018 | 09:05:29 | VH21 | Rural Short | Third Party | Vehicle impact | 1 | 133 | 0.00099087 | 7.45e-06 | No
29/10/2018 | 09:37:02 | ST41 | Rural Long | Planned |  | 137 | 237.562 | 0.23753 | 0.00099987 | No
29/10/2018 | 09:55:11 | MV62 | Rural Short | Planned |  | 7 | 81 | 0.0042242 | 5.215e-05 | No
29/10/2018 | 10:24:21 | GA41 | Rural Long | Planned |  | 1 | 38 | 0.00027734 | 7.3e-06 | No
29/10/2018 | 10:27:57 | G10 | Rural Long | Planned |  | 52 | 97 | 0.036813 | 0.00037951 | No
29/10/2018 | 10:35:55 | MV12 | Urban | Planned |  | 14 | 182 | 0.0040734 | 2.238e-05 | No
29/10/2018 | 10:47:34 | M72 | Rural Long | Planned |  | 12 | 119 | 0.010422 | 8.758e-05 | No
29/10/2018 | 10:55:00 | GA800A | Rural Short | Network business | Switching and protection error | 219 | 38.8904 | 0.063453 | 0.0016316 | No
29/10/2018 | 11:04:24 | WK31 | Rural Short | Planned |  | 28 | 183 | 0.038175 | 0.0002086 | No
29/10/2018 | 12:32:00 | WK11 | Rural Short | Unknown | Unknown | 14 | 113 | 0.011786 | 0.0001043 | No
29/10/2018 | 12:54:40 | GA36 | Rural Long | Planned |  | 95 | 60 | 0.041601 | 0.00069334 | No
29/10/2018 | 14:20:56 | BT03 | Rural Long | Asset failure | LV | 1 | 161 | 0.001175 | 7.3e-06 | No
29/10/2018 | 16:03:05 | SA33 | Urban | Asset failure | LV | 1 | 383 | 0.00061229 | 1.6e-06 | No
29/10/2018 | 17:59:54 | EL260C | Urban | Asset failure | LV | 50 | 37 | 0.0029576 | 7.993e-05 | No
29/10/2018 | 18:15:51 | GA27 | Rural Long | Unknown | Unknown | 26 | 11 | 0.0020873 | 0.00018976 | No
29/10/2018 | 18:44:58 | EL260C | Urban | Other |  | 16.6667 | 70 | 0.0018651 | 2.664e-05 | No
29/10/2018 | 19:59:36 | NL234A | Urban | Asset failure | LV | 1 | 198 | 0.00031654 | 1.6e-06 | No
29/10/2018 | 22:30:09 | HH341G | Urban | Planned |  | 113 | 382 | 0.069008 | 0.00018065 | No
29/10/2018 | 23:11:23 | CBD103E | Urban | Planned |  | 77 | 324 | 0.039884 | 0.0001231 | No
30/10/2018 | 08:15:23 | G15 | Rural Long | Planned |  | 34 | 345 | 0.08561 | 0.00024814 | No
30/10/2018 | 08:50:44 | W06 | Rural Long | Planned |  | 150 | 310 | 0.33937 | 0.0010948 | No
30/10/2018 | 08:50:52 | SM410D | Urban | Planned |  | 49 | 331 | 0.025929 | 7.834e-05 | No
30/10/2018 | 08:52:40 | YK17 | Rural Long | Planned |  | 148 | 457 | 0.49363 | 0.0010801 | No
30/10/2018 | 08:57:58 | BT03 | Rural Long | Unknown | Unknown | 168 | 30.6667 | 0.037601 | 0.0012261 | No
30/10/2018 | 09:07:08 | HH428A | Urban | Unknown | Unknown | 82 | 30 | 0.0039327 | 0.00013109 | No
30/10/2018 | 09:18:50 | NU34 | Rural Long | Planned |  | 3 | 311 | 0.0068093 | 2.19e-05 | No
30/10/2018 | 09:19:27 | MB14 | Rural Short | Planned |  | 106 | 314 | 0.24797 | 0.00078972 | No
30/10/2018 | 09:26:23 | HH177E | Urban | Asset failure | LV | 12.6667 | 199 | 0.0040297 | 2.025e-05 | No
30/10/2018 | 09:26:58 | ST41 | Rural Long | Planned |  | 101 | 250 | 0.18428 | 0.00073713 | No
30/10/2018 | 09:40:02 | M01 | Rural Long | Planned |  | 89 | 48 | 0.031179 | 0.00064955 | No
30/10/2018 | 09:54:38 | MV54 | Rural Short | Planned |  | 122 | 228 | 0.20723 | 0.00090892 | No
30/10/2018 | 09:58:00 | M81 | Rural Long | Planned |  | 2 | 65 | 0.00094878 | 1.46e-05 | No
30/10/2018 | 10:01:52 | CN73 | Rural Long | Planned |  | 27 | 77 | 0.015173 | 0.00019706 | No
30/10/2018 | 10:30:05 | SM402D | Urban | Asset failure | LV | 1 | 224 | 0.0003581 | 1.6e-06 | No
30/10/2018 | 10:38:00 | AP424B | Urban | Unknown | Unknown | 177 | 135 | 0.0382 | 0.00028297 | No
30/10/2018 | 10:40:54 | HH145D | Urban | Third Party | Dig-in | 53 | 118 | 0.0099981 | 8.473e-05 | No
30/10/2018 | 10:58:32 | HH522B | Urban | Planned |  | 274 | 288 | 0.12615 | 0.00043804 | No
30/10/2018 | 12:35:40 | CN33 | Rural Long | Planned |  | 2 | 108 | 0.0015764 | 1.46e-05 | No
30/10/2018 | 12:39:29 | MG17 | Rural Long | Asset failure | LV | 1 | 90 | 0.00065685 | 7.3e-06 | No
30/10/2018 | 13:14:34 | AP425A | Urban | Asset failure | LV | 15.6667 | 51 | 0.0012773 | 2.505e-05 | No
30/10/2018 | 13:35:02 | BT07 | Rural Long | Planned |  | 1 | 22 | 0.00016056 | 7.3e-06 | No
30/10/2018 | 13:49:37 | NU02 | Rural Long | Unknown | Unknown | 251 | 54 | 0.098922 | 0.0018319 | No
30/10/2018 | 15:00:43 | MG24 | Rural Short | Unknown | Unknown | 2 | 90 | 0.001341 | 1.49e-05 | No
30/10/2018 | 16:20:40 | NU15 | Rural Long | Unknown | Unknown | 1 | 68 | 0.00049629 | 7.3e-06 | No
30/10/2018 | 20:54:40 | HH428C | Urban | Asset failure | HV | 29 | 443 | 0.020538 | 4.636e-05 | No
30/10/2018 | 21:20:16 | HH428C | Urban | Third Party | Vehicle impact | 62 | 326 | 0.032312 | 9.912e-05 | No
30/10/2018 | 21:26:10 | SM126C | Urban | Animal | Animal impact | 53 | 49 | 0.0041518 | 8.473e-05 | No
30/10/2018 | 22:42:26 | MG44 | Urban | Planned |  | 8 | 207 | 0.0026474 | 1.279e-05 | No
30/10/2018 | 23:49:21 | SM126A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 102 | 0.00016306 | 1.6e-06 | No
31/10/2018 | 08:11:14 | VH43 | Rural Short | Planned |  | 1 | 509 | 0.0037921 | 7.45e-06 | No
31/10/2018 | 08:35:22 | GU32 | Rural Long | Planned |  | 9 | 324 | 0.021282 | 6.569e-05 | No
31/10/2018 | 08:39:08 | M73 | Rural Long | Planned |  | 29 | 51 | 0.010794 | 0.00021165 | No
31/10/2018 | 08:50:55 | MV53 | Rural Short | Planned |  | 63 | 182 | 0.085423 | 0.00046936 | No
31/10/2018 | 08:55:25 | ST34 | Rural Long | Planned |  | 55 | 195 | 0.078275 | 0.00040141 | No
31/10/2018 | 08:57:48 | MV14 | Rural Short | Planned |  | 8 | 61 | 0.0036357 | 5.96e-05 | No
31/10/2018 | 08:59:07 | ST51 | Rural Short | Planned |  | 53 | 125 | 0.049357 | 0.00039486 | No
31/10/2018 | 09:02:12 | HH121C | Urban | Planned |  | 134 | 292 | 0.062553 | 0.00021422 | No
31/10/2018 | 09:27:59 | MI33 | Rural Long | Unknown | Unknown | 1 | 237 | 0.0017297 | 7.3e-06 | No
31/10/2018 | 09:34:51 | SD54102 | Rural Long | Planned |  | 28 | 323 | 0.066006 | 0.00020435 | No
31/10/2018 | 09:45:47 | SB03 | Rural Long | Planned |  | 46 | 70.087 | 0.02353 | 0.00033572 | No
31/10/2018 | 10:01:14 | ST41 | Rural Long | Unknown | Unknown | 122 | 212 | 0.18876 | 0.0008904 | No
31/10/2018 | 10:11:08 | WK32 | Rural Short | Planned |  | 2 | 36 | 0.00053641 | 1.49e-05 | No
31/10/2018 | 10:11:54 | GA800A | Rural Short | Planned |  | 1 | 148 | 0.0011026 | 7.45e-06 | No
31/10/2018 | 10:32:24 | SA18 | Urban | Planned |  | 173 | 301 | 0.083248 | 0.00027657 | No
31/10/2018 | 10:39:28 | CM02 | Rural Long | Overloads |  | 2 | 361 | 0.0052694 | 1.46e-05 | No
31/10/2018 | 10:55:46 | NU24 | Rural Long | Planned |  | 27 | 106 | 0.020888 | 0.00019706 | No
31/10/2018 | 12:17:20 | VH22 | Rural Short | Planned |  | 4 | 115 | 0.0034271 | 2.98e-05 | No
31/10/2018 | 16:06:49 | HH107A | Urban | Asset failure | LV | 82 | 25 | 0.0032773 | 0.00013109 | No
31/10/2018 | 18:10:27 | CD02 | Rural Long | Weather |  | 32 | 1233 | 0.28796 | 0.00023355 | No
31/10/2018 | 19:15:21 | CN53 | Rural Long | Unknown | Unknown | 1 | 7 | 5.109e-05 | 7.3e-06 | No
31/10/2018 | 19:31:28 | CD19 | Rural Long | Weather |  | 17 | 929 | 0.11526 | 0.00012407 | No
31/10/2018 | 19:35:27 | AP365E | Urban | Planned |  | 17 | 425 | 0.01155 | 2.718e-05 | No
31/10/2018 | 20:16:00 | ST22 | Rural Short | Animal | Animal impact | 13 | 172 | 0.016659 | 9.685e-05 | No
31/10/2018 | 21:52:54 | HH496A | Urban | Asset failure | LV | 1 | 148 | 0.0002366 | 1.6e-06 | No
31/10/2018 | 22:02:29 | CBD103B | Urban | Planned |  | 0 | 2 | 3.2e-06 | 0 | No
31/10/2018 | 22:02:29 | CBD103B | Urban | Planned |  | 22 | 494.5909 | 0.017395 | 3.517e-05 | No
31/10/2018 | 22:06:41 | HH409A | Urban | Vegetation | Grow-in - NSP responsibility | 91 | 24 | 0.0034915 | 0.00014548 | No
31/10/2018 | 22:56:54 | EL18 | Urban | Asset failure | LV | 1 | 348 | 0.00055634 | 1.6e-06 | No
1/11/2018 | 01:06:47 | PL24 | Rural Long | Unknown | Unknown | 32 | 628 | 0.14667 | 0.00023355 | No
1/11/2018 | 02:19:39 | NL760B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 28.6666 | 159 | 0.0072867 | 4.583e-05 | No
1/11/2018 | 08:13:23 | ST43 | Rural Long | Planned |  | 6 | 182 | 0.0079698 | 4.379e-05 | No
1/11/2018 | 08:34:26 | YK17 | Rural Long | Planned |  | 148 | 294 | 0.31757 | 0.0010801 | No
1/11/2018 | 08:38:27 | ST42 | Rural Long | Planned |  | 12 | 163 | 0.014276 | 8.758e-05 | No
1/11/2018 | 08:42:38 | WK32 | Rural Short | Planned |  | 1 | 195 | 0.0014528 | 7.45e-06 | No
1/11/2018 | 08:53:00 | SA17 | Urban | Unknown | Unknown | 8 | 171 | 0.002187 | 1.279e-05 | No
1/11/2018 | 08:53:08 | MV63 | Rural Short | Planned |  | 82 | 91 | 0.055593 | 0.00061091 | No
1/11/2018 | 08:58:32 | MTB13 | Rural Short | Planned |  | 4 | 295 | 0.0087912 | 2.98e-05 | No
1/11/2018 | 09:08:47 | VH45 | Rural Short | Planned |  | 2 | 63 | 0.00093872 | 1.49e-05 | No
1/11/2018 | 09:22:54 | HH432C | Urban | Planned |  | 112 | 22 | 0.0039391 | 0.00017905 | No
1/11/2018 | 09:27:27 | WHY09 | Urban | Planned |  | 65 | 132 | 0.013717 | 0.00010391 | No
1/11/2018 | 09:37:17 | ST35 | Rural Long | Planned |  | 63 | 252.4444 | 0.11607 | 0.0004598 | No
1/11/2018 | 09:40:44 | MV63 | Rural Short | Planned |  | 1 | 4 | 2.98e-05 | 7.45e-06 | No
1/11/2018 | 09:53:44 | MG27 | Rural Long | Planned |  | 1 | 137 | 0.00099987 | 7.3e-06 | No
1/11/2018 | 09:56:25 | SM216A | Urban | Planned |  | 4 | 8 | 5.116e-05 | 6.39e-06 | No
1/11/2018 | 10:05:10 | NU19 | Rural Long | Planned |  | 11 | 43 | 0.0034521 | 8.028e-05 | No
1/11/2018 | 10:45:48 | HH177B | Urban | Planned |  | 30 | 56 | 0.0026858 | 4.796e-05 | No
1/11/2018 | 10:46:17 | SG07 | Rural Short | Planned |  | 1 | 106 | 0.00078972 | 7.45e-06 | No
1/11/2018 | 11:02:50 | GA41 | Rural Long | Planned |  | 55 | 207 | 0.083092 | 0.00040141 | No
1/11/2018 | 11:25:25 | AP425C | Urban | Planned |  | 92 | 1 | 0.00014708 | 0.00014708 | No
1/11/2018 | 12:06:48 | ST42 | Rural Long | Planned |  | 14 | 62 | 0.006335 | 0.00010218 | No
1/11/2018 | 12:16:32 | MG19 | Rural Long | Asset failure | Distribution substation | 409 | 156.2445 | 0.46639 | 0.002985 | No
1/11/2018 | 13:16:54 | MV13 | Rural Short | Planned |  | 2 | 53 | 0.00078972 | 1.49e-05 | No
1/11/2018 | 13:37:36 | W27 | Rural Long | Weather |  | 32 | 28 | 0.0065393 | 0.00023355 | No
1/11/2018 | 13:52:07 | HH432C | Urban | Planned |  | 112 | 23 | 0.0041182 | 0.00017905 | No
1/11/2018 | 14:21:29 | AP373C | Urban | Third Party | Other | 1 | 210 | 0.00033572 | 1.6e-06 | No
1/11/2018 | 14:36:15 | SA520A | Urban | Asset failure | LV | 24 | 478 | 0.01834 | 3.837e-05 | No
1/11/2018 | 15:10:04 | YK12 | Rural Long | Asset failure | Distribution substation | 90 | 251.2667 | 0.16504 | 0.00065685 | No
1/11/2018 | 15:30:18 | NA22 | Rural Long | Unknown | Unknown | 1 | 40 | 0.00029193 | 7.3e-06 | No
1/11/2018 | 15:52:41 | HH341H | Urban | Other |  | 42.3333 | 112 | 0.0075798 | 6.768e-05 | No
1/11/2018 | 16:02:56 | SG13 | Rural Short | Unknown | Unknown | 2 | 285 | 0.0042466 | 1.49e-05 | No
1/11/2018 | 16:58:36 | MTB12 | Rural Short | Animal | Animal impact | 7 | 221 | 0.011525 | 5.215e-05 | No
1/11/2018 | 17:00:12 | W27 | Rural Long | Unknown | Unknown | 73 | 294.9315 | 0.15713 | 0.00053278 | No
1/11/2018 | 17:28:04 | HH496A | Urban | Vegetation | Grow-in - NSP responsibility | 14.3333 | 74 | 0.0016957 | 2.291e-05 | No
1/11/2018 | 18:02:36 | W26 | Rural Long | Weather |  | 95 | 1123.0105 | 0.77863 | 0.00069334 | No
1/11/2018 | 18:11:37 | ME347C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 165 | 0.00026378 | 1.6e-06 | No
1/11/2018 | 18:21:59 | SM410B | Urban | Unknown | Unknown | 36.3333 | 52 | 0.0030204 | 5.809e-05 | No
1/11/2018 | 18:26:28 | SA11 | Urban | Asset failure | LV | 19.6666 | 66 | 0.0020751 | 3.144e-05 | No
1/11/2018 | 18:30:14 | SA20 | Urban | Asset failure | LV | 1 | 64 | 0.00010232 | 1.6e-06 | No
1/11/2018 | 19:32:09 | CV25 | Rural Long | Weather |  | 14 | 218 | 0.022275 | 0.00010218 | No
1/11/2018 | 19:33:46 | SM179D | Urban | Asset failure | LV | 36 | 128 | 0.0073667 | 5.755e-05 | No
1/11/2018 | 20:31:45 | CV23 | Rural Long | Weather |  | 69 | 954.6957 | 0.48077 | 0.00050359 | No
1/11/2018 | 20:32:16 | VH43 | Rural Short | Weather |  | 14 | 1219.4286 | 0.12719 | 0.0001043 | No
1/11/2018 | 20:32:16 | VH43 | Rural Short | Weather |  | 0 | 762 | 0.068124 | 0 | No
1/11/2018 | 22:58:28 | MV62 | Rural Short | Weather |  | 2078 | 82.1574 | 1.2719 | 0.015481 | No
1/11/2018 | 23:08:08 | MV33 | Rural Short | Unknown | Unknown | 37 | 292 | 0.080491 | 0.00027566 | No
1/11/2018 | 23:19:52 | ST16 | Rural Short | Weather |  | 52 | 905.4808 | 0.35079 | 0.00038741 | No
1/11/2018 | 23:19:52 | ST16 | Rural Short | Weather |  | 0 | 225.3636 | 0.073876 | 0 | No
1/11/2018 | 23:42:00 | ST15 | Rural Short | Weather |  | 41 | 1315.9024 | 0.40195 | 0.00030546 | No
1/11/2018 | 23:53:06 | HH148C | Urban | Weather |  | 119 | 641 | 0.12195 | 0.00019024 | No
1/11/2018 | 23:53:06 | HH148C | Urban | Weather |  | 795 | 1 | 0.001271 | 0.001271 | No
2/11/2018 | 00:14:17 | AP226E | Urban | Overloads |  | 1 | 79 | 0.0001263 | 1.6e-06 | Yes
2/11/2018 | 00:20:10 | ST23 | Rural Short | Weather |  | 7 | 795 | 0.04146 | 5.215e-05 | Yes
2/11/2018 | 00:51:14 | CM20 | Rural Long | Weather |  | 229 | 793.0349 | 1.3254 | 0.0016713 | Yes
2/11/2018 | 00:57:01 | SD35500 | Rural Long | Weather |  | 565 | 462.0619 | 1.9053 | 0.0041236 | Yes
2/11/2018 | 01:16:20 | CM11 | Rural Long | Weather |  | 66 | 2130.5758 | 1.0263 | 0.00048169 | Yes
2/11/2018 | 01:16:20 | CM11 | Rural Long | Weather |  | 0 | 241.9231 | 0.045907 | 0 | Yes
2/11/2018 | 01:24:21 | YK18 | Rural Long | Weather |  | 90 | 465.4889 | 0.30576 | 0.00065685 | Yes
2/11/2018 | 01:28:43 | W01 | Rural Long | Weather |  | 201 | 681 | 0.999 | 0.001467 | Yes
2/11/2018 | 01:49:46 | SD45101 | Rural Long | Weather |  | 100 | 1412.87 | 1.0312 | 0.00072983 | Yes
2/11/2018 | 01:49:46 | SD45101 | Rural Long | Weather |  | 0 | 61 | 0.033835 | 0 | Yes
2/11/2018 | 01:53:58 | VH17 | Rural Short | Unknown | Unknown | 5 | 883 | 0.032892 | 3.725e-05 | Yes
2/11/2018 | 02:01:49 | CV31 | Rural Long | Unknown | Unknown | 58 | 849.569 | 0.35963 | 0.0004233 | Yes
2/11/2018 | 02:06:40 | VH72 | Rural Short | Weather |  | 49 | 793 | 0.28949 | 0.00036506 | Yes
2/11/2018 | 02:11:14 | MV62 | Rural Short | Unknown | Unknown | 1122 | 9.7665 | 0.081639 | 0.0083591 | Yes
2/11/2018 | 02:14:28 | YK22 | Rural Short | Weather |  | 79 | 681.1266 | 0.40089 | 0.00058856 | Yes
2/11/2018 | 02:20:53 | MV63 | Rural Short | Weather |  | 365 | 226.6055 | 0.61621 | 0.0027193 | Yes
2/11/2018 | 02:25:56 | NL115C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 403 | 0.00064427 | 1.6e-06 | Yes
2/11/2018 | 02:26:38 | VH32 | Rural Short | Weather |  | 585 | 711.1094 | 3.0993 | 0.0043583 | Yes
2/11/2018 | 02:30:14 | YK20 | Rural Long | Unknown | Unknown | 128 | 632.6406 | 0.591 | 0.00093419 | Yes
2/11/2018 | 02:31:37 | VH32 | Rural Short | Unknown | Unknown | 9 | 2419 | 0.1622 | 6.705e-05 | Yes
2/11/2018 | 02:45:00 | CV05 | Rural Long | Unknown | Unknown | 55 | 550 | 0.22077 | 0.00040141 | Yes
2/11/2018 | 02:45:53 | CV21 | Rural Long | Weather |  | 30 | 1411.9 | 0.30914 | 0.00021895 | Yes
2/11/2018 | 02:52:18 | MT01 | Rural Long | Unknown | Unknown | 111 | 667.2432 | 0.54054 | 0.00081012 | Yes
2/11/2018 | 03:07:37 | NL111C | Urban | Weather |  | 34.3333 | 353 | 0.019375 | 5.489e-05 | Yes
2/11/2018 | 03:10:00 | NL760B | Urban | Weather |  | 2675 | 10.7308 | 0.04589 | 0.0042765 | Yes
2/11/2018 | 03:11:15 | MV15 | Rural Short | Unknown | Unknown | 9 | 459 | 0.030777 | 6.705e-05 | Yes
2/11/2018 | 03:15:07 | CN25 | Rural Long | Weather |  | 52 | 615.5 | 0.23359 | 0.00037951 | Yes
2/11/2018 | 03:15:36 | MB63 | Rural Long | Asset failure | HV | 248 | 590.2419 | 1.0683 | 0.00181 | Yes
2/11/2018 | 03:16:55 | BT26 | Rural Long | Unknown | Unknown | 323 | 681.3622 | 1.6062 | 0.0023574 | Yes
2/11/2018 | 03:18:03 | GA15 | Rural Short | Weather |  | 1 | 1873 | 0.013954 | 7.45e-06 | Yes
2/11/2018 | 03:18:16 | MT10 | Rural Long | Weather |  | 99 | 812.4747 | 0.58704 | 0.00072254 | Yes
2/11/2018 | 03:18:16 | MT20 | Rural Long | Weather |  | 10 | 617 | 0.045031 | 7.298e-05 | Yes
2/11/2018 | 03:20:10 | CV24 | Rural Long | Unknown | Unknown | 13 | 1034 | 0.098104 | 9.488e-05 | Yes
2/11/2018 | 03:22:17 | EL23 | Urban | Weather |  | 638 | 31.873 | 0.032509 | 0.0010199 | Yes
2/11/2018 | 03:22:42 | EL260A | Urban | Weather |  | 377 | 316.4987 | 0.19075 | 0.0006027 | Yes
2/11/2018 | 03:22:57 | EL16 | Urban | Weather |  | 9 | 701.1111 | 0.010088 | 1.439e-05 | Yes
2/11/2018 | 03:24:44 | CN03 | Rural Long | Weather |  | 51 | 903.1373 | 0.33616 | 0.00037222 | Yes
2/11/2018 | 03:26:22 | CN72 | Rural Long | Weather |  | 91 | 1924 | 1.2778 | 0.00066415 | Yes
2/11/2018 | 03:26:38 | EL23 | Urban | Weather |  | 1 | 434 | 0.00069382 | 1.6e-06 | Yes
2/11/2018 | 03:26:38 | GA22 | Rural Short | Weather |  | 978 | 471.2924 | 3.434 | 0.0072863 | Yes
2/11/2018 | 03:28:07 | EL20 | Urban | Unknown | Unknown | 467 | 382 | 0.28519 | 0.00074658 | Yes
2/11/2018 | 03:29:38 | SD40200 | Rural Long | Weather |  | 1 | 1826 | 0.013327 | 7.3e-06 | Yes
2/11/2018 | 03:29:38 | MB28 | Rural Short | Weather |  | 139 | 160.3813 | 0.16609 | 0.0010356 | Yes
2/11/2018 | 03:30:10 | AP372D | Urban | Overloads |  | 23.3333 | 310 | 0.011564 | 3.73e-05 | Yes
2/11/2018 | 03:31:14 | GA800A | Rural Short | Weather |  | 4 | 341 | 0.010162 | 2.98e-05 | Yes
2/11/2018 | 03:33:06 | EL17 | Urban | Unknown | Unknown | 8 | 586 | 0.0074946 | 1.279e-05 | Yes
2/11/2018 | 03:33:14 | MB83 | Rural Long | Weather |  | 74 | 853 | 0.46069 | 0.00054008 | Yes
2/11/2018 | 03:33:46 | EL17 | Urban | Weather |  | 989 | 208 | 0.32887 | 0.0015811 | Yes
2/11/2018 | 03:36:25 | EL19 | Urban | Weather |  | 84 | 452.5595 | 0.060774 | 0.00013429 | Yes
2/11/2018 | 03:39:13 | KA08 | Rural Long | Weather |  | 69 | 462 | 0.23266 | 0.00050359 | Yes
2/11/2018 | 03:40:00 | EL11 | Urban | Weather |  | 2203 | 223.034 | 0.7855 | 0.0035219 | Yes
2/11/2018 | 03:41:04 | BT04 | Rural Long | Weather |  | 345 | 217 | 0.54639 | 0.0025179 | Yes
2/11/2018 | 03:41:54 | BT04 | Rural Long | Unknown | Unknown | 78 | 1052 | 0.59887 | 0.00056927 | Yes
2/11/2018 | 04:03:52 | MV13 | Rural Short | Weather |  | 11 | 504 | 0.041304 | 8.195e-05 | Yes
2/11/2018 | 04:11:19 | NL234C | Urban | Asset failure | LV | 11.6667 | 484 | 0.0090272 | 1.865e-05 | Yes
2/11/2018 | 04:30:06 | NA04 | Rural Long | Unknown | Unknown | 9 | 405 | 0.026602 | 6.569e-05 | Yes
2/11/2018 | 04:33:29 | MT12 | Rural Long | Unknown | Unknown | 26 | 328 | 0.06224 | 0.00018976 | Yes
2/11/2018 | 04:52:22 | NU31 | Rural Long | Unknown | Unknown | 11 | 264 | 0.021194 | 8.028e-05 | Yes
2/11/2018 | 04:54:38 | M71 | Rural Long | Animal | Animal impact | 147 | 306 | 0.32829 | 0.0010729 | Yes
2/11/2018 | 04:57:50 | SD35500 | Rural Long | Weather |  | 1842 | 341 | 4.5842 | 0.013444 | Yes
2/11/2018 | 05:03:57 | AP355A | Urban | Weather |  | 109 | 222 | 0.038685 | 0.00017426 | Yes
2/11/2018 | 05:09:52 | CL05 | Rural Long | Unknown | Unknown | 49 | 290 | 0.10371 | 0.00035762 | Yes
2/11/2018 | 05:11:16 | BT02 | Rural Long | Unknown | Unknown | 167 | 439 | 0.53506 | 0.0012188 | Yes
2/11/2018 | 05:13:00 | HH432F | Urban | Weather |  | 10.3333 | 255 | 0.0042125 | 1.652e-05 | Yes
2/11/2018 | 05:16:19 | CBD103C | Urban | Asset failure | HV | 106 | 198 | 0.033553 | 0.00016946 | Yes
2/11/2018 | 05:16:27 | MTB21 | Rural Short | Weather |  | 81 | 333 | 0.20095 | 0.00060346 | Yes
2/11/2018 | 05:28:05 | MTB52 | Rural Long | Weather |  | 975 | 298.7159 | 2.1256 | 0.0071159 | Yes
2/11/2018 | 05:37:28 | MTB61 | Rural Short | Unknown | Unknown | 11 | 388 | 0.031797 | 8.195e-05 | Yes
2/11/2018 | 05:37:53 | MV62 | Rural Short | Weather |  | 2078 | 71.6405 | 1.1091 | 0.015481 | Yes
2/11/2018 | 05:43:00 | BT06 | Rural Long | Weather |  | 116 | 422 | 0.35727 | 0.00084661 | Yes
2/11/2018 | 05:43:00 | BT14 | Rural Long | Unknown | Unknown | 87 | 574.0575 | 0.3645 | 0.00063496 | Yes
2/11/2018 | 05:43:00 | BT14 | Rural Long | Weather |  | 87 | 1727.8276 | 1.0971 | 0.00063496 | Yes
2/11/2018 | 05:44:14 | NL544B | Urban | Weather |  | 168 | 517.1905 | 0.13891 | 0.00026858 | Yes
2/11/2018 | 05:46:06 | VH22 | Rural Short | Unknown | Unknown | 24 | 641 | 0.11461 | 0.0001788 | Yes
2/11/2018 | 05:46:58 | MV53 | Rural Short | Weather |  | 2 | 503 | 0.0074948 | 1.49e-05 | Yes
2/11/2018 | 05:47:24 | MV51 | Rural Short | Weather |  | 120 | 384 | 0.3433 | 0.00089402 | Yes
2/11/2018 | 05:47:38 | M23 | Rural Long | Unknown | Unknown | 125 | 484.768 | 0.44225 | 0.00091229 | Yes
2/11/2018 | 05:47:55 | VH43 | Rural Short | Weather |  | 101 | 138 | 0.10384 | 0.00075247 | Yes
2/11/2018 | 05:54:21 | ST35 | Rural Long | Weather |  | 7 | 617 | 0.031522 | 5.109e-05 | Yes
2/11/2018 | 05:55:49 | ST42 | Rural Long | Weather |  | 15 | 667 | 0.07302 | 0.00010948 | Yes
2/11/2018 | 05:57:15 | MV41 | Rural Short | Weather |  | 256 | 586 | 1.1176 | 0.0019072 | Yes
2/11/2018 | 05:57:43 | LX71 | Rural Long | Unknown | Unknown | 128 | 350.8594 | 0.32777 | 0.00093419 | Yes
2/11/2018 | 05:59:59 | VH45 | Rural Short | Weather |  | 1285 | 255.8397 | 2.4493 | 0.0095734 | Yes
2/11/2018 | 06:06:33 | MV54 | Rural Short | Weather |  | 121 | 120.4215 | 0.10856 | 0.00090147 | Yes
2/11/2018 | 06:07:17 | BT14 | Rural Long | Weather |  | 63 | 1659 | 0.7628 | 0.0004598 | Yes
2/11/2018 | 06:16:22 | MV33 | Rural Short | Unknown | Unknown | 37 | 393 | 0.10833 | 0.00027566 | Yes
2/11/2018 | 06:16:49 | ST36 | Rural Long | Animal | Animal impact | 40 | 503 | 0.14684 | 0.00029193 | Yes
2/11/2018 | 06:29:58 | CL06 | Rural Long | Weather |  | 5 | 750 | 0.027369 | 3.649e-05 | Yes
2/11/2018 | 06:36:32 | CM09 | Rural Long | Unknown | Unknown | 13 | 1504 | 0.1427 | 9.488e-05 | Yes
2/11/2018 | 06:37:22 | NL760B | Urban | Weather |  | 6 | 371 | 0.0035587 | 9.59e-06 | Yes
2/11/2018 | 06:38:08 | MG34 | Rural Long | Animal | Animal impact | 11 | 190 | 0.015254 | 8.028e-05 | Yes
2/11/2018 | 06:42:21 | LM12 | Rural Long | Weather |  | 18.3333 | 300 | 0.040141 | 0.0001338 | Yes
2/11/2018 | 06:43:18 | ST11 | Rural Short | Unknown | Unknown | 3 | 317 | 0.0070851 | 2.235e-05 | Yes
2/11/2018 | 06:52:07 | NA05 | Rural Long | Unknown | Unknown | 14.6667 | 160 | 0.017127 | 0.00010704 | Yes
2/11/2018 | 06:52:40 | MB01 | Rural Long | Unknown | Unknown | 47 | 302 | 0.10359 | 0.00034302 | Yes
2/11/2018 | 07:02:01 | CV15 | Rural Long | Unknown | Unknown | 26 | 576 | 0.1093 | 0.00018976 | Yes
2/11/2018 | 07:13:47 | WK91 | Rural Short | Unknown | Unknown | 52 | 601.3462 | 0.23297 | 0.00038741 | Yes
2/11/2018 | 07:18:52 | CM26 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 2094 | 0.15283 | 7.298e-05 | Yes
2/11/2018 | 07:18:55 | MV62 | Rural Short | Weather |  | 956 | 67.59 | 0.4814 | 0.0071223 | Yes
2/11/2018 | 07:26:27 | HH409F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 134 | 0.00021422 | 1.6e-06 | Yes
2/11/2018 | 07:27:46 | MV15 | Rural Short | Weather |  | 3.6667 | 442 | 0.012074 | 2.732e-05 | Yes
2/11/2018 | 07:39:18 | BT06 | Rural Long | Unknown | Unknown | 3 | 392 | 0.0085828 | 2.19e-05 | Yes
2/11/2018 | 08:14:26 | MV11 | Rural Short | Unknown | Unknown | 5 | 375 | 0.013969 | 3.725e-05 | Yes
2/11/2018 | 08:16:33 | ST44 | Rural Long | Weather |  | 4 | 464 | 0.013546 | 2.919e-05 | Yes
2/11/2018 | 08:17:00 | BT02 | Rural Long | Weather |  | 7 | 417 | 0.021304 | 5.109e-05 | Yes
2/11/2018 | 08:22:59 | MV11 | Rural Short | Weather |  | 3 | 205 | 0.0045818 | 2.235e-05 | Yes
2/11/2018 | 08:23:20 | NL234C | Urban | Asset failure | LV | 115 | 115 | 0.021142 | 0.00018385 | Yes
2/11/2018 | 08:28:42 | CM21 | Rural Long | Weather |  | 13 | 1919.4615 | 0.18212 | 9.488e-05 | Yes
2/11/2018 | 08:43:56 | PA02 | Urban | Asset failure | LV | 20 | 271 | 0.0086648 | 3.197e-05 | Yes
2/11/2018 | 08:44:57 | PA02 | Urban | Asset failure | LV | 20 | 241 | 0.0077056 | 3.197e-05 | Yes
2/11/2018 | 08:45:13 | PA02 | Urban | Asset failure | LV | 29 | 242 | 0.01122 | 4.636e-05 | Yes
2/11/2018 | 09:26:24 | W24 | Rural Long | Unknown | Unknown | 13 | 1589 | 0.15076 | 9.488e-05 | Yes
2/11/2018 | 09:53:24 | VH44 | Rural Short | Unknown | Unknown | 3.3333 | 491 | 0.012193 | 2.483e-05 | Yes
2/11/2018 | 09:54:48 | AP139C | Urban | Third Party | Vehicle impact | 896 | 156.8806 | 0.22472 | 0.0014324 | Yes
2/11/2018 | 10:10:10 | ST22 | Rural Short | Weather |  | 3 | 273 | 0.0061017 | 2.235e-05 | Yes
2/11/2018 | 10:10:50 | MV41 | Rural Short | Unknown | Unknown | 255 | 333 | 0.63263 | 0.0018998 | Yes
2/11/2018 | 10:14:24 | CM22 | Rural Long | Weather |  | 16 | 1991.625 | 0.23257 | 0.00011677 | Yes
2/11/2018 | 10:14:24 | CM22 | Rural Long | Weather |  | 0 | 17 | 0.0016129 | 0 | Yes
2/11/2018 | 10:17:19 | YK15 | Rural Long | Weather |  | 75 | 44 | 0.024085 | 0.00054738 | Yes
2/11/2018 | 10:20:03 | EL15 | Urban | Unknown | Unknown | 2.6667 | 645 | 0.0027497 | 4.26e-06 | Yes
2/11/2018 | 10:22:49 | MV62 | Rural Short | Unknown | Unknown | 15 | 137 | 0.01531 | 0.00011175 | Yes
2/11/2018 | 10:32:29 | AP365E | Urban | Unknown | Unknown | 2.6667 | 958 | 0.0040841 | 4.26e-06 | Yes
2/11/2018 | 10:48:22 | NL115B | Urban | Unknown | Unknown | 19 | 124 | 0.0037665 | 3.037e-05 | Yes
2/11/2018 | 10:51:50 | MV42 | Rural Short | Weather |  | 546 | 133.5458 | 0.54324 | 0.0040678 | Yes
2/11/2018 | 11:00:04 | PP02 | Urban | Asset failure | LV | 79 | 270 | 0.0341 | 0.0001263 | Yes
2/11/2018 | 11:21:32 | GA03 | Rural Long | Unknown | Unknown | 7 | 183 | 0.0093492 | 5.109e-05 | Yes
2/11/2018 | 12:01:31 | MT23 | Rural Long | Asset failure | Distribution substation | 3 | 653 | 0.014297 | 2.19e-05 | Yes
2/11/2018 | 12:01:31 | MT23 | Rural Long | Weather |  | 139 | 408 | 0.4139 | 0.0010145 | Yes
2/11/2018 | 12:20:25 | CV19 | Rural Long | Weather |  | 9 | 1394 | 0.091565 | 6.569e-05 | Yes
2/11/2018 | 12:41:17 | MT09 | Rural Long | Weather |  | 66 | 304 | 0.14643 | 0.00048169 | Yes
2/11/2018 | 13:02:37 | BT28 | Rural Long | Weather |  | 36 | 298 | 0.078297 | 0.00026274 | Yes
2/11/2018 | 13:15:24 | W21 | Rural Long | Weather |  | 53 | 456.7736 | 0.17669 | 0.00038681 | Yes
2/11/2018 | 13:22:56 | ME427A | Urban | Third Party | Vehicle impact | 108 | 502 | 0.086674 | 0.00017266 | Yes
2/11/2018 | 13:34:33 | W16 | Rural Long | Weather |  | 25 | 475.6 | 0.086777 | 0.00018246 | Yes
2/11/2018 | 13:46:54 | AP529C | Urban | Planned |  | 115 | 13 | 0.00239 | 0.00018385 | Yes
2/11/2018 | 13:49:18 | ST11 | Rural Short | Unknown | Unknown | 34 | 425 | 0.10765 | 0.00025331 | Yes
2/11/2018 | 14:05:12 | YK11 | Rural Long | Weather |  | 94 | 297.7872 | 0.2043 | 0.00068604 | Yes
2/11/2018 | 14:05:46 | GA53 | Rural Short | Unknown | Unknown | 3.3333 | 15 | 0.00037251 | 2.483e-05 | Yes
2/11/2018 | 14:28:58 | VH44 | Rural Short | Weather |  | 7 | 221 | 0.011525 | 5.215e-05 | Yes
2/11/2018 | 14:55:24 | ST21 | Rural Short | Weather |  | 10 | 35 | 0.0026076 | 7.45e-05 | Yes
2/11/2018 | 15:01:42 | GU17 | Rural Long | Weather |  | 2 | 197 | 0.0028756 | 1.46e-05 | Yes
2/11/2018 | 15:04:39 | MTB12 | Rural Short | Weather |  | 3 | 822 | 0.018372 | 2.235e-05 | Yes
2/11/2018 | 15:22:10 | VH43 | Rural Short | Weather |  | 3 | 249 | 0.0055653 | 2.235e-05 | Yes
2/11/2018 | 15:27:59 | EL11 | Urban | Weather |  | 2170 | 5.7051 | 0.019792 | 0.0034691 | Yes
2/11/2018 | 15:28:37 | MTB22 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 1690 | 0.012591 | 7.45e-06 | Yes
2/11/2018 | 15:57:22 | MT01 | Rural Long | Asset failure | LV | 1 | 95 | 0.00069334 | 7.3e-06 | Yes
2/11/2018 | 15:57:42 | VH45 | Rural Short | Asset failure | LV | 17 | 334 | 0.042302 | 0.00012665 | Yes
2/11/2018 | 16:02:01 | ST51 | Rural Short | Weather |  | 29.3333 | 268 | 0.058568 | 0.00021854 | Yes
2/11/2018 | 16:10:58 | MT16 | Rural Long | Unknown | Unknown | 113 | 87.3894 | 0.072071 | 0.00082471 | Yes
2/11/2018 | 16:21:12 | NU15 | Rural Long | Unknown | Unknown | 2 | 207 | 0.0030215 | 1.46e-05 | Yes
2/11/2018 | 17:01:06 | MV34 | Rural Short | Other |  | 12 | 149 | 0.013321 | 8.94e-05 | Yes
2/11/2018 | 17:04:47 | SD35400 | Rural Short | Weather |  | 2 | 1201 | 0.017895 | 1.49e-05 | Yes
2/11/2018 | 17:10:29 | NU23 | Rural Long | Weather |  | 44 | 10.2727 | 0.0032988 | 0.00032113 | Yes
2/11/2018 | 17:43:05 | MT02 | Rural Long | Weather |  | 1 | 301 | 0.0021968 | 7.3e-06 | Yes
2/11/2018 | 17:44:44 | SG04 | Rural Short | Asset failure | LV | 1 | 614 | 0.0045744 | 7.45e-06 | Yes
2/11/2018 | 17:46:29 | YK04 | Rural Short | Weather |  | 2 | 1441 | 0.021471 | 1.49e-05 | Yes
2/11/2018 | 18:15:23 | VH14 | Rural Short | Unknown | Unknown | 6 | 159 | 0.0071074 | 4.47e-05 | Yes
2/11/2018 | 18:15:23 | CN83 | Rural Long | Weather |  | 7 | 1219 | 0.062277 | 5.109e-05 | Yes
2/11/2018 | 18:16:02 | CN91 | Rural Long | Weather |  | 10.3333 | 1312 | 0.098946 | 7.542e-05 | Yes
2/11/2018 | 19:29:44 | SM349C | Urban | Overloads |  | 1 | 250 | 0.00039967 | 1.6e-06 | Yes
2/11/2018 | 20:00:54 | BT18 | Rural Long | Other |  | 1 | 1070 | 0.0078092 | 7.3e-06 | Yes
2/11/2018 | 20:02:37 | ST44 | Rural Long | Unknown | Unknown | 3 | 1070 | 0.023428 | 2.19e-05 | Yes
2/11/2018 | 20:23:04 | CV31 | Rural Long | Weather |  | 13 | 882 | 0.083683 | 9.488e-05 | Yes
2/11/2018 | 20:47:13 | ST51 | Rural Short | Unknown | Unknown | 29.3333 | 983 | 0.21482 | 0.00021854 | Yes
2/11/2018 | 20:52:20 | MT22 | Rural Long | Weather |  | 448.3335 | 33.9703 | 0.11115 | 0.0032721 | Yes
2/11/2018 | 22:23:19 | MB62 | Rural Long | Asset failure | HV | 248 | 425.625 | 0.77038 | 0.00181 | Yes
3/11/2018 | 00:29:17 | MV62 | Rural Short | Weather |  | 1 | 962 | 0.007167 | 7.45e-06 | No
3/11/2018 | 01:00:47 | SD45101 | Rural Long | Unknown | Unknown | 74 | 677 | 0.36563 | 0.00054008 | No
3/11/2018 | 01:16:02 | CM24 | Rural Long | Weather |  | 42 | 827.119 | 0.25354 | 0.00030653 | No
3/11/2018 | 06:38:55 | MT16 | Rural Long | Unknown | Unknown | 113 | 238.2124 | 0.19646 | 0.00082471 | No
3/11/2018 | 07:40:12 | HH496B | Urban | Planned |  | 65 | 114.5231 | 0.011901 | 0.00010391 | No
3/11/2018 | 07:45:27 | NU13 | Rural Long | Planned |  | 1 | 496 | 0.00362 | 7.3e-06 | No
3/11/2018 | 08:53:00 | BT26 | Rural Long | Unknown | Unknown | 323 | 9.0991 | 0.02145 | 0.0023574 | No
3/11/2018 | 09:40:41 | GA22 | Rural Short | Unknown | Unknown | 3 | 684 | 0.015288 | 2.235e-05 | No
3/11/2018 | 10:38:11 | M23 | Rural Long | Weather |  | 2 | 45 | 0.00065685 | 1.46e-05 | No
3/11/2018 | 11:04:59 | EL15 | Urban | Weather |  | 2 | 703 | 0.0022477 | 3.2e-06 | No
3/11/2018 | 11:11:29 | HH107C | Urban | Asset failure | LV | 39 | 18 | 0.0011223 | 6.235e-05 | No
3/11/2018 | 11:54:06 | EL17 | Urban | Weather |  | 2 | 124 | 0.00039647 | 3.2e-06 | No
3/11/2018 | 15:01:07 | GA16 | Rural Long | Asset failure | HV | 1 | 274 | 0.0019997 | 7.3e-06 | No
3/11/2018 | 15:15:35 | BT26 | Rural Long | Weather |  | 7.6667 | 73 | 0.0040846 | 5.595e-05 | No
3/11/2018 | 16:52:53 | HH145B | Urban | Overloads |  | 1 | 90 | 0.00014388 | 1.6e-06 | No
3/11/2018 | 23:49:09 | NL210A | Urban | Animal | Animal impact | 10 | 123 | 0.0019664 | 1.599e-05 | No
4/11/2018 | 01:45:00 | WK61 | Rural Short | Planned |  | 451 | 171 | 0.57456 | 0.00336 | No
4/11/2018 | 01:59:55 | HH496C | Urban | Asset failure | HV | 3019 | 42.1351 | 0.20336 | 0.0048264 | No
4/11/2018 | 03:54:45 | MV62 | Rural Short | Asset failure | HV | 611 | 253.1064 | 1.1522 | 0.004552 | No
4/11/2018 | 05:34:30 | MTB22 | Rural Short | Planned |  | 213 | 70 | 0.11108 | 0.0015869 | No
4/11/2018 | 09:12:08 | BT26 | Rural Long | Weather |  | 323 | 135.0867 | 0.31845 | 0.0023574 | No
4/11/2018 | 09:38:09 | SA14 | Urban | Planned |  | 2 | 340 | 0.0010871 | 3.2e-06 | No
4/11/2018 | 09:46:01 | SG12 | Rural Short | Asset failure | LV | 5.6667 | 203 | 0.0085702 | 4.222e-05 | No
4/11/2018 | 10:56:20 | AP125D | Urban | Vegetation | Grow-in - NSP responsibility | 27.3333 | 29 | 0.0012672 | 4.37e-05 | No
4/11/2018 | 12:39:29 | MV62 | Rural Short | Unknown | Unknown | 15 | 308 | 0.03442 | 0.00011175 | No
4/11/2018 | 14:02:37 | CV24 | Rural Long | Asset failure | Distribution substation | 73 | 1 | 0.00053278 | 0.00053278 | No
4/11/2018 | 14:27:24 | SM410B | Urban | Asset failure | LV | 35 | 97 | 0.0054275 | 5.595e-05 | No
4/11/2018 | 14:28:52 | W27 | Rural Long | Weather |  | 11 | 482 | 0.038696 | 8.028e-05 | No
4/11/2018 | 17:16:21 | CM10 | Rural Long | Unknown | Unknown | 58 | 252 | 0.10667 | 0.0004233 | No
4/11/2018 | 18:26:08 | NL544B | Urban | Weather |  | 168 | 237.0476 | 0.063666 | 0.00026858 | No
4/11/2018 | 19:11:55 | ST41 | Rural Long | Weather |  | 372 | 111.3091 | 0.3022 | 0.002715 | No
4/11/2018 | 19:12:30 | WK91 | Rural Short | Weather |  | 52 | 792.6538 | 0.30708 | 0.00038741 | No
4/11/2018 | 19:49:44 | MV64 | Urban | Animal | Animal impact | 11.3333 | 218 | 0.0039498 | 1.812e-05 | No
4/11/2018 | 20:13:34 | AP226D | Urban | Unknown | Unknown | 2264 | 5.4024 | 0.019553 | 0.0036194 | No
4/11/2018 | 20:22:05 | R04 | Rural Long | Unknown | Unknown | 575 | 217.447 | 0.91253 | 0.0041965 | No
4/11/2018 | 20:22:05 | R04 | Rural Long | Unknown | Unknown | 0 | 54.2503 | 0.28943 | 0 | No
4/11/2018 | 20:29:13 | SD35500 | Rural Long | Weather |  | 565 | 287 | 1.1835 | 0.0041236 | No
4/11/2018 | 21:36:16 | LX71 | Rural Long | Weather |  | 128 | 394.7031 | 0.36873 | 0.00093419 | No
4/11/2018 | 21:48:07 | CM10 | Rural Long | Unknown | Unknown | 45 | 805 | 0.26438 | 0.00032843 | No
4/11/2018 | 22:29:58 | SM350D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 965 | 0.0015427 | 1.6e-06 | No
5/11/2018 | 00:27:34 | HH107B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 73 | 147 | 0.017155 | 0.0001167 | No
5/11/2018 | 00:48:24 | AP149D | Urban | Asset failure | HV | 392 | 223 | 0.13975 | 0.00062668 | No
5/11/2018 | 01:19:50 | MV61 | Urban | Asset failure | LV | 39.3333 | 88 | 0.0055335 | 6.288e-05 | No
5/11/2018 | 02:09:22 | LM43 | Rural Long | Weather |  | 50 | 398.96 | 0.14559 | 0.00036492 | No
5/11/2018 | 06:16:01 | MG51 | Rural Long | Weather |  | 15 | 124 | 0.013575 | 0.00010948 | No
5/11/2018 | 07:30:45 | YK15 | Rural Long | Weather |  | 75 | 304.2 | 0.16651 | 0.00054738 | No
5/11/2018 | 08:30:09 | BT26 | Rural Long | Asset failure | LV | 1 | 276 | 0.0020143 | 7.3e-06 | No
5/11/2018 | 08:34:09 | MV63 | Rural Short | Planned |  | 36 | 260 | 0.069733 | 0.00026821 | No
5/11/2018 | 08:47:24 | PP12 | Rural Long | Unknown | Unknown | 31 | 127.6129 | 0.028872 | 0.00022625 | No
5/11/2018 | 09:04:16 | KI12 | Rural Long | Planned |  | 24 | 173 | 0.030303 | 0.00017516 | No
5/11/2018 | 09:25:53 | ST11 | Rural Short | Planned |  | 72 | 291 | 0.1561 | 0.00053641 | No
5/11/2018 | 09:37:43 | GA28 | Rural Long | Planned |  | 1 | 246 | 0.0017954 | 7.3e-06 | No
5/11/2018 | 09:53:45 | VH23 | Rural Short | Planned |  | 731 | 260 | 1.416 | 0.0054461 | No
5/11/2018 | 10:10:19 | MTB21 | Rural Short | Planned |  | 2 | 114 | 0.0016986 | 1.49e-05 | No
5/11/2018 | 10:15:43 | SG13 | Rural Short | Planned |  | 32 | 324 | 0.077243 | 0.0002384 | No
5/11/2018 | 12:05:35 | VH45 | Rural Short | Weather |  | 2 | 134 | 0.0019966 | 1.49e-05 | No
5/11/2018 | 13:40:38 | MG43 | Rural Short | Unknown | Unknown | 430 | 230 | 0.73682 | 0.0032036 | No
5/11/2018 | 13:45:19 | EL19 | Urban | Unknown | Unknown | 2 | 29 | 9.272e-05 | 3.2e-06 | No
5/11/2018 | 14:04:49 | PA18 | Rural Long | Asset failure | LV | 1 | 418 | 0.0030507 | 7.3e-06 | No
5/11/2018 | 14:31:48 | MTB13 | Rural Short | Planned |  | 26 | 116 | 0.02247 | 0.0001937 | No
5/11/2018 | 14:49:41 | MT06 | Rural Long | Asset failure | LV | 1 | 226 | 0.0016494 | 7.3e-06 | No
5/11/2018 | 16:42:22 | HH432C | Urban | Asset failure | LV | 73 | 245 | 0.028592 | 0.0001167 | No
5/11/2018 | 16:52:39 | MTB13 | Rural Short | Asset failure | LV | 1 | 147 | 0.0010952 | 7.45e-06 | No
5/11/2018 | 16:53:24 | HH432C | Urban | Asset failure | LV | 127 | 233 | 0.047306 | 0.00020303 | No
5/11/2018 | 17:24:16 | EL13 | Urban | Asset failure | LV | 8.6667 | 251 | 0.0034777 | 1.386e-05 | No
5/11/2018 | 17:29:28 | MT07 | Rural Long | Unknown | Unknown | 44 | 29 | 0.0093127 | 0.00032113 | No
5/11/2018 | 18:02:57 | SM349A | Urban | Asset failure | LV | 46.6666 | 27 | 0.0020143 | 7.46e-05 | No
5/11/2018 | 18:28:44 | BU03 | Rural Long | Weather |  | 47 | 351 | 0.1204 | 0.00034302 | No
5/11/2018 | 19:20:47 | SA32 | Urban | Asset failure | LV | 58 | 52 | 0.0048216 | 9.272e-05 | No
5/11/2018 | 19:28:49 | CV28 | Rural Long | Weather |  | 19 | 1079 | 0.14962 | 0.00013867 | No
5/11/2018 | 19:28:49 | CV28 | Rural Long | Weather |  | 61 | 16 | 0.0071232 | 0.0004452 | No
5/11/2018 | 20:32:15 | SM411C | Urban | Animal | Animal impact | 11 | 82 | 0.001442 | 1.759e-05 | No
5/11/2018 | 20:49:43 | SD32300 | Rural Long | Weather |  | 3 | 785 | 0.017188 | 2.19e-05 | No
5/11/2018 | 21:27:17 | CM10 | Rural Long | Unknown | Unknown | 45 | 878 | 0.28836 | 0.00032843 | No
5/11/2018 | 21:27:17 | CM10 | Rural Long | Unknown | Unknown | 13 | 907.6154 | 0.086113 | 9.488e-05 | No
5/11/2018 | 21:40:12 | SD31300 | Rural Long | Weather |  | 1177 | 252 | 2.1647 | 0.0085901 | No
5/11/2018 | 21:40:12 | SD31300 | Rural Long | Weather |  | 0 | 695 | 5.9701 | 0 | No
5/11/2018 | 23:57:28 | PA24 | Rural Long | Weather |  | 30 | 782.9 | 0.17142 | 0.00021895 | No
5/11/2018 | 23:57:28 | PA24 | Rural Long | Weather |  | 0 | 158.8 | 0.034769 | 0 | No
6/11/2018 | 00:34:07 | R04 | Rural Long | Unknown | Unknown | 575 | 201.0991 | 0.84392 | 0.0041965 | No
6/11/2018 | 01:00:51 | G31 | Rural Long | Weather |  | 55 | 751.0545 | 0.30148 | 0.00040141 | No
6/11/2018 | 02:51:13 | R18 | Rural Long | Unknown | Unknown | 12 | 408 | 0.035733 | 8.758e-05 | No
6/11/2018 | 02:57:19 | GA36 | Rural Long | Weather |  | 94 | 630.2766 | 0.4324 | 0.00068604 | No
6/11/2018 | 06:01:21 | SA520D | Urban | Unknown | Unknown | 1 | 478 | 0.00076417 | 1.6e-06 | No
6/11/2018 | 06:27:24 | BU08 | Rural Long | Weather |  | 48 | 615.5625 | 0.21564 | 0.00035032 | No
6/11/2018 | 06:42:30 | KI32 | Rural Short | Unknown | Unknown | 4 | 76 | 0.0022649 | 2.98e-05 | No
6/11/2018 | 06:44:48 | HH102D | Urban | Unknown | Unknown | 8.3333 | 187 | 0.0024913 | 1.332e-05 | No
6/11/2018 | 08:26:23 | HH341E | Urban | Asset failure | LV | 1 | 213 | 0.00034052 | 1.6e-06 | No
6/11/2018 | 08:38:04 | BM54 | Rural Short | Weather |  | 18 | 93.7222 | 0.012568 | 0.0001341 | No
6/11/2018 | 08:40:22 | SM410B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 94 | 0.0078143 | 8.313e-05 | No
6/11/2018 | 08:43:17 | AP132D | Urban | Planned |  | 86 | 294 | 0.040421 | 0.00013749 | No
6/11/2018 | 08:52:03 | MTB41 | Rural Short | Planned |  | 43 | 223 | 0.071439 | 0.00032036 | No
6/11/2018 | 08:58:12 | MV63 | Rural Short | Planned |  | 262 | 368.6756 | 0.71963 | 0.0019519 | No
6/11/2018 | 08:58:41 | SB18 | Rural Long | Planned |  | 4 | 195 | 0.0056927 | 2.919e-05 | No
6/11/2018 | 09:01:56 | HH121C | Urban | Planned |  | 134 | 302 | 0.064695 | 0.00021422 | No
6/11/2018 | 09:16:53 | SM137B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 82 | 0.00013109 | 1.6e-06 | No
6/11/2018 | 09:25:01 | BU10 | Rural Long | Unknown | Unknown | 12 | 15 | 0.0013137 | 8.758e-05 | No
6/11/2018 | 09:52:03 | G41 | Rural Long | Unknown | Unknown | 40 | 127 | 0.037076 | 0.00029193 | No
6/11/2018 | 09:55:24 | AP529A | Urban | Asset failure | LV | 25.3333 | 164 | 0.006642 | 4.05e-05 | No
6/11/2018 | 10:00:11 | MV63 | Rural Short | Planned |  | 3 | 17 | 0.00037996 | 2.235e-05 | No
6/11/2018 | 10:03:06 | SD33200 | Rural Long | Unknown | Unknown | 3 | 97 | 0.0021238 | 2.19e-05 | No
6/11/2018 | 10:10:43 | AP424F | Urban | Planned |  | 11 | 168 | 0.0029544 | 1.759e-05 | No
6/11/2018 | 10:21:21 | MTB54 | Rural Long | Asset failure | LV | 1 | 44 | 0.00032113 | 7.3e-06 | No
6/11/2018 | 10:27:49 | ST36 | Rural Long | Planned |  | 121 | 239 | 0.21106 | 0.0008831 | No
6/11/2018 | 10:40:09 | MV63 | Rural Short | Planned |  | 2 | 37 | 0.00055131 | 1.49e-05 | No
6/11/2018 | 11:30:01 | MV63 | Rural Short | Planned |  | 1 | 1 | 7.45e-06 | 7.45e-06 | No
6/11/2018 | 12:56:46 | G41 | Rural Long | Asset failure | LV | 1 | 39 | 0.00028464 | 7.3e-06 | No
6/11/2018 | 13:23:47 | SD31300 | Rural Long | Unknown | Unknown | 2 | 597 | 0.0087142 | 1.46e-05 | No
6/11/2018 | 13:30:52 | G32 | Rural Long | Unknown | Unknown | 98 | 683.551 | 0.4889 | 0.00071524 | No
6/11/2018 | 14:15:14 | HH341G | Urban | Other |  | 42.6667 | 14 | 0.00095494 | 6.821e-05 | No
6/11/2018 | 14:31:37 | G29 | Rural Long | Asset failure | HV | 77 | 883.0909 | 0.49627 | 0.00056197 | No
6/11/2018 | 14:43:05 | SD32200 | Rural Long | Unknown | Unknown | 3 | 110 | 0.0024084 | 2.19e-05 | No
6/11/2018 | 15:24:44 | HH341G | Urban | Asset failure | LV | 1 | 55 | 8.793e-05 | 1.6e-06 | No
6/11/2018 | 15:49:35 | ST35 | Rural Long | Unknown | Unknown | 35 | 36 | 0.0091959 | 0.00025544 | No
6/11/2018 | 18:06:09 | CM25 | Rural Long | Asset failure | HV | 2 | 132 | 0.0019268 | 1.46e-05 | No
6/11/2018 | 18:19:24 | MI14 | Rural Long | Asset failure | LV | 18 | 207 | 0.027194 | 0.00013137 | No
6/11/2018 | 21:24:56 | HH102D | Urban | Unknown | Unknown | 8.3333 | 62 | 0.00082598 | 1.332e-05 | No
7/11/2018 | 01:47:24 | GA09 | Rural Long | Unknown | Unknown | 144 | 4 | 0.0042038 | 0.001051 | No
7/11/2018 | 04:51:30 | HH102D | Urban | Overloads |  | 1 | 329 | 0.00052596 | 1.6e-06 | No
7/11/2018 | 05:33:57 | W06 | Rural Long | Unknown | Unknown | 312 | 350.0769 | 0.79715 | 0.0022771 | No
7/11/2018 | 05:38:50 | BM56 | Rural Short | Unknown | Unknown | 324 | 84 | 0.20276 | 0.0024138 | No
7/11/2018 | 06:35:43 | AP149E | Urban | Animal | Animal impact | 2027 | 73.148 | 0.23704 | 0.0032405 | No
7/11/2018 | 06:58:14 | G01 | Rural Long | Overloads |  | 1 | 667 | 0.004868 | 7.3e-06 | No
7/11/2018 | 07:26:56 | MG52 | Rural Short | Animal | Animal impact | 1 | 69 | 0.00051406 | 7.45e-06 | No
7/11/2018 | 07:27:05 | VH11 | Urban | Asset failure | LV | 1 | 127 | 0.00020303 | 1.6e-06 | No
7/11/2018 | 07:50:47 | SM172B | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
7/11/2018 | 08:46:21 | MV53 | Rural Short | Planned |  | 14 | 99 | 0.010326 | 0.0001043 | No
7/11/2018 | 08:55:04 | MG17 | Rural Long | Planned |  | 1 | 147 | 0.0010729 | 7.3e-06 | No
7/11/2018 | 09:01:21 | KA01 | Rural Short | Planned |  | 17 | 347 | 0.043948 | 0.00012665 | No
7/11/2018 | 09:15:46 | VH17 | Rural Short | Planned |  | 4 | 95 | 0.0028311 | 2.98e-05 | No
7/11/2018 | 09:28:49 | ST35 | Rural Long | Planned |  | 10 | 165 | 0.012042 | 7.298e-05 | No
7/11/2018 | 09:36:52 | W30 | Rural Short | Weather |  | 63 | 434.0159 | 0.20371 | 0.00046936 | No
7/11/2018 | 09:37:46 | SA19 | Urban | Planned |  | 63 | 286 | 0.028805 | 0.00010072 | No
7/11/2018 | 09:38:08 | WK51 | Rural Short | Planned |  | 6 | 180 | 0.0080462 | 4.47e-05 | No
7/11/2018 | 09:46:58 | MB43 | Rural Long | Planned |  | 3 | 209 | 0.0045761 | 2.19e-05 | No
7/11/2018 | 09:55:21 | HH121G | Urban | Planned |  | 149 | 146 | 0.034778 | 0.0002382 | No
7/11/2018 | 09:59:28 | HH121B | Urban | Planned |  | 17 | 168 | 0.0045658 | 2.718e-05 | No
7/11/2018 | 10:09:26 | VH72 | Rural Short | Planned |  | 75 | 285 | 0.15925 | 0.00055876 | No
7/11/2018 | 10:29:09 | HH341G | Urban | Planned |  | 2038 | 26 | 0.084711 | 0.0032581 | No
7/11/2018 | 10:41:06 | MG05 | Rural Long | Unknown | Unknown | 1194 | 4.005 | 0.034901 | 0.0087142 | No
7/11/2018 | 10:52:26 | MV41 | Rural Short | Planned |  | 1 | 37 | 0.00027566 | 7.45e-06 | No
7/11/2018 | 12:16:16 | MT25 | Rural Long | Weather |  | 2 | 167 | 0.0024376 | 1.46e-05 | No
7/11/2018 | 13:31:14 | NL234C | Urban | Asset failure | HV | 2623 | 54.8101 | 0.22984 | 0.0041933 | No
7/11/2018 | 14:03:34 | CM11 | Rural Long | Planned |  | 24 | 76 | 0.013312 | 0.00017516 | No
7/11/2018 | 15:33:36 | SA711C | Urban | Vegetation | Grow-in - NSP responsibility | 19.3333 | 34 | 0.0010509 | 3.091e-05 | No
7/11/2018 | 15:39:46 | VH23 | Rural Short | Asset failure | LV | 4.6667 | 27 | 0.00093872 | 3.477e-05 | No
7/11/2018 | 16:11:36 | MTB52 | Rural Long | Asset failure | LV | 3.3333 | 112 | 0.0027247 | 2.433e-05 | No
7/11/2018 | 16:48:34 | HH130B | Urban | Overloads |  | 1 | 232 | 0.00037089 | 1.6e-06 | No
7/11/2018 | 17:43:45 | HH145C | Urban | Asset failure | LV | 1 | 220 | 0.00035171 | 1.6e-06 | No
7/11/2018 | 17:59:29 | HH145B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 18.6666 | 96 | 0.0028648 | 2.984e-05 | No
8/11/2018 | 02:30:01 | HH409D | Urban | Unknown | Unknown | 174 | 126.2759 | 0.035126 | 0.00027817 | No
8/11/2018 | 06:44:52 | M73 | Rural Long | Unknown | Unknown | 24 | 394.8333 | 0.069159 | 0.00017516 | No
8/11/2018 | 07:08:17 | WHY01 | Urban | Asset failure | LV | 1 | 118 | 0.00018864 | 1.6e-06 | No
8/11/2018 | 08:31:01 | MV15 | Rural Short | Planned |  | 15 | 306 | 0.034196 | 0.00011175 | No
8/11/2018 | 08:44:28 | ST36 | Rural Long | Planned |  | 34 | 311 | 0.077173 | 0.00024814 | No
8/11/2018 | 08:52:25 | KI54 | Rural Long | Planned |  | 7 | 148 | 0.0075611 | 5.109e-05 | No
8/11/2018 | 09:01:31 | GA22 | Rural Short | Planned |  | 24 | 342 | 0.061151 | 0.0001788 | No
8/11/2018 | 09:06:14 | VH15 | Rural Short | Planned |  | 215 | 380 | 0.60868 | 0.0016018 | No
8/11/2018 | 09:19:37 | AP125D | Urban | Planned |  | 521 | 319 | 0.2657 | 0.00083291 | No
8/11/2018 | 09:27:48 | AP424B | Urban | Planned |  | 145 | 345 | 0.079974 | 0.00023181 | No
8/11/2018 | 09:28:39 | MV63 | Rural Short | Planned |  | 46 | 281 | 0.096301 | 0.00034271 | No
8/11/2018 | 09:28:46 | ST21 | Rural Short | Planned |  | 31 | 143 | 0.033027 | 0.00023095 | No
8/11/2018 | 09:28:54 | SM350E | Urban | Asset failure | LV | 2 | 139 | 0.00044443 | 3.2e-06 | No
8/11/2018 | 09:29:33 | AP424B | Urban | Overloads |  | 1.3333 | 76 | 0.000162 | 2.13e-06 | No
8/11/2018 | 09:30:11 | MI28 | Rural Long | Planned |  | 6 | 120 | 0.0052548 | 4.379e-05 | No
8/11/2018 | 09:37:22 | AP424B | Urban | Overloads |  | 1 | 66 | 0.00010551 | 1.6e-06 | No
8/11/2018 | 09:37:41 | GU32 | Rural Long | Planned |  | 39 | 247 | 0.070305 | 0.00028464 | No
8/11/2018 | 09:54:07 | SA19 | Urban | Planned |  | 20 | 160 | 0.0051158 | 3.197e-05 | No
8/11/2018 | 09:54:30 | GA52 | Rural Long | Planned |  | 60 | 329 | 0.14407 | 0.0004379 | No
8/11/2018 | 10:03:34 | PP05 | Rural Long | Planned |  | 56 | 290 | 0.11853 | 0.00040871 | No
8/11/2018 | 10:06:56 | SG07 | Rural Short | Planned |  | 5 | 325 | 0.012106 | 3.725e-05 | No
8/11/2018 | 10:08:52 | MV32 | Rural Short | Planned |  | 1 | 242 | 0.0018029 | 7.45e-06 | No
8/11/2018 | 10:18:11 | CN25 | Rural Long | Planned |  | 88 | 358 | 0.22993 | 0.00064225 | No
8/11/2018 | 10:22:35 | MV33 | Rural Short | Weather |  | 4.3333 | 122 | 0.0039387 | 3.228e-05 | No
8/11/2018 | 11:22:45 | AP424F | Urban | Planned |  | 101 | 252 | 0.040689 | 0.00016147 | No
8/11/2018 | 11:59:55 | SD32300 | Rural Long | Unknown | Unknown | 2 | 140 | 0.0020435 | 1.46e-05 | No
8/11/2018 | 12:13:18 | ST22 | Rural Short | Animal | Animal impact | 4 | 199 | 0.0059303 | 2.98e-05 | No
8/11/2018 | 12:13:57 | ST22 | Rural Short | Unknown | Unknown | 4 | 164 | 0.0048873 | 2.98e-05 | No
8/11/2018 | 13:14:52 | WHY06 | Urban | Third Party | Vehicle impact | 5 | 84 | 0.00067144 | 7.99e-06 | No
8/11/2018 | 14:07:58 | SM350F | Urban | Asset failure | LV | 25.3333 | 53 | 0.0021465 | 4.05e-05 | No
8/11/2018 | 14:09:25 | KA03 | Rural Long | Asset failure | LV | 14 | 34 | 0.003474 | 0.00010218 | No
8/11/2018 | 14:59:14 | KI11 | Rural Long | Third Party | Vehicle impact | 1 | 124 | 0.00090499 | 7.3e-06 | No
8/11/2018 | 15:03:42 | HH102D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 248 | 0.00039647 | 1.6e-06 | No
8/11/2018 | 16:22:01 | HH409C | Urban | Asset failure | LV | 86 | 85 | 0.011686 | 0.00013749 | No
8/11/2018 | 19:29:16 | SD35200 | Rural Long | Unknown | Unknown | 3 | 121 | 0.0026493 | 2.19e-05 | No
8/11/2018 | 22:54:31 | HH177G | Urban | Asset failure | LV | 64 | 91 | 0.0093107 | 0.00010232 | No
9/11/2018 | 04:11:38 | MT19 | Rural Long | Asset failure | LV | 2 | 337 | 0.0049191 | 1.46e-05 | No
9/11/2018 | 05:28:07 | HH145A | Urban | Animal | Animal impact | 738 | 143 | 0.16871 | 0.0011798 | No
9/11/2018 | 05:29:34 | NL115E | Urban | Unknown | Unknown | 9.3333 | 188 | 0.0028051 | 1.492e-05 | No
9/11/2018 | 08:36:58 | AP365A | Urban | Planned |  | 52 | 325 | 0.027018 | 8.313e-05 | No
9/11/2018 | 08:40:43 | WHY06 | Urban | Planned |  | 26 | 108 | 0.0044891 | 4.157e-05 | No
9/11/2018 | 08:46:28 | MV61 | Urban | Asset failure | LV | 1 | 540 | 0.00086328 | 1.6e-06 | No
9/11/2018 | 08:48:30 | VH15 | Rural Short | Planned |  | 16 | 284 | 0.033853 | 0.0001192 | No
9/11/2018 | 08:54:44 | MTB22 | Rural Short | Planned |  | 19 | 79 | 0.011183 | 0.00014155 | No
9/11/2018 | 09:00:52 | PA02 | Urban | Planned |  | 103 | 295 | 0.048576 | 0.00016466 | No
9/11/2018 | 09:03:18 | SG07 | Rural Short | Planned |  | 23 | 34 | 0.005826 | 0.00017135 | No
9/11/2018 | 09:12:39 | VH22 | Rural Short | Asset failure | LV | 1 | 175 | 0.0013038 | 7.45e-06 | No
9/11/2018 | 09:15:26 | EL12 | Urban | Planned |  | 29 | 318 | 0.014743 | 4.636e-05 | No
9/11/2018 | 09:18:05 | AP146C | Urban | Planned |  | 59 | 360 | 0.033956 | 9.432e-05 | No
9/11/2018 | 09:20:00 | YK23 | Rural Long | Planned |  | 1 | 48 | 0.00035032 | 7.3e-06 | No
9/11/2018 | 09:20:26 | MV53 | Rural Short | Planned |  | 59 | 268 | 0.1178 | 0.00043956 | No
9/11/2018 | 09:22:05 | AP365A / AP139A | Urban | Planned |  | 157 | 67.121 | 0.016847 | 0.00025099 | No
9/11/2018 | 09:26:27 | KI53 | Rural Long | Planned |  | 2 | 286 | 0.0041747 | 1.46e-05 | No
9/11/2018 | 09:28:40 | MV33 | Rural Short | Planned |  | 5 | 144 | 0.0053641 | 3.725e-05 | No
9/11/2018 | 09:33:48 | BT14 | Rural Long | Overloads |  | 2 | 1625 | 0.02372 | 1.46e-05 | No
9/11/2018 | 09:36:22 | MTB63 | Rural Short | Planned |  | 5 | 257 | 0.0095734 | 3.725e-05 | No
9/11/2018 | 09:36:54 | AP149B | Urban | Planned |  | 20 | 108 | 0.0034531 | 3.197e-05 | No
9/11/2018 | 09:39:50 | NL111Q | Urban | Asset failure | LV | 39 | 124 | 0.0077312 | 6.235e-05 | No
9/11/2018 | 09:43:39 | MTB54 | Rural Long | Planned |  | 12 | 166 | 0.014538 | 8.758e-05 | No
9/11/2018 | 09:50:13 | GU42 | Rural Long | Planned |  | 7 | 294 | 0.01502 | 5.109e-05 | No
9/11/2018 | 09:59:51 | SD38200 | Rural Long | Planned |  | 15 | 182 | 0.019924 | 0.00010948 | No
9/11/2018 | 10:06:16 | HH177E | Urban | Planned |  | 155 | 260 | 0.064427 | 0.00024779 | No
9/11/2018 | 10:14:01 | CN53 | Rural Long | Planned |  | 1 | 66 | 0.00048169 | 7.3e-06 | No
9/11/2018 | 10:18:58 | SM411E | Urban | Planned |  | 2 | 191 | 0.00061069 | 3.2e-06 | No
9/11/2018 | 10:19:44 | MV15 | Rural Short | Planned |  | 1 | 201 | 0.0014975 | 7.45e-06 | No
9/11/2018 | 10:48:00 | AP424F | Urban | Asset failure | HV | 533 | 2 | 0.0017042 | 0.00085209 | No
9/11/2018 | 10:48:00 | EL23 | Urban | Planned |  | 2 | 280 | 0.00089526 | 3.2e-06 | No
9/11/2018 | 11:11:01 | MG14 | Rural Long | Planned |  | 15 | 89 | 0.0097433 | 0.00010948 | No
9/11/2018 | 12:14:02 | HH177F | Urban | Planned |  | 1 | 56 | 8.953e-05 | 1.6e-06 | No
9/11/2018 | 12:50:54 | G15 | Rural Long | Overloads |  | 2 | 90 | 0.0013137 | 1.46e-05 | No
9/11/2018 | 13:35:26 | SM350B | Urban | Asset failure | LV | 13.6667 | 129 | 0.0028185 | 2.185e-05 | No
9/11/2018 | 14:22:15 | HH177G | Urban | Overloads |  | 1 | 415 | 0.00066345 | 1.6e-06 | No
9/11/2018 | 14:58:26 | EL12 | Urban | Unknown | Unknown | 4 | 170 | 0.0010871 | 6.39e-06 | No
9/11/2018 | 16:13:46 | MG34 | Rural Long | Weather |  | 1 | 142 | 0.0010364 | 7.3e-06 | No
9/11/2018 | 17:45:03 | SM410B | Urban | Overloads |  | 31 | 92 | 0.0045594 | 4.956e-05 | No
9/11/2018 | 20:23:44 | SM350G | Urban | Asset failure | LV | 15.3333 | 87 | 0.0021326 | 2.451e-05 | No
9/11/2018 | 22:21:28 | MB82 | Rural Long | Unknown | Unknown | 44 | 236 | 0.075786 | 0.00032113 | No
10/11/2018 | 07:09:24 | AP365A | Urban | Asset failure | LV | 21.3333 | 179 | 0.0061048 | 3.411e-05 | No
10/11/2018 | 07:39:37 | G07 | Rural Long | Asset failure | HV | 2 | 324 | 0.0047293 | 1.46e-05 | No
10/11/2018 | 08:45:04 | ST11 | Rural Short | Animal | Animal impact | 1 | 220 | 0.001639 | 7.45e-06 | No
10/11/2018 | 09:55:57 | HH148C | Urban | Other |  | 34 | 48 | 0.002609 | 5.435e-05 | No
10/11/2018 | 10:00:12 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 82 | 0.00061091 | 7.45e-06 | No
10/11/2018 | 11:07:27 | BT14 | Rural Long | Asset failure | HV | 1 | 31 | 0.00022625 | 7.3e-06 | No
10/11/2018 | 15:46:19 | CM29 | Rural Long | Unknown | Unknown | 64 | 223 | 0.10416 | 0.00046709 | No
10/11/2018 | 17:53:34 | BM54 | Rural Short | Animal | Animal impact | 34 | 89 | 0.022544 | 0.00025331 | No
10/11/2018 | 18:50:47 | PL04 | Urban | Unknown | Unknown | 19 | 158 | 0.0047992 | 3.037e-05 | No
10/11/2018 | 19:59:04 | CN76 | Rural Long | Unknown | Unknown | 74 | 175.8514 | 0.094973 | 0.00054008 | No
10/11/2018 | 23:23:10 | HH177F | Urban | Other |  | 2 | 649 | 0.0020751 | 3.2e-06 | No
11/11/2018 | 06:15:23 | GU41 | Rural Long | Unknown | Unknown | 4 | 219 | 0.0063933 | 2.919e-05 | No
11/11/2018 | 07:43:42 | HH121A | Urban | Other |  | 1 | 190 | 0.00030375 | 1.6e-06 | No
11/11/2018 | 08:22:24 | SA520H | Urban | Planned |  | 3 | 210 | 0.0010072 | 4.8e-06 | No
11/11/2018 | 08:54:21 | SA19 | Urban | Planned |  | 2 | 360 | 0.0011511 | 3.2e-06 | No
11/11/2018 | 09:12:02 | VH34 | Rural Short | Planned |  | 15 | 135 | 0.015087 | 0.00011175 | No
11/11/2018 | 09:45:52 | MTB54 | Rural Long | Planned |  | 17 | 264 | 0.032755 | 0.00012407 | No
11/11/2018 | 10:24:36 | KI15 | Rural Long | Third Party | Vehicle impact | 60 | 451.9333 | 0.1979 | 0.0004379 | No
11/11/2018 | 10:43:07 | SG13 | Rural Short | Asset failure | LV | 1 | 74 | 0.00055131 | 7.45e-06 | No
11/11/2018 | 11:38:00 | WK72 | Rural Short | Unknown | Unknown | 1 | 19 | 0.00014155 | 7.45e-06 | No
11/11/2018 | 12:30:38 | SB01 | Rural Long | Unknown | Unknown | 10 | 42 | 0.0030653 | 7.298e-05 | No
11/11/2018 | 13:17:56 | NL451D | Urban | Asset failure | LV | 1 | 183 | 0.00029256 | 1.6e-06 | No
11/11/2018 | 14:13:31 | EL10 | Urban | Animal | Animal impact | 1 | 625 | 0.00099917 | 1.6e-06 | No
11/11/2018 | 15:22:01 | SD49100 | Urban | 5 - STPIS Exclusion (3.3)(a) |  | 4357 | 19.8901 | 0.13854 | 0.0069654 | No
11/11/2018 | 15:22:01 | SD49100 | Rural Short | 5 - STPIS Exclusion (3.3)(a) |  | 11893 | 21.1233 | 1.8716 | 0.088605 | No
11/11/2018 | 15:22:01 | SD49100 | Rural Long | 5 - STPIS Exclusion (3.3)(a) |  | 10705 | 23.752 | 1.8557 | 0.078129 | No
11/11/2018 | 19:16:33 | SM374B | Urban | Vegetation | Grow-in - NSP responsibility | 24.6666 | 32 | 0.0012619 | 3.943e-05 | No
11/11/2018 | 19:35:09 | SM410B | Urban | Asset failure | LV | 48 | 123 | 0.0094386 | 7.674e-05 | No
12/11/2018 | 05:53:25 | MTB13 | Rural Short | Unknown | Unknown | 20 | 166 | 0.024734 | 0.000149 | No
12/11/2018 | 09:02:45 | MV22 | Rural Short | Planned |  | 26 | 93 | 0.018014 | 0.0001937 | No
12/11/2018 | 09:03:20 | CV29 | Rural Long | Planned |  | 14 | 292 | 0.029836 | 0.00010218 | No
12/11/2018 | 09:15:55 | AP132D | Urban | Planned |  | 112 | 203 | 0.036347 | 0.00017905 | No
12/11/2018 | 09:16:35 | EL18 | Urban | Planned |  | 18 | 197 | 0.0056689 | 2.878e-05 | No
12/11/2018 | 09:18:44 | GA19 | Rural Long | Planned |  | 57 | 169 | 0.070305 | 0.00041601 | No
12/11/2018 | 09:25:48 | BT02 | Rural Long | Planned |  | 15 | 264 | 0.028901 | 0.00010948 | No
12/11/2018 | 09:29:35 | MTB14 | Rural Short | Planned |  | 63 | 308 | 0.14456 | 0.00046936 | No
12/11/2018 | 09:31:35 | ST35 | Rural Long | Planned |  | 7 | 158 | 0.008072 | 5.109e-05 | No
12/11/2018 | 09:54:17 | MV53 | Rural Short | Planned |  | 24 | 253 | 0.045237 | 0.0001788 | No
12/11/2018 | 11:29:56 | SD32200 | Rural Long | Planned |  | 2 | 37 | 0.00054008 | 1.46e-05 | No
12/11/2018 | 13:13:31 | SD32200 | Rural Long | Unknown | Unknown | 2 | 23 | 0.00033572 | 1.46e-05 | No
12/11/2018 | 13:53:15 | SM374A | Urban | Unknown | Unknown | 40 | 36 | 0.0023021 | 6.395e-05 | No
12/11/2018 | 13:58:13 | SA32 | Urban | Asset failure | LV | 62 | 63 | 0.0062444 | 9.912e-05 | No
12/11/2018 | 14:18:25 | CL07 | Rural Long | Asset failure | HV | 58 | 191.4828 | 0.081055 | 0.0004233 | No
12/11/2018 | 15:41:07 | LM41 | Rural Long | Asset failure | LV | 6.6667 | 204 | 0.0099257 | 4.866e-05 | No
12/11/2018 | 15:54:26 | HH145E | Urban | Planned |  | 44 | 104 | 0.0073155 | 7.034e-05 | No
12/11/2018 | 16:35:38 | CBD366Q-GG2-outer | CBD | Asset failure | HV | 2 | 165 | 0.064059 | 0.00038824 | No
12/11/2018 | 16:35:38 | CBD366Q-GG2-outer | Urban | Asset failure | HV | 789 | 158 | 0.19929 | 0.0012614 | No
12/11/2018 | 17:16:33 | HH107A | Urban | Other |  | 86 | 204 | 0.028047 | 0.00013749 | No
12/11/2018 | 17:30:16 | MG03 | Rural Short | Unknown | Unknown | 4 | 35 | 0.001043 | 2.98e-05 | No
12/11/2018 | 17:32:44 | HH107A | Urban | Other |  | 87 | 186 | 0.02587 | 0.00013908 | No
12/11/2018 | 17:56:00 | GA745B | Rural Short | Unknown | Unknown | 445 | 5.1169 | 0.016964 | 0.0033153 | No
12/11/2018 | 18:30:07 | NL111Q | Urban | Asset failure | LV | 73 | 60 | 0.0070022 | 0.0001167 | No
12/11/2018 | 18:40:51 | MV34 | Rural Short | Asset failure | LV | 12 | 214 | 0.019132 | 8.94e-05 | No
12/11/2018 | 20:08:48 | AP424F | Urban | Asset failure | HV | 1334 | 70.7916 | 0.15097 | 0.0021326 | No
12/11/2018 | 20:08:48 | AP424F | Urban | Asset failure | HV | 0 | 2 | 0.0017042 | 0 | No
13/11/2018 | 04:07:01 | W06 | Rural Long | Asset failure | HV | 312 | 433.3846 | 0.98685 | 0.0022771 | No
13/11/2018 | 06:06:39 | ST12 | Rural Short | Asset failure | HV | 19 | 185 | 0.026187 | 0.00014155 | No
13/11/2018 | 06:34:10 | EL20 | Urban | Third Party | Vehicle impact | 467 | 182.2634 | 0.13607 | 0.00074658 | No
13/11/2018 | 06:46:20 | W23 | Rural Long | Unknown | Unknown | 47 | 385 | 0.13206 | 0.00034302 | No
13/11/2018 | 08:03:38 | NL210A | Urban | Planned |  | 16 | 385 | 0.0098478 | 2.558e-05 | No
13/11/2018 | 08:17:13 | CN25 | Rural Long | Asset failure | HV | 88 | 521.6932 | 0.33506 | 0.00064225 | No
13/11/2018 | 08:30:39 | YK03 | Rural Long | Planned |  | 100 | 236 | 0.17224 | 0.00072983 | No
13/11/2018 | 09:15:04 | SD39200 | Rural Long | Planned |  | 21 | 267 | 0.040922 | 0.00015327 | No
13/11/2018 | 09:20:24 | CV29 | Rural Long | Planned |  | 22 | 347 | 0.055716 | 0.00016056 | No
13/11/2018 | 09:25:08 | CL09 | Rural Long | Unknown | Unknown | 2 | 113 | 0.0016494 | 1.46e-05 | No
13/11/2018 | 09:25:14 | MI05 | Rural Long | Planned |  | 49 | 154 | 0.055073 | 0.00035762 | No
13/11/2018 | 09:43:54 | VH72 | Rural Short | Planned |  | 105 | 302 | 0.23624 | 0.00078227 | No
13/11/2018 | 10:19:20 | EL15 | Urban | Planned |  | 22 | 122 | 0.0042908 | 3.517e-05 | No
13/11/2018 | 10:33:41 | MV14 | Rural Short | Planned |  | 99 | 316 | 0.23307 | 0.00073756 | No
13/11/2018 | 11:48:31 | SG14 | Rural Short | Planned |  | 106 | 149 | 0.11767 | 0.00078972 | No
13/11/2018 | 11:53:38 | MT06 | Rural Long | Unknown | Unknown | 43 | 6 | 0.001883 | 0.00031383 | No
13/11/2018 | 13:00:37 | ST24 | Rural Short | Asset failure | LV | 2 | 82 | 0.0012218 | 1.49e-05 | No
13/11/2018 | 13:38:53 | HH177E | Urban | Asset failure | LV | 66 | 71 | 0.0074914 | 0.00010551 | No
13/11/2018 | 13:39:59 | MV42 | Rural Short | Asset failure | LV | 1 | 55 | 0.00040976 | 7.45e-06 | No
13/11/2018 | 13:51:07 | AP125C | Urban | Planned |  | 209 | 55 | 0.018377 | 0.00033412 | No
13/11/2018 | 14:11:25 | MT17 | Rural Short | Unknown | Unknown | 76 | 6 | 0.0033973 | 0.00056621 | No
13/11/2018 | 14:11:41 | HH409E | Urban | Asset failure | LV | 1 | 407 | 0.00065066 | 1.6e-06 | No
13/11/2018 | 14:37:44 | EL19 | Urban | Unknown | Unknown | 88 | 73 | 0.01027 | 0.00014068 | No
13/11/2018 | 15:40:25 | SA744D | Urban | Asset failure | HV | 4999 | 20.786 | 0.16612 | 0.0079918 | No
13/11/2018 | 16:16:32 | SA14 | Urban | Asset failure | LV | 134 | 156 | 0.033419 | 0.00021422 | No
13/11/2018 | 16:17:03 | SA13 | Urban | Asset failure | LV | 50 | 156 | 0.01247 | 7.993e-05 | No
13/11/2018 | 20:07:21 | GU11 | Rural Long | Unknown | Unknown | 1.3333 | 215 | 0.0020922 | 9.73e-06 | No
13/11/2018 | 21:31:01 | WHY08 | Urban | Asset failure | HV | 20.6667 | 262 | 0.0086563 | 3.304e-05 | No
13/11/2018 | 21:35:32 | SM411E | Urban | Asset failure | LV | 10 | 166 | 0.0026538 | 1.599e-05 | No
13/11/2018 | 21:42:13 | SM374A | Urban | Asset failure | LV | 102 | 81 | 0.013208 | 0.00016306 | No
14/11/2018 | 00:23:48 | HH432D | Urban | Planned |  | 10 | 284 | 0.0045402 | 1.599e-05 | No
14/11/2018 | 03:17:04 | VH33 | Rural Short | Weather |  | 134 | 357.2164 | 0.35662 | 0.00099832 | No
14/11/2018 | 06:09:51 | EL19 | Urban | Animal | Animal impact | 36 | 187 | 0.010762 | 5.755e-05 | No
14/11/2018 | 06:57:36 | CN03 | Rural Long | Asset failure | HV | 51 | 487 | 0.18127 | 0.00037222 | No
14/11/2018 | 06:59:31 | GU11 | Rural Long | Unknown | Unknown | 2 | 246 | 0.0035908 | 1.46e-05 | No
14/11/2018 | 07:15:42 | SG10 | Rural Short | Asset failure | LV | 1 | 141 | 0.0010505 | 7.45e-06 | No
14/11/2018 | 08:18:14 | KI31 | Rural Short | Planned |  | 3 | 202.3333 | 0.0045222 | 2.235e-05 | No
14/11/2018 | 08:35:47 | MG52 | Rural Short | Unknown | Unknown | 22 | 76 | 0.012457 | 0.0001639 | No
14/11/2018 | 08:51:33 | MV13 | Rural Short | Planned |  | 9 | 169 | 0.011332 | 6.705e-05 | No
14/11/2018 | 08:52:16 | AP125C | Urban | Planned |  | 92 | 318 | 0.046771 | 0.00014708 | No
14/11/2018 | 08:55:01 | MTB51 | Rural Long | Planned |  | 37 | 311 | 0.083982 | 0.00027004 | No
14/11/2018 | 09:08:20 | KA28 | Rural Long | Planned |  | 33 | 184 | 0.044316 | 0.00024085 | No
14/11/2018 | 09:11:00 | GA04 | Rural Long | Planned |  | 1 | 49 | 0.00035762 | 7.3e-06 | No
14/11/2018 | 09:16:35 | VH34 | Rural Short | Asset failure | LV | 3 | 306 | 0.0068392 | 2.235e-05 | No
14/11/2018 | 09:31:53 | MTB54 | Rural Long | Planned |  | 81 | 464 | 0.2743 | 0.00059117 | No
14/11/2018 | 09:33:51 | CV29 | Rural Long | Planned |  | 8 | 308 | 0.017983 | 5.839e-05 | No
14/11/2018 | 09:35:50 | MT01 | Rural Long | Planned |  | 2 | 50 | 0.00072983 | 1.46e-05 | No
14/11/2018 | 09:51:08 | HH177E | Urban | Planned |  | 49 | 204 | 0.01598 | 7.834e-05 | No
14/11/2018 | 09:52:37 | EL11 | Urban | Planned |  | 42 | 142 | 0.0095345 | 6.714e-05 | No
14/11/2018 | 10:07:42 | MTB14 | Rural Short | Planned |  | 49 | 161 | 0.058774 | 0.00036506 | No
14/11/2018 | 10:10:36 | VH15 | Rural Short | Asset failure | LV | 1 | 182 | 0.0013559 | 7.45e-06 | No
14/11/2018 | 10:22:43 | SG03 | Rural Short | Planned |  | 61 | 204 | 0.09271 | 0.00045446 | No
14/11/2018 | 10:22:59 | VH22 | Rural Short | Planned |  | 341 | 103.261 | 0.26233 | 0.0025405 | No
14/11/2018 | 10:44:07 | MG45 | Urban | Asset failure | HV | 705.3337 | 7.3819 | 0.0083238 | 0.0011276 | No
14/11/2018 | 11:25:33 | MT20 | Rural Long | Planned |  | 1 | 192 | 0.0014013 | 7.3e-06 | No
14/11/2018 | 12:04:59 | MV13 | Rural Short | Planned |  | 9 | 101 | 0.0067722 | 6.705e-05 | No
14/11/2018 | 12:10:42 | MV13 | Rural Short | Planned |  | 4 | 167 | 0.0049767 | 2.98e-05 | No
14/11/2018 | 14:16:18 | HH121D | Urban | Planned |  | 58 | 106 | 0.0098286 | 9.272e-05 | No
14/11/2018 | 14:25:16 | MV13 | Rural Short | Unknown | Unknown | 2 | 253 | 0.0037698 | 1.49e-05 | No
14/11/2018 | 14:43:41 | HH409D | Urban | Planned |  | 161 | 1 | 0.00025739 | 0.00025739 | No
14/11/2018 | 14:45:15 | GA02 | Rural Short | Third Party | Other | 1638 | 61 | 0.7444 | 0.012203 | No
14/11/2018 | 15:11:09 | HH145D | Urban | Overloads |  | 56 | 178 | 0.015936 | 8.953e-05 | No
15/11/2018 | 00:26:06 | GA08 | Rural Long | Unknown | Unknown | 44.3333 | 183 | 0.059211 | 0.00032356 | No
15/11/2018 | 00:29:43 | GA08 | Rural Long | Unknown | Unknown | 44.3333 | 189 | 0.061153 | 0.00032356 | No
15/11/2018 | 05:58:29 | VH15 | Rural Short | Weather |  | 25 | 241 | 0.044887 | 0.00018625 | No
15/11/2018 | 07:54:29 | LX41 | Rural Short | Unknown | Unknown | 4 | 184 | 0.0054833 | 2.98e-05 | No
15/11/2018 | 08:02:08 | R04 | Rural Long | Third Party | Other | 5 | 308 | 0.011239 | 3.649e-05 | No
15/11/2018 | 08:18:40 | NL210A | Urban | Planned |  | 16 | 426 | 0.010897 | 2.558e-05 | No
15/11/2018 | 08:20:04 | GU11 | Rural Long | Planned |  | 11 | 352 | 0.028259 | 8.028e-05 | No
15/11/2018 | 08:20:07 | CL01 | Rural Long | Third Party | Vehicle impact | 358 | 362.3659 | 0.94679 | 0.0026128 | No
15/11/2018 | 08:32:26 | MTB13 | Rural Short | Planned |  | 456 | 366 | 1.2434 | 0.0033973 | No
15/11/2018 | 08:33:25 | ST41 | Rural Long | Planned |  | 23 | 368 | 0.061773 | 0.00016786 | No
15/11/2018 | 08:35:09 | YK03 | Rural Long | Planned |  | 165 | 344 | 0.41425 | 0.0012042 | No
15/11/2018 | 08:35:40 | MTB61 | Rural Short | Planned |  | 11 | 225 | 0.018439 | 8.195e-05 | No
15/11/2018 | 09:01:51 | HH130F | Urban | Planned |  | 101 | 130 | 0.020991 | 0.00016147 | No
15/11/2018 | 09:05:57 | MG32 | Rural Long | Planned |  | 21 | 202 | 0.03096 | 0.00015327 | No
15/11/2018 | 09:14:55 | SD32200 | Rural Long | Unknown | Unknown | 210 | 308 | 0.47206 | 0.0015326 | No
15/11/2018 | 09:15:59 | CV29 | Rural Long | Planned |  | 16 | 352 | 0.041104 | 0.00011677 | No
15/11/2018 | 09:17:36 | SB18 | Rural Long | Planned |  | 7 | 242 | 0.012363 | 5.109e-05 | No
15/11/2018 | 09:28:13 | MV63 | Rural Short | Planned |  | 29 | 262 | 0.056606 | 0.00021605 | No
15/11/2018 | 09:49:44 | VH33 | Rural Short | Planned |  | 81 | 281 | 0.16957 | 0.00060346 | No
15/11/2018 | 11:53:06 | HH177F | Urban | Third Party | Vehicle impact | 53 | 93 | 0.0078799 | 8.473e-05 | No
15/11/2018 | 12:46:06 | SSD340 | Rural Short | Animal | Animal impact | 7937 | 64 | 3.7844 | 0.059132 | No
15/11/2018 | 13:55:05 | HH496D | Urban | Asset failure | HV | 275 | 2 | 0.00087927 | 0.00043964 | No
15/11/2018 | 14:00:57 | MTB82 | Rural Short | Planned |  | 2 | 28 | 0.00041721 | 1.49e-05 | No
15/11/2018 | 15:48:37 | MG29 | Rural Long | Asset failure | LV | 1 | 230 | 0.0016786 | 7.3e-06 | No
15/11/2018 | 16:04:55 | NL760B | Urban | Overloads |  | 1 | 214 | 0.00034212 | 1.6e-06 | No
15/11/2018 | 18:13:03 | SD33200 | Rural Long | Asset failure | Subtransmission | 23 | 256 | 0.042973 | 0.00016786 | No
15/11/2018 | 20:46:58 | MG41 | Urban | Third Party | Vehicle impact | 1730 | 8.6318 | 0.023873 | 0.0027657 | No
15/11/2018 | 23:03:15 | SA19 | Urban | Planned |  | 65 | 362 | 0.037617 | 0.00010391 | No
16/11/2018 | 00:01:40 | HH386E | Urban | Asset failure | LV | 25 | 220 | 0.0087927 | 3.997e-05 | No
16/11/2018 | 00:45:02 | HH386E | Urban | Asset failure | LV | 12 | 163 | 0.003127 | 1.918e-05 | No
16/11/2018 | 04:09:08 | MTB21 | Rural Short | Unknown | Unknown | 23 | 299 | 0.051235 | 0.00017135 | No
16/11/2018 | 04:23:54 | GA01 | Urban | Unknown | Unknown | 20 | 454 | 0.014516 | 3.197e-05 | No
16/11/2018 | 05:33:36 | EL07 | Urban | Asset failure | LV | 1 | 243 | 0.00038848 | 1.6e-06 | No
16/11/2018 | 06:28:39 | WK65 | Rural Short | Asset failure | LV | 1 | 406 | 0.0030248 | 7.45e-06 | No
16/11/2018 | 07:50:44 | ST24 | Rural Short | Planned |  | 20 | 64 | 0.0095362 | 0.000149 | No
16/11/2018 | 08:30:46 | ST11 | Rural Short | Planned |  | 141 | 386 | 0.40548 | 0.0010505 | No
16/11/2018 | 08:45:00 | KI31 | Rural Short | Planned |  | 4 | 295 | 0.0087912 | 2.98e-05 | No
16/11/2018 | 08:47:49 | KA22 | Rural Long | Planned |  | 42 | 4 | 0.0012261 | 0.00030653 | No
16/11/2018 | 08:53:15 | VH17 | Rural Short | Planned |  | 8 | 341 | 0.020324 | 5.96e-05 | No
16/11/2018 | 08:54:41 | SG10 | Rural Short | Planned |  | 43 | 387 | 0.12398 | 0.00032036 | No
16/11/2018 | 09:05:39 | SG09 | Rural Short | Planned |  | 66 | 242 | 0.11899 | 0.00049171 | No
16/11/2018 | 09:08:28 | VH22 | Rural Short | Planned |  | 123 | 78 | 0.071477 | 0.00091637 | No
16/11/2018 | 09:09:39 | PL803A | Urban | Asset failure | LV | 1 | 96 | 0.00015347 | 1.6e-06 | No
16/11/2018 | 09:35:52 | NA04 | Rural Long | Planned |  | 16 | 272 | 0.031762 | 0.00011677 | No
16/11/2018 | 09:39:34 | SD39300 | Rural Long | Other |  | 1 | 137 | 0.00099987 | 7.3e-06 | No
16/11/2018 | 09:40:10 | MV12 | Urban | Planned |  | 5 | 294 | 0.00235 | 7.99e-06 | No
16/11/2018 | 09:45:22 | GU13 | Rural Long | Planned |  | 15 | 307 | 0.033609 | 0.00010948 | No
16/11/2018 | 09:59:08 | AP365A | Urban | Planned |  | 249 | 193 | 0.076828 | 0.00039807 | No
16/11/2018 | 10:00:00 | SSD528 | Rural Short | Planned |  | 11 | 84 | 0.0068839 | 8.195e-05 | No
16/11/2018 | 10:02:25 | KI31 | Rural Short | Planned |  | 1 | 1121 | 0.0083516 | 7.45e-06 | No
16/11/2018 | 10:18:00 | BT07 | Rural Long | Planned |  | 2 | 109 | 0.001591 | 1.46e-05 | No
16/11/2018 | 10:27:07 | VH17 | Rural Short | Planned |  | 2 | 85 | 0.0012665 | 1.49e-05 | No
16/11/2018 | 10:31:53 | SM350A | Urban | Planned |  | 88 | 225 | 0.031654 | 0.00014068 | No
16/11/2018 | 11:10:09 | R28 | Rural Long | Planned |  | 1 | 43 | 0.00031383 | 7.3e-06 | No
16/11/2018 | 11:18:51 | GU41 | Rural Long | Planned |  | 3 | 145 | 0.0031748 | 2.19e-05 | No
16/11/2018 | 11:32:53 | NL115E | Urban | Planned |  | 35 | 77 | 0.0043084 | 5.595e-05 | No
16/11/2018 | 11:39:08 | GU14 | Rural Long | Planned |  | 13 | 77 | 0.0073056 | 9.488e-05 | No
16/11/2018 | 11:41:38 | AP139B | Urban | Unknown | Unknown | 4.6667 | 135.1428 | 0.0010082 | 7.46e-06 | No
16/11/2018 | 12:13:18 | SA36 | Urban | Overloads |  | 2 | 117 | 0.00037409 | 3.2e-06 | No
16/11/2018 | 12:56:51 | KA02 | Rural Short | Asset failure | LV | 15 | 124 | 0.013857 | 0.00011175 | No
16/11/2018 | 14:02:25 | NL760B | Urban | Planned |  | 5 | 88 | 0.00070342 | 7.99e-06 | No
16/11/2018 | 15:46:31 | AP424B | Urban | Asset failure | LV | 1 | 317 | 0.00050678 | 1.6e-06 | No
16/11/2018 | 16:04:19 | AP424B | Urban | Asset failure | LV | 1 | 215 | 0.00034372 | 1.6e-06 | No
16/11/2018 | 16:54:28 | ME347G | Urban | Asset failure | LV | 1 | 224 | 0.0003581 | 1.6e-06 | No
16/11/2018 | 17:30:33 | AP425D | Urban | Overloads |  | 1 | 63 | 0.00010072 | 1.6e-06 | No
16/11/2018 | 19:44:24 | MT13 | Rural Long | Third Party | Vehicle impact | 1 | 125 | 0.00091229 | 7.3e-06 | No
16/11/2018 | 21:39:34 | SA520B | Urban | Asset failure | LV | 6 | 51 | 0.00048919 | 9.59e-06 | No
16/11/2018 | 21:55:01 | PA06 | Rural Long | Other |  | 1 | 779 | 0.0056854 | 7.3e-06 | No
16/11/2018 | 22:11:29 | BM15 | Rural Short | Asset failure | HV | 202 | 299 | 0.44997 | 0.0015049 | No
17/11/2018 | 02:55:12 | SM349D | Urban | Third Party | Vehicle impact | 156 | 316 | 0.078808 | 0.00024939 | No
17/11/2018 | 04:34:24 | NU02 | Rural Long | Unknown | Unknown | 106 | 121 | 0.093608 | 0.00077362 | No
17/11/2018 | 04:53:15 | EL10 | Urban | Asset failure | LV | 1 | 428 | 0.00068423 | 1.6e-06 | No
17/11/2018 | 07:05:56 | BT02 | Rural Long | Unknown | Unknown | 1.6667 | 225 | 0.0027369 | 1.216e-05 | No
17/11/2018 | 07:18:27 | MI14 | Rural Long | Animal | Animal impact | 34 | 133 | 0.033003 | 0.00024814 | No
17/11/2018 | 07:40:07 | HH177E | Urban | Asset failure | LV | 1 | 207 | 0.00033093 | 1.6e-06 | No
17/11/2018 | 09:05:33 | BM55 | Rural Short | Unknown | Unknown | 24 | 59 | 0.010549 | 0.0001788 | No
17/11/2018 | 10:13:55 | SM374D | Urban | Planned |  | 39 | 1790 | 0.1116 | 6.235e-05 | No
17/11/2018 | 13:15:41 | HH177C | Urban | Asset failure | LV | 17.6666 | 113 | 0.0031915 | 2.824e-05 | No
17/11/2018 | 13:24:47 | WHY10 | Urban | Asset failure | LV | 2 | 68 | 0.00021742 | 3.2e-06 | No
17/11/2018 | 14:06:53 | SM374E | Urban | Asset failure | LV | 1 | 242 | 0.00038688 | 1.6e-06 | No
17/11/2018 | 14:49:35 | HH496D | Urban | Planned |  | 275 | 92 | 0.040446 | 0.00043964 | No
17/11/2018 | 15:37:29 | MB25 | Rural Long | Asset failure | HV | 67 | 43.2239 | 0.021136 | 0.00048899 | No
17/11/2018 | 16:22:20 | EL03 | Urban | Asset failure | LV | 2 | 345 | 0.0011031 | 3.2e-06 | No
17/11/2018 | 16:28:58 | HH107A | Urban | Unknown | Unknown | 14.3333 | 14 | 0.0003208 | 2.291e-05 | No
17/11/2018 | 17:23:37 | AP227A | Urban | Asset failure | LV | 1 | 245 | 0.00039168 | 1.6e-06 | No
17/11/2018 | 17:46:34 | EL03 | Urban | Asset failure | LV | 1 | 262 | 0.00041885 | 1.6e-06 | No
17/11/2018 | 17:59:11 | EL03 | Urban | Asset failure | HV | 3.3333 | 196 | 0.0010445 | 5.33e-06 | No
17/11/2018 | 19:15:38 | W27 | Rural Long | Asset failure | HV | 2 | 50 | 0.00072983 | 1.46e-05 | No
17/11/2018 | 22:27:06 | HH386C | Urban | Unknown | Unknown | 1381 | 4.8161 | 0.010633 | 0.0022078 | No
17/11/2018 | 23:53:10 | MV52 | Rural Short | Asset failure | HV | 23 | 60 | 0.010281 | 0.00017135 | No
18/11/2018 | 00:31:18 | HH121B | Urban | Unknown | Unknown | 34.6666 | 123 | 0.0068167 | 5.542e-05 | No
18/11/2018 | 00:58:09 | HH386C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 155 | 94 | 0.023293 | 0.00024779 | No
18/11/2018 | 06:46:27 | GA15 | Rural Short | Unknown | Unknown | 1 | 233 | 0.0017359 | 7.45e-06 | No
18/11/2018 | 07:41:30 | SM179D | Urban | Overloads |  | 1 | 166 | 0.00026538 | 1.6e-06 | No
18/11/2018 | 07:54:06 | SM411E | Urban | Other |  | 14.3333 | 91 | 0.0020852 | 2.291e-05 | No
18/11/2018 | 08:42:32 | PA02 | Urban | Planned |  | 37 | 283 | 0.01674 | 5.915e-05 | No
18/11/2018 | 08:45:28 | MV14 | Rural Short | Planned |  | 1 | 119 | 0.00088657 | 7.45e-06 | No
18/11/2018 | 09:52:41 | HH386C | Urban | Planned |  | 98 | 131 | 0.020524 | 0.00015667 | No
18/11/2018 | 10:23:55 | SM350E | Urban | Asset failure | LV | 1 | 35 | 5.595e-05 | 1.6e-06 | No
18/11/2018 | 15:07:21 | SA17 | Urban | Asset failure | LV | 1 | 133 | 0.00021262 | 1.6e-06 | No
18/11/2018 | 16:19:38 | HH121A | Urban | Asset failure | LV | 29 | 142 | 0.0065833 | 4.636e-05 | No
18/11/2018 | 17:39:07 | EL01A | Urban | Asset failure | LV | 1 | 140 | 0.00022381 | 1.6e-06 | No
18/11/2018 | 20:12:50 | NL210B | Urban | Overloads |  | 1 | 173 | 0.00027657 | 1.6e-06 | No
18/11/2018 | 21:30:50 | SD31400 | Rural Long | Animal | Animal impact | 4 | 183 | 0.0053424 | 2.919e-05 | No
18/11/2018 | 23:30:14 | SM126E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 197 | 0.00031494 | 1.6e-06 | No
19/11/2018 | 08:14:36 | MV33 | Rural Short | Planned |  | 128 | 300.2422 | 0.28632 | 0.00095362 | No
19/11/2018 | 08:49:55 | PL803C | Urban | Planned |  | 1 | 270 | 0.00043164 | 1.6e-06 | No
19/11/2018 | 08:56:06 | NL760A | Urban | Planned |  | 38 | 209.7895 | 0.012745 | 6.075e-05 | No
19/11/2018 | 09:03:13 | SG13 | Rural Short | Planned |  | 39 | 310 | 0.090072 | 0.00029056 | No
19/11/2018 | 09:03:56 | AP125C | Urban | Planned |  | 135 | 203 | 0.043812 | 0.00021582 | No
19/11/2018 | 09:32:11 | MV63 | Rural Short | Planned |  | 53 | 146 | 0.057649 | 0.00039486 | No
19/11/2018 | 09:32:36 | HH177E | Urban | Planned |  | 83 | 97 | 0.012871 | 0.00013269 | No
19/11/2018 | 09:58:16 | SD38100 | Rural Long | Planned |  | 4 | 283 | 0.0082617 | 2.919e-05 | No
19/11/2018 | 10:06:44 | EL02 | Urban | Planned |  | 229 | 130 | 0.047593 | 0.0003661 | No
19/11/2018 | 10:07:29 | SM216C | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 141 | 0.00045083 | 3.2e-06 | No
19/11/2018 | 10:10:13 | SD40200 | Rural Long | Planned |  | 1 | 128 | 0.00093419 | 7.3e-06 | No
19/11/2018 | 10:29:57 | SB18 | Rural Long | Planned |  | 7 | 216 | 0.011035 | 5.109e-05 | No
19/11/2018 | 10:38:54 | LM13 | Rural Long | Planned |  | 2 | 85 | 0.0012407 | 1.46e-05 | No
19/11/2018 | 11:30:23 | HH428B | Urban | Third Party | Vehicle impact | 37 | 208 | 0.012303 | 5.915e-05 | No
19/11/2018 | 12:22:06 | HH177E | Urban | Planned |  | 71 | 73 | 0.0082859 | 0.00011351 | No
19/11/2018 | 13:33:38 | NL115B | Urban | Asset failure | LV | 16.3333 | 50 | 0.0013056 | 2.611e-05 | No
19/11/2018 | 13:33:45 | CD02 | Rural Long | Weather |  | 427 | 65 | 0.20257 | 0.0031164 | No
19/11/2018 | 13:59:33 | AP146A | Urban | Unknown | Unknown | 2 | 146 | 0.00046681 | 3.2e-06 | No
19/11/2018 | 14:09:15 | HH121A | Urban | Asset failure | LV | 23.3333 | 117 | 0.0043644 | 3.73e-05 | No
19/11/2018 | 14:38:23 | SG13 | Rural Short | Planned |  | 1 | 51 | 0.00037996 | 7.45e-06 | No
19/11/2018 | 14:41:27 | CD16 | Rural Short | Weather |  | 63 | 372.4127 | 0.1748 | 0.00046936 | No
19/11/2018 | 14:42:18 | SB15 | Rural Long | Weather |  | 80 | 304 | 0.1775 | 0.00058387 | No
19/11/2018 | 15:15:56 | AP373E | Urban | Unknown | Unknown | 5 | 1072 | 0.0085689 | 7.99e-06 | No
19/11/2018 | 15:15:56 | AP373E | Urban | Unknown | Unknown | 216 | 3 | 0.0010359 | 0.00034531 | No
19/11/2018 | 15:36:45 | SB21 | Rural Long | Weather |  | 79 | 936.8481 | 0.54016 | 0.00057657 | No
19/11/2018 | 15:38:38 | CD02 | Rural Long | Weather |  | 427 | 223.719 | 0.6972 | 0.0031164 | No
19/11/2018 | 16:32:33 | BM52 | Urban | Asset failure | LV | 1 | 267 | 0.00042685 | 1.6e-06 | No
19/11/2018 | 16:56:08 | CM10 | Rural Long | Weather |  | 45 | 218.6 | 0.071794 | 0.00032843 | No
19/11/2018 | 17:05:30 | NA10 | Rural Long | Unknown | Unknown | 1 | 11238 | 0.082019 | 7.3e-06 | No
19/11/2018 | 18:06:56 | MT10 | Rural Long | Weather |  | 99 | 108 | 0.078034 | 0.00072254 | No
19/11/2018 | 18:10:39 | PA02 | Urban | Overloads |  | 1 | 198 | 0.00031654 | 1.6e-06 | No
19/11/2018 | 18:12:44 | SM350E | Urban | Asset failure | HV | 840 | 117.4619 | 0.15774 | 0.0013429 | No
19/11/2018 | 18:35:17 | AP149F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2596 | 181.1314 | 0.75172 | 0.0041502 | No
19/11/2018 | 18:36:01 | AP149F | Urban | Vegetation | Grow-in - NSP responsibility | 26 | 191 | 0.007939 | 4.157e-05 | No
19/11/2018 | 18:40:17 | GA800A | Rural Short | Unknown | Unknown | 2 | 428 | 0.0063773 | 1.49e-05 | No
19/11/2018 | 18:40:26 | SM216B | Urban | Asset failure | HV | 2778 | 74.923 | 0.33274 | 0.0044411 | No
19/11/2018 | 18:40:58 | SM374A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 845 | 250.5231 | 0.33843 | 0.0013509 | No
19/11/2018 | 18:44:10 | AP355F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 44 | 628 | 0.044175 | 7.034e-05 | No
19/11/2018 | 18:46:39 | HH429C | Urban | Asset failure | LV | 84 | 400 | 0.053715 | 0.00013429 | No
19/11/2018 | 18:47:34 | SM126B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 890 | 236 | 0.33579 | 0.0014228 | No
19/11/2018 | 18:55:58 | SM172C | Urban | Asset failure | LV | 133.3334 | 292 | 0.062242 | 0.00021316 | No
19/11/2018 | 18:56:24 | HH428D | Urban | Unknown | Unknown | 34.6666 | 296 | 0.016405 | 5.542e-05 | No
19/11/2018 | 18:57:22 | HH432F | Urban | Vegetation | Grow-in - NSP responsibility | 11 | 238 | 0.0041853 | 1.759e-05 | No
19/11/2018 | 18:57:31 | NL115E | Urban | Unknown | Unknown | 13.3333 | 271 | 0.0057765 | 2.132e-05 | No
19/11/2018 | 18:58:18 | HH121F | Urban | Vegetation | Grow-in - NSP responsibility | 19.3333 | 243 | 0.0075106 | 3.091e-05 | No
19/11/2018 | 19:00:52 | NL760C | Urban | Asset failure | LV | 1 | 306 | 0.00048919 | 1.6e-06 | No
19/11/2018 | 19:01:55 | HH409E | Urban | Unknown | Unknown | 29.6666 | 188 | 0.0089163 | 4.743e-05 | No
19/11/2018 | 19:25:29 | HH118B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 10 | 377 | 0.006027 | 1.599e-05 | No
19/11/2018 | 19:47:08 | LX41 | Rural Short | Asset failure | LV | 1 | 183 | 0.0013634 | 7.45e-06 | No
19/11/2018 | 19:55:41 | W01 | Rural Long | Unknown | Unknown | 201 | 821 | 1.2044 | 0.001467 | No
19/11/2018 | 20:23:14 | ME131A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 165 | 0.00026378 | 1.6e-06 | No
19/11/2018 | 20:42:08 | AP149B | Urban | Asset failure | LV | 18.6666 | 34 | 0.0010146 | 2.984e-05 | No
19/11/2018 | 21:22:47 | PA02 | Urban | Overloads |  | 1 | 77 | 0.0001231 | 1.6e-06 | No
19/11/2018 | 21:48:39 | VH32 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 99 | 0.0014751 | 1.49e-05 | No
19/11/2018 | 21:52:12 | GA800A | Rural Short | Unknown | Unknown | 1 | 235 | 0.0017508 | 7.45e-06 | No
19/11/2018 | 22:02:27 | W18 | Rural Long | Weather |  | 55 | 940.8182 | 0.37765 | 0.00040141 | No
19/11/2018 | 22:06:39 | W23 | Rural Long | Unknown | Unknown | 47 | 854.8936 | 0.29325 | 0.00034302 | No
19/11/2018 | 22:29:15 | W32 | Rural Long | Weather |  | 19 | 940.1579 | 0.13037 | 0.00013867 | No
19/11/2018 | 22:32:01 | W26 | Rural Long | Weather |  | 95 | 768.8211 | 0.53306 | 0.00069334 | No
19/11/2018 | 22:32:01 | W26 | Rural Long | Weather |  | 0 | 105.2857 | 0.0053789 | 0 | No
19/11/2018 | 22:40:57 | HH429C | Urban | Asset failure | LV | 29 | 167 | 0.0077424 | 4.636e-05 | No
19/11/2018 | 22:44:22 | ME200G | Urban | Unknown | Unknown | 4.6667 | 898 | 0.0066995 | 7.46e-06 | No
19/11/2018 | 22:45:35 | SM402B | Urban | Asset failure | LV | 16.6667 | 64 | 0.0017052 | 2.664e-05 | No
20/11/2018 | 00:38:59 | AP424D | Urban | Asset failure | LV | 3.6667 | 117 | 0.00068583 | 5.86e-06 | No
20/11/2018 | 01:15:16 | CV32 | Rural Long | Weather |  | 68 | 842.8235 | 0.41828 | 0.00049629 | No
20/11/2018 | 07:29:53 | CD24 | Rural Long | Weather |  | 2 | 451 | 0.0065831 | 1.46e-05 | No
20/11/2018 | 08:32:02 | LM63 | Rural Long | Planned |  | 75 | 292 | 0.15983 | 0.00054738 | No
20/11/2018 | 08:37:07 | PL06 | Urban | Planned |  | 21 | 133 | 0.0044651 | 3.357e-05 | No
20/11/2018 | 08:49:53 | MV62 | Rural Short | Weather |  | 52 | 262 | 0.1015 | 0.00038741 | No
20/11/2018 | 08:53:31 | ME231A | Urban | Asset failure | HV | 716 | 117.757 | 0.13479 | 0.0011447 | No
20/11/2018 | 09:02:26 | CN24 | Rural Long | Unknown | Unknown | 108 | 290 | 0.22858 | 0.00078822 | No
20/11/2018 | 09:03:25 | SG10 | Rural Short | Planned |  | 27 | 184 | 0.037012 | 0.00020115 | No
20/11/2018 | 09:10:14 | NU15 | Rural Long | Planned |  | 5 | 263 | 0.0095973 | 3.649e-05 | No
20/11/2018 | 09:31:14 | HH148C | Urban | Planned |  | 99 | 302 | 0.047797 | 0.00015827 | No
20/11/2018 | 09:31:18 | SM402B | Urban | Other |  | 16.6667 | 90 | 0.002398 | 2.664e-05 | No
20/11/2018 | 09:40:41 | NL115C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1048 | 86.5926 | 0.14508 | 0.0016754 | No
20/11/2018 | 09:43:19 | KA06 | Rural Long | Planned |  | 55 | 231 | 0.092725 | 0.00040141 | No
20/11/2018 | 09:47:00 | HH148C | Urban | Planned |  | 234 | 254 | 0.095019 | 0.00037409 | No
20/11/2018 | 09:52:48 | SG13 | Rural Short | Planned |  | 32 | 206 | 0.049111 | 0.0002384 | No
20/11/2018 | 10:00:17 | KA29 | Rural Long | Planned |  | 2 | 33 | 0.00048169 | 1.46e-05 | No
20/11/2018 | 10:01:33 | KA29 | Rural Long | Planned |  | 1 | 32 | 0.00023355 | 7.3e-06 | No
20/11/2018 | 10:06:02 | SA20 | Urban | Overloads |  | 1 | 105 | 0.00016786 | 1.6e-06 | No
20/11/2018 | 10:15:45 | BT07 | Rural Long | Planned |  | 2 | 32 | 0.00046709 | 1.46e-05 | No
20/11/2018 | 10:24:46 | CD26 | Rural Long | Unknown | Unknown | 4 | 367 | 0.010714 | 2.919e-05 | No
20/11/2018 | 10:53:07 | ME200E | Urban | Planned |  | 71 | 212 | 0.024063 | 0.00011351 | No
20/11/2018 | 11:11:14 | ME347F | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
20/11/2018 | 11:20:03 | NA51 | Rural Long | Weather |  | 750 | 125.744 | 0.68829 | 0.0054738 | No
20/11/2018 | 11:54:59 | G11 | Rural Long | Asset failure | LV | 1 | 157 | 0.0011458 | 7.3e-06 | No
20/11/2018 | 12:00:07 | M92 | Rural Long | Planned |  | 3 | 50 | 0.0010948 | 2.19e-05 | No
20/11/2018 | 12:04:40 | SD38200 | Rural Long | Planned |  | 1 | 75 | 0.00054738 | 7.3e-06 | No
20/11/2018 | 12:34:00 | HH121B | Urban | Third Party | Vehicle impact | 871 | 61.2859 | 0.085337 | 0.0013924 | No
20/11/2018 | 13:06:39 | SB01 | Rural Long | Weather |  | 662.0003 | 44.5418 | 0.2152 | 0.0048315 | No
20/11/2018 | 14:10:38 | BT37 | Rural Long | Planned |  | 1 | 14 | 0.00010218 | 7.3e-06 | No
20/11/2018 | 14:40:16 | PL14 | Urban | Third Party | Dig-in | 1 | 60 | 9.592e-05 | 1.6e-06 | No
20/11/2018 | 14:48:34 | AP351D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 334 | 0.00053396 | 1.6e-06 | No
20/11/2018 | 15:00:35 | SB21 | Rural Long | Weather |  | 79 | 142.557 | 0.082194 | 0.00057657 | No
20/11/2018 | 15:41:05 | LX33 | Rural Short | Unknown | Unknown | 62 | 224.3548 | 0.10363 | 0.00046191 | No
20/11/2018 | 16:02:05 | BT28 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 36 | 204.25 | 0.053665 | 0.00026274 | No
20/11/2018 | 17:05:48 | KA11 | Rural Long | Unknown | Unknown | 1 | 52 | 0.00037951 | 7.3e-06 | No
20/11/2018 | 17:30:20 | HH386A | Urban | Asset failure | LV | 1 | 339 | 0.00054195 | 1.6e-06 | No
20/11/2018 | 19:46:27 | NL111B | Urban | Asset failure | LV | 1 | 68 | 0.00010871 | 1.6e-06 | No
20/11/2018 | 19:50:12 | NL115B | Urban | Asset failure | LV | 1 | 110 | 0.00017585 | 1.6e-06 | No
20/11/2018 | 23:31:27 | CBD366N | CBD | Planned |  | 11 | 25 | 0.053383 | 0.0021353 | No
20/11/2018 | 23:31:27 | CBD366N | CBD | Planned |  | 0 | 13.7273 | 0.029312 | 0 | No
21/11/2018 | 00:15:40 | SM179B | Urban | Asset failure | LV | 50 | 97 | 0.0077536 | 7.993e-05 | Yes
21/11/2018 | 00:45:27 | AP149C | Urban | Vegetation | Grow-in - NSP responsibility | 1384 | 78.4646 | 0.17361 | 0.0022126 | Yes
21/11/2018 | 02:26:44 | AP373B | Urban | Unknown | Unknown | 11 | 6 | 0.00010551 | 1.759e-05 | Yes
21/11/2018 | 05:57:53 | HH341B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 202 | 0.00032293 | 1.6e-06 | Yes
21/11/2018 | 06:13:55 | MV42 | Rural Short | Planned |  | 519 | 105 | 0.406 | 0.0038666 | Yes
21/11/2018 | 06:51:37 | SD35500 | Rural Long | Weather |  | 565 | 194.9558 | 0.80391 | 0.0041236 | Yes
21/11/2018 | 07:07:42 | W23 | Rural Long | Unknown | Unknown | 47 | 177 | 0.060715 | 0.00034302 | Yes
21/11/2018 | 09:03:56 | VH22 | Rural Short | Planned |  | 112 | 87 | 0.072594 | 0.00083442 | Yes
21/11/2018 | 09:06:03 | AP125D | Urban | Planned |  | 3 | 84 | 0.00040287 | 4.8e-06 | Yes
21/11/2018 | 09:15:37 | AP125D | Urban | Planned |  | 160 | 212 | 0.054227 | 0.00025579 | Yes
21/11/2018 | 09:16:27 | GU41 | Rural Long | Asset failure | LV | 1 | 150 | 0.0010948 | 7.3e-06 | Yes
21/11/2018 | 09:20:17 | MV34 | Rural Short | Other |  | 10.3333 | 152 | 0.011702 | 7.698e-05 | Yes
21/11/2018 | 09:26:16 | NL234B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 89 | 0.00014228 | 1.6e-06 | Yes
21/11/2018 | 09:28:04 | SG13 | Rural Short | Planned |  | 35 | 203 | 0.052933 | 0.00026076 | Yes
21/11/2018 | 09:39:53 | SM349C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 45 | 347 | 0.024963 | 7.194e-05 | Yes
21/11/2018 | 09:42:41 | HH386D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 448 | 50 | 0.03581 | 0.00071621 | Yes
21/11/2018 | 09:50:53 | WK21 | Rural Short | Planned |  | 1 | 95 | 0.00070776 | 7.45e-06 | Yes
21/11/2018 | 09:52:37 | GU37 | Rural Long | Planned |  | 34 | 262 | 0.065014 | 0.00024814 | Yes
21/11/2018 | 09:53:00 | MTB72 | Rural Long | Unknown | Unknown | 122 | 1489 | 1.3258 | 0.0008904 | Yes
21/11/2018 | 09:57:09 | SD32400 | Rural Long | Asset failure | Subtransmission | 2460 | 202.9236 | 3.6433 | 0.017954 | Yes
21/11/2018 | 10:00:12 | NA15 | Rural Long | Planned |  | 2 | 30 | 0.0004379 | 1.46e-05 | Yes
21/11/2018 | 10:07:00 | AP226D | Urban | Unknown | Unknown | 49 | 103 | 0.0080685 | 7.834e-05 | Yes
21/11/2018 | 10:08:42 | VH44 | Rural Short | Planned |  | 34 | 62 | 0.015705 | 0.00025331 | Yes
21/11/2018 | 10:08:48 | HH177C | Urban | Unknown | Unknown | 2341 | 62.4771 | 0.23382 | 0.0037425 | Yes
21/11/2018 | 10:11:24 | HH409D | Urban | Asset failure | LV | 77 | 39 | 0.0048008 | 0.0001231 | Yes
21/11/2018 | 10:22:51 | ME131C | Urban | Vegetation | Grow-in - NSP responsibility | 24.6666 | 127 | 0.0050081 | 3.943e-05 | Yes
21/11/2018 | 10:57:09 | MI08 | Rural Long | Planned |  | 6 | 187 | 0.0081887 | 4.379e-05 | Yes
21/11/2018 | 11:18:00 | CD16 | Rural Short | Asset failure | HV | 11 | 43.3636 | 0.0035537 | 8.195e-05 | Yes
21/11/2018 | 11:37:00 | W23 | Rural Long | Unknown | Unknown | 21 | 38 | 0.0058241 | 0.00015327 | Yes
21/11/2018 | 11:40:22 | SG03 | Rural Short | Planned |  | 17 | 210 | 0.026597 | 0.00012665 | Yes
21/11/2018 | 12:10:34 | AP149A | Urban | Weather |  | 18.6667 | 91 | 0.0027156 | 2.984e-05 | Yes
21/11/2018 | 12:21:39 | YK23 | Rural Long | Asset failure | LV | 1 | 91 | 0.00066415 | 7.3e-06 | Yes
21/11/2018 | 12:26:30 | HH432F | Urban | Unknown | Unknown | 38.6666 | 287 | 0.017741 | 6.182e-05 | Yes
21/11/2018 | 13:48:01 | HH121C | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 67 | 0.0010711 | 1.599e-05 | Yes
21/11/2018 | 14:09:00 | HH428F | Urban | Unknown | Unknown | 69 | 210 | 0.023165 | 0.00011031 | Yes
21/11/2018 | 14:20:00 | AP226D | Urban | Vegetation | Grow-in - NSP responsibility | 49 | 340 | 0.026634 | 7.834e-05 | Yes
21/11/2018 | 14:27:01 | HH409E | Urban | Weather |  | 23.3333 | 150 | 0.0055954 | 3.73e-05 | Yes
21/11/2018 | 14:37:22 | AP529E | Urban | Vegetation | Grow-in - NSP responsibility | 64 | 492 | 0.050339 | 0.00010232 | Yes
21/11/2018 | 14:38:15 | HH341D | Urban | Unknown | Unknown | 13.6667 | 326 | 0.0071226 | 2.185e-05 | Yes
21/11/2018 | 14:39:46 | HH522C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 429 | 137 | 0.093959 | 0.00068583 | Yes
21/11/2018 | 14:41:38 | HH432F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 8.3333 | 96 | 0.0012789 | 1.332e-05 | Yes
21/11/2018 | 14:58:00 | AP372B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1223 | 101 | 0.19747 | 0.0019552 | Yes
21/11/2018 | 14:58:14 | NL115E | Urban | Vegetation | Grow-in - NSP responsibility | 13.3333 | 1315.0001 | 0.02803 | 2.132e-05 | Yes
21/11/2018 | 14:58:18 | SM179B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13.6667 | 120 | 0.0026218 | 2.185e-05 | Yes
21/11/2018 | 14:58:43 | HH121E | Urban | Unknown | Unknown | 8 | 153 | 0.0019568 | 1.279e-05 | Yes
21/11/2018 | 15:00:41 | SM350E | Urban | Weather |  | 17.3333 | 277 | 0.0076758 | 2.771e-05 | Yes
21/11/2018 | 15:03:09 | HH177C | Urban | Asset failure | LV | 18.6666 | 374 | 0.011161 | 2.984e-05 | Yes
21/11/2018 | 15:03:52 | AP149E | Urban | Weather |  | 3 | 2039 | 0.0097791 | 4.8e-06 | Yes
21/11/2018 | 15:04:00 | GA05 | Rural Short | Unknown | Unknown | 45 | 208 | 0.069733 | 0.00033526 | Yes
21/11/2018 | 15:08:05 | AP226D | Urban | Other |  | 55 | 302 | 0.026554 | 8.793e-05 | Yes
21/11/2018 | 15:08:29 | HH177E | Urban | Asset failure | LV | 26 | 429 | 0.017832 | 4.157e-05 | Yes
21/11/2018 | 15:10:11 | GA800A | Rural Short | Weather |  | 6 | 1348 | 0.060257 | 4.47e-05 | Yes
21/11/2018 | 15:14:26 | KI41 | Rural Long | Third Party | Other | 7 | 311 | 0.015888 | 5.109e-05 | Yes
21/11/2018 | 15:15:00 | YK11 | Rural Long | Unknown | Unknown | 94 | 178 | 0.12212 | 0.00068604 | Yes
21/11/2018 | 15:15:00 | ST35 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 590 | 0.13779 | 0.00023355 | Yes
21/11/2018 | 15:20:47 | SM216G | Urban | Unknown | Unknown | 12.6667 | 1504.0001 | 0.030456 | 2.025e-05 | Yes
21/11/2018 | 15:21:30 | YK27 | Rural Long | Animal | Animal nesting/burrowing, etc and other | 6.6667 | 128 | 0.0062279 | 4.866e-05 | Yes
21/11/2018 | 15:23:34 | GA45 | Rural Short | Asset failure | HV | 88 | 272 | 0.17833 | 0.00065561 | Yes
21/11/2018 | 15:27:54 | SM374B | Urban | Unknown | Unknown | 7.3333 | 1575 | 0.018465 | 1.172e-05 | Yes
21/11/2018 | 15:28:00 | G11 | Rural Long | Unknown | Unknown | 60 | 142 | 0.062182 | 0.0004379 | Yes
21/11/2018 | 15:29:00 | YK12 | Rural Long | Asset failure | HV | 35 | 261.5714 | 0.066816 | 0.00025544 | Yes
21/11/2018 | 15:31:00 | HH102C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1267 | 47.7656 | 0.09675 | 0.0020255 | Yes
21/11/2018 | 15:31:10 | AP424C | Urban | Unknown | Unknown | 15.6667 | 631 | 0.015804 | 2.505e-05 | Yes
21/11/2018 | 15:33:00 | SM410B | Urban | Asset failure | HV | 1904 | 155.4343 | 0.47312 | 0.0030439 | Yes
21/11/2018 | 15:49:37 | HH428C | Urban | Unknown | Unknown | 40.6666 | 1739.0001 | 0.11306 | 6.501e-05 | Yes
21/11/2018 | 15:51:51 | SA711C | Urban | Asset failure | LV | 32 | 837 | 0.042819 | 5.116e-05 | Yes
21/11/2018 | 15:52:56 | HH102D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 61.9999 | 795 | 0.078799 | 9.912e-05 | Yes
21/11/2018 | 15:53:09 | AP149E | Urban | Vegetation | Grow-in - NSP responsibility | 19.3333 | 1088.9999 | 0.033658 | 3.091e-05 | Yes
21/11/2018 | 16:01:55 | HH121E | Urban | Other |  | 91 | 1636 | 0.238 | 0.00014548 | Yes
21/11/2018 | 16:18:00 | GA27 | Rural Long | Unknown | Unknown | 464 | 132 | 0.44701 | 0.0033864 | Yes
21/11/2018 | 16:25:09 | HH386G | Urban | Vegetation | Grow-in - NSP responsibility | 28.6667 | 340 | 0.015582 | 4.583e-05 | Yes
21/11/2018 | 16:26:40 | NL115B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 18.6666 | 272 | 0.008117 | 2.984e-05 | Yes
21/11/2018 | 16:27:00 | NA52 | Rural Long | Asset failure | HV | 445 | 184.2629 | 0.59844 | 0.0032478 | Yes
21/11/2018 | 16:28:00 | SA520E | Urban | Unknown | Unknown | 550 | 300 | 0.26378 | 0.00087927 | Yes
21/11/2018 | 16:28:00 | SG02 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 722 | 139 | 0.74768 | 0.005379 | Yes
21/11/2018 | 16:30:00 | SA32 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2386 | 451 | 1.7203 | 0.0038144 | Yes
21/11/2018 | 16:31:00 | HH107A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2432 | 95 | 0.36936 | 0.003888 | Yes
21/11/2018 | 16:32:17 | AP351D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 1755 | 0.0056114 | 3.2e-06 | Yes
21/11/2018 | 16:32:21 | HH107B | Urban | Asset failure | LV | 17 | 150 | 0.0040766 | 2.718e-05 | Yes
21/11/2018 | 16:33:37 | HH177C | Urban | Asset failure | LV | 33 | 1370 | 0.072276 | 5.276e-05 | Yes
21/11/2018 | 16:34:00 | HH107C | Urban | Vegetation | Grow-in - NSP responsibility | 46 | 1754 | 0.12899 | 7.354e-05 | Yes
21/11/2018 | 16:44:00 | GA07 | Rural Long | Unknown | Unknown | 52 | 153.8077 | 0.058372 | 0.00037951 | Yes
21/11/2018 | 16:47:00 | AP373C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 270 | 343 | 0.14805 | 0.00043164 | Yes
21/11/2018 | 16:51:12 | HH130B | Urban | Unknown | Unknown | 53 | 1571 | 0.13311 | 8.473e-05 | Yes
21/11/2018 | 16:51:12 | HH130B | Urban | Unknown | Unknown | 75 | 83 | 0.0099518 | 0.0001199 | Yes
21/11/2018 | 16:51:42 | HH341D | Urban | Asset failure | LV | 19.6666 | 246 | 0.0077344 | 3.144e-05 | Yes
21/11/2018 | 16:57:00 | SA17 | Urban | Unknown | Unknown | 672 | 326 | 0.35022 | 0.0010743 | Yes
21/11/2018 | 16:59:00 | MTB53 | Rural Long | Unknown | Unknown | 170 | 174.4353 | 0.21642 | 0.0012407 | Yes
21/11/2018 | 17:00:41 | HH121G | Urban | Unknown | Unknown | 21.3333 | 249 | 0.0084922 | 3.411e-05 | Yes
21/11/2018 | 17:10:58 | HH130C | Urban | Overloads |  | 17.6666 | 1508 | 0.042591 | 2.824e-05 | Yes
21/11/2018 | 17:17:57 | HH148B | Urban | Asset failure | LV | 13.3333 | 1506.0001 | 0.032101 | 2.132e-05 | Yes
21/11/2018 | 17:19:00 | SM216A | Urban | Asset failure | HV | 2106 | 84.5 | 0.2845 | 0.0033668 | Yes
21/11/2018 | 17:23:14 | NL210E | Urban | Animal | Animal impact | 15.3333 | 1348 | 0.033044 | 2.451e-05 | Yes
21/11/2018 | 17:30:28 | PL803C | Urban | Asset failure | LV | 1 | 63 | 0.00010072 | 1.6e-06 | Yes
21/11/2018 | 17:37:08 | HH121G | Urban | Asset failure | LV | 15 | 1312 | 0.031462 | 2.398e-05 | Yes
21/11/2018 | 17:41:53 | HH177G | Urban | Asset failure | LV | 49 | 111 | 0.0086952 | 7.834e-05 | Yes
21/11/2018 | 18:10:50 | HH121E | Urban | Vegetation | Grow-in - NSP responsibility | 8 | 654 | 0.0083643 | 1.279e-05 | Yes
21/11/2018 | 18:21:16 | HH428C | Urban | Vegetation | Grow-in - NSP responsibility | 11 | 704 | 0.01238 | 1.759e-05 | Yes
21/11/2018 | 18:22:15 | NU05 | Rural Short | Unknown | Unknown | 12 | 173 | 0.015466 | 8.94e-05 | Yes
21/11/2018 | 18:25:42 | HH409E | Urban | Third Party | Other | 22.6667 | 1585 | 0.057435 | 3.624e-05 | Yes
21/11/2018 | 18:34:17 | MB22 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 152 | 0.0011324 | 7.45e-06 | Yes
21/11/2018 | 18:38:30 | HH386F | Urban | Overloads |  | 18.3333 | 1370 | 0.040153 | 2.931e-05 | Yes
21/11/2018 | 18:40:24 | SM349A | Urban | Vegetation | Grow-in - NSP responsibility | 17 | 132 | 0.0035874 | 2.718e-05 | Yes
21/11/2018 | 18:45:06 | HH432C | Urban | Asset failure | LV | 21 | 1167 | 0.039179 | 3.357e-05 | Yes
21/11/2018 | 18:47:15 | MV33 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 423 | 0.0031514 | 7.45e-06 | Yes
21/11/2018 | 18:52:00 | VH31 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 808 | 131.7525 | 0.79311 | 0.0060197 | Yes
21/11/2018 | 18:52:22 | NL234A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 76 | 0.0001215 | 1.6e-06 | Yes
21/11/2018 | 18:59:27 | VH11 | Urban | Overloads |  | 1 | 1005 | 0.0016067 | 1.6e-06 | Yes
21/11/2018 | 18:59:56 | ME131B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 62 | 47 | 0.0046585 | 9.912e-05 | Yes
21/11/2018 | 19:02:00 | PA07 | Rural Long | Unknown | Unknown | 42 | 223 | 0.068356 | 0.00030653 | Yes
21/11/2018 | 19:05:18 | SM410A | Urban | Overloads |  | 26.3333 | 934 | 0.03932 | 4.21e-05 | Yes
21/11/2018 | 19:16:21 | NL760B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 172 | 0.00027497 | 1.6e-06 | Yes
21/11/2018 | 19:19:47 | AP149E | Urban | Asset failure | LV | 31.3333 | 1091 | 0.05465 | 5.009e-05 | Yes
21/11/2018 | 19:35:27 | AP226D | Urban | Asset failure | LV | 1 | 210 | 0.00033572 | 1.6e-06 | Yes
21/11/2018 | 19:36:17 | AP149H | Urban | Asset failure | LV | 21 | 275 | 0.0092323 | 3.357e-05 | Yes
21/11/2018 | 19:37:00 | ST35 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 136 | 333.2574 | 0.33078 | 0.00099257 | Yes
21/11/2018 | 19:37:00 | ST35 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 106 | 0.024756 | 0.00023355 | Yes
21/11/2018 | 19:40:23 | ME200G | Urban | Overloads |  | 30.6666 | 1416 | 0.069421 | 4.903e-05 | Yes
21/11/2018 | 19:46:49 | SM349F | Urban | Vegetation | Grow-in - NSP responsibility | 32.6667 | 1744 | 0.091078 | 5.222e-05 | Yes
21/11/2018 | 19:50:00 | SM137B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2022 | 204.7003 | 0.6617 | 0.0032325 | Yes
21/11/2018 | 19:50:01 | ME231A | Urban | Asset failure | LV | 1.3333 | 1546.0001 | 0.0032954 | 2.13e-06 | Yes
21/11/2018 | 19:53:26 | HH429C | Urban | Weather |  | 32.6666 | 1153 | 0.060214 | 5.222e-05 | Yes
21/11/2018 | 19:55:00 | SG01 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 432 | 171 | 0.55036 | 0.0032185 | Yes
21/11/2018 | 19:56:14 | AP425C | Urban | Unknown | Unknown | 15 | 1309 | 0.03139 | 2.398e-05 | Yes
21/11/2018 | 20:09:28 | HH432F | Urban | Asset failure | LV | 38.6666 | 1137 | 0.070284 | 6.182e-05 | Yes
21/11/2018 | 20:10:04 | HH386E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19.3333 | 1367 | 0.042251 | 3.091e-05 | Yes
21/11/2018 | 20:12:54 | SM410C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 117 | 1585 | 0.29647 | 0.00018704 | Yes
21/11/2018 | 20:14:28 | SM410C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 58.6667 | 887 | 0.083191 | 9.379e-05 | Yes
21/11/2018 | 20:21:00 | MTB32 | Rural Long | Unknown | Unknown | 61 | 514 | 0.22883 | 0.0004452 | Yes
21/11/2018 | 20:23:36 | MTB53 | Rural Long | Unknown | Unknown | 48 | 546 | 0.19127 | 0.00035032 | Yes
21/11/2018 | 20:23:36 | MTB53 | Rural Long | Unknown | Unknown | 236 | 2.4068 | 0.0041455 | 0.0017224 | Yes
21/11/2018 | 20:29:01 | SM350E | Urban | Weather |  | 8 | 1409 | 0.01802 | 1.279e-05 | Yes
21/11/2018 | 20:38:00 | YK11 | Rural Long | Asset failure | HV | 94 | 349.7021 | 0.23991 | 0.00068604 | Yes
21/11/2018 | 20:41:26 | AP227B | Urban | Vegetation | Grow-in - NSP responsibility | 8.6667 | 1062 | 0.014714 | 1.386e-05 | Yes
21/11/2018 | 20:41:53 | MV64 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 89 | 0.00014228 | 1.6e-06 | Yes
21/11/2018 | 20:46:25 | AP344B | Urban | Unknown | Unknown | 20.6667 | 1012 | 0.033436 | 3.304e-05 | Yes
21/11/2018 | 20:49:00 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 354 | 856 | 2.2576 | 0.0026374 | Yes
21/11/2018 | 20:50:17 | HH428D | Urban | Unknown | Unknown | 29 | 1346 | 0.062403 | 4.636e-05 | Yes
21/11/2018 | 20:52:42 | HH177B | Urban | Asset failure | LV | 16.3333 | 433 | 0.011306 | 2.611e-05 | Yes
21/11/2018 | 20:53:18 | AP146C | Urban | Unknown | Unknown | 24 | 1125 | 0.043164 | 3.837e-05 | Yes
21/11/2018 | 20:56:19 | AP425C | Urban | Overloads |  | 16.6667 | 1150 | 0.030641 | 2.664e-05 | Yes
21/11/2018 | 20:56:47 | HH409E | Urban | Unknown | Unknown | 23.3333 | 1420.0001 | 0.052969 | 3.73e-05 | Yes
21/11/2018 | 20:58:42 | HH121A | Urban | Unknown | Unknown | 21.3333 | 1333 | 0.045462 | 3.411e-05 | Yes
21/11/2018 | 20:59:52 | HH107B | Urban | Unknown | Unknown | 27.6666 | 1329.9999 | 0.058826 | 4.423e-05 | Yes
21/11/2018 | 21:00:18 | AP149B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1428 | 108.2808 | 0.2472 | 0.0022829 | Yes
21/11/2018 | 21:00:31 | SM350G | Urban | Vegetation | Grow-in - NSP responsibility | 60.6667 | 1213.9999 | 0.11774 | 9.699e-05 | Yes
21/11/2018 | 21:00:59 | AP372F | Urban | Asset failure | LV | 17.6666 | 1086 | 0.030672 | 2.824e-05 | Yes
21/11/2018 | 21:01:47 | SM350A | Urban | Weather |  | 11.6667 | 1225 | 0.022848 | 1.865e-05 | Yes
21/11/2018 | 21:06:05 | AP125C | Urban | Asset failure | LV | 22 | 1039 | 0.036542 | 3.517e-05 | Yes
21/11/2018 | 21:06:10 | SM349B | Urban | Asset failure | LV | 49.3333 | 1314 | 0.10363 | 7.887e-05 | Yes
21/11/2018 | 21:07:05 | SM349D | Urban | Unknown | Unknown | 13.6667 | 1082 | 0.02364 | 2.185e-05 | Yes
21/11/2018 | 21:11:03 | HH432F | Urban | Vegetation | Grow-in - NSP responsibility | 26 | 1077.0001 | 0.044766 | 4.157e-05 | Yes
21/11/2018 | 21:12:30 | HH118D | Urban | Asset failure | LV | 12.3333 | 1008 | 0.019875 | 1.972e-05 | Yes
21/11/2018 | 21:12:45 | SM411E | Urban | Vegetation | Grow-in - NSP responsibility | 25.6666 | 1293.0001 | 0.053055 | 4.103e-05 | Yes
21/11/2018 | 21:12:50 | SM216G | Urban | Weather |  | 29.6666 | 1095 | 0.051933 | 4.743e-05 | Yes
21/11/2018 | 21:14:26 | SG10 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 3.3333 | 404 | 0.010033 | 2.483e-05 | Yes
21/11/2018 | 21:16:00 | ME200E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1618 | 111 | 0.28712 | 0.0025867 | Yes
21/11/2018 | 21:17:03 | AP529E | Urban | Asset failure | LV | 21.3333 | 929 | 0.031684 | 3.411e-05 | Yes
21/11/2018 | 21:17:27 | AP424B | Urban | Unknown | Unknown | 18.3333 | 1127 | 0.033031 | 2.931e-05 | Yes
21/11/2018 | 21:18:47 | HH121C | Urban | Other |  | 31.6666 | 1332 | 0.067432 | 5.062e-05 | Yes
21/11/2018 | 21:19:49 | HH428D | Urban | Overloads |  | 30.3333 | 504 | 0.024441 | 4.849e-05 | Yes
21/11/2018 | 21:22:37 | HH177E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 360 | 0.00057552 | 1.6e-06 | Yes
21/11/2018 | 21:22:38 | HH177G | Urban | Weather |  | 24 | 1333.0001 | 0.051145 | 3.837e-05 | Yes
21/11/2018 | 21:23:20 | HH403A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 44 | 457 | 0.032146 | 7.034e-05 | Yes
21/11/2018 | 21:24:57 | HH121C | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 1503 | 0.024028 | 1.599e-05 | Yes
21/11/2018 | 21:27:00 | MV42 | Rural Short | Unknown | Unknown | 264 | 193 | 0.3796 | 0.0019668 | Yes
21/11/2018 | 21:31:49 | HH432B | Urban | Vegetation | Grow-in - NSP responsibility | 108 | 1199 | 0.20702 | 0.00017266 | Yes
21/11/2018 | 21:33:33 | HH121A | Urban | Vegetation | Grow-in - NSP responsibility | 30.6667 | 1311 | 0.064273 | 4.903e-05 | Yes
21/11/2018 | 21:35:30 | SA17 | Urban | Unknown | Unknown | 20.6666 | 101 | 0.003337 | 3.304e-05 | Yes
21/11/2018 | 21:36:25 | ME231D | Urban | Weather |  | 29 | 1412 | 0.065462 | 4.636e-05 | Yes
21/11/2018 | 21:39:43 | HH121G | Urban | Overloads |  | 33.6666 | 1288 | 0.069323 | 5.382e-05 | Yes
21/11/2018 | 21:42:38 | SM126E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2082 | 1257.0576 | 4.184 | 0.0033284 | Yes
21/11/2018 | 21:42:38 | SM126E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 0 | 7 | 0.023299 | 0 | Yes
21/11/2018 | 21:43:00 | AP139D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1886 | 819.1113 | 2.4697 | 0.0030151 | Yes
21/11/2018 | 21:46:33 | NL111P | Urban | Asset failure | LV | 21.6666 | 390 | 0.013509 | 3.464e-05 | Yes
21/11/2018 | 21:48:22 | SM216C | Urban | Asset failure | LV | 29 | 965 | 0.044739 | 4.636e-05 | Yes
21/11/2018 | 21:49:08 | AP424C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 25.3333 | 211 | 0.0085454 | 4.05e-05 | Yes
21/11/2018 | 21:52:50 | ME131C | Urban | Weather |  | 24.6666 | 1270 | 0.050081 | 3.943e-05 | Yes
21/11/2018 | 21:53:24 | SM410B | Urban | Other |  | 41 | 1858 | 0.12178 | 6.555e-05 | Yes
21/11/2018 | 21:56:00 | M92 | Rural Long | Weather |  | 467 | 638.3555 | 2.1757 | 0.0034083 | Yes
21/11/2018 | 21:56:00 | M92 | Rural Long | Weather |  | 0 | 5.9122 | 0.013765 | 0 | Yes
21/11/2018 | 21:58:00 | AP529D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 802 | 0.0012821 | 1.6e-06 | Yes
21/11/2018 | 21:58:00 | SG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 66 | 466 | 0.22914 | 0.00049171 | Yes
21/11/2018 | 21:58:00 | SG04 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 74 | 2 | 0.0011026 | 0.00055131 | Yes
21/11/2018 | 21:59:00 | AP139B | Urban | Vegetation | Grow-in - NSP responsibility | 8.6667 | 1079 | 0.01495 | 1.386e-05 | Yes
21/11/2018 | 22:00:00 | SM411F | Urban | Unknown | Unknown | 835 | 943 | 1.2588 | 0.0013349 | Yes
21/11/2018 | 22:00:03 | HH403A | Urban | Weather |  | 15.6667 | 266 | 0.0066622 | 2.505e-05 | Yes
21/11/2018 | 22:01:56 | HH107B | Urban | Asset failure | LV | 31 | 1338.9999 | 0.066359 | 4.956e-05 | Yes
21/11/2018 | 22:02:00 | SA744D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2500 | 14 | 0.055954 | 0.0039967 | Yes
21/11/2018 | 22:03:45 | HH429B | Urban | Unknown | Unknown | 32.6667 | 1069 | 0.055827 | 5.222e-05 | Yes
21/11/2018 | 22:06:00 | SA18 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2030 | 176.2778 | 0.57208 | 0.0032453 | Yes
21/11/2018 | 22:08:23 | AP529A | Urban | Asset failure | LV | 24.6666 | 1007 | 0.03971 | 3.943e-05 | Yes
21/11/2018 | 22:11:32 | AP529D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 791 | 0.0012645 | 1.6e-06 | Yes
21/11/2018 | 22:21:54 | AP227A | Urban | Asset failure | LV | 151 | 1097 | 0.26482 | 0.0002414 | Yes
21/11/2018 | 22:22:18 | HH121G | Urban | Vegetation | Grow-in - NSP responsibility | 21.3333 | 1299.0001 | 0.044302 | 3.411e-05 | Yes
21/11/2018 | 22:23:04 | CBD412M | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 427 | 0.00068263 | 1.6e-06 | Yes
21/11/2018 | 22:40:23 | SG07 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 200 | 0.00149 | 7.45e-06 | Yes
21/11/2018 | 22:42:00 | SM126D | Urban | Unknown | Unknown | 2118 | 939 | 3.1794 | 0.003386 | Yes
21/11/2018 | 22:43:13 | HH177C | Urban | Vegetation | Grow-in - NSP responsibility | 16.3333 | 1062 | 0.027731 | 2.611e-05 | Yes
21/11/2018 | 22:43:55 | HH409F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 198 | 780 | 0.2469 | 0.00031654 | Yes
21/11/2018 | 22:44:00 | HH386C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1381 | 1012.9638 | 2.2364 | 0.0022078 | Yes
21/11/2018 | 22:44:00 | HH386C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 0 | 3 | 0.0050886 | 0 | Yes
21/11/2018 | 22:47:06 | NL234A | Urban | Asset failure | LV | 30 | 254 | 0.012182 | 4.796e-05 | Yes
21/11/2018 | 22:48:52 | AP149H | Urban | Weather |  | 22 | 1267.0001 | 0.044561 | 3.517e-05 | Yes
21/11/2018 | 22:51:25 | NL210A | Urban | Other |  | 18.3333 | 980 | 0.028723 | 2.931e-05 | Yes
21/11/2018 | 23:04:19 | ME347E | Urban | Unknown | Unknown | 39.3334 | 1037.0001 | 0.065208 | 6.288e-05 | Yes
21/11/2018 | 23:09:00 | AP226D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2264 | 317 | 1.1473 | 0.0036194 | Yes
21/11/2018 | 23:13:36 | SM410D | Urban | Weather |  | 42 | 1020.9999 | 0.068554 | 6.714e-05 | Yes
21/11/2018 | 23:15:00 | HH118C | Urban | Vegetation | Grow-in - NSP responsibility | 2010 | 140.3124 | 0.45087 | 0.0032133 | Yes
21/11/2018 | 23:18:00 | MT05 | Rural Long | Weather |  | 74.3334 | 644 | 0.34938 | 0.00054251 | Yes
21/11/2018 | 23:19:00 | SG10 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 763 | 82 | 0.46613 | 0.0056845 | Yes
21/11/2018 | 23:20:00 | NL111Q | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2861 | 78.7033 | 0.35997 | 0.0045738 | Yes
21/11/2018 | 23:23:14 | SM137A | Urban | Overloads |  | 44.3333 | 951 | 0.067402 | 7.087e-05 | Yes
21/11/2018 | 23:27:47 | AP149B | Urban | Weather |  | 18.6666 | 1152.9999 | 0.034408 | 2.984e-05 | Yes
21/11/2018 | 23:27:50 | SA711C | Urban | Vegetation | Grow-in - NSP responsibility | 53 | 118 | 0.0099981 | 8.473e-05 | Yes
21/11/2018 | 23:28:00 | ME427F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1624 | 954.705 | 2.4787 | 0.0025963 | Yes
21/11/2018 | 23:39:21 | SM350E | Urban | Weather |  | 1 | 1250 | 0.0019983 | 1.6e-06 | Yes
21/11/2018 | 23:40:00 | SG13 | Rural Short | Third Party | Other | 264 | 425.6591 | 0.8372 | 0.0019668 | Yes
21/11/2018 | 23:40:00 | SG13 | Rural Short | Third Party | Other | 0 | 2 | 0.0027268 | 0 | Yes
21/11/2018 | 23:43:00 | SM126C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2161 | 767.1911 | 2.6504 | 0.0034547 | Yes
21/11/2018 | 23:43:33 | SG07 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 80 | 711 | 0.42376 | 0.00059601 | Yes
21/11/2018 | 23:44:51 | SM374A | Urban | Weather |  | 40 | 1050 | 0.067144 | 6.395e-05 | Yes
21/11/2018 | 23:56:47 | NL234C | Urban | Unknown | Unknown | 11.6667 | 691 | 0.012888 | 1.865e-05 | Yes
21/11/2018 | 23:57:10 | SM349H | Urban | Unknown | Unknown | 30.3333 | 907 | 0.043983 | 4.849e-05 | Yes
21/11/2018 | 23:58:45 | NL111C | Urban | Unknown | Unknown | 34.6667 | 668 | 0.037021 | 5.542e-05 | Yes
22/11/2018 | 00:07:30 | HH341A | Urban | Asset failure | LV | 128 | 1324 | 0.27093 | 0.00020463 | Yes
22/11/2018 | 00:14:50 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 911 | 681 | 0.9918 | 0.0014564 | Yes
22/11/2018 | 00:19:00 | AP510D | Urban | Weather |  | 1198 | 471.7321 | 0.90347 | 0.0019152 | Yes
22/11/2018 | 00:25:00 | NL544B | Urban | Asset failure | HV | 3 | 1010 | 0.004844 | 4.8e-06 | Yes
22/11/2018 | 00:26:10 | SM137A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 206 | 871 | 0.28684 | 0.00032933 | Yes
22/11/2018 | 00:31:44 | SA32 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 79 | 1131 | 0.14284 | 0.0001263 | Yes
22/11/2018 | 00:32:41 | AP529D | Urban | Asset failure | LV | 35 | 843 | 0.047169 | 5.595e-05 | Yes
22/11/2018 | 00:41:00 | SA520E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 550 | 199 | 0.17497 | 0.00087927 | Yes
22/11/2018 | 00:49:00 | NL234A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 698 | 282.2335 | 0.31494 | 0.0011159 | Yes
22/11/2018 | 00:51:00 | NL234B | Urban | Unknown | Unknown | 1821 | 129.492 | 0.37698 | 0.0029112 | Yes
22/11/2018 | 00:53:23 | SM374A | Urban | Asset failure | LV | 34 | 1035 | 0.056257 | 5.435e-05 | Yes
22/11/2018 | 00:54:31 | SM137B | Urban | Asset failure | LV | 43 | 891 | 0.06125 | 6.874e-05 | Yes
22/11/2018 | 01:24:49 | SM410C | Urban | Vegetation | Grow-in - NSP responsibility | 139 | 51 | 0.011333 | 0.00022222 | Yes
22/11/2018 | 01:31:26 | AP529E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19 | 611 | 0.018559 | 3.037e-05 | Yes
22/11/2018 | 01:34:10 | AP424E | Urban | Asset failure | LV | 10.6667 | 61 | 0.0010402 | 1.705e-05 | Yes
22/11/2018 | 01:39:11 | HH432F | Urban | Weather |  | 31 | 1266 | 0.062742 | 4.956e-05 | Yes
22/11/2018 | 01:42:24 | SM350F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 66 | 0.0015827 | 2.398e-05 | Yes
22/11/2018 | 01:44:22 | NL511B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 22.3333 | 706 | 0.025207 | 3.57e-05 | Yes
22/11/2018 | 01:50:27 | SA32 | Urban | Unknown | Unknown | 25.6666 | 278 | 0.011407 | 4.103e-05 | Yes
22/11/2018 | 02:06:55 | SM179B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 27.3333 | 881 | 0.038497 | 4.37e-05 | Yes
22/11/2018 | 02:33:00 | GU43 | Rural Long | Unknown | Unknown | 514 | 172 | 0.64523 | 0.0037514 | Yes
22/11/2018 | 02:37:00 | VH22 | Rural Short | Unknown | Unknown | 65 | 194 | 0.093946 | 0.00048426 | Yes
22/11/2018 | 02:44:00 | SM374E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1730 | 506 | 1.3994 | 0.0027657 | Yes
22/11/2018 | 02:46:14 | NL760B | Urban | Vegetation | Grow-in - NSP responsibility | 37.3333 | 16 | 0.00095494 | 5.968e-05 | Yes
22/11/2018 | 02:53:52 | ME347C | Urban | Other |  | 8.3333 | 880.9999 | 0.011737 | 1.332e-05 | Yes
22/11/2018 | 03:13:00 | VH22 | Rural Short | Asset failure | HV | 16 | 317 | 0.037787 | 0.0001192 | Yes
22/11/2018 | 03:43:00 | SA16 | Urban | Third Party | Other | 1880 | 52 | 0.15629 | 0.0030055 | Yes
22/11/2018 | 03:52:59 | SM350F | Urban | Unknown | Unknown | 26 | 858.0001 | 0.035663 | 4.157e-05 | Yes
22/11/2018 | 03:54:01 | HH102A | Urban | Asset failure | HV | 65 | 1058 | 0.10994 | 0.00010391 | Yes
22/11/2018 | 03:55:26 | HH102A | Urban | Asset failure | HV | 634 | 82 | 0.083112 | 0.0010136 | Yes
22/11/2018 | 04:05:02 | NL511B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 575 | 0.021142 | 3.677e-05 | Yes
22/11/2018 | 04:09:58 | HH177A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 589 | 0.00094162 | 1.6e-06 | Yes
22/11/2018 | 04:30:37 | HH130F | Urban | Vegetation | Grow-in - NSP responsibility | 29.3333 | 943.0001 | 0.044221 | 4.689e-05 | Yes
22/11/2018 | 04:40:00 | CN31 | Rural Long | Asset failure | HV | 15 | 147 | 0.016093 | 0.00010948 | Yes
22/11/2018 | 04:43:00 | MV61 | Urban | Weather |  | 1949 | 15 | 0.046737 | 0.0031158 | Yes
22/11/2018 | 04:43:00 | MV62 | Rural Short | Weather |  | 2078 | 545 | 8.4374 | 0.015481 | Yes
22/11/2018 | 04:55:55 | MTB13 | Rural Short | Asset failure | LV | 1 | 461 | 0.0034345 | 7.45e-06 | Yes
22/11/2018 | 05:06:15 | HH432B | Urban | Vegetation | Grow-in - NSP responsibility | 27.3333 | 737 | 0.032205 | 4.37e-05 | Yes
22/11/2018 | 05:13:08 | HH341E | Urban | Overloads |  | 19.3333 | 1523.9999 | 0.047103 | 3.091e-05 | Yes
22/11/2018 | 05:39:10 | ME347F | Urban | Weather |  | 26 | 633 | 0.026311 | 4.157e-05 | Yes
22/11/2018 | 05:39:47 | HH118C | Urban | Vegetation | Grow-in - NSP responsibility | 23.3333 | 992 | 0.037004 | 3.73e-05 | Yes
22/11/2018 | 05:45:06 | ME200E | Urban | Vegetation | Grow-in - NSP responsibility | 72.6666 | 489 | 0.056807 | 0.00011617 | Yes
22/11/2018 | 05:47:34 | HH428F | Urban | Overloads |  | 51 | 812.9999 | 0.066286 | 8.153e-05 | Yes
22/11/2018 | 05:53:15 | HH341E | Urban | Asset failure | LV | 19.3333 | 962 | 0.029733 | 3.091e-05 | Yes
22/11/2018 | 05:59:57 | SM402B | Urban | Asset failure | LV | 16.6667 | 592 | 0.015774 | 2.664e-05 | Yes
22/11/2018 | 06:00:42 | SA744C | Urban | Third Party | Other | 6.3333 | 536 | 0.005427 | 1.012e-05 | Yes
22/11/2018 | 06:07:01 | HH118E | Urban | Asset failure | LV | 25 | 897 | 0.03585 | 3.997e-05 | Yes
22/11/2018 | 06:12:23 | KA03 | Rural Long | Weather |  | 1 | 293 | 0.0021384 | 7.3e-06 | Yes
22/11/2018 | 06:12:59 | HH148C | Urban | Asset failure | LV | 13 | 952 | 0.019785 | 2.078e-05 | Yes
22/11/2018 | 06:15:37 | SM402B | Urban | Asset failure | LV | 20 | 578 | 0.018481 | 3.197e-05 | Yes
22/11/2018 | 06:20:02 | AP226B | Urban | Asset failure | LV | 22 | 540 | 0.018992 | 3.517e-05 | Yes
22/11/2018 | 06:20:55 | HH130A | Urban | Vegetation | Grow-in - NSP responsibility | 32.6667 | 504 | 0.026321 | 5.222e-05 | Yes
22/11/2018 | 06:20:58 | MB123 | Rural Long | Unknown | Unknown | 75 | 222 | 0.12152 | 0.00054738 | Yes
22/11/2018 | 06:21:46 | MTB21 | Rural Short | Vegetation | Grow-in - NSP responsibility | 9.6667 | 463 | 0.033344 | 7.202e-05 | Yes
22/11/2018 | 06:22:16 | SA36 | Urban | Asset failure | HV | 2 | 1882 | 0.0060174 | 3.2e-06 | Yes
22/11/2018 | 06:30:06 | HH145C | Urban | Unknown | Unknown | 23.3333 | 949 | 0.0354 | 3.73e-05 | Yes
22/11/2018 | 06:33:54 | AP529D | Urban | Vegetation | Grow-in - NSP responsibility | 19.6666 | 640 | 0.020122 | 3.144e-05 | Yes
22/11/2018 | 06:35:36 | SM410B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 293 | 0.00046841 | 1.6e-06 | Yes
22/11/2018 | 06:42:43 | AP149F | Urban | Asset failure | LV | 61 | 1270 | 0.12385 | 9.752e-05 | Yes
22/11/2018 | 06:44:41 | HH102C | Urban | Vegetation | Grow-in - NSP responsibility | 16.3333 | 926 | 0.024179 | 2.611e-05 | Yes
22/11/2018 | 06:46:33 | VH23 | Rural Short | Asset failure | LV | 18 | 88 | 0.011801 | 0.0001341 | Yes
22/11/2018 | 06:49:43 | SA11 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13.6667 | 429 | 0.009373 | 2.185e-05 | Yes
22/11/2018 | 06:56:00 | PL07 | Urban | Asset failure | LV | 61 | 754 | 0.073529 | 9.752e-05 | Yes
22/11/2018 | 07:23:58 | VH45 | Rural Short | Asset failure | LV | 1 | 90 | 0.00067051 | 7.45e-06 | Yes
22/11/2018 | 07:24:04 | MTB21 | Rural Short | Asset failure | LV | 2.3333 | 880 | 0.015298 | 1.738e-05 | Yes
22/11/2018 | 07:31:44 | AP227B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 839.0001 | 0.0040239 | 4.8e-06 | Yes
22/11/2018 | 07:39:18 | AP344E | Urban | Asset failure | LV | 29.3333 | 585 | 0.027433 | 4.689e-05 | Yes
22/11/2018 | 07:46:26 | ST21 | Rural Short | Unknown | Unknown | 11 | 159 | 0.01303 | 8.195e-05 | Yes
22/11/2018 | 08:05:37 | MV15 | Rural Short | Asset failure | LV | 1.6667 | 402 | 0.0049916 | 1.242e-05 | Yes
22/11/2018 | 08:10:16 | MTB51 | Rural Long | Asset failure | LV | 1 | 284 | 0.0020727 | 7.3e-06 | Yes
22/11/2018 | 08:11:00 | SA36 | Urban | Unknown | Unknown | 2 | 890 | 0.0028456 | 3.2e-06 | Yes
22/11/2018 | 08:20:32 | SM402A | Urban | Weather |  | 5.3333 | 396 | 0.0033764 | 8.53e-06 | Yes
22/11/2018 | 08:39:35 | EL01N | Urban | Third Party | Other | 1 | 473 | 0.00075617 | 1.6e-06 | Yes
22/11/2018 | 08:40:34 | AP132D | Urban | Asset failure | LV | 1 | 355 | 0.00056753 | 1.6e-06 | Yes
22/11/2018 | 08:58:25 | SA20 | Urban | Asset failure | LV | 19 | 307 | 0.0093251 | 3.037e-05 | Yes
22/11/2018 | 09:03:35 | SG07 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 12 | 775 | 0.069286 | 8.94e-05 | Yes
22/11/2018 | 09:11:33 | AP227D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 71 | 484 | 0.054937 | 0.00011351 | Yes
22/11/2018 | 09:14:00 | AP372A | Urban | Asset failure | LV | 22 | 61 | 0.0021454 | 3.517e-05 | Yes
22/11/2018 | 09:16:06 | SG07 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 765 | 0.011399 | 1.49e-05 | Yes
22/11/2018 | 09:22:32 | AP529C | Urban | Unknown | Unknown | 1 | 382 | 0.00061069 | 1.6e-06 | Yes
22/11/2018 | 09:27:35 | MV61 | Urban | Asset failure | LV | 1 | 570 | 0.00091124 | 1.6e-06 | Yes
22/11/2018 | 09:28:17 | MT17 | Rural Short | Asset failure | LV | 1 | 308 | 0.0022947 | 7.45e-06 | Yes
22/11/2018 | 09:42:56 | HH409D | Urban | Asset failure | LV | 22.3333 | 47 | 0.0016781 | 3.57e-05 | Yes
22/11/2018 | 09:45:44 | HH341E | Urban | Asset failure | LV | 63 | 247 | 0.024877 | 0.00010072 | Yes
22/11/2018 | 09:56:13 | SA17 | Urban | Vegetation | Grow-in - NSP responsibility | 48 | 848 | 0.065072 | 7.674e-05 | Yes
22/11/2018 | 09:57:21 | SG03 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 338 | 0.0025181 | 7.45e-06 | Yes
22/11/2018 | 10:02:30 | SA14 | Urban | Asset failure | LV | 1 | 322 | 0.00051477 | 1.6e-06 | Yes
22/11/2018 | 10:05:39 | NL115C | Urban | Vegetation | Grow-in - NSP responsibility | 2.3333 | 309 | 0.0011526 | 3.73e-06 | Yes
22/11/2018 | 10:06:32 | AP529E | Urban | Asset failure | LV | 2 | 500 | 0.0015987 | 3.2e-06 | Yes
22/11/2018 | 10:06:35 | SM349F | Urban | Vegetation | Grow-in - NSP responsibility | 23.6666 | 705 | 0.026674 | 3.784e-05 | Yes
22/11/2018 | 10:32:07 | SM402D | Urban | Vegetation | Grow-in - NSP responsibility | 21 | 47 | 0.0015779 | 3.357e-05 | Yes
22/11/2018 | 10:39:56 | MB12 | Rural Short | Asset failure | LV | 1 | 95 | 0.00070776 | 7.45e-06 | Yes
22/11/2018 | 11:02:51 | AP529E | Urban | Asset failure | LV | 14 | 89 | 0.001992 | 2.238e-05 | Yes
22/11/2018 | 11:03:37 | AP351B | Urban | Third Party | Other | 3 | 450 | 0.0021582 | 4.8e-06 | Yes
22/11/2018 | 11:05:00 | PL14 | Urban | Third Party | Vehicle impact | 1 | 86 | 0.00013749 | 1.6e-06 | Yes
22/11/2018 | 11:10:59 | SM179B | Urban | Asset failure | LV | 12 | 437 | 0.0083834 | 1.918e-05 | Yes
22/11/2018 | 11:20:32 | CBD412E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 132 | 0.00021103 | 1.6e-06 | Yes
22/11/2018 | 11:23:04 | VH21 | Rural Short | Asset failure | LV | 1 | 84 | 0.00062581 | 7.45e-06 | Yes
22/11/2018 | 11:38:18 | SM172D | Urban | Asset failure | LV | 23.3333 | 462 | 0.017234 | 3.73e-05 | Yes
22/11/2018 | 11:42:14 | AP146D | Urban | Vegetation | Grow-in - NSP responsibility | 45 | 84 | 0.006043 | 7.194e-05 | Yes
22/11/2018 | 11:42:40 | HH341D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2214 | 166.6107 | 0.58971 | 0.0035395 | Yes
22/11/2018 | 11:45:14 | MV31 | Rural Short | Asset failure | LV | 1 | 143 | 0.0010654 | 7.45e-06 | Yes
22/11/2018 | 11:57:12 | HH102D | Urban | Vegetation | Grow-in - NSP responsibility | 15 | 758 | 0.018177 | 2.398e-05 | Yes
22/11/2018 | 12:05:48 | HH102D | Urban | Unknown | Unknown | 28 | 747 | 0.033438 | 4.476e-05 | Yes
22/11/2018 | 12:19:00 | SA16 | Urban | Unknown | Unknown | 1880 | 177 | 0.53198 | 0.0030055 | Yes
22/11/2018 | 12:29:55 | VH61 | Rural Short | Asset failure | LV | 2 | 168 | 0.0025032 | 1.49e-05 | Yes
22/11/2018 | 12:52:13 | CBD367N | Urban | Vegetation | Grow-in - NSP responsibility | 1.6667 | 224 | 0.00059684 | 2.66e-06 | Yes
22/11/2018 | 13:05:48 | SM126C | Urban | Unknown | Unknown | 35 | 437 | 0.024452 | 5.595e-05 | Yes
22/11/2018 | 13:08:07 | SA711C | Urban | Asset failure | LV | 1 | 252 | 0.00040287 | 1.6e-06 | Yes
22/11/2018 | 13:21:57 | HH102D | Urban | Other |  | 2 | 670 | 0.0021422 | 3.2e-06 | Yes
22/11/2018 | 13:35:05 | SM350G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 47.3334 | 475 | 0.035944 | 7.567e-05 | Yes
22/11/2018 | 13:40:24 | MV53 | Rural Short | Unknown | Unknown | 6 | 276 | 0.012337 | 4.47e-05 | Yes
22/11/2018 | 13:46:16 | SM126E | Urban | Asset failure | HV | 2 | 590 | 0.0018864 | 3.2e-06 | Yes
22/11/2018 | 13:50:21 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 516 | 0.0076885 | 1.49e-05 | Yes
22/11/2018 | 13:57:56 | VH45 | Rural Short | Unknown | Unknown | 1 | 256 | 0.0019072 | 7.45e-06 | Yes
22/11/2018 | 14:20:00 | SM137B | Urban | Asset failure | HV | 93 | 97 | 0.014422 | 0.00014868 | Yes
22/11/2018 | 14:35:21 | HH429C | Urban | Vegetation | Grow-in - NSP responsibility | 42 | 539 | 0.036191 | 6.714e-05 | Yes
22/11/2018 | 14:39:18 | MTB53 | Rural Long | Asset failure | LV | 1 | 301 | 0.0021968 | 7.3e-06 | Yes
22/11/2018 | 15:44:08 | SA16 | Urban | Asset failure | LV | 58 | 319 | 0.029579 | 9.272e-05 | Yes
22/11/2018 | 15:46:49 | SA16 | Urban | Unknown | Unknown | 38 | 146 | 0.0088694 | 6.075e-05 | Yes
22/11/2018 | 15:47:49 | NL115F | Urban | Asset failure | LV | 115 | 174 | 0.031989 | 0.00018385 | Yes
22/11/2018 | 16:13:52 | HH386C | Urban | Unknown | Unknown | 27.3333 | 468 | 0.02045 | 4.37e-05 | Yes
22/11/2018 | 16:25:41 | MG34 | Rural Long | Asset failure | HV | 1 | 25 | 0.00018246 | 7.3e-06 | Yes
22/11/2018 | 16:42:34 | SA36 | Urban | Asset failure | LV | 12 | 308 | 0.0059087 | 1.918e-05 | Yes
22/11/2018 | 16:53:09 | SM216B | Urban | Vegetation | Grow-in - NSP responsibility | 69 | 306 | 0.033754 | 0.00011031 | Yes
22/11/2018 | 17:19:27 | NL115C | Urban | Asset failure | LV | 47 | 93 | 0.0069878 | 7.514e-05 | Yes
22/11/2018 | 17:29:59 | AP227D | Urban | Asset failure | LV | 23.6666 | 122 | 0.0046159 | 3.784e-05 | Yes
22/11/2018 | 17:33:23 | ME427F | Urban | Weather |  | 70.6667 | 77 | 0.0086989 | 0.00011297 | Yes
22/11/2018 | 17:39:22 | NL111C | Urban | Vegetation | Grow-in - NSP responsibility | 81 | 160 | 0.020719 | 0.00012949 | Yes
22/11/2018 | 18:22:06 | SM350F | Urban | Vegetation | Grow-in - NSP responsibility | 52 | 415 | 0.034499 | 8.313e-05 | Yes
22/11/2018 | 18:27:18 | AP425C | Urban | Unknown | Unknown | 2.6667 | 957.0001 | 0.0040798 | 4.26e-06 | Yes
22/11/2018 | 18:48:58 | SA16 | Urban | Asset failure | LV | 54 | 130 | 0.011223 | 8.633e-05 | Yes
22/11/2018 | 18:50:24 | SA16 | Urban | Overloads |  | 1 | 146 | 0.00023341 | 1.6e-06 | Yes
22/11/2018 | 19:44:23 | AP227D | Urban | Asset failure | HV | 47.3334 | 173 | 0.013091 | 7.567e-05 | Yes
22/11/2018 | 19:47:19 | ME131A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 530 | 0.0008473 | 1.6e-06 | Yes
22/11/2018 | 19:50:11 | SM137A | Urban | Weather |  | 7 | 121 | 0.0013541 | 1.119e-05 | Yes
22/11/2018 | 20:06:40 | HH177E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 58 | 290 | 0.02689 | 9.272e-05 | Yes
22/11/2018 | 20:36:44 | SM410B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 979 | 0.0015651 | 1.6e-06 | Yes
22/11/2018 | 20:58:00 | AP227D | Urban | Asset failure | HV | 47.3334 | 108 | 0.0081724 | 7.567e-05 | Yes
22/11/2018 | 22:36:20 | SM216B | Urban | Overloads |  | 23 | 85 | 0.0031254 | 3.677e-05 | Yes
23/11/2018 | 00:30:34 | SM410A | Urban | Other |  | 3 | 251 | 0.0012038 | 4.8e-06 | No
23/11/2018 | 00:47:11 | HH432F | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 149 | 0.0002382 | 1.6e-06 | No
23/11/2018 | 01:54:18 | SM216E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 105 | 36 | 0.006043 | 0.00016786 | No
23/11/2018 | 02:30:17 | SD40502 | Rural Long | Asset failure | Distribution substation | 2672 | 301.7754 | 5.885 | 0.019501 | No
23/11/2018 | 03:31:55 | SA744D | Urban | Asset failure | LV | 42 | 132 | 0.0088631 | 6.714e-05 | No
23/11/2018 | 05:35:22 | HH341A | Urban | Weather |  | 44 | 31 | 0.0021806 | 7.034e-05 | No
23/11/2018 | 06:53:12 | SM216B | Urban | Asset failure | LV | 1.3333 | 272 | 0.00057979 | 2.13e-06 | No
23/11/2018 | 07:26:25 | AP529D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 586 | 0.00093682 | 1.6e-06 | No
23/11/2018 | 08:01:01 | KI31 | Rural Short | Planned |  | 2 | 32 | 0.00047681 | 1.49e-05 | No
23/11/2018 | 08:09:56 | SM350A | Urban | Third Party | Vehicle impact | 35.3334 | 85 | 0.0048014 | 5.649e-05 | No
23/11/2018 | 08:19:58 | HH432E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 677 | 0.0010823 | 1.6e-06 | No
23/11/2018 | 08:36:49 | SA36 | Urban | Asset failure | HV | 1 | 375 | 0.0005995 | 1.6e-06 | No
23/11/2018 | 08:50:37 | AP344F | Urban | Asset failure | LV | 3 | 1881 | 0.0090213 | 4.8e-06 | No
23/11/2018 | 09:12:59 | SA17 | Urban | Asset failure | LV | 67 | 81 | 0.008676 | 0.00010711 | No
23/11/2018 | 09:48:53 | SM350A | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
23/11/2018 | 10:10:21 | CD03 | Rural Short | Planned |  | 1 | 87 | 0.00064816 | 7.45e-06 | No
23/11/2018 | 10:31:00 | MV33 | Rural Short | Planned |  | 43 | 199 | 0.063751 | 0.00032036 | No
23/11/2018 | 10:39:08 | MV64 | Urban | Asset failure | LV | 63 | 126 | 0.01269 | 0.00010072 | No
23/11/2018 | 10:53:58 | AP424B | Urban | Asset failure | LV | 1 | 78 | 0.0001247 | 1.6e-06 | No
23/11/2018 | 11:08:10 | AP373E | Urban | Asset failure | LV | 1 | 156 | 0.00024939 | 1.6e-06 | No
23/11/2018 | 11:45:28 | AP146C | Urban | Asset failure | LV | 6 | 28 | 0.00026858 | 9.59e-06 | No
23/11/2018 | 11:45:30 | SM126E | Urban | Weather |  | 1 | 60 | 9.592e-05 | 1.6e-06 | No
23/11/2018 | 11:46:28 | PP03 | Urban | Overloads |  | 1 | 602 | 0.0009624 | 1.6e-06 | No
23/11/2018 | 12:24:57 | EL02 | Urban | Asset failure | LV | 27 | 106 | 0.0045754 | 4.316e-05 | No
23/11/2018 | 12:25:11 | EL02 | Urban | Asset failure | LV | 24 | 104 | 0.0039903 | 3.837e-05 | No
23/11/2018 | 12:25:53 | HH341E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 66 | 0.00010551 | 1.6e-06 | No
23/11/2018 | 12:52:23 | AP344F | Urban | Asset failure | LV | 1 | 378 | 0.0006043 | 1.6e-06 | No
23/11/2018 | 13:58:45 | KI12 | Rural Long | Unknown | Unknown | 2 | 140 | 0.0020435 | 1.46e-05 | No
23/11/2018 | 16:09:27 | SA16 | Urban | Asset failure | LV | 57 | 76 | 0.0069255 | 9.112e-05 | No
23/11/2018 | 16:25:52 | SA16 | Urban | Asset failure | LV | 2.3333 | 209 | 0.00077962 | 3.73e-06 | No
23/11/2018 | 16:42:37 | VH18 | Rural Short | Unknown | Unknown | 1 | 170 | 0.0012665 | 7.45e-06 | No
23/11/2018 | 17:20:30 | AP373J | Urban | Planned |  | 1 | 2971 | 0.0047497 | 1.6e-06 | No
23/11/2018 | 20:50:09 | AP227A | Urban | Unknown | Unknown | 164 | 20 | 0.0052436 | 0.00026218 | No
24/11/2018 | 00:28:16 | HH145B | Urban | Unknown | Unknown | 231 | 134 | 0.049485 | 0.00036929 | No
24/11/2018 | 09:05:15 | SM126B | Urban | Unknown | Unknown | 8.6667 | 215 | 0.0029789 | 1.386e-05 | No
24/11/2018 | 09:14:15 | MB13 | Rural Short | Asset failure | LV | 1 | 229 | 0.0017061 | 7.45e-06 | No
24/11/2018 | 10:34:03 | AP227B | Urban | Asset failure | LV | 53 | 63 | 0.005338 | 8.473e-05 | No
24/11/2018 | 10:39:40 | HH522B | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
24/11/2018 | 11:06:40 | NL210A | Urban | Asset failure | LV | 1 | 380 | 0.0006075 | 1.6e-06 | No
24/11/2018 | 12:01:23 | NL210B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 109 | 0.00017426 | 1.6e-06 | No
24/11/2018 | 12:03:02 | SM349B | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 292 | 0.00093363 | 3.2e-06 | No
24/11/2018 | 14:41:59 | SD54100 | Urban | Weather |  | 1573 | 239 | 0.60102 | 0.0025147 | No
24/11/2018 | 14:41:59 | SD54100 | Rural Long | Weather |  | 2687 | 239.9073 | 4.7047 | 0.019611 | No
24/11/2018 | 14:46:38 | NL511B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1882 | 89 | 0.26777 | 0.0030087 | No
24/11/2018 | 15:31:43 | HH145B | Urban | Asset failure | LV | 1 | 207 | 0.00033093 | 1.6e-06 | No
24/11/2018 | 16:24:19 | CV28 | Rural Long | Weather |  | 23 | 181.4783 | 0.030463 | 0.00016786 | No
24/11/2018 | 16:52:06 | HH177F | Urban | Asset failure | LV | 1 | 265 | 0.00042365 | 1.6e-06 | No
24/11/2018 | 19:40:13 | HH130A | Urban | Asset failure | LV | 1 | 193 | 0.00030854 | 1.6e-06 | No
24/11/2018 | 21:13:18 | R11 | Rural Long | Unknown | Unknown | 1 | 23 | 0.00016786 | 7.3e-06 | No
24/11/2018 | 23:06:43 | HH177G | Urban | Overloads |  | 1 | 390 | 0.00062348 | 1.6e-06 | No
25/11/2018 | 01:41:13 | HH386G | Urban | Animal | Animal impact | 835 | 76 | 0.10145 | 0.0013349 | No
25/11/2018 | 04:19:18 | HH522A | Urban | Asset failure | LV | 21.3333 | 499 | 0.017018 | 3.411e-05 | No
25/11/2018 | 07:59:19 | ME427A | Urban | Planned |  | 2 | 136 | 0.00043484 | 3.2e-06 | No
25/11/2018 | 08:21:15 | MG44 | Urban | Planned |  | 15 | 135 | 0.0032373 | 2.398e-05 | No
25/11/2018 | 09:03:42 | AP351E | Urban | Planned |  | 1 | 256 | 0.00040926 | 1.6e-06 | No
25/11/2018 | 09:04:06 | NL760A | Urban | Planned |  | 29 | 230 | 0.010663 | 4.636e-05 | No
25/11/2018 | 09:21:49 | SM402A | Urban | Planned |  | 6 | 225 | 0.0021582 | 9.59e-06 | No
25/11/2018 | 09:24:17 | HH403A | Urban | Planned |  | 90 | 263 | 0.037841 | 0.00014388 | No
25/11/2018 | 10:30:54 | CBD103A | Urban | Asset failure | LV | 1 | 197 | 0.00031494 | 1.6e-06 | No
25/11/2018 | 10:57:23 | SM411C | Urban | Asset failure | LV | 18.6666 | 227 | 0.0067741 | 2.984e-05 | No
25/11/2018 | 11:37:28 | SA17 | Urban | Asset failure | LV | 50 | 71 | 0.0056753 | 7.993e-05 | No
25/11/2018 | 11:48:29 | SD54102 | Rural Long | Other |  | 1 | 152 | 0.0011094 | 7.3e-06 | No
25/11/2018 | 11:58:35 | HH386E | Urban | Asset failure | LV | 2 | 261 | 0.00083451 | 3.2e-06 | No
25/11/2018 | 12:17:22 | HH341B | Urban | Asset failure | LV | 1 | 277 | 0.00044283 | 1.6e-06 | No
25/11/2018 | 12:40:10 | SD54102 | Rural Long | Unknown | Unknown | 1 | 90 | 0.00065685 | 7.3e-06 | No
25/11/2018 | 13:10:17 | HH522B | Urban | Asset failure | LV | 1 | 371 | 0.00059311 | 1.6e-06 | No
25/11/2018 | 13:38:44 | G08 | Rural Long | Asset failure | HV | 31 | 321.7097 | 0.072786 | 0.00022625 | No
25/11/2018 | 13:54:03 | HH107A | Urban | Planned |  | 1 | 27 | 4.316e-05 | 1.6e-06 | No
25/11/2018 | 14:09:29 | PA26 | Rural Long | Other |  | 15 | 32 | 0.0035032 | 0.00010947 | No
25/11/2018 | 14:44:27 | PA26 | Rural Long | Other |  | 1 | 9 | 6.569e-05 | 7.3e-06 | No
25/11/2018 | 14:48:56 | SM349C | Urban | Overloads |  | 1 | 175 | 0.00027977 | 1.6e-06 | No
25/11/2018 | 15:37:35 | CD15 | Rural Long | Unknown | Unknown | 1 | 188 | 0.0013721 | 7.3e-06 | No
25/11/2018 | 16:18:11 | AP365F | Urban | Weather |  | 143 | 117 | 0.026747 | 0.00022861 | No
25/11/2018 | 20:57:35 | HH409D | Urban | Asset failure | LV | 1 | 365 | 0.00058352 | 1.6e-06 | No
25/11/2018 | 21:37:02 | HH409D | Urban | Animal | Animal impact | 173 | 209 | 0.057803 | 0.00027657 | No
25/11/2018 | 21:37:02 | HH409D | Urban | Animal | Animal impact | 1 | 4 | 6.39e-06 | 1.6e-06 | No
25/11/2018 | 22:54:15 | HH177G | Urban | Overloads |  | 1 | 813 | 0.0012997 | 1.6e-06 | No
26/11/2018 | 01:33:13 | HH148D | Urban | Unknown | Unknown | 889 | 11.2373 | 0.015971 | 0.0014212 | No
26/11/2018 | 04:56:26 | MB13 | Rural Short | Asset failure | LV | 5 | 107 | 0.0039858 | 3.725e-05 | No
26/11/2018 | 08:30:02 | M11 | Rural Long | Other |  | 1 | 114 | 0.00083201 | 7.3e-06 | No
26/11/2018 | 08:39:36 | R23 | Rural Long | Asset failure | LV | 1 | 85 | 0.00062036 | 7.3e-06 | No
26/11/2018 | 08:40:21 | WHY07 | Urban | Asset failure | LV | 1 | 147 | 0.00023501 | 1.6e-06 | No
26/11/2018 | 08:48:38 | HH107C | Urban | Planned |  | 371 | 536 | 0.31791 | 0.00059311 | No
26/11/2018 | 10:01:00 | CV31 | Rural Long | Planned |  | 1 | 160 | 0.0011677 | 7.3e-06 | No
26/11/2018 | 10:22:45 | MI08 | Rural Long | Planned |  | 1 | 265 | 0.0019341 | 7.3e-06 | No
26/11/2018 | 11:04:43 | SB18 | Rural Long | Planned |  | 10 | 191 | 0.01394 | 7.298e-05 | No
26/11/2018 | 11:43:53 | SA17 | Urban | Asset failure | LV | 50 | 65 | 0.0051957 | 7.993e-05 | No
26/11/2018 | 11:44:18 | SA17 | Urban | Asset failure | LV | 31 | 66 | 0.0032709 | 4.956e-05 | No
26/11/2018 | 12:02:46 | HH145D | Urban | Unknown | Unknown | 37.3334 | 95 | 0.00567 | 5.968e-05 | No
26/11/2018 | 12:45:46 | CD01 | Rural Short | Weather |  | 633 | 99.9273 | 0.47125 | 0.0047159 | No
26/11/2018 | 12:47:51 | G02 | Rural Long | Planned |  | 289 | 136 | 0.28685 | 0.0021092 | No
26/11/2018 | 12:59:11 | SA17 | Urban | Asset failure | LV | 63 | 78 | 0.0078559 | 0.00010072 | No
26/11/2018 | 13:00:03 | SA17 | Urban | Asset failure | LV | 62 | 121 | 0.011993 | 9.912e-05 | No
26/11/2018 | 14:40:57 | WK65 | Rural Short | Third Party | Other | 130 | 164.7308 | 0.15954 | 0.00096852 | No
26/11/2018 | 17:13:00 | M11 | Rural Long | Asset failure | LV | 5 | 72 | 0.0026274 | 3.649e-05 | No
26/11/2018 | 17:15:36 | NL210B | Urban | Overloads |  | 1 | 275 | 0.00043964 | 1.6e-06 | No
26/11/2018 | 18:16:53 | VH34 | Rural Short | Asset failure | LV | 4 | 90 | 0.0026821 | 2.98e-05 | No
26/11/2018 | 19:10:22 | SA41 | Urban | Asset failure | LV | 1 | 135 | 0.00021582 | 1.6e-06 | No
26/11/2018 | 19:29:23 | KA30 | Rural Short | Unknown | Unknown | 1 | 2216 | 0.01651 | 7.45e-06 | No
26/11/2018 | 20:11:14 | WK42 | Rural Short | Asset failure | LV | 1 | 1290 | 0.0096107 | 7.45e-06 | No
26/11/2018 | 22:11:03 | CD03 | Rural Short | Asset failure | LV | 1 | 167 | 0.0012442 | 7.45e-06 | No
26/11/2018 | 23:47:19 | SD37500 | Rural Short | Third Party | Vehicle impact | 2269 | 165.6558 | 2.8003 | 0.016904 | No
27/11/2018 | 05:06:59 | SM126C | Urban | Unknown | Unknown | 872 | 36.6479 | 0.051089 | 0.001394 | No
27/11/2018 | 07:17:10 | HH145B | Urban | Asset failure | LV | 1 | 267 | 0.00042685 | 1.6e-06 | No
27/11/2018 | 08:13:19 | EL25 | Urban | Overloads |  | 1 | 210 | 0.00033572 | 1.6e-06 | No
27/11/2018 | 08:23:26 | GU15 | Rural Long | Planned |  | 5 | 232 | 0.0084661 | 3.649e-05 | No
27/11/2018 | 08:30:02 | AP125D | Urban | Planned |  | 435 | 313 | 0.21767 | 0.00069542 | No
27/11/2018 | 08:47:55 | AP125C | Urban | Asset failure | LV | 1 | 317 | 0.00050678 | 1.6e-06 | No
27/11/2018 | 08:49:15 | MV63 | Rural Short | Planned |  | 53 | 213 | 0.084105 | 0.00039486 | No
27/11/2018 | 08:55:50 | NL210A | Urban | Planned |  | 3 | 391 | 0.0018752 | 4.8e-06 | No
27/11/2018 | 08:57:13 | MB81 | Rural Long | Planned |  | 17 | 204 | 0.025311 | 0.00012407 | No
27/11/2018 | 08:57:56 | ST22 | Rural Short | Planned |  | 10 | 5 | 0.00037251 | 7.45e-05 | No
27/11/2018 | 09:01:45 | MTB13 | Rural Short | Planned |  | 58 | 172 | 0.074323 | 0.00043211 | No
27/11/2018 | 09:28:57 | CBD412A | CBD | Vegetation | Grow-in - NSP responsibility | 4 | 267 | 0.20732 | 0.00077647 | No
27/11/2018 | 09:30:38 | M93 | Rural Long | Planned |  | 16 | 131 | 0.015297 | 0.00011677 | No
27/11/2018 | 09:46:59 | ST16 | Rural Short | Planned |  | 52 | 358 | 0.13869 | 0.00038741 | No
27/11/2018 | 10:05:30 | R16 | Rural Long | Planned |  | 3 | 142 | 0.0031091 | 2.19e-05 | No
27/11/2018 | 10:17:50 | CN24 | Rural Long | Other |  | 1.3333 | 509 | 0.0049531 | 9.73e-06 | No
27/11/2018 | 10:22:06 | LM52 | Rural Long | Planned |  | 36 | 355 | 0.093273 | 0.00026274 | No
27/11/2018 | 12:04:31 | HH130A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 358 | 0.00057233 | 1.6e-06 | No
27/11/2018 | 12:41:05 | EL15 | Urban | Third Party | Vehicle impact | 21 | 388.8571 | 0.013055 | 3.357e-05 | No
27/11/2018 | 13:31:48 | NL760B | Urban | Asset failure | LV | 1 | 538 | 0.00086009 | 1.6e-06 | No
27/11/2018 | 13:32:40 | AP125D | Urban | Asset failure | LV | 1 | 286 | 0.00045722 | 1.6e-06 | No
27/11/2018 | 13:36:59 | PP12 | Rural Long | Unknown | Unknown | 18 | 143.3333 | 0.01883 | 0.00013137 | No
27/11/2018 | 14:47:04 | GA22 | Rural Short | Third Party | Other | 1 | 164 | 0.0012218 | 7.45e-06 | No
27/11/2018 | 15:14:43 | AP529E | Urban | Asset failure | LV | 1 | 243 | 0.00038848 | 1.6e-06 | No
27/11/2018 | 16:12:35 | SA31 | Urban | Asset failure | LV | 1 | 228 | 0.0003645 | 1.6e-06 | No
27/11/2018 | 16:26:54 | SM374A | Urban | Vegetation | Grow-in - NSP responsibility | 60 | 246 | 0.023596 | 9.592e-05 | No
27/11/2018 | 18:29:03 | HH145E | Urban | Asset failure | LV | 61 | 330 | 0.032181 | 9.752e-05 | No
27/11/2018 | 19:45:02 | HH432C | Urban | Overloads |  | 1 | 159 | 0.00025419 | 1.6e-06 | No
27/11/2018 | 21:00:26 | HH121C | Urban | Third Party | Vehicle impact | 34 | 216 | 0.011741 | 5.435e-05 | No
27/11/2018 | 21:43:08 | SA14 | Urban | Asset failure | LV | 44 | 64 | 0.0045019 | 7.034e-05 | No
27/11/2018 | 22:36:31 | NL451A / NL451B | Urban | Planned |  | 93 | 297.6129 | 0.044248 | 0.00014868 | No
28/11/2018 | 00:45:02 | HH432E | Urban | Planned |  | 14 | 42 | 0.00094002 | 2.238e-05 | No
28/11/2018 | 02:11:12 | VH71 | Rural Short | Asset failure | HV | 1 | 573 | 0.0042689 | 7.45e-06 | No
28/11/2018 | 02:53:12 | PL32 | Urban | Third Party | Vehicle impact | 3922 | 77.4809 | 0.48581 | 0.00627 | No
28/11/2018 | 06:22:34 | G20 | Rural Long | Unknown | Unknown | 57 | 284.6316 | 0.11841 | 0.00041601 | No
28/11/2018 | 07:44:15 | MV12 | Urban | Weather |  | 6 | 504 | 0.0048344 | 9.59e-06 | No
28/11/2018 | 07:46:27 | MTB22 | Rural Short | Planned |  | 4 | 2 | 5.96e-05 | 2.98e-05 | No
28/11/2018 | 08:26:04 | GU11 | Rural Long | Planned |  | 30 | 244 | 0.053424 | 0.00021895 | No
28/11/2018 | 08:32:39 | LX43 | Rural Short | Planned |  | 33 | 304 | 0.07474 | 0.00024585 | No
28/11/2018 | 08:55:46 | AP226C | Urban | Planned |  | 71 | 52 | 0.0059023 | 0.00011351 | No
28/11/2018 | 09:14:15 | MTB52 | Rural Long | Unknown | Unknown | 68 | 8 | 0.0039703 | 0.00049629 | No
28/11/2018 | 09:16:00 | HH341G | Urban | Planned |  | 3 | 402 | 0.001928 | 4.8e-06 | No
28/11/2018 | 09:21:18 | YK03 | Rural Long | Planned |  | 3 | 329 | 0.0072035 | 2.19e-05 | No
28/11/2018 | 09:30:27 | NL111A | Urban | Asset failure | HV | 1509 | 68.0252 | 0.1641 | 0.0024124 | No
28/11/2018 | 09:36:43 | HH341G | Urban | Planned |  | 1 | 381 | 0.0006091 | 1.6e-06 | No
28/11/2018 | 09:50:06 | MG22 | Rural Long | Planned |  | 2 | 277 | 0.0040433 | 1.46e-05 | No
28/11/2018 | 10:10:33 | MTB51 | Rural Long | Planned |  | 67 | 196 | 0.095842 | 0.00048899 | No
28/11/2018 | 10:10:52 | MV62 | Rural Short | Planned |  | 90 | 133 | 0.089178 | 0.00067051 | No
28/11/2018 | 10:24:47 | AP125D | Urban | Asset failure | LV | 1 | 134 | 0.00021422 | 1.6e-06 | No
28/11/2018 | 10:33:42 | MV61 | Urban | Planned |  | 1 | 325 | 0.00051957 | 1.6e-06 | No
28/11/2018 | 10:36:16 | CN61 | Rural Long | Planned |  | 1 | 107 | 0.00078092 | 7.3e-06 | No
28/11/2018 | 10:39:13 | CV19 | Rural Long | Asset failure | HV | 9 | 244.4444 | 0.016056 | 6.569e-05 | No
28/11/2018 | 12:40:07 | ME131C | Urban | Asset failure | LV | 1 | 358 | 0.00057233 | 1.6e-06 | No
28/11/2018 | 13:07:22 | HH145C | Urban | Overloads |  | 1 | 63 | 0.00010072 | 1.6e-06 | No
28/11/2018 | 13:22:26 | NL451C | Urban | Asset failure | LV | 63 | 52 | 0.0052373 | 0.00010072 | No
28/11/2018 | 13:43:34 | VH17 | Rural Short | Planned |  | 2 | 55 | 0.00081952 | 1.49e-05 | No
28/11/2018 | 14:02:44 | SSD495 | Urban | Planned |  | 1 | 1451 | 0.0023197 | 1.6e-06 | No
28/11/2018 | 14:02:44 | SSD495 | Urban | Planned |  | 1 | 31 | 4.956e-05 | 1.6e-06 | No
28/11/2018 | 15:28:51 | HH145D | Urban | Overloads |  | 64 | 160.0833 | 0.016379 | 0.00010232 | No
28/11/2018 | 17:18:54 | VH15 | Rural Short | Planned |  | 44 | 107 | 0.035075 | 0.00032781 | No
28/11/2018 | 18:49:39 | MV61 | Urban | Asset failure | LV | 1 | 260 | 0.00041566 | 1.6e-06 | No
28/11/2018 | 19:45:12 | HH341D | Urban | Asset failure | LV | 1 | 159 | 0.00025419 | 1.6e-06 | No
29/11/2018 | 05:20:56 | HH145A | Urban | Asset failure | LV | 7.6667 | 297 | 0.0036402 | 1.226e-05 | No
29/11/2018 | 05:54:12 | HH102C | Urban | Asset failure | LV | 38.6666 | 197 | 0.012178 | 6.182e-05 | No
29/11/2018 | 07:02:43 | WHY01 | Urban | Asset failure | LV | 1 | 463 | 0.00074019 | 1.6e-06 | No
29/11/2018 | 08:42:50 | EL20 | Urban | Planned |  | 19 | 61 | 0.0018529 | 3.037e-05 | No
29/11/2018 | 08:50:11 | MG32 | Rural Long | Planned |  | 252 | 343 | 0.63084 | 0.0018392 | No
29/11/2018 | 08:55:02 | MTB53 | Rural Long | Planned |  | 230 | 348 | 0.58416 | 0.0016786 | No
29/11/2018 | 09:21:32 | HH496E | Urban | Planned |  | 1 | 1627 | 0.002601 | 1.6e-06 | No
29/11/2018 | 09:21:44 | SG12 | Rural Short | Planned |  | 253 | 322 | 0.60693 | 0.0018849 | No
29/11/2018 | 09:36:39 | NL210A | Urban | Planned |  | 3 | 300 | 0.0014388 | 4.8e-06 | No
29/11/2018 | 10:02:04 | AP424E | Urban | Planned |  | 208 | 338 | 0.11239 | 0.00033252 | No
29/11/2018 | 10:07:17 | NL210A | Urban | Planned |  | 110 | 193 | 0.03394 | 0.00017585 | No
29/11/2018 | 10:57:29 | G42 | Rural Long | Planned |  | 2 | 34 | 0.00049629 | 1.46e-05 | No
29/11/2018 | 11:00:14 | MG29 | Rural Long | Planned |  | 2 | 104 | 0.001518 | 1.46e-05 | No
29/11/2018 | 11:03:11 | LM52 | Rural Long | Planned |  | 1 | 99 | 0.00072254 | 7.3e-06 | No
29/11/2018 | 11:28:45 | HH107A | Urban | Planned |  | 87 | 230 | 0.031989 | 0.00013908 | No
29/11/2018 | 13:26:53 | HH341G | Urban | Asset failure | LV | 154 | 59 | 0.014526 | 0.0002462 | No
29/11/2018 | 16:35:23 | CL06 | Rural Long | Unknown | Unknown | 138 | 99 | 0.09971 | 0.0010072 | No
29/11/2018 | 17:29:20 | SG12 | Rural Short | Third Party | Vehicle impact | 1 | 141 | 0.0010505 | 7.45e-06 | No
29/11/2018 | 18:28:05 | MG17 | Rural Long | Asset failure | Distribution substation | 1 | 3 | 2.19e-05 | 7.3e-06 | No
29/11/2018 | 22:47:02 | HH432F | Urban | Overloads |  | 1.3333 | 269 | 0.00057339 | 2.13e-06 | No
29/11/2018 | 22:59:02 | AP227B | Urban | Asset failure | LV | 26 | 100 | 0.0041566 | 4.157e-05 | No
30/11/2018 | 01:33:38 | HH341K | Urban | Asset failure | LV | 61 | 63 | 0.0061437 | 9.752e-05 | No
30/11/2018 | 06:37:08 | HH341D | Urban | Unknown | Unknown | 18.6666 | 147 | 0.0043868 | 2.984e-05 | No
30/11/2018 | 06:58:14 | NL111C | Urban | Planned |  | 1 | 97 | 0.00015507 | 1.6e-06 | No
30/11/2018 | 07:20:23 | VH44 | Rural Short | Unknown | Unknown | 1 | 88 | 0.00065561 | 7.45e-06 | No
30/11/2018 | 07:44:11 | MI33 | Rural Long | Asset failure | HV | 1 | 122 | 0.0008904 | 7.3e-06 | No
30/11/2018 | 08:26:06 | MV52 | Rural Short | Planned |  | 56 | 362 | 0.15103 | 0.00041721 | No
30/11/2018 | 08:51:32 | SM172E | Urban | Planned |  | 21 | 314 | 0.010542 | 3.357e-05 | No
30/11/2018 | 08:58:22 | CL10 | Rural Long | Planned |  | 1 | 211 | 0.0015399 | 7.3e-06 | No
30/11/2018 | 09:10:00 | LX51 | Rural Short | Planned |  | 29 | 245 | 0.052933 | 0.00021605 | No
30/11/2018 | 09:18:41 | MTB54 | Rural Long | Planned |  | 1 | 156 | 0.0011385 | 7.3e-06 | No
30/11/2018 | 09:20:55 | SM179B | Urban | Planned |  | 1 | 217 | 0.00034691 | 1.6e-06 | No
30/11/2018 | 09:22:44 | SM350G | Urban | Planned |  | 15 | 212 | 0.0050838 | 2.398e-05 | No
30/11/2018 | 09:25:33 | CD16 | Rural Short | Planned |  | 2 | 14 | 0.0002086 | 1.49e-05 | No
30/11/2018 | 09:34:07 | VH23 | Rural Short | Planned |  | 544 | 335 | 1.3577 | 0.0040529 | No
30/11/2018 | 09:44:42 | HH177E | Urban | Planned |  | 92 | 80 | 0.011766 | 0.00014708 | No
30/11/2018 | 09:57:28 | SM350G | Urban | Planned |  | 143 | 140 | 0.032005 | 0.00022861 | No
30/11/2018 | 10:06:57 | MTB53 | Rural Long | Planned |  | 13 | 74 | 0.007021 | 9.488e-05 | No
30/11/2018 | 10:19:15 | MV13 | Rural Short | Planned |  | 67 | 217 | 0.10832 | 0.00049916 | No
30/11/2018 | 10:22:29 | SA18 | Urban | Asset failure | LV | 58 | 106 | 0.0098286 | 9.272e-05 | No
30/11/2018 | 10:51:20 | SM350F | Urban | Planned |  | 1 | 127 | 0.00020303 | 1.6e-06 | No
30/11/2018 | 11:02:46 | CN77 | Rural Long | Unknown | Unknown | 75 | 194 | 0.10619 | 0.00054738 | No
30/11/2018 | 11:15:12 | SM350F | Urban | Planned |  | 1 | 103 | 0.00016466 | 1.6e-06 | No
30/11/2018 | 11:19:37 | CD03 | Rural Short | Asset failure | LV | 2 | 45 | 0.00067051 | 1.49e-05 | No
30/11/2018 | 11:25:34 | MI31 | Rural Long | Unknown | Unknown | 2 | 4 | 5.839e-05 | 1.46e-05 | No
30/11/2018 | 11:41:36 | VH17 | Rural Short | Planned |  | 23 | 67 | 0.011481 | 0.00017135 | No
30/11/2018 | 11:53:06 | G12 | Rural Long | Planned |  | 1 | 95 | 0.00069334 | 7.3e-06 | No
30/11/2018 | 11:54:18 | NA32 | Rural Long | Asset failure | LV | 1 | 327 | 0.0023866 | 7.3e-06 | No
30/11/2018 | 14:21:23 | SA11 | Urban | Asset failure | LV | 1 | 312 | 0.00049879 | 1.6e-06 | No
30/11/2018 | 18:36:24 | CD17 | Rural Long | Unknown | Unknown | 13 | 233 | 0.022107 | 9.488e-05 | No
30/11/2018 | 18:45:19 | PA19 | Rural Long | Unknown | Unknown | 0 | 2677 | 0.039075 | 0 | No
30/11/2018 | 18:45:19 | PA19 | Rural Long | Unknown | Unknown | 2 | 1260 | 0.018392 | 1.46e-05 | No
30/11/2018 | 19:12:53 | SA11 | Urban | Other |  | 1 | 89 | 0.00014228 | 1.6e-06 | No
30/11/2018 | 21:17:53 | HH102B | Urban | Asset failure | LV | 93 | 73 | 0.010853 | 0.00014868 | No
30/11/2018 | 22:06:22 | HH386D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 139 | 141 | 0.031332 | 0.00022222 | No
1/12/2018 | 02:45:38 | CN77 | Rural Long | Unknown | Unknown | 76 | 352.7237 | 0.19565 | 0.00055467 | No
1/12/2018 | 07:02:38 | M91 | Rural Long | Asset failure | HV | 370 | 332.6649 | 0.89832 | 0.0027004 | No
1/12/2018 | 07:52:26 | NU19 | Rural Long | Asset failure | HV | 984 | 181 | 1.2999 | 0.0071816 | No
1/12/2018 | 08:40:57 | HH386D | Urban | Asset failure | LV | 14.6667 | 122 | 0.0028606 | 2.345e-05 | No
1/12/2018 | 09:17:45 | SM216G | Urban | Asset failure | LV | 86 | 53 | 0.0072868 | 0.00013749 | No
1/12/2018 | 09:27:37 | CV17 | Rural Long | Planned |  | 7 | 138 | 0.0070502 | 5.109e-05 | No
1/12/2018 | 10:04:40 | SM410C | Urban | Asset failure | LV | 1 | 337 | 0.00053875 | 1.6e-06 | No
1/12/2018 | 10:09:03 | HH386D | Urban | Asset failure | LV | 1.3333 | 35 | 7.46e-05 | 2.13e-06 | No
1/12/2018 | 10:19:38 | AP425A | Urban | Vegetation | Grow-in - NSP responsibility | 29 | 502 | 0.023273 | 4.636e-05 | No
1/12/2018 | 11:02:49 | SB16 | Rural Long | Weather |  | 35 | 652.6 | 0.1667 | 0.00025544 | No
1/12/2018 | 11:12:42 | SB22 | Rural Long | Weather |  | 17 | 1602 | 0.19876 | 0.00012407 | No
1/12/2018 | 11:18:28 | PL07 | Urban | Weather |  | 3161 | 70.7846 | 0.3577 | 0.0050534 | No
1/12/2018 | 11:19:14 | HH341D | Urban | Vegetation | Grow-in - NSP responsibility | 41.3334 | 223 | 0.014736 | 6.608e-05 | No
1/12/2018 | 11:20:59 | GA43 | Rural Short | Unknown | Unknown | 4.6667 | 373 | 0.012968 | 3.477e-05 | No
1/12/2018 | 11:30:50 | GU43 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 148 | 98 | 0.10586 | 0.0010801 | No
1/12/2018 | 11:36:54 | HH121A | Urban | Asset failure | LV | 27.6666 | 127 | 0.0056172 | 4.423e-05 | No
1/12/2018 | 12:05:03 | W16 | Rural Long | Weather |  | 25 | 373.8 | 0.068203 | 0.00018246 | No
1/12/2018 | 12:16:24 | SA36 | Urban | Asset failure | LV | 14.6667 | 406 | 0.0095196 | 2.345e-05 | No
1/12/2018 | 12:34:24 | GA16 | Rural Long | Weather |  | 35 | 1588.1143 | 0.40567 | 0.00025544 | No
1/12/2018 | 12:35:38 | KA15 | Rural Long | Weather |  | 59 | 318.8136 | 0.13728 | 0.0004306 | No
1/12/2018 | 12:42:03 | BM53 | Rural Short | Weather |  | 30 | 38 | 0.0084932 | 0.0002235 | No
1/12/2018 | 12:52:35 | HH522B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20.6666 | 187 | 0.0061783 | 3.304e-05 | No
1/12/2018 | 12:53:58 | ME427A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 193 | 0.00061709 | 3.2e-06 | No
1/12/2018 | 13:14:56 | NU33 | Rural Long | Asset failure | LV | 24 | 448 | 0.078472 | 0.00017516 | No
1/12/2018 | 13:17:29 | KI51 | Rural Long | Weather |  | 38 | 1376.7632 | 0.38183 | 0.00027734 | No
1/12/2018 | 13:28:37 | W21 | Rural Long | Weather |  | 8 | 1411 | 0.082384 | 5.839e-05 | No
1/12/2018 | 13:43:22 | CD02 | Rural Long | Asset failure | HV | 774 | 241.3837 | 1.3636 | 0.0056489 | No
1/12/2018 | 13:43:35 | EL13 | Urban | Weather |  | 73 | 429 | 0.050066 | 0.0001167 | No
1/12/2018 | 13:49:09 | EL07 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1105 | 110 | 0.19432 | 0.0017665 | No
1/12/2018 | 13:52:02 | CL19 | Rural Long | Weather |  | 81 | 167.6667 | 0.099119 | 0.00059117 | No
1/12/2018 | 13:57:13 | HH121A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 27.6666 | 228 | 0.010084 | 4.423e-05 | No
1/12/2018 | 14:03:36 | HH386D | Urban | Vegetation | Grow-in - NSP responsibility | 15 | 65 | 0.0015587 | 2.398e-05 | No
1/12/2018 | 14:05:10 | MT12 | Rural Long | Unknown | Unknown | 26 | 1248 | 0.23682 | 0.00018976 | No
1/12/2018 | 14:06:02 | SA34 | Urban | Asset failure | HV | 1243 | 143 | 0.28416 | 0.0019872 | No
1/12/2018 | 14:09:48 | KI55 | Rural Long | Asset failure | HV | 65 | 269.2308 | 0.12772 | 0.00047439 | No
1/12/2018 | 14:12:57 | HH403A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1440 | 50 | 0.1151 | 0.0023021 | No
1/12/2018 | 14:14:06 | MV32 | Rural Short | Unknown | Unknown | 5 | 269 | 0.01002 | 3.725e-05 | No
1/12/2018 | 14:26:32 | HH428E | Urban | Asset failure | LV | 1 | 65 | 0.00010391 | 1.6e-06 | No
1/12/2018 | 14:28:59 | GA46 | Rural Long | Unknown | Unknown | 89 | 1301 | 0.84507 | 0.00064955 | No
1/12/2018 | 14:30:31 | HH432F | Urban | Vegetation | Grow-in - NSP responsibility | 53 | 31 | 0.0026266 | 8.473e-05 | No
1/12/2018 | 14:35:12 | GA27 | Rural Long | Weather |  | 464 | 101 | 0.34203 | 0.0033864 | No
1/12/2018 | 14:36:25 | R35 | Rural Long | Weather |  | 73 | 275 | 0.14651 | 0.00053278 | No
1/12/2018 | 14:46:26 | R28 | Rural Long | Weather |  | 88 | 1364.2045 | 0.87617 | 0.00064225 | No
1/12/2018 | 14:46:26 | R28 | Rural Long | Weather |  | 0 | 182 | 0.0039849 | 0 | No
1/12/2018 | 14:46:44 | GA21 | Rural Long | Unknown | Unknown | 21 | 643 | 0.098549 | 0.00015327 | No
1/12/2018 | 14:49:28 | GA10 | Rural Long | Weather |  | 83 | 423 | 0.25624 | 0.00060576 | No
1/12/2018 | 14:50:49 | HH386G | Urban | Asset failure | LV | 1.3333 | 226 | 0.00048173 | 2.13e-06 | No
1/12/2018 | 14:52:11 | GA47 | Rural Long | Unknown | Unknown | 52 | 1399 | 0.53094 | 0.00037951 | No
1/12/2018 | 14:53:43 | SD52300 | Rural Short | Unknown | Unknown | 578 | 260 | 1.1196 | 0.0043062 | No
1/12/2018 | 14:53:43 | SD52300 | Rural Long | Unknown | Unknown | 2461 | 260 | 4.6699 | 0.017961 | No
1/12/2018 | 14:55:27 | EL19 | Urban | Unknown | Unknown | 400 | 17.32 | 0.011076 | 0.00063947 | No
1/12/2018 | 14:55:27 | GA800A | Rural Short | Unknown | Unknown | 201 | 1 | 0.0014975 | 0.0014975 | No
1/12/2018 | 14:57:08 | MV32 | Rural Short | Weather |  | 2 | 269 | 0.0040082 | 1.49e-05 | No
1/12/2018 | 14:57:55 | GA25 | Rural Short | Weather |  | 68 | 438.6176 | 0.22221 | 0.00050661 | No
1/12/2018 | 14:57:55 | GA25 | Rural Short | Weather |  | 0 | 33 | 0.0024585 | 0 | No
1/12/2018 | 15:00:13 | SD31300 | Rural Long | Unknown | Unknown | 2 | 1917 | 0.027982 | 1.46e-05 | No
1/12/2018 | 15:06:47 | R04 | Rural Long | Weather |  | 5 | 1448 | 0.05284 | 3.649e-05 | No
1/12/2018 | 15:08:19 | NU15 | Rural Long | Unknown | Unknown | 18 | 482 | 0.06332 | 0.00013137 | No
1/12/2018 | 15:09:43 | MB27 | Rural Short | Asset failure | HV | 7.3333 | 131 | 0.0071571 | 5.463e-05 | No
1/12/2018 | 15:18:02 | R04 | Rural Long | Unknown | Unknown | 47 | 1509 | 0.51762 | 0.00034302 | No
1/12/2018 | 15:39:34 | MB72 | Rural Long | Planned |  | 19 | 1333.5789 | 0.18493 | 0.00013867 | No
1/12/2018 | 15:47:15 | W17 | Rural Long | Weather |  | 31 | 1164 | 0.26335 | 0.00022625 | No
1/12/2018 | 15:47:30 | W21 | Rural Long | Weather |  | 4 | 1471 | 0.042943 | 2.919e-05 | No
1/12/2018 | 15:51:43 | SD34400 | Rural Long | Unknown | Unknown | 49 | 174 | 0.062226 | 0.00035762 | No
1/12/2018 | 15:53:26 | MB24 | Rural Short | Asset failure | LV | 8.3333 | 171 | 0.010616 | 6.208e-05 | No
1/12/2018 | 15:55:33 | HH341C | Urban | Asset failure | LV | 5 | 319 | 0.0025499 | 7.99e-06 | No
1/12/2018 | 15:58:19 | VH45 | Rural Short | Weather |  | 39 | 180 | 0.0523 | 0.00029056 | No
1/12/2018 | 15:58:23 | MV33 | Rural Short | Weather |  | 37 | 357.4054 | 0.098521 | 0.00027566 | No
1/12/2018 | 16:03:00 | SSD440 | Rural Short | 5 - STPIS Exclusion (3.3)(a) |  | 125 | 1622 | 1.5105 | 0.00093127 | No
1/12/2018 | 16:03:00 | SSD440 | Rural Long | 5 - STPIS Exclusion (3.3)(a) |  | 561 | 1660.0731 | 6.7969 | 0.0040944 | No
1/12/2018 | 16:05:33 | MV15 | Rural Short | Weather |  | 9 | 523 | 0.035068 | 6.705e-05 | No
1/12/2018 | 16:05:54 | VH43 | Rural Short | Weather |  | 3 | 566 | 0.01265 | 2.235e-05 | No
1/12/2018 | 16:06:46 | MV51 | Rural Short | Unknown | Unknown | 119 | 657.7479 | 0.58314 | 0.00088657 | No
1/12/2018 | 16:06:46 | MV51 | Rural Short | Unknown | Unknown | 0 | 1 | 0.00048426 | 0 | No
1/12/2018 | 16:12:27 | ST36 | Rural Long | Weather |  | 40 | 213 | 0.062182 | 0.00029193 | No
1/12/2018 | 16:17:06 | SSD528 | Rural Short | Planned |  | 1 | 24 | 0.0001788 | 7.45e-06 | No
1/12/2018 | 16:17:10 | SD44400 | Rural Short | Unknown | Unknown | 895 | 90 | 0.60011 | 0.0066679 | No
1/12/2018 | 16:18:00 | SD59100 | Rural Long | Unknown | Unknown | 3 | 2832 | 0.062007 | 2.19e-05 | No
1/12/2018 | 16:30:15 | BM51 | Urban | Unknown | Unknown | 7.6667 | 98 | 0.0012011 | 1.226e-05 | No
1/12/2018 | 16:35:16 | GA22 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 139 | 0.0010356 | 7.45e-06 | No
1/12/2018 | 16:37:23 | CN42 | Rural Long | Weather |  | 104 | 1204 | 0.91387 | 0.00075903 | No
1/12/2018 | 16:38:07 | ST44 | Rural Long | Weather |  | 120 | 254.3 | 0.22272 | 0.0008758 | No
1/12/2018 | 16:48:15 | GA50 | Urban | Other |  | 27 | 171 | 0.0073811 | 4.316e-05 | No
1/12/2018 | 16:56:17 | PA24 | Rural Long | Weather |  | 30 | 1286.8 | 0.28175 | 0.00021895 | No
1/12/2018 | 17:08:51 | BT04 | Rural Long | Weather |  | 31 | 217 | 0.049096 | 0.00022625 | No
1/12/2018 | 17:15:34 | KA18 | Rural Long | Weather |  | 23 | 1180 | 0.19808 | 0.00016786 | No
1/12/2018 | 17:28:18 | M83 | Rural Long | Asset failure | HV | 87 | 1193.5747 | 0.75787 | 0.00063496 | No
1/12/2018 | 17:28:18 | M83 | Rural Long | Asset failure | HV | 0 | 18 | 0.0028901 | 0 | No
1/12/2018 | 17:29:45 | CN77 | Rural Long | Unknown | Unknown | 76 | 1536.1316 | 0.85205 | 0.00055467 | No
1/12/2018 | 17:29:45 | CN77 | Rural Long | Unknown | Unknown | 0 | 84.4286 | 0.0043133 | 0 | No
1/12/2018 | 17:30:58 | BT20 | Rural Long | Weather |  | 65 | 506.2615 | 0.24017 | 0.00047439 | No
1/12/2018 | 17:31:29 | PA13 | Rural Long | Weather |  | 12.6667 | 1130.0001 | 0.10446 | 9.245e-05 | No
1/12/2018 | 17:37:33 | GA800A | Rural Short | Weather |  | 219 | 259.6621 | 0.42366 | 0.0016316 | No
1/12/2018 | 17:37:33 | GA800A | Rural Short | Weather |  | 0 | 93.7925 | 0.037035 | 0 | No
1/12/2018 | 17:49:31 | HH118E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 53 | 154 | 0.013048 | 8.473e-05 | No
1/12/2018 | 17:52:57 | GU18 | Rural Long | Unknown | Unknown | 33 | 382.8788 | 0.092215 | 0.00024085 | No
1/12/2018 | 17:54:34 | KA30 | Rural Short | Weather |  | 65 | 948.7231 | 0.45943 | 0.00048426 | No
1/12/2018 | 17:56:55 | MG34 | Rural Long | Weather |  | 207 | 172 | 0.25985 | 0.0015108 | No
1/12/2018 | 17:58:06 | HH177E | Urban | Asset failure | LV | 17.3333 | 99 | 0.0027433 | 2.771e-05 | No
1/12/2018 | 18:00:43 | SD44400 | Rural Short | Weather |  | 895 | 271.3765 | 1.8095 | 0.0066679 | No
1/12/2018 | 18:00:43 | SD44400 | Rural Short | Weather |  | 0 | 4 | 0.026582 | 0 | No
1/12/2018 | 18:10:43 | CL20 | Rural Long | Weather |  | 87 | 1341.4713 | 0.85177 | 0.00063496 | No
1/12/2018 | 18:11:18 | CL16 | Rural Long | Asset failure | HV | 294 | 1134.4592 | 2.4342 | 0.0021457 | No
1/12/2018 | 18:18:01 | CL16 | Rural Long | Unknown | Unknown | 223 | 1052 | 1.7122 | 0.0016275 | No
1/12/2018 | 18:18:01 | CL16 | Rural Long | Unknown | Unknown | 204 | 2 | 0.0029777 | 0.0014889 | No
1/12/2018 | 18:33:31 | EL12 | Urban | Unknown | Unknown | 6 | 1112.6667 | 0.010673 | 9.59e-06 | No
1/12/2018 | 18:35:47 | BT01 | Rural Long | Unknown | Unknown | 5.6667 | 213 | 0.0088091 | 4.136e-05 | No
1/12/2018 | 18:44:10 | CL04 | Rural Long | Weather |  | 26 | 1272 | 0.24137 | 0.00018976 | No
1/12/2018 | 18:45:59 | G42 | Rural Long | Unknown | Unknown | 18 | 1969.2222 | 0.2587 | 0.00013137 | No
1/12/2018 | 19:19:47 | NA57 | Rural Long | Unknown | Unknown | 73 | 978.1918 | 0.52116 | 0.00053278 | No
1/12/2018 | 19:19:47 | NA57 | Rural Long | Unknown | Unknown | 0 | 255.3571 | 0.18264 | 0 | No
1/12/2018 | 19:25:59 | NA60 | Rural Long | Asset failure | HV | 26 | 1401 | 0.26585 | 0.00018976 | No
1/12/2018 | 19:25:59 | NA60 | Rural Long | Asset failure | HV | 30 | 853.0667 | 0.18678 | 0.00021895 | No
1/12/2018 | 19:25:59 | NA60 | Rural Long | Asset failure | HV | 0 | 148.8571 | 0.0076049 | 0 | No
1/12/2018 | 19:32:33 | MB03 | Rural Long | Weather |  | 34 | 1648 | 0.40894 | 0.00024814 | No
1/12/2018 | 19:34:06 | LM31 | Rural Long | Weather |  | 83 | 1213.988 | 0.73539 | 0.00060576 | No
1/12/2018 | 19:39:26 | NA07 | Rural Long | Unknown | Unknown | 13.6667 | 243 | 0.024238 | 9.974e-05 | No
1/12/2018 | 20:25:26 | MG16 | Rural Long | Weather |  | 471 | 188 | 0.64625 | 0.0034375 | No
1/12/2018 | 20:26:04 | SD31300 | Rural Long | Unknown | Unknown | 3 | 1174 | 0.025705 | 2.19e-05 | No
1/12/2018 | 20:38:06 | LM51 | Rural Long | Unknown | Unknown | 19 | 889.8421 | 0.12339 | 0.00013867 | No
1/12/2018 | 20:50:31 | CN32 | Rural Long | Weather |  | 1 | 995 | 0.0072619 | 7.3e-06 | No
1/12/2018 | 22:37:02 | NU03 | Rural Long | Unknown | Unknown | 10 | 943 | 0.068823 | 7.298e-05 | No
1/12/2018 | 23:29:11 | ST16 | Rural Short | Animal | Animal impact | 52 | 875 | 0.33898 | 0.00038741 | No
1/12/2018 | 23:56:06 | VH71 | Rural Short | Weather |  | 3 | 5 | 0.00011175 | 2.235e-05 | No
2/12/2018 | 00:42:35 | GA45 | Rural Short | Weather |  | 88 | 768.9432 | 0.50413 | 0.00065561 | No
2/12/2018 | 01:22:40 | M13 | Rural Long | Third Party | Vehicle impact | 972 | 433.6667 | 3.0764 | 0.007094 | No
2/12/2018 | 03:08:39 | BU05 | Rural Long | Weather |  | 87 | 654.7126 | 0.41571 | 0.00063496 | No
2/12/2018 | 04:43:13 | NL111P | Urban | Planned |  | 89 | 254 | 0.03614 | 0.00014228 | No
2/12/2018 | 05:35:27 | MI14 | Rural Long | Weather |  | 697 | 246.3659 | 1.2532 | 0.0050869 | No
2/12/2018 | 05:39:12 | MI14 | Rural Long | Other |  | 1 | 284 | 0.0020727 | 7.3e-06 | No
2/12/2018 | 07:26:31 | CL04 | Rural Long | Asset failure | HV | 1 | 864 | 0.0063058 | 7.3e-06 | No
2/12/2018 | 07:43:43 | SD31300 | Rural Long | Unknown | Unknown | 1 | 426 | 0.0031091 | 7.3e-06 | No
2/12/2018 | 07:46:43 | KI41 | Rural Long | Weather |  | 2 | 15 | 0.00021895 | 1.46e-05 | No
2/12/2018 | 08:31:54 | HH177C | Urban | Asset failure | LV | 18.6666 | 149 | 0.0044464 | 2.984e-05 | No
2/12/2018 | 08:51:54 | MI33 | Rural Long | Weather |  | 33 | 431 | 0.1038 | 0.00024085 | No
2/12/2018 | 09:55:35 | SA13 / SA14 | Urban | Planned |  | 163 | 358.4356 | 0.093403 | 0.00026058 | No
2/12/2018 | 10:27:01 | AP227B | Urban | Asset failure | LV | 1 | 153 | 0.0002446 | 1.6e-06 | No
2/12/2018 | 10:50:14 | W01 | Rural Long | Unknown | Unknown | 2 | 399 | 0.0058241 | 1.46e-05 | No
2/12/2018 | 11:19:17 | SD34300 | Rural Short | Third Party | Vehicle impact | 1 | 108 | 0.00080462 | 7.45e-06 | No
2/12/2018 | 11:48:54 | VH21 | Rural Short | Asset failure | LV | 1 | 257 | 0.0019147 | 7.45e-06 | No
2/12/2018 | 13:14:18 | NA10 | Rural Long | Overloads |  | 2 | 165 | 0.0024084 | 1.46e-05 | No
2/12/2018 | 13:20:25 | LX71 | Rural Long | Unknown | Unknown | 4 | 365 | 0.010656 | 2.919e-05 | No
2/12/2018 | 13:24:57 | MB61 | Rural Long | Asset failure | LV | 1 | 144 | 0.001051 | 7.3e-06 | No
2/12/2018 | 13:44:29 | CN42 | Rural Long | Asset failure | HV | 3 | 205 | 0.0044885 | 2.19e-05 | No
2/12/2018 | 16:43:58 | NA29 | Rural Long | Unknown | Unknown | 32 | 736.1875 | 0.17193 | 0.00023355 | No
2/12/2018 | 17:08:51 | ST42 | Rural Long | Unknown | Unknown | 2 | 118 | 0.0017224 | 1.46e-05 | No
2/12/2018 | 17:16:41 | SM350B | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
2/12/2018 | 18:47:17 | NL115F | Urban | Asset failure | LV | 7.6667 | 200 | 0.0024513 | 1.226e-05 | No
2/12/2018 | 18:49:47 | AP425C | Urban | Asset failure | LV | 1 | 157 | 0.00025099 | 1.6e-06 | No
2/12/2018 | 18:54:40 | MB24 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 25 | 59 | 0.010989 | 0.00018625 | No
2/12/2018 | 19:06:00 | SSD440 | Rural Short | Weather |  | 125 | 989 | 0.92102 | 0.00093127 | No
2/12/2018 | 19:38:53 | AP125D | Urban | Asset failure | HV | 199 | 88 | 0.027996 | 0.00031814 | No
2/12/2018 | 20:33:06 | SD38100 | Rural Long | Vegetation | Grow-in - NSP responsibility | 4 | 172 | 0.0050213 | 2.919e-05 | No
2/12/2018 | 20:47:36 | MV61 | Urban | Asset failure | LV | 56.6666 | 158 | 0.014313 | 9.059e-05 | No
2/12/2018 | 21:42:22 | LC02 | Rural Long | Animal | Animal impact | 47 | 873 | 0.29946 | 0.00034302 | No
2/12/2018 | 21:46:49 | AP424C | Urban | Overloads |  | 1 | 129 | 0.00020623 | 1.6e-06 | No
2/12/2018 | 23:37:41 | CBD366S | Urban | Planned |  | 59 | 3 | 0.00028297 | 9.432e-05 | No
2/12/2018 | 23:45:01 | MV61 | Urban | Asset failure | LV | 1 | 86 | 0.00013749 | 1.6e-06 | No
2/12/2018 | 23:58:30 | MV61 | Urban | Asset failure | LV | 1 | 83 | 0.00013269 | 1.6e-06 | No
3/12/2018 | 03:16:01 | PP01 | Urban | Asset failure | LV | 1 | 720 | 0.0011511 | 1.6e-06 | No
3/12/2018 | 03:42:21 | AP529A | Urban | Asset failure | LV | 1 | 448 | 0.00071621 | 1.6e-06 | No
3/12/2018 | 05:45:20 | NA57 | Rural Long | Weather |  | 73 | 493.863 | 0.26312 | 0.00053278 | No
3/12/2018 | 05:58:42 | MV51 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 119 | 235 | 0.20834 | 0.00088657 | No
3/12/2018 | 06:48:22 | CBD412M | Urban | Asset failure | LV | 1 | 422 | 0.00067464 | 1.6e-06 | No
3/12/2018 | 08:01:06 | R26 | Rural Long | Overloads |  | 2 | 173 | 0.0025252 | 1.46e-05 | No
3/12/2018 | 09:20:37 | AP125C | Urban | Planned |  | 100 | 144 | 0.023021 | 0.00015987 | No
3/12/2018 | 09:26:28 | MI02 | Rural Short | Planned |  | 4 | 288 | 0.0085826 | 2.98e-05 | No
3/12/2018 | 09:29:09 | HH145D | Urban | Asset failure | LV | 1 | 325 | 0.00051957 | 1.6e-06 | No
3/12/2018 | 09:37:33 | MV33 | Rural Short | Unknown | Unknown | 4.3333 | 168 | 0.0054237 | 3.228e-05 | No
3/12/2018 | 10:00:42 | W15 | Rural Long | Planned |  | 2 | 42 | 0.00061306 | 1.46e-05 | No
3/12/2018 | 10:09:26 | SG03 | Rural Short | Planned |  | 76 | 375 | 0.21233 | 0.00056621 | No
3/12/2018 | 10:26:19 | VH33 | Rural Short | Planned |  | 134 | 269 | 0.26855 | 0.00099832 | No
3/12/2018 | 10:33:46 | GA08 | Rural Long | Planned |  | 2 | 44 | 0.00064225 | 1.46e-05 | No
3/12/2018 | 10:35:23 | MV51 | Rural Short | Asset failure | LV | 1 | 201 | 0.0014975 | 7.45e-06 | No
3/12/2018 | 11:34:35 | NU20 | Rural Long | Asset failure | LV | 1 | 208 | 0.001518 | 7.3e-06 | No
3/12/2018 | 12:08:43 | HH409F | Urban | Planned |  | 226 | 32 | 0.011562 | 0.0003613 | No
3/12/2018 | 12:22:44 | MTB51 | Rural Long | Planned |  | 73 | 147.0411 | 0.07834 | 0.00053278 | No
3/12/2018 | 12:43:58 | SD33200 | Rural Long | Planned |  | 1512 | 2 | 0.02207 | 0.011035 | No
3/12/2018 | 14:29:08 | G25 | Rural Long | Asset failure | Distribution substation | 30 | 1450.7667 | 0.31765 | 0.00021895 | No
3/12/2018 | 14:41:39 | PP01 | Urban | Asset failure | LV | 6.6667 | 121 | 0.0012896 | 1.066e-05 | No
3/12/2018 | 16:02:30 | NL111P | Urban | Asset failure | LV | 52 | 85 | 0.0070661 | 8.313e-05 | No
3/12/2018 | 16:14:53 | EL12 | Urban | Weather |  | 1 | 446 | 0.00071301 | 1.6e-06 | No
3/12/2018 | 17:36:29 | SM350H | Urban | Asset failure | HV | 1913 | 189.3544 | 0.5791 | 0.0030583 | No
3/12/2018 | 17:38:17 | NA51 | Rural Long | Unknown | Unknown | 1 | 274 | 0.0019997 | 7.3e-06 | No
3/12/2018 | 17:58:24 | CN42 | Rural Long | Asset failure | LV | 1 | 229 | 0.0016713 | 7.3e-06 | No
3/12/2018 | 19:06:04 | EL12 | Urban | Asset failure | Distribution substation | 1 | 249 | 0.00039807 | 1.6e-06 | No
3/12/2018 | 19:39:27 | MG46 | Rural Short | Asset failure | LV | 1 | 174 | 0.0012963 | 7.45e-06 | No
3/12/2018 | 19:56:33 | GA15 | Rural Short | Unknown | Unknown | 2 | 304 | 0.0045297 | 1.49e-05 | No
3/12/2018 | 23:47:48 | SD31300 | Rural Long | Unknown | Unknown | 1 | 1118 | 0.0081595 | 7.3e-06 | No
4/12/2018 | 01:28:11 | SM350E | Urban | Animal | Animal impact | 56 | 121 | 0.010833 | 8.953e-05 | No
4/12/2018 | 04:08:18 | SM350E | Urban | Animal | Animal impact | 84 | 107 | 0.014369 | 0.00013429 | No
4/12/2018 | 07:23:27 | HH145D | Urban | Asset failure | LV | 1 | 452 | 0.0007226 | 1.6e-06 | No
4/12/2018 | 07:49:38 | SM126E | Urban | Asset failure | LV | 13.3333 | 365 | 0.0077802 | 2.132e-05 | No
4/12/2018 | 08:40:14 | MV53 | Rural Short | Planned |  | 19 | 305 | 0.043174 | 0.00014155 | No
4/12/2018 | 08:40:40 | HH145E | Urban | Asset failure | LV | 62 | 21 | 0.0020815 | 9.912e-05 | No
4/12/2018 | 08:44:56 | NL451B | Urban | Planned |  | 78 | 268 | 0.033419 | 0.0001247 | No
4/12/2018 | 08:49:09 | SG08 | Rural Short | Planned |  | 198 | 422 | 0.6225 | 0.0014751 | No
4/12/2018 | 08:53:13 | AP125D | Urban | Planned |  | 202 | 375 | 0.1211 | 0.00032293 | No
4/12/2018 | 09:03:53 | AP424B | Urban | Planned |  | 1 | 16 | 2.558e-05 | 1.6e-06 | No
4/12/2018 | 09:12:02 | KA23 | Rural Long | Planned |  | 69 | 345 | 0.17374 | 0.00050359 | No
4/12/2018 | 09:12:04 | SM411E | Urban | Planned |  | 64 | 315 | 0.032229 | 0.00010232 | No
4/12/2018 | 09:16:11 | SA31 | Urban | Planned |  | 179 | 244.419 | 0.069944 | 0.00028616 | No
4/12/2018 | 09:19:29 | NU04 | Rural Short | Planned |  | 32 | 51 | 0.012159 | 0.0002384 | No
4/12/2018 | 09:23:54 | AP424F | Urban | Planned |  | 296 | 22 | 0.010411 | 0.00047321 | No
4/12/2018 | 09:24:24 | NL234A | Urban | Planned |  | 67 | 272 | 0.029134 | 0.00010711 | No
4/12/2018 | 09:26:07 | SM349E | Urban | Asset failure | LV | 45 | 23 | 0.0016546 | 7.194e-05 | No
4/12/2018 | 09:30:45 | HH496A | Urban | Planned |  | 524 | 230.7099 | 0.19327 | 0.00083771 | No
4/12/2018 | 09:53:45 | CV09 | Rural Long | Weather |  | 2 | 369 | 0.0053862 | 1.46e-05 | No
4/12/2018 | 10:12:59 | HH177A | Urban | Third Party | Vehicle impact | 63 | 76 | 0.0076545 | 0.00010072 | No
4/12/2018 | 10:48:40 | AP125D | Urban | Asset failure | LV | 1 | 406 | 0.00064906 | 1.6e-06 | No
4/12/2018 | 11:41:10 | NU22 | Rural Long | Planned |  | 50 | 47 | 0.017151 | 0.00036492 | No
4/12/2018 | 12:17:55 | W06 | Rural Long | Asset failure | LV | 1 | 115 | 0.00083931 | 7.3e-06 | No
4/12/2018 | 13:04:12 | PP03 | Urban | Asset failure | LV | 1 | 429 | 0.00068583 | 1.6e-06 | No
4/12/2018 | 13:42:05 | GA800A | Rural Short | Asset failure | LV | 39 | 147 | 0.042712 | 0.00029056 | No
4/12/2018 | 13:50:20 | HH130F | Urban | Asset failure | LV | 20.6666 | 163 | 0.0053854 | 3.304e-05 | No
4/12/2018 | 13:51:44 | EL14 | Urban | Third Party | Vehicle impact | 52.6667 | 377 | 0.031742 | 8.42e-05 | No
4/12/2018 | 14:04:51 | GA800A | Rural Short | Asset failure | LV | 40 | 125 | 0.037251 | 0.00029801 | No
4/12/2018 | 14:40:13 | ME231A | Urban | Asset failure | LV | 2 | 286 | 0.00091444 | 3.2e-06 | No
4/12/2018 | 15:10:09 | NL111Q | Urban | Asset failure | LV | 17 | 22 | 0.0005979 | 2.718e-05 | No
4/12/2018 | 18:33:42 | SM374B | Urban | Asset failure | LV | 121 | 65 | 0.012574 | 0.00019344 | No
4/12/2018 | 18:41:12 | SA19 | Urban | Asset failure | LV | 58 | 69 | 0.0063979 | 9.272e-05 | No
4/12/2018 | 21:26:43 | EL14 | Urban | Asset failure | HV | 14 | 149 | 0.0033348 | 2.238e-05 | No
4/12/2018 | 21:30:55 | EL14 | Urban | Asset failure | HV | 33.3334 | 149 | 0.0079401 | 5.329e-05 | No
4/12/2018 | 22:19:41 | HH121B | Urban | Asset failure | LV | 38 | 48 | 0.002916 | 6.075e-05 | No
4/12/2018 | 23:25:36 | HH177D | Urban | Vegetation | Grow-in - NSP responsibility | 70 | 25 | 0.0027977 | 0.00011191 | No
5/12/2018 | 02:13:51 | NL115C | Urban | Weather |  | 480.6669 | 81.6699 | 0.062758 | 0.00076843 | No
5/12/2018 | 03:26:58 | HH130F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 39 | 0.0019951 | 5.116e-05 | No
5/12/2018 | 05:20:07 | SM126C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 179 | 292 | 0.08356 | 0.00028616 | No
5/12/2018 | 06:49:30 | MG37 | Rural Long | Unknown | Unknown | 85 | 28 | 0.01737 | 0.00062036 | No
5/12/2018 | 08:14:05 | SA18 | Urban | Asset failure | LV | 1 | 157 | 0.00025099 | 1.6e-06 | No
5/12/2018 | 08:35:30 | MV64 | Urban | Planned |  | 218 | 300 | 0.10455 | 0.00034851 | No
5/12/2018 | 08:57:50 | PA04 | Rural Short | Planned |  | 42 | 336 | 0.10514 | 0.00031291 | No
5/12/2018 | 09:15:15 | SG14 | Rural Short | Planned |  | 138 | 333 | 0.34236 | 0.0010281 | No
5/12/2018 | 09:27:02 | EL01A | Urban | Planned |  | 160 | 18 | 0.0046042 | 0.00025579 | No
5/12/2018 | 09:28:15 | ME200A | Urban | Planned |  | 1 | 398 | 0.00063627 | 1.6e-06 | No
5/12/2018 | 09:31:57 | G05 | Rural Long | Asset failure | LV | 25 | 312 | 0.056927 | 0.00018246 | No
5/12/2018 | 09:38:13 | MV52 | Rural Short | Planned |  | 15 | 96 | 0.010728 | 0.00011175 | No
5/12/2018 | 09:43:18 | HH121B | Urban | Planned |  | 86 | 247 | 0.033959 | 0.00013749 | No
5/12/2018 | 09:52:44 | EL15 | Urban | Planned |  | 3 | 118 | 0.00056593 | 4.8e-06 | No
5/12/2018 | 09:54:34 | SB18 | Rural Long | Planned |  | 6 | 2 | 8.758e-05 | 4.379e-05 | No
5/12/2018 | 10:04:52 | PL30 | Rural Long | Planned |  | 2 | 51.5 | 0.00075173 | 1.46e-05 | No
5/12/2018 | 11:15:40 | ME200A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 964 | 2 | 0.0030822 | 0.0015411 | No
5/12/2018 | 11:39:11 | NL511A | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
5/12/2018 | 12:11:13 | HH409D | Urban | Asset failure | LV | 13.3333 | 21 | 0.00044763 | 2.132e-05 | No
5/12/2018 | 12:30:34 | AP355H | Urban | Planned |  | 1 | 90 | 0.00014388 | 1.6e-06 | No
5/12/2018 | 13:26:45 | WHY12 | Urban | Asset failure | LV | 41 | 90 | 0.0058991 | 6.555e-05 | No
5/12/2018 | 13:27:42 | HH522B | Urban | Asset failure | LV | 20.6666 | 186 | 0.0061453 | 3.304e-05 | No
5/12/2018 | 13:54:31 | SM410D | Urban | Asset failure | LV | 1 | 283 | 0.00045243 | 1.6e-06 | No
5/12/2018 | 14:04:32 | SA711C | Urban | Asset failure | LV | 1 | 246 | 0.00039327 | 1.6e-06 | No
5/12/2018 | 15:25:12 | HH145C | Urban | Overloads |  | 1 | 300 | 0.0004796 | 1.6e-06 | No
5/12/2018 | 16:13:46 | CBD103A | Urban | Third Party | Other | 1 | 319 | 0.00050998 | 1.6e-06 | No
5/12/2018 | 16:20:07 | LX71 | Rural Long | Unknown | Unknown | 1 | 18 | 0.00013137 | 7.3e-06 | No
5/12/2018 | 16:47:53 | MTB54 | Rural Long | Unknown | Unknown | 243 | 282.4486 | 0.50092 | 0.0017735 | No
5/12/2018 | 18:05:00 | VH33 | Rural Short | Asset failure | LV | 1 | 313 | 0.0023319 | 7.45e-06 | No
5/12/2018 | 18:05:45 | SA41 | Urban | Third Party | Vehicle impact | 99 | 66 | 0.010446 | 0.00015827 | No
5/12/2018 | 18:10:17 | HH432B | Urban | Asset failure | LV | 1 | 219 | 0.00035011 | 1.6e-06 | No
5/12/2018 | 18:25:30 | HH102B | Urban | Asset failure | LV | 1 | 199 | 0.00031814 | 1.6e-06 | No
5/12/2018 | 22:59:44 | SM126C | Urban | Animal | Animal impact | 53 | 71 | 0.0060158 | 8.473e-05 | No
6/12/2018 | 00:46:55 | PL07 | Urban | Asset failure | Distribution substation | 6 | 216.3333 | 0.0020751 | 9.59e-06 | No
6/12/2018 | 06:16:38 | CD03 | Rural Short | Asset failure | LV | 1 | 200 | 0.00149 | 7.45e-06 | No
6/12/2018 | 06:39:36 | EL11 | Urban | Asset failure | LV | 1 | 218 | 0.00034851 | 1.6e-06 | No
6/12/2018 | 08:00:59 | BM11 | Rural Short | Planned |  | 19 | 179 | 0.025338 | 0.00014155 | No
6/12/2018 | 08:34:28 | SD31300 | Rural Long | Unknown | Unknown | 4.6667 | 178 | 0.0060625 | 3.406e-05 | No
6/12/2018 | 08:46:43 | ME200A | Urban | Planned |  | 1 | 213 | 0.00034052 | 1.6e-06 | No
6/12/2018 | 08:56:55 | PA23 | Rural Long | Planned |  | 2 | 33 | 0.00048169 | 1.46e-05 | No
6/12/2018 | 09:12:35 | NA09 | Rural Long | Planned |  | 5 | 1 | 3.649e-05 | 3.649e-05 | No
6/12/2018 | 09:15:32 | YK12 | Rural Long | Planned |  | 2 | 61 | 0.0008904 | 1.46e-05 | No
6/12/2018 | 09:41:40 | MTB41 | Rural Short | Planned |  | 89 | 219 | 0.14521 | 0.00066306 | No
6/12/2018 | 10:25:34 | SD41300 | Rural Short | Animal | Animal impact | 2 | 196 | 0.0029205 | 1.49e-05 | No
6/12/2018 | 11:15:51 | NU16 | Rural Long | Other |  | 1 | 6 | 4.379e-05 | 7.3e-06 | No
6/12/2018 | 11:58:08 | AP424A | Urban | Animal | Animal impact | 1 | 121 | 0.00019344 | 1.6e-06 | No
6/12/2018 | 12:05:04 | KI15 | Rural Long | Unknown | Unknown | 2 | 125 | 0.0018246 | 1.46e-05 | No
6/12/2018 | 12:43:41 | EL19 | Urban | Asset failure | HV | 178 | 135.691 | 0.038613 | 0.00028456 | No
6/12/2018 | 13:31:29 | CN83 | Rural Long | Unknown | Unknown | 24 | 155 | 0.02715 | 0.00017516 | No
6/12/2018 | 14:34:36 | MB22 | Rural Short | Asset failure | LV | 1 | 131 | 0.00097597 | 7.45e-06 | No
6/12/2018 | 14:45:15 | KI15 | Rural Long | Unknown | Unknown | 2 | 15 | 0.00021895 | 1.46e-05 | No
6/12/2018 | 15:03:04 | MI15 | Rural Long | Asset failure | Distribution substation | 132 | 318.4242 | 0.30676 | 0.00096338 | No
6/12/2018 | 15:48:11 | AP132D | Urban | Unknown | Unknown | 1768 | 55 | 0.15546 | 0.0028265 | No
6/12/2018 | 16:03:32 | KA29 | Rural Long | Asset failure | LV | 2 | 63 | 0.00091959 | 1.46e-05 | No
6/12/2018 | 16:15:00 | PP09 | Rural Long | Asset failure | LV | 17 | 159 | 0.019727 | 0.00012407 | No
6/12/2018 | 17:26:20 | AP149E | Urban | Asset failure | LV | 25.6666 | 45 | 0.0018465 | 4.103e-05 | No
6/12/2018 | 18:25:17 | HH386F | Urban | Asset failure | Distribution substation | 33 | 320 | 0.016882 | 5.276e-05 | No
6/12/2018 | 18:38:53 | HH341K | Urban | Asset failure | LV | 24.6666 | 436 | 0.017193 | 3.943e-05 | No
6/12/2018 | 18:39:32 | KA22 | Rural Long | Asset failure | LV | 1 | 148 | 0.0010801 | 7.3e-06 | No
6/12/2018 | 18:41:34 | MG10 | Rural Long | Unknown | Unknown | 127 | 142.4646 | 0.13205 | 0.00092689 | No
6/12/2018 | 18:51:35 | EL17 | Urban | Unknown | Unknown | 1 | 434 | 0.00069382 | 1.6e-06 | No
6/12/2018 | 19:11:04 | AP149B | Urban | Asset failure | LV | 32.3333 | 126 | 0.006513 | 5.169e-05 | No
6/12/2018 | 19:28:19 | CV31 | Rural Long | Asset failure | HV | 11 | 1038.4545 | 0.083369 | 8.028e-05 | No
6/12/2018 | 19:28:19 | CV31 | Rural Long | Asset failure | HV | 45 | 20 | 0.0065685 | 0.00032843 | No
6/12/2018 | 20:52:42 | ST35 | Rural Long | Unknown | Unknown | 1 | 140 | 0.0010218 | 7.3e-06 | No
6/12/2018 | 21:15:02 | ST35 | Rural Long | Unknown | Unknown | 2 | 119 | 0.001737 | 1.46e-05 | No
6/12/2018 | 21:58:53 | SM350E | Urban | Asset failure | LV | 1 | 161 | 0.00025739 | 1.6e-06 | No
6/12/2018 | 22:14:40 | ME116D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 25 | 244 | 0.0097519 | 3.997e-05 | No
6/12/2018 | 23:05:33 | AP425D | Urban | Asset failure | HV | 82 | 331 | 0.043391 | 0.00013109 | No
7/12/2018 | 00:32:05 | MG10 | Rural Long | Weather |  | 1 | 554 | 0.0040433 | 7.3e-06 | No
7/12/2018 | 02:09:38 | MV54 | Rural Short | Unknown | Unknown | 121 | 586.719 | 0.52891 | 0.00090147 | No
7/12/2018 | 07:38:38 | BT02 | Rural Long | Animal | Animal impact | 4.6667 | 174 | 0.0059263 | 3.406e-05 | No
7/12/2018 | 09:08:00 | SG13 | Rural Short | Planned |  | 81 | 99 | 0.059743 | 0.00060346 | No
7/12/2018 | 09:10:36 | SG07 | Rural Short | Planned |  | 104 | 431 | 0.33395 | 0.00077482 | No
7/12/2018 | 09:32:59 | W15 | Rural Long | Planned |  | 19 | 35 | 0.0048534 | 0.00013867 | No
7/12/2018 | 09:50:05 | HH121B | Urban | Planned |  | 48 | 106 | 0.0081341 | 7.674e-05 | No
7/12/2018 | 11:07:29 | PL04 | Urban | Unknown | Unknown | 2 | 122 | 0.00039008 | 3.2e-06 | No
7/12/2018 | 11:27:48 | CD16 | Rural Short | Planned |  | 2 | 48 | 0.00071521 | 1.49e-05 | No
7/12/2018 | 11:42:33 | ME231E | Urban | Asset failure | LV | 2 | 153 | 0.00048919 | 3.2e-06 | No
7/12/2018 | 11:43:25 | MG19 | Rural Long | Planned |  | 3 | 7 | 0.00015327 | 2.19e-05 | No
7/12/2018 | 11:58:35 | GA23 | Rural Short | Asset failure | HV | 90 | 147 | 0.098565 | 0.00067051 | No
7/12/2018 | 12:09:54 | GU42 | Rural Long | Animal | Animal impact | 1 | 136 | 0.00099257 | 7.3e-06 | No
7/12/2018 | 12:10:06 | SM216B | Urban | Unknown | Unknown | 161 | 93 | 0.023937 | 0.00025739 | No
7/12/2018 | 12:36:21 | HH121D | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
7/12/2018 | 12:45:01 | HH145E | Urban | Third Party | Other | 16.3333 | 470 | 0.012272 | 2.611e-05 | No
7/12/2018 | 12:59:53 | PP03 | Urban | Asset failure | LV | 52 | 157 | 0.013052 | 8.313e-05 | No
7/12/2018 | 13:01:52 | KA04 | Rural Long | Asset failure | LV | 1 | 100 | 0.00072983 | 7.3e-06 | No
7/12/2018 | 13:29:19 | HH121D | Urban | Overloads |  | 1 | 326 | 0.00052117 | 1.6e-06 | No
7/12/2018 | 13:49:55 | HH428C | Urban | Unknown | Unknown | 40.6666 | 270 | 0.017553 | 6.501e-05 | No
7/12/2018 | 13:58:44 | SG07 | Rural Short | Planned |  | 1 | 43 | 0.00032036 | 7.45e-06 | No
7/12/2018 | 14:12:49 | HH130A | Urban | Vegetation | Grow-in - NSP responsibility | 41 | 32 | 0.0020975 | 6.555e-05 | No
7/12/2018 | 14:45:55 | SM350H | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1069 | 85 | 0.14526 | 0.001709 | No
7/12/2018 | 15:00:00 | CBD27R | CBD | Unknown | Unknown | 18 | 112 | 0.39134 | 0.0034941 | No
7/12/2018 | 15:18:43 | NU14 | Rural Long | Unknown | Unknown | 15 | 173.6 | 0.019005 | 0.00010948 | No
7/12/2018 | 15:31:21 | CBD353E | CBD | Unknown | Unknown | 3 | 99 | 0.057653 | 0.00058235 | No
7/12/2018 | 16:08:54 | EL09 | Urban | Asset failure | LV | 19.3333 | 365 | 0.011281 | 3.091e-05 | No
7/12/2018 | 16:10:38 | SM126A | Urban | Asset failure | LV | 1 | 217 | 0.00034691 | 1.6e-06 | No
7/12/2018 | 16:57:12 | EL10 | Urban | Asset failure | LV | 73 | 221 | 0.025791 | 0.0001167 | No
7/12/2018 | 16:57:25 | EL10 | Urban | Asset failure | LV | 58 | 218 | 0.020214 | 9.272e-05 | No
7/12/2018 | 17:54:28 | MG32 | Rural Long | Asset failure | LV | 13 | 67 | 0.0063568 | 9.488e-05 | No
7/12/2018 | 19:44:04 | GU42 | Rural Long | Unknown | Unknown | 1 | 1335 | 0.0097433 | 7.3e-06 | No
7/12/2018 | 20:34:24 | BT04 | Rural Long | Third Party | Vehicle impact | 16 | 270 | 0.031529 | 0.00011677 | No
7/12/2018 | 21:30:15 | HH148B | Urban | Asset failure | LV | 1 | 53 | 8.473e-05 | 1.6e-06 | No
7/12/2018 | 22:08:27 | SB17 | Rural Long | Weather |  | 90 | 929.4556 | 0.61051 | 0.00065685 | No
7/12/2018 | 22:31:54 | PL23 | Rural Long | Unknown | Unknown | 14 | 879 | 0.089813 | 0.00010218 | No
7/12/2018 | 22:39:35 | KI56 | Rural Long | Weather |  | 113 | 1159.3628 | 0.95614 | 0.00082471 | No
7/12/2018 | 22:39:35 | KI56 | Rural Long | Weather |  | 0 | 8 | 0.0023938 | 0 | No
7/12/2018 | 22:55:37 | SB21 | Rural Long | Unknown | Unknown | 79 | 719 | 0.41455 | 0.00057657 | No
7/12/2018 | 23:02:09 | SA20 | Urban | Asset failure | LV | 40.6666 | 116 | 0.0075415 | 6.501e-05 | No
7/12/2018 | 23:06:13 | W29 | Rural Long | Weather |  | 82 | 2129.8049 | 1.2746 | 0.00059846 | No
7/12/2018 | 23:06:13 | W29 | Rural Long | Weather |  | 0 | 50.2083 | 0.026383 | 0 | No
8/12/2018 | 00:02:26 | KI21 | Rural Long | Unknown | Unknown | 13.6667 | 1207 | 0.12039 | 9.974e-05 | No
8/12/2018 | 00:51:51 | ME347C | Urban | Overloads |  | 1 | 121 | 0.00019344 | 1.6e-06 | No
8/12/2018 | 01:13:28 | W03 | Rural Long | Unknown | Unknown | 15 | 621 | 0.067984 | 0.00010948 | No
8/12/2018 | 02:01:22 | W04 | Rural Long | Unknown | Unknown | 1 | 2297 | 0.016764 | 7.3e-06 | No
8/12/2018 | 03:19:20 | MI03 | Rural Long | Weather |  | 100 | 486.6 | 0.35514 | 0.00072983 | No
8/12/2018 | 05:18:57 | CM02 | Rural Long | Weather |  | 6 | 966 | 0.042301 | 4.379e-05 | No
8/12/2018 | 05:46:44 | CM02 | Rural Long | Unknown | Unknown | 55 | 316 | 0.12685 | 0.00040141 | No
8/12/2018 | 06:02:08 | CM03 | Rural Long | Unknown | Unknown | 13 | 645 | 0.061197 | 9.488e-05 | No
8/12/2018 | 06:51:16 | PL24 | Rural Long | Unknown | Unknown | 32 | 278 | 0.064926 | 0.00023355 | No
8/12/2018 | 07:20:00 | CM03 | Rural Long | Unknown | Unknown | 50 | 229.96 | 0.083916 | 0.00036492 | No
8/12/2018 | 07:20:21 | CM11 | Rural Long | Weather |  | 65 | 332 | 0.1575 | 0.00047439 | No
8/12/2018 | 07:24:21 | MI01 | Rural Long | Asset failure | HV | 1 | 296 | 0.0021603 | 7.3e-06 | No
8/12/2018 | 07:45:12 | YK05 | Rural Long | Unknown | Unknown | 5 | 104 | 0.0037951 | 3.649e-05 | No
8/12/2018 | 07:45:25 | G17 | Rural Long | Animal | Animal impact | 4 | 220 | 0.0064225 | 2.919e-05 | No
8/12/2018 | 07:56:20 | CD02 | Rural Long | Weather |  | 386 | 234.6995 | 0.66119 | 0.0028172 | No
8/12/2018 | 07:57:10 | CD18 | Rural Long | Weather |  | 42 | 2035.2857 | 0.62388 | 0.00030653 | No
8/12/2018 | 08:10:57 | MV51 | Rural Short | Unknown | Unknown | 119 | 293.2857 | 0.26002 | 0.00088657 | No
8/12/2018 | 08:12:59 | CD17 | Rural Long | Unknown | Unknown | 13 | 2102 | 0.19943 | 9.488e-05 | No
8/12/2018 | 08:18:41 | SB18 | Rural Long | Weather |  | 12 | 2157 | 0.18891 | 8.758e-05 | No
8/12/2018 | 08:26:19 | SA11 | Urban | Animal | Animal impact | 36 | 149 | 0.0085753 | 5.755e-05 | No
8/12/2018 | 08:56:58 | MT18 | Rural Long | Weather |  | 35 | 269 | 0.068714 | 0.00025544 | No
8/12/2018 | 09:10:52 | MG09 | Rural Short | Weather |  | 329 | 254.383 | 0.62352 | 0.0024511 | No
8/12/2018 | 09:12:38 | CM12 | Rural Long | Weather |  | 32 | 407.4375 | 0.095156 | 0.00023355 | No
8/12/2018 | 09:23:44 | CD25 | Rural Long | Weather |  | 23 | 280.6957 | 0.047118 | 0.00016786 | No
8/12/2018 | 09:25:55 | YK17 | Rural Long | Unknown | Unknown | 1211 | 155 | 1.3699 | 0.0088383 | No
8/12/2018 | 09:32:08 | PP03 | Urban | Other |  | 1 | 252 | 0.00040287 | 1.6e-06 | No
8/12/2018 | 09:35:44 | W31 | Rural Short | Weather |  | 14 | 2074 | 0.21632 | 0.0001043 | No
8/12/2018 | 09:37:45 | SB19 | Rural Long | Weather |  | 0 | 1 | 0.00035762 | 0 | No
8/12/2018 | 09:37:45 | SB19 | Rural Long | Weather |  | 55 | 2710.0909 | 1.0879 | 0.00040141 | No
8/12/2018 | 09:48:07 | HH102D | Urban | Planned |  | 37 | 266 | 0.015734 | 5.915e-05 | No
8/12/2018 | 10:48:20 | AP132B | Urban | Animal | Animal impact | 18 | 201.2222 | 0.0057904 | 2.878e-05 | No
8/12/2018 | 10:49:00 | CV18 | Rural Short | Weather |  | 62 | 221 | 0.10208 | 0.00046191 | No
8/12/2018 | 10:50:03 | CV16 | Rural Long | Weather |  | 41 | 1499.5366 | 0.44871 | 0.00029923 | No
8/12/2018 | 10:53:00 | W24 | Rural Long | Weather |  | 13 | 1967 | 0.18663 | 9.488e-05 | No
8/12/2018 | 10:53:00 | W24 | Rural Long | Weather |  | 14 | 90 | 0.0091959 | 0.00010218 | No
8/12/2018 | 10:53:20 | W24 | Rural Long | Other |  | 2 | 3192 | 0.046593 | 1.46e-05 | No
8/12/2018 | 11:08:23 | HH107C | Urban | Asset failure | LV | 1.6667 | 104 | 0.0002771 | 2.66e-06 | No
8/12/2018 | 11:16:21 | CV29 | Rural Long | Unknown | Unknown | 29 | 1543.1724 | 0.32662 | 0.00021165 | No
8/12/2018 | 11:33:54 | CM22 | Rural Long | Weather |  | 38 | 376 | 0.10428 | 0.00027734 | No
8/12/2018 | 11:42:24 | SB21 | Rural Long | Weather |  | 79 | 284.962 | 0.1643 | 0.00057657 | No
8/12/2018 | 11:44:02 | CV15 | Rural Long | Unknown | Unknown | 59 | 802.8475 | 0.34571 | 0.0004306 | No
8/12/2018 | 12:12:28 | PL30 | Rural Long | Unknown | Unknown | 36 | 91.1389 | 0.023946 | 0.00026274 | No
8/12/2018 | 12:55:32 | CM09 | Rural Long | Unknown | Unknown | 13 | 311 | 0.029507 | 9.488e-05 | No
8/12/2018 | 13:04:06 | KA21 | Rural Long | Weather |  | 50 | 191 | 0.069699 | 0.00036492 | No
8/12/2018 | 13:16:18 | CM10 | Rural Long | Weather |  | 56 | 133 | 0.054358 | 0.00040871 | No
8/12/2018 | 13:56:49 | SA744D | Urban | Overloads |  | 1 | 185 | 0.00029575 | 1.6e-06 | No
8/12/2018 | 14:30:36 | YK04 | Rural Short | Weather |  | 171 | 40 | 0.050959 | 0.001274 | No
8/12/2018 | 15:53:13 | MG42 | Rural Short | Third Party | Other | 1402 | 67 | 0.69982 | 0.010445 | No
8/12/2018 | 17:07:28 | W03 | Rural Long | Unknown | Unknown | 4 | 1396 | 0.040754 | 2.919e-05 | No
8/12/2018 | 17:47:56 | SB20 | Rural Long | Unknown | Unknown | 11 | 82 | 0.0065831 | 8.028e-05 | No
8/12/2018 | 17:54:24 | SM402B | Urban | Vegetation | Grow-in - NSP responsibility | 33.6666 | 197 | 0.010603 | 5.382e-05 | No
8/12/2018 | 18:40:25 | CM09 | Rural Long | Weather |  | 13 | 1009.5385 | 0.095783 | 9.488e-05 | No
8/12/2018 | 20:31:53 | W04 | Rural Long | Asset failure | LV | 5.3333 | 1241.0001 | 0.048305 | 3.892e-05 | No
8/12/2018 | 21:18:36 | SA11 | Urban | Planned |  | 2 | 177 | 0.00056593 | 3.2e-06 | No
9/12/2018 | 03:32:58 | WHY01 | Urban | Weather |  | 569.3336 | 158.1218 | 0.14392 | 0.00091018 | No
9/12/2018 | 05:18:37 | SD31300 | Rural Long | Unknown | Unknown | 6 | 207 | 0.0090645 | 4.379e-05 | No
9/12/2018 | 05:25:14 | BM56 | Rural Short | Unknown | Unknown | 40 | 110 | 0.032781 | 0.00029801 | No
9/12/2018 | 05:31:11 | SD31300 | Rural Long | Unknown | Unknown | 3 | 258 | 0.0056489 | 2.19e-05 | No
9/12/2018 | 07:10:00 | CL09 | Rural Long | Unknown | Unknown | 29 | 164 | 0.034711 | 0.00021165 | No
9/12/2018 | 07:24:34 | SM349F | Urban | Asset failure | LV | 3 | 99 | 0.00047481 | 4.8e-06 | No
9/12/2018 | 08:09:11 | LX71 | Rural Long | Unknown | Unknown | 24 | 122 | 0.02137 | 0.00017516 | No
9/12/2018 | 08:12:21 | NL451C | Urban | Animal | Animal impact | 1432 | 45.0265 | 0.10308 | 0.0022893 | No
9/12/2018 | 08:23:00 | SA12 | Urban | Planned |  | 1 | 344 | 0.00054994 | 1.6e-06 | No
9/12/2018 | 08:24:27 | ME200A | Urban | Planned |  | 15 | 241 | 0.0057792 | 2.398e-05 | No
9/12/2018 | 08:43:57 | MV62 | Rural Short | Asset failure | HV | 16 | 202.125 | 0.024094 | 0.0001192 | No
9/12/2018 | 10:05:23 | HH386F | Urban | Planned |  | 105 | 102 | 0.017122 | 0.00016786 | No
9/12/2018 | 10:39:53 | SM411F | Urban | Overloads |  | 4 | 396 | 0.0025323 | 6.39e-06 | No
9/12/2018 | 10:48:16 | ST21 | Rural Short | Asset failure | Distribution substation | 2 | 602 | 0.00897 | 1.49e-05 | No
9/12/2018 | 10:59:10 | HH341A | Urban | Planned |  | 4 | 278 | 0.0017777 | 6.39e-06 | No
9/12/2018 | 11:36:38 | R23 | Rural Long | Asset failure | LV | 1 | 120 | 0.0008758 | 7.3e-06 | No
9/12/2018 | 13:11:53 | BT03 | Rural Long | Weather |  | 143.3334 | 335.8721 | 0.35135 | 0.0010461 | No
9/12/2018 | 13:32:31 | BT02 | Rural Long | Weather |  | 93 | 469.5699 | 0.31872 | 0.00067875 | No
9/12/2018 | 14:24:24 | NA04 | Rural Long | Unknown | Unknown | 36.6667 | 554 | 0.14825 | 0.00026761 | No
9/12/2018 | 14:44:57 | NA02 | Rural Long | Unknown | Unknown | 87 | 69 | 0.043812 | 0.00063496 | No
9/12/2018 | 15:38:49 | NA04 | Rural Long | Unknown | Unknown | 15 | 231 | 0.025289 | 0.00010948 | No
9/12/2018 | 16:28:46 | BM53 | Rural Short | Unknown | Unknown | 13 | 77 | 0.0074576 | 9.685e-05 | No
9/12/2018 | 16:32:13 | W04 | Rural Long | Unknown | Unknown | 1 | 15 | 0.00010948 | 7.3e-06 | No
9/12/2018 | 16:41:02 | LX21 | Rural Short | Unknown | Unknown | 4 | 98 | 0.0029205 | 2.98e-05 | No
9/12/2018 | 16:44:08 | LX24 | Rural Short | Weather |  | 2 | 99 | 0.0014751 | 1.49e-05 | No
9/12/2018 | 20:39:55 | NL111Q | Urban | Asset failure | LV | 1 | 182 | 0.00029096 | 1.6e-06 | No
9/12/2018 | 20:56:15 | HH177B | Urban | Unknown | Unknown | 29.3333 | 195 | 0.0091444 | 4.689e-05 | No
9/12/2018 | 21:07:35 | HH177B | Urban | Asset failure | LV | 1 | 218 | 0.00034851 | 1.6e-06 | No
9/12/2018 | 21:07:44 | AP139C | Urban | Asset failure | LV | 2 | 268 | 0.00085689 | 3.2e-06 | No
9/12/2018 | 21:43:01 | ST21 | Rural Short | Overloads |  | 2 | 32 | 0.00047681 | 1.49e-05 | No
9/12/2018 | 22:56:30 | SG07 | Rural Short | Unknown | Unknown | 631.0003 | 1 | 0.0047011 | 0.0047011 | No
9/12/2018 | 22:56:30 | SG07 | Rural Short | Unknown | Unknown | 54.6667 | 219 | 0.089193 | 0.00040728 | No
10/12/2018 | 03:27:13 | W29 | Rural Long | Unknown | Unknown | 82 | 389.6098 | 0.23317 | 0.00059846 | No
10/12/2018 | 06:11:15 | SM349D | Urban | Animal | Animal impact | 307 | 153 | 0.075091 | 0.00049079 | No
10/12/2018 | 07:56:05 | SB03 | Rural Long | Unknown | Unknown | 3 | 293 | 0.0064152 | 2.19e-05 | No
10/12/2018 | 08:09:21 | MV53 | Rural Short | Planned |  | 31 | 242 | 0.055891 | 0.00023095 | No
10/12/2018 | 08:10:17 | NL234A | Urban | Asset failure | LV | 1 | 382 | 0.00061069 | 1.6e-06 | No
10/12/2018 | 08:18:40 | HH496B | Urban | Asset failure | LV | 8 | 141 | 0.0018033 | 1.279e-05 | No
10/12/2018 | 08:35:06 | HH409D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 25 | 280 | 0.011191 | 3.997e-05 | No
10/12/2018 | 08:57:54 | VH61 | Rural Short | Asset failure | LV | 2 | 98 | 0.0014602 | 1.49e-05 | No
10/12/2018 | 09:06:14 | SA41 | Urban | Planned |  | 8 | 240 | 0.0030695 | 1.279e-05 | No
10/12/2018 | 09:15:46 | MV22 | Rural Short | Planned |  | 33 | 290 | 0.071298 | 0.00024585 | No
10/12/2018 | 09:16:36 | GU43 | Rural Long | Planned |  | 31 | 288 | 0.06516 | 0.00022625 | No
10/12/2018 | 09:27:43 | BT26 | Rural Long | Weather |  | 322 | 5.646 | 0.013268 | 0.0023501 | No
10/12/2018 | 09:40:22 | GA08 | Rural Long | Planned |  | 60 | 302 | 0.13225 | 0.0004379 | No
10/12/2018 | 09:52:32 | HH386F | Urban | Planned |  | 2 | 308 | 0.00098478 | 3.2e-06 | No
10/12/2018 | 10:18:35 | ST36 | Rural Long | Planned |  | 159 | 281 | 0.32608 | 0.0011604 | No
10/12/2018 | 10:40:27 | MG09 | Rural Short | Asset failure | LV | 1.3333 | 154 | 0.0015298 | 9.93e-06 | No
10/12/2018 | 11:18:48 | GA18 | Rural Long | Unknown | Unknown | 2 | 44 | 0.00064225 | 1.46e-05 | No
10/12/2018 | 11:25:30 | HH432B | Urban | Asset failure | LV | 123 | 69 | 0.013568 | 0.00019664 | No
10/12/2018 | 11:32:34 | BT18 | Rural Long | Third Party | Vehicle impact | 29 | 271.7586 | 0.057518 | 0.00021165 | No
10/12/2018 | 12:41:11 | NL210C | Urban | Vegetation | Grow-in - NSP responsibility | 18 | 52 | 0.0014964 | 2.878e-05 | No
10/12/2018 | 13:29:48 | HH121B | Urban | Asset failure | LV | 12.6667 | 117 | 0.0023692 | 2.025e-05 | No
10/12/2018 | 13:30:28 | SA20 | Urban | Asset failure | LV | 1 | 150 | 0.0002398 | 1.6e-06 | No
10/12/2018 | 13:35:51 | CV08 | Rural Long | Asset failure | LV | 1 | 195 | 0.0014232 | 7.3e-06 | No
10/12/2018 | 14:34:59 | NA27 | Rural Long | Weather |  | 2 | 35 | 0.00051088 | 1.46e-05 | No
10/12/2018 | 14:44:09 | AP529C | Urban | Asset failure | LV | 26 | 190 | 0.0078975 | 4.157e-05 | No
10/12/2018 | 16:40:47 | W31 | Rural Short | Weather |  | 1 | 7 | 5.215e-05 | 7.45e-06 | No
10/12/2018 | 17:26:00 | VH12 | Rural Short | Asset failure | LV | 1 | 105 | 0.00078227 | 7.45e-06 | No
10/12/2018 | 17:35:22 | HH121B | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
10/12/2018 | 20:00:46 | CL08 | Rural Long | Third Party | Vehicle impact | 2 | 21 | 0.00030653 | 1.46e-05 | No
10/12/2018 | 22:39:23 | CBD353N | CBD | Planned |  | 1 | 3227 | 0.62642 | 0.00019412 | No
10/12/2018 | 23:00:18 | SA42 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 37 | 0.0002366 | 6.39e-06 | No
11/12/2018 | 02:22:08 | CV18 | Rural Short | Unknown | Unknown | 30 | 258 | 0.057664 | 0.0002235 | No
11/12/2018 | 04:43:39 | BS0336 | Urban | Planned |  | 1 | 66 | 0.00010551 | 1.6e-06 | No
11/12/2018 | 07:48:43 | SG02 | Rural Short | Unknown | Unknown | 723 | 81.0069 | 0.43634 | 0.0053865 | No
11/12/2018 | 08:12:30 | ST24 | Rural Short | Planned |  | 11 | 189 | 0.015489 | 8.195e-05 | No
11/12/2018 | 08:16:31 | AP125D | Urban | Planned |  | 153 | 340.3725 | 0.083254 | 0.0002446 | No
11/12/2018 | 08:22:37 | MV14 | Rural Short | Planned |  | 84 | 302.4643 | 0.18929 | 0.00062581 | No
11/12/2018 | 08:47:29 | SM349C | Urban | Planned |  | 36 | 198 | 0.011395 | 5.755e-05 | No
11/12/2018 | 08:52:48 | NU23 | Rural Long | Planned |  | 28 | 130 | 0.026566 | 0.00020435 | No
11/12/2018 | 08:55:30 | HH121G | Urban | Third Party | Vehicle impact | 69 | 334 | 0.036843 | 0.00011031 | No
11/12/2018 | 09:01:38 | HH341K | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 152 | 0.000243 | 1.6e-06 | No
11/12/2018 | 09:02:59 | NL544B | Urban | Planned |  | 265 | 213 | 0.090237 | 0.00042365 | No
11/12/2018 | 09:09:57 | VH22 | Rural Short | Planned |  | 17 | 129 | 0.016338 | 0.00012665 | No
11/12/2018 | 09:10:09 | MB91 | Rural Long | Planned |  | 11 | 233 | 0.018706 | 8.028e-05 | No
11/12/2018 | 09:13:43 | GU41 | Rural Long | Planned |  | 9 | 236 | 0.015502 | 6.569e-05 | No
11/12/2018 | 09:15:11 | VH15 | Rural Short | Planned |  | 2 | 195 | 0.0029056 | 1.49e-05 | No
11/12/2018 | 09:19:08 | MG02 | Rural Long | Asset failure | LV | 1 | 115 | 0.00083931 | 7.3e-06 | No
11/12/2018 | 09:19:08 | EL260B | Urban | Planned |  | 389 | 8.1003 | 0.0050374 | 0.00062188 | No
11/12/2018 | 09:19:08 | EL260B | Urban | Planned |  | 49 | 43.1837 | 0.0033828 | 7.834e-05 | No
11/12/2018 | 09:24:20 | EL18 | Urban | Planned |  | 15 | 238 | 0.0057073 | 2.398e-05 | No
11/12/2018 | 09:31:25 | MV53 | Rural Short | Asset failure | LV | 5 | 507 | 0.018886 | 3.725e-05 | No
11/12/2018 | 09:33:16 | NL544B | Urban | Planned |  | 1 | 104 | 0.00016626 | 1.6e-06 | No
11/12/2018 | 09:50:30 | VH23 | Rural Short | Planned |  | 402 | 224 | 0.67087 | 0.002995 | No
11/12/2018 | 10:44:51 | WK21 | Rural Short | Planned |  | 76 | 199 | 0.11268 | 0.00056621 | No
11/12/2018 | 11:48:06 | GU14 | Rural Long | Asset failure | HV | 6 | 221 | 0.0096776 | 4.379e-05 | No
11/12/2018 | 11:57:26 | SD45101 | Rural Long | Planned |  | 2 | 42 | 0.00061306 | 1.46e-05 | No
11/12/2018 | 11:57:49 | SM349F | Urban | Asset failure | LV | 148 | 111 | 0.026263 | 0.0002366 | No
11/12/2018 | 12:12:32 | MTB54 | Rural Long | Planned |  | 42 | 210 | 0.064371 | 0.00030653 | No
11/12/2018 | 13:14:57 | M93 | Rural Long | Asset failure | HV | 2 | 38 | 0.00055467 | 1.46e-05 | No
11/12/2018 | 13:23:40 | SM350B | Urban | Planned |  | 1629 | 2 | 0.0052085 | 0.0026042 | No
11/12/2018 | 14:48:38 | VH31 | Rural Short | Unknown | Unknown | 223 | 125 | 0.20767 | 0.0016614 | No
11/12/2018 | 16:11:43 | SD37102 | Rural Long | Unknown | Unknown | 3.3333 | 215 | 0.0052305 | 2.433e-05 | No
11/12/2018 | 18:17:07 | SM349E | Urban | Overloads |  | 1 | 254 | 0.00040606 | 1.6e-06 | No
11/12/2018 | 19:09:49 | HH496F | Urban | Planned |  | 42 | 329 | 0.02209 | 6.714e-05 | No
11/12/2018 | 20:27:09 | W30 | Rural Short | Weather |  | 4 | 1195 | 0.035612 | 2.98e-05 | No
11/12/2018 | 20:57:00 | SM137B | Urban | Asset failure | LV | 31 | 75 | 0.0037169 | 4.956e-05 | No
12/12/2018 | 00:28:19 | KI32 | Rural Short | Asset failure | HV | 741 | 122.5628 | 0.67662 | 0.0055206 | No
12/12/2018 | 02:04:20 | W29 | Rural Long | Weather |  | 82 | 450.6829 | 0.26972 | 0.00059846 | No
12/12/2018 | 07:39:36 | BM34 | Rural Short | Unknown | Unknown | 460 | 32 | 0.10967 | 0.0034271 | No
12/12/2018 | 08:09:31 | ST24 | Rural Short | Planned |  | 52 | 134.8462 | 0.05224 | 0.00038741 | No
12/12/2018 | 08:22:48 | AP227D | Urban | Asset failure | LV | 1 | 220 | 0.00035171 | 1.6e-06 | No
12/12/2018 | 08:46:45 | VH33 | Rural Short | Planned |  | 136 | 357 | 0.36172 | 0.0010132 | No
12/12/2018 | 08:50:06 | HH130D | Urban | Planned |  | 4 | 349 | 0.0022317 | 6.39e-06 | No
12/12/2018 | 08:56:59 | MV13 | Rural Short | Planned |  | 51 | 210 | 0.079791 | 0.00037996 | No
12/12/2018 | 09:06:48 | HH148D | Urban | Planned |  | 6 | 219 | 0.0021007 | 9.59e-06 | No
12/12/2018 | 09:06:53 | HH496A / HH145B | Urban | Planned |  | 892 | 229.9933 | 0.32797 | 0.001426 | No
12/12/2018 | 09:07:11 | ST44 | Rural Long | Planned |  | 3 | 63 | 0.0013794 | 2.19e-05 | No
12/12/2018 | 09:10:19 | HH130D | Urban | Planned |  | 2 | 8 | 2.558e-05 | 3.2e-06 | No
12/12/2018 | 09:15:03 | HH496G | Urban | Planned |  | 131 | 348 | 0.07288 | 0.00020943 | No
12/12/2018 | 09:17:15 | AP146E | Urban | Planned |  | 3 | 152 | 0.000729 | 4.8e-06 | No
12/12/2018 | 09:23:05 | EL20 | Urban | Planned |  | 28 | 257 | 0.011504 | 4.476e-05 | No
12/12/2018 | 09:24:23 | SG13 | Rural Short | Planned |  | 72 | 457 | 0.24514 | 0.00053641 | No
12/12/2018 | 09:30:49 | AP146B | Urban | Planned |  | 68 | 180 | 0.019568 | 0.00010871 | No
12/12/2018 | 09:34:07 | MTB32 | Rural Long | Planned |  | 104 | 330 | 0.25048 | 0.00075903 | No
12/12/2018 | 09:36:28 | ST41 | Rural Long | Planned |  | 105 | 178 | 0.13641 | 0.00076633 | No
12/12/2018 | 09:42:13 | GU32 | Rural Long | Planned |  | 5 | 294 | 0.010729 | 3.649e-05 | No
12/12/2018 | 09:44:26 | BM44 | Rural Short | Planned |  | 12 | 244 | 0.021814 | 8.94e-05 | No
12/12/2018 | 09:55:55 | PP08 | Rural Long | Planned |  | 17 | 163 | 0.020224 | 0.00012407 | No
12/12/2018 | 10:10:38 | R12 | Rural Long | Planned |  | 2 | 67 | 0.00097798 | 1.46e-05 | No
12/12/2018 | 11:43:58 | G17 | Rural Long | Unknown | Unknown | 5 | 141 | 0.0051453 | 3.649e-05 | No
12/12/2018 | 12:13:50 | NA02 | Rural Long | Unknown | Unknown | 13 | 357 | 0.033872 | 9.488e-05 | No
12/12/2018 | 14:10:00 | BT20 | Rural Long | Planned |  | 34 | 4.1765 | 0.0010364 | 0.00024814 | No
12/12/2018 | 14:25:08 | BT20 | Rural Long | Asset failure | HV | 1 | 11519 | 0.08407 | 7.3e-06 | No
12/12/2018 | 14:29:08 | NL210E | Urban | Asset failure | LV | 1 | 359 | 0.00057392 | 1.6e-06 | No
12/12/2018 | 15:24:44 | CM29 | Rural Long | Weather |  | 64 | 221 | 0.10323 | 0.00046709 | No
12/12/2018 | 15:41:49 | YK05 | Rural Long | Asset failure | HV | 39 | 213 | 0.060627 | 0.00028464 | No
12/12/2018 | 15:47:20 | LX53 | Rural Short | Unknown | Unknown | 16 | 128 | 0.015258 | 0.0001192 | No
12/12/2018 | 15:51:02 | BM34 | Rural Short | Vegetation | Grow-in - NSP responsibility | 460 | 82 | 0.28102 | 0.0034271 | No
12/12/2018 | 15:53:09 | BT31 | Rural Long | Weather |  | 61 | 487.6885 | 0.21712 | 0.0004452 | No
12/12/2018 | 15:59:00 | CM15 | Rural Long | Weather |  | 7 | 592.1429 | 0.030252 | 5.109e-05 | No
12/12/2018 | 16:18:15 | BT04 | Rural Long | Weather |  | 101 | 209.2673 | 0.15426 | 0.00073713 | No
12/12/2018 | 16:18:53 | CV31 | Rural Long | Unknown | Unknown | 29 | 56 | 0.011853 | 0.00021165 | No
12/12/2018 | 16:53:39 | LM64 | Rural Long | Weather |  | 68 | 293 | 0.14541 | 0.00049629 | No
12/12/2018 | 17:09:38 | MV51 | Rural Short | Unknown | Unknown | 119 | 143 | 0.12678 | 0.00088657 | No
12/12/2018 | 17:15:43 | MT06 | Rural Long | Asset failure | LV | 11.3333 | 267 | 0.022085 | 8.271e-05 | No
12/12/2018 | 17:26:27 | GA37 | Rural Long | Weather |  | 1 | 231 | 0.0016859 | 7.3e-06 | No
12/12/2018 | 17:28:00 | BT23 | Rural Long | Weather |  | 50 | 985.94 | 0.35979 | 0.00036492 | No
12/12/2018 | 17:28:00 | BT23 | Rural Long | Weather |  | 0 | 64.5185 | 0.012714 | 0 | No
12/12/2018 | 17:28:26 | MB13 | Rural Short | Asset failure | LV | 1 | 305 | 0.0022723 | 7.45e-06 | No
12/12/2018 | 18:31:28 | LX41 | Rural Short | Weather |  | 3 | 336 | 0.0075097 | 2.235e-05 | No
12/12/2018 | 21:25:45 | SB18 | Rural Long | Weather |  | 12 | 233.3333 | 0.020435 | 8.758e-05 | No
12/12/2018 | 21:25:45 | SB18 | Rural Long | Weather |  | 0 | 141 | 0.0061744 | 0 | No
12/12/2018 | 21:57:55 | PL30 | Rural Long | Weather |  | 19 | 611.7895 | 0.084836 | 0.00013867 | No
12/12/2018 | 21:57:55 | PL30 | Rural Long | Weather |  | 0 | 474 | 0.013838 | 0 | No
12/12/2018 | 22:52:21 | ST42 | Rural Long | Weather |  | 791 | 136.7434 | 0.78942 | 0.005773 | No
12/12/2018 | 22:54:28 | ST12 | Rural Short | Unknown | Unknown | 20 | 729 | 0.10862 | 0.000149 | No
12/12/2018 | 22:57:20 | CN25 | Rural Long | Weather |  | 51 | 308.1765 | 0.11471 | 0.00037222 | No
12/12/2018 | 23:04:44 | ST34 | Rural Long | Weather |  | 69 | 312.971 | 0.15761 | 0.00050359 | No
12/12/2018 | 23:05:37 | LX41 | Rural Short | Weather |  | 3 | 49 | 0.0010952 | 2.235e-05 | No
12/12/2018 | 23:15:36 | MTB32 | Rural Long | Weather |  | 7 | 150 | 0.0076632 | 5.109e-05 | No
12/12/2018 | 23:37:22 | EL01R | Urban | Animal | Animal impact | 61.3334 | 204 | 0.020003 | 9.805e-05 | No
12/12/2018 | 23:51:27 | CN75 | Rural Long | Unknown | Unknown | 57 | 229 | 0.095265 | 0.00041601 | No
12/12/2018 | 23:51:27 | CN75 | Rural Long | Unknown | Unknown | 0 | 138.9649 | 0.05781 | 0 | No
12/12/2018 | 23:54:30 | BM34 | Rural Short | Unknown | Unknown | 460 | 189.7891 | 0.65042 | 0.0034271 | No
12/12/2018 | 23:54:30 | BM34 | Rural Short | Unknown | Unknown | 0 | 2 | 0.00084932 | 0 | No
12/12/2018 | 23:56:06 | GU31 | Rural Long | Weather |  | 4 | 369 | 0.010772 | 2.919e-05 | No
13/12/2018 | 00:03:04 | W31 | Rural Short | Unknown | Unknown | 14 | 647 | 0.067483 | 0.0001043 | No
13/12/2018 | 00:27:55 | NU22 | Rural Long | Unknown | Unknown | 24 | 309 | 0.054124 | 0.00017516 | No
13/12/2018 | 00:30:27 | CN83 | Rural Long | Weather |  | 94 | 929.6383 | 0.63777 | 0.00068604 | No
13/12/2018 | 00:30:27 | CN83 | Rural Long | Weather |  | 0 | 33 | 0.020231 | 0 | No
13/12/2018 | 01:06:16 | ME427E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 101 | 0.00016147 | 1.6e-06 | No
13/12/2018 | 02:44:00 | LM51 | Rural Long | Unknown | Unknown | 104 | 470 | 0.35674 | 0.00075903 | No
13/12/2018 | 02:50:16 | CN52 | Rural Long | Unknown | Unknown | 2 | 4 | 5.839e-05 | 1.46e-05 | No
13/12/2018 | 03:18:35 | SM172E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 108 | 480 | 0.082875 | 0.00017266 | No
13/12/2018 | 03:32:50 | LX54 | Rural Short | Unknown | Unknown | 10 | 527 | 0.039262 | 7.45e-05 | No
13/12/2018 | 03:39:12 | MV51 | Rural Short | Weather |  | 119 | 404.4118 | 0.35854 | 0.00088657 | No
13/12/2018 | 04:27:18 | SD38100 | Rural Long | Unknown | Unknown | 5 | 437 | 0.015947 | 3.649e-05 | No
13/12/2018 | 04:29:33 | NU14 | Rural Long | Unknown | Unknown | 16.6667 | 271 | 0.032964 | 0.00012164 | No
13/12/2018 | 04:57:10 | KA04 | Rural Long | Weather |  | 946 | 53 | 0.36592 | 0.0069042 | No
13/12/2018 | 04:59:09 | MB43 | Rural Long | Asset failure | Distribution substation | 85 | 1382.6824 | 0.85776 | 0.00062036 | No
13/12/2018 | 04:59:09 | MB43 | Rural Long | Asset failure | Distribution substation | 0 | 9.7619 | 0.0044885 | 0 | No
13/12/2018 | 05:04:04 | VH32 | Rural Short | Weather |  | 107 | 183.028 | 0.1459 | 0.00079717 | No
13/12/2018 | 05:59:00 | SD40101 | Rural Long | Weather |  | 1215 | 763 | 6.7659 | 0.0088675 | No
13/12/2018 | 06:18:25 | NU22 | Rural Long | Unknown | Unknown | 4 | 306 | 0.0089332 | 2.919e-05 | No
13/12/2018 | 06:19:16 | ST23 | Rural Short | Unknown | Unknown | 5.6667 | 197 | 0.0083169 | 4.222e-05 | No
13/12/2018 | 06:20:03 | SM374A | Urban | Vegetation | Grow-in - NSP responsibility | 16 | 334 | 0.0085433 | 2.558e-05 | No
13/12/2018 | 06:42:09 | MT01 | Rural Long | Asset failure | HV | 4 | 263 | 0.0076778 | 2.919e-05 | No
13/12/2018 | 06:44:32 | CN33 | Rural Long | Unknown | Unknown | 8 | 594 | 0.034682 | 5.839e-05 | No
13/12/2018 | 06:47:02 | AP227A | Urban | Asset failure | LV | 1.3333 | 133 | 0.0002835 | 2.13e-06 | No
13/12/2018 | 07:29:57 | PA19 | Rural Long | Unknown | Unknown | 2 | 157 | 0.0022917 | 1.46e-05 | No
13/12/2018 | 07:46:29 | VH32 | Rural Short | Asset failure | HV | 1 | 109 | 0.00081207 | 7.45e-06 | No
13/12/2018 | 07:56:33 | SM410A | Urban | Unknown | Unknown | 1705 | 72 | 0.19625 | 0.0027257 | No
13/12/2018 | 08:00:30 | HH409E | Urban | Asset failure | LV | 1 | 80 | 0.00012789 | 1.6e-06 | No
13/12/2018 | 08:08:54 | KA02 | Rural Short | Weather |  | 1 | 1692 | 0.012606 | 7.45e-06 | No
13/12/2018 | 08:18:00 | W06 | Rural Long | Other |  | 1 | 272 | 0.0019852 | 7.3e-06 | No
13/12/2018 | 08:23:15 | ME231F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 51 | 0.00032613 | 6.39e-06 | No
13/12/2018 | 08:35:32 | BM31 | Rural Short | Unknown | Unknown | 451 | 239 | 0.80304 | 0.00336 | No
13/12/2018 | 08:59:47 | ME427E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 683 | 0.0010919 | 1.6e-06 | No
13/12/2018 | 09:05:01 | MTB13 | Rural Short | Planned |  | 35 | 44 | 0.011473 | 0.00026076 | No
13/12/2018 | 09:09:17 | ST44 | Rural Long | Planned |  | 36 | 157 | 0.04125 | 0.00026274 | No
13/12/2018 | 09:18:36 | NL111C | Urban | Asset failure | LV | 12 | 232 | 0.0044507 | 1.918e-05 | No
13/12/2018 | 09:20:05 | CD26 | Rural Long | Planned |  | 5 | 277 | 0.010108 | 3.649e-05 | No
13/12/2018 | 09:31:31 | SA35 | Urban | Planned |  | 26 | 181 | 0.0075234 | 4.157e-05 | No
13/12/2018 | 09:39:39 | MTB32 | Rural Long | Planned |  | 43 | 303 | 0.09509 | 0.00031383 | No
13/12/2018 | 09:42:59 | HH102C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 232 | 0.0063052 | 2.718e-05 | No
13/12/2018 | 09:47:46 | MV64 | Urban | Unknown | Unknown | 605 | 141.0132 | 0.13639 | 0.0009672 | No
13/12/2018 | 09:48:40 | HH432B | Urban | Planned |  | 56 | 8 | 0.00071621 | 8.953e-05 | No
13/12/2018 | 10:10:41 | HH177C | Urban | Planned |  | 309 | 163 | 0.08052 | 0.00049399 | No
13/12/2018 | 10:17:50 | SG08 / SG09 | Rural Short | Planned |  | 260 | 322.4038 | 0.62451 | 0.001937 | No
13/12/2018 | 10:43:05 | GA36 | Rural Long | Asset failure | HV | 3 | 411 | 0.0089988 | 2.19e-05 | No
13/12/2018 | 10:51:00 | CN52 | Rural Long | Asset failure | HV | 87 | 1130.0345 | 0.71752 | 0.00063496 | No
13/12/2018 | 10:51:00 | CN52 | Rural Long | Asset failure | HV | 0 | 9 | 0.0034813 | 0 | No
13/12/2018 | 10:58:57 | GA26 | Urban | Planned |  | 19 | 36 | 0.0010935 | 3.037e-05 | No
13/12/2018 | 11:13:58 | HH341H | Urban | Asset failure | LV | 2 | 199 | 0.00063627 | 3.2e-06 | No
13/12/2018 | 11:23:31 | ST23 | Rural Short | Weather |  | 5.6667 | 341 | 0.014396 | 4.222e-05 | No
13/12/2018 | 11:24:58 | ST34 | Rural Long | Unknown | Unknown | 55 | 296 | 0.11882 | 0.00040141 | No
13/12/2018 | 11:36:02 | NA61 | Rural Long | Weather |  | 17 | 34 | 0.0042184 | 0.00012407 | No
13/12/2018 | 11:45:50 | HH145C | Urban | Planned |  | 220 | 111 | 0.03904 | 0.00035171 | No
13/12/2018 | 11:51:49 | SM410D | Urban | Vegetation | Grow-in - NSP responsibility | 1895 | 272.0908 | 0.8243 | 0.0030295 | No
13/12/2018 | 11:56:00 | LM63 | Rural Long | Asset failure | HV | 75 | 190.28 | 0.10415 | 0.00054738 | No
13/12/2018 | 12:22:00 | HH145C | Urban | Planned |  | 1 | 64 | 0.00010232 | 1.6e-06 | No
13/12/2018 | 12:29:04 | ME347C | Urban | Other |  | 8.3333 | 242 | 0.003224 | 1.332e-05 | No
13/12/2018 | 12:52:01 | HH121C | Urban | Vegetation | Grow-in - NSP responsibility | 10 | 181 | 0.0028936 | 1.599e-05 | No
13/12/2018 | 12:58:41 | HH341H | Urban | Vegetation | Grow-in - NSP responsibility | 27 | 97 | 0.0041869 | 4.316e-05 | No
13/12/2018 | 13:00:00 | EL20 | Urban | Third Party | Other | 463 | 27.8078 | 0.020583 | 0.00074019 | No
13/12/2018 | 13:00:54 | MTB11 | Rural Short | Planned |  | 60 | 67 | 0.02995 | 0.00044701 | No
13/12/2018 | 13:00:54 | MTB32 | Rural Long | Unknown | Unknown | 314 | 103.6115 | 0.23744 | 0.0022917 | No
13/12/2018 | 13:00:54 | MTB32 | Rural Long | Planned |  | 225 | 100 | 0.16421 | 0.0016421 | No
13/12/2018 | 13:07:40 | W04 | Rural Long | Asset failure | LV | 3 | 348 | 0.0076195 | 2.19e-05 | No
13/12/2018 | 13:15:01 | AP424A | Urban | Unknown | Unknown | 1903 | 70.4125 | 0.21421 | 0.0030423 | No
13/12/2018 | 13:22:37 | AP351C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 28.3333 | 142 | 0.006432 | 4.53e-05 | No
13/12/2018 | 13:28:00 | NA61 | Rural Long | Weather |  | 17 | 351.2941 | 0.043586 | 0.00012407 | No
13/12/2018 | 13:32:36 | HH429B | Urban | Asset failure | LV | 32.6667 | 186 | 0.0097135 | 5.222e-05 | No
13/12/2018 | 13:33:36 | PA05 | Rural Long | Asset failure | LV | 12.6667 | 88 | 0.0081352 | 9.245e-05 | No
13/12/2018 | 13:45:44 | ME231F | Urban | Asset failure | LV | 132 | 390 | 0.0823 | 0.00021103 | No
13/12/2018 | 13:54:08 | PP04 | Rural Short | Asset failure | LV | 17 | 200 | 0.025331 | 0.00012665 | No
13/12/2018 | 13:55:00 | PA13 | Rural Long | Asset failure | HV | 29.3333 | 1 | 0.00021408 | 0.00021408 | No
13/12/2018 | 14:05:30 | GA22 | Rural Short | Asset failure | HV | 295 | 216.9966 | 0.47691 | 0.0021978 | No
13/12/2018 | 14:30:44 | LX71 | Rural Long | Weather |  | 2 | 49 | 0.00071524 | 1.46e-05 | No
13/12/2018 | 14:30:45 | ST41 | Rural Long | Weather |  | 96 | 38 | 0.026624 | 0.00070064 | No
13/12/2018 | 14:40:00 | CV24 | Rural Long | Asset failure | HV | 73 | 105.7671 | 0.05635 | 0.00053278 | No
13/12/2018 | 15:27:10 | HH145A | Urban | Vegetation | Grow-in - NSP responsibility | 289 | 69 | 0.031879 | 0.00046202 | No
13/12/2018 | 15:35:30 | HH121F | Urban | Unknown | Unknown | 16.6667 | 196 | 0.0052223 | 2.664e-05 | No
13/12/2018 | 15:45:32 | HH341C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 881 | 153.0806 | 0.2156 | 0.0014084 | No
13/12/2018 | 15:51:14 | AP425A | Urban | Asset failure | LV | 16.6667 | 89 | 0.0023714 | 2.664e-05 | No
13/12/2018 | 16:36:30 | NL511B | Urban | Asset failure | LV | 1 | 143 | 0.00022861 | 1.6e-06 | No
13/12/2018 | 16:40:51 | NL511B | Urban | Asset failure | LV | 1 | 140 | 0.00022381 | 1.6e-06 | No
13/12/2018 | 16:46:07 | CN25 | Rural Long | Asset failure | HV | 51 | 1098.0588 | 0.40871 | 0.00037222 | No
13/12/2018 | 16:49:01 | SD32200 | Rural Long | Other |  | 4.3333 | 169 | 0.0053448 | 3.163e-05 | No
13/12/2018 | 17:34:45 | HH403B | Urban | Vegetation | Grow-in - NSP responsibility | 5 | 31 | 0.00024779 | 7.99e-06 | No
13/12/2018 | 18:10:25 | VH21 | Rural Short | Asset failure | LV | 1 | 295 | 0.0021978 | 7.45e-06 | No
13/12/2018 | 18:18:46 | SA744C | Urban | Asset failure | HV | 1 | 292 | 0.00046681 | 1.6e-06 | No
13/12/2018 | 18:21:13 | ST23 | Rural Short | Weather |  | 5.6667 | 209 | 0.0088235 | 4.222e-05 | No
13/12/2018 | 18:33:48 | AP529D | Urban | Asset failure | LV | 19.6666 | 116 | 0.0036471 | 3.144e-05 | No
13/12/2018 | 19:04:29 | ST35 | Rural Long | Unknown | Unknown | 844 | 11.6576 | 0.071808 | 0.0061598 | No
13/12/2018 | 19:20:21 | MB62 | Rural Long | Weather |  | 648 | 132 | 0.62427 | 0.0047293 | No
13/12/2018 | 19:38:56 | AP424C | Urban | Asset failure | LV | 30 | 62 | 0.0029735 | 4.796e-05 | No
13/12/2018 | 19:40:39 | BM56 | Rural Short | Asset failure | HV | 175.3334 | 245.2186 | 0.32032 | 0.0013063 | No
13/12/2018 | 19:40:39 | BM56 | Rural Short | Asset failure | HV | 0 | 3.5319 | 0.0071397 | 0 | No
13/12/2018 | 20:03:25 | CN33 | Rural Long | Weather |  | 8 | 1016 | 0.059321 | 5.839e-05 | No
13/12/2018 | 21:12:34 | CN02 | Rural Long | Unknown | Unknown | 1 | 29 | 0.00021165 | 7.3e-06 | No
13/12/2018 | 21:29:55 | EL19 | Urban | Unknown | Unknown | 34 | 326 | 0.01772 | 5.435e-05 | No
13/12/2018 | 21:30:05 | HH130F | Urban | Asset failure | LV | 1 | 168 | 0.00026858 | 1.6e-06 | No
13/12/2018 | 22:08:01 | AP355B | Urban | Asset failure | HV | 21 | 57 | 0.0019136 | 3.357e-05 | No
13/12/2018 | 22:38:37 | SA16 / SA19 | Urban | Planned |  | 52 | 345.8654 | 0.028752 | 8.313e-05 | No
13/12/2018 | 23:07:42 | AP132D | Urban | Asset failure | LV | 19.6666 | 108 | 0.0033956 | 3.144e-05 | No
14/12/2018 | 00:18:40 | HH386A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 66 | 0.00010551 | 1.6e-06 | No
14/12/2018 | 00:28:23 | VH15 | Rural Short | Weather |  | 3456 | 179.4986 | 4.6217 | 0.025748 | No
14/12/2018 | 01:51:31 | AP424A | Urban | Weather |  | 1903 | 12.2386 | 0.037233 | 0.0030423 | No
14/12/2018 | 02:58:42 | SM410C | Urban | Weather |  | 2741 | 206.8449 | 0.90639 | 0.004382 | No
14/12/2018 | 03:15:53 | MV34 | Rural Short | Unknown | Unknown | 228 | 70.3947 | 0.11957 | 0.0016986 | No
14/12/2018 | 03:16:52 | HH102C | Urban | Unknown | Unknown | 236 | 91 | 0.034333 | 0.00037729 | No
14/12/2018 | 04:15:38 | LM51 | Rural Long | Unknown | Unknown | 104 | 955.5673 | 0.7253 | 0.00075903 | No
14/12/2018 | 04:20:50 | AP146C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 495 | 0.00079134 | 1.6e-06 | No
14/12/2018 | 05:03:59 | SA33 | Urban | Unknown | Unknown | 1 | 69 | 0.00011031 | 1.6e-06 | No
14/12/2018 | 05:45:10 | CV26 | Rural Long | Weather |  | 66 | 374 | 0.18015 | 0.00048169 | No
14/12/2018 | 06:02:56 | MG44 | Urban | Asset failure | HV | 65 | 449 | 0.046657 | 0.00010391 | No
14/12/2018 | 06:08:19 | SG04 | Rural Short | Unknown | Unknown | 210 | 177 | 0.27692 | 0.0015645 | No
14/12/2018 | 06:16:19 | MG05 | Rural Long | Unknown | Unknown | 1194 | 84.7697 | 0.7387 | 0.0087142 | No
14/12/2018 | 06:58:31 | VH15 | Rural Short | Asset failure | LV | 7 | 273 | 0.014237 | 5.215e-05 | No
14/12/2018 | 07:17:19 | AP149E | Urban | Asset failure | LV | 24 | 102 | 0.0039136 | 3.837e-05 | No
14/12/2018 | 07:41:18 | VH12 | Rural Short | Asset failure | LV | 16 | 96 | 0.011443 | 0.0001192 | No
14/12/2018 | 08:04:36 | MI01 | Rural Long | Weather |  | 1 | 190 | 0.0013867 | 7.3e-06 | No
14/12/2018 | 08:05:03 | LX41 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 442 | 132 | 0.43467 | 0.003293 | No
14/12/2018 | 08:27:31 | AP365E | Urban | Asset failure | LV | 1 | 216 | 0.00034531 | 1.6e-06 | No
14/12/2018 | 08:54:21 | AP125C | Urban | Asset failure | LV | 1 | 100 | 0.00015987 | 1.6e-06 | No
14/12/2018 | 08:55:05 | SM179D | Urban | Vegetation | Grow-in - NSP responsibility | 3.3333 | 127 | 0.00067677 | 5.33e-06 | No
14/12/2018 | 09:02:43 | PA18 | Rural Long | Planned |  | 94 | 173 | 0.11869 | 0.00068604 | No
14/12/2018 | 09:10:09 | HH409C | Urban | Asset failure | LV | 2.3333 | 314 | 0.0011713 | 3.73e-06 | No
14/12/2018 | 09:11:15 | NL544B | Urban | Asset failure | LV | 27.3333 | 5 | 0.00021849 | 4.37e-05 | No
14/12/2018 | 09:11:27 | MV62 | Rural Short | Planned |  | 17 | 152 | 0.019251 | 0.00012665 | No
14/12/2018 | 09:15:13 | HH386B / HH386C | Urban | Planned |  | 94 | 134.6277 | 0.020231 | 0.00015028 | No
14/12/2018 | 09:21:30 | MG46 | Rural Short | Other |  | 1 | 105 | 0.00078226 | 7.45e-06 | No
14/12/2018 | 09:26:34 | ST14 | Rural Short | Planned |  | 21 | 295 | 0.046154 | 0.00015645 | No
14/12/2018 | 09:44:28 | VH23 | Rural Short | Asset failure | LV | 4.6667 | 51 | 0.0017731 | 3.477e-05 | No
14/12/2018 | 09:48:51 | VH23 | Rural Short | Asset failure | LV | 1 | 95 | 0.00070776 | 7.45e-06 | No
14/12/2018 | 09:53:44 | GA800A | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 349 | 0.0026001 | 7.45e-06 | No
14/12/2018 | 09:55:36 | AP344D | Urban | Planned |  | 49 | 341 | 0.026712 | 7.834e-05 | No
14/12/2018 | 09:55:41 | EL01Q | Urban | Planned |  | 23 | 173 | 0.0063611 | 3.677e-05 | No
14/12/2018 | 10:03:49 | SA17 | Urban | Asset failure | LV | 1 | 159 | 0.00025419 | 1.6e-06 | No
14/12/2018 | 10:21:50 | NL115F | Urban | Asset failure | LV | 1 | 71 | 0.00011351 | 1.6e-06 | No
14/12/2018 | 10:28:57 | MV52 | Rural Short | Planned |  | 21 | 5 | 0.00078227 | 0.00015645 | No
14/12/2018 | 10:31:56 | AP149E | Urban | Planned |  | 88 | 13 | 0.0018289 | 0.00014068 | No
14/12/2018 | 10:47:59 | VH33 | Rural Short | Asset failure | LV | 1 | 264 | 0.0019668 | 7.45e-06 | No
14/12/2018 | 10:50:17 | AP529D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 48 | 0.0015347 | 3.197e-05 | No
14/12/2018 | 10:52:05 | CL13 | Rural Long | Unknown | Unknown | 2 | 61 | 0.0008904 | 1.46e-05 | No
14/12/2018 | 10:56:31 | VH32 | Rural Short | Unknown | Unknown | 21.3333 | 14 | 0.0022251 | 0.00015894 | No
14/12/2018 | 11:04:03 | AP365A | Urban | Asset failure | LV | 22.6666 | 89 | 0.0032251 | 3.624e-05 | No
14/12/2018 | 11:32:29 | BM43 | Rural Short | Weather |  | 51 | 5 | 0.0018998 | 0.00037996 | No
14/12/2018 | 11:58:29 | LX41 | Rural Short | Asset failure | LV | 1 | 200 | 0.00149 | 7.45e-06 | No
14/12/2018 | 12:54:29 | W06 | Rural Long | Weather |  | 313 | 320 | 0.731 | 0.0022844 | No
14/12/2018 | 13:23:05 | PP16 | Rural Short | Asset failure | LV | 2 | 116 | 0.0017284 | 1.49e-05 | No
14/12/2018 | 13:24:53 | VH72 | Rural Short | Unknown | Unknown | 13.6667 | 23 | 0.0023418 | 0.00010182 | No
14/12/2018 | 13:30:27 | AP149B | Urban | Planned |  | 57 | 1 | 9.112e-05 | 9.112e-05 | No
14/12/2018 | 13:48:16 | KI57 | Rural Short | Asset failure | HV | 165 | 86 | 0.10572 | 0.0012293 | No
14/12/2018 | 13:54:09 | AP149E | Urban | Asset failure | LV | 10 | 364 | 0.0058192 | 1.599e-05 | No
14/12/2018 | 14:13:35 | AP344D | Urban | Planned |  | 4 | 39 | 0.00024939 | 6.39e-06 | No
14/12/2018 | 14:36:42 | HH121A | Urban | Asset failure | LV | 21.3333 | 16 | 0.00054568 | 3.411e-05 | No
14/12/2018 | 15:02:53 | GA800A | Rural Short | Vegetation | Grow-in - NSP responsibility | 3.3333 | 47 | 0.0011672 | 2.483e-05 | No
14/12/2018 | 16:24:22 | PL12 | Rural Long | Unknown | Unknown | 1 | 41 | 0.00029923 | 7.3e-06 | No
14/12/2018 | 16:30:01 | HH341G | Urban | Asset failure | LV | 1 | 340 | 0.00054355 | 1.6e-06 | No
14/12/2018 | 16:32:46 | EL25 | Urban | Asset failure | LV | 55 | 110 | 0.009672 | 8.793e-05 | No
14/12/2018 | 16:35:26 | MG17 | Rural Long | Asset failure | HV | 7 | 74 | 0.0037805 | 5.109e-05 | No
14/12/2018 | 16:35:36 | MG37 | Rural Long | Unknown | Unknown | 1 | 9 | 6.569e-05 | 7.3e-06 | No
14/12/2018 | 16:42:57 | SB03 | Rural Long | Weather |  | 3 | 1634 | 0.035776 | 2.19e-05 | No
14/12/2018 | 17:43:34 | W31 | Rural Short | Unknown | Unknown | 30 | 201.7333 | 0.045088 | 0.0002235 | No
14/12/2018 | 17:50:52 | BM13 | Rural Short | Animal | Animal impact | 2 | 245 | 0.0036506 | 1.49e-05 | No
14/12/2018 | 18:17:41 | MG32 | Rural Long | Unknown | Unknown | 1 | 135 | 0.00098528 | 7.3e-06 | No
14/12/2018 | 18:17:41 | MG32 | Rural Long | Unknown | Unknown | 8.3333 | 82 | 0.0049872 | 6.082e-05 | No
14/12/2018 | 18:31:37 | SA16 | Urban | Asset failure | LV | 1 | 283 | 0.00045243 | 1.6e-06 | No
14/12/2018 | 18:44:43 | CBD103C | Urban | Vegetation | Grow-in - NSP responsibility | 27.3333 | 66 | 0.002884 | 4.37e-05 | No
14/12/2018 | 19:00:48 | SD34200 | Rural Short | Animal | Animal impact | 325.6668 | 189 | 0.45856 | 0.0024263 | No
14/12/2018 | 19:46:56 | SM410C | Urban | Asset failure | LV | 1 | 459 | 0.00073379 | 1.6e-06 | No
14/12/2018 | 20:15:36 | AP372B | Urban | Asset failure | LV | 1 | 194 | 0.00031014 | 1.6e-06 | No
14/12/2018 | 20:52:32 | W29 | Rural Long | Unknown | Unknown | 12 | 2371 | 0.20765 | 8.758e-05 | No
14/12/2018 | 21:06:43 | AP139C | Urban | Overloads |  | 1 | 274 | 0.00043804 | 1.6e-06 | No
14/12/2018 | 21:20:45 | MG46 | Rural Short | Unknown | Unknown | 2 | 9 | 0.0001341 | 1.49e-05 | No
14/12/2018 | 23:40:14 | SA744D | Urban | Asset failure | LV | 34 | 161 | 0.0087511 | 5.435e-05 | No
15/12/2018 | 00:45:18 | W26 | Rural Long | Asset failure | HV | 94 | 1081.383 | 0.74188 | 0.00068604 | No
15/12/2018 | 02:36:04 | EL260C | Urban | Asset failure | LV | 1 | 92 | 0.00014708 | 1.6e-06 | No
15/12/2018 | 07:23:59 | PA19 | Rural Long | Unknown | Unknown | 2 | 225 | 0.0032842 | 1.46e-05 | No
15/12/2018 | 07:41:17 | ST41 | Rural Long | Asset failure | HV | 3 | 370 | 0.0081011 | 2.19e-05 | No
15/12/2018 | 08:18:07 | MG32 | Rural Long | Unknown | Unknown | 8.3333 | 93 | 0.0056562 | 6.082e-05 | No
15/12/2018 | 08:51:46 | NU35 | Rural Long | Asset failure | HV | 2 | 110 | 0.0016056 | 1.46e-05 | No
15/12/2018 | 09:50:11 | VH23 | Rural Short | Overloads |  | 1 | 106 | 0.00078972 | 7.45e-06 | No
15/12/2018 | 11:15:37 | SM216B | Urban | Asset failure | LV | 117 | 101 | 0.018892 | 0.00018704 | No
15/12/2018 | 11:42:03 | CBD366N | CBD | Planned |  | 14 | 1085 | 2.9487 | 0.0027177 | No
15/12/2018 | 12:27:28 | GA48 | Rural Short | Asset failure | HV | 46 | 269.6957 | 0.092427 | 0.00034271 | No
15/12/2018 | 13:14:57 | VH15 | Rural Short | Asset failure | LV | 1 | 253 | 0.0018849 | 7.45e-06 | No
15/12/2018 | 13:36:38 | MV33 | Rural Short | Unknown | Unknown | 1.6667 | 146 | 0.0018129 | 1.242e-05 | No
15/12/2018 | 14:43:35 | LX71 | Rural Long | Animal | Animal impact | 24 | 202 | 0.035382 | 0.00017516 | No
15/12/2018 | 14:55:35 | MB34 | Rural Long | Asset failure | HV | 70 | 130 | 0.066415 | 0.00051088 | No
15/12/2018 | 14:55:35 | MB34 | Rural Long | Asset failure | HV | 0 | 1 | 0.00051088 | 0 | No
15/12/2018 | 15:26:40 | WK11 | Rural Short | Asset failure | HV | 5 | 102.2 | 0.003807 | 3.725e-05 | No
15/12/2018 | 16:42:43 | SA32 | Urban | Asset failure | LV | 58 | 58 | 0.0053779 | 9.272e-05 | No
15/12/2018 | 17:50:34 | SSD326 | Urban | 5 - STPIS Exclusion (3.3)(a) |  | 1588 | 1 | 0.0025387 | 0.0025387 | No
15/12/2018 | 17:50:34 | SSD326 | Rural Short | 5 - STPIS Exclusion (3.3)(a) |  | 5568 | 1 | 0.041482 | 0.041482 | No
15/12/2018 | 17:50:34 | SSD326 | Rural Long | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 1 | 7.3e-06 | 7.3e-06 | No
15/12/2018 | 20:03:00 | WK11 | Rural Short | Unknown | Unknown | 62 | 64 | 0.029562 | 0.00046191 | No
15/12/2018 | 20:09:41 | MG52 | Rural Short | Unknown | Unknown | 1 | 62 | 0.00046191 | 7.45e-06 | No
15/12/2018 | 20:55:33 | WHY08 | Urban | Unknown | Unknown | 48 | 24 | 0.0018417 | 7.674e-05 | No
15/12/2018 | 21:25:16 | NA52 | Rural Long | Unknown | Unknown | 1 | 27 | 0.00019706 | 7.3e-06 | No
15/12/2018 | 21:43:33 | M11 | Rural Long | Asset failure | LV | 5 | 62 | 0.0022625 | 3.649e-05 | No
15/12/2018 | 21:55:05 | ST22 | Rural Short | Asset failure | Distribution substation | 285 | 83.2877 | 0.17684 | 0.0021233 | No
16/12/2018 | 02:37:07 | MG44 | Urban | Unknown | Unknown | 132 | 56 | 0.011817 | 0.00021103 | No
16/12/2018 | 05:48:29 | PP12 | Rural Long | Weather |  | 16 | 17.9375 | 0.0020946 | 0.00011677 | No
16/12/2018 | 08:13:40 | SD46100 | Rural Long | Planned |  | 608 | 90 | 0.39937 | 0.0044374 | No
16/12/2018 | 08:33:22 | SA744D | Urban | Asset failure | LV | 11.3333 | 123 | 0.0022286 | 1.812e-05 | No
16/12/2018 | 08:59:10 | AP373C | Urban | Unknown | Unknown | 1 | 258 | 0.00041246 | 1.6e-06 | No
16/12/2018 | 09:47:37 | MG06 | Rural Short | Asset failure | LV | 2 | 220 | 0.0032781 | 1.49e-05 | No
16/12/2018 | 09:55:02 | HH177B | Urban | Planned |  | 526 | 247 | 0.2077 | 0.0008409 | No
16/12/2018 | 10:18:01 | HH341B | Urban | Asset failure | LV | 63 | 40 | 0.0040287 | 0.00010072 | No
16/12/2018 | 12:15:43 | SD34200 | Rural Short | Third Party | Vehicle impact | 17 | 160.8235 | 0.020369 | 0.00012665 | No
16/12/2018 | 13:41:42 | M21 | Rural Long | Unknown | Unknown | 1 | 433 | 0.0031602 | 7.3e-06 | No
16/12/2018 | 16:43:36 | EL13 | Urban | Asset failure | LV | 1 | 223 | 0.0003565 | 1.6e-06 | No
16/12/2018 | 18:51:18 | HH403A | Urban | Asset failure | LV | 1 | 181 | 0.00028936 | 1.6e-06 | No
16/12/2018 | 19:27:18 | CD03 | Rural Short | Asset failure | HV | 744 | 408.2003 | 2.2626 | 0.0055429 | No
16/12/2018 | 19:27:18 | CD03 | Rural Short | Asset failure | HV | 0 | 96.5 | 0.0071894 | 0 | No
16/12/2018 | 21:45:29 | AP373A | Urban | Planned |  | 6 | 489 | 0.0046905 | 9.59e-06 | No
16/12/2018 | 23:00:43 | SD54300 | Rural Long | Planned |  | 1790 | 187 | 2.443 | 0.013064 | No
17/12/2018 | 05:56:24 | NL210E | Urban | Unknown | Unknown | 767.667 | 1.0495 | 0.001288 | 0.0012273 | No
17/12/2018 | 07:07:40 | NL511C | Urban | Asset failure | LV | 1 | 156 | 0.00024939 | 1.6e-06 | No
17/12/2018 | 07:33:41 | VH31 | Rural Short | Unknown | Unknown | 808 | 203 | 1.222 | 0.0060197 | No
17/12/2018 | 08:02:16 | ST44 | Rural Long | Planned |  | 41 | 429 | 0.12837 | 0.00029923 | No
17/12/2018 | 08:55:41 | EL09 | Urban | Planned |  | 344 | 82 | 0.045095 | 0.00054994 | No
17/12/2018 | 08:55:41 | EL09 | Urban | Planned |  | 0 | 18.0233 | 0.0099118 | 0 | No
17/12/2018 | 08:58:24 | SG12 | Rural Short | Unknown | Unknown | 106.3334 | 11 | 0.0087142 | 0.0007922 | No
17/12/2018 | 09:00:35 | MV63 | Rural Short | Planned |  | 3 | 261 | 0.0058335 | 2.235e-05 | No
17/12/2018 | 09:02:44 | LX41 | Rural Short | Planned |  | 7 | 285 | 0.014863 | 5.215e-05 | No
17/12/2018 | 09:10:27 | SG10 | Rural Short | Planned |  | 232 | 347 | 0.59977 | 0.0017284 | No
17/12/2018 | 09:16:23 | SM349C | Urban | Planned |  | 162 | 299 | 0.077437 | 0.00025899 | No
17/12/2018 | 09:16:56 | WHY02 | Urban | Planned |  | 5 | 174 | 0.0013908 | 7.99e-06 | No
17/12/2018 | 09:49:24 | HH121F | Urban | Planned |  | 61 | 210 | 0.020479 | 9.752e-05 | No
17/12/2018 | 10:01:11 | HH121E | Urban | Planned |  | 55 | 111 | 0.0097599 | 8.793e-05 | No
17/12/2018 | 10:10:07 | BT14 | Rural Long | Planned |  | 8 | 326 | 0.019034 | 5.839e-05 | No
17/12/2018 | 10:51:06 | CL26 | Rural Long | Third Party | Other | 2 | 177 | 0.0025836 | 1.46e-05 | No
17/12/2018 | 11:18:47 | LM53 | Rural Long | Planned |  | 65 | 110 | 0.052183 | 0.00047439 | No
17/12/2018 | 11:34:33 | YK15 | Rural Long | Planned |  | 2 | 11 | 0.00016056 | 1.46e-05 | No
17/12/2018 | 11:35:25 | MG19 | Rural Long | Unknown | Unknown | 112 | 2 | 0.0016348 | 0.00081741 | No
17/12/2018 | 11:55:58 | SM349F | Urban | Asset failure | LV | 111 | 72 | 0.012777 | 0.00017745 | No
17/12/2018 | 11:59:04 | AP365E | Urban | Overloads |  | 1 | 179 | 0.00028616 | 1.6e-06 | No
17/12/2018 | 12:28:04 | W31 | Rural Short | Weather |  | 30 | 238.4 | 0.053283 | 0.0002235 | No
17/12/2018 | 14:02:34 | HH386C | Urban | Asset failure | LV | 1 | 258 | 0.00041246 | 1.6e-06 | No
17/12/2018 | 15:11:45 | MB22 | Rural Short | Asset failure | LV | 1 | 50 | 0.00037251 | 7.45e-06 | No
17/12/2018 | 16:27:09 | SA17 | Urban | Asset failure | LV | 1 | 129 | 0.00020623 | 1.6e-06 | No
17/12/2018 | 18:15:39 | HH145B | Urban | Planned |  | 788 | 1 | 0.0012598 | 0.0012598 | No
17/12/2018 | 19:29:23 | SM410C | Urban | Asset failure | LV | 12 | 117 | 0.0022445 | 1.918e-05 | No
17/12/2018 | 20:01:31 | AP149E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2021 | 46 | 0.14862 | 0.0032309 | No
17/12/2018 | 20:29:11 | SA20 | Urban | Asset failure | LV | 55 | 77 | 0.0067704 | 8.793e-05 | No
17/12/2018 | 20:37:47 | SA14 | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
17/12/2018 | 20:58:03 | CV01 | Rural Short | Unknown | Unknown | 34 | 143 | 0.036223 | 0.00025331 | No
17/12/2018 | 21:02:22 | HH386G | Urban | Asset failure | LV | 21 | 24 | 0.00080573 | 3.357e-05 | No
17/12/2018 | 21:13:51 | AP355H | Urban | Planned |  | 1 | 42 | 6.714e-05 | 1.6e-06 | No
17/12/2018 | 21:14:42 | AP149E | Urban | Asset failure | LV | 19.3333 | 49 | 0.0015145 | 3.091e-05 | No
17/12/2018 | 21:24:20 | AP355H | Urban | Planned |  | 110 | 441 | 0.077552 | 0.00017585 | No
17/12/2018 | 21:33:47 | SM410C | Urban | Asset failure | LV | 12 | 95 | 0.0018225 | 1.918e-05 | No
17/12/2018 | 22:20:43 | AP149E | Urban | Asset failure | LV | 19.3333 | 74 | 0.0022872 | 3.091e-05 | No
18/12/2018 | 03:44:53 | GU32 | Rural Long | Unknown | Unknown | 5 | 254 | 0.0092689 | 3.649e-05 | No
18/12/2018 | 05:29:42 | HH403A | Urban | Overloads |  | 1 | 407 | 0.00065066 | 1.6e-06 | No
18/12/2018 | 05:51:48 | HH522B | Urban | Asset failure | LV | 1 | 239 | 0.00038208 | 1.6e-06 | No
18/12/2018 | 06:14:16 | MG46 | Rural Short | Other |  | 1 | 559 | 0.0041646 | 7.45e-06 | No
18/12/2018 | 06:28:23 | VH32 | Rural Short | Asset failure | HV | 2 | 219 | 0.0032632 | 1.49e-05 | No
18/12/2018 | 08:24:23 | NL21 | Urban | Planned |  | 127 | 422 | 0.085679 | 0.00020303 | No
18/12/2018 | 08:26:54 | NA13 | Rural Long | Planned |  | 7 | 258 | 0.013181 | 5.109e-05 | No
18/12/2018 | 08:34:59 | MV14 | Rural Short | Planned |  | 84 | 332.6786 | 0.20819 | 0.00062581 | No
18/12/2018 | 08:37:44 | NL234B | Urban | Asset failure | LV | 1 | 240 | 0.00038368 | 1.6e-06 | No
18/12/2018 | 08:37:49 | PP18 | Rural Long | Planned |  | 48 | 378 | 0.13242 | 0.00035032 | No
18/12/2018 | 08:47:49 | GA800A | Rural Short | Planned |  | 328 | 271.8384 | 0.66428 | 0.0024436 | No
18/12/2018 | 08:55:55 | MV64 | Urban | Planned |  | 361 | 370 | 0.21354 | 0.00057712 | No
18/12/2018 | 09:01:19 | BM54 | Rural Short | Planned |  | 38 | 204 | 0.057754 | 0.00028311 | No
18/12/2018 | 09:02:26 | CD03 | Rural Short | Unknown | Unknown | 5 | 420.6 | 0.015668 | 3.725e-05 | No
18/12/2018 | 09:06:13 | PA14 | Rural Long | Planned |  | 69 | 13 | 0.0065466 | 0.00050359 | No
18/12/2018 | 09:09:57 | MTB13 | Rural Short | Planned |  | 9 | 314 | 0.021054 | 6.705e-05 | No
18/12/2018 | 09:14:00 | MTB41 | Rural Short | Planned |  | 31 | 333 | 0.076908 | 0.00023095 | No
18/12/2018 | 09:16:29 | SA31 | Urban | Planned |  | 731 | 19.9466 | 0.02331 | 0.0011686 | No
18/12/2018 | 09:16:29 | SA31 | Urban | Planned |  | 0 | 20.4419 | 0.023889 | 0 | No
18/12/2018 | 09:28:57 | VH23 | Rural Short | Planned |  | 12 | 294 | 0.026284 | 8.94e-05 | No
18/12/2018 | 09:36:13 | NL111C | Urban | Asset failure | LV | 13 | 164 | 0.0034084 | 2.078e-05 | No
18/12/2018 | 09:50:02 | CBD412M | Urban | Animal | Animal nesting/burrowing, etc and other | 2 | 313 | 0.0010008 | 3.2e-06 | No
18/12/2018 | 09:51:42 | NU03 | Rural Long | Third Party | Other | 53 | 64 | 0.024756 | 0.00038681 | No
18/12/2018 | 09:54:42 | MV11 | Rural Short | Unknown | Unknown | 559.6669 | 1 | 0.0041696 | 0.0041696 | No
18/12/2018 | 10:07:27 | WHY10 | Urban | Planned |  | 115 | 182 | 0.03346 | 0.00018385 | No
18/12/2018 | 10:09:01 | VH15 | Rural Short | Planned |  | 5 | 293 | 0.010914 | 3.725e-05 | No
18/12/2018 | 10:25:39 | W24 | Rural Long | Planned |  | 27 | 241 | 0.04749 | 0.00019706 | No
18/12/2018 | 10:34:14 | PA22 | Rural Long | Planned |  | 31 | 101 | 0.022851 | 0.00022625 | No
18/12/2018 | 10:40:37 | GA01 | Urban | Planned |  | 190 | 81 | 0.024604 | 0.00030375 | No
18/12/2018 | 11:06:57 | EL16 | Urban | Planned |  | 1 | 1303 | 0.0020831 | 1.6e-06 | No
18/12/2018 | 11:08:54 | HH177E | Urban | Planned |  | 69 | 87 | 0.0095969 | 0.00011031 | No
18/12/2018 | 11:46:47 | VH11 | Urban | Asset failure | LV | 1 | 226 | 0.0003613 | 1.6e-06 | No
18/12/2018 | 12:08:17 | ME427D | Urban | Unknown | Unknown | 1012 | 103.0751 | 0.16676 | 0.0016179 | No
18/12/2018 | 12:26:44 | HH409C | Urban | Asset failure | LV | 86 | 72 | 0.009899 | 0.00013749 | No
18/12/2018 | 14:58:17 | AP214D | Urban | Asset failure | LV | 1 | 142 | 0.00022701 | 1.6e-06 | No
18/12/2018 | 15:22:49 | PL07 | Urban | Asset failure | LV | 4 | 48 | 0.00030695 | 6.39e-06 | No
18/12/2018 | 16:26:56 | MTB22 | Rural Short | Animal | Animal impact | 26.3333 | 117 | 0.022954 | 0.00019619 | No
18/12/2018 | 16:38:03 | VH12 | Rural Short | Asset failure | LV | 17.6666 | 33 | 0.0043434 | 0.00013162 | No
18/12/2018 | 17:07:13 | EL19 | Urban | Unknown | Unknown | 9 | 48 | 0.00069063 | 1.439e-05 | No
18/12/2018 | 17:25:13 | NL511B | Urban | Asset failure | LV | 50 | 52 | 0.0041566 | 7.993e-05 | No
18/12/2018 | 18:05:49 | HH341D | Urban | Asset failure | LV | 120 | 61 | 0.011702 | 0.00019184 | No
18/12/2018 | 19:36:37 | SM126C | Urban | Unknown | Unknown | 2162 | 14.9158 | 0.051554 | 0.0034563 | No
18/12/2018 | 20:18:12 | SM137A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 6.3333 | 194 | 0.0019642 | 1.012e-05 | No
18/12/2018 | 20:25:32 | AP373B | Urban | Third Party | Vehicle impact | 24 | 486 | 0.018647 | 3.837e-05 | No
19/12/2018 | 00:29:47 | HH409E | Urban | Asset failure | LV | 80 | 188 | 0.024044 | 0.00012789 | No
19/12/2018 | 01:34:04 | CV15 | Rural Long | Weather |  | 59 | 542.5254 | 0.23361 | 0.0004306 | No
19/12/2018 | 01:52:00 | PL33 | Rural Long | Asset failure | HV | 1091 | 67.3914 | 0.5366 | 0.0079625 | No
19/12/2018 | 02:32:52 | PL04 | Urban | Unknown | Unknown | 2 | 398 | 0.0012725 | 3.2e-06 | No
19/12/2018 | 02:45:43 | PL33 | Rural Long | Weather |  | 19 | 811 | 0.11246 | 0.00013867 | No
19/12/2018 | 03:27:47 | PL01 | Urban | Weather |  | 34 | 277 | 0.015056 | 5.435e-05 | No
19/12/2018 | 04:43:38 | HH121G | Urban | Unknown | Unknown | 33.6666 | 215 | 0.011572 | 5.382e-05 | No
19/12/2018 | 04:52:00 | EL260C | Urban | Asset failure | LV | 12.3333 | 194 | 0.0038251 | 1.972e-05 | No
19/12/2018 | 05:22:18 | NL210C | Urban | Asset failure | LV | 60 | 394 | 0.037793 | 9.592e-05 | No
19/12/2018 | 05:47:53 | SM350H | Urban | Vegetation | Grow-in - NSP responsibility | 21 | 179 | 0.0060094 | 3.357e-05 | No
19/12/2018 | 06:23:55 | PL34 | Rural Long | Weather |  | 66 | 292.9091 | 0.14109 | 0.00048169 | No
19/12/2018 | 07:05:43 | MTB52 | Rural Long | Weather |  | 68 | 100 | 0.049629 | 0.00049629 | No
19/12/2018 | 07:06:25 | SG04 | Rural Short | Unknown | Unknown | 1 | 104 | 0.00077482 | 7.45e-06 | No
19/12/2018 | 07:20:38 | AP373B | Urban | Vegetation | Grow-in - NSP responsibility | 3.6667 | 148 | 0.00086755 | 5.86e-06 | No
19/12/2018 | 07:20:46 | HH386A | Urban | Unknown | Unknown | 412 | 105.1845 | 0.06928 | 0.00065865 | No
19/12/2018 | 07:45:16 | MTB82 | Rural Short | Weather |  | 32 | 253 | 0.060316 | 0.0002384 | No
19/12/2018 | 07:46:28 | MTB51 | Rural Long | Weather |  | 734.3337 | 138.1044 | 0.74016 | 0.0053594 | No
19/12/2018 | 07:56:31 | AP372F | Urban | Other |  | 19.6666 | 354 | 0.01113 | 3.144e-05 | No
19/12/2018 | 08:08:39 | PP08 | Rural Long | Asset failure | LV | 12.3333 | 232 | 0.020883 | 9.001e-05 | No
19/12/2018 | 08:14:45 | ST43 | Rural Long | Planned |  | 75 | 126 | 0.068969 | 0.00054738 | No
19/12/2018 | 08:15:24 | LM33 | Rural Long | Weather |  | 27 | 466 | 0.091828 | 0.00019706 | No
19/12/2018 | 08:37:20 | AP529E | Urban | Planned |  | 40 | 71 | 0.0045402 | 6.395e-05 | No
19/12/2018 | 08:46:07 | GA01 | Urban | Planned |  | 33 | 185 | 0.0097599 | 5.276e-05 | No
19/12/2018 | 08:47:52 | EL12 | Urban | Planned |  | 1 | 106 | 0.00016946 | 1.6e-06 | No
19/12/2018 | 08:51:27 | PA02 | Urban | Planned |  | 132 | 12 | 0.0025323 | 0.00021103 | No
19/12/2018 | 08:52:42 | HH341G | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 209 | 0.00033412 | 1.6e-06 | No
19/12/2018 | 08:56:16 | HH177C | Urban | Planned |  | 108 | 131 | 0.022618 | 0.00017266 | No
19/12/2018 | 09:00:17 | BM56 | Rural Short | Planned |  | 23 | 203 | 0.034785 | 0.00017135 | No
19/12/2018 | 09:01:59 | GA22 | Rural Short | Planned |  | 27 | 137 | 0.027558 | 0.00020115 | No
19/12/2018 | 09:07:19 | SM349E | Urban | Asset failure | LV | 1 | 341 | 0.00054515 | 1.6e-06 | No
19/12/2018 | 09:17:56 | SM350H | Urban | Unknown | Unknown | 21 | 95 | 0.0031894 | 3.357e-05 | No
19/12/2018 | 09:20:33 | CM24 | Rural Long | Weather |  | 5 | 602 | 0.021968 | 3.649e-05 | No
19/12/2018 | 09:33:43 | HH386G | Urban | Unknown | Unknown | 24.6666 | 137 | 0.0054024 | 3.943e-05 | No
19/12/2018 | 09:49:27 | AP529C | Urban | Planned |  | 1 | 265 | 0.00042365 | 1.6e-06 | No
19/12/2018 | 10:00:10 | LC02 | Rural Long | Unknown | Unknown | 1 | 354 | 0.0025836 | 7.3e-06 | No
19/12/2018 | 10:36:13 | BT04 | Rural Long | Asset failure | LV | 1 | 262 | 0.0019122 | 7.3e-06 | No
19/12/2018 | 10:37:43 | MV53 | Rural Short | Planned |  | 10 | 151 | 0.01125 | 7.45e-05 | No
19/12/2018 | 10:50:03 | SG01 | Rural Short | Weather |  | 3.3333 | 86 | 0.0021357 | 2.483e-05 | No
19/12/2018 | 10:52:33 | CD03 | Rural Short | Planned |  | 1 | 96 | 0.00071521 | 7.45e-06 | No
19/12/2018 | 11:32:23 | MI33 | Rural Long | Planned |  | 50 | 2.9 | 0.0010583 | 0.00036492 | No
19/12/2018 | 11:34:57 | HH428C | Urban | Overloads |  | 33.6666 | 417 | 0.022444 | 5.382e-05 | No
19/12/2018 | 11:36:06 | HH341E | Urban | Asset failure | LV | 29.3333 | 187 | 0.0087693 | 4.689e-05 | No
19/12/2018 | 11:36:22 | EL25 | Urban | Asset failure | LV | 1 | 178 | 0.00028456 | 1.6e-06 | No
19/12/2018 | 12:03:38 | HH341B | Urban | Asset failure | HV | 46 | 357 | 0.026253 | 7.354e-05 | No
19/12/2018 | 12:47:39 | CD03 | Rural Short | Planned |  | 5 | 165 | 0.0061464 | 3.725e-05 | No
19/12/2018 | 12:58:56 | PL25 | Rural Long | Asset failure | HV | 66 | 100.5455 | 0.048432 | 0.00048169 | No
19/12/2018 | 13:03:45 | MTB63 | Rural Short | Weather |  | 2.6667 | 51 | 0.0010132 | 1.987e-05 | No
19/12/2018 | 13:06:38 | SA16 | Urban | Asset failure | LV | 1 | 499 | 0.00079774 | 1.6e-06 | No
19/12/2018 | 13:35:41 | SA32 | Urban | Overloads |  | 1 | 674 | 0.0010775 | 1.6e-06 | No
19/12/2018 | 14:08:00 | HH145A | Urban | Unknown | Unknown | 35 | 465 | 0.026018 | 5.595e-05 | No
19/12/2018 | 14:11:41 | EL11 | Urban | Unknown | Unknown | 3 | 17 | 8.153e-05 | 4.8e-06 | No
19/12/2018 | 14:17:55 | MB62 | Rural Long | Asset failure | LV | 1 | 219 | 0.0015983 | 7.3e-06 | No
19/12/2018 | 14:36:45 | MT18 | Rural Long | Unknown | Unknown | 2 | 31 | 0.0004525 | 1.46e-05 | No
19/12/2018 | 16:36:44 | BM41 | Urban | Asset failure | LV | 1 | 220 | 0.00035171 | 1.6e-06 | No
19/12/2018 | 17:29:25 | HH522A | Urban | Asset failure | LV | 1 | 887 | 0.001418 | 1.6e-06 | No
19/12/2018 | 19:25:04 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 134 | 0.0036418 | 2.718e-05 | No
19/12/2018 | 21:18:23 | AP372A | Urban | Asset failure | LV | 8.3333 | 151 | 0.0020117 | 1.332e-05 | No
19/12/2018 | 22:03:29 | HH386G | Urban | Unknown | Unknown | 24.6666 | 49 | 0.0019323 | 3.943e-05 | No
19/12/2018 | 23:06:15 | HH386G | Urban | Unknown | Unknown | 24.6666 | 79 | 0.0031153 | 3.943e-05 | No
20/12/2018 | 05:15:06 | EL16 | Urban | Third Party | Vehicle impact | 6 | 847 | 0.0081245 | 9.59e-06 | No
20/12/2018 | 05:20:13 | EL16 | Urban | Third Party | Vehicle impact | 4 | 692 | 0.0044251 | 6.39e-06 | No
20/12/2018 | 06:54:41 | M13 | Rural Long | Asset failure | HV | 971 | 119.2101 | 0.8448 | 0.0070867 | No
20/12/2018 | 07:10:24 | GA30 | Rural Long | Weather |  | 272 | 240.1471 | 0.47673 | 0.0019852 | No
20/12/2018 | 08:14:10 | WHY09 | Urban | Planned |  | 51 | 264 | 0.021525 | 8.153e-05 | No
20/12/2018 | 08:32:02 | MG02 | Rural Long | Planned |  | 21 | 60 | 0.0091959 | 0.00015327 | No
20/12/2018 | 09:02:48 | LX41 | Rural Short | Planned |  | 10 | 317 | 0.023617 | 7.45e-05 | No
20/12/2018 | 09:16:47 | AP529C | Urban | Planned |  | 56 | 75 | 0.0067144 | 8.953e-05 | No
20/12/2018 | 09:22:46 | KI32 | Rural Short | Planned |  | 46 | 152 | 0.052091 | 0.00034271 | No
20/12/2018 | 09:32:45 | PA19 | Rural Long | Planned |  | 23 | 267 | 0.044819 | 0.00016786 | No
20/12/2018 | 09:33:57 | SM126A | Urban | Planned |  | 34 | 129 | 0.0070118 | 5.435e-05 | No
20/12/2018 | 09:43:01 | M81 | Rural Long | Planned |  | 16 | 257 | 0.030011 | 0.00011677 | No
20/12/2018 | 10:11:41 | AP226E | Urban | Planned |  | 98 | 134 | 0.020994 | 0.00015667 | No
20/12/2018 | 10:59:15 | NU03 | Rural Long | Asset failure | LV | 2 | 278 | 0.0040579 | 1.46e-05 | No
20/12/2018 | 11:36:04 | SM349C | Urban | Planned |  | 233 | 64 | 0.023839 | 0.00037249 | No
20/12/2018 | 11:56:00 | MI33 | Rural Long | Asset failure | HV | 1 | 122 | 0.0008904 | 7.3e-06 | No
20/12/2018 | 13:16:57 | GA30 | Rural Long | Planned |  | 2 | 5 | 7.298e-05 | 1.46e-05 | No
20/12/2018 | 13:59:17 | SD38200 | Rural Long | Planned |  | 2 | 11 | 0.00016056 | 1.46e-05 | No
20/12/2018 | 14:16:08 | NL210A | Urban | Asset failure | HV | 643 | 9.6407 | 0.0099102 | 0.0010279 | No
20/12/2018 | 15:45:03 | ME231E | Urban | Asset failure | LV | 7 | 172 | 0.0019248 | 1.119e-05 | No
20/12/2018 | 16:39:10 | AP125D | Urban | Asset failure | LV | 16.6667 | 63 | 0.0016786 | 2.664e-05 | No
20/12/2018 | 18:11:32 | HH145E | Urban | Asset failure | LV | 1 | 309 | 0.00049399 | 1.6e-06 | No
20/12/2018 | 19:35:43 | G23 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 178 | 0.0012991 | 7.3e-06 | No
20/12/2018 | 19:59:01 | SA20 | Urban | Asset failure | LV | 122 | 61 | 0.011897 | 0.00019504 | No
20/12/2018 | 21:09:27 | HH403B | Urban | Asset failure | LV | 54 | 59 | 0.0050934 | 8.633e-05 | No
20/12/2018 | 21:09:57 | HH177E | Urban | Asset failure | LV | 61 | 49 | 0.0047784 | 9.752e-05 | No
20/12/2018 | 21:27:46 | CN31 | Rural Long | Weather |  | 15 | 868 | 0.095024 | 0.00010948 | No
21/12/2018 | 08:09:22 | HH403A | Urban | Third Party | Vehicle impact | 263 | 407 | 0.17112 | 0.00042045 | No
21/12/2018 | 08:38:52 | MG10 | Rural Long | Planned |  | 1 | 92 | 0.00067145 | 7.3e-06 | No
21/12/2018 | 08:53:48 | VH10 | Rural Short | Planned |  | 68 | 15 | 0.0075991 | 0.00050661 | No
21/12/2018 | 09:38:05 | HH130B | Urban | Overloads |  | 1 | 188 | 0.00030055 | 1.6e-06 | No
21/12/2018 | 09:55:53 | AP214D | Urban | Planned |  | 54 | 210 | 0.018129 | 8.633e-05 | No
21/12/2018 | 10:45:35 | NA04 | Rural Long | Planned |  | 73 | 10 | 0.0053278 | 0.00053278 | No
21/12/2018 | 10:51:00 | HH118D | Urban | Asset failure | LV | 31 | 259 | 0.012836 | 4.956e-05 | No
21/12/2018 | 12:48:03 | SD35300 | Rural Long | Unknown | Unknown | 1 | 10 | 7.298e-05 | 7.3e-06 | No
21/12/2018 | 14:39:39 | LX73 | Rural Long | Asset failure | HV | 48 | 163.4167 | 0.057248 | 0.00035032 | No
21/12/2018 | 14:56:14 | HH130C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 168 | 0.00026858 | 1.6e-06 | No
21/12/2018 | 15:01:25 | CN51 | Rural Long | Asset failure | LV | 1 | 257 | 0.0018757 | 7.3e-06 | No
21/12/2018 | 15:18:14 | ME427D | Urban | Asset failure | LV | 1 | 292 | 0.00046681 | 1.6e-06 | No
21/12/2018 | 15:51:39 | NL21 | Urban | Asset failure | LV | 1.3333 | 315 | 0.00067144 | 2.13e-06 | No
21/12/2018 | 16:12:21 | CL12 | Rural Long | Third Party | Vehicle impact | 93 | 280.2581 | 0.19022 | 0.00067875 | No
21/12/2018 | 18:46:09 | NU06 | Rural Long | Asset failure | LV | 1 | 221 | 0.0016129 | 7.3e-06 | No
22/12/2018 | 05:50:17 | HH403A | Urban | Asset failure | LV | 24.6666 | 235 | 0.009267 | 3.943e-05 | No
22/12/2018 | 08:21:43 | CBD366Q-GG2-outer | Urban | Animal | Animal impact | 793 | 154.0013 | 0.19523 | 0.0012677 | No
22/12/2018 | 09:01:23 | NL234B | Urban | Overloads |  | 1 | 390 | 0.00062348 | 1.6e-06 | No
22/12/2018 | 12:54:23 | HH341B | Urban | Asset failure | LV | 3.3333 | 411 | 0.0021902 | 5.33e-06 | No
22/12/2018 | 13:00:21 | KI51 | Rural Long | Unknown | Unknown | 2 | 30 | 0.0004379 | 1.46e-05 | No
22/12/2018 | 13:14:55 | VH15 | Rural Short | Asset failure | LV | 1 | 399 | 0.0029726 | 7.45e-06 | No
22/12/2018 | 15:25:25 | ST12 | Rural Short | Planned |  | 958 | 1 | 0.0071372 | 0.0071372 | No
22/12/2018 | 17:25:52 | GU13 | Rural Long | Unknown | Unknown | 6 | 47 | 0.0020581 | 4.379e-05 | No
22/12/2018 | 19:50:04 | GA15 | Rural Short | Overloads |  | 1 | 194 | 0.0014453 | 7.45e-06 | No
23/12/2018 | 08:46:49 | HH496A | Urban | Asset failure | LV | 13 | 165 | 0.0034292 | 2.078e-05 | No
23/12/2018 | 09:44:39 | ME200A | Urban | Unknown | Unknown | 9 | 231 | 0.0033236 | 1.439e-05 | No
23/12/2018 | 11:21:26 | CM10 | Rural Long | Unknown | Unknown | 22 | 39 | 0.006262 | 0.00016056 | No
23/12/2018 | 11:50:00 | MG19 | Rural Long | Asset failure | HV | 112 | 245.1161 | 0.20036 | 0.00081741 | No
23/12/2018 | 12:00:37 | NL234B | Urban | Weather |  | 1 | 479 | 0.00076577 | 1.6e-06 | No
23/12/2018 | 12:45:01 | HH341D | Urban | Asset failure | LV | 25.6666 | 81 | 0.0033236 | 4.103e-05 | No
23/12/2018 | 12:58:27 | MG03 | Rural Short | Asset failure | LV | 1 | 242 | 0.0018029 | 7.45e-06 | No
23/12/2018 | 14:24:27 | HH177G | Urban | Overloads |  | 1 | 133 | 0.00021262 | 1.6e-06 | No
23/12/2018 | 15:38:06 | MTB82 | Rural Short | 5 - STPIS Exclusion (3.3)(a) |  | 1 | 18 | 0.0001341 | 7.45e-06 | No
23/12/2018 | 17:36:45 | ME347C | Urban | Overloads |  | 1 | 259 | 0.00041406 | 1.6e-06 | No
23/12/2018 | 18:11:02 | AP372D | Urban | Asset failure | LV | 31.6666 | 158 | 0.0079987 | 5.062e-05 | No
23/12/2018 | 18:20:31 | HH386F | Urban | Overloads |  | 1 | 207 | 0.00033093 | 1.6e-06 | No
23/12/2018 | 18:48:30 | PA10 | Rural Long | Asset failure | Distribution substation | 380 | 340.1316 | 0.94331 | 0.0027734 | No
23/12/2018 | 18:59:12 | SD37102 | Rural Long | Unknown | Unknown | 88 | 136 | 0.087347 | 0.00064225 | No
23/12/2018 | 23:56:45 | AP424C | Urban | Asset failure | HV | 2159 | 149.8842 | 0.51733 | 0.0034515 | No
24/12/2018 | 01:30:12 | MV53 | Rural Short | Animal | Animal impact | 512 | 50 | 0.19072 | 0.0038145 | No
24/12/2018 | 06:10:05 | MG27 | Rural Long | Unknown | Unknown | 3 | 191 | 0.004182 | 2.19e-05 | No
24/12/2018 | 08:02:10 | MG12 | Rural Long | Unknown | Unknown | 2 | 130 | 0.0018976 | 1.46e-05 | No
24/12/2018 | 08:52:08 | NA18 | Rural Long | Asset failure | HV | 65 | 129.9846 | 0.061664 | 0.00047439 | No
24/12/2018 | 09:48:32 | CL13 | Rural Long | Planned |  | 2 | 46 | 0.00067145 | 1.46e-05 | No
24/12/2018 | 12:29:54 | HH432F | Urban | Unknown | Unknown | 22 | 76 | 0.002673 | 3.517e-05 | No
24/12/2018 | 12:44:34 | SM172A | Urban | Planned |  | 1303 | 1 | 0.0020831 | 0.0020831 | No
24/12/2018 | 13:17:22 | SG07 | Rural Short | Planned |  | 41 | 1 | 0.00030546 | 0.00030546 | No
24/12/2018 | 14:48:02 | GA45 | Rural Short | Planned |  | 88 | 1 | 0.00065561 | 0.00065561 | No
24/12/2018 | 15:40:49 | KA12 | Rural Long | Unknown | Unknown | 1 | 12 | 8.758e-05 | 7.3e-06 | No
24/12/2018 | 15:48:42 | NU05 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 16 | 75 | 0.0089402 | 0.0001192 | No
24/12/2018 | 16:02:53 | GU14 | Rural Long | Overloads |  | 1 | 226 | 0.0016494 | 7.3e-06 | No
24/12/2018 | 16:25:32 | SM349E | Urban | Asset failure | LV | 5 | 115 | 0.00091924 | 7.99e-06 | No
24/12/2018 | 16:56:45 | MT12 | Rural Long | Unknown | Unknown | 21 | 151.6667 | 0.023245 | 0.00015327 | No
24/12/2018 | 17:20:45 | SM216E | Urban | Asset failure | LV | 101 | 292 | 0.047148 | 0.00016147 | No
24/12/2018 | 17:49:38 | NU15 | Rural Long | Unknown | Unknown | 2.6667 | 83 | 0.0016154 | 1.946e-05 | No
24/12/2018 | 18:11:10 | SM349F | Urban | Asset failure | LV | 1 | 273 | 0.00043644 | 1.6e-06 | No
24/12/2018 | 19:57:52 | MV51 | Rural Short | Asset failure | Distribution substation | 119 | 156.4958 | 0.13874 | 0.00088657 | No
24/12/2018 | 21:19:45 | GA22 | Rural Short | Unknown | Unknown | 5.3333 | 105 | 0.0041721 | 3.973e-05 | No
25/12/2018 | 05:31:00 | VH23 | Rural Short | Asset failure | HV | 877 | 3 | 0.019601 | 0.0065338 | No
25/12/2018 | 10:08:13 | MG06 | Rural Short | Asset failure | HV | 41 | 24 | 0.007331 | 0.00030546 | No
25/12/2018 | 10:30:47 | PA13 | Rural Long | Other |  | 1 | 115 | 0.00083931 | 7.3e-06 | No
25/12/2018 | 12:33:22 | SD54300 | Rural Long | Asset failure | Subtransmission | 1 | 84 | 0.00061306 | 7.3e-06 | No
25/12/2018 | 12:33:29 | SD54300 | Rural Long | Unknown | Unknown | 2.6667 | 81 | 0.0015764 | 1.946e-05 | No
25/12/2018 | 12:52:16 | AP227D | Urban | Asset failure | LV | 1 | 230 | 0.0003677 | 1.6e-06 | No
25/12/2018 | 13:10:42 | GU34 | Rural Long | Unknown | Unknown | 2 | 72 | 0.001051 | 1.46e-05 | No
25/12/2018 | 17:45:08 | MI01 | Rural Long | Asset failure | LV | 19.6666 | 97 | 0.013923 | 0.00014353 | No
25/12/2018 | 18:40:34 | GA44 | Rural Short | Asset failure | LV | 2 | 364 | 0.0054237 | 1.49e-05 | No
25/12/2018 | 19:30:48 | EL07 | Urban | Asset failure | LV | 1 | 218 | 0.00034851 | 1.6e-06 | No
25/12/2018 | 20:18:23 | SA11 | Urban | Overloads |  | 12 | 126 | 0.0024172 | 1.918e-05 | No
25/12/2018 | 23:03:57 | SM411E | Urban | Unknown | Unknown | 135 | 62 | 0.013381 | 0.00021582 | No
25/12/2018 | 23:49:42 | HH428C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 66 | 472 | 0.049802 | 0.00010551 | No
26/12/2018 | 00:19:11 | SA11 | Urban | Asset failure | LV | 1 | 167 | 0.00026698 | 1.6e-06 | No
26/12/2018 | 01:12:14 | BM56 | Rural Short | Unknown | Unknown | 14 | 7 | 0.00073011 | 0.0001043 | No
26/12/2018 | 04:07:48 | MTB13 | Rural Short | Unknown | Unknown | 26.3333 | 6 | 0.0011771 | 0.00019619 | No
26/12/2018 | 07:50:36 | MB72 | Rural Long | Unknown | Unknown | 2 | 79 | 0.0011531 | 1.46e-05 | No
26/12/2018 | 10:20:00 | WK31 | Rural Short | Asset failure | HV | 38 | 174 | 0.04926 | 0.00028311 | No
26/12/2018 | 10:26:51 | WHY03 | Urban | Asset failure | LV | 1 | 463 | 0.00074019 | 1.6e-06 | No
26/12/2018 | 10:51:55 | HH177D | Urban | Asset failure | HV | 1078 | 153.192 | 0.26401 | 0.0017234 | No
26/12/2018 | 17:19:33 | HH121C | Urban | Overloads |  | 1 | 170 | 0.00027177 | 1.6e-06 | No
26/12/2018 | 18:07:22 | HH107C | Urban | Asset failure | LV | 38.6666 | 161 | 0.0099523 | 6.182e-05 | No
26/12/2018 | 18:33:47 | SA520D | Urban | Asset failure | LV | 1 | 186 | 0.00029735 | 1.6e-06 | No
26/12/2018 | 19:37:00 | NL111P | Urban | Asset failure | LV | 26.6666 | 95 | 0.00405 | 4.263e-05 | No
26/12/2018 | 21:44:42 | SA520D | Urban | Overloads |  | 1 | 4 | 6.39e-06 | 1.6e-06 | No
26/12/2018 | 22:55:00 | VH18 | Rural Short | Unknown | Unknown | 27 | 228 | 0.045863 | 0.00020115 | No
26/12/2018 | 22:55:00 | VH18 | Rural Short | Unknown | Unknown | 52 | 5 | 0.001937 | 0.00038741 | No
27/12/2018 | 00:57:03 | SM126B | Urban | Animal | Animal impact | 498 | 168.9237 | 0.13449 | 0.00079614 | No
27/12/2018 | 01:25:26 | CD01 | Rural Short | Asset failure | LV | 1 | 461 | 0.0034345 | 7.45e-06 | No
27/12/2018 | 06:05:08 | SSD153 | Rural Short | Planned |  | 2400 | 474 | 8.4753 | 0.01788 | No
27/12/2018 | 06:05:08 | SSD153 | Rural Long | Planned |  | 6188 | 474 | 21.4068 | 0.045162 | No
27/12/2018 | 06:26:53 | GA50 | Urban | Asset failure | HV | 1221 | 219.5135 | 0.42849 | 0.001952 | No
27/12/2018 | 08:23:33 | EL01E | Urban | Planned |  | 3 | 384 | 0.0018417 | 4.8e-06 | No
27/12/2018 | 08:36:25 | MG09 | Rural Short | Planned |  | 1 | 90 | 0.00067051 | 7.45e-06 | No
27/12/2018 | 09:04:21 | CM02 | Rural Long | Asset failure | LV | 2 | 133 | 0.0019414 | 1.46e-05 | No
27/12/2018 | 09:04:52 | VH43 | Rural Short | Third Party | Other | 1 | 25 | 0.00018625 | 7.45e-06 | No
27/12/2018 | 09:10:38 | HH341K | Urban | Vegetation | Grow-in - NSP responsibility | 15.6667 | 44 | 0.001102 | 2.505e-05 | No
27/12/2018 | 09:14:35 | VH22 | Rural Short | Asset failure | LV | 1 | 153 | 0.0011399 | 7.45e-06 | No
27/12/2018 | 09:24:08 | WHY04 | Urban | Asset failure | LV | 1 | 50 | 7.993e-05 | 1.6e-06 | No
27/12/2018 | 10:27:48 | AP139D | Urban | Asset failure | LV | 1 | 84 | 0.00013429 | 1.6e-06 | No
27/12/2018 | 11:45:41 | EL03 | Urban | Asset failure | LV | 46 | 31 | 0.0022797 | 7.354e-05 | No
27/12/2018 | 12:01:04 | SSD167 | Rural Short | Asset failure | Zone substation | 855 | 106.9591 | 0.68132 | 0.0063699 | No
27/12/2018 | 12:13:05 | CL23 | Rural Long | Asset failure | LV | 1 | 162 | 0.0011823 | 7.3e-06 | No
27/12/2018 | 13:16:47 | AP344F | Urban | Asset failure | LV | 1 | 210 | 0.00033572 | 1.6e-06 | No
27/12/2018 | 14:34:39 | EL19 | Urban | Unknown | Unknown | 1 | 12 | 1.918e-05 | 1.6e-06 | No
27/12/2018 | 14:50:15 | HH130C | Urban | Vegetation | Grow-in - NSP responsibility | 1530 | 2.2275 | 0.0054483 | 0.002446 | No
27/12/2018 | 14:57:15 | WK41 | Rural Short | Overloads |  | 1 | 228 | 0.0016986 | 7.45e-06 | No
27/12/2018 | 15:22:06 | HH428D | Urban | Unknown | Unknown | 30.6666 | 90 | 0.0044123 | 4.903e-05 | No
27/12/2018 | 17:20:53 | BM21 | Rural Short | Asset failure | LV | 1 | 303 | 0.0022574 | 7.45e-06 | No
27/12/2018 | 17:41:31 | SM350F | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 95 | 0.00015187 | 1.6e-06 | No
27/12/2018 | 17:50:20 | HH496F | Urban | Asset failure | LV | 15.3333 | 421 | 0.01032 | 2.451e-05 | No
27/12/2018 | 17:50:35 | PP09 | Rural Long | Unknown | Unknown | 32.6667 | 107 | 0.02551 | 0.00023841 | No
27/12/2018 | 17:51:40 | AP139B | Urban | Asset failure | LV | 71 | 110 | 0.012486 | 0.00011351 | No
27/12/2018 | 18:03:47 | KA03 | Rural Long | Weather |  | 15.3333 | 240 | 0.026858 | 0.00011191 | No
27/12/2018 | 18:21:57 | PA07 | Rural Long | Asset failure | LV | 1 | 201 | 0.001467 | 7.3e-06 | No
27/12/2018 | 19:28:54 | HH428B | Urban | Asset failure | LV | 33.6666 | 129 | 0.006943 | 5.382e-05 | No
27/12/2018 | 19:49:20 | WK65 | Rural Short | Unknown | Unknown | 4 | 3 | 8.94e-05 | 2.98e-05 | No
27/12/2018 | 20:39:09 | NL210C | Urban | Asset failure | LV | 20 | 87 | 0.0027817 | 3.197e-05 | No
27/12/2018 | 23:13:13 | HH102C | Urban | Asset failure | LV | 1 | 248 | 0.00039647 | 1.6e-06 | No
28/12/2018 | 01:40:47 | HH145A | Urban | Planned |  | 44 | 75 | 0.0052756 | 7.034e-05 | No
28/12/2018 | 02:08:34 | SG12 | Rural Short | Overloads |  | 5.6667 | 520 | 0.021953 | 4.222e-05 | No
28/12/2018 | 04:44:57 | HH121D | Urban | Overloads |  | 1 | 254 | 0.00040606 | 1.6e-06 | No
28/12/2018 | 06:01:33 | AP214C | Urban | Overloads |  | 1 | 260 | 0.00041566 | 1.6e-06 | No
28/12/2018 | 06:36:23 | MTB11 | Rural Short | Animal | Animal impact | 3 | 97 | 0.002168 | 2.235e-05 | No
28/12/2018 | 07:31:53 | SM410D | Urban | Unknown | Unknown | 1 | 102 | 0.00016306 | 1.6e-06 | No
28/12/2018 | 08:19:39 | CM10 | Rural Long | Asset failure | HV | 22 | 263.8636 | 0.042367 | 0.00016056 | No
28/12/2018 | 08:20:21 | BM13 | Rural Short | Planned |  | 27 | 15 | 0.0030173 | 0.00020115 | No
28/12/2018 | 09:03:24 | MV14 | Rural Short | Asset failure | LV | 1 | 194 | 0.0014453 | 7.45e-06 | No
28/12/2018 | 09:03:27 | HH522C | Urban | Planned |  | 72 | 15 | 0.0017266 | 0.0001151 | No
28/12/2018 | 10:28:50 | NU31 | Rural Long | Asset failure | LV | 1 | 155 | 0.0011312 | 7.3e-06 | No
28/12/2018 | 11:15:20 | HH496A | Urban | Asset failure | LV | 1 | 55 | 8.793e-05 | 1.6e-06 | No
28/12/2018 | 11:57:44 | AP424C | Urban | Asset failure | LV | 1 | 96 | 0.00015347 | 1.6e-06 | No
28/12/2018 | 13:08:36 | HH177F | Urban | Unknown | Unknown | 8 | 89 | 0.0011383 | 1.279e-05 | No
28/12/2018 | 13:12:10 | KA31 | Rural Long | Asset failure | LV | 1 | 158 | 0.0011531 | 7.3e-06 | No
28/12/2018 | 15:04:26 | LX42 | Rural Short | Weather |  | 2 | 4275 | 0.063699 | 1.49e-05 | No
28/12/2018 | 16:03:31 | G13 | Rural Long | Asset failure | HV | 13 | 272 | 0.025807 | 9.488e-05 | No
28/12/2018 | 16:10:30 | BT02 | Rural Long | Unknown | Unknown | 2 | 471 | 0.006875 | 1.46e-05 | No
28/12/2018 | 16:15:23 | SM349C | Urban | Asset failure | HV | 108.0001 | 151 | 0.026071 | 0.00017266 | No
28/12/2018 | 16:54:07 | HH177E | Urban | Overloads |  | 1 | 78 | 0.0001247 | 1.6e-06 | No
28/12/2018 | 17:52:20 | NL21 | Urban | Vegetation | Grow-in - NSP responsibility | 2.6667 | 130 | 0.00055421 | 4.26e-06 | No
28/12/2018 | 17:54:22 | SA11 | Urban | Asset failure | LV | 1 | 183 | 0.00029256 | 1.6e-06 | No
28/12/2018 | 18:33:52 | EL07 | Urban | Asset failure | LV | 1 | 189 | 0.00030215 | 1.6e-06 | No
28/12/2018 | 19:09:32 | SM350H | Urban | Asset failure | LV | 1 | 424 | 0.00067784 | 1.6e-06 | No
28/12/2018 | 19:26:35 | HH121D | Urban | Asset failure | LV | 1 | 319 | 0.00050998 | 1.6e-06 | No
28/12/2018 | 20:50:26 | PA19 | Rural Long | Unknown | Unknown | 2 | 780 | 0.011385 | 1.46e-05 | No
28/12/2018 | 21:35:06 | ME347A | Urban | Overloads |  | 1 | 374 | 0.0005979 | 1.6e-06 | No
28/12/2018 | 22:30:34 | CV26 | Rural Long | Weather |  | 41 | 720.4878 | 0.21559 | 0.00029923 | No
28/12/2018 | 23:58:21 | ME131C | Urban | Network business | Switching and protection error | 17.6666 | 145 | 0.0040953 | 2.824e-05 | No
29/12/2018 | 00:31:35 | MG34 | Rural Long | Weather |  | 212.6667 | 134.3574 | 0.20854 | 0.0015521 | No
29/12/2018 | 02:31:25 | MV64 | Urban | Asset failure | LV | 14.3333 | 372 | 0.0085241 | 2.291e-05 | No
29/12/2018 | 03:35:54 | KI16 | Rural Long | Unknown | Unknown | 109 | 428.5688 | 0.34093 | 0.00079552 | No
29/12/2018 | 04:11:36 | MTB53 | Rural Long | Unknown | Unknown | 231 | 225 | 0.37933 | 0.0016859 | No
29/12/2018 | 04:44:58 | HH341B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 37 | 121 | 0.0071573 | 5.915e-05 | No
29/12/2018 | 07:01:41 | HH102C | Urban | Asset failure | LV | 52 | 278 | 0.02311 | 8.313e-05 | No
29/12/2018 | 08:31:22 | VH21 | Rural Short | Asset failure | LV | 1 | 124 | 0.00092382 | 7.45e-06 | No
29/12/2018 | 08:53:15 | M13 | Rural Long | Animal | Animal impact | 971 | 102 | 0.72284 | 0.0070867 | No
29/12/2018 | 09:06:00 | AP529E | Urban | Asset failure | LV | 21.3333 | 97 | 0.0033082 | 3.411e-05 | No
29/12/2018 | 11:35:43 | MI14 | Rural Long | Unknown | Unknown | 2 | 10 | 0.00014597 | 1.46e-05 | No
29/12/2018 | 12:08:39 | ST11 | Rural Short | Asset failure | LV | 1.3333 | 365 | 0.0036257 | 9.93e-06 | No
29/12/2018 | 13:05:09 | SG11 | Rural Short | Asset failure | LV | 1 | 483 | 0.0035984 | 7.45e-06 | No
29/12/2018 | 13:37:38 | HH428D | Urban | Asset failure | LV | 1 | 104 | 0.00016626 | 1.6e-06 | No
29/12/2018 | 13:48:39 | HH428D | Urban | Asset failure | LV | 1 | 94 | 0.00015028 | 1.6e-06 | No
29/12/2018 | 14:17:24 | SM179A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 206 | 0.00032933 | 1.6e-06 | No
29/12/2018 | 16:23:45 | MG41 | Urban | Asset failure | LV | 18.3333 | 121 | 0.0035464 | 2.931e-05 | No
29/12/2018 | 16:57:59 | HH386D | Urban | Asset failure | LV | 1 | 262 | 0.00041885 | 1.6e-06 | No
29/12/2018 | 20:08:44 | SM374B | Urban | Overloads |  | 1 | 158 | 0.00025259 | 1.6e-06 | No
29/12/2018 | 20:56:37 | MI12 | Rural Long | Unknown | Unknown | 14 | 11 | 0.0011239 | 0.00010218 | No
29/12/2018 | 23:55:29 | PA19 | Rural Long | Weather |  | 23 | 490.6957 | 0.082369 | 0.00016786 | No
30/12/2018 | 00:27:52 | PL754A | Rural Long | Unknown | Unknown | 17.3333 | 9.7885 | 0.0012383 | 0.0001265 | No
30/12/2018 | 02:01:36 | SD33200 | Rural Long | Network business | Switching and protection error | 1229 | 194 | 1.7401 | 0.0089697 | No
30/12/2018 | 02:51:17 | BS0336 | Urban | Unknown | Unknown | 1 | 76 | 0.0001215 | 1.6e-06 | No
30/12/2018 | 02:59:42 | PP17 | Rural Long | Asset failure | Distribution substation | 51 | 724.098 | 0.26952 | 0.00037222 | No
30/12/2018 | 03:18:33 | SD1622 | Rural Short | Unknown | Unknown | 3158 | 22.9829 | 0.54073 | 0.023528 | No
30/12/2018 | 03:24:52 | BM56 | Rural Short | Unknown | Unknown | 14 | 554 | 0.057783 | 0.0001043 | No
30/12/2018 | 04:04:57 | BU08 | Rural Long | Weather |  | 77 | 735.3247 | 0.41323 | 0.00056197 | No
30/12/2018 | 04:34:09 | SD31100 | Rural Long | Weather |  | 1 | 1323 | 0.0096557 | 7.3e-06 | No
30/12/2018 | 04:38:00 | WHY363A | Rural Short | Unknown | Unknown | 53 | 876.7736 | 0.3462 | 0.00039486 | No
30/12/2018 | 04:49:47 | SD32103 | Rural Short | Weather |  | 35 | 355 | 0.092568 | 0.00026076 | No
30/12/2018 | 05:44:00 | PP16 | Rural Short | Weather |  | 73 | 396.4795 | 0.21563 | 0.00054386 | No
30/12/2018 | 05:57:07 | BU02 | Rural Long | Weather |  | 101 | 384.4752 | 0.28341 | 0.00073713 | No
30/12/2018 | 06:09:00 | G11 | Rural Long | Weather |  | 60 | 580.9333 | 0.25439 | 0.0004379 | No
30/12/2018 | 06:09:00 | G11 | Rural Long | Weather |  | 0 | 89 | 0.0032478 | 0 | No
30/12/2018 | 06:16:55 | CL15 | Rural Long | Weather |  | 81.6667 | 362.9633 | 0.21634 | 0.00059603 | No
30/12/2018 | 06:51:20 | CL07 | Rural Long | Weather |  | 58 | 259.9483 | 0.11004 | 0.0004233 | No
30/12/2018 | 08:25:42 | R04 | Rural Long | Weather |  | 38 | 341 | 0.094572 | 0.00027734 | No
30/12/2018 | 08:53:32 | WK31 | Rural Short | Unknown | Unknown | 137 | 107 | 0.10921 | 0.0010207 | No
30/12/2018 | 08:55:53 | WK42 | Rural Short | Unknown | Unknown | 156 | 253.2179 | 0.2943 | 0.0011622 | No
30/12/2018 | 09:00:33 | CL04 | Rural Long | Weather |  | 2 | 276 | 0.0040287 | 1.46e-05 | No
30/12/2018 | 09:00:37 | WK43 | Rural Short | Unknown | Unknown | 22 | 420 | 0.068839 | 0.0001639 | No
30/12/2018 | 09:15:27 | MI12 | Rural Long | Weather |  | 4.6667 | 183 | 0.0062328 | 3.406e-05 | No
30/12/2018 | 09:33:00 | WK44 | Rural Short | Weather |  | 19 | 717 | 0.10149 | 0.00014155 | No
30/12/2018 | 09:45:38 | NL111P | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 138 | 0.00022062 | 1.6e-06 | No
30/12/2018 | 09:49:45 | SD39100 | Rural Long | Weather |  | 852.0002 | 120.1624 | 0.74719 | 0.0062182 | No
30/12/2018 | 09:50:10 | WK65 | Rural Short | Animal | Animal impact | 69 | 327 | 0.1681 | 0.00051406 | No
30/12/2018 | 10:09:22 | LX54 | Rural Short | Unknown | Unknown | 22 | 201 | 0.032945 | 0.0001639 | No
30/12/2018 | 10:21:32 | HH341E | Urban | Overloads |  | 1 | 165 | 0.00026378 | 1.6e-06 | No
30/12/2018 | 10:23:55 | HH121B | Urban | Asset failure | LV | 1 | 216 | 0.00034531 | 1.6e-06 | No
30/12/2018 | 11:00:39 | SD39100 | Rural Long | Unknown | Unknown | 2 | 330 | 0.0048169 | 1.46e-05 | No
30/12/2018 | 11:04:18 | GA03 | Rural Long | Unknown | Unknown | 27 | 193 | 0.038032 | 0.00019706 | No
30/12/2018 | 11:07:47 | LX75 | Rural Long | Weather |  | 46 | 305.8261 | 0.10267 | 0.00033572 | No
30/12/2018 | 11:17:41 | PA24 | Rural Long | Weather |  | 3 | 1456 | 0.031879 | 2.19e-05 | No
30/12/2018 | 11:41:12 | BU10 | Rural Long | Weather |  | 11 | 88 | 0.0070648 | 8.028e-05 | No
30/12/2018 | 11:51:15 | CL06 | Rural Long | Weather |  | 7 | 259 | 0.013232 | 5.109e-05 | No
30/12/2018 | 12:35:41 | R14 | Rural Long | Unknown | Unknown | 1 | 274 | 0.0019997 | 7.3e-06 | No
30/12/2018 | 12:54:35 | LX71 | Rural Long | Unknown | Unknown | 14 | 487 | 0.04976 | 0.00010218 | No
30/12/2018 | 13:01:40 | KA01 | Rural Short | Asset failure | LV | 1 | 345 | 0.0025703 | 7.45e-06 | No
30/12/2018 | 15:22:59 | SD40800 | Rural Long | Unknown | Unknown | 11 | 459 | 0.036849 | 8.028e-05 | No
30/12/2018 | 15:41:01 | WK31 | Rural Short | Asset failure | LV | 2 | 158 | 0.0023543 | 1.49e-05 | No
30/12/2018 | 16:21:16 | YK03 | Rural Long | Asset failure | Distribution substation | 12 | 105 | 0.0091959 | 8.758e-05 | No
30/12/2018 | 18:27:05 | SD31300 | Rural Long | Unknown | Unknown | 5 | 420 | 0.015327 | 3.649e-05 | No
30/12/2018 | 19:45:09 | AP529E | Urban | Asset failure | LV | 21.3333 | 66 | 0.0022509 | 3.411e-05 | No
31/12/2018 | 00:00:49 | G13 | Rural Long | Weather |  | 23 | 817 | 0.13714 | 0.00016786 | No
31/12/2018 | 02:59:30 | G14 | Rural Long | Weather |  | 97 | 604.268 | 0.42778 | 0.00070794 | No
31/12/2018 | 06:57:55 | KA05 | Rural Long | Unknown | Unknown | 26.3333 | 72 | 0.013838 | 0.00019219 | No
31/12/2018 | 08:38:12 | ST22 | Rural Short | Unknown | Unknown | 1 | 267 | 0.0019892 | 7.45e-06 | No
31/12/2018 | 08:42:06 | BM56 | Rural Short | Weather |  | 40 | 134 | 0.039933 | 0.00029801 | No
31/12/2018 | 09:35:28 | MB23 | Rural Short | Asset failure | LV | 1 | 316 | 0.0023543 | 7.45e-06 | No
31/12/2018 | 10:54:03 | BT02 | Rural Long | Unknown | Unknown | 1 | 109 | 0.00079552 | 7.3e-06 | No
31/12/2018 | 11:17:01 | LX71 | Rural Long | Weather |  | 7 | 108 | 0.0055175 | 5.109e-05 | No
31/12/2018 | 11:17:30 | NA29 | Rural Long | Planned |  | 1 | 8 | 5.839e-05 | 7.3e-06 | No
31/12/2018 | 11:20:28 | MTB13 | Rural Short | Asset failure | LV | 1 | 204 | 0.0015198 | 7.45e-06 | No
31/12/2018 | 12:32:43 | MTB53 | Rural Long | Asset failure | LV | 1.3333 | 94 | 0.00091472 | 9.73e-06 | No
31/12/2018 | 12:32:55 | SA520D | Urban | Asset failure | LV | 1 | 145 | 0.00023181 | 1.6e-06 | No
31/12/2018 | 16:27:32 | CM11 | Rural Long | Third Party | Vehicle impact | 12 | 172 | 0.015064 | 8.758e-05 | No
31/12/2018 | 16:35:00 | NA57 | Rural Long | Asset failure | HV | 43 | 73 | 0.022909 | 0.00031383 | No
31/12/2018 | 16:44:28 | SM402E | Urban | Asset failure | LV | 1 | 151 | 0.0002414 | 1.6e-06 | No
31/12/2018 | 17:59:14 | SM411E | Urban | Unknown | Unknown | 111 | 211 | 0.037443 | 0.00017745 | No
31/12/2018 | 19:33:03 | AP226D | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
31/12/2018 | 19:47:26 | EL25 | Urban | Third Party | Vehicle impact | 666 | 48.8108 | 0.05197 | 0.0010647 | No
31/12/2018 | 20:09:59 | LM64 | Rural Long | Unknown | Unknown | 68 | 220 | 0.10918 | 0.00049629 | No
31/12/2018 | 21:09:43 | KA10 | Rural Long | Unknown | Unknown | 71 | 367.6761 | 0.19052 | 0.00051818 | No
1/01/2019 | 07:58:14 | NU01 | Rural Short | Asset failure | HV | 126 | 118 | 0.11077 | 0.00093872 | No
1/01/2019 | 08:07:12 | ME347A | Urban | Vegetation | Grow-in - NSP responsibility | 88 | 141 | 0.019836 | 0.00014068 | No
1/01/2019 | 09:16:00 | GA43 | Rural Short | Asset failure | LV | 1 | 335 | 0.0024958 | 7.45e-06 | No
1/01/2019 | 09:58:05 | LM64 | Rural Long | Asset failure | HV | 68 | 464.9412 | 0.23074 | 0.00049629 | No
1/01/2019 | 14:18:41 | VH17 | Rural Short | Asset failure | LV | 1 | 224 | 0.0016688 | 7.45e-06 | No
1/01/2019 | 14:20:28 | MG46 | Rural Short | Other |  | 1 | 101 | 0.00075247 | 7.45e-06 | No
1/01/2019 | 18:33:37 | ME347C | Urban | Overloads |  | 1 | 158 | 0.00025259 | 1.6e-06 | No
1/01/2019 | 20:37:43 | HH145A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 49.3334 | 81 | 0.0063883 | 7.887e-05 | No
1/01/2019 | 22:20:57 | EL07 | Urban | Asset failure | LV | 32.3333 | 313 | 0.016179 | 5.169e-05 | No
1/01/2019 | 22:23:00 | HH428B | Urban | Asset failure | LV | 12.3333 | 97 | 0.0019126 | 1.972e-05 | No
2/01/2019 | 05:34:12 | WK31 | Rural Short | Unknown | Unknown | 138 | 227 | 0.23338 | 0.0010281 | No
2/01/2019 | 07:38:48 | SD35400 | Rural Short | Weather |  | 852 | 207.2183 | 1.3153 | 0.0063475 | No
2/01/2019 | 08:43:10 | HH522B | Urban | Asset failure | LV | 16.3333 | 84 | 0.0021934 | 2.611e-05 | No
2/01/2019 | 08:45:26 | CL12 | Rural Long | Planned |  | 27 | 170 | 0.033499 | 0.00019706 | No
2/01/2019 | 09:00:00 | MG29 | Rural Long | Asset failure | LV | 2 | 145 | 0.0021165 | 1.46e-05 | No
2/01/2019 | 09:12:48 | AP344E | Urban | Planned |  | 109 | 379 | 0.066043 | 0.00017426 | No
2/01/2019 | 09:15:01 | MI24 | Rural Long | Planned |  | 1 | 124 | 0.00090499 | 7.3e-06 | No
2/01/2019 | 09:15:12 | W01 | Rural Long | Planned |  | 1 | 29 | 0.00021165 | 7.3e-06 | No
2/01/2019 | 09:20:02 | BM43 | Rural Short | Planned |  | 50 | 276 | 0.10281 | 0.00037251 | No
2/01/2019 | 09:21:45 | SB21 | Rural Long | Planned |  | 1 | 16 | 0.00011677 | 7.3e-06 | No
2/01/2019 | 09:24:08 | VH10 | Rural Short | Planned |  | 2 | 294 | 0.0043807 | 1.49e-05 | No
2/01/2019 | 10:01:21 | MI19 | Rural Long | Planned |  | 90 | 67 | 0.044009 | 0.00065685 | No
2/01/2019 | 10:16:26 | HH102B | Urban | Planned |  | 102 | 27 | 0.0044028 | 0.00016306 | No
2/01/2019 | 10:22:39 | MTB12 | Rural Short | Asset failure | LV | 1 | 125 | 0.00093127 | 7.45e-06 | No
2/01/2019 | 10:54:28 | PL11 | Rural Long | Planned |  | 2 | 267 | 0.0038973 | 1.46e-05 | No
2/01/2019 | 11:00:51 | SM172D | Urban | Planned |  | 59 | 35 | 0.0033013 | 9.432e-05 | No
2/01/2019 | 12:35:30 | SM349B | Urban | Planned |  | 121 | 15 | 0.0029016 | 0.00019344 | No
2/01/2019 | 13:33:41 | HH403D | Urban | Planned |  | 112 | 16 | 0.0028648 | 0.00017905 | No
2/01/2019 | 13:39:22 | SD32200 | Rural Long | Weather |  | 210 | 178 | 0.27281 | 0.0015326 | No
2/01/2019 | 13:57:35 | SA35 | Urban | Asset failure | LV | 1 | 32 | 5.116e-05 | 1.6e-06 | No
2/01/2019 | 14:29:52 | NL544B | Urban | Vegetation | Grow-in - NSP responsibility | 3 | 13 | 6.235e-05 | 4.8e-06 | No
2/01/2019 | 17:07:23 | AP351E | Urban | Overloads |  | 1 | 18 | 2.878e-05 | 1.6e-06 | No
2/01/2019 | 17:15:38 | VH15 | Rural Short | Asset failure | Distribution substation | 147 | 200.7347 | 0.21984 | 0.0010952 | No
2/01/2019 | 17:37:17 | SA20 | Urban | Asset failure | LV | 1 | 202 | 0.00032293 | 1.6e-06 | No
2/01/2019 | 17:39:24 | SM410A | Urban | Overloads |  | 1 | 197 | 0.00031494 | 1.6e-06 | No
2/01/2019 | 17:44:26 | MV15 | Rural Short | Asset failure | Distribution substation | 9 | 2311.7778 | 0.15501 | 6.705e-05 | No
2/01/2019 | 19:11:19 | NU04 | Rural Short | Overloads |  | 1 | 184 | 0.0013708 | 7.45e-06 | No
2/01/2019 | 19:46:01 | AP344A | Urban | Asset failure | LV | 71 | 129 | 0.014642 | 0.00011351 | No
2/01/2019 | 20:51:54 | NU03 | Rural Long | Unknown | Unknown | 5 | 183 | 0.006678 | 3.649e-05 | No
3/01/2019 | 00:05:33 | HH107A | Urban | Unknown | Unknown | 1 | 534 | 0.00085369 | 1.6e-06 | No
3/01/2019 | 03:51:03 | BS0336 | Urban | Unknown | Unknown | 1 | 63 | 0.00010072 | 1.6e-06 | No
3/01/2019 | 06:47:55 | SD38100 | Rural Long | Unknown | Unknown | 4 | 124 | 0.00362 | 2.919e-05 | No
3/01/2019 | 07:24:33 | EL07 | Urban | Asset failure | LV | 1 | 117 | 0.00018704 | 1.6e-06 | No
3/01/2019 | 08:26:35 | SA18 | Urban | Planned |  | 55 | 5 | 0.00043964 | 8.793e-05 | No
3/01/2019 | 08:40:52 | MB21 | Urban | Planned |  | 60 | 11 | 0.0010551 | 9.592e-05 | No
3/01/2019 | 08:44:14 | SA42 | Urban | Planned |  | 10 | 16 | 0.00025579 | 1.599e-05 | No
3/01/2019 | 08:44:26 | SA14 | Urban | Planned |  | 34 | 10 | 0.00054355 | 5.435e-05 | No
3/01/2019 | 08:50:18 | LX53 | Rural Short | Unknown | Unknown | 16 | 110 | 0.013112 | 0.0001192 | No
3/01/2019 | 09:04:29 | SA36 | Urban | Planned |  | 18 | 85 | 0.002446 | 2.878e-05 | No
3/01/2019 | 09:11:32 | HH145A | Urban | Planned |  | 18 | 908 | 0.026129 | 2.878e-05 | No
3/01/2019 | 09:16:51 | W24 | Rural Long | Planned |  | 52 | 45 | 0.017078 | 0.00037951 | No
3/01/2019 | 09:32:04 | M41 | Rural Long | Asset failure | LV | 2 | 8 | 0.00011677 | 1.46e-05 | No
3/01/2019 | 09:45:13 | KI12 | Rural Long | Planned |  | 2 | 46 | 0.00067145 | 1.46e-05 | No
3/01/2019 | 09:47:36 | MB61 | Rural Long | Asset failure | LV | 1 | 80 | 0.00058387 | 7.3e-06 | No
3/01/2019 | 09:50:38 | WHY12 | Urban | Asset failure | HV | 48.6667 | 230 | 0.017895 | 7.78e-05 | No
3/01/2019 | 10:38:04 | SM179C | Urban | Vegetation | Grow-in - NSP responsibility | 98 | 59 | 0.0092435 | 0.00015667 | No
3/01/2019 | 12:38:22 | SM402D | Urban | Asset failure | LV | 1 | 278 | 0.00044443 | 1.6e-06 | No
3/01/2019 | 13:13:26 | HH145A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 17.3333 | 71 | 0.0019674 | 2.771e-05 | No
3/01/2019 | 14:07:57 | SM179A | Urban | Planned |  | 117 | 2 | 0.00037409 | 0.00018704 | No
3/01/2019 | 14:26:55 | HH428F | Urban | Asset failure | LV | 14 | 53 | 0.0011862 | 2.238e-05 | No
3/01/2019 | 14:30:46 | SA520D | Urban | Overloads |  | 1 | 175 | 0.00027977 | 1.6e-06 | No
3/01/2019 | 14:50:51 | HH102B | Urban | Asset failure | LV | 20.3333 | 162 | 0.005266 | 3.251e-05 | No
3/01/2019 | 15:36:38 | HH341C | Urban | Unknown | Unknown | 25 | 138 | 0.0055154 | 3.997e-05 | No
3/01/2019 | 16:12:41 | MG03 | Rural Short | Animal | Animal impact | 1 | 68 | 0.00050661 | 7.45e-06 | No
3/01/2019 | 16:24:45 | CN02 | Rural Long | Asset failure | Distribution substation | 34 | 465.3824 | 0.11548 | 0.00024814 | No
3/01/2019 | 17:14:57 | VH12 | Rural Short | Asset failure | LV | 1 | 339 | 0.0025256 | 7.45e-06 | No
3/01/2019 | 17:44:42 | MG05 | Rural Long | Unknown | Unknown | 7 | 163 | 0.0083274 | 5.109e-05 | No
3/01/2019 | 17:45:51 | EL01R | Urban | Overloads |  | 1 | 97 | 0.00015507 | 1.6e-06 | No
3/01/2019 | 17:48:03 | HH130B | Urban | Overloads |  | 1 | 413 | 0.00066025 | 1.6e-06 | No
3/01/2019 | 18:03:04 | HH121B | Urban | Unknown | Unknown | 35.6666 | 222 | 0.012658 | 5.702e-05 | No
3/01/2019 | 18:19:44 | HH341G | Urban | Unknown | Unknown | 37 | 92 | 0.0054419 | 5.915e-05 | No
3/01/2019 | 18:22:43 | SD34400 | Rural Long | Asset failure | Subtransmission | 1 | 250 | 0.0018246 | 7.3e-06 | No
3/01/2019 | 18:23:27 | SA11 | Urban | Overloads |  | 19.3333 | 121 | 0.0037398 | 3.091e-05 | No
3/01/2019 | 18:34:35 | HH428F | Urban | Asset failure | LV | 40.3333 | 216 | 0.013928 | 6.448e-05 | No
3/01/2019 | 18:42:32 | ME131A | Urban | Third Party | Other | 233 | 21 | 0.0078223 | 0.00037249 | No
3/01/2019 | 18:49:59 | AP355A | Urban | Asset failure | LV | 29 | 129 | 0.0059806 | 4.636e-05 | No
3/01/2019 | 18:59:14 | EL01A | Urban | Unknown | Unknown | 33.3333 | 128 | 0.006821 | 5.329e-05 | No
3/01/2019 | 19:18:03 | PP04 | Rural Short | Asset failure | LV | 1 | 190 | 0.0014155 | 7.45e-06 | No
3/01/2019 | 19:23:54 | HH121D | Urban | Asset failure | LV | 27.3333 | 231 | 0.010094 | 4.37e-05 | No
3/01/2019 | 19:24:22 | HH121C | Urban | Asset failure | LV | 15 | 335 | 0.0080333 | 2.398e-05 | No
3/01/2019 | 19:25:34 | HH121D | Urban | Asset failure | LV | 2.6667 | 259 | 0.0011041 | 4.26e-06 | No
3/01/2019 | 19:44:31 | HH429C | Urban | Unknown | Unknown | 28 | 225 | 0.010072 | 4.476e-05 | No
3/01/2019 | 19:48:18 | PA04 | Rural Short | Other |  | 8 | 101 | 0.0060197 | 5.96e-05 | No
3/01/2019 | 19:54:22 | NA59 | Rural Long | Overloads |  | 4.3333 | 147 | 0.004649 | 3.163e-05 | No
3/01/2019 | 19:54:48 | MV64 | Urban | Unknown | Unknown | 24.3333 | 252 | 0.0098031 | 3.89e-05 | No
3/01/2019 | 20:00:48 | AP227A | Urban | Asset failure | LV | 17 | 144 | 0.0039136 | 2.718e-05 | No
3/01/2019 | 20:24:08 | NU03 | Rural Long | Unknown | Unknown | 26.6667 | 157 | 0.030556 | 0.00019462 | No
3/01/2019 | 20:24:23 | G38 | Rural Long | Asset failure | Distribution substation | 39 | 517.0769 | 0.14718 | 0.00028464 | No
3/01/2019 | 20:41:34 | CL09 | Rural Long | Asset failure | HV | 14 | 158 | 0.016144 | 0.00010218 | No
3/01/2019 | 21:14:34 | HH409D | Urban | Unknown | Unknown | 18.6666 | 284 | 0.0084751 | 2.984e-05 | No
3/01/2019 | 21:24:54 | SG11 | Rural Short | Unknown | Unknown | 20 | 165 | 0.024585 | 0.000149 | No
3/01/2019 | 22:09:40 | ME231D | Urban | Asset failure | LV | 7 | 203 | 0.0022717 | 1.119e-05 | No
4/01/2019 | 03:21:41 | AP149B | Urban | Overloads |  | 1 | 470 | 0.00075138 | 1.6e-06 | No
4/01/2019 | 04:06:44 | HH177G | Urban | Vegetation | Grow-in - NSP responsibility | 36 | 277 | 0.015942 | 5.755e-05 | No
4/01/2019 | 04:23:20 | PL33 | Rural Long | Asset failure | HV | 19 | 319 | 0.044235 | 0.00013867 | No
4/01/2019 | 06:10:17 | AP227A | Urban | Asset failure | LV | 1 | 196 | 0.00031334 | 1.6e-06 | No
4/01/2019 | 07:47:20 | AP355A | Urban | Overloads |  | 1 | 514 | 0.00082172 | 1.6e-06 | No
4/01/2019 | 08:46:20 | NA34 | Rural Long | Asset failure | HV | 12 | 78 | 0.0068312 | 8.758e-05 | No
4/01/2019 | 08:57:50 | HH130A | Urban | Planned |  | 170 | 282 | 0.07664 | 0.00027177 | No
4/01/2019 | 09:01:46 | HH386C | Urban | Asset failure | HV | 84 | 143 | 0.019203 | 0.00013429 | No
4/01/2019 | 09:02:03 | WHY02 | Urban | Planned |  | 18 | 226 | 0.0065034 | 2.878e-05 | No
4/01/2019 | 09:09:21 | R33 | Rural Long | Planned |  | 20 | 149 | 0.021749 | 0.00014597 | No
4/01/2019 | 09:23:19 | AP226E | Urban | Planned |  | 72 | 255 | 0.029352 | 0.0001151 | No
4/01/2019 | 09:42:10 | MV14 | Rural Short | Planned |  | 15 | 252 | 0.028162 | 0.00011175 | No
4/01/2019 | 11:25:44 | VH33 | Rural Short | Asset failure | HV | 12 | 39 | 0.0034867 | 8.94e-05 | No
4/01/2019 | 11:48:23 | HH386D | Urban | Other |  | 1 | 157 | 0.00025099 | 1.6e-06 | No
4/01/2019 | 11:56:10 | CL09 | Rural Long | Unknown | Unknown | 14 | 176 | 0.017983 | 0.00010218 | No
4/01/2019 | 12:10:42 | ME131B | Urban | Planned |  | 64 | 6 | 0.00061389 | 0.00010232 | No
4/01/2019 | 12:54:57 | GU31 | Rural Long | Asset failure | LV | 1 | 216 | 0.0015764 | 7.3e-06 | No
4/01/2019 | 12:55:56 | HH409F | Urban | Asset failure | LV | 1 | 253 | 0.00040446 | 1.6e-06 | No
4/01/2019 | 13:16:41 | HH107B | Urban | Asset failure | LV | 46.3333 | 94 | 0.0069628 | 7.407e-05 | No
4/01/2019 | 14:03:47 | CD16 | Rural Short | Planned |  | 2 | 12 | 0.0001788 | 1.49e-05 | No
4/01/2019 | 15:15:31 | MV31 | Rural Short | Unknown | Unknown | 8 | 61 | 0.0036357 | 5.96e-05 | No
4/01/2019 | 17:46:14 | HH107B | Urban | Vegetation | Grow-in - NSP responsibility | 139 | 58 | 0.012889 | 0.00022222 | No
4/01/2019 | 18:19:51 | AP149E | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
4/01/2019 | 19:15:54 | EL260C | Urban | Animal | Animal impact | 70 | 60 | 0.0067144 | 0.00011191 | No
4/01/2019 | 20:37:57 | SA40 | Urban | Asset failure | LV | 1 | 11 | 1.759e-05 | 1.6e-06 | No
5/01/2019 | 07:19:25 | LX54 | Rural Short | Asset failure | HV | 1 | 140 | 0.001043 | 7.45e-06 | No
5/01/2019 | 08:02:53 | SM137C | Urban | Planned |  | 3 | 283 | 0.0013573 | 4.8e-06 | No
5/01/2019 | 08:20:17 | BT06 | Rural Long | Asset failure | LV | 1 | 315 | 0.002299 | 7.3e-06 | No
5/01/2019 | 08:57:14 | HH403A | Urban | Asset failure | LV | 1 | 218 | 0.00034851 | 1.6e-06 | No
5/01/2019 | 10:48:47 | EL25 | Urban | Asset failure | LV | 1 | 293 | 0.00046841 | 1.6e-06 | No
5/01/2019 | 11:17:43 | YK19 | Rural Long | Unknown | Unknown | 55 | 292.8727 | 0.11756 | 0.00040141 | No
5/01/2019 | 11:22:42 | SM374B | Urban | Overloads |  | 1 | 382 | 0.00061069 | 1.6e-06 | No
5/01/2019 | 12:41:58 | CN77 | Rural Long | Unknown | Unknown | 47 | 230 | 0.078895 | 0.00034302 | No
5/01/2019 | 16:34:28 | MV33 | Rural Short | Unknown | Unknown | 4.3333 | 160 | 0.0051654 | 3.228e-05 | No
5/01/2019 | 16:35:13 | HH177F | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 106 | 0.00016946 | 1.6e-06 | No
5/01/2019 | 17:08:48 | MG34 | Rural Long | Asset failure | HV | 2 | 37 | 0.00054008 | 1.46e-05 | No
5/01/2019 | 19:20:11 | AP146A | Urban | Overloads |  | 615 | 74.8602 | 0.073601 | 0.00098319 | No
5/01/2019 | 19:51:40 | MI07 | Rural Long | Asset failure | HV | 77 | 393 | 0.22085 | 0.00056197 | No
6/01/2019 | 02:01:41 | SB21 | Rural Long | Asset failure | HV | 79 | 215.6329 | 0.12433 | 0.00057657 | No
6/01/2019 | 05:57:53 | YK19 | Rural Long | Asset failure | HV | 5 | 454 | 0.016567 | 3.649e-05 | No
6/01/2019 | 06:18:06 | CN77 | Rural Long | Unknown | Unknown | 47 | 275 | 0.094331 | 0.00034302 | No
6/01/2019 | 08:23:13 | SA40 | Urban | Asset failure | LV | 1 | 195 | 0.00031174 | 1.6e-06 | No
6/01/2019 | 11:00:23 | HH432F | Urban | Overloads |  | 1 | 216 | 0.00034531 | 1.6e-06 | No
6/01/2019 | 14:29:22 | HH341G | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
6/01/2019 | 15:47:25 | BM34 | Rural Short | Asset failure | LV | 8 | 145 | 0.0086422 | 5.96e-05 | No
6/01/2019 | 16:48:39 | ME200E | Urban | Other |  | 3.6667 | 241 | 0.0014127 | 5.86e-06 | No
6/01/2019 | 17:02:39 | HH432F | Urban | Overloads |  | 1 | 175 | 0.00027977 | 1.6e-06 | No
6/01/2019 | 20:43:28 | SM350A | Urban | Overloads |  | 1 | 157 | 0.00025099 | 1.6e-06 | No
6/01/2019 | 23:13:31 | SM126C | Urban | Animal | Animal impact | 53 | 118 | 0.0099981 | 8.473e-05 | No
7/01/2019 | 05:10:25 | CM16 | Rural Long | Asset failure | Distribution substation | 86 | 603.093 | 0.37854 | 0.00062766 | No
7/01/2019 | 08:21:36 | MI32 | Rural Long | Asset failure | LV | 39 | 78 | 0.022202 | 0.00028464 | No
7/01/2019 | 08:42:26 | VH23 | Rural Short | Planned |  | 545 | 158 | 0.64153 | 0.0040603 | No
7/01/2019 | 08:57:59 | SD35403 | Rural Short | Planned |  | 3 | 177 | 0.003956 | 2.235e-05 | No
7/01/2019 | 09:00:18 | SA11 | Urban | Planned |  | 17 | 224 | 0.0060878 | 2.718e-05 | No
7/01/2019 | 09:19:39 | SG04 | Rural Short | Planned |  | 16 | 200 | 0.02384 | 0.0001192 | No
7/01/2019 | 09:24:02 | SA33 | Urban | Planned |  | 144 | 92.9861 | 0.021406 | 0.00023021 | No
7/01/2019 | 09:26:25 | SA33 | Urban | Planned |  | 1 | 22 | 3.517e-05 | 1.6e-06 | No
7/01/2019 | 09:30:54 | SA18 | Urban | Planned |  | 284 | 305 | 0.13848 | 0.00045402 | No
7/01/2019 | 09:35:02 | NL210F | Urban | Planned |  | 29 | 1935 | 0.08971 | 4.636e-05 | No
7/01/2019 | 09:48:13 | MB24 | Rural Short | Planned |  | 1 | 17 | 0.00012665 | 7.45e-06 | No
7/01/2019 | 10:24:07 | BS0336 | Urban | Unknown | Unknown | 1 | 47 | 7.514e-05 | 1.6e-06 | No
7/01/2019 | 10:37:54 | G23 | Rural Long | Planned |  | 2 | 208 | 0.0030361 | 1.46e-05 | No
7/01/2019 | 10:40:06 | CL05 | Rural Long | Asset failure | LV | 1 | 288 | 0.0021019 | 7.3e-06 | No
7/01/2019 | 11:19:47 | MTB51 | Rural Long | Planned |  | 1 | 29 | 0.00021165 | 7.3e-06 | No
7/01/2019 | 11:32:09 | CV08 | Rural Long | Planned |  | 133 | 180 | 0.17472 | 0.00097068 | No
7/01/2019 | 11:58:45 | SD40600 | Rural Long | Unknown | Unknown | 1 | 126 | 0.00091959 | 7.3e-06 | No
7/01/2019 | 13:34:07 | SA33 | Urban | Planned |  | 1 | 48 | 7.674e-05 | 1.6e-06 | No
7/01/2019 | 14:27:58 | PP07 | Rural Long | Unknown | Unknown | 3 | 33 | 0.00072254 | 2.19e-05 | No
7/01/2019 | 16:26:24 | MB03 | Rural Long | Asset failure | LV | 1 | 104 | 0.00075903 | 7.3e-06 | No
7/01/2019 | 17:47:38 | SA17 | Urban | Overloads |  | 1 | 97 | 0.00015507 | 1.6e-06 | No
7/01/2019 | 19:54:05 | M13 | Rural Long | Animal | Animal impact | 976 | 73 | 0.51999 | 0.0071232 | No
8/01/2019 | 00:04:47 | SG12 | Rural Short | Unknown | Unknown | 105.6667 | 100 | 0.078723 | 0.00078723 | No
8/01/2019 | 06:11:06 | MG15 | Rural Short | Unknown | Unknown | 25 | 178.36 | 0.03322 | 0.00018625 | No
8/01/2019 | 06:43:41 | MB81 | Rural Long | Asset failure | HV | 1 | 214 | 0.0015618 | 7.3e-06 | No
8/01/2019 | 07:01:14 | MTB21 | Rural Short | Third Party | Other | 7 | 66 | 0.003442 | 5.215e-05 | No
8/01/2019 | 07:47:32 | NL234B | Urban | Asset failure | HV | 127 | 79.9291 | 0.016228 | 0.00020303 | No
8/01/2019 | 07:49:03 | EL12 | Urban | Animal | Animal impact | 4 | 134 | 0.00085689 | 6.39e-06 | No
8/01/2019 | 09:09:41 | HK05 | Rural Long | Planned |  | 57 | 388 | 0.16141 | 0.00041601 | No
8/01/2019 | 09:17:22 | SA36 | Urban | Planned |  | 3 | 265 | 0.001271 | 4.8e-06 | No
8/01/2019 | 09:21:45 | MV15 | Rural Short | Planned |  | 19 | 249 | 0.035247 | 0.00014155 | No
8/01/2019 | 09:22:00 | HH177E | Urban | Planned |  | 184 | 57 | 0.016767 | 0.00029416 | No
8/01/2019 | 09:24:18 | SD38100 | Rural Long | Planned |  | 16 | 81 | 0.0094587 | 0.00011677 | No
8/01/2019 | 09:27:55 | SG10 | Rural Short | Planned |  | 19 | 130 | 0.018402 | 0.00014155 | No
8/01/2019 | 09:29:29 | LM51 | Rural Long | Planned |  | 75 | 127 | 0.069517 | 0.00054738 | No
8/01/2019 | 09:32:28 | VH17 | Rural Short | Planned |  | 61 | 196 | 0.089074 | 0.00045446 | No
8/01/2019 | 09:33:32 | PP10 | Urban | Planned |  | 51 | 277 | 0.022584 | 8.153e-05 | No
8/01/2019 | 09:34:55 | HH130B | Urban | Planned |  | 115 | 124 | 0.022797 | 0.00018385 | No
8/01/2019 | 09:37:25 | EL18 | Urban | Planned |  | 212 | 66.533 | 0.022549 | 0.00033892 | No
8/01/2019 | 09:40:07 | ST23 | Rural Short | Planned |  | 1 | 77 | 0.00057366 | 7.45e-06 | No
8/01/2019 | 09:46:04 | SM349A | Urban | Planned |  | 1 | 87 | 0.00013908 | 1.6e-06 | No
8/01/2019 | 09:56:38 | HH341B | Urban | Planned |  | 119 | 218 | 0.041473 | 0.00019024 | No
8/01/2019 | 10:10:45 | HH341J | Urban | Asset failure | LV | 71 | 63 | 0.0071509 | 0.00011351 | No
8/01/2019 | 10:30:16 | NU20 | Rural Long | Planned |  | 15 | 246 | 0.026931 | 0.00010948 | No
8/01/2019 | 10:35:44 | SA18 | Urban | Planned |  | 117 | 157 | 0.029366 | 0.00018704 | No
8/01/2019 | 11:14:11 | CBD27C | CBD | Unknown | Unknown | 99 | 43 | 0.82636 | 0.019218 | No
8/01/2019 | 12:44:16 | M13 | Rural Long | Unknown | Unknown | 8 | 64 | 0.0037368 | 5.839e-05 | No
8/01/2019 | 14:59:15 | SD58101 | Rural Short | Unknown | Unknown | 5 | 1 | 3.725e-05 | 3.725e-05 | No
8/01/2019 | 15:54:40 | M21 | Rural Long | Unknown | Unknown | 2 | 185 | 0.0027004 | 1.46e-05 | No
8/01/2019 | 18:25:52 | KI16 | Rural Long | Asset failure | HV | 109 | 155 | 0.12331 | 0.00079552 | No
8/01/2019 | 18:54:06 | PL24 | Rural Long | Unknown | Unknown | 32 | 279 | 0.06516 | 0.00023355 | No
8/01/2019 | 18:56:58 | SM350E | Urban | Overloads |  | 1 | 134 | 0.00021422 | 1.6e-06 | No
8/01/2019 | 20:54:59 | HH102A | Urban | Asset failure | LV | 19.6666 | 83 | 0.0026096 | 3.144e-05 | No
8/01/2019 | 21:06:09 | CN77 | Rural Long | Weather |  | 23 | 883.6522 | 0.14833 | 0.00016786 | No
8/01/2019 | 21:26:04 | ST41 | Rural Long | Asset failure | HV | 101 | 131.495 | 0.096929 | 0.00073713 | No
8/01/2019 | 22:10:32 | VH45 | Rural Short | Unknown | Unknown | 3 | 288 | 0.0064369 | 2.235e-05 | No
8/01/2019 | 22:55:02 | SA18 | Urban | Asset failure | LV | 19.6666 | 42 | 0.0013205 | 3.144e-05 | No
8/01/2019 | 23:13:43 | VH22 | Rural Short | Asset failure | HV | 60 | 66 | 0.029503 | 0.00044701 | No
9/01/2019 | 01:56:45 | HH121G | Urban | Asset failure | LV | 78 | 135 | 0.016834 | 0.0001247 | No
9/01/2019 | 07:54:47 | KA06 | Rural Long | Planned |  | 28 | 371 | 0.075815 | 0.00020435 | No
9/01/2019 | 08:14:46 | GU31 | Rural Long | Planned |  | 29 | 275 | 0.058204 | 0.00021165 | No
9/01/2019 | 08:29:32 | MV62 | Rural Short | Planned |  | 7 | 53 | 0.002764 | 5.215e-05 | No
9/01/2019 | 08:38:24 | SG04 | Rural Short | Planned |  | 445 | 371.3528 | 1.2312 | 0.0033153 | No
9/01/2019 | 08:42:25 | PL21 | Rural Long | Planned |  | 1 | 76 | 0.00055467 | 7.3e-06 | No
9/01/2019 | 08:47:56 | MG32 | Rural Long | Planned |  | 9 | 303 | 0.019903 | 6.569e-05 | No
9/01/2019 | 08:51:35 | GA800A | Rural Short | Planned |  | 1 | 25 | 0.00018625 | 7.45e-06 | No
9/01/2019 | 09:01:53 | KI13 | Rural Long | Planned |  | 89 | 57.5955 | 0.037411 | 0.00064955 | No
9/01/2019 | 09:22:01 | GA29 | Rural Long | Planned |  | 71 | 325 | 0.16841 | 0.00051818 | No
9/01/2019 | 09:30:29 | GA800A | Rural Short | Planned |  | 2 | 40 | 0.00059601 | 1.49e-05 | No
9/01/2019 | 09:39:45 | MTB54 | Rural Long | Planned |  | 11 | 324 | 0.026011 | 8.028e-05 | No
9/01/2019 | 09:40:26 | ME231A | Urban | Planned |  | 65 | 246 | 0.025563 | 0.00010391 | No
9/01/2019 | 09:51:55 | CD23 | Rural Long | Planned |  | 3 | 278 | 0.0060868 | 2.19e-05 | No
9/01/2019 | 11:10:30 | GA800A | Rural Short | Planned |  | 2 | 11 | 0.0001639 | 1.49e-05 | No
9/01/2019 | 11:25:00 | LM52 | Rural Long | Planned |  | 36 | 255 | 0.066999 | 0.00026274 | No
9/01/2019 | 11:36:03 | PL14 | Urban | Planned |  | 2 | 61 | 0.00019504 | 3.2e-06 | No
9/01/2019 | 11:45:47 | GU21 | Rural Long | Asset failure | LV | 2 | 163 | 0.0023793 | 1.46e-05 | No
9/01/2019 | 11:52:16 | CL17 | Rural Long | Asset failure | LV | 1 | 523 | 0.003817 | 7.3e-06 | No
9/01/2019 | 12:39:25 | VH21 | Rural Short | Asset failure | LV | 1 | 126 | 0.00093872 | 7.45e-06 | No
9/01/2019 | 13:25:41 | EL19 | Urban | Unknown | Unknown | 2 | 20 | 6.395e-05 | 3.2e-06 | No
9/01/2019 | 15:41:31 | NL115C | Urban | Asset failure | LV | 1 | 159 | 0.00025419 | 1.6e-06 | No
9/01/2019 | 15:48:04 | ST41 | Rural Long | Asset failure | LV | 2 | 88 | 0.0012845 | 1.46e-05 | No
9/01/2019 | 16:48:27 | WK65 | Rural Short | Unknown | Unknown | 126 | 17 | 0.015958 | 0.00093872 | No
9/01/2019 | 18:07:51 | WHY06 | Urban | Asset failure | LV | 1 | 929 | 0.0014852 | 1.6e-06 | No
10/01/2019 | 00:10:17 | NL210D | Urban | Animal | Animal impact | 575 | 14.713 | 0.013525 | 0.00091924 | No
10/01/2019 | 00:33:04 | SM349H | Urban | Asset failure | LV | 34 | 137 | 0.0074466 | 5.435e-05 | No
10/01/2019 | 00:39:46 | MV12 | Urban | Planned |  | 81 | 250 | 0.032373 | 0.00012949 | No
10/01/2019 | 01:48:47 | HH409D | Urban | Unknown | Unknown | 175 | 255.5429 | 0.071493 | 0.00027977 | No
10/01/2019 | 08:00:47 | CN71 | Rural Long | Planned |  | 75 | 148 | 0.081012 | 0.00054738 | No
10/01/2019 | 08:22:27 | NA02 | Rural Long | Asset failure | LV | 1 | 247 | 0.0018027 | 7.3e-06 | No
10/01/2019 | 08:30:58 | YK03 | Rural Long | Planned |  | 617 | 191.8136 | 0.86375 | 0.0045031 | No
10/01/2019 | 08:45:32 | HK02 | Rural Long | Planned |  | 25 | 423 | 0.07718 | 0.00018246 | No
10/01/2019 | 08:56:45 | GA15 | Rural Short | Planned |  | 130 | 221 | 0.21404 | 0.00096852 | No
10/01/2019 | 09:05:58 | HH386B | Urban | Planned |  | 80 | 116 | 0.014836 | 0.00012789 | No
10/01/2019 | 09:08:51 | SG14 | Rural Short | Planned |  | 46 | 169 | 0.057917 | 0.00034271 | No
10/01/2019 | 09:10:00 | GA20 | Rural Long | Planned |  | 1 | 185 | 0.0013502 | 7.3e-06 | No
10/01/2019 | 09:30:39 | PL04 | Urban | Planned |  | 2 | 163 | 0.00052117 | 3.2e-06 | No
10/01/2019 | 09:35:30 | SA17 | Urban | Planned |  | 141 | 94 | 0.021189 | 0.00022541 | No
10/01/2019 | 09:43:14 | SM126B | Urban | Asset failure | LV | 1 | 717 | 0.0011462 | 1.6e-06 | No
10/01/2019 | 09:43:43 | VH18 | Rural Short | Planned |  | 1 | 101 | 0.00075247 | 7.45e-06 | No
10/01/2019 | 10:28:21 | PP09 | Rural Long | Planned |  | 23 | 246 | 0.041294 | 0.00016786 | No
10/01/2019 | 11:04:44 | LM56 | Rural Long | Planned |  | 12 | 60 | 0.0052548 | 8.758e-05 | No
10/01/2019 | 11:13:54 | CN25 | Rural Long | Unknown | Unknown | 25 | 138 | 0.025179 | 0.00018246 | No
10/01/2019 | 11:22:18 | NA02 | Rural Long | Asset failure | HV | 1 | 41 | 0.00029923 | 7.3e-06 | No
10/01/2019 | 11:40:11 | BT20 | Rural Long | Unknown | Unknown | 64 | 281 | 0.13125 | 0.00046709 | No
10/01/2019 | 11:46:58 | GA22 | Rural Short | Planned |  | 24 | 61 | 0.010907 | 0.0001788 | No
10/01/2019 | 12:08:06 | EL11 | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
10/01/2019 | 14:26:08 | GA47 | Rural Long | Third Party | Vehicle impact | 52 | 230.9808 | 0.08766 | 0.00037951 | No
10/01/2019 | 15:24:20 | AP355A | Urban | Third Party | Dig-in | 2003 | 61.0195 | 0.19539 | 0.0032021 | No
10/01/2019 | 15:41:43 | GA25 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 108 | 0.00080462 | 7.45e-06 | No
10/01/2019 | 18:23:23 | HH496A | Urban | Asset failure | HV | 585 | 239.6393 | 0.22412 | 0.00093522 | No
10/01/2019 | 18:23:23 | HH496A | Urban | Asset failure | HV | 216 | 2 | 0.00069063 | 0.00034531 | No
10/01/2019 | 18:47:34 | NL451A | Urban | Asset failure | LV | 11 | 374 | 0.0065769 | 1.759e-05 | No
10/01/2019 | 21:07:31 | NU05 | Rural Short | Unknown | Unknown | 3 | 259 | 0.0057888 | 2.235e-05 | No
10/01/2019 | 21:51:56 | HH145E | Urban | Asset failure | LV | 1 | 304 | 0.000486 | 1.6e-06 | No
10/01/2019 | 22:24:10 | SM126C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 239 | 0.00038208 | 1.6e-06 | No
10/01/2019 | 23:02:33 | AP125D | Urban | Unknown | Unknown | 32 | 303 | 0.015501 | 5.116e-05 | No
10/01/2019 | 23:53:18 | EL23 | Urban | Third Party | Other | 13 | 1 | 2.078e-05 | 2.078e-05 | No
11/01/2019 | 01:31:20 | BS0336 | Urban | Unknown | Unknown | 1 | 501 | 0.00080094 | 1.6e-06 | No
11/01/2019 | 02:13:16 | HH409D | Urban | Asset failure | LV | 26.6666 | 73 | 0.0031121 | 4.263e-05 | No
11/01/2019 | 04:55:58 | SG09 | Rural Short | Third Party | Other | 20 | 159 | 0.023691 | 0.000149 | No
11/01/2019 | 08:07:21 | AP424D | Urban | Planned |  | 101 | 17 | 0.0027449 | 0.00016147 | No
11/01/2019 | 08:10:10 | BT06 | Rural Long | Unknown | Unknown | 1 | 378 | 0.0027588 | 7.3e-06 | No
11/01/2019 | 08:27:25 | VH22 | Rural Short | Animal | Animal impact | 70 | 69 | 0.035984 | 0.00052151 | No
11/01/2019 | 08:42:55 | CN83 | Rural Long | Planned |  | 14 | 169 | 0.017268 | 0.00010218 | No
11/01/2019 | 08:46:25 | SA33 | Urban | Third Party | Vehicle impact | 83 | 320 | 0.042461 | 0.00013269 | No
11/01/2019 | 08:50:02 | GU13 | Rural Long | Planned |  | 29 | 21 | 0.0044447 | 0.00021165 | No
11/01/2019 | 08:52:16 | SB15 | Rural Long | Planned |  | 35 | 2 | 0.00051088 | 0.00025544 | No
11/01/2019 | 08:52:33 | SA36 | Urban | Asset failure | LV | 1 | 212 | 0.00033892 | 1.6e-06 | No
11/01/2019 | 08:53:24 | ST15 | Rural Short | Planned |  | 33 | 75 | 0.018439 | 0.00024585 | No
11/01/2019 | 08:54:29 | HH409D | Urban | Planned |  | 15 | 74 | 0.0017745 | 2.398e-05 | No
11/01/2019 | 09:06:15 | CD25 | Rural Long | Planned |  | 1 | 13 | 9.488e-05 | 7.3e-06 | No
11/01/2019 | 09:25:18 | MT15 | Rural Long | Planned |  | 2 | 57 | 0.00083201 | 1.46e-05 | No
11/01/2019 | 09:25:19 | MTB71 | Rural Short | Planned |  | 3 | 203 | 0.0045371 | 2.235e-05 | No
11/01/2019 | 09:25:41 | MI06 | Rural Long | Planned |  | 19 | 113 | 0.01567 | 0.00013867 | No
11/01/2019 | 09:39:02 | ST15 / ST16 | Rural Short | Planned |  | 67 | 163.8358 | 0.08178 | 0.00049916 | No
11/01/2019 | 10:00:21 | MTB53 | Rural Long | Planned |  | 2 | 52 | 0.00075903 | 1.46e-05 | No
11/01/2019 | 10:50:12 | SA34 | Urban | Third Party | Vehicle impact | 29 | 270 | 0.012518 | 4.636e-05 | No
11/01/2019 | 10:51:08 | HH177D | Urban | Planned |  | 123 | 48 | 0.0094386 | 0.00019664 | No
11/01/2019 | 10:58:08 | SM350E | Urban | Planned |  | 183 | 170.9891 | 0.050024 | 0.00029256 | No
11/01/2019 | 12:03:25 | GA01 | Urban | Other |  | 1 | 427 | 0.00068263 | 1.6e-06 | No
11/01/2019 | 12:06:24 | EL260A | Urban | Third Party | Vehicle impact | 22 | 292 | 0.01027 | 3.517e-05 | No
11/01/2019 | 13:08:03 | MTB21 | Rural Short | Unknown | Unknown | 15 | 38 | 0.0042466 | 0.00011175 | No
11/01/2019 | 13:56:22 | MB23 | Rural Short | Asset failure | LV | 27 | 94 | 0.018908 | 0.00020115 | No
11/01/2019 | 14:08:51 | SSD384 | Urban | Planned |  | 1 | 10069 | 0.016097 | 1.6e-06 | No
11/01/2019 | 14:35:37 | MI32 | Rural Long | Other |  | 13 | 170 | 0.016129 | 9.488e-05 | No
11/01/2019 | 15:39:45 | SA711C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 260 | 0.00041566 | 1.6e-06 | No
11/01/2019 | 16:27:18 | EL09 | Urban | Asset failure | LV | 1 | 255 | 0.00040766 | 1.6e-06 | No
11/01/2019 | 17:18:24 | NU21 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 2323 | 75.1098 | 1.2734 | 0.016954 | No
11/01/2019 | 17:18:36 | NU21 | Rural Long | Vegetation | Grow-in - NSP responsibility | 4 | 82 | 0.0023938 | 2.919e-05 | No
11/01/2019 | 18:19:46 | GU35 | Rural Long | Overloads |  | 4 | 277 | 0.0080866 | 2.919e-05 | No
11/01/2019 | 18:45:51 | AP529C | Urban | Asset failure | LV | 1 | 163 | 0.00026058 | 1.6e-06 | No
11/01/2019 | 18:48:36 | SA33 | Urban | Asset failure | LV | 26 | 206 | 0.0085625 | 4.157e-05 | No
11/01/2019 | 19:05:26 | SM349A | Urban | Asset failure | HV | 1679 | 54.1453 | 0.14534 | 0.0026842 | No
11/01/2019 | 19:10:51 | SM349C | Urban | Asset failure | LV | 22.3333 | 113 | 0.0040345 | 3.57e-05 | No
11/01/2019 | 19:47:30 | SM349E | Urban | Overloads |  | 25.6666 | 94 | 0.0038571 | 4.103e-05 | No
11/01/2019 | 20:17:26 | HH121C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2238 | 87.3177 | 0.31241 | 0.0035778 | No
11/01/2019 | 20:17:26 | HH121C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 0 | 1 | 0.0007242 | 0 | No
11/01/2019 | 20:51:55 | MV62 | Rural Short | Asset failure | LV | 5.6667 | 203 | 0.0085702 | 4.222e-05 | No
11/01/2019 | 23:09:00 | HH121D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21.6666 | 80 | 0.002771 | 3.464e-05 | No
12/01/2019 | 03:04:37 | HH409C | Urban | Weather |  | 1 | 95 | 0.00015187 | 1.6e-06 | No
12/01/2019 | 03:30:14 | HH145D | Urban | Asset failure | LV | 1 | 190 | 0.00030375 | 1.6e-06 | No
12/01/2019 | 03:32:30 | HH522B | Urban | Vegetation | Grow-in - NSP responsibility | 1.3333 | 121 | 0.00025792 | 2.13e-06 | No
12/01/2019 | 04:11:19 | SM411C | Urban | Vegetation | Grow-in - NSP responsibility | 18.3333 | 426 | 0.012486 | 2.931e-05 | No
12/01/2019 | 05:03:00 | SM126A | Urban | Unknown | Unknown | 24 | 437 | 0.016767 | 3.837e-05 | No
12/01/2019 | 05:16:04 | SM411A | Urban | Vegetation | Grow-in - NSP responsibility | 38 | 64 | 0.003888 | 6.075e-05 | No
12/01/2019 | 06:02:37 | SM216C | Urban | Unknown | Unknown | 36.3333 | 116 | 0.0067379 | 5.809e-05 | No
12/01/2019 | 06:49:23 | MT15 | Rural Long | Asset failure | LV | 1 | 201 | 0.001467 | 7.3e-06 | No
12/01/2019 | 07:10:23 | HH121A | Urban | Asset failure | LV | 23 | 369 | 0.013568 | 3.677e-05 | No
12/01/2019 | 07:12:49 | SSD338 | Rural Short | Planned |  | 6 | 584 | 0.026105 | 4.47e-05 | No
12/01/2019 | 07:17:46 | SM411A | Urban | Vegetation | Grow-in - NSP responsibility | 23 | 430 | 0.015811 | 3.677e-05 | No
12/01/2019 | 07:17:59 | HH522A | Urban | Unknown | Unknown | 35.3334 | 292 | 0.016494 | 5.649e-05 | No
12/01/2019 | 07:20:22 | HH148C | Urban | Asset failure | LV | 28 | 679 | 0.030394 | 4.476e-05 | No
12/01/2019 | 07:36:51 | HH121G | Urban | Unknown | Unknown | 33.6666 | 508 | 0.027342 | 5.382e-05 | No
12/01/2019 | 08:18:49 | G38 | Rural Long | Planned |  | 20 | 73 | 0.010656 | 0.00014597 | No
12/01/2019 | 08:25:22 | G16 | Rural Long | Planned |  | 12 | 68 | 0.0059554 | 8.758e-05 | No
12/01/2019 | 08:26:55 | SM350E | Urban | Asset failure | LV | 20.6666 | 436 | 0.014405 | 3.304e-05 | No
12/01/2019 | 08:31:07 | HH409D | Urban | Unknown | Unknown | 45.3334 | 425 | 0.030801 | 7.247e-05 | No
12/01/2019 | 09:12:46 | MV61 | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
12/01/2019 | 09:31:03 | BT26 | Rural Long | Overloads |  | 1 | 285 | 0.00208 | 7.3e-06 | No
12/01/2019 | 09:47:42 | BM44 | Rural Short | Asset failure | LV | 1 | 227 | 0.0016912 | 7.45e-06 | No
12/01/2019 | 11:45:34 | NL451E | Urban | Asset failure | LV | 37 | 121 | 0.0071573 | 5.915e-05 | No
12/01/2019 | 12:54:50 | MV63 | Rural Short | Asset failure | LV | 2 | 59 | 0.00087912 | 1.49e-05 | No
12/01/2019 | 13:09:37 | HH145A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 145 | 0.00023181 | 1.6e-06 | No
12/01/2019 | 14:02:52 | AP214D | Urban | Asset failure | LV | 1 | 327 | 0.00052277 | 1.6e-06 | No
12/01/2019 | 14:33:22 | ME116D | Urban | Vegetation | Grow-in - NSP responsibility | 1257 | 30 | 0.060286 | 0.0020095 | No
12/01/2019 | 16:05:22 | NL115F | Urban | Asset failure | LV | 1 | 536 | 0.00085689 | 1.6e-06 | No
12/01/2019 | 16:42:06 | M61 | Rural Long | Asset failure | HV | 17.3333 | 170 | 0.021506 | 0.0001265 | No
12/01/2019 | 18:15:47 | G02 | Rural Long | Overloads |  | 1 | 510 | 0.0037222 | 7.3e-06 | No
12/01/2019 | 21:08:35 | ST22 | Rural Short | Asset failure | LV | 1 | 165 | 0.0012293 | 7.45e-06 | No
12/01/2019 | 21:44:16 | SM172D | Urban | Asset failure | LV | 54.3333 | 65 | 0.005646 | 8.686e-05 | No
12/01/2019 | 21:50:54 | SM349A | Urban | Unknown | Unknown | 87 | 58 | 0.0080669 | 0.00013908 | No
12/01/2019 | 22:39:23 | G05 | Rural Long | Third Party | Vehicle impact | 612 | 598.3186 | 2.6724 | 0.0044666 | No
12/01/2019 | 22:39:23 | G05 | Rural Long | Third Party | Vehicle impact | 0 | 1 | 0.0010729 | 0 | No
13/01/2019 | 02:57:48 | ST43 | Rural Long | Animal | Animal impact | 2 | 523 | 0.0076341 | 1.46e-05 | No
13/01/2019 | 06:35:40 | SG12 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 541 | 134.3105 | 0.54134 | 0.0040305 | No
13/01/2019 | 08:18:55 | SM172F | Urban | Planned |  | 72 | 190 | 0.02187 | 0.0001151 | No
13/01/2019 | 08:41:50 | SA31 | Urban | Asset failure | LV | 8.3333 | 351 | 0.0046761 | 1.332e-05 | No
13/01/2019 | 09:24:30 | AP139A | Urban | Planned |  | 12 | 289 | 0.0055442 | 1.918e-05 | No
13/01/2019 | 10:22:41 | AP424B | Urban | Asset failure | LV | 8.6667 | 68 | 0.00094215 | 1.386e-05 | No
13/01/2019 | 11:05:23 | HH386D | Urban | Asset failure | LV | 1 | 246 | 0.00039327 | 1.6e-06 | No
13/01/2019 | 11:05:57 | PL20 | Rural Long | Asset failure | HV | 40 | 76 | 0.022187 | 0.00029193 | No
13/01/2019 | 11:12:12 | SA16 | Urban | Overloads |  | 2 | 299 | 0.00095601 | 3.2e-06 | No
13/01/2019 | 11:29:22 | EL20 | Urban | Asset failure | HV | 1 | 30 | 4.796e-05 | 1.6e-06 | No
13/01/2019 | 12:50:11 | HH121C | Urban | Asset failure | HV | 122 | 136 | 0.026525 | 0.00019504 | No
13/01/2019 | 13:04:40 | SA40 | Urban | Overloads |  | 1 | 241 | 0.00038528 | 1.6e-06 | No
13/01/2019 | 14:17:30 | SM216A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 389 | 0.00062188 | 1.6e-06 | No
13/01/2019 | 14:31:18 | VH11 | Urban | Third Party | Other | 1 | 262 | 0.00041885 | 1.6e-06 | No
13/01/2019 | 15:48:19 | SM410C | Urban | Weather |  | 11 | 445 | 0.0078255 | 1.759e-05 | No
13/01/2019 | 16:50:39 | EL20 | Urban | Asset failure | LV | 1 | 78 | 0.0001247 | 1.6e-06 | No
13/01/2019 | 17:31:33 | HH107B | Urban | Asset failure | LV | 25.3333 | 83 | 0.0033615 | 4.05e-05 | No
13/01/2019 | 20:39:43 | HH177D | Urban | Asset failure | LV | 1 | 174 | 0.00027817 | 1.6e-06 | No
13/01/2019 | 20:55:11 | BT15 | Rural Long | Asset failure | Distribution substation | 107 | 411.6542 | 0.32147 | 0.00078092 | No
14/01/2019 | 00:55:02 | YK14 | Rural Long | Weather |  | 43 | 545.7209 | 0.17126 | 0.00031383 | No
14/01/2019 | 03:29:20 | NL115E | Urban | Unknown | Unknown | 163 | 151 | 0.039348 | 0.00026058 | No
14/01/2019 | 05:52:27 | YK01 | Rural Long | Weather |  | 70 | 307.2286 | 0.15696 | 0.00051088 | No
14/01/2019 | 06:10:48 | MB17 | Rural Short | Animal | Animal impact | 1 | 126 | 0.00093872 | 7.45e-06 | No
14/01/2019 | 07:08:15 | SD49200 | Rural Long | Unknown | Unknown | 728 | 140 | 0.74385 | 0.0053132 | No
14/01/2019 | 07:43:14 | EL04 | Urban | Unknown | Unknown | 2 | 105 | 0.00033572 | 3.2e-06 | No
14/01/2019 | 08:00:57 | LX41 | Rural Short | Planned |  | 42 | 122 | 0.038175 | 0.00031291 | No
14/01/2019 | 08:30:44 | SG02 | Rural Short | Asset failure | LV | 12.6667 | 59 | 0.0055677 | 9.437e-05 | No
14/01/2019 | 08:35:39 | HH522A | Urban | Planned |  | 49 | 65 | 0.0050918 | 7.834e-05 | No
14/01/2019 | 08:42:56 | PL803A | Urban | Planned |  | 1 | 6046 | 0.0096656 | 1.6e-06 | No
14/01/2019 | 08:46:44 | KA13 | Rural Long | Planned |  | 56 | 30 | 0.012261 | 0.00040871 | No
14/01/2019 | 08:56:27 | PA07 | Rural Long | Asset failure | LV | 1 | 73 | 0.00053278 | 7.3e-06 | No
14/01/2019 | 09:02:15 | SG11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 417 | 0.0031067 | 7.45e-06 | No
14/01/2019 | 09:04:22 | NU32 | Rural Long | Unknown | Unknown | 1 | 62 | 0.0004525 | 7.3e-06 | No
14/01/2019 | 09:06:59 | NL21 | Urban | Planned |  | 8 | 105 | 0.0013429 | 1.279e-05 | No
14/01/2019 | 09:09:18 | SG02 | Rural Short | Planned |  | 86 | 227 | 0.14544 | 0.00064071 | No
14/01/2019 | 09:19:03 | SM349F | Urban | Asset failure | LV | 38 | 86 | 0.0052245 | 6.075e-05 | No
14/01/2019 | 09:26:18 | ME427A / AP355D | Urban | Planned |  | 2 | 6114 | 0.019549 | 3.2e-06 | No
14/01/2019 | 09:49:29 | MV52 | Rural Short | Planned |  | 73 | 270 | 0.14684 | 0.00054386 | No
14/01/2019 | 09:57:53 | VH33 | Rural Short | Planned |  | 25 | 221 | 0.041162 | 0.00018625 | No
14/01/2019 | 13:09:55 | SM349F | Urban | Overloads |  | 1 | 202 | 0.00032293 | 1.6e-06 | No
14/01/2019 | 13:25:06 | ME200G | Urban | Overloads |  | 1 | 276 | 0.00044123 | 1.6e-06 | No
14/01/2019 | 15:02:56 | SD37102 | Rural Long | Asset failure | Subtransmission | 18 | 35 | 0.0045979 | 0.00013137 | No
14/01/2019 | 16:08:43 | HH121G | Urban | Unknown | Unknown | 38 | 96 | 0.005832 | 6.075e-05 | No
14/01/2019 | 17:04:16 | HH386A | Urban | Asset failure | LV | 27.3333 | 72 | 0.0031462 | 4.37e-05 | No
14/01/2019 | 17:05:26 | BT01 | Rural Long | Overloads |  | 1 | 303 | 0.0022114 | 7.3e-06 | No
14/01/2019 | 17:24:28 | MV13 | Rural Short | Overloads |  | 1 | 267 | 0.0019892 | 7.45e-06 | No
14/01/2019 | 17:40:01 | HH341H | Urban | Unknown | Unknown | 42.3333 | 59 | 0.003993 | 6.768e-05 | No
14/01/2019 | 18:57:00 | NL451C | Urban | Asset failure | LV | 19 | 92 | 0.0027945 | 3.037e-05 | No
14/01/2019 | 19:01:27 | HH102B | Urban | Unknown | Unknown | 20.3333 | 119 | 0.0038683 | 3.251e-05 | No
14/01/2019 | 20:22:17 | HH130A | Urban | Unknown | Unknown | 26 | 67 | 0.0027849 | 4.157e-05 | No
14/01/2019 | 20:35:20 | BM21 | Rural Short | Asset failure | LV | 21.3333 | 82 | 0.013033 | 0.00015894 | No
14/01/2019 | 21:04:01 | SA18 | Urban | Overloads |  | 1 | 110 | 0.00017585 | 1.6e-06 | No
14/01/2019 | 21:27:56 | SM179D | Urban | Asset failure | HV | 117 | 47 | 0.0087911 | 0.00018704 | No
14/01/2019 | 22:10:33 | MG37 | Rural Long | Weather |  | 85 | 28 | 0.01737 | 0.00062036 | No
14/01/2019 | 22:35:40 | HH177G | Urban | Other |  | 1 | 108 | 0.00017266 | 1.6e-06 | No
15/01/2019 | 00:10:11 | BM55 | Rural Short | Unknown | Unknown | 4.3333 | 592 | 0.019112 | 3.228e-05 | No
15/01/2019 | 00:28:40 | SA35 | Urban | Asset failure | LV | 1 | 210 | 0.00033572 | 1.6e-06 | No
15/01/2019 | 00:43:10 | HH130B | Urban | Asset failure | LV | 1 | 123 | 0.00019664 | 1.6e-06 | No
15/01/2019 | 02:14:07 | MV34 | Rural Short | Overloads |  | 11.6667 | 429 | 0.037288 | 8.692e-05 | No
15/01/2019 | 03:20:14 | HH102B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 104 | 0.00016626 | 1.6e-06 | No
15/01/2019 | 04:11:19 | SA35 | Urban | Asset failure | LV | 1 | 263 | 0.00042045 | 1.6e-06 | No
15/01/2019 | 04:39:56 | NL234A | Urban | Asset failure | LV | 17.6666 | 215 | 0.0060723 | 2.824e-05 | No
15/01/2019 | 07:14:20 | BS0336 | Urban | Unknown | Unknown | 1 | 181 | 0.00028936 | 1.6e-06 | No
15/01/2019 | 08:16:54 | CN02 | Rural Long | Planned |  | 19 | 130 | 0.018027 | 0.00013867 | No
15/01/2019 | 08:34:17 | KI13 | Rural Long | Planned |  | 65 | 262 | 0.12429 | 0.00047439 | No
15/01/2019 | 08:41:41 | MV53 | Rural Short | Planned |  | 58 | 232 | 0.10025 | 0.00043211 | No
15/01/2019 | 08:45:52 | R02 | Rural Long | Asset failure | LV | 1 | 319 | 0.0023282 | 7.3e-06 | No
15/01/2019 | 09:10:30 | M44 | Rural Long | Planned |  | 1 | 39 | 0.00028464 | 7.3e-06 | No
15/01/2019 | 09:12:44 | HH386B | Urban | Asset failure | LV | 1 | 118 | 0.00018864 | 1.6e-06 | No
15/01/2019 | 10:15:22 | YK28 | Rural Long | Unknown | Unknown | 57 | 253 | 0.10525 | 0.00041601 | No
15/01/2019 | 10:35:27 | VH23 | Rural Short | Asset failure | LV | 1 | 110 | 0.00081952 | 7.45e-06 | No
15/01/2019 | 10:48:13 | EL10 | Urban | Overloads |  | 1 | 67 | 0.00010711 | 1.6e-06 | No
15/01/2019 | 12:00:27 | PA07 | Rural Long | Asset failure | LV | 1 | 85 | 0.00062036 | 7.3e-06 | No
15/01/2019 | 12:56:34 | EL16 | Urban | Asset failure | LV | 2 | 72 | 0.00023021 | 3.2e-06 | No
15/01/2019 | 13:37:14 | NL451C | Urban | Overloads |  | 1 | 74 | 0.0001183 | 1.6e-06 | No
15/01/2019 | 13:53:59 | SD49500 | Rural Long | Unknown | Unknown | 1 | 63 | 0.0004598 | 7.3e-06 | No
15/01/2019 | 13:54:26 | HH496F | Urban | Asset failure | HV | 2839 | 21.572 | 0.097908 | 0.0045386 | No
15/01/2019 | 13:54:26 | HH496F | Urban | Asset failure | HV | 0 | 1 | 0.00021103 | 0 | No
15/01/2019 | 15:10:05 | SM374E | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
15/01/2019 | 15:25:36 | NL234C | Urban | Asset failure | LV | 35.3333 | 93 | 0.0052532 | 5.649e-05 | No
15/01/2019 | 17:05:09 | EL15 | Urban | Asset failure | HV | 297 | 53.0572 | 0.025192 | 0.00047481 | No
15/01/2019 | 17:11:39 | NL451C | Urban | Asset failure | LV | 1 | 106 | 0.00016946 | 1.6e-06 | No
15/01/2019 | 17:28:29 | HH107B | Urban | Asset failure | LV | 23.6666 | 56 | 0.0021188 | 3.784e-05 | No
15/01/2019 | 17:34:29 | SA17 | Urban | Asset failure | LV | 46 | 335 | 0.024636 | 7.354e-05 | No
15/01/2019 | 17:52:01 | SM126B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 204 | 0.00032613 | 1.6e-06 | No
15/01/2019 | 18:15:59 | HH121D | Urban | Overloads |  | 27.3333 | 96 | 0.0041949 | 4.37e-05 | No
15/01/2019 | 18:32:57 | AP424E | Urban | Asset failure | LV | 18.3333 | 127 | 0.0037222 | 2.931e-05 | No
15/01/2019 | 18:44:20 | SA744D | Urban | Asset failure | LV | 19.6666 | 311 | 0.009778 | 3.144e-05 | No
15/01/2019 | 18:51:20 | ME427F | Urban | Asset failure | LV | 25.6666 | 57 | 0.0023389 | 4.103e-05 | No
15/01/2019 | 18:57:56 | HH432C | Urban | Asset failure | LV | 34.6666 | 141 | 0.0078143 | 5.542e-05 | No
15/01/2019 | 19:06:52 | SA18 | Urban | Unknown | Unknown | 23.6666 | 361 | 0.013659 | 3.784e-05 | No
15/01/2019 | 19:31:32 | SA711C | Urban | Unknown | Unknown | 33.3333 | 304 | 0.0162 | 5.329e-05 | No
15/01/2019 | 20:31:54 | AP214B | Urban | Asset failure | LV | 21 | 98 | 0.0032901 | 3.357e-05 | No
15/01/2019 | 20:43:34 | HH409D | Urban | Unknown | Unknown | 26 | 71 | 0.0029512 | 4.157e-05 | No
15/01/2019 | 20:50:41 | SM402C | Urban | Asset failure | LV | 2 | 177 | 0.00056593 | 3.2e-06 | No
15/01/2019 | 21:50:11 | NL511A | Urban | Asset failure | LV | 29.3333 | 65 | 0.0030481 | 4.689e-05 | No
15/01/2019 | 22:21:14 | MI03 | Rural Long | Animal | Animal impact | 101 | 185.0198 | 0.13638 | 0.00073713 | No
15/01/2019 | 22:21:14 | MI03 | Rural Long | Animal | Animal impact | 0 | 9 | 0.00065685 | 0 | No
15/01/2019 | 23:41:20 | W15 | Rural Long | Asset failure | HV | 51 | 122.2941 | 0.04552 | 0.00037222 | No
16/01/2019 | 00:51:34 | HH102C | Urban | Unknown | Unknown | 126 | 161 | 0.032431 | 0.00020143 | No
16/01/2019 | 02:03:28 | AP424E | Urban | Asset failure | LV | 1 | 123 | 0.00019664 | 1.6e-06 | No
16/01/2019 | 02:45:18 | SM126C | Urban | Animal | Animal impact | 53 | 77 | 0.0065242 | 8.473e-05 | No
16/01/2019 | 03:44:55 | EL01R | Urban | Unknown | Unknown | 1 | 118 | 0.00018864 | 1.6e-06 | No
16/01/2019 | 03:57:37 | WHY17 | Rural Short | Weather |  | 52 | 204 | 0.079031 | 0.00038741 | No
16/01/2019 | 08:22:24 | CN25 | Rural Long | Planned |  | 35 | 318 | 0.08123 | 0.00025544 | No
16/01/2019 | 08:32:18 | M21 | Rural Long | Overloads |  | 1.6667 | 167 | 0.0020314 | 1.216e-05 | No
16/01/2019 | 08:33:41 | GA800A | Rural Short | Planned |  | 43 | 31 | 0.0099311 | 0.00032036 | No
16/01/2019 | 08:37:33 | MB16 | Rural Short | Planned |  | 1 | 16 | 0.0001192 | 7.45e-06 | No
16/01/2019 | 08:42:21 | MG43 | Rural Short | Overloads |  | 1 | 174 | 0.0012963 | 7.45e-06 | No
16/01/2019 | 08:48:05 | AP125D | Urban | Planned |  | 84 | 97 | 0.013026 | 0.00013429 | No
16/01/2019 | 09:04:44 | MB123 | Rural Long | Planned |  | 75 | 225 | 0.12316 | 0.00054738 | No
16/01/2019 | 09:04:57 | HH121D | Urban | Asset failure | LV | 2 | 318 | 0.0010168 | 3.2e-06 | No
16/01/2019 | 09:05:09 | ST34 | Rural Long | Planned |  | 54 | 204 | 0.080398 | 0.00039411 | No
16/01/2019 | 09:07:25 | KI13 | Rural Long | Planned |  | 18 | 203 | 0.026668 | 0.00013137 | No
16/01/2019 | 09:23:51 | AP132A | Urban | Unknown | Unknown | 1 | 80 | 0.00012789 | 1.6e-06 | No
16/01/2019 | 09:41:18 | G18 | Rural Long | Planned |  | 1 | 68 | 0.00049629 | 7.3e-06 | No
16/01/2019 | 09:42:17 | AP510E | Urban | Planned |  | 1 | 319 | 0.00050998 | 1.6e-06 | No
16/01/2019 | 10:33:40 | GU43 | Rural Long | Unknown | Unknown | 1 | 34 | 0.00024814 | 7.3e-06 | No
16/01/2019 | 10:59:51 | SA31 | Urban | Overloads |  | 1 | 80 | 0.00012789 | 1.6e-06 | No
16/01/2019 | 11:12:51 | SM216B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2784 | 82 | 0.36496 | 0.0044507 | No
16/01/2019 | 12:30:36 | CM35 | Rural Long | Unknown | Unknown | 1 | 109 | 0.00079552 | 7.3e-06 | No
16/01/2019 | 14:34:12 | HH177B | Urban | Asset failure | LV | 1 | 348 | 0.00055634 | 1.6e-06 | No
16/01/2019 | 15:03:25 | NU11 | Rural Long | Unknown | Unknown | 1 | 28 | 0.00020435 | 7.3e-06 | No
16/01/2019 | 15:37:24 | HH121C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 116 | 68 | 0.01261 | 0.00018545 | No
16/01/2019 | 15:50:44 | MV64 | Urban | Overloads |  | 22 | 51 | 0.0017937 | 3.517e-05 | No
16/01/2019 | 16:14:10 | HH409F | Urban | Asset failure | LV | 1 | 366 | 0.00058512 | 1.6e-06 | No
16/01/2019 | 16:23:43 | SM216A | Urban | Asset failure | LV | 1 | 97 | 0.00015507 | 1.6e-06 | No
16/01/2019 | 16:30:04 | CM02 | Rural Long | Asset failure | LV | 1 | 150 | 0.0010948 | 7.3e-06 | No
16/01/2019 | 16:58:41 | CN42 | Rural Long | Asset failure | LV | 7 | 23 | 0.001175 | 5.109e-05 | No
16/01/2019 | 17:27:07 | NL210F | Urban | Asset failure | LV | 1 | 188 | 0.00030055 | 1.6e-06 | No
16/01/2019 | 17:29:41 | SM374B | Urban | Asset failure | LV | 1 | 139 | 0.00022222 | 1.6e-06 | No
16/01/2019 | 17:48:55 | MT03 | Rural Long | Asset failure | LV | 1 | 197 | 0.0014378 | 7.3e-06 | No
16/01/2019 | 18:46:28 | M13 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 63 | 0.0004598 | 7.3e-06 | No
16/01/2019 | 19:18:52 | M21 | Rural Long | Asset failure | LV | 1 | 140 | 0.0010218 | 7.3e-06 | No
16/01/2019 | 20:31:40 | AP355A | Urban | Overloads |  | 1 | 145 | 0.00023181 | 1.6e-06 | No
16/01/2019 | 20:45:12 | AP125B | Urban | Unknown | Unknown | 5 | 99 | 0.00079134 | 7.99e-06 | No
16/01/2019 | 20:51:21 | AP529C | Urban | Asset failure | LV | 22.3333 | 64 | 0.002285 | 3.57e-05 | No
17/01/2019 | 00:57:34 | HH107A | Urban | Vegetation | Grow-in - NSP responsibility | 43 | 50 | 0.0034371 | 6.874e-05 | No
17/01/2019 | 01:06:36 | PL04 | Urban | Weather |  | 34 | 220 | 0.011958 | 5.435e-05 | No
17/01/2019 | 02:06:08 | WHY17 | Rural Short | Planned |  | 52 | 462 | 0.17898 | 0.00038741 | No
17/01/2019 | 04:01:33 | MTB32 | Rural Long | Unknown | Unknown | 1 | 249 | 0.0018173 | 7.3e-06 | No
17/01/2019 | 06:57:58 | MTB52 | Rural Long | Unknown | Unknown | 2 | 17 | 0.00024814 | 1.46e-05 | No
17/01/2019 | 07:00:00 | CBD103C | Urban | Vegetation | Grow-in - NSP responsibility | 23.6666 | 159 | 0.0060158 | 3.784e-05 | No
17/01/2019 | 07:05:47 | SG10 | Rural Short | Asset failure | LV | 1 | 93 | 0.00069286 | 7.45e-06 | No
17/01/2019 | 07:54:12 | CV02 | Rural Long | Animal | Animal impact | 42 | 241 | 0.073874 | 0.00030653 | No
17/01/2019 | 08:01:22 | BT01 | Rural Long | Animal | Animal impact | 162 | 100 | 0.11823 | 0.0011823 | No
17/01/2019 | 08:11:36 | LM62 | Rural Long | Planned |  | 8 | 113 | 0.0065977 | 5.839e-05 | No
17/01/2019 | 08:30:27 | CN53 | Rural Long | Planned |  | 29 | 280 | 0.059263 | 0.00021165 | No
17/01/2019 | 08:48:44 | GA800A | Rural Short | Planned |  | 1 | 14 | 0.0001043 | 7.45e-06 | No
17/01/2019 | 08:55:10 | YK04 | Rural Short | Asset failure | HV | 13 | 77 | 0.0074576 | 9.685e-05 | No
17/01/2019 | 09:03:59 | SA520E | Urban | Planned |  | 15 | 38 | 0.00091124 | 2.398e-05 | No
17/01/2019 | 09:17:39 | VH51 | Rural Short | Planned |  | 12 | 826 | 0.073846 | 8.94e-05 | No
17/01/2019 | 09:30:15 | WK72 | Rural Short | Planned |  | 1 | 75 | 0.00055876 | 7.45e-06 | No
17/01/2019 | 09:36:36 | SA520J | Urban | Planned |  | 2 | 76 | 0.000243 | 3.2e-06 | No
17/01/2019 | 09:39:23 | HH130D | Urban | Planned |  | 48 | 82 | 0.0062924 | 7.674e-05 | No
17/01/2019 | 09:44:05 | SG13 | Rural Short | Planned |  | 482 | 213 | 0.76488 | 0.003591 | No
17/01/2019 | 10:00:58 | AP529C | Urban | Planned |  | 169 | 86 | 0.023235 | 0.00027018 | No
17/01/2019 | 10:15:33 | GA800A | Rural Short | Planned |  | 5 | 18 | 0.00067051 | 3.725e-05 | No
17/01/2019 | 10:58:48 | NU04 | Rural Short | Unknown | Unknown | 2.3333 | 136 | 0.0023642 | 1.738e-05 | No
17/01/2019 | 11:29:24 | MI01 | Rural Long | Asset failure | HV | 2 | 32 | 0.00046709 | 1.46e-05 | No
17/01/2019 | 11:42:44 | BT02 | Rural Long | Planned |  | 2 | 130 | 0.0018976 | 1.46e-05 | No
17/01/2019 | 11:53:38 | MG05 | Rural Long | Asset failure | LV | 2 | 168 | 0.0024522 | 1.46e-05 | No
17/01/2019 | 12:12:17 | GU41 | Rural Long | Asset failure | LV | 1.6667 | 159 | 0.0019341 | 1.216e-05 | No
17/01/2019 | 12:18:26 | GA800A | Rural Short | Planned |  | 5 | 16 | 0.00059601 | 3.725e-05 | No
17/01/2019 | 13:00:15 | ME347G | Urban | Asset failure | LV | 8 | 309 | 0.0039519 | 1.279e-05 | No
17/01/2019 | 13:00:53 | HH118D | Urban | Unknown | Unknown | 15.6667 | 49 | 0.0012273 | 2.505e-05 | No
17/01/2019 | 14:15:35 | HH386B | Urban | Asset failure | LV | 1 | 584 | 0.00093363 | 1.6e-06 | No
17/01/2019 | 14:30:51 | G13 | Rural Long | Asset failure | HV | 15 | 509 | 0.055723 | 0.00010948 | No
17/01/2019 | 14:35:45 | MB34 | Rural Long | Asset failure | LV | 1 | 522 | 0.0038097 | 7.3e-06 | No
17/01/2019 | 15:34:08 | SG14 | Rural Short | Asset failure | LV | 1 | 147 | 0.0010952 | 7.45e-06 | No
17/01/2019 | 15:38:43 | SA17 | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
17/01/2019 | 15:42:32 | SD49100 | Rural Long | Unknown | Unknown | 2 | 145 | 0.0021165 | 1.46e-05 | No
17/01/2019 | 16:12:52 | NL451C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 33.3333 | 137 | 0.0073006 | 5.329e-05 | No
17/01/2019 | 17:36:02 | SA16 | Urban | Overloads |  | 1 | 172 | 0.00027497 | 1.6e-06 | No
17/01/2019 | 17:49:23 | CD16 | Rural Short | Asset failure | HV | 265 | 90.7057 | 0.17908 | 0.0019743 | No
17/01/2019 | 17:55:07 | KA22 | Rural Long | Asset failure | LV | 1 | 230 | 0.0016786 | 7.3e-06 | No
17/01/2019 | 17:57:24 | SA20 | Urban | Animal | Animal impact | 2270 | 70 | 0.25403 | 0.003629 | No
17/01/2019 | 19:55:20 | SA19 | Urban | Asset failure | LV | 14.3333 | 161 | 0.0036892 | 2.291e-05 | No
17/01/2019 | 20:14:02 | HH177F | Urban | Asset failure | LV | 25 | 520 | 0.020783 | 3.997e-05 | No
17/01/2019 | 20:36:41 | MG46 | Rural Short | Weather |  | 14 | 133 | 0.013872 | 0.0001043 | No
17/01/2019 | 20:43:19 | MG13 | Rural Short | Weather |  | 1 | 373 | 0.0027789 | 7.45e-06 | No
17/01/2019 | 21:44:21 | MI20 | Rural Long | Weather |  | 5 | 146 | 0.0053278 | 3.649e-05 | No
17/01/2019 | 23:06:01 | MG12 | Rural Long | Weather |  | 2 | 131 | 0.0019122 | 1.46e-05 | No
18/01/2019 | 00:21:14 | W04 | Rural Long | Weather |  | 262 | 270.855 | 0.51792 | 0.0019122 | No
18/01/2019 | 03:22:04 | SD35300 | Rural Long | Asset failure | Subtransmission | 1429 | 209.6921 | 2.1869 | 0.010429 | No
18/01/2019 | 06:07:30 | HH121B | Urban | Planned |  | 59 | 54 | 0.0050934 | 9.432e-05 | No
18/01/2019 | 06:47:52 | CV757A | Rural Long | Weather |  | 251 | 266.6056 | 0.48839 | 0.0018319 | No
18/01/2019 | 06:50:25 | EL02 | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
18/01/2019 | 06:51:30 | SD35100 | Rural Long | Animal | Animal impact | 68 | 136 | 0.067495 | 0.00049629 | No
18/01/2019 | 08:07:31 | SB02 | Rural Long | Unknown | Unknown | 314 | 113.1338 | 0.25927 | 0.0022917 | No
18/01/2019 | 08:08:46 | CN24 | Rural Long | Planned |  | 11 | 288 | 0.023121 | 8.028e-05 | No
18/01/2019 | 08:10:52 | HH522A | Urban | Asset failure | LV | 1 | 321 | 0.00051317 | 1.6e-06 | No
18/01/2019 | 08:12:43 | PA05 | Rural Long | Planned |  | 301 | 341.0399 | 0.7492 | 0.0021968 | No
18/01/2019 | 08:24:26 | CN25 | Rural Long | Unknown | Unknown | 51 | 288 | 0.1072 | 0.00037222 | No
18/01/2019 | 08:33:28 | HH121F | Urban | Planned |  | 111 | 56 | 0.0099374 | 0.00017745 | No
18/01/2019 | 08:42:15 | GU42 | Rural Long | Planned |  | 14 | 81 | 0.0082763 | 0.00010218 | No
18/01/2019 | 08:43:40 | HH102A | Urban | Planned |  | 61 | 322 | 0.031401 | 9.752e-05 | No
18/01/2019 | 08:51:53 | MG12 | Rural Long | Unknown | Unknown | 1 | 269 | 0.0019633 | 7.3e-06 | No
18/01/2019 | 09:00:14 | MTB54 | Rural Long | Planned |  | 25 | 301 | 0.05492 | 0.00018246 | No
18/01/2019 | 09:00:58 | MV22 | Rural Short | Planned |  | 39 | 471 | 0.13685 | 0.00029056 | No
18/01/2019 | 09:01:58 | MB71 | Rural Long | Planned |  | 12 | 202 | 0.017691 | 8.758e-05 | No
18/01/2019 | 09:02:43 | GA27 | Rural Long | Planned |  | 94 | 343 | 0.23531 | 0.00068604 | No
18/01/2019 | 09:04:21 | HH121F | Urban | Planned |  | 2 | 80 | 0.00025579 | 3.2e-06 | No
18/01/2019 | 09:10:08 | AP425C | Urban | Asset failure | LV | 50 | 46 | 0.003677 | 7.993e-05 | No
18/01/2019 | 09:12:46 | CN73 | Rural Long | Planned |  | 27 | 203 | 0.040002 | 0.00019706 | No
18/01/2019 | 09:13:36 | VH22 | Rural Short | Planned |  | 1 | 114 | 0.00084932 | 7.45e-06 | No
18/01/2019 | 09:33:17 | BT03 | Rural Long | Asset failure | LV | 1 | 139 | 0.0010145 | 7.3e-06 | No
18/01/2019 | 09:37:03 | AP529A | Urban | Planned |  | 1 | 95 | 0.00015187 | 1.6e-06 | No
18/01/2019 | 09:38:53 | BT02 | Rural Long | Planned |  | 3 | 4 | 8.758e-05 | 2.19e-05 | No
18/01/2019 | 09:39:09 | SM349A | Urban | Planned |  | 3 | 288 | 0.0013813 | 4.8e-06 | No
18/01/2019 | 09:41:00 | SA18 | Urban | Planned |  | 89 | 148 | 0.021058 | 0.00014228 | No
18/01/2019 | 09:50:38 | AP373B | Urban | Planned |  | 6 | 118 | 0.0011319 | 9.59e-06 | No
18/01/2019 | 09:53:37 | AP529E | Urban | Planned |  | 214 | 181 | 0.061923 | 0.00034212 | No
18/01/2019 | 09:57:09 | ME200D | Urban | Other |  | 1 | 600 | 0.0009592 | 1.6e-06 | No
18/01/2019 | 10:00:18 | GA40 | Rural Short | Planned |  | 50 | 256 | 0.095362 | 0.00037251 | No
18/01/2019 | 10:38:57 | BS0336 | Urban | Planned |  | 1 | 2975 | 0.0047561 | 1.6e-06 | No
18/01/2019 | 11:54:41 | CD01 | Rural Short | Planned |  | 16 | 168 | 0.020026 | 0.0001192 | No
18/01/2019 | 13:18:47 | KA02 | Rural Short | Unknown | Unknown | 805 | 53.4646 | 0.32065 | 0.0059974 | No
18/01/2019 | 13:32:22 | MI17 | Rural Long | Asset failure | HV | 4 | 244 | 0.0071232 | 2.919e-05 | No
18/01/2019 | 13:52:31 | WK41 | Rural Short | Asset failure | LV | 1 | 74 | 0.00055131 | 7.45e-06 | No
18/01/2019 | 15:04:33 | HH341E | Urban | Overloads |  | 5 | 96 | 0.00076736 | 7.99e-06 | No
18/01/2019 | 17:55:17 | SM410B | Urban | Other |  | 1 | 155 | 0.00024779 | 1.6e-06 | No
18/01/2019 | 18:33:18 | AP355B | Urban | Unknown | Unknown | 21 | 30 | 0.0010072 | 3.357e-05 | No
18/01/2019 | 19:05:32 | AP425C | Urban | Asset failure | LV | 1 | 196 | 0.00031334 | 1.6e-06 | No
18/01/2019 | 21:14:25 | HH177B | Urban | Asset failure | LV | 1 | 175 | 0.00027977 | 1.6e-06 | No
19/01/2019 | 06:33:25 | AP125D | Urban | Asset failure | LV | 1 | 310 | 0.00049559 | 1.6e-06 | No
19/01/2019 | 08:05:25 | MI21 | Rural Long | Asset failure | LV | 1 | 211 | 0.0015399 | 7.3e-06 | No
19/01/2019 | 08:24:43 | AP529D | Urban | Asset failure | LV | 1 | 165 | 0.00026378 | 1.6e-06 | No
19/01/2019 | 12:20:16 | NL544B | Urban | Asset failure | LV | 1 | 191 | 0.00030535 | 1.6e-06 | No
19/01/2019 | 13:28:43 | AP149B | Urban | Asset failure | LV | 1 | 253 | 0.00040446 | 1.6e-06 | No
19/01/2019 | 14:38:42 | SB17 | Rural Long | Unknown | Unknown | 73 | 481 | 0.25627 | 0.00053278 | No
19/01/2019 | 14:41:38 | SB02 | Rural Long | Asset failure | HV | 241 | 246.2946 | 0.43321 | 0.0017589 | No
19/01/2019 | 14:58:43 | SM410D | Urban | Animal | Animal impact | 14 | 113 | 0.0025291 | 2.238e-05 | No
19/01/2019 | 15:04:27 | AP227A | Urban | Asset failure | LV | 18.3333 | 202 | 0.0059204 | 2.931e-05 | No
19/01/2019 | 15:19:30 | EL10 | Urban | Asset failure | LV | 10.6667 | 109 | 0.0018587 | 1.705e-05 | No
19/01/2019 | 18:28:14 | ST34 | Rural Long | Asset failure | HV | 545 | 116.2367 | 0.46234 | 0.0039776 | No
19/01/2019 | 19:14:28 | AP125D | Urban | Asset failure | LV | 1 | 177 | 0.00028297 | 1.6e-06 | No
19/01/2019 | 20:26:59 | SSD165 | Urban | Planned |  | 1 | 36 | 5.755e-05 | 1.6e-06 | No
19/01/2019 | 21:46:44 | MI01 | Rural Long | Animal | Animal impact | 473 | 84 | 0.28998 | 0.0034521 | No
20/01/2019 | 02:14:02 | AP355D | Urban | Asset failure | HV | 323 | 333.0372 | 0.17197 | 0.00051637 | No
20/01/2019 | 06:23:38 | SM350E | Urban | Asset failure | LV | 26.6666 | 134 | 0.0057126 | 4.263e-05 | No
20/01/2019 | 06:38:55 | HH148D | Urban | Unknown | Unknown | 889 | 2.4274 | 0.0034499 | 0.0014212 | No
20/01/2019 | 07:52:31 | CD23 | Rural Long | Unknown | Unknown | 37 | 251.0541 | 0.067794 | 0.00027004 | No
20/01/2019 | 08:21:34 | NU29 | Rural Long | Planned |  | 16 | 374 | 0.043673 | 0.00011677 | No
20/01/2019 | 08:34:44 | MG41 | Urban | Planned |  | 6 | 121 | 0.0011606 | 9.59e-06 | No
20/01/2019 | 08:55:07 | NU21 | Rural Long | Planned |  | 1 | 467 | 0.0034083 | 7.3e-06 | No
20/01/2019 | 08:58:37 | SM172B | Urban | Planned |  | 66 | 107.6667 | 0.01136 | 0.00010551 | No
20/01/2019 | 09:01:15 | NL210C | Urban | Asset failure | LV | 1 | 369 | 0.00058991 | 1.6e-06 | No
20/01/2019 | 09:23:08 | AP355B | Urban | Planned |  | 4 | 313 | 0.0020015 | 6.39e-06 | No
20/01/2019 | 09:26:50 | AP214C | Urban | Planned |  | 90 | 291 | 0.041869 | 0.00014388 | No
20/01/2019 | 11:28:39 | SA36 | Urban | Unknown | Unknown | 14.6667 | 40 | 0.00093789 | 2.345e-05 | No
20/01/2019 | 12:13:41 | ME427A | Urban | Overloads |  | 2 | 177 | 0.00056593 | 3.2e-06 | No
20/01/2019 | 13:15:43 | VH23 | Rural Short | Asset failure | LV | 1 | 330 | 0.0024585 | 7.45e-06 | No
20/01/2019 | 14:58:38 | WHY13 | Urban | Asset failure | HV | 297 | 361.5589 | 0.17167 | 0.00047481 | No
20/01/2019 | 16:03:56 | EL07 | Urban | Third Party | Vehicle impact | 2 | 94 | 0.00030055 | 3.2e-06 | No
20/01/2019 | 17:27:05 | CD02 | Rural Long | Asset failure | HV | 129 | 194.5891 | 0.1832 | 0.00094149 | No
20/01/2019 | 20:30:19 | NA62 | Rural Long | Asset failure | HV | 31 | 166.0645 | 0.037572 | 0.00022625 | No
20/01/2019 | 20:45:41 | HH121F | Urban | Overloads |  | 1 | 123 | 0.00019664 | 1.6e-06 | No
21/01/2019 | 01:10:31 | CN25 | Rural Long | Unknown | Unknown | 51 | 535 | 0.19914 | 0.00037222 | No
21/01/2019 | 02:36:25 | BM53 | Rural Short | Asset failure | LV | 13 | 212 | 0.020533 | 9.685e-05 | No
21/01/2019 | 03:01:11 | WHY13 | Urban | Asset failure | Distribution substation | 41 | 759 | 0.049749 | 6.555e-05 | No
21/01/2019 | 07:42:20 | HH145B | Urban | Overloads |  | 1 | 61 | 9.752e-05 | 1.6e-06 | No
21/01/2019 | 08:29:58 | ST24 | Rural Short | Planned |  | 182 | 233.2692 | 0.3163 | 0.0013559 | No
21/01/2019 | 08:48:15 | SD38200 | Rural Long | Planned |  | 4 | 98 | 0.002861 | 2.919e-05 | No
21/01/2019 | 09:06:20 | HH386B | Urban | Planned |  | 91 | 272 | 0.03957 | 0.00014548 | No
21/01/2019 | 09:07:29 | ST36 | Rural Long | Planned |  | 190 | 328.7684 | 0.4559 | 0.0013867 | No
21/01/2019 | 09:20:34 | GA22 | Rural Short | Planned |  | 13 | 297 | 0.028765 | 9.685e-05 | No
21/01/2019 | 09:29:02 | M13 | Rural Long | Planned |  | 4 | 181 | 0.005284 | 2.919e-05 | No
21/01/2019 | 09:34:54 | GA53 | Rural Short | Planned |  | 222 | 164 | 0.27125 | 0.0016539 | No
21/01/2019 | 10:08:40 | PL27 | Rural Long | Planned |  | 27 | 217 | 0.042761 | 0.00019706 | No
21/01/2019 | 10:15:18 | HH177E | Urban | Planned |  | 185 | 87 | 0.025731 | 0.00029575 | No
21/01/2019 | 10:21:42 | SB23 | Rural Long | Planned |  | 2 | 99 | 0.0014451 | 1.46e-05 | No
21/01/2019 | 11:14:35 | CM05 | Rural Long | Asset failure | LV | 1 | 167 | 0.0012188 | 7.3e-06 | No
21/01/2019 | 11:52:10 | EL13 | Urban | Planned |  | 1 | 33 | 5.276e-05 | 1.6e-06 | No
21/01/2019 | 12:45:52 | KI45 | Rural Long | Planned |  | 1 | 44 | 0.00032113 | 7.3e-06 | No
21/01/2019 | 12:48:23 | SM172B | Urban | Asset failure | LV | 18.3333 | 132 | 0.0038688 | 2.931e-05 | No
21/01/2019 | 13:23:01 | ST43 | Rural Long | Unknown | Unknown | 2 | 122 | 0.0017808 | 1.46e-05 | No
21/01/2019 | 14:05:05 | ME347F | Urban | Asset failure | LV | 2 | 206 | 0.00065865 | 3.2e-06 | No
21/01/2019 | 14:35:52 | HH148C | Urban | Planned |  | 68 | 19 | 0.0020655 | 0.00010871 | No
21/01/2019 | 15:00:44 | NL234D | Urban | Unknown | Unknown | 26.6667 | 83 | 0.0035384 | 4.263e-05 | No
21/01/2019 | 16:19:00 | G07 | Rural Long | Third Party | Other | 27 | 331 | 0.065225 | 0.00019706 | No
21/01/2019 | 17:35:31 | HH148C | Urban | Unknown | Unknown | 68 | 38 | 0.004131 | 0.00010871 | No
21/01/2019 | 18:01:05 | SM172E | Urban | Overloads |  | 1 | 295 | 0.00047161 | 1.6e-06 | No
21/01/2019 | 19:16:07 | HH130F | Urban | Overloads |  | 2 | 120 | 0.00038368 | 3.2e-06 | No
22/01/2019 | 02:13:55 | HH432F | Urban | Animal | Animal impact | 2142 | 58.9328 | 0.20181 | 0.0034244 | No
22/01/2019 | 05:09:05 | WHY12 | Urban | Asset failure | HV | 1572 | 155.0197 | 0.38958 | 0.0025131 | No
22/01/2019 | 05:10:05 | ST36 | Rural Long | Unknown | Unknown | 11 | 266 | 0.021355 | 8.028e-05 | No
22/01/2019 | 06:08:50 | WHY363A | Rural Short | Asset failure | HV | 52 | 297 | 0.11506 | 0.00038741 | No
22/01/2019 | 08:32:04 | HH121A | Urban | Planned |  | 22 | 26 | 0.00091444 | 3.517e-05 | No
22/01/2019 | 08:36:17 | KA04 | Rural Long | Planned |  | 166 | 161.8675 | 0.19611 | 0.0012115 | No
22/01/2019 | 08:37:08 | SG04 | Rural Short | Planned |  | 51 | 188 | 0.071432 | 0.00037996 | No
22/01/2019 | 08:42:59 | M13 | Rural Long | Planned |  | 2 | 27 | 0.00039411 | 1.46e-05 | No
22/01/2019 | 08:48:43 | HH121F | Urban | Planned |  | 50 | 94 | 0.0075138 | 7.993e-05 | No
22/01/2019 | 08:58:28 | MB34 | Rural Long | Planned |  | 1 | 53 | 0.00038681 | 7.3e-06 | No
22/01/2019 | 09:05:21 | MV22 | Rural Short | Planned |  | 1 | 40 | 0.00029801 | 7.45e-06 | No
22/01/2019 | 09:20:03 | VH33 | Rural Short | Planned |  | 4 | 106 | 0.0031589 | 2.98e-05 | No
22/01/2019 | 09:22:20 | SG12 | Rural Short | Planned |  | 433 | 259 | 0.83551 | 0.0032259 | No
22/01/2019 | 09:49:33 | WHY13 | Urban | Unknown | Unknown | 124 | 31 | 0.0061453 | 0.00019824 | No
22/01/2019 | 10:15:14 | NA52 | Rural Long | Planned |  | 30 | 145 | 0.031748 | 0.00021895 | No
22/01/2019 | 11:03:46 | NU23 | Rural Long | Third Party | Vehicle impact | 44 | 276.0909 | 0.08866 | 0.00032113 | No
22/01/2019 | 11:17:45 | SG02 | Rural Short | Planned |  | 17 | 48 | 0.0060793 | 0.00012665 | No
22/01/2019 | 11:23:04 | GU37 | Rural Long | Unknown | Unknown | 54 | 3.2593 | 0.0012845 | 0.00039411 | No
22/01/2019 | 11:28:29 | SA14 | Urban | Asset failure | LV | 1 | 148 | 0.0002366 | 1.6e-06 | No
22/01/2019 | 11:31:00 | SA17 | Urban | Overloads |  | 1 | 121 | 0.00019344 | 1.6e-06 | No
22/01/2019 | 11:41:23 | HH107B | Urban | Overloads |  | 1 | 127 | 0.00020303 | 1.6e-06 | No
22/01/2019 | 12:19:05 | NL111Q | Urban | Overloads |  | 1 | 153 | 0.0002446 | 1.6e-06 | No
22/01/2019 | 12:38:36 | AP227A | Urban | Asset failure | LV | 1 | 150 | 0.0002398 | 1.6e-06 | No
22/01/2019 | 13:08:23 | BM11 | Rural Short | Unknown | Unknown | 1 | 125 | 0.00093127 | 7.45e-06 | No
22/01/2019 | 13:29:47 | VH22 | Rural Short | Unknown | Unknown | 15 | 25 | 0.0027938 | 0.00011175 | No
22/01/2019 | 14:23:41 | HH118D | Urban | Unknown | Unknown | 15.6667 | 124 | 0.0031057 | 2.505e-05 | No
22/01/2019 | 15:08:05 | ME347E | Urban | Unknown | Unknown | 10 | 169 | 0.0027018 | 1.599e-05 | No
22/01/2019 | 15:08:59 | ME200B | Urban | Unknown | Unknown | 8 | 151 | 0.0019312 | 1.279e-05 | No
22/01/2019 | 16:10:41 | GA33 | Rural Short | Asset failure | LV | 1 | 69 | 0.00051406 | 7.45e-06 | No
22/01/2019 | 16:15:25 | ME116D | Urban | Other |  | 9 | 251 | 0.0036114 | 1.439e-05 | No
22/01/2019 | 16:15:48 | BT28 | Rural Long | Unknown | Unknown | 3 | 1067 | 0.023362 | 2.19e-05 | No
22/01/2019 | 16:18:50 | NL234A | Urban | Asset failure | LV | 33.6666 | 68 | 0.0036599 | 5.382e-05 | No
22/01/2019 | 16:39:39 | EL18 | Urban | Asset failure | LV | 1 | 84 | 0.00013429 | 1.6e-06 | No
22/01/2019 | 17:19:50 | HH148C | Urban | Unknown | Unknown | 68 | 10 | 0.0010871 | 0.00010871 | No
22/01/2019 | 18:05:33 | HH102D | Urban | Unknown | Unknown | 31 | 30 | 0.0014868 | 4.956e-05 | No
22/01/2019 | 18:38:36 | SM126E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 178 | 0.00028456 | 1.6e-06 | No
22/01/2019 | 18:43:39 | HH130B | Urban | Overloads |  | 1 | 220 | 0.00035171 | 1.6e-06 | No
22/01/2019 | 18:59:29 | AP149E | Urban | Asset failure | LV | 18 | 130 | 0.0037409 | 2.878e-05 | No
22/01/2019 | 19:12:31 | HH341E | Urban | Asset failure | LV | 29.3333 | 27 | 0.0012661 | 4.689e-05 | No
22/01/2019 | 19:31:43 | SM179D | Urban | Asset failure | LV | 36.3333 | 80 | 0.0046468 | 5.809e-05 | No
22/01/2019 | 19:49:59 | HH102C | Urban | Asset failure | LV | 17 | 99 | 0.0026906 | 2.718e-05 | No
22/01/2019 | 20:06:44 | CV30 | Rural Long | Asset failure | HV | 9 | 981 | 0.064437 | 6.569e-05 | No
22/01/2019 | 20:37:13 | SG01 | Rural Short | Asset failure | LV | 3.6667 | 67 | 0.0018303 | 2.732e-05 | No
22/01/2019 | 21:42:24 | ME347C | Urban | Asset failure | LV | 69 | 64 | 0.0070598 | 0.00011031 | No
23/01/2019 | 00:29:13 | NL115B | Urban | Overloads |  | 78 | 192 | 0.023942 | 0.0001247 | No
23/01/2019 | 08:09:36 | GA51 | Rural Short | Planned |  | 13 | 44 | 0.0042615 | 9.685e-05 | No
23/01/2019 | 08:22:16 | EL02 | Urban | Planned |  | 129 | 84 | 0.017323 | 0.00020623 | No
23/01/2019 | 08:25:21 | MTB11 | Rural Short | Planned |  | 1 | 116 | 0.00086422 | 7.45e-06 | No
23/01/2019 | 09:06:28 | HH341B | Urban | Asset failure | LV | 15.3333 | 98 | 0.0024023 | 2.451e-05 | No
23/01/2019 | 09:18:34 | MTB32 | Rural Long | Planned |  | 6 | 147 | 0.0064371 | 4.379e-05 | No
23/01/2019 | 09:20:12 | ST34 | Rural Long | Unknown | Unknown | 3 | 362 | 0.007926 | 2.19e-05 | No
23/01/2019 | 09:21:34 | SA744C | Urban | Asset failure | LV | 1 | 134 | 0.00021422 | 1.6e-06 | No
23/01/2019 | 09:40:00 | HH403B | Urban | Third Party | Vehicle impact | 2402 | 34.9729 | 0.1343 | 0.00384 | No
23/01/2019 | 10:01:59 | G30 | Rural Long | Planned |  | 1 | 125 | 0.00091229 | 7.3e-06 | No
23/01/2019 | 10:35:01 | MV62 | Rural Short | Animal | Animal impact | 1 | 94 | 0.00070031 | 7.45e-06 | No
23/01/2019 | 10:46:51 | ME347G | Urban | Unknown | Unknown | 1492 | 7.2493 | 0.017291 | 0.0023852 | No
23/01/2019 | 11:43:33 | AP125D | Urban | Asset failure | LV | 1 | 59 | 9.432e-05 | 1.6e-06 | No
23/01/2019 | 12:14:24 | HH341K | Urban | Asset failure | LV | 1 | 106 | 0.00016946 | 1.6e-06 | No
23/01/2019 | 12:18:35 | AP125D | Urban | Asset failure | LV | 1 | 25 | 3.997e-05 | 1.6e-06 | No
23/01/2019 | 12:27:23 | CL09 | Rural Long | Unknown | Unknown | 2 | 72 | 0.001051 | 1.46e-05 | No
23/01/2019 | 12:56:58 | SM402B | Urban | Overloads |  | 18 | 59 | 0.0016978 | 2.878e-05 | No
23/01/2019 | 15:26:21 | WHY12 | Urban | Unknown | Unknown | 1572 | 2 | 0.0050262 | 0.0025131 | No
23/01/2019 | 16:19:54 | NL115B | Urban | Asset failure | LV | 1 | 139 | 0.00022222 | 1.6e-06 | No
23/01/2019 | 16:21:15 | EL08G | Urban | Unknown | Unknown | 31 | 47 | 0.0023293 | 4.956e-05 | No
23/01/2019 | 16:23:38 | AP373C | Urban | Unknown | Unknown | 1 | 8 | 1.279e-05 | 1.6e-06 | No
23/01/2019 | 16:34:00 | HH177C | Urban | Asset failure | LV | 1 | 241 | 0.00038528 | 1.6e-06 | No
23/01/2019 | 16:54:52 | CD01 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 78 | 0.00058111 | 7.45e-06 | No
23/01/2019 | 17:11:49 | ME427F | Urban | Asset failure | LV | 25.6666 | 104 | 0.0042674 | 4.103e-05 | No
23/01/2019 | 17:15:02 | CM03 | Rural Long | Unknown | Unknown | 50 | 253.72 | 0.092587 | 0.00036492 | No
23/01/2019 | 18:05:45 | SM410A | Urban | Unknown | Unknown | 26.3333 | 45 | 0.0018944 | 4.21e-05 | No
23/01/2019 | 18:34:50 | HH409D | Urban | Unknown | Unknown | 18.6666 | 87 | 0.0025963 | 2.984e-05 | No
23/01/2019 | 18:54:50 | MI26 | Rural Long | Unknown | Unknown | 71 | 210.662 | 0.10916 | 0.00051818 | No
23/01/2019 | 19:03:22 | AP529A | Urban | Unknown | Unknown | 30.3333 | 104 | 0.0050433 | 4.849e-05 | No
23/01/2019 | 19:21:30 | ME427A | Urban | Overloads |  | 1 | 115 | 0.00018385 | 1.6e-06 | No
23/01/2019 | 19:25:34 | SM350E | Urban | Unknown | Unknown | 8 | 67 | 0.00085689 | 1.279e-05 | No
23/01/2019 | 19:36:40 | AP529A | Urban | Unknown | Unknown | 34.3333 | 99 | 0.0054339 | 5.489e-05 | No
23/01/2019 | 19:45:10 | SB17 | Rural Long | Other |  | 1 | 304 | 0.0022187 | 7.3e-06 | No
23/01/2019 | 19:49:49 | HH341J | Urban | Unknown | Unknown | 17.6666 | 52 | 0.0014686 | 2.824e-05 | No
23/01/2019 | 20:14:32 | AP227A | Urban | Overloads |  | 1 | 120 | 0.00019184 | 1.6e-06 | No
23/01/2019 | 20:28:32 | PP03 | Urban | Overloads |  | 16.6667 | 103 | 0.0027444 | 2.664e-05 | No
23/01/2019 | 20:39:09 | HH102C | Urban | Unknown | Unknown | 33.3333 | 32 | 0.0017052 | 5.329e-05 | No
23/01/2019 | 20:51:15 | AP424E | Urban | Unknown | Unknown | 38 | 60 | 0.003645 | 6.075e-05 | No
23/01/2019 | 21:14:00 | WHY12 / WHY13 | Urban | Planned |  | 83 | 331 | 0.04392 | 0.00013269 | No
23/01/2019 | 22:01:31 | HH386A | Urban | Asset failure | LV | 9.3333 | 155 | 0.0023128 | 1.492e-05 | No
23/01/2019 | 23:14:19 | MTB52 | Rural Long | Asset failure | HV | 976 | 78.0574 | 0.55602 | 0.0071232 | No
24/01/2019 | 01:56:06 | AP529A | Urban | Unknown | Unknown | 35.3333 | 77 | 0.0043495 | 5.649e-05 | No
24/01/2019 | 05:08:00 | WHY12 / WHY13 | Urban | Planned |  | 1572 | 8.8931 | 0.022349 | 0.0025131 | No
24/01/2019 | 08:12:48 | WHY01 | Urban | Overloads |  | 1 | 185 | 0.00029575 | 1.6e-06 | No
24/01/2019 | 08:19:51 | CL04 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 163 | 0.0023793 | 1.46e-05 | No
24/01/2019 | 09:19:12 | HH121F | Urban | Overloads |  | 1 | 224 | 0.0003581 | 1.6e-06 | No
24/01/2019 | 09:47:27 | ST42 | Rural Long | Asset failure | HV | 154 | 157.5584 | 0.17709 | 0.0011239 | No
24/01/2019 | 10:19:59 | PL21 | Rural Long | Unknown | Unknown | 1 | 48 | 0.00035032 | 7.3e-06 | No
24/01/2019 | 11:34:19 | HH121C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2249 | 2.341 | 0.008417 | 0.0035954 | No
24/01/2019 | 13:07:11 | SM411D | Urban | Asset failure | LV | 1 | 133 | 0.00021262 | 1.6e-06 | No
24/01/2019 | 13:20:55 | MT21 | Rural Long | Asset failure | HV | 215 | 126 | 0.19771 | 0.0015691 | No
24/01/2019 | 14:20:57 | NL115C | Urban | Asset failure | HV | 6 | 62 | 0.00059471 | 9.59e-06 | No
24/01/2019 | 14:39:25 | HH522A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1688 | 27 | 0.072861 | 0.0026986 | No
24/01/2019 | 14:45:55 | VH31 | Rural Short | Asset failure | Distribution substation | 29 | 429 | 0.092687 | 0.00021605 | No
24/01/2019 | 14:51:51 | EL16 | Urban | Overloads |  | 3 | 63 | 0.00030215 | 4.8e-06 | No
24/01/2019 | 14:57:20 | NL115C | Urban | Asset failure | HV | 58 | 100 | 0.0092723 | 9.272e-05 | No
24/01/2019 | 14:58:25 | HH428A | Urban | Unknown | Unknown | 72.6667 | 535 | 0.062151 | 0.00011617 | No
24/01/2019 | 15:30:30 | HH118D | Urban | Unknown | Unknown | 15.6667 | 135 | 0.0033812 | 2.505e-05 | No
24/01/2019 | 16:18:27 | ME231D | Urban | Other |  | 1 | 681 | 0.0010887 | 1.6e-06 | No
24/01/2019 | 16:22:05 | SM349F | Urban | Overloads |  | 1 | 73 | 0.0001167 | 1.6e-06 | No
24/01/2019 | 16:37:31 | GA26 | Urban | Asset failure | LV | 52 | 37 | 0.0030759 | 8.313e-05 | No
24/01/2019 | 16:48:15 | HH145B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 90 | 0.00014388 | 1.6e-06 | No
24/01/2019 | 16:55:36 | SM410A | Urban | Asset failure | LV | 35 | 160 | 0.0089526 | 5.595e-05 | No
24/01/2019 | 16:58:09 | SM216E | Urban | Overloads |  | 18.6666 | 155 | 0.0046255 | 2.984e-05 | No
24/01/2019 | 16:59:41 | SM216E | Urban | Overloads |  | 26.6666 | 152 | 0.00648 | 4.263e-05 | No
24/01/2019 | 17:06:02 | CN33 | Rural Long | Unknown | Unknown | 8 | 481.5 | 0.028113 | 5.839e-05 | No
24/01/2019 | 17:13:16 | W27 | Rural Long | Unknown | Unknown | 73 | 188.5479 | 0.10045 | 0.00053278 | No
24/01/2019 | 17:40:57 | PP14 | Rural Long | Overloads |  | 1 | 511 | 0.0037295 | 7.3e-06 | No
24/01/2019 | 17:48:11 | SG07 | Rural Short | Asset failure | LV | 1 | 142 | 0.0010579 | 7.45e-06 | No
24/01/2019 | 17:48:41 | AP227B | Urban | Asset failure | LV | 14.3333 | 470 | 0.01077 | 2.291e-05 | No
24/01/2019 | 17:55:17 | CV753A | Rural Long | Overloads |  | 5 | 174 | 0.0063495 | 3.649e-05 | No
24/01/2019 | 17:58:42 | SM411B | Urban | Other |  | 31 | 587 | 0.029091 | 4.956e-05 | No
24/01/2019 | 18:02:15 | AP355A | Urban | Unknown | Unknown | 29 | 267 | 0.012379 | 4.636e-05 | No
24/01/2019 | 18:09:22 | HH428D | Urban | Unknown | Unknown | 72 | 166 | 0.019107 | 0.0001151 | No
24/01/2019 | 18:09:36 | AP125B | Urban | Asset failure | HV | 1749 | 225.5826 | 0.63075 | 0.0027961 | No
24/01/2019 | 18:14:14 | SM402D | Urban | Overloads |  | 63 | 466 | 0.046934 | 0.00010072 | No
24/01/2019 | 18:16:23 | SM216A | Urban | Overloads |  | 32.6666 | 221 | 0.011541 | 5.222e-05 | No
24/01/2019 | 18:16:53 | NL210A | Urban | Unknown | Unknown | 11.3333 | 346 | 0.0062689 | 1.812e-05 | No
24/01/2019 | 18:21:22 | AP132D | Urban | Overloads |  | 36.3333 | 497 | 0.028868 | 5.809e-05 | No
24/01/2019 | 18:30:16 | SM349E | Urban | Asset failure | LV | 41 | 254 | 0.016649 | 6.555e-05 | No
24/01/2019 | 18:33:26 | MV64 | Urban | Unknown | Unknown | 24 | 131 | 0.0050262 | 3.837e-05 | No
24/01/2019 | 18:38:13 | SM137A | Urban | Unknown | Unknown | 45 | 154 | 0.011079 | 7.194e-05 | No
24/01/2019 | 18:39:11 | SA20 | Urban | Overloads |  | 18.3333 | 107 | 0.0031361 | 2.931e-05 | No
24/01/2019 | 18:41:01 | AP355A | Urban | Asset failure | LV | 23 | 502 | 0.018458 | 3.677e-05 | No
24/01/2019 | 18:42:47 | AP146E | Urban | Asset failure | LV | 45.3333 | 208 | 0.015074 | 7.247e-05 | No
24/01/2019 | 18:45:51 | NL234A | Urban | Unknown | Unknown | 25.3333 | 290 | 0.011745 | 4.05e-05 | No
24/01/2019 | 18:49:37 | SM172C | Urban | Asset failure | LV | 68.6666 | 186 | 0.020418 | 0.00010978 | No
24/01/2019 | 18:54:29 | HH341J | Urban | Animal | Animal nesting/burrowing, etc and other | 17.6666 | 356 | 0.010055 | 2.824e-05 | No
24/01/2019 | 18:57:47 | NL111Q | Urban | Unknown | Unknown | 22 | 76 | 0.002673 | 3.517e-05 | No
24/01/2019 | 19:00:09 | HH107B | Urban | Overloads |  | 44.6666 | 166 | 0.011854 | 7.141e-05 | No
24/01/2019 | 19:00:43 | NL234C | Urban | Unknown | Unknown | 28 | 149 | 0.0066697 | 4.476e-05 | No
24/01/2019 | 19:00:53 | SM349F | Urban | Unknown | Unknown | 49.6666 | 229 | 0.018183 | 7.94e-05 | No
24/01/2019 | 19:03:18 | NL234A | Urban | Overloads |  | 28.6666 | 346 | 0.015857 | 4.583e-05 | No
24/01/2019 | 19:04:12 | HH409A | Urban | Unknown | Unknown | 11 | 207 | 0.0036402 | 1.759e-05 | No
24/01/2019 | 19:10:15 | MTB61 | Rural Short | Asset failure | LV | 1 | 262 | 0.0019519 | 7.45e-06 | No
24/01/2019 | 19:13:13 | NL234C | Urban | Unknown | Unknown | 31.3333 | 135 | 0.0067624 | 5.009e-05 | No
24/01/2019 | 19:13:48 | SM374E | Urban | Vegetation | Grow-in - NSP responsibility | 66 | 392 | 0.041361 | 0.00010551 | No
24/01/2019 | 19:14:01 | AP372B | Urban | Unknown | Unknown | 35.3333 | 316 | 0.01785 | 5.649e-05 | No
24/01/2019 | 19:16:03 | NA01 | Rural Long | Unknown | Unknown | 30.6666 | 102 | 0.022829 | 0.00022382 | No
24/01/2019 | 19:17:55 | HH107A | Urban | Other |  | 24.3333 | 354 | 0.013771 | 3.89e-05 | No
24/01/2019 | 19:20:07 | ME200G | Urban | Overloads |  | 32.6666 | 326 | 0.017025 | 5.222e-05 | No
24/01/2019 | 19:21:27 | HH118D | Urban | Unknown | Unknown | 37.3333 | 263 | 0.015697 | 5.968e-05 | No
24/01/2019 | 19:22:52 | HH386F | Urban | Overloads |  | 16.6667 | 203 | 0.0054088 | 2.664e-05 | No
24/01/2019 | 19:23:38 | HH341D | Urban | Overloads |  | 24.6666 | 165 | 0.0065066 | 3.943e-05 | No
24/01/2019 | 19:23:53 | HH145A | Urban | Asset failure | LV | 64 | 271 | 0.027727 | 0.00010232 | No
24/01/2019 | 19:26:25 | GU21 | Rural Long | Overloads |  | 12 | 168 | 0.014713 | 8.758e-05 | No
24/01/2019 | 19:26:57 | HH428A | Urban | Asset failure | HV | 64 | 248 | 0.025374 | 0.00010232 | No
24/01/2019 | 19:28:11 | HH341C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 37.3333 | 260 | 0.015518 | 5.968e-05 | No
24/01/2019 | 19:28:29 | HH522C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 13.3333 | 117 | 0.0024939 | 2.132e-05 | No
24/01/2019 | 19:31:01 | AP149E | Urban | Unknown | Unknown | 20.3333 | 425 | 0.013815 | 3.251e-05 | No
24/01/2019 | 19:33:04 | NL210A | Urban | Unknown | Unknown | 25.3333 | 254 | 0.010287 | 4.05e-05 | No
24/01/2019 | 19:34:02 | EL09 | Urban | Overloads |  | 35.3333 | 288 | 0.016268 | 5.649e-05 | No
24/01/2019 | 19:35:19 | NA02 | Rural Long | Unknown | Unknown | 15.6667 | 251 | 0.0287 | 0.00011434 | No
24/01/2019 | 19:36:43 | SM411C | Urban | Unknown | Unknown | 18 | 339 | 0.0097551 | 2.878e-05 | No
24/01/2019 | 19:38:22 | AP227A | Urban | Other |  | 51 | 152 | 0.012393 | 8.153e-05 | No
24/01/2019 | 19:38:45 | SSD424 | Urban | Asset failure | Zone substation | 12239 | 89.2955 | 1.7472 | 0.019566 | No
24/01/2019 | 19:39:25 | SM350G | Urban | Unknown | Unknown | 19.3333 | 296 | 0.0091487 | 3.091e-05 | No
24/01/2019 | 19:40:40 | HH386F | Urban | Overloads |  | 23.6666 | 214 | 0.0080967 | 3.784e-05 | No
24/01/2019 | 19:49:18 | AP365E | Urban | Unknown | Unknown | 25.3333 | 368 | 0.014904 | 4.05e-05 | No
24/01/2019 | 19:49:34 | AP226D | Urban | Asset failure | HV | 2272 | 80.1461 | 0.29111 | 0.0036322 | No
24/01/2019 | 19:50:47 | HH341C | Urban | Unknown | Unknown | 30 | 280 | 0.013429 | 4.796e-05 | No
24/01/2019 | 19:51:33 | MV34 | Rural Short | Asset failure | LV | 16 | 161 | 0.019192 | 0.0001192 | No
24/01/2019 | 19:52:35 | HH409E | Urban | Asset failure | LV | 21 | 204 | 0.0068487 | 3.357e-05 | No
24/01/2019 | 19:52:42 | NL234C | Urban | Unknown | Unknown | 29.6666 | 155 | 0.0073512 | 4.743e-05 | No
24/01/2019 | 19:55:41 | HH102C | Urban | Unknown | Unknown | 33.3333 | 192 | 0.010232 | 5.329e-05 | No
24/01/2019 | 19:57:29 | SM350F | Urban | Unknown | Unknown | 25.6666 | 529 | 0.021706 | 4.103e-05 | No
24/01/2019 | 19:59:54 | SM172A | Urban | Overloads |  | 29.6666 | 411 | 0.019493 | 4.743e-05 | No
24/01/2019 | 19:59:57 | AP344D | Urban | Unknown | Unknown | 26 | 455 | 0.018912 | 4.157e-05 | No
24/01/2019 | 20:00:29 | AP344D | Urban | Overloads |  | 54.9999 | 446 | 0.039215 | 8.793e-05 | No
24/01/2019 | 20:00:33 | PP04 | Rural Short | Asset failure | LV | 26.3333 | 137 | 0.026878 | 0.00019619 | No
24/01/2019 | 20:00:48 | AP149D | Urban | Other |  | 59.3333 | 264 | 0.025042 | 9.485e-05 | No
24/01/2019 | 20:01:31 | HH145C | Urban | Unknown | Unknown | 1514 | 74.6902 | 0.18078 | 0.0024204 | No
24/01/2019 | 20:03:11 | SM126E | Urban | Asset failure | LV | 16.6667 | 348 | 0.0092723 | 2.664e-05 | No
24/01/2019 | 20:03:18 | SM216E | Urban | Unknown | Unknown | 18.6666 | 290 | 0.0086541 | 2.984e-05 | No
24/01/2019 | 20:03:53 | CBD103C | Urban | Other |  | 54 | 108 | 0.0093235 | 8.633e-05 | No
24/01/2019 | 20:04:40 | SM216E | Urban | Unknown | Unknown | 26.6666 | 284 | 0.012107 | 4.263e-05 | No
24/01/2019 | 20:06:11 | MB27 | Rural Short | Unknown | Unknown | 18.6666 | 138 | 0.019192 | 0.00013907 | No
24/01/2019 | 20:06:16 | HH432F | Urban | Unknown | Unknown | 17.6666 | 394 | 0.011128 | 2.824e-05 | No
24/01/2019 | 20:11:00 | HH121D | Urban | Unknown | Unknown | 29 | 181 | 0.0083914 | 4.636e-05 | No
24/01/2019 | 20:11:05 | AP529A | Urban | Unknown | Unknown | 35.3333 | 168 | 0.0094897 | 5.649e-05 | No
24/01/2019 | 20:11:17 | VH45 | Rural Short | Unknown | Unknown | 27.3333 | 298 | 0.060684 | 0.00020364 | No
24/01/2019 | 20:13:16 | SM349F | Urban | Unknown | Unknown | 22 | 379 | 0.01333 | 3.517e-05 | No
24/01/2019 | 20:14:53 | CN75 | Rural Long | Unknown | Unknown | 57 | 574.4737 | 0.23898 | 0.00041601 | No
24/01/2019 | 20:16:15 | MV64 | Urban | Unknown | Unknown | 23.6666 | 248 | 0.0093831 | 3.784e-05 | No
24/01/2019 | 20:17:36 | SM350H | Urban | Asset failure | LV | 16.3333 | 115 | 0.0030028 | 2.611e-05 | No
24/01/2019 | 20:20:14 | HH409F | Urban | Animal | Animal nesting/burrowing, etc and other | 21 | 133 | 0.0044651 | 3.357e-05 | No
24/01/2019 | 20:22:07 | AP424B | Urban | Overloads |  | 26 | 177 | 0.0073571 | 4.157e-05 | No
24/01/2019 | 20:22:13 | SM411E | Urban | Asset failure | LV | 48 | 255 | 0.019568 | 7.674e-05 | No
24/01/2019 | 20:24:22 | AP227A | Urban | Unknown | Unknown | 91 | 144 | 0.020949 | 0.00014548 | No
24/01/2019 | 20:25:19 | WK41 | Rural Short | Planned |  | 2 | 190 | 0.0028311 | 1.49e-05 | No
24/01/2019 | 20:28:55 | SM216C | Urban | Asset failure | LV | 72 | 119 | 0.013697 | 0.0001151 | No
24/01/2019 | 20:30:11 | HH145B | Urban | Overloads |  | 14 | 218 | 0.0048791 | 2.238e-05 | No
24/01/2019 | 20:31:12 | HH145D | Urban | Asset failure | LV | 19.6666 | 158 | 0.0049676 | 3.144e-05 | No
24/01/2019 | 20:31:22 | AP149H | Urban | Asset failure | LV | 18.3333 | 69 | 0.0020223 | 2.931e-05 | No
24/01/2019 | 20:33:14 | HH432C | Urban | Vegetation | Grow-in - NSP responsibility | 22.3333 | 278 | 0.0099256 | 3.57e-05 | No
24/01/2019 | 20:34:25 | SM410A | Urban | Other |  | 52.6667 | 398 | 0.03351 | 8.42e-05 | No
24/01/2019 | 20:34:43 | HH102B | Urban | Other |  | 20.6666 | 301 | 0.0099448 | 3.304e-05 | No
24/01/2019 | 20:35:09 | VH16 | Rural Short | Asset failure | LV | 15 | 253 | 0.028273 | 0.00011175 | No
24/01/2019 | 20:36:00 | AP529A | Urban | Unknown | Unknown | 77 | 185 | 0.022773 | 0.0001231 | No
24/01/2019 | 20:36:54 | HH429C | Urban | Unknown | Unknown | 27.6666 | 320 | 0.014154 | 4.423e-05 | No
24/01/2019 | 20:41:13 | AP149F | Urban | Unknown | Unknown | 35.3333 | 246 | 0.013896 | 5.649e-05 | No
24/01/2019 | 20:45:43 | MTB21 | Rural Short | Overloads |  | 14.3333 | 53 | 0.0056596 | 0.00010679 | No
24/01/2019 | 20:46:36 | AP149F | Urban | Unknown | Unknown | 54 | 82 | 0.0070789 | 8.633e-05 | No
24/01/2019 | 20:47:38 | AP424C | Urban | Unknown | Unknown | 25.3333 | 123 | 0.0049815 | 4.05e-05 | No
24/01/2019 | 20:50:39 | AP149E | Urban | Overloads |  | 1 | 422 | 0.00067464 | 1.6e-06 | No
24/01/2019 | 20:52:13 | HH432C | Urban | Overloads |  | 60.6666 | 150 | 0.014548 | 9.699e-05 | No
24/01/2019 | 20:52:15 | MG19 | Rural Long | Unknown | Unknown | 410 | 34 | 0.10174 | 0.0029923 | No
24/01/2019 | 20:53:02 | M83 | Rural Long | Unknown | Unknown | 65 | 205.8769 | 0.097666 | 0.00047439 | No
24/01/2019 | 20:54:07 | AP529C | Urban | Unknown | Unknown | 19.3333 | 375 | 0.01159 | 3.091e-05 | No
24/01/2019 | 20:54:46 | ME427F | Urban | Animal | Animal nesting/burrowing, etc and other | 25.6666 | 371 | 0.015223 | 4.103e-05 | No
24/01/2019 | 20:54:46 | ME347A | Urban | Overloads |  | 31 | 201 | 0.0099613 | 4.956e-05 | No
24/01/2019 | 20:55:28 | AP365E | Urban | Unknown | Unknown | 27 | 385 | 0.016618 | 4.316e-05 | No
24/01/2019 | 20:56:05 | SA711C | Urban | Unknown | Unknown | 33.3333 | 65 | 0.0034638 | 5.329e-05 | No
24/01/2019 | 20:57:33 | MV64 | Urban | Unknown | Unknown | 1 | 215 | 0.00034372 | 1.6e-06 | No
24/01/2019 | 20:58:01 | SA32 | Urban | Overloads |  | 17 | 135 | 0.003669 | 2.718e-05 | No
24/01/2019 | 20:58:34 | HH341E | Urban | Asset failure | LV | 34.6666 | 213 | 0.011805 | 5.542e-05 | No
24/01/2019 | 20:58:59 | MV64 | Urban | Unknown | Unknown | 24 | 155 | 0.0059471 | 3.837e-05 | No
24/01/2019 | 21:03:46 | HH148B | Urban | Overloads |  | 27.3333 | 209 | 0.0091327 | 4.37e-05 | No
24/01/2019 | 21:09:25 | AP125D | Urban | Overloads |  | 1 | 392 | 0.00062668 | 1.6e-06 | No
24/01/2019 | 21:10:32 | HH121E | Urban | Animal | Animal nesting/burrowing, etc and other | 26.3333 | 146 | 0.0061464 | 4.21e-05 | No
24/01/2019 | 21:11:35 | HH177G | Urban | Unknown | Unknown | 27 | 157 | 0.0067768 | 4.316e-05 | No
24/01/2019 | 21:15:39 | MV53 | Rural Short | Asset failure | HV | 193 | 316.0933 | 0.4545 | 0.0014379 | No
24/01/2019 | 21:15:39 | MV53 | Rural Short | Asset failure | HV | 0 | 2 | 0.0026672 | 0 | No
24/01/2019 | 21:22:56 | AP424B | Urban | Overloads |  | 33.6666 | 92 | 0.0049516 | 5.382e-05 | No
24/01/2019 | 21:23:34 | MV64 | Urban | Unknown | Unknown | 1 | 184 | 0.00029416 | 1.6e-06 | No
24/01/2019 | 21:27:46 | HH107B | Urban | Overloads |  | 34.3333 | 57 | 0.0031286 | 5.489e-05 | No
24/01/2019 | 21:30:45 | AP149D | Urban | Overloads |  | 37 | 309 | 0.018278 | 5.915e-05 | No
24/01/2019 | 21:32:00 | HH428D | Urban | Unknown | Unknown | 72 | 165 | 0.018992 | 0.0001151 | No
24/01/2019 | 21:32:13 | AP149E | Urban | Unknown | Unknown | 48 | 274 | 0.021026 | 7.674e-05 | No
24/01/2019 | 21:33:11 | HH429C | Urban | Unknown | Unknown | 28 | 167 | 0.0074754 | 4.476e-05 | No
24/01/2019 | 21:37:47 | AP424B | Urban | Unknown | Unknown | 34.3333 | 222 | 0.012185 | 5.489e-05 | No
24/01/2019 | 21:40:06 | HH121E | Urban | Animal | Animal nesting/burrowing, etc and other | 7 | 91 | 0.0010184 | 1.119e-05 | No
24/01/2019 | 21:44:35 | NL210A | Urban | Unknown | Unknown | 1 | 298 | 0.00047641 | 1.6e-06 | No
24/01/2019 | 21:44:41 | SM137A | Urban | Unknown | Unknown | 45 | 156 | 0.011223 | 7.194e-05 | No
24/01/2019 | 21:44:49 | HH121G | Urban | Asset failure | LV | 31.6666 | 156 | 0.0078975 | 5.062e-05 | No
24/01/2019 | 21:45:02 | AP226D | Urban | Unknown | Unknown | 34 | 31 | 0.001685 | 5.435e-05 | No
24/01/2019 | 21:46:12 | HH121D | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 135 | 0.00021582 | 1.6e-06 | No
24/01/2019 | 21:47:34 | ME427F | Urban | Asset failure | LV | 32 | 96 | 0.0049111 | 5.116e-05 | No
24/01/2019 | 21:48:33 | HH107A | Urban | Unknown | Unknown | 27.6666 | 108 | 0.0047768 | 4.423e-05 | No
24/01/2019 | 22:01:02 | HH107B | Urban | Overloads |  | 44.6666 | 117 | 0.0083547 | 7.141e-05 | No
24/01/2019 | 22:03:43 | AP125D | Urban | Overloads |  | 1 | 340 | 0.00054355 | 1.6e-06 | No
24/01/2019 | 22:11:43 | HH130C | Urban | Unknown | Unknown | 22 | 164 | 0.005768 | 3.517e-05 | No
24/01/2019 | 22:20:56 | SM350F | Urban | Overloads |  | 19.3333 | 239 | 0.0073869 | 3.091e-05 | No
24/01/2019 | 22:23:37 | SM179A | Urban | Asset failure | LV | 7 | 330 | 0.0036929 | 1.119e-05 | No
24/01/2019 | 22:27:00 | AP226C | Urban | Unknown | Unknown | 13 | 233 | 0.0048424 | 2.078e-05 | No
24/01/2019 | 22:30:46 | NA01 | Rural Long | Asset failure | LV | 1 | 27 | 0.00019706 | 7.3e-06 | No
24/01/2019 | 22:33:53 | HH428B | Urban | Unknown | Unknown | 34 | 129 | 0.0070118 | 5.435e-05 | No
24/01/2019 | 22:33:56 | HH121D | Urban | Animal | Animal nesting/burrowing, etc and other | 27.3333 | 183 | 0.0079966 | 4.37e-05 | No
24/01/2019 | 22:35:47 | HH121D | Urban | Animal | Animal nesting/burrowing, etc and other | 2.6667 | 182 | 0.00077589 | 4.26e-06 | No
24/01/2019 | 22:53:09 | AP424E | Urban | Unknown | Unknown | 33.3333 | 149 | 0.0079401 | 5.329e-05 | No
24/01/2019 | 22:57:04 | AP424E | Urban | Unknown | Unknown | 17.6666 | 164 | 0.0046319 | 2.824e-05 | No
24/01/2019 | 23:03:20 | HH121D | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 82 | 0.00013109 | 1.6e-06 | No
24/01/2019 | 23:09:01 | SM410D | Urban | Asset failure | Distribution substation | 1916 | 167.9958 | 0.51458 | 0.0030631 | No
24/01/2019 | 23:34:46 | HH107D | Urban | Asset failure | LV | 1 | 190 | 0.00030375 | 1.6e-06 | No
24/01/2019 | 23:38:35 | HH102C | Urban | Unknown | Unknown | 33.3333 | 87 | 0.0046362 | 5.329e-05 | No
24/01/2019 | 23:43:42 | AP125C | Urban | Overloads |  | 22.3333 | 75 | 0.0026778 | 3.57e-05 | No
24/01/2019 | 23:48:13 | SM179C | Urban | Other |  | 1 | 239 | 0.00038208 | 1.6e-06 | No
25/01/2019 | 00:04:14 | HH121D | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 21 | 3.357e-05 | 1.6e-06 | No
25/01/2019 | 00:06:00 | AP424B | Urban | Overloads |  | 26 | 145 | 0.006027 | 4.157e-05 | No
25/01/2019 | 00:06:40 | AP424B | Urban | Overloads |  | 33.3333 | 110 | 0.0058618 | 5.329e-05 | No
25/01/2019 | 00:17:09 | EL09 | Urban | Unknown | Unknown | 764 | 1 | 0.0012214 | 0.0012214 | No
25/01/2019 | 00:23:57 | HH145C | Urban | Unknown | Unknown | 51 | 201 | 0.016388 | 8.153e-05 | No
25/01/2019 | 00:38:40 | MTB54 | Rural Long | Asset failure | HV | 243 | 92.5556 | 0.16415 | 0.0017735 | No
25/01/2019 | 00:58:53 | CBD366M | CBD | Planned |  | 1 | 271 | 0.052606 | 0.00019412 | No
25/01/2019 | 01:56:14 | MB81 | Rural Long | Asset failure | HV | 370 | 97.5189 | 0.26334 | 0.0027004 | No
25/01/2019 | 02:26:20 | HH130A | Urban | Overloads |  | 34.6666 | 106 | 0.0058746 | 5.542e-05 | No
25/01/2019 | 03:30:50 | SM349C | Urban | Overloads |  | 38.6666 | 52 | 0.0032144 | 6.182e-05 | No
25/01/2019 | 04:09:18 | AP372A | Urban | Unknown | Unknown | 15 | 289 | 0.0069302 | 2.398e-05 | No
25/01/2019 | 06:08:18 | HH428F | Urban | Unknown | Unknown | 31.6666 | 126 | 0.0063787 | 5.062e-05 | No
25/01/2019 | 06:30:47 | AP424A | Urban | Unknown | Unknown | 22.6666 | 147 | 0.0053268 | 3.624e-05 | No
25/01/2019 | 06:56:42 | SM350A | Urban | Asset failure | LV | 15.6667 | 102 | 0.0025547 | 2.505e-05 | No
25/01/2019 | 08:04:25 | BM11 | Rural Short | Planned |  | 2 | 16 | 0.0002384 | 1.49e-05 | No
25/01/2019 | 08:11:28 | MV54 | Rural Short | Planned |  | 93 | 351 | 0.2432 | 0.00069286 | No
25/01/2019 | 08:33:56 | CN83 | Rural Long | Asset failure | Distribution substation | 2 | 255 | 0.0037222 | 1.46e-05 | No
25/01/2019 | 08:42:45 | NU04 | Rural Short | Planned |  | 27 | 18 | 0.0036208 | 0.00020115 | No
25/01/2019 | 08:50:22 | YK03 | Rural Long | Planned |  | 49 | 201 | 0.071881 | 0.00035762 | No
25/01/2019 | 08:54:01 | KA04 | Rural Long | Planned |  | 107 | 294 | 0.22959 | 0.00078092 | No
25/01/2019 | 08:54:51 | ST35 | Rural Long | Planned |  | 62 | 238 | 0.10769 | 0.0004525 | No
25/01/2019 | 09:02:03 | HH432B | Urban | Asset failure | LV | 2 | 76 | 0.000243 | 3.2e-06 | No
25/01/2019 | 09:12:50 | CD23 | Rural Long | Unknown | Unknown | 37 | 118.027 | 0.031872 | 0.00027004 | No
25/01/2019 | 09:14:32 | VH17 | Rural Short | Planned |  | 2 | 162 | 0.0024138 | 1.49e-05 | No
25/01/2019 | 09:16:36 | SA36 | Urban | Planned |  | 7 | 368 | 0.0041182 | 1.119e-05 | No
25/01/2019 | 09:20:36 | PL14 | Urban | Planned |  | 1 | 109 | 0.00017426 | 1.6e-06 | No
25/01/2019 | 09:27:32 | BM12 | Rural Short | Planned |  | 2 | 9 | 0.0001341 | 1.49e-05 | No
25/01/2019 | 09:30:49 | HH148D | Urban | Planned |  | 45 | 148 | 0.010647 | 7.194e-05 | No
25/01/2019 | 09:44:13 | MV62 | Rural Short | Planned |  | 355 | 302 | 0.79873 | 0.0026448 | No
25/01/2019 | 09:58:44 | HH496F | Urban | Asset failure | LV | 72 | 365 | 0.042013 | 0.0001151 | No
25/01/2019 | 10:25:33 | CL04 | Rural Long | Unknown | Unknown | 2 | 259 | 0.0037805 | 1.46e-05 | No
25/01/2019 | 10:39:15 | MG46 | Rural Short | Unknown | Unknown | 6 | 54 | 0.0024138 | 4.47e-05 | No
25/01/2019 | 10:42:38 | BM56 | Rural Short | Planned |  | 5 | 16 | 0.00059601 | 3.725e-05 | No
25/01/2019 | 10:43:12 | MV12 | Urban | Planned |  | 14 | 235 | 0.0052596 | 2.238e-05 | No
25/01/2019 | 11:10:29 | MI08 | Rural Long | Planned |  | 1 | 171 | 0.001248 | 7.3e-06 | No
25/01/2019 | 12:03:10 | BU01 | Rural Long | Planned |  | 26 | 29 | 0.005503 | 0.00018976 | No
25/01/2019 | 12:56:12 | PA07 | Rural Long | Overloads |  | 1 | 48 | 0.00035032 | 7.3e-06 | No
25/01/2019 | 13:04:04 | HH130B | Urban | Overloads |  | 1 | 247 | 0.00039487 | 1.6e-06 | No
25/01/2019 | 13:26:50 | NL544B | Urban | Third Party | Vehicle impact | 168 | 76.8333 | 0.020636 | 0.00026858 | No
25/01/2019 | 14:00:56 | MI20 | Rural Long | Unknown | Unknown | 339 | 153.2714 | 0.37921 | 0.0024741 | No
25/01/2019 | 14:07:23 | MTB51 | Rural Long | Planned |  | 64 | 7 | 0.0032697 | 0.00046709 | No
25/01/2019 | 15:53:57 | EL18 | Urban | Asset failure | LV | 1 | 97 | 0.00015507 | 1.6e-06 | No
25/01/2019 | 16:46:15 | SD35300 | Rural Long | Weather |  | 1429 | 165 | 1.7208 | 0.010429 | No
25/01/2019 | 17:56:50 | MT06 | Rural Long | Asset failure | Distribution substation | 46 | 63 | 0.021151 | 0.00033572 | No
25/01/2019 | 18:08:59 | LM43 | Rural Long | Unknown | Unknown | 1 | 41 | 0.00029923 | 7.3e-06 | No
25/01/2019 | 18:18:31 | SM216C | Urban | Overloads |  | 1 | 53 | 8.473e-05 | 1.6e-06 | No
25/01/2019 | 19:49:25 | HH145E | Urban | Asset failure | LV | 1.3333 | 95 | 0.0002025 | 2.13e-06 | No
25/01/2019 | 19:57:36 | SM374E | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
26/01/2019 | 00:09:44 | AP355H | Urban | Animal | Animal impact | 1449 | 94 | 0.21775 | 0.0023165 | No
26/01/2019 | 03:22:38 | CD23 | Rural Long | Unknown | Unknown | 37 | 281.5676 | 0.076034 | 0.00027004 | No
26/01/2019 | 09:11:20 | MT06 | Rural Long | Planned |  | 46 | 133 | 0.044651 | 0.00033572 | No
26/01/2019 | 09:12:27 | ST41 | Rural Long | Asset failure | LV | 2 | 125 | 0.0018246 | 1.46e-05 | No
26/01/2019 | 10:18:14 | ME231D | Urban | Asset failure | LV | 15 | 164 | 0.0039327 | 2.398e-05 | No
26/01/2019 | 12:03:08 | AP529D | Urban | Asset failure | HV | 1001.6672 | 7.5211 | 0.012044 | 0.0016013 | No
26/01/2019 | 14:57:43 | MI14 | Rural Long | Asset failure | LV | 1 | 357 | 0.0026055 | 7.3e-06 | No
26/01/2019 | 15:14:11 | AP149F | Urban | Asset failure | LV | 4 | 255 | 0.0016306 | 6.39e-06 | No
26/01/2019 | 15:51:17 | CD02 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 430 | 153 | 0.48016 | 0.0031383 | No
26/01/2019 | 15:53:00 | MB65 | Rural Long | Unknown | Unknown | 1 | 21 | 0.00015327 | 7.3e-06 | No
26/01/2019 | 16:35:12 | NL760C | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
26/01/2019 | 17:42:21 | HH121B | Urban | Asset failure | LV | 47 | 16 | 0.0012022 | 7.514e-05 | No
26/01/2019 | 19:54:36 | BM15 | Rural Short | Third Party | Vehicle impact | 3 | 123 | 0.0027491 | 2.235e-05 | No
26/01/2019 | 21:21:36 | G11 | Rural Long | Unknown | Unknown | 60 | 237.4167 | 0.10396 | 0.0004379 | No
26/01/2019 | 21:21:36 | G11 | Rural Long | Unknown | Unknown | 0 | 159.5091 | 0.064028 | 0 | No
26/01/2019 | 21:30:12 | SD31300 | Rural Long | Unknown | Unknown | 1 | 142 | 0.0010364 | 7.3e-06 | No
26/01/2019 | 21:31:32 | PA19 | Rural Long | Weather |  | 2 | 823 | 0.012013 | 1.46e-05 | No
26/01/2019 | 21:41:20 | MG48 | Rural Long | Weather |  | 101 | 172.604 | 0.12723 | 0.00073713 | No
26/01/2019 | 21:46:09 | BM11 | Rural Short | Weather |  | 329.0001 | 74.3577 | 0.18226 | 0.0024511 | No
26/01/2019 | 21:46:09 | BM11 | Rural Short | Weather |  | 0 | 18 | 0.0023691 | 0 | No
26/01/2019 | 22:42:00 | AP132A | Urban | Asset failure | HV | 20 | 259 | 0.0082811 | 3.197e-05 | No
26/01/2019 | 22:45:51 | MG32 | Rural Long | Weather |  | 70 | 21 | 0.010729 | 0.00051088 | No
27/01/2019 | 00:03:47 | SG13 | Rural Short | Planned |  | 1394 | 1 | 0.010386 | 0.010386 | No
27/01/2019 | 07:30:09 | G11 | Rural Long | Unknown | Unknown | 60 | 235.9667 | 0.10333 | 0.0004379 | No
27/01/2019 | 10:30:48 | HH130C | Urban | Unknown | Unknown | 120 | 102 | 0.019568 | 0.00019184 | No
27/01/2019 | 11:40:12 | HH386B | Urban | Asset failure | LV | 26.6666 | 136 | 0.0057979 | 4.263e-05 | No
27/01/2019 | 15:12:55 | MV22 | Rural Short | Unknown | Unknown | 2 | 289 | 0.0043062 | 1.49e-05 | No
27/01/2019 | 15:34:20 | SA16 | Urban | Asset failure | LV | 1 | 132 | 0.00021103 | 1.6e-06 | No
28/01/2019 | 00:12:24 | ST36 | Rural Long | Asset failure | HV | 421 | 138.323 | 0.42501 | 0.0030726 | No
28/01/2019 | 00:30:55 | HH341D | Urban | Asset failure | LV | 1 | 584 | 0.00093363 | 1.6e-06 | No
28/01/2019 | 17:08:10 | HH428C | Urban | Asset failure | LV | 1 | 110 | 0.00017585 | 1.6e-06 | No
28/01/2019 | 17:09:03 | AP146A | Urban | Asset failure | LV | 1 | 126 | 0.00020143 | 1.6e-06 | No
28/01/2019 | 19:49:56 | SA34 | Urban | Asset failure | HV | 1240 | 119.5194 | 0.23693 | 0.0019824 | No
28/01/2019 | 20:19:44 | EL23 | Urban | Asset failure | LV | 1 | 289 | 0.00046202 | 1.6e-06 | No
28/01/2019 | 20:22:59 | AP149D | Urban | Asset failure | LV | 1 | 154 | 0.0002462 | 1.6e-06 | No
28/01/2019 | 22:09:33 | MV53 | Rural Short | Animal | Animal impact | 513 | 86 | 0.32869 | 0.0038219 | No
29/01/2019 | 01:22:53 | HH386A | Urban | Unknown | Unknown | 19.6666 | 390 | 0.012262 | 3.144e-05 | No
29/01/2019 | 03:47:41 | HH102B | Urban | Asset failure | LV | 1 | 474 | 0.00075777 | 1.6e-06 | No
29/01/2019 | 06:45:22 | LM51 | Rural Long | Unknown | Unknown | 19 | 204 | 0.028288 | 0.00013867 | No
29/01/2019 | 08:30:45 | HH177G | Urban | Asset failure | LV | 20.3333 | 64 | 0.0020804 | 3.251e-05 | No
29/01/2019 | 08:53:35 | MTB32 | Rural Long | Planned |  | 150 | 331 | 0.36236 | 0.0010948 | No
29/01/2019 | 09:00:06 | MI16 | Rural Long | Unknown | Unknown | 23 | 45 | 0.0075538 | 0.00016786 | No
29/01/2019 | 09:02:42 | NU12 | Rural Long | Planned |  | 17 | 344 | 0.042681 | 0.00012407 | No
29/01/2019 | 09:04:30 | EL16 | Urban | Planned |  | 40 | 309 | 0.01976 | 6.395e-05 | No
29/01/2019 | 09:10:27 | SM216A | Urban | Planned |  | 110 | 304 | 0.05346 | 0.00017585 | No
29/01/2019 | 09:18:20 | GU17 | Rural Long | Planned |  | 6 | 28 | 0.0012261 | 4.379e-05 | No
29/01/2019 | 09:24:19 | AP125B | Urban | Planned |  | 289 | 21 | 0.0097024 | 0.00046202 | No
29/01/2019 | 09:25:40 | R11 | Rural Long | Planned |  | 60 | 197 | 0.086266 | 0.0004379 | No
29/01/2019 | 09:36:12 | GA15 | Rural Short | Planned |  | 738 | 298.1423 | 1.6392 | 0.0054982 | No
29/01/2019 | 09:37:03 | MTB51 | Rural Long | Planned |  | 9 | 459 | 0.030149 | 6.569e-05 | No
29/01/2019 | 09:38:29 | SA17 | Urban | Planned |  | 62 | 109 | 0.010804 | 9.912e-05 | No
29/01/2019 | 09:48:40 | HH386B | Urban | Planned |  | 100 | 45 | 0.007194 | 0.00015987 | No
29/01/2019 | 10:05:52 | HH386A | Urban | Planned |  | 82 | 254 | 0.033297 | 0.00013109 | No
29/01/2019 | 10:10:11 | HH522C | Urban | Planned |  | 88 | 192 | 0.027011 | 0.00014068 | No
29/01/2019 | 10:16:47 | MTB51 | Rural Long | Planned |  | 3 | 116 | 0.0025398 | 2.19e-05 | No
29/01/2019 | 10:34:48 | AP372A | Urban | Planned |  | 1 | 123 | 0.00019664 | 1.6e-06 | No
29/01/2019 | 11:12:51 | MG24 | Rural Short | Unknown | Unknown | 2 | 7 | 0.0001043 | 1.49e-05 | No
29/01/2019 | 11:52:11 | CM16 | Rural Long | Weather |  | 30 | 107 | 0.023428 | 0.00021895 | No
29/01/2019 | 12:58:53 | SM216E | Urban | Overloads |  | 1 | 249 | 0.00039807 | 1.6e-06 | No
29/01/2019 | 13:25:49 | ME347G | Urban | Asset failure | LV | 1 | 362 | 0.00057872 | 1.6e-06 | No
29/01/2019 | 13:41:25 | SA38 | Urban | Asset failure | LV | 1 | 372 | 0.00059471 | 1.6e-06 | No
29/01/2019 | 13:42:35 | AP355B | Urban | Asset failure | HV | 481 | 34 | 0.026145 | 0.00076896 | No
29/01/2019 | 15:36:31 | MT11 | Rural Long | Asset failure | HV | 1 | 118 | 0.0008612 | 7.3e-06 | No
29/01/2019 | 15:37:25 | AP227C | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
29/01/2019 | 16:51:43 | CM18 | Rural Long | Unknown | Unknown | 3 | 44 | 0.00096338 | 2.19e-05 | No
29/01/2019 | 17:21:29 | SD46100 | Rural Long | Asset failure | Subtransmission | 616 | 85 | 0.38214 | 0.0044958 | No
29/01/2019 | 17:43:22 | SA520A | Urban | Asset failure | LV | 4 | 134 | 0.00085689 | 6.39e-06 | No
29/01/2019 | 19:25:37 | HH145C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1514 | 40 | 0.096816 | 0.0024204 | No
29/01/2019 | 19:27:46 | MI17 | Rural Long | Unknown | Unknown | 27 | 101 | 0.019903 | 0.00019706 | No
29/01/2019 | 20:27:20 | NL234C | Urban | Asset failure | LV | 62 | 159 | 0.01576 | 9.912e-05 | No
29/01/2019 | 20:28:37 | NL234C | Urban | Asset failure | LV | 44 | 146 | 0.01027 | 7.034e-05 | No
29/01/2019 | 20:33:16 | EL260C | Urban | Animal | Animal impact | 9 | 53 | 0.00076257 | 1.439e-05 | No
29/01/2019 | 21:06:25 | W06 | Rural Long | Unknown | Unknown | 313 | 157.2141 | 0.35914 | 0.0022844 | No
29/01/2019 | 21:06:25 | W06 | Rural Long | Unknown | Unknown | 0 | 58.655 | 0.20719 | 0 | No
29/01/2019 | 22:14:58 | SM216A | Urban | Asset failure | LV | 21.3333 | 31 | 0.0010573 | 3.411e-05 | No
29/01/2019 | 23:40:33 | SG03 | Rural Short | Animal | Animal impact | 38 | 141 | 0.039918 | 0.00028311 | No
30/01/2019 | 06:17:35 | VH22 | Rural Short | Animal | Animal impact | 70 | 169 | 0.088135 | 0.00052151 | No
30/01/2019 | 06:28:37 | NA29 | Rural Long | Asset failure | HV | 1 | 249 | 0.0018173 | 7.3e-06 | No
30/01/2019 | 06:43:23 | MG51 | Rural Long | Unknown | Unknown | 15 | 186 | 0.020362 | 0.00010948 | No
30/01/2019 | 06:43:38 | VH22 | Rural Short | Weather |  | 22 | 334 | 0.054744 | 0.0001639 | No
30/01/2019 | 06:54:56 | MTB32 | Rural Long | Asset failure | LV | 1 | 119 | 0.0008685 | 7.3e-06 | No
30/01/2019 | 08:01:40 | G28 | Rural Long | Planned |  | 2 | 35 | 0.00051088 | 1.46e-05 | No
30/01/2019 | 08:28:39 | GU43 | Rural Long | Asset failure | LV | 2 | 61 | 0.0008904 | 1.46e-05 | No
30/01/2019 | 08:30:33 | GA28 | Rural Long | Planned |  | 166 | 235 | 0.28471 | 0.0012115 | No
30/01/2019 | 08:36:27 | AP425B | Urban | Other |  | 1 | 109 | 0.00017426 | 1.6e-06 | No
30/01/2019 | 08:39:14 | MG17 | Rural Long | Unknown | Unknown | 14.6667 | 4 | 0.00042817 | 0.00010704 | No
30/01/2019 | 08:54:09 | SA520E | Urban | Planned |  | 1 | 108 | 0.00017266 | 1.6e-06 | No
30/01/2019 | 09:01:27 | MTB13 | Rural Short | Planned |  | 23 | 290 | 0.049693 | 0.00017135 | No
30/01/2019 | 09:04:09 | MTB41 | Rural Short | Planned |  | 74 | 372 | 0.20509 | 0.00055131 | No
30/01/2019 | 09:04:36 | HH130B | Urban | Overloads |  | 1 | 183 | 0.00029256 | 1.6e-06 | No
30/01/2019 | 09:08:43 | HH130A | Urban | Planned |  | 83 | 84 | 0.011146 | 0.00013269 | No
30/01/2019 | 09:10:43 | SA17 | Urban | Planned |  | 131 | 241 | 0.050472 | 0.00020943 | No
30/01/2019 | 09:13:20 | SA744D / SA42 | Urban | Planned |  | 1201 | 112.4138 | 0.21584 | 0.00192 | No
30/01/2019 | 09:18:14 | EL20 | Urban | Planned |  | 27 | 77 | 0.0033237 | 4.316e-05 | No
30/01/2019 | 09:20:24 | EL19 | Urban | Asset failure | LV | 13 | 48 | 0.00099757 | 2.078e-05 | No
30/01/2019 | 09:25:46 | VH33 | Rural Short | Planned |  | 24 | 169 | 0.030218 | 0.0001788 | No
30/01/2019 | 09:39:31 | MV63 | Rural Short | Planned |  | 57 | 187 | 0.079411 | 0.00042466 | No
30/01/2019 | 09:42:28 | SM411F | Urban | Planned |  | 146 | 163 | 0.038045 | 0.00023341 | No
30/01/2019 | 09:59:43 | PL08 | Urban | Planned |  | 5 | 261 | 0.0020863 | 7.99e-06 | No
30/01/2019 | 10:05:14 | MV13 | Rural Short | Planned |  | 18 | 199 | 0.026686 | 0.0001341 | No
30/01/2019 | 10:10:28 | BT15 | Rural Long | Asset failure | LV | 1 | 223 | 0.0016275 | 7.3e-06 | No
30/01/2019 | 10:29:09 | MT18 | Rural Long | Asset failure | HV | 35 | 130.8286 | 0.033419 | 0.00025544 | No
30/01/2019 | 11:31:54 | GA15 | Rural Short | Planned |  | 4 | 24 | 0.00071521 | 2.98e-05 | No
30/01/2019 | 11:44:38 | MTB61 | Rural Short | Asset failure | LV | 1 | 142 | 0.0010579 | 7.45e-06 | No
30/01/2019 | 11:50:41 | MI02 | Rural Short | Unknown | Unknown | 1 | 19 | 0.00014155 | 7.45e-06 | No
30/01/2019 | 12:34:02 | HH341F | Urban | Overloads |  | 11.3333 | 155 | 0.0028083 | 1.812e-05 | No
30/01/2019 | 16:36:52 | MG06 | Rural Short | Unknown | Unknown | 1 | 53 | 0.00039486 | 7.45e-06 | No
30/01/2019 | 16:58:35 | SM350F | Urban | Asset failure | LV | 1 | 71 | 0.00011351 | 1.6e-06 | No
30/01/2019 | 17:02:13 | HH177E | Urban | Asset failure | LV | 37.6666 | 98 | 0.0059012 | 6.022e-05 | No
30/01/2019 | 17:09:05 | PL27 | Rural Long | Unknown | Unknown | 27 | 25 | 0.0049264 | 0.00019706 | No
30/01/2019 | 17:16:30 | VH21 | Rural Short | Planned |  | 2257 | 4 | 0.06726 | 0.016815 | No
30/01/2019 | 17:34:07 | SA36 | Urban | Asset failure | LV | 11 | 103 | 0.0018113 | 1.759e-05 | No
30/01/2019 | 17:45:48 | PP04 | Rural Short | Asset failure | LV | 2 | 134 | 0.0019966 | 1.49e-05 | No
30/01/2019 | 19:30:14 | PP04 | Rural Short | Unknown | Unknown | 1 | 13 | 9.685e-05 | 7.45e-06 | No
30/01/2019 | 20:02:05 | VH21 | Rural Short | Weather |  | 951 | 375.9937 | 2.6639 | 0.0070851 | No
30/01/2019 | 20:10:04 | MG09 | Rural Short | Asset failure | LV | 1 | 112 | 0.00083442 | 7.45e-06 | No
30/01/2019 | 20:45:52 | MV32 | Rural Short | Animal | Animal impact | 5 | 246 | 0.0091637 | 3.725e-05 | No
30/01/2019 | 20:52:01 | AP355A | Urban | Unknown | Unknown | 29 | 77 | 0.0035698 | 4.636e-05 | No
31/01/2019 | 01:18:13 | HH432F | Urban | Asset failure | LV | 1 | 512 | 0.00081852 | 1.6e-06 | No
31/01/2019 | 01:35:02 | SG03 | Rural Short | Animal | Animal impact | 1037 | 97.7599 | 0.75527 | 0.0077258 | No
31/01/2019 | 05:03:40 | W24 | Rural Long | Third Party | Vehicle impact | 12 | 539 | 0.047206 | 8.758e-05 | No
31/01/2019 | 06:20:02 | MG17 | Rural Long | Asset failure | HV | 982 | 102.6813 | 0.73591 | 0.007167 | No
31/01/2019 | 07:33:00 | ME231C | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 329 | 0.0010519 | 3.2e-06 | No
31/01/2019 | 07:54:57 | SSD750 | Urban | Planned |  | 3034 | 369 | 1.7898 | 0.0048504 | No
31/01/2019 | 07:54:57 | SSD750 | Rural Short | Planned |  | 695 | 369 | 1.9106 | 0.0051779 | No
31/01/2019 | 07:54:57 | SSD750 | Rural Long | Planned |  | 4570 | 369 | 12.3074 | 0.033353 | No
31/01/2019 | 08:13:40 | VH51 | Rural Short | Planned |  | 12 | 472 | 0.042198 | 8.94e-05 | No
31/01/2019 | 08:33:12 | SG03 | Rural Short | Planned |  | 41 | 376 | 0.11485 | 0.00030546 | No
31/01/2019 | 09:02:54 | HH429C | Urban | Planned |  | 233 | 139 | 0.051776 | 0.00037249 | No
31/01/2019 | 09:10:30 | MB66 | Rural Long | Planned |  | 1 | 38 | 0.00027734 | 7.3e-06 | No
31/01/2019 | 09:11:27 | NA52 | Rural Long | Planned |  | 60 | 381 | 0.16684 | 0.0004379 | No
31/01/2019 | 09:35:47 | HH341H | Urban | Planned |  | 54 | 270 | 0.023309 | 8.633e-05 | No
31/01/2019 | 09:38:18 | GA800A | Rural Short | Planned |  | 420 | 134.3667 | 0.42044 | 0.0031291 | No
31/01/2019 | 09:45:00 | SA17 | Urban | Planned |  | 122 | 63 | 0.012287 | 0.00019504 | No
31/01/2019 | 09:45:46 | CN31 | Rural Long | Planned |  | 1 | 70 | 0.00051088 | 7.3e-06 | No
31/01/2019 | 10:16:40 | MT15 | Rural Long | Planned |  | 2 | 144 | 0.0021019 | 1.46e-05 | No
31/01/2019 | 10:20:04 | AP373D | Urban | Third Party | Vehicle impact | 17 | 366 | 0.009947 | 2.718e-05 | No
31/01/2019 | 10:48:51 | MV53 | Rural Short | Planned |  | 3 | 5 | 0.00011175 | 2.235e-05 | No
31/01/2019 | 11:56:51 | M13 | Rural Long | Planned |  | 1 | 50 | 0.00036492 | 7.3e-06 | No
31/01/2019 | 11:59:47 | CN02 | Rural Long | Unknown | Unknown | 12 | 65 | 0.0056927 | 8.758e-05 | No
31/01/2019 | 12:42:50 | SA38 | Urban | Animal | Animal impact | 1 | 469 | 0.00074978 | 1.6e-06 | No
31/01/2019 | 12:47:11 | GA800A | Rural Short | Asset failure | HV | 177 | 43 | 0.056703 | 0.0013187 | No
31/01/2019 | 13:47:03 | NU25 | Rural Long | Asset failure | LV | 1 | 98 | 0.00071524 | 7.3e-06 | No
31/01/2019 | 14:09:14 | SM349B | Urban | Unknown | Unknown | 43.3334 | 39 | 0.0027018 | 6.928e-05 | No
31/01/2019 | 14:52:25 | MI08 | Rural Long | Unknown | Unknown | 2 | 289 | 0.0042184 | 1.46e-05 | No
31/01/2019 | 15:16:25 | EL16 | Urban | Unknown | Unknown | 252 | 101 | 0.040689 | 0.00040287 | No
31/01/2019 | 16:08:26 | VH23 | Rural Short | Asset failure | LV | 1 | 196 | 0.0014602 | 7.45e-06 | No
31/01/2019 | 17:03:03 | HH341K | Urban | Vegetation | Grow-in - NSP responsibility | 18.6666 | 83 | 0.0024769 | 2.984e-05 | No
31/01/2019 | 19:34:58 | NL210A | Urban | Overloads |  | 1 | 315 | 0.00050358 | 1.6e-06 | No
31/01/2019 | 21:23:56 | HH107A | Urban | Asset failure | LV | 43 | 95 | 0.0065306 | 6.874e-05 | No
31/01/2019 | 21:24:47 | AP373C | Urban | Asset failure | LV | 76 | 94 | 0.011421 | 0.0001215 | No
1/02/2019 | 00:11:19 | HH145B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1299 | 34 | 0.070607 | 0.0020767 | No
1/02/2019 | 00:36:12 | HH145B | Urban | Asset failure | LV | 28.6666 | 638 | 0.029239 | 4.583e-05 | No
1/02/2019 | 00:51:09 | HH341G | Urban | Vegetation | Grow-in - NSP responsibility | 25 | 322 | 0.012869 | 3.997e-05 | No
1/02/2019 | 01:18:13 | HH121A | Urban | Vegetation | Grow-in - NSP responsibility | 22.6666 | 112 | 0.0040585 | 3.624e-05 | No
1/02/2019 | 02:03:56 | HH409C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 44.6666 | 51 | 0.0036418 | 7.141e-05 | No
1/02/2019 | 02:23:24 | PL24 | Rural Long | Unknown | Unknown | 44 | 492.2273 | 0.15807 | 0.00032113 | No
1/02/2019 | 02:28:17 | HH118D | Urban | Unknown | Unknown | 28.3333 | 450 | 0.020383 | 4.53e-05 | No
1/02/2019 | 02:41:22 | HH522B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 268 | 417.2724 | 0.17878 | 0.00042844 | No
1/02/2019 | 02:52:38 | HH121C | Urban | Asset failure | LV | 11.3333 | 535 | 0.0096933 | 1.812e-05 | No
1/02/2019 | 02:59:00 | HH121C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 53.3334 | 330 | 0.028137 | 8.526e-05 | No
1/02/2019 | 03:00:57 | SM126A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 411 | 139.9124 | 0.09193 | 0.00065706 | No
1/02/2019 | 03:57:30 | HH118A | Urban | Weather |  | 14.6667 | 329 | 0.0077141 | 2.345e-05 | No
1/02/2019 | 04:28:11 | SM179D | Urban | Unknown | Unknown | 26.6666 | 305 | 0.013003 | 4.263e-05 | No
1/02/2019 | 05:22:53 | HH121E | Urban | Asset failure | LV | 8 | 337 | 0.00431 | 1.279e-05 | No
1/02/2019 | 05:44:12 | HH130F | Urban | Vegetation | Grow-in - NSP responsibility | 19.3333 | 371 | 0.011467 | 3.091e-05 | No
1/02/2019 | 06:14:00 | NU05 | Rural Short | Other |  | 1 | 177 | 0.0013187 | 7.45e-06 | No
1/02/2019 | 06:35:56 | SM374B | Urban | Asset failure | LV | 103 | 153 | 0.025194 | 0.00016466 | No
1/02/2019 | 06:38:53 | HH386E | Urban | Weather |  | 1 | 376 | 0.0006011 | 1.6e-06 | No
1/02/2019 | 07:13:01 | HH121G | Urban | Vegetation | Grow-in - NSP responsibility | 66.6667 | 106 | 0.011297 | 0.00010658 | No
1/02/2019 | 08:06:26 | HH145A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 5 | 349 | 0.0027897 | 7.99e-06 | No
1/02/2019 | 08:32:16 | HH130F | Urban | Planned |  | 1 | 323 | 0.00051637 | 1.6e-06 | No
1/02/2019 | 08:45:41 | SA33 | Urban | Asset failure | LV | 1 | 325 | 0.00051957 | 1.6e-06 | No
1/02/2019 | 08:48:08 | MB81 | Rural Long | Planned |  | 26 | 192 | 0.036433 | 0.00018976 | No
1/02/2019 | 09:00:04 | SG06 | Rural Short | Planned |  | 45 | 107 | 0.035872 | 0.00033526 | No
1/02/2019 | 09:14:25 | MTB53 | Rural Long | Planned |  | 2 | 331 | 0.0048315 | 1.46e-05 | No
1/02/2019 | 09:24:16 | HH428C | Urban | Planned |  | 39 | 127 | 0.0079182 | 6.235e-05 | No
1/02/2019 | 09:25:15 | CN02 | Rural Long | Unknown | Unknown | 12 | 184 | 0.016115 | 8.758e-05 | No
1/02/2019 | 09:31:07 | MTB54 | Rural Long | Planned |  | 242 | 317 | 0.55988 | 0.0017662 | No
1/02/2019 | 09:33:15 | W28 | Rural Long | Planned |  | 3 | 147 | 0.0032186 | 2.19e-05 | No
1/02/2019 | 09:34:45 | PA04 | Rural Short | Planned |  | 58 | 93 | 0.040186 | 0.00043211 | No
1/02/2019 | 09:40:32 | HH130A | Urban | Planned |  | 166 | 224 | 0.059445 | 0.00026538 | No
1/02/2019 | 09:43:21 | G15 | Rural Long | Planned |  | 83 | 259 | 0.15689 | 0.00060576 | No
1/02/2019 | 09:51:05 | ST41 | Rural Long | Planned |  | 10 | 252 | 0.018392 | 7.298e-05 | No
1/02/2019 | 10:00:59 | CBD366C | CBD | Planned |  | 2 | 5759 | 2.2359 | 0.00038824 | No
1/02/2019 | 10:10:57 | MTB41 | Rural Short | Planned |  | 2 | 68 | 0.0010132 | 1.49e-05 | No
1/02/2019 | 10:17:15 | GA26 | Urban | Planned |  | 60 | 252 | 0.024172 | 9.592e-05 | No
1/02/2019 | 10:18:40 | HH409D | Urban | Planned |  | 33 | 121 | 0.0063835 | 5.276e-05 | No
1/02/2019 | 10:20:26 | GU41 | Rural Long | Planned |  | 47 | 280 | 0.096046 | 0.00034302 | No
1/02/2019 | 10:31:10 | SA744D | Urban | Planned |  | 184 | 33 | 0.0097071 | 0.00029416 | No
1/02/2019 | 10:31:48 | HH118B | Urban | Weather |  | 19.3333 | 70 | 0.0021635 | 3.091e-05 | No
1/02/2019 | 13:03:59 | MI07 | Rural Long | Unknown | Unknown | 3 | 52 | 0.0011385 | 2.19e-05 | No
1/02/2019 | 13:38:20 | R15 | Rural Long | Planned |  | 1 | 70 | 0.00051088 | 7.3e-06 | No
1/02/2019 | 14:39:52 | LX21 | Rural Short | Asset failure | HV | 2 | 232 | 0.0034569 | 1.49e-05 | No
1/02/2019 | 14:51:48 | HH386D | Urban | Asset failure | LV | 1 | 139 | 0.00022222 | 1.6e-06 | No
1/02/2019 | 15:22:07 | HH432E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 583 | 147.8113 | 0.13776 | 0.00093203 | No
1/02/2019 | 15:38:11 | SA41 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 54 | 8.633e-05 | 1.6e-06 | No
1/02/2019 | 15:38:50 | HH409D | Urban | Asset failure | LV | 2 | 130 | 0.00041566 | 3.2e-06 | No
1/02/2019 | 16:48:12 | GU17 | Rural Long | Asset failure | HV | 9 | 2 | 0.00013137 | 6.569e-05 | No
1/02/2019 | 18:09:16 | AP146C | Urban | Asset failure | LV | 20 | 123 | 0.0039327 | 3.197e-05 | No
1/02/2019 | 18:11:54 | HH386C | Urban | Overloads |  | 22 | 20 | 0.00070342 | 3.517e-05 | No
1/02/2019 | 22:03:38 | WK42 | Rural Short | Asset failure | LV | 2 | 94 | 0.0014006 | 1.49e-05 | No
1/02/2019 | 22:22:52 | HH145B | Urban | Asset failure | LV | 35.3333 | 140 | 0.0079081 | 5.649e-05 | No
1/02/2019 | 23:14:37 | BT02 | Rural Long | Animal | Animal impact | 2 | 617 | 0.0090061 | 1.46e-05 | No
1/02/2019 | 23:27:15 | LM53 | Rural Long | Unknown | Unknown | 1 | 180 | 0.0013137 | 7.3e-06 | No
2/02/2019 | 00:34:43 | HH177G | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
2/02/2019 | 03:58:15 | SM126D | Urban | Animal | Animal impact | 62 | 381 | 0.037764 | 9.912e-05 | No
2/02/2019 | 04:31:28 | PL24 | Rural Long | Asset failure | HV | 44 | 317 | 0.1018 | 0.00032113 | No
2/02/2019 | 07:00:08 | VH17 | Rural Short | Unknown | Unknown | 20 | 127 | 0.018923 | 0.000149 | No
2/02/2019 | 08:25:16 | R18 | Rural Long | Unknown | Unknown | 3 | 101 | 0.0022114 | 2.19e-05 | No
2/02/2019 | 08:44:27 | NL111C | Urban | Planned |  | 2 | 391 | 0.0012502 | 3.2e-06 | No
2/02/2019 | 08:50:43 | G17 | Rural Long | Animal | Animal impact | 4 | 194 | 0.0056635 | 2.919e-05 | No
2/02/2019 | 09:19:53 | HH432E | Urban | Weather |  | 2 | 144 | 0.00046042 | 3.2e-06 | No
2/02/2019 | 10:23:32 | SM350B | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
2/02/2019 | 11:04:25 | HH429C | Urban | Asset failure | LV | 1 | 167 | 0.00026698 | 1.6e-06 | No
2/02/2019 | 13:21:05 | BM21 | Rural Short | Asset failure | LV | 1 | 104 | 0.00077482 | 7.45e-06 | No
2/02/2019 | 14:36:18 | AP227A | Urban | Asset failure | LV | 62 | 109 | 0.010804 | 9.912e-05 | No
2/02/2019 | 14:50:15 | AP214D | Urban | Unknown | Unknown | 37 | 136 | 0.0080445 | 5.915e-05 | No
2/02/2019 | 15:50:45 | SM411D | Urban | Asset failure | LV | 2 | 418 | 0.0013365 | 3.2e-06 | No
2/02/2019 | 16:22:42 | AP424F | Urban | Overloads |  | 13 | 61 | 0.0012677 | 2.078e-05 | No
2/02/2019 | 16:42:34 | HH432C | Urban | Unknown | Unknown | 20.3333 | 39 | 0.0012677 | 3.251e-05 | No
2/02/2019 | 16:51:38 | AP355A | Urban | Asset failure | LV | 36.6666 | 82 | 0.0048067 | 5.862e-05 | No
2/02/2019 | 17:44:39 | PA02 | Urban | Overloads |  | 1 | 95 | 0.00015187 | 1.6e-06 | No
2/02/2019 | 19:46:39 | SM216B | Urban | Overloads |  | 30 | 77 | 0.0036929 | 4.796e-05 | No
2/02/2019 | 22:06:37 | MV61 | Urban | Overloads |  | 1 | 156 | 0.00024939 | 1.6e-06 | No
2/02/2019 | 22:06:51 | HH409D | Urban | Overloads |  | 18.6666 | 63 | 0.00188 | 2.984e-05 | No
2/02/2019 | 23:01:59 | HH496F | Urban | Unknown | Unknown | 24.6667 | 43 | 0.0016957 | 3.943e-05 | No
3/02/2019 | 00:23:37 | HH121G | Urban | Planned |  | 30 | 454 | 0.021774 | 4.796e-05 | No
3/02/2019 | 01:16:00 | HH409E | Urban | Overloads |  | 37 | 151 | 0.0089318 | 5.915e-05 | No
3/02/2019 | 05:54:26 | SG10 | Rural Short | Asset failure | LV | 14.6667 | 323 | 0.035294 | 0.00010927 | No
3/02/2019 | 06:41:00 | SB17 | Rural Long | Unknown | Unknown | 36 | 275.4444 | 0.07237 | 0.00026274 | No
3/02/2019 | 08:10:34 | SA19 | Urban | Planned |  | 44 | 212 | 0.014912 | 7.034e-05 | No
3/02/2019 | 08:16:14 | AP149D | Urban | Planned |  | 1 | 355 | 0.00056753 | 1.6e-06 | No
3/02/2019 | 08:59:17 | SM402A | Urban | Planned |  | 10 | 212 | 0.0033892 | 1.599e-05 | No
3/02/2019 | 09:08:00 | CM10 | Rural Long | Unknown | Unknown | 22 | 176 | 0.028259 | 0.00016056 | No
3/02/2019 | 09:11:01 | SSD746 | Urban | Planned |  | 1 | 353 | 0.00056433 | 1.6e-06 | No
3/02/2019 | 11:16:18 | HH121B | Urban | Asset failure | LV | 1 | 203 | 0.00032453 | 1.6e-06 | No
3/02/2019 | 11:58:22 | NL111C | Urban | Asset failure | LV | 36 | 101 | 0.0058128 | 5.755e-05 | No
3/02/2019 | 13:53:10 | SM172C | Urban | Asset failure | LV | 5 | 112 | 0.00089526 | 7.99e-06 | No
3/02/2019 | 13:53:52 | SM172C | Urban | Asset failure | LV | 18 | 111 | 0.0031942 | 2.878e-05 | No
3/02/2019 | 14:13:54 | SM126B | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
3/02/2019 | 14:29:05 | GA25 | Rural Short | Unknown | Unknown | 33.6666 | 117 | 0.029346 | 0.00025082 | No
3/02/2019 | 15:54:55 | HH432F | Urban | Asset failure | LV | 66 | 28 | 0.0029544 | 0.00010551 | No
3/02/2019 | 16:01:22 | BT27 | Rural Long | Asset failure | Distribution substation | 57 | 282.8772 | 0.11768 | 0.00041601 | No
3/02/2019 | 17:50:15 | EL01N | Urban | Asset failure | LV | 1 | 104 | 0.00016626 | 1.6e-06 | No
3/02/2019 | 18:14:03 | MV42 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 32 | 404 | 0.096316 | 0.0002384 | No
3/02/2019 | 19:00:00 | SD54300 | Rural Long | Asset failure | Subtransmission | 833 | 45.1104 | 0.27425 | 0.0060795 | No
3/02/2019 | 19:39:08 | SM411F | Urban | Asset failure | LV | 25.6666 | 79 | 0.0032416 | 4.103e-05 | No
3/02/2019 | 21:26:42 | AP125D | Urban | Asset failure | LV | 1 | 219 | 0.00035011 | 1.6e-06 | No
3/02/2019 | 22:05:37 | HH522C | Urban | Unknown | Unknown | 2473 | 109.2859 | 0.43206 | 0.0039535 | No
3/02/2019 | 22:31:27 | HH130A | Urban | Third Party | Other | 1 | 158 | 0.00025259 | 1.6e-06 | No
4/02/2019 | 02:16:52 | SM411D | Urban | Unknown | Unknown | 21.6666 | 88 | 0.0030481 | 3.464e-05 | No
4/02/2019 | 03:16:52 | HH177F | Urban | Asset failure | LV | 16.3333 | 29 | 0.00075724 | 2.611e-05 | No
4/02/2019 | 03:46:07 | AP214A | Urban | Animal | Animal impact | 1579 | 122.8854 | 0.3102 | 0.0025243 | No
4/02/2019 | 07:00:34 | CV19 | Rural Long | Planned |  | 2 | 306 | 0.0044666 | 1.46e-05 | No
4/02/2019 | 07:23:29 | WHY04 | Urban | Asset failure | LV | 1 | 230 | 0.0003677 | 1.6e-06 | No
4/02/2019 | 07:37:04 | NU21 | Rural Long | Weather |  | 2 | 104 | 0.001518 | 1.46e-05 | No
4/02/2019 | 07:56:40 | HH409C | Urban | Animal | Animal nesting/burrowing, etc and other | 134 | 42 | 0.0089973 | 0.00021422 | No
4/02/2019 | 07:59:46 | ST44 | Rural Long | Planned |  | 83 | 335.4699 | 0.20321 | 0.00060576 | No
4/02/2019 | 08:21:30 | EL01N | Urban | Overloads |  | 34.6666 | 97 | 0.0053758 | 5.542e-05 | No
4/02/2019 | 08:33:44 | EL01N | Urban | Unknown | Unknown | 104 | 78 | 0.012968 | 0.00016626 | No
4/02/2019 | 08:33:44 | EL01N | Urban | Planned |  | 939 | 2 | 0.0030023 | 0.0015012 | No
4/02/2019 | 08:58:28 | LX31 | Rural Short | Planned |  | 5 | 161 | 0.0059974 | 3.725e-05 | No
4/02/2019 | 09:05:14 | MV15 | Rural Short | Planned |  | 11 | 154 | 0.012621 | 8.195e-05 | No
4/02/2019 | 09:09:39 | HH341G | Urban | Planned |  | 2 | 40 | 0.00012789 | 3.2e-06 | No
4/02/2019 | 09:11:56 | HH107C | Urban | Planned |  | 58 | 295 | 0.027353 | 9.272e-05 | No
4/02/2019 | 09:14:04 | PL803C | Urban | Planned |  | 1 | 312 | 0.00049879 | 1.6e-06 | No
4/02/2019 | 09:14:32 | ST36 | Rural Long | Planned |  | 206 | 367 | 0.55177 | 0.0015035 | No
4/02/2019 | 09:18:46 | CL11 | Rural Short | Planned |  | 61 | 272 | 0.12361 | 0.00045446 | No
4/02/2019 | 09:34:07 | SM349F | Urban | Planned |  | 161 | 14 | 0.0036034 | 0.00025739 | No
4/02/2019 | 10:25:40 | WHY10 | Urban | Asset failure | LV | 1 | 163 | 0.00026058 | 1.6e-06 | No
4/02/2019 | 10:34:19 | MG42 | Rural Short | Planned |  | 10 | 214 | 0.015943 | 7.45e-05 | No
4/02/2019 | 10:48:25 | CN52 | Rural Long | Planned |  | 2 | 113 | 0.0016494 | 1.46e-05 | No
4/02/2019 | 11:15:18 | SM349C | Urban | Planned |  | 893 | 1 | 0.0014276 | 0.0014276 | No
4/02/2019 | 11:27:44 | EL19 | Urban | Third Party | Other | 2 | 15 | 4.796e-05 | 3.2e-06 | No
4/02/2019 | 11:42:10 | MG17 | Rural Long | Unknown | Unknown | 20 | 123 | 0.017954 | 0.00014597 | No
4/02/2019 | 12:37:42 | CM01 | Rural Long | Planned |  | 2 | 30 | 0.0004379 | 1.46e-05 | No
4/02/2019 | 13:11:47 | G11 | Rural Long | Unknown | Unknown | 5 | 267 | 0.0097433 | 3.649e-05 | No
4/02/2019 | 14:39:14 | NU15 | Rural Long | Unknown | Unknown | 59.3333 | 57 | 0.024683 | 0.00043303 | No
4/02/2019 | 16:15:43 | CN53 | Rural Long | Asset failure | HV | 2 | 48 | 0.00070064 | 1.46e-05 | No
4/02/2019 | 16:38:54 | BM31 | Rural Short | Asset failure | LV | 1 | 202 | 0.0015049 | 7.45e-06 | No
4/02/2019 | 18:01:33 | AP424B | Urban | Asset failure | LV | 78 | 54 | 0.0067336 | 0.0001247 | No
4/02/2019 | 22:15:52 | EL01R | Urban | Animal | Animal impact | 86.6667 | 126 | 0.017458 | 0.00013855 | No
4/02/2019 | 23:07:25 | MTB21 | Rural Short | Unknown | Unknown | 30 | 159 | 0.035537 | 0.0002235 | No
5/02/2019 | 00:19:51 | EL01R | Urban | Animal | Animal impact | 933 | 2 | 0.0029831 | 0.0014916 | No
5/02/2019 | 01:22:52 | ME200F | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 131 | 0.00020943 | 1.6e-06 | No
5/02/2019 | 04:15:18 | HH145D | Urban | Vegetation | Grow-in - NSP responsibility | 24 | 243 | 0.0093235 | 3.837e-05 | No
5/02/2019 | 04:24:59 | GA01 | Urban | Asset failure | LV | 19 | 73 | 0.0022174 | 3.037e-05 | No
5/02/2019 | 04:33:35 | MI29 | Rural Short | Animal | Animal impact | 1 | 103 | 0.00076737 | 7.45e-06 | No
5/02/2019 | 04:33:35 | SD49800 | Rural Short | Animal | Animal impact | 4 | 113.75 | 0.0033898 | 2.98e-05 | No
5/02/2019 | 04:47:56 | HH130E | Urban | Asset failure | HV | 543.3336 | 108.5939 | 0.094326 | 0.00086861 | No
5/02/2019 | 04:54:42 | MV64 | Urban | Asset failure | LV | 8 | 57 | 0.000729 | 1.279e-05 | No
5/02/2019 | 05:29:02 | HH409F | Urban | Other |  | 23 | 248 | 0.0091188 | 3.677e-05 | No
5/02/2019 | 07:10:55 | NL451E | Urban | Unknown | Unknown | 12 | 216 | 0.0041438 | 1.918e-05 | No
5/02/2019 | 08:10:09 | HK05 | Rural Long | Planned |  | 35 | 454 | 0.11597 | 0.00025544 | No
5/02/2019 | 08:41:26 | YK23 | Rural Long | Overloads |  | 1 | 35 | 0.00025544 | 7.3e-06 | No
5/02/2019 | 08:43:41 | AP372F | Urban | Planned |  | 2 | 61 | 0.00019504 | 3.2e-06 | No
5/02/2019 | 08:44:27 | EL09 | Urban | Asset failure | LV | 1 | 165 | 0.00026378 | 1.6e-06 | No
5/02/2019 | 08:49:25 | NL760C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 21.6666 | 39 | 0.0013509 | 3.464e-05 | No
5/02/2019 | 08:53:56 | SM179C | Urban | Asset failure | LV | 1 | 226 | 0.0003613 | 1.6e-06 | No
5/02/2019 | 08:56:57 | EL17 | Urban | Planned |  | 75 | 59 | 0.0070741 | 0.0001199 | No
5/02/2019 | 09:04:54 | LX24 | Rural Short | Planned |  | 18 | 220 | 0.029503 | 0.0001341 | No
5/02/2019 | 09:05:14 | GA28 | Rural Long | Planned |  | 357 | 245 | 0.63835 | 0.0026055 | No
5/02/2019 | 09:09:10 | HH130A / HH130F | Urban | Planned |  | 2024 | 49.5128 | 0.16021 | 0.0032357 | No
5/02/2019 | 09:09:24 | AP372D | Urban | Planned |  | 148 | 296 | 0.070035 | 0.0002366 | No
5/02/2019 | 09:12:11 | SD41300 | Rural Short | Planned |  | 1 | 190 | 0.0014155 | 7.45e-06 | No
5/02/2019 | 09:15:37 | EL02 / EL04 | Urban | Planned |  | 290 | 248.331 | 0.11513 | 0.00046362 | No
5/02/2019 | 09:18:30 | VH72 | Rural Short | Planned |  | 16 | 144 | 0.017165 | 0.0001192 | No
5/02/2019 | 09:43:12 | VH15 | Rural Short | Planned |  | 33 | 182 | 0.044746 | 0.00024585 | No
5/02/2019 | 09:43:58 | BT02 | Rural Long | Planned |  | 3 | 286 | 0.006262 | 2.19e-05 | No
5/02/2019 | 09:51:09 | HH409D | Urban | Planned |  | 397 | 109 | 0.069179 | 0.00063467 | No
5/02/2019 | 10:04:51 | M21 | Rural Long | Unknown | Unknown | 1 | 1375 | 0.010035 | 7.3e-06 | No
5/02/2019 | 10:30:07 | MV13 | Rural Short | Planned |  | 36 | 258 | 0.069197 | 0.00026821 | No
5/02/2019 | 10:35:44 | AP424D | Urban | Planned |  | 157 | 245 | 0.061493 | 0.00025099 | No
5/02/2019 | 10:36:49 | AP372B | Urban | Planned |  | 58 | 238 | 0.022068 | 9.272e-05 | No
5/02/2019 | 11:36:34 | MV13 | Rural Short | Planned |  | 26 | 161 | 0.031186 | 0.0001937 | No
5/02/2019 | 12:29:06 | HH177E | Urban | Unknown | Unknown | 109 | 23 | 0.0040079 | 0.00017426 | No
5/02/2019 | 13:02:28 | WHY06 | Urban | Asset failure | LV | 1 | 52 | 8.313e-05 | 1.6e-06 | No
5/02/2019 | 13:11:56 | NL451E | Urban | Unknown | Unknown | 12 | 75 | 0.0014388 | 1.918e-05 | No
5/02/2019 | 13:57:42 | SM350H | Urban | Asset failure | LV | 1 | 157 | 0.00025099 | 1.6e-06 | No
5/02/2019 | 15:27:08 | NA05 | Rural Long | Unknown | Unknown | 3 | 5 | 0.00010948 | 2.19e-05 | No
5/02/2019 | 15:35:43 | ST12 | Rural Short | Asset failure | LV | 1 | 192 | 0.0014304 | 7.45e-06 | No
5/02/2019 | 18:39:32 | NL115F | Urban | Asset failure | LV | 1 | 165 | 0.00026378 | 1.6e-06 | No
5/02/2019 | 18:55:45 | HH177E | Urban | Asset failure | LV | 1 | 143 | 0.00022861 | 1.6e-06 | No
5/02/2019 | 19:05:31 | SA520E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19.3333 | 79 | 0.0024417 | 3.091e-05 | No
5/02/2019 | 19:15:11 | HH177E | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
5/02/2019 | 20:21:03 | AP146C | Urban | Asset failure | LV | 1 | 58 | 9.272e-05 | 1.6e-06 | No
5/02/2019 | 23:23:58 | GU43 | Rural Long | Asset failure | HV | 2 | 41 | 0.00059846 | 1.46e-05 | No
5/02/2019 | 23:57:58 | CD18 | Rural Long | Unknown | Unknown | 24 | 218 | 0.038185 | 0.00017516 | No
6/02/2019 | 00:20:19 | HH341A | Urban | Animal | Animal impact | 69 | 71 | 0.0078319 | 0.00011031 | No
6/02/2019 | 00:27:42 | HH341A | Urban | Animal | Animal impact | 1 | 68 | 0.00010871 | 1.6e-06 | No
6/02/2019 | 01:49:53 | MG17 | Rural Long | Unknown | Unknown | 20 | 113 | 0.016494 | 0.00014597 | No
6/02/2019 | 03:33:37 | WHY363A | Rural Short | Unknown | Unknown | 52 | 208 | 0.080581 | 0.00038741 | No
6/02/2019 | 04:37:56 | MI22 | Rural Long | Unknown | Unknown | 174 | 92 | 0.11683 | 0.0012699 | No
6/02/2019 | 05:24:26 | CD18 | Rural Long | Unknown | Unknown | 42 | 339.1429 | 0.10396 | 0.00030653 | No
6/02/2019 | 05:40:19 | SD34300 | Rural Short | Unknown | Unknown | 590 | 213 | 0.93626 | 0.0043956 | No
6/02/2019 | 05:41:36 | KI57 | Rural Short | Weather |  | 144 | 376.5694 | 0.40399 | 0.0010728 | No
6/02/2019 | 05:46:04 | MG27 | Rural Long | Third Party | Other | 91 | 217.4066 | 0.14439 | 0.00066415 | No
6/02/2019 | 06:13:17 | SD34201 | Rural Short | Unknown | Unknown | 1 | 234 | 0.0017433 | 7.45e-06 | No
6/02/2019 | 06:27:15 | SD35100 | Rural Long | Weather |  | 2112 | 105.0133 | 1.6187 | 0.015414 | No
6/02/2019 | 06:36:43 | VH16 | Rural Short | Weather |  | 1133 | 111.3248 | 0.93969 | 0.008441 | No
6/02/2019 | 07:25:16 | G11 | Rural Long | Asset failure | HV | 5 | 352 | 0.012845 | 3.649e-05 | No
6/02/2019 | 08:00:01 | SSD231 | Urban | Asset failure | Zone substation | 6944 | 68.8502 | 0.76432 | 0.011101 | No
6/02/2019 | 08:14:41 | PA18 | Rural Long | Unknown | Unknown | 94 | 235 | 0.16122 | 0.00068604 | No
6/02/2019 | 08:17:27 | ST12 | Rural Short | Planned |  | 584 | 343.0822 | 1.4927 | 0.0043509 | No
6/02/2019 | 08:19:42 | MV63 | Rural Short | Asset failure | HV | 260 | 196.2846 | 0.38021 | 0.001937 | No
6/02/2019 | 08:38:52 | ST36 | Rural Long | Planned |  | 65 | 363 | 0.1722 | 0.00047439 | No
6/02/2019 | 08:43:39 | VH22 | Rural Short | Weather |  | 2010 | 94.6164 | 1.4169 | 0.014975 | No
6/02/2019 | 08:50:14 | PL07 | Urban | Planned |  | 87 | 343 | 0.047706 | 0.00013908 | No
6/02/2019 | 08:55:48 | CN25 | Rural Long | Unknown | Unknown | 51 | 229 | 0.085237 | 0.00037222 | No
6/02/2019 | 08:55:58 | MTB51 | Rural Long | Planned |  | 5 | 347 | 0.012663 | 3.649e-05 | No
6/02/2019 | 09:09:43 | VH44 | Rural Short | Weather |  | 300 | 96.5067 | 0.2157 | 0.002235 | No
6/02/2019 | 09:09:44 | WK21 | Rural Short | Planned |  | 1 | 20 | 0.000149 | 7.45e-06 | No
6/02/2019 | 09:09:56 | W27 | Rural Long | Unknown | Unknown | 9 | 96 | 0.0063058 | 6.569e-05 | No
6/02/2019 | 09:20:24 | NA13 | Rural Long | Planned |  | 4 | 280 | 0.0081741 | 2.919e-05 | No
6/02/2019 | 09:32:37 | EL260C | Urban | Planned |  | 69 | 271 | 0.029894 | 0.00011031 | No
6/02/2019 | 09:45:58 | VH72 | Rural Short | Planned |  | 2 | 219 | 0.0032632 | 1.49e-05 | No
6/02/2019 | 09:56:01 | MI02 | Rural Short | Asset failure | HV | 4 | 343 | 0.010222 | 2.98e-05 | No
6/02/2019 | 10:14:57 | WK65 | Rural Short | Planned |  | 31 | 93 | 0.021479 | 0.00023095 | No
6/02/2019 | 10:20:33 | HH107B | Urban | Planned |  | 218 | 329 | 0.11466 | 0.00034851 | No
6/02/2019 | 10:52:23 | LX73 | Rural Long | Unknown | Unknown | 8 | 316 | 0.01845 | 5.839e-05 | No
6/02/2019 | 10:52:27 | ME116B | Urban | Planned |  | 42 | 127.7143 | 0.0085753 | 6.714e-05 | No
6/02/2019 | 10:54:22 | ME131D | Urban | Third Party | Vehicle impact | 731 | 128.1204 | 0.14973 | 0.0011686 | No
6/02/2019 | 10:59:48 | CV31 | Rural Long | Planned |  | 1 | 76 | 0.00055467 | 7.3e-06 | No
6/02/2019 | 11:28:42 | CN81 | Rural Long | Weather |  | 14 | 217 | 0.022172 | 0.00010218 | No
6/02/2019 | 11:59:58 | WHY03 | Urban | Asset failure | LV | 2 | 117 | 0.00037409 | 3.2e-06 | No
6/02/2019 | 13:33:13 | G17 | Rural Long | Unknown | Unknown | 10 | 217 | 0.015837 | 7.298e-05 | No
6/02/2019 | 14:21:36 | GU41 | Rural Long | Unknown | Unknown | 1 | 132 | 0.00096338 | 7.3e-06 | No
6/02/2019 | 14:22:13 | MT11 | Rural Long | Unknown | Unknown | 68 | 38 | 0.018859 | 0.00049629 | No
6/02/2019 | 15:08:17 | GU32 | Rural Long | Asset failure | LV | 1 | 232 | 0.0016932 | 7.3e-06 | No
6/02/2019 | 15:54:36 | WK31 | Rural Short | Asset failure | HV | 532 | 101.5789 | 0.40261 | 0.0039635 | No
6/02/2019 | 16:23:15 | SA33 | Urban | Asset failure | LV | 1 | 127 | 0.00020303 | 1.6e-06 | No
6/02/2019 | 18:10:23 | LM51 | Rural Long | Unknown | Unknown | 19 | 337 | 0.046731 | 0.00013867 | No
6/02/2019 | 20:30:49 | CN25 | Rural Long | Weather |  | 51 | 861.2941 | 0.32059 | 0.00037222 | No
6/02/2019 | 20:30:49 | CN25 | Rural Long | Weather |  | 9 | 31 | 0.0020362 | 6.569e-05 | No
6/02/2019 | 22:41:02 | MG51 | Rural Long | Weather |  | 15 | 93 | 0.010181 | 0.00010948 | No
7/02/2019 | 01:02:29 | HH121G | Urban | Unknown | Unknown | 470 | 185 | 0.139 | 0.00075138 | No
7/02/2019 | 01:18:32 | MG17 | Rural Long | Weather |  | 983 | 155.0529 | 1.1124 | 0.0071743 | No
7/02/2019 | 02:18:00 | W27 | Rural Long | Unknown | Unknown | 64 | 536 | 0.25036 | 0.00046709 | No
7/02/2019 | 03:07:09 | CN72 | Rural Long | Asset failure | HV | 92 | 434.1957 | 0.29154 | 0.00067145 | No
7/02/2019 | 06:35:42 | AP373B | Urban | Third Party | Vehicle impact | 132 | 73.4242 | 0.015494 | 0.00021103 | No
7/02/2019 | 07:10:38 | AP227D | Urban | Third Party | Vehicle impact | 49 | 314 | 0.024597 | 7.834e-05 | No
7/02/2019 | 08:12:37 | G13 | Rural Long | Asset failure | LV | 1 | 298 | 0.0021749 | 7.3e-06 | No
7/02/2019 | 08:13:34 | NL511B | Urban | Overloads |  | 1 | 419 | 0.00066984 | 1.6e-06 | No
7/02/2019 | 08:24:45 | SM350F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 69 | 177 | 0.019525 | 0.00011031 | No
7/02/2019 | 08:46:16 | HH432E | Urban | Planned |  | 14 | 62 | 0.0013877 | 2.238e-05 | No
7/02/2019 | 08:55:42 | HK02 | Rural Long | Planned |  | 21 | 376 | 0.057628 | 0.00015327 | No
7/02/2019 | 08:59:45 | HH107B | Urban | Planned |  | 613 | 142.4731 | 0.13962 | 0.00097999 | No
7/02/2019 | 09:00:01 | ST36 | Rural Long | Planned |  | 40 | 226 | 0.065977 | 0.00029193 | No
7/02/2019 | 09:09:36 | HH107B | Urban | Planned |  | 1 | 31 | 4.956e-05 | 1.6e-06 | No
7/02/2019 | 09:09:43 | MV62 | Rural Short | Planned |  | 25 | 163 | 0.030359 | 0.00018625 | No
7/02/2019 | 09:14:31 | MTB41 | Rural Short | Planned |  | 60 | 192 | 0.085826 | 0.00044701 | No
7/02/2019 | 09:21:30 | SD48200 | Rural Long | Unknown | Unknown | 2 | 117 | 0.0017078 | 1.46e-05 | No
7/02/2019 | 09:24:07 | MTB13 | Rural Short | Planned |  | 35 | 192 | 0.050065 | 0.00026076 | No
7/02/2019 | 09:32:08 | VH22 | Rural Short | Planned |  | 22 | 368 | 0.060316 | 0.0001639 | No
7/02/2019 | 09:37:37 | GA53 | Rural Short | Planned |  | 39 | 201 | 0.058402 | 0.00029056 | No
7/02/2019 | 09:40:21 | SM137B | Urban | Planned |  | 79 | 294 | 0.037131 | 0.0001263 | No
7/02/2019 | 09:46:44 | ST16 | Rural Short | Planned |  | 44 | 191 | 0.062611 | 0.00032781 | No
7/02/2019 | 09:53:01 | HH409D | Urban | Planned |  | 361 | 224 | 0.12928 | 0.00057712 | No
7/02/2019 | 10:01:39 | GA745B | Rural Short | Planned |  | 2 | 178 | 0.0026523 | 1.49e-05 | No
7/02/2019 | 10:05:26 | SG13 | Rural Short | Planned |  | 61 | 286 | 0.12998 | 0.00045446 | No
7/02/2019 | 10:07:35 | HH107B | Urban | Planned |  | 1 | 70 | 0.00011191 | 1.6e-06 | No
7/02/2019 | 10:10:58 | R26 | Rural Long | Planned |  | 2 | 25 | 0.00036492 | 1.46e-05 | No
7/02/2019 | 10:20:03 | SM411E | Urban | Planned |  | 43 | 70 | 0.004812 | 6.874e-05 | No
7/02/2019 | 10:40:16 | GA08 | Rural Long | Planned |  | 19 | 137 | 0.018998 | 0.00013867 | No
7/02/2019 | 10:42:23 | MTB63 | Rural Short | Planned |  | 2 | 236 | 0.0035165 | 1.49e-05 | No
7/02/2019 | 11:00:14 | HH409D | Urban | Planned |  | 1 | 153 | 0.0002446 | 1.6e-06 | No
7/02/2019 | 11:25:46 | WK31 | Rural Short | Asset failure | HV | 32.3333 | 107.1546 | 0.025812 | 0.00024089 | No
7/02/2019 | 12:01:13 | NA19 | Rural Long | Unknown | Unknown | 38 | 132 | 0.036608 | 0.00027734 | No
7/02/2019 | 12:57:06 | HH107B | Urban | Planned |  | 2 | 106 | 0.00033892 | 3.2e-06 | No
7/02/2019 | 14:13:45 | SD34102 | Rural Long | Weather |  | 1 | 151 | 0.0011021 | 7.3e-06 | No
7/02/2019 | 15:56:43 | SM411F | Urban | Asset failure | LV | 1 | 173 | 0.00027657 | 1.6e-06 | No
7/02/2019 | 16:38:52 | CV23 | Rural Long | Unknown | Unknown | 1 | 45 | 0.00032843 | 7.3e-06 | No
7/02/2019 | 17:43:45 | SM402B | Urban | Overloads |  | 1 | 174 | 0.00027817 | 1.6e-06 | No
7/02/2019 | 18:36:46 | SA13 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 17 | 126 | 0.0034244 | 2.718e-05 | No
7/02/2019 | 18:48:42 | NL111C | Urban | Asset failure | LV | 143 | 110 | 0.025147 | 0.00022861 | No
7/02/2019 | 18:56:08 | NL111C | Urban | Asset failure | LV | 98 | 104 | 0.016294 | 0.00015667 | No
7/02/2019 | 21:08:47 | GA800A | Rural Short | Asset failure | LV | 1 | 186 | 0.0013857 | 7.45e-06 | No
7/02/2019 | 21:09:56 | MTB32 | Rural Long | Unknown | Unknown | 50 | 177 | 0.06459 | 0.00036492 | No
8/02/2019 | 03:11:31 | HH341C | Urban | Animal | Animal impact | 376 | 28 | 0.016831 | 0.0006011 | No
8/02/2019 | 03:39:43 | AP425D | Urban | Asset failure | LV | 27 | 355 | 0.015323 | 4.316e-05 | No
8/02/2019 | 05:02:06 | GA09 | Rural Long | Animal | Animal impact | 8 | 258 | 0.015064 | 5.839e-05 | No
8/02/2019 | 07:03:18 | AP351C | Urban | Asset failure | LV | 1 | 269 | 0.00043004 | 1.6e-06 | No
8/02/2019 | 07:47:01 | MV13 | Rural Short | Unknown | Unknown | 3 | 573 | 0.012807 | 2.235e-05 | No
8/02/2019 | 08:07:10 | WHY363A | Rural Short | Planned |  | 53 | 78 | 0.030799 | 0.00039486 | No
8/02/2019 | 08:30:41 | YK29 | Rural Long | Planned |  | 72 | 101 | 0.053074 | 0.00052548 | No
8/02/2019 | 08:44:29 | SG03 | Rural Short | Planned |  | 50 | 235.44 | 0.087703 | 0.00037251 | No
8/02/2019 | 08:53:05 | CM10 | Rural Long | Unknown | Unknown | 22 | 195 | 0.03131 | 0.00016056 | No
8/02/2019 | 08:54:09 | MG19 | Rural Long | Planned |  | 1 | 19 | 0.00013867 | 7.3e-06 | No
8/02/2019 | 08:56:47 | ST15 | Rural Short | Planned |  | 87 | 366 | 0.23723 | 0.00064816 | No
8/02/2019 | 09:07:39 | ST11 | Rural Short | Planned |  | 2 | 135 | 0.0020115 | 1.49e-05 | No
8/02/2019 | 09:09:16 | R21 | Rural Long | Planned |  | 3 | 7490 | 0.16399 | 2.19e-05 | No
8/02/2019 | 09:11:42 | MV32 | Rural Short | Planned |  | 13 | 300 | 0.029056 | 9.685e-05 | No
8/02/2019 | 09:13:41 | GA48 | Rural Short | Planned |  | 46 | 150.9348 | 0.051726 | 0.00034271 | No
8/02/2019 | 09:20:59 | ST11 | Rural Short | Planned |  | 1 | 67 | 0.00049916 | 7.45e-06 | No
8/02/2019 | 09:21:29 | WK32 | Rural Short | Planned |  | 1 | 248 | 0.0018476 | 7.45e-06 | No
8/02/2019 | 09:25:40 | SD38200 | Rural Long | Planned |  | 1 | 31 | 0.00022625 | 7.3e-06 | No
8/02/2019 | 09:30:06 | SM411E | Urban | Planned |  | 74 | 271 | 0.03206 | 0.0001183 | No
8/02/2019 | 09:30:31 | BU04 | Rural Long | Planned |  | 4 | 132 | 0.0038535 | 2.919e-05 | No
8/02/2019 | 09:35:47 | AP214A | Urban | Planned |  | 84 | 174 | 0.023366 | 0.00013429 | No
8/02/2019 | 09:36:14 | MB25 | Rural Long | Planned |  | 1 | 32 | 0.00023355 | 7.3e-06 | No
8/02/2019 | 09:42:47 | SA17 | Urban | Planned |  | 25 | 55 | 0.0021982 | 3.997e-05 | No
8/02/2019 | 09:51:06 | HH428D | Urban | Asset failure | LV | 1 | 211 | 0.00033732 | 1.6e-06 | No
8/02/2019 | 10:01:34 | HH148B | Urban | Planned |  | 43 | 246 | 0.016911 | 6.874e-05 | No
8/02/2019 | 10:05:53 | PP09 | Rural Long | Planned |  | 9 | 249 | 0.016356 | 6.569e-05 | No
8/02/2019 | 10:12:11 | AP424F | Urban | Planned |  | 2 | 7492 | 0.023955 | 3.2e-06 | No
8/02/2019 | 10:20:32 | AP149B | Urban | Planned |  | 97 | 10 | 0.0015507 | 0.00015507 | No
8/02/2019 | 10:53:01 | MB25 | Rural Long | Unknown | Unknown | 41 | 50 | 0.014962 | 0.00029923 | No
8/02/2019 | 12:32:37 | ME231B | Urban | Planned |  | 82 | 17 | 0.0022286 | 0.00013109 | No
8/02/2019 | 13:58:12 | MB24 | Rural Short | Planned |  | 2 | 30 | 0.00044701 | 1.49e-05 | No
8/02/2019 | 14:16:05 | AP355A | Urban | Asset failure | LV | 29 | 173 | 0.0080205 | 4.636e-05 | No
8/02/2019 | 16:27:27 | M81 | Rural Long | Asset failure | HV | 515 | 135.5398 | 0.50945 | 0.0037586 | No
8/02/2019 | 16:29:09 | VH16 | Rural Short | Asset failure | LV | 8.6667 | 1275.9999 | 0.082389 | 6.457e-05 | No
8/02/2019 | 16:42:49 | G12 | Rural Long | Asset failure | HV | 66 | 366.0909 | 0.17634 | 0.00048169 | No
8/02/2019 | 16:42:49 | G12 | Rural Long | Asset failure | HV | 0 | 2 | 0.0008612 | 0 | No
8/02/2019 | 17:03:44 | W29 | Rural Long | Asset failure | HV | 12 | 1185 | 0.10378 | 8.758e-05 | No
8/02/2019 | 18:40:59 | SM410A | Urban | Asset failure | LV | 1 | 298 | 0.00047641 | 1.6e-06 | No
8/02/2019 | 19:16:40 | HH121D | Urban | Overloads |  | 1 | 348 | 0.00055634 | 1.6e-06 | No
8/02/2019 | 20:08:20 | SA744D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 93 | 0.00014868 | 1.6e-06 | No
8/02/2019 | 20:37:32 | GA25 | Rural Short | Asset failure | LV | 1 | 157 | 0.0011697 | 7.45e-06 | No
8/02/2019 | 21:23:19 | HH403B | Urban | 7 - STPIS Exclusion (3.3)(a) |  | 1 | 75 | 0.0001199 | 1.6e-06 | No
8/02/2019 | 21:35:16 | MTB81 | Rural Short | Asset failure | LV | 1.3333 | 146 | 0.0014503 | 9.93e-06 | No
8/02/2019 | 22:08:58 | HH428D | Urban | Animal | Animal impact | 2041 | 58 | 0.18925 | 0.0032629 | No
9/02/2019 | 00:22:08 | MI20 | Rural Long | Asset failure | HV | 937 | 89.0555 | 0.60901 | 0.0068385 | No
9/02/2019 | 01:29:31 | HH130F | Urban | Asset failure | LV | 89 | 83 | 0.011809 | 0.00014228 | No
9/02/2019 | 02:55:00 | MG05 | Rural Long | Unknown | Unknown | 260 | 337.3423 | 0.64013 | 0.0018976 | No
9/02/2019 | 03:50:37 | VH72 | Rural Short | Weather |  | 49 | 469 | 0.17121 | 0.00036506 | No
9/02/2019 | 04:01:21 | MI02 | Rural Short | Unknown | Unknown | 229 | 334 | 0.56983 | 0.0017061 | No
9/02/2019 | 05:21:06 | KA02 | Rural Short | Asset failure | HV | 802 | 101.4526 | 0.60618 | 0.005975 | No
9/02/2019 | 07:15:38 | NL451E | Urban | Asset failure | LV | 12 | 416 | 0.0079806 | 1.918e-05 | No
9/02/2019 | 08:06:18 | MV31 | Rural Short | Weather |  | 104 | 333 | 0.25801 | 0.00077482 | No
9/02/2019 | 08:09:44 | ST21 | Rural Short | Weather |  | 882 | 131.1168 | 0.86157 | 0.006571 | No
9/02/2019 | 08:14:26 | HH341A | Urban | Vegetation | Grow-in - NSP responsibility | 4 | 216 | 0.0013813 | 6.39e-06 | No
9/02/2019 | 08:39:42 | AP373B | Urban | Planned |  | 2 | 1747 | 0.0055858 | 3.2e-06 | No
9/02/2019 | 09:18:55 | AP372D | Urban | Asset failure | LV | 23.3333 | 122 | 0.0045509 | 3.73e-05 | No
9/02/2019 | 09:18:59 | VH15 | Rural Short | Unknown | Unknown | 2040 | 57 | 0.8663 | 0.015198 | No
9/02/2019 | 09:41:59 | SM126C | Urban | Unknown | Unknown | 119.3334 | 9 | 0.001717 | 0.00019078 | No
9/02/2019 | 09:49:53 | NL760B | Urban | Asset failure | LV | 1 | 113 | 0.00018065 | 1.6e-06 | No
9/02/2019 | 10:09:04 | HH409E | Urban | Vegetation | Grow-in - NSP responsibility | 30 | 154 | 0.0073859 | 4.796e-05 | No
9/02/2019 | 11:06:27 | SD34300 | Rural Short | Asset failure | Subtransmission | 135 | 40.3333 | 0.040566 | 0.0010058 | No
9/02/2019 | 11:10:44 | HH409D | Urban | Asset failure | LV | 1 | 179 | 0.00028616 | 1.6e-06 | No
9/02/2019 | 11:33:44 | AP372B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 294 | 0.00047001 | 1.6e-06 | No
9/02/2019 | 11:39:30 | VH15 | Rural Short | Asset failure | LV | 11 | 102 | 0.0083591 | 8.195e-05 | No
9/02/2019 | 13:01:07 | MG16 | Rural Long | Asset failure | LV | 1 | 420 | 0.0030653 | 7.3e-06 | No
9/02/2019 | 16:14:11 | SA744D | Urban | Asset failure | LV | 1 | 136 | 0.00021742 | 1.6e-06 | No
9/02/2019 | 16:49:04 | GA18 | Rural Long | Asset failure | HV | 2 | 270 | 0.0039411 | 1.46e-05 | No
9/02/2019 | 18:40:17 | GA18 | Rural Long | Unknown | Unknown | 2 | 42 | 0.00061306 | 1.46e-05 | No
9/02/2019 | 19:19:33 | AP214B | Urban | Asset failure | HV | 102 | 50 | 0.0081532 | 0.00016306 | No
9/02/2019 | 20:30:36 | CV31 | Rural Long | Unknown | Unknown | 13 | 197 | 0.018691 | 9.488e-05 | No
9/02/2019 | 20:30:53 | SM410D | Urban | Unknown | Unknown | 33.3334 | 160 | 0.0085263 | 5.329e-05 | No
10/02/2019 | 04:15:14 | MV22 | Rural Short | Planned |  | 166 | 177 | 0.2189 | 0.0012367 | No
10/02/2019 | 04:47:27 | SD45202 | Rural Long | Planned |  | 2908 | 3 | 0.063671 | 0.021224 | No
10/02/2019 | 04:57:34 | SSD163 | Rural Long | Planned |  | 427 | 5 | 0.015582 | 0.0031164 | No
10/02/2019 | 07:10:50 | G14 | Rural Long | Unknown | Unknown | 13 | 299 | 0.028369 | 9.488e-05 | No
10/02/2019 | 08:25:01 | AP344E | Urban | Planned |  | 39 | 460 | 0.02868 | 6.235e-05 | No
10/02/2019 | 09:23:11 | HH429C | Urban | Planned |  | 210 | 192 | 0.064459 | 0.00033572 | No
10/02/2019 | 11:03:03 | NL451E | Urban | Animal | Animal impact | 36 | 104 | 0.0059854 | 5.755e-05 | No
10/02/2019 | 11:21:05 | EL19 | Urban | Asset failure | LV | 9 | 26 | 0.00037409 | 1.439e-05 | No
10/02/2019 | 14:44:32 | SM126E | Urban | Unknown | Unknown | 39 | 6 | 0.00037409 | 6.235e-05 | No
10/02/2019 | 16:16:49 | HH409A | Urban | Asset failure | HV | 68.6667 | 53 | 0.0058181 | 0.00010978 | No
10/02/2019 | 17:09:40 | SM349A | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | No
10/02/2019 | 17:18:16 | AP424E | Urban | Third Party | Dig-in | 65 | 227 | 0.023588 | 0.00010391 | No
10/02/2019 | 17:39:59 | MT01 | Rural Long | Asset failure | LV | 43 | 321 | 0.10074 | 0.00031383 | No
10/02/2019 | 19:58:09 | HH121F | Urban | Asset failure | LV | 46 | 105 | 0.0077216 | 7.354e-05 | No
10/02/2019 | 21:49:02 | CN42 | Rural Long | Asset failure | LV | 1 | 169 | 0.0012334 | 7.3e-06 | No
11/02/2019 | 01:12:06 | AP146B | Urban | Animal | Animal impact | 2347 | 197.5275 | 0.74114 | 0.0037521 | No
11/02/2019 | 04:25:47 | MI02 | Rural Short | Weather |  | 176.6667 | 272 | 0.358 | 0.0013162 | No
11/02/2019 | 06:32:32 | SM172C | Urban | Animal | Animal impact | 30 | 118 | 0.0056593 | 4.796e-05 | No
11/02/2019 | 07:08:26 | HH496A | Urban | Unknown | Unknown | 2005 | 11.9167 | 0.038197 | 0.0032053 | No
11/02/2019 | 07:41:22 | SD44200 | Rural Short | Asset failure | Subtransmission | 1 | 184 | 0.0013708 | 7.45e-06 | No
11/02/2019 | 08:14:32 | MT15 | Rural Long | Planned |  | 37 | 168 | 0.045366 | 0.00027004 | No
11/02/2019 | 08:24:02 | W29 | Rural Long | Unknown | Unknown | 1 | 259 | 0.0018903 | 7.3e-06 | No
11/02/2019 | 08:25:25 | PL04 | Urban | Planned |  | 32 | 255 | 0.013045 | 5.116e-05 | No
11/02/2019 | 08:55:32 | HH121E | Urban | Planned |  | 79 | 210 | 0.026522 | 0.0001263 | No
11/02/2019 | 08:58:10 | EL12 | Urban | Planned |  | 27 | 297 | 0.01282 | 4.316e-05 | No
11/02/2019 | 09:01:51 | MG42 | Rural Short | Planned |  | 18 | 308 | 0.041304 | 0.0001341 | No
11/02/2019 | 09:08:18 | SM216C | Urban | Asset failure | LV | 2 | 189 | 0.0006043 | 3.2e-06 | No
11/02/2019 | 09:18:24 | WK31 | Rural Short | Planned |  | 31 | 215 | 0.049655 | 0.00023095 | No
11/02/2019 | 09:20:06 | MV22 | Rural Short | Planned |  | 32 | 187 | 0.044582 | 0.0002384 | No
11/02/2019 | 09:37:21 | MB32 | Rural Long | Planned |  | 36 | 174 | 0.045717 | 0.00026274 | No
11/02/2019 | 09:42:39 | HH386A | Urban | Planned |  | 210 | 224 | 0.075202 | 0.00033572 | No
11/02/2019 | 10:08:16 | EL17 | Urban | Planned |  | 2 | 18 | 5.755e-05 | 3.2e-06 | No
11/02/2019 | 10:15:23 | SD38100 | Rural Long | Planned |  | 8 | 3 | 0.00017516 | 5.839e-05 | No
11/02/2019 | 11:24:47 | MV34 | Rural Short | Planned |  | 284 | 235 | 0.49722 | 0.0021158 | No
11/02/2019 | 11:35:54 | MG05 | Rural Long | Weather |  | 172 | 20.6919 | 0.025975 | 0.0012553 | No
11/02/2019 | 11:45:48 | ST11 | Rural Short | Asset failure | HV | 201.3334 | 185.596 | 0.27839 | 0.0015 | No
11/02/2019 | 11:55:52 | SG02 | Rural Short | Asset failure | HV | 182 | 203.1978 | 0.27552 | 0.0013559 | No
11/02/2019 | 12:23:55 | W29 | Rural Long | Unknown | Unknown | 1 | 9 | 6.569e-05 | 7.3e-06 | No
11/02/2019 | 13:40:38 | MT18 | Rural Long | Unknown | Unknown | 12 | 30 | 0.0026274 | 8.758e-05 | No
11/02/2019 | 14:22:28 | VH18 | Rural Short | Unknown | Unknown | 2 | 13 | 0.0001937 | 1.49e-05 | No
11/02/2019 | 15:13:19 | EL01L | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
11/02/2019 | 15:21:29 | MT15 | Rural Long | Asset failure | HV | 1 | 29 | 0.00021165 | 7.3e-06 | No
11/02/2019 | 15:32:50 | MT15 | Rural Long | Unknown | Unknown | 1 | 13 | 9.488e-05 | 7.3e-06 | No
11/02/2019 | 16:06:09 | MT01 | Rural Long | Overloads |  | 40 | 54 | 0.015764 | 0.00029193 | No
11/02/2019 | 17:36:48 | MT01 | Rural Long | Asset failure | HV | 40 | 214 | 0.062474 | 0.00029193 | No
11/02/2019 | 19:28:00 | PP02 | Urban | Third Party | Vehicle impact | 49 | 41 | 0.0032117 | 7.834e-05 | No
11/02/2019 | 19:33:23 | SD54300 | Rural Long | Asset failure | Subtransmission | 2 | 53 | 0.00077362 | 1.46e-05 | No
11/02/2019 | 20:59:53 | MG10 | Rural Long | Asset failure | HV | 1 | 27 | 0.00019706 | 7.3e-06 | No
12/02/2019 | 04:40:06 | ST35 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 189 | 146 | 0.20139 | 0.0013794 | No
12/02/2019 | 04:42:13 | AP372B | Urban | Vegetation | Grow-in - NSP responsibility | 106 | 277 | 0.04694 | 0.00016946 | No
12/02/2019 | 04:56:35 | SG11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 503 | 170 | 0.63706 | 0.0037474 | No
12/02/2019 | 05:13:35 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1094 | 58 | 0.47273 | 0.0081505 | No
12/02/2019 | 06:42:09 | HH118C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 236 | 0.00037729 | 1.6e-06 | No
12/02/2019 | 07:03:46 | MTB32 | Rural Long | Asset failure | Distribution substation | 60 | 303.95 | 0.1331 | 0.0004379 | No
12/02/2019 | 08:15:59 | SG06 | Rural Short | Unknown | Unknown | 7 | 417 | 0.021747 | 5.215e-05 | No
12/02/2019 | 08:17:08 | NL111B | Urban | Vegetation | Grow-in - NSP responsibility | 17 | 96 | 0.002609 | 2.718e-05 | No
12/02/2019 | 08:17:23 | MTB41 | Rural Short | Unknown | Unknown | 25 | 192 | 0.035761 | 0.00018625 | No
12/02/2019 | 08:18:21 | SM349D | Urban | Planned |  | 1469 | 6 | 0.014091 | 0.0023485 | No
12/02/2019 | 08:42:45 | CN24 | Rural Long | Planned |  | 531 | 324.5895 | 1.2579 | 0.0038754 | No
12/02/2019 | 08:42:58 | MI14 | Rural Long | Asset failure | LV | 24.3333 | 92 | 0.016339 | 0.00017759 | No
12/02/2019 | 09:03:40 | SG14 | Rural Short | Planned |  | 107 | 303 | 0.24154 | 0.00079717 | No
12/02/2019 | 09:05:23 | MTB52 | Rural Long | Planned |  | 123 | 336 | 0.30163 | 0.0008977 | No
12/02/2019 | 09:05:54 | BM12 | Rural Short | Planned |  | 3 | 105 | 0.0023468 | 2.235e-05 | No
12/02/2019 | 09:14:05 | SD31200 | Rural Long | Planned |  | 245 | 493.0449 | 0.88161 | 0.0017881 | No
12/02/2019 | 09:19:21 | SB18 | Rural Long | Planned |  | 1 | 178 | 0.0012991 | 7.3e-06 | No
12/02/2019 | 09:37:24 | GA53 | Rural Short | Planned |  | 18 | 368 | 0.04935 | 0.0001341 | No
12/02/2019 | 09:45:02 | HH107B | Urban | Planned |  | 282 | 366 | 0.165 | 0.00045083 | No
12/02/2019 | 09:58:12 | HH409F | Urban | Planned |  | 103 | 194 | 0.031945 | 0.00016466 | No
12/02/2019 | 10:29:26 | HH432B | Urban | Planned |  | 50 | 113 | 0.0090325 | 7.993e-05 | No
12/02/2019 | 10:43:28 | HH341J | Urban | Planned |  | 295 | 179 | 0.084418 | 0.00047161 | No
12/02/2019 | 11:06:43 | HH121C | Urban | Asset failure | HV | 834 | 59.4341 | 0.079243 | 0.0013333 | No
12/02/2019 | 11:23:06 | HH148D | Urban | Unknown | Unknown | 9 | 58 | 0.00083451 | 1.439e-05 | No
12/02/2019 | 12:00:41 | PA03 | Urban | Asset failure | HV | 113.3334 | 77 | 0.013951 | 0.00018118 | No
12/02/2019 | 12:12:05 | WHY363A | Rural Short | Unknown | Unknown | 52 | 29 | 0.011235 | 0.00038741 | No
12/02/2019 | 12:58:05 | PL24 | Rural Long | Unknown | Unknown | 44 | 296.7273 | 0.095287 | 0.00032113 | No
12/02/2019 | 15:02:47 | W29 | Rural Long | Unknown | Unknown | 1 | 8 | 5.839e-05 | 7.3e-06 | No
12/02/2019 | 15:55:05 | BT02 | Rural Long | Unknown | Unknown | 1 | 61 | 0.0004452 | 7.3e-06 | No
12/02/2019 | 18:02:53 | WK23 | Rural Short | Asset failure | HV | 20 | 203 | 0.030248 | 0.000149 | No
12/02/2019 | 18:16:17 | MB72 | Rural Long | Asset failure | LV | 1 | 164 | 0.0011969 | 7.3e-06 | No
12/02/2019 | 18:48:38 | MTB52 | Rural Long | Unknown | Unknown | 17.3333 | 15 | 0.0018976 | 0.0001265 | No
12/02/2019 | 19:20:12 | MTB32 | Rural Long | Unknown | Unknown | 60 | 282.25 | 0.1236 | 0.0004379 | No
12/02/2019 | 19:20:12 | MTB32 | Rural Long | Unknown | Unknown | 0 | 1 | 0.00054008 | 0 | No
12/02/2019 | 21:32:35 | GA26 | Urban | Planned |  | 54 | 337 | 0.029093 | 8.633e-05 | No
13/02/2019 | 01:00:22 | AP355A | Urban | Overloads |  | 1 | 107 | 0.00017106 | 1.6e-06 | No
13/02/2019 | 03:10:19 | MV52 | Rural Short | Animal | Animal impact | 83 | 118 | 0.072967 | 0.00061836 | No
13/02/2019 | 06:45:23 | CN24 | Rural Long | Asset failure | LV | 22 | 180 | 0.028901 | 0.00016056 | No
13/02/2019 | 07:33:12 | MI16 | Rural Long | Weather |  | 297 | 184 | 0.39884 | 0.0021676 | No
13/02/2019 | 08:27:53 | CN25 | Rural Long | Planned |  | 80 | 383 | 0.22362 | 0.00058387 | No
13/02/2019 | 08:30:04 | ST44 | Rural Long | Planned |  | 77 | 336.7273 | 0.18923 | 0.00056197 | No
13/02/2019 | 08:48:09 | GA09 | Rural Long | Planned |  | 10 | 16 | 0.0011677 | 7.298e-05 | No
13/02/2019 | 08:52:23 | MTB54 | Rural Long | Planned |  | 80 | 331 | 0.19326 | 0.00058387 | No
13/02/2019 | 08:54:36 | SG10 | Rural Short | Planned |  | 240 | 168 | 0.30039 | 0.001788 | No
13/02/2019 | 08:56:44 | EL12 | Urban | Planned |  | 4 | 143 | 0.00091444 | 6.39e-06 | No
13/02/2019 | 08:58:46 | EL17 | Urban | Planned |  | 124 | 184.0968 | 0.036495 | 0.00019824 | No
13/02/2019 | 09:02:20 | YK17 | Rural Long | Planned |  | 65 | 51 | 0.024194 | 0.00047439 | No
13/02/2019 | 09:22:05 | HH409D | Urban | Planned |  | 136 | 64 | 0.013915 | 0.00021742 | No
13/02/2019 | 09:22:48 | MTB41 | Rural Short | Planned |  | 2 | 408 | 0.0060793 | 1.49e-05 | No
13/02/2019 | 09:23:38 | HH341D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2214 | 47 | 0.16635 | 0.0035395 | No
13/02/2019 | 09:25:16 | PA02 | Urban | Planned |  | 76 | 341 | 0.041431 | 0.0001215 | No
13/02/2019 | 09:35:01 | MG29 | Rural Long | Planned |  | 13 | 137 | 0.012998 | 9.488e-05 | No
13/02/2019 | 09:40:54 | MI09 | Rural Long | Planned |  | 13 | 299 | 0.028369 | 9.488e-05 | No
13/02/2019 | 09:52:07 | GU37 | Rural Long | Planned |  | 16 | 78 | 0.0091083 | 0.00011677 | No
13/02/2019 | 09:56:09 | KI54 | Rural Long | Planned |  | 108 | 293 | 0.23095 | 0.00078822 | No
13/02/2019 | 09:57:55 | VH12 | Rural Short | Planned |  | 281 | 324 | 0.67829 | 0.0020935 | No
13/02/2019 | 10:11:32 | G13 | Rural Long | Planned |  | 2 | 179 | 0.0026128 | 1.46e-05 | No
13/02/2019 | 10:16:24 | HH121G | Urban | Planned |  | 1 | 67 | 0.00010711 | 1.6e-06 | No
13/02/2019 | 10:20:46 | MT19 | Rural Long | Planned |  | 1 | 26 | 0.00018976 | 7.3e-06 | No
13/02/2019 | 10:35:23 | BT02 | Rural Long | Planned |  | 2 | 177 | 0.0025836 | 1.46e-05 | No
13/02/2019 | 11:51:25 | NL111D | Urban | Asset failure | LV | 1 | 70 | 0.00011191 | 1.6e-06 | No
13/02/2019 | 12:00:02 | GU37 | Rural Long | Planned |  | 1 | 38 | 0.00027734 | 7.3e-06 | No
13/02/2019 | 13:02:40 | HH107B | Urban | Third Party | Other | 774 | 30 | 0.037121 | 0.0012374 | No
13/02/2019 | 13:30:50 | MT11 | Rural Long | Planned |  | 68 | 115 | 0.057073 | 0.00049629 | No
13/02/2019 | 15:08:16 | NA30 | Rural Long | Animal | Animal impact | 37 | 202 | 0.054548 | 0.00027004 | No
13/02/2019 | 15:32:46 | SM216C | Urban | Network business | Network error | 2965 | 1 | 0.0047401 | 0.0047401 | No
13/02/2019 | 15:56:42 | SM216C | Urban | Unknown | Unknown | 37.3333 | 78 | 0.0046553 | 5.968e-05 | No
13/02/2019 | 16:56:43 | AP125D | Urban | Overloads |  | 28 | 30 | 0.0013429 | 4.476e-05 | No
14/02/2019 | 00:03:04 | SSD303 | Rural Long | Planned |  | 1219 | 6.5381 | 0.058168 | 0.0088967 | No
14/02/2019 | 03:28:03 | VH32 | Rural Short | Asset failure | HV | 113 | 361.7286 | 0.30453 | 0.00084187 | No
14/02/2019 | 07:26:20 | HH121D | Urban | Overloads |  | 1 | 162 | 0.00025899 | 1.6e-06 | No
14/02/2019 | 08:56:59 | NU02 | Rural Long | Planned |  | 3 | 300 | 0.0065685 | 2.19e-05 | No
14/02/2019 | 09:01:49 | CN73 | Rural Long | Planned |  | 103 | 366 | 0.27513 | 0.00075173 | No
14/02/2019 | 09:03:41 | EL12 | Urban | Planned |  | 99 | 318 | 0.050329 | 0.00015827 | No
14/02/2019 | 09:09:19 | HH522C | Urban | Planned |  | 244 | 305 | 0.11897 | 0.00039008 | No
14/02/2019 | 09:10:48 | HH121F | Urban | Planned |  | 181 | 50 | 0.014468 | 0.00028936 | No
14/02/2019 | 09:11:35 | MTB54 | Rural Long | Planned |  | 107 | 334 | 0.26083 | 0.00078092 | No
14/02/2019 | 09:14:29 | GU32 | Rural Long | Planned |  | 2 | 103 | 0.0015035 | 1.46e-05 | No
14/02/2019 | 09:16:46 | BM56 | Rural Short | Planned |  | 54 | 233 | 0.093738 | 0.00040231 | No
14/02/2019 | 09:18:08 | HH496G | Urban | Planned |  | 90 | 4 | 0.00057552 | 0.00014388 | No
14/02/2019 | 09:20:04 | CBD27C | CBD | Planned |  | 126 | 64 | 1.5654 | 0.024459 | No
14/02/2019 | 09:20:36 | CM09 / CM20 | Rural Long | Planned |  | 4 | 177.75 | 0.0051891 | 2.919e-05 | No
14/02/2019 | 09:24:55 | SB22 | Rural Long | Planned |  | 46 | 264 | 0.088631 | 0.00033572 | No
14/02/2019 | 09:26:36 | BM56 | Rural Short | Planned |  | 1 | 1328 | 0.0098938 | 7.45e-06 | No
14/02/2019 | 09:28:27 | SG07 | Rural Short | Planned |  | 24 | 75 | 0.01341 | 0.0001788 | No
14/02/2019 | 09:31:08 | BT01 | Rural Long | Planned |  | 40 | 360 | 0.1051 | 0.00029193 | No
14/02/2019 | 09:36:07 | AP146B | Urban | Planned |  | 61 | 22 | 0.0021454 | 9.752e-05 | No
14/02/2019 | 09:36:11 | R18 | Rural Long | Planned |  | 5 | 249 | 0.0090864 | 3.649e-05 | No
14/02/2019 | 09:50:57 | HH102D | Urban | Planned |  | 168 | 302 | 0.08111 | 0.00026858 | No
14/02/2019 | 09:53:16 | GA05 | Rural Short | Planned |  | 4 | 240 | 0.0071521 | 2.98e-05 | No
14/02/2019 | 10:04:28 | MTB41 | Rural Short | Planned |  | 12 | 231 | 0.020652 | 8.94e-05 | No
14/02/2019 | 10:13:21 | EL01C | Urban | Unknown | Unknown | 1 | 98 | 0.00015667 | 1.6e-06 | No
14/02/2019 | 10:15:51 | CN12 | Rural Long | Unknown | Unknown | 1 | 65 | 0.00047439 | 7.3e-06 | No
14/02/2019 | 10:20:59 | SM350C | Urban | Planned |  | 63 | 6 | 0.0006043 | 0.00010072 | No
14/02/2019 | 10:23:15 | MT10 | Rural Long | Asset failure | HV | 18 | 150 | 0.019706 | 0.00013137 | No
14/02/2019 | 10:43:11 | BT02 | Rural Long | Planned |  | 5 | 82 | 0.0029923 | 3.649e-05 | No
14/02/2019 | 11:10:22 | VH10 | Rural Short | Planned |  | 2 | 54 | 0.00080462 | 1.49e-05 | No
14/02/2019 | 11:13:45 | SM216C | Urban | Asset failure | LV | 112 | 71 | 0.012713 | 0.00017905 | No
14/02/2019 | 11:18:51 | CV19 | Rural Long | Unknown | Unknown | 9 | 191 | 0.012546 | 6.569e-05 | No
14/02/2019 | 11:38:21 | CBD103C | Urban | Planned |  | 1 | 90 | 0.00014388 | 1.6e-06 | No
14/02/2019 | 11:58:22 | GU13 | Rural Long | Planned |  | 26 | 182 | 0.034536 | 0.00018976 | No
14/02/2019 | 12:10:33 | YK16 | Rural Long | Unknown | Unknown | 1 | 8 | 5.839e-05 | 7.3e-06 | No
14/02/2019 | 12:14:53 | W27 | Rural Long | Asset failure | Distribution substation | 2 | 408 | 0.0059554 | 1.46e-05 | No
14/02/2019 | 12:27:12 | GA53 | Rural Short | Third Party | Vehicle impact | 30 | 214 | 0.04783 | 0.0002235 | No
14/02/2019 | 14:04:30 | VH33 | Rural Short | Asset failure | LV | 1 | 85 | 0.00063326 | 7.45e-06 | No
14/02/2019 | 14:25:09 | MV13 | Rural Short | Overloads |  | 1 | 152 | 0.0011324 | 7.45e-06 | No
14/02/2019 | 15:30:17 | MB42 | Rural Long | Unknown | Unknown | 1 | 49 | 0.00035762 | 7.3e-06 | No
14/02/2019 | 21:04:49 | AP424F | Urban | Asset failure | LV | 1 | 169 | 0.00027018 | 1.6e-06 | No
15/02/2019 | 00:32:39 | GA50 | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
15/02/2019 | 01:26:31 | MG12 | Rural Long | Animal | Animal impact | 306 | 126 | 0.28139 | 0.0022333 | No
15/02/2019 | 05:41:07 | SA520D | Urban | Unknown | Unknown | 44.6667 | 229 | 0.016352 | 7.141e-05 | No
15/02/2019 | 06:33:18 | ST35 | Rural Long | Unknown | Unknown | 189 | 40.2169 | 0.055475 | 0.0013794 | No
15/02/2019 | 06:55:31 | MB17 | Rural Short | Animal | Animal impact | 1 | 171 | 0.001274 | 7.45e-06 | No
15/02/2019 | 08:09:21 | AP424B | Urban | Planned |  | 105 | 257 | 0.04314 | 0.00016786 | No
15/02/2019 | 08:27:34 | MTB32 | Rural Long | Planned |  | 5 | 184 | 0.0067145 | 3.649e-05 | No
15/02/2019 | 08:28:28 | NU21 | Rural Long | Planned |  | 48 | 178.1042 | 0.062393 | 0.00035032 | No
15/02/2019 | 08:36:48 | SD38200 | Rural Long | Planned |  | 17 | 38 | 0.0047147 | 0.00012407 | No
15/02/2019 | 08:51:36 | CN21 | Rural Long | Planned |  | 114 | 79.6053 | 0.066232 | 0.00083201 | No
15/02/2019 | 08:55:07 | HH409A | Urban | Planned |  | 118 | 40 | 0.0075458 | 0.00018864 | No
15/02/2019 | 08:57:20 | PL14 | Urban | Planned |  | 12 | 276 | 0.0052948 | 1.918e-05 | No
15/02/2019 | 09:00:43 | EL17 | Urban | Planned |  | 85 | 138.8235 | 0.018864 | 0.00013589 | No
15/02/2019 | 09:16:20 | HH386C | Urban | Planned |  | 2 | 87 | 0.00027817 | 3.2e-06 | No
15/02/2019 | 09:22:53 | MTB61 | Rural Short | Planned |  | 136 | 70 | 0.070925 | 0.0010132 | No
15/02/2019 | 09:24:10 | VH18 | Rural Short | Planned |  | 18 | 188 | 0.025211 | 0.0001341 | No
15/02/2019 | 09:30:00 | MB82 | Rural Long | Planned |  | 1 | 21 | 0.00015327 | 7.3e-06 | No
15/02/2019 | 09:30:29 | ST35 | Rural Long | Planned |  | 32 | 207 | 0.048344 | 0.00023355 | No
15/02/2019 | 09:41:51 | HH386B | Urban | Planned |  | 157 | 74 | 0.018573 | 0.00025099 | No
15/02/2019 | 09:43:51 | WHY13 | Urban | Planned |  | 71 | 25 | 0.0028377 | 0.00011351 | No
15/02/2019 | 09:50:41 | SG13 | Rural Short | Planned |  | 35 | 241 | 0.062842 | 0.00026076 | No
15/02/2019 | 09:55:19 | MV52 | Rural Short | Planned |  | 33 | 192 | 0.047204 | 0.00024585 | No
15/02/2019 | 10:03:44 | WK65 | Rural Short | Planned |  | 2 | 72 | 0.0010728 | 1.49e-05 | No
15/02/2019 | 11:24:31 | EL23 | Urban | Overloads |  | 1.3333 | 82 | 0.00017479 | 2.13e-06 | No
15/02/2019 | 11:40:21 | HH429C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 359 | 0.00057392 | 1.6e-06 | No
15/02/2019 | 11:43:19 | HH522C | Urban | Planned |  | 172 | 235 | 0.064618 | 0.00027497 | No
15/02/2019 | 11:50:15 | CD03 | Rural Short | Planned |  | 3 | 50 | 0.0011175 | 2.235e-05 | No
15/02/2019 | 11:54:35 | HH496G | Urban | Planned |  | 90 | 7 | 0.0010072 | 0.00014388 | No
15/02/2019 | 11:57:19 | AP125D | Urban | Overloads |  | 1 | 386 | 0.00061709 | 1.6e-06 | No
15/02/2019 | 12:06:00 | CV33 | Rural Long | Planned |  | 2 | 44 | 0.00064225 | 1.46e-05 | No
15/02/2019 | 12:13:52 | AP529E | Urban | Asset failure | LV | 1 | 55 | 8.793e-05 | 1.6e-06 | No
15/02/2019 | 12:21:05 | AP226D | Urban | Asset failure | HV | 69 | 389 | 0.04291 | 0.00011031 | No
15/02/2019 | 13:54:02 | SM179D | Urban | Asset failure | LV | 1 | 322 | 0.00051477 | 1.6e-06 | No
15/02/2019 | 13:55:28 | SG01 | Rural Short | Asset failure | LV | 1 | 64 | 0.00047681 | 7.45e-06 | No
15/02/2019 | 15:06:38 | AP425B | Urban | Third Party | Vehicle impact | 38 | 79 | 0.0047992 | 6.075e-05 | No
15/02/2019 | 19:59:43 | SSD165 | Urban | Planned |  | 1 | 34 | 5.435e-05 | 1.6e-06 | No
16/02/2019 | 01:17:54 | MTB13 | Rural Short | Unknown | Unknown | 106 | 228 | 0.18006 | 0.00078972 | No
16/02/2019 | 03:52:35 | HH341H | Urban | Vegetation | Grow-in - NSP responsibility | 5 | 632 | 0.0050518 | 7.99e-06 | No
16/02/2019 | 07:11:23 | HH409C | Urban | Asset failure | HV | 97 | 345 | 0.0535 | 0.00015507 | No
16/02/2019 | 08:24:02 | SSD272 | Rural Short | Planned |  | 1 | 1826 | 0.013604 | 7.45e-06 | No
16/02/2019 | 10:02:12 | HH130F | Urban | Asset failure | LV | 1 | 360 | 0.00057552 | 1.6e-06 | No
16/02/2019 | 12:25:19 | AP529B | Urban | Asset failure | HV | 546 | 177.337 | 0.15479 | 0.00087288 | No
16/02/2019 | 14:46:01 | MTB61 | Rural Short | Third Party | Other | 1274 | 52.0918 | 0.49443 | 0.0094915 | No
16/02/2019 | 18:23:37 | MT01 | Rural Long | Asset failure | LV | 1 | 256 | 0.0018684 | 7.3e-06 | No
17/02/2019 | 04:53:56 | MTB22 | Rural Short | Planned |  | 216 | 177 | 0.28483 | 0.0016092 | No
17/02/2019 | 06:53:52 | VH23 | Rural Short | Unknown | Unknown | 15.6667 | 129 | 0.015057 | 0.00011672 | No
17/02/2019 | 08:32:22 | HH107C | Urban | Planned |  | 119 | 236 | 0.044897 | 0.00019024 | No
17/02/2019 | 08:52:16 | AP226D | Urban | Network business | Switching and protection error | 69 | 159 | 0.017539 | 0.00011031 | No
17/02/2019 | 12:09:16 | HH432C | Urban | Asset failure | LV | 1 | 498 | 0.00079614 | 1.6e-06 | No
17/02/2019 | 13:56:58 | HH107C | Urban | Asset failure | LV | 39.6666 | 257 | 0.016297 | 6.341e-05 | No
17/02/2019 | 14:10:53 | NL111Q | Urban | Overloads |  | 1 | 133 | 0.00021262 | 1.6e-06 | No
17/02/2019 | 17:18:58 | HH107A | Urban | Asset failure | LV | 28.3333 | 133 | 0.0060243 | 4.53e-05 | No
17/02/2019 | 17:30:07 | NL210A | Urban | Unknown | Unknown | 11.6667 | 62 | 0.0011564 | 1.865e-05 | No
17/02/2019 | 18:32:16 | HH429C | Urban | Overloads |  | 1 | 178 | 0.00028456 | 1.6e-06 | No
17/02/2019 | 19:10:41 | MV52 | Rural Short | Animal | Animal impact | 26.6667 | 93 | 0.018476 | 0.00019867 | No
17/02/2019 | 20:09:19 | SM350E | Urban | Asset failure | LV | 1 | 175 | 0.00027977 | 1.6e-06 | No
17/02/2019 | 21:03:20 | WHY07 | Urban | Other |  | 1 | 253 | 0.00040446 | 1.6e-06 | No
17/02/2019 | 21:06:40 | EL02 | Urban | Asset failure | LV | 74 | 98 | 0.011594 | 0.0001183 | No
17/02/2019 | 22:18:23 | SM349A | Urban | Asset failure | LV | 1 | 120 | 0.00019184 | 1.6e-06 | No
18/02/2019 | 03:58:35 | HH121G | Urban | Animal | Animal impact | 470 | 78 | 0.058607 | 0.00075138 | No
18/02/2019 | 08:39:45 | SM126E | Urban | Planned |  | 45 | 5 | 0.0003597 | 7.194e-05 | No
18/02/2019 | 08:51:42 | WHY07 | Urban | Planned |  | 2 | 310 | 0.00099118 | 3.2e-06 | No
18/02/2019 | 08:58:45 | PL33 | Rural Long | Planned |  | 1 | 194 | 0.0014159 | 7.3e-06 | No
18/02/2019 | 09:00:44 | CL10 | Rural Long | Planned |  | 1 | 62 | 0.0004525 | 7.3e-06 | No
18/02/2019 | 09:16:50 | NA12 | Rural Long | Unknown | Unknown | 1 | 113 | 0.00082471 | 7.3e-06 | No
18/02/2019 | 09:20:09 | GU43 | Rural Long | Planned |  | 1 | 124 | 0.00090499 | 7.3e-06 | No
18/02/2019 | 09:24:53 | NU05 | Rural Short | Planned |  | 25 | 308 | 0.057366 | 0.00018625 | No
18/02/2019 | 09:29:12 | CD03 | Rural Short | Asset failure | LV | 2 | 20 | 0.00029801 | 1.49e-05 | No
18/02/2019 | 09:46:40 | SG09 | Rural Short | Planned |  | 146 | 277 | 0.3013 | 0.0010877 | No
18/02/2019 | 09:46:51 | SG13 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 133 | 0.00099087 | 7.45e-06 | No
18/02/2019 | 09:49:56 | HH386B | Urban | Planned |  | 137 | 56 | 0.012265 | 0.00021902 | No
18/02/2019 | 09:50:31 | MTB61 | Rural Short | Planned |  | 11 | 96 | 0.0078674 | 8.195e-05 | No
18/02/2019 | 10:00:21 | KA31 | Rural Long | Planned |  | 2 | 29 | 0.0004233 | 1.46e-05 | No
18/02/2019 | 10:04:28 | SB16 | Rural Long | Planned |  | 3 | 110 | 0.0024084 | 2.19e-05 | No
18/02/2019 | 10:05:32 | BT37 | Rural Long | Planned |  | 1 | 90 | 0.00065685 | 7.3e-06 | No
18/02/2019 | 10:16:22 | ST36 | Rural Long | Planned |  | 110 | 268 | 0.21516 | 0.00080282 | No
18/02/2019 | 11:05:37 | EL260C | Urban | Animal | Animal impact | 69 | 3 | 0.00033093 | 0.00011031 | No
18/02/2019 | 11:12:42 | CD03 | Rural Short | Asset failure | LV | 6 | 29 | 0.0012963 | 4.47e-05 | No
18/02/2019 | 11:38:45 | NL544B | Urban | Planned |  | 2 | 174 | 0.00055634 | 3.2e-06 | No
18/02/2019 | 11:43:04 | HH102C | Urban | Planned |  | 116 | 77 | 0.014279 | 0.00018545 | No
18/02/2019 | 11:44:04 | EL12 | Urban | Planned |  | 7 | 152 | 0.001701 | 1.119e-05 | No
18/02/2019 | 11:57:43 | HH107A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 323 | 0.00051637 | 1.6e-06 | No
18/02/2019 | 13:02:49 | AP226D | Urban | Other |  | 69 | 34 | 0.0037505 | 0.00011031 | No
18/02/2019 | 14:12:17 | MG10 | Rural Long | Unknown | Unknown | 1 | 29 | 0.00021165 | 7.3e-06 | No
18/02/2019 | 16:24:37 | ME200E | Urban | Third Party | Other | 1659 | 26 | 0.068957 | 0.0026522 | No
18/02/2019 | 16:35:46 | PL27 | Rural Long | Unknown | Unknown | 2 | 15 | 0.00021895 | 1.46e-05 | No
18/02/2019 | 20:46:26 | HH386D | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 124 | 0.00019824 | 1.6e-06 | No
18/02/2019 | 20:53:16 | EL15 | Urban | Asset failure | LV | 1 | 86 | 0.00013749 | 1.6e-06 | No
18/02/2019 | 20:57:08 | M73 | Rural Long | Weather |  | 74 | 310 | 0.16742 | 0.00054008 | No
18/02/2019 | 21:23:29 | NL115C | Urban | Third Party | Vehicle impact | 7 | 368 | 0.0041182 | 1.119e-05 | No
19/02/2019 | 00:55:04 | CBD412A | Urban | Planned |  | 116 | 106 | 0.019657 | 0.00018545 | No
19/02/2019 | 07:03:41 | M73 | Rural Long | Overloads |  | 1 | 211 | 0.0015399 | 7.3e-06 | No
19/02/2019 | 07:21:30 | BM15 | Rural Short | Animal | Animal impact | 4 | 84 | 0.0025032 | 2.98e-05 | No
19/02/2019 | 08:31:11 | MG17 | Rural Long | Planned |  | 246 | 315 | 0.56555 | 0.0017954 | No
19/02/2019 | 08:35:18 | WK52 | Rural Short | Planned |  | 1 | 110 | 0.00081952 | 7.45e-06 | No
19/02/2019 | 08:41:29 | VH19 | Rural Short | Planned |  | 62 | 380 | 0.17553 | 0.00046191 | No
19/02/2019 | 08:45:25 | SA744D | Urban | Planned |  | 204 | 283 | 0.092295 | 0.00032613 | No
19/02/2019 | 08:46:32 | ST12 | Rural Short | Planned |  | 384 | 347.1146 | 0.99305 | 0.0028609 | No
19/02/2019 | 09:14:46 | W06 | Rural Long | Planned |  | 150 | 324 | 0.3547 | 0.0010948 | No
19/02/2019 | 09:22:47 | SA20 | Urban | Asset failure | HV | 1 | 16 | 2.558e-05 | 1.6e-06 | No
19/02/2019 | 09:24:54 | ST36 | Rural Long | Planned |  | 34 | 253 | 0.06278 | 0.00024814 | No
19/02/2019 | 09:26:30 | SA17 | Urban | Planned |  | 1 | 267 | 0.00042685 | 1.6e-06 | No
19/02/2019 | 09:28:39 | SM216B | Urban | Planned |  | 120 | 41 | 0.0078655 | 0.00019184 | No
19/02/2019 | 09:32:59 | CD20 | Rural Long | Planned |  | 62 | 175 | 0.079187 | 0.0004525 | No
19/02/2019 | 09:41:49 | HH428A | Urban | Planned |  | 109 | 186 | 0.032412 | 0.00017426 | No
19/02/2019 | 09:45:31 | CL16 | Rural Long | Planned |  | 41 | 56 | 0.016757 | 0.00029923 | No
19/02/2019 | 10:05:49 | HH177E | Urban | Planned |  | 1 | 289 | 0.00046202 | 1.6e-06 | No
19/02/2019 | 10:18:05 | PL27 | Rural Long | Unknown | Unknown | 144 | 67 | 0.070414 | 0.001051 | No
19/02/2019 | 10:18:28 | HH177E | Urban | Planned |  | 108 | 249 | 0.042992 | 0.00017266 | No
19/02/2019 | 10:19:51 | CV26 | Rural Long | Planned |  | 8 | 86 | 0.0050213 | 5.839e-05 | No
19/02/2019 | 10:27:18 | HH386A | Urban | Planned |  | 210 | 106 | 0.035587 | 0.00033572 | No
19/02/2019 | 11:09:36 | SA744D | Urban | Planned |  | 3 | 83 | 0.00039807 | 4.8e-06 | No
19/02/2019 | 12:01:52 | BT37 | Rural Long | Unknown | Unknown | 24 | 66 | 0.011561 | 0.00017516 | No
19/02/2019 | 14:15:09 | MG31 | Rural Long | Asset failure | HV | 1 | 48 | 0.00035032 | 7.3e-06 | No
19/02/2019 | 14:17:12 | GA33 | Rural Short | Asset failure | Distribution substation | 36 | 169 | 0.045327 | 0.00026821 | No
19/02/2019 | 14:25:24 | SD55100 | Rural Long | Planned |  | 1 | 34 | 0.00024814 | 7.3e-06 | No
19/02/2019 | 15:35:15 | SSD521 | Rural Short | Network business | Switching and protection error | 1782 | 11 | 0.14604 | 0.013276 | No
19/02/2019 | 16:46:47 | HH522B | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
19/02/2019 | 17:05:03 | VH17 | Rural Short | Asset failure | HV | 2 | 135 | 0.0020115 | 1.49e-05 | No
19/02/2019 | 20:02:55 | MG17 | Rural Long | Asset failure | LV | 7 | 73 | 0.0037295 | 5.109e-05 | No
19/02/2019 | 21:52:34 | SA20 | Urban | Unknown | Unknown | 161 | 38 | 0.0097807 | 0.00025739 | No
19/02/2019 | 22:13:26 | AP227D | Urban | Planned |  | 41 | 254 | 0.016649 | 6.555e-05 | No
19/02/2019 | 22:16:31 | CBD367J | Urban | Planned |  | 3 | 294 | 0.00141 | 4.8e-06 | No
20/02/2019 | 02:47:28 | HH177G | Urban | Asset failure | LV | 16.6667 | 381 | 0.010152 | 2.664e-05 | No
20/02/2019 | 03:55:08 | HH341D | Urban | Animal | Animal impact | 554 | 86 | 0.076167 | 0.00088567 | No
20/02/2019 | 07:10:26 | CD18 | Rural Long | Weather |  | 24 | 300 | 0.052548 | 0.00017516 | No
20/02/2019 | 08:04:58 | HK05 | Rural Long | Planned |  | 35 | 478 | 0.1221 | 0.00025544 | No
20/02/2019 | 08:41:46 | BM53 | Rural Short | Planned |  | 35 | 298 | 0.077705 | 0.00026076 | No
20/02/2019 | 08:42:05 | SD33200 | Rural Long | Planned |  | 1 | 160 | 0.0011677 | 7.3e-06 | No
20/02/2019 | 09:01:34 | PL04 | Urban | Planned |  | 4 | 288 | 0.0018417 | 6.39e-06 | No
20/02/2019 | 09:02:04 | EL10 | Urban | Planned |  | 56 | 303 | 0.027126 | 8.953e-05 | No
20/02/2019 | 09:03:02 | CV33 | Rural Long | Planned |  | 3 | 132 | 0.0028901 | 2.19e-05 | No
20/02/2019 | 09:10:36 | MTB52 | Rural Long | Planned |  | 21 | 206 | 0.031573 | 0.00015327 | No
20/02/2019 | 09:25:51 | YK02 | Rural Short | Planned |  | 4 | 188 | 0.0056025 | 2.98e-05 | No
20/02/2019 | 09:29:01 | VH18 | Rural Short | Planned |  | 44 | 190 | 0.062283 | 0.00032781 | No
20/02/2019 | 09:35:48 | SG09 | Rural Short | Planned |  | 39 | 310 | 0.090072 | 0.00029056 | No
20/02/2019 | 09:43:15 | ST13 | Rural Short | Planned |  | 141 | 65.0851 | 0.06837 | 0.0010505 | No
20/02/2019 | 09:45:03 | BT02 | Rural Long | Planned |  | 2 | 65 | 0.00094878 | 1.46e-05 | No
20/02/2019 | 09:56:03 | GU13 | Rural Long | Planned |  | 338 | 290.7189 | 0.71716 | 0.0024668 | No
20/02/2019 | 10:24:06 | HH107C | Urban | Planned |  | 69 | 311 | 0.034306 | 0.00011031 | No
20/02/2019 | 11:21:13 | BT02 | Rural Long | Planned |  | 3 | 161 | 0.0035251 | 2.19e-05 | No
20/02/2019 | 12:00:26 | PL25 | Rural Long | Planned |  | 66 | 149 | 0.071772 | 0.00048169 | No
20/02/2019 | 12:27:03 | AP226D | Urban | Planned |  | 1 | 153 | 0.0002446 | 1.6e-06 | No
20/02/2019 | 17:03:19 | SG03 | Rural Short | Asset failure | LV | 2 | 209 | 0.0031142 | 1.49e-05 | No
20/02/2019 | 20:36:21 | EL10 | Urban | Asset failure | HV | 947 | 97.8501 | 0.14814 | 0.001514 | No
20/02/2019 | 20:36:21 | EL10 | Urban | Asset failure | HV | 0 | 1 | 0.0011846 | 0 | No
20/02/2019 | 21:25:00 | AP227D | Urban | Planned |  | 25 | 287.72 | 0.011499 | 3.997e-05 | No
20/02/2019 | 22:24:01 | CBD412S | Urban | Planned |  | 36 | 2 | 0.0001151 | 5.755e-05 | No
20/02/2019 | 22:24:01 | CBD412S | Urban | Planned |  | 0 | 8 | 0.00046042 | 0 | No
21/02/2019 | 06:44:02 | NU21 | Rural Long | Asset failure | LV | 9.6667 | 134 | 0.0094538 | 7.055e-05 | No
21/02/2019 | 07:09:47 | MG11 | Rural Short | Unknown | Unknown | 2.6667 | 83 | 0.001649 | 1.987e-05 | No
21/02/2019 | 07:28:13 | BM57 | Rural Short | Animal | Animal impact | 1 | 84 | 0.00062581 | 7.45e-06 | No
21/02/2019 | 07:30:31 | CN11 | Rural Long | Planned |  | 7 | 15 | 0.00076633 | 5.109e-05 | No
21/02/2019 | 08:18:54 | MV64 | Urban | Third Party | Vehicle impact | 2621 | 1 | 0.0041901 | 0.0041901 | No
21/02/2019 | 08:18:54 | MV63 | Rural Short | Third Party | Vehicle impact | 629 | 89.1733 | 0.41788 | 0.0046861 | No
21/02/2019 | 09:04:08 | EL19 | Urban | Planned |  | 87 | 72.7931 | 0.010124 | 0.00013908 | No
21/02/2019 | 09:16:24 | VH18 | Rural Short | Planned |  | 3 | 322 | 0.0071968 | 2.235e-05 | No
21/02/2019 | 09:24:15 | AP424B | Urban | Planned |  | 105 | 258 | 0.043308 | 0.00016786 | No
21/02/2019 | 09:25:36 | HH522C | Urban | Planned |  | 61 | 303 | 0.029548 | 9.752e-05 | No
21/02/2019 | 09:33:19 | CV29 | Rural Long | Planned |  | 8 | 239 | 0.013954 | 5.839e-05 | No
21/02/2019 | 09:47:13 | KI53 | Rural Long | Planned |  | 7 | 276 | 0.0141 | 5.109e-05 | No
21/02/2019 | 09:49:38 | MTB52 | Rural Long | Planned |  | 39 | 255 | 0.072582 | 0.00028464 | No
21/02/2019 | 09:50:01 | HH341G | Urban | Planned |  | 350 | 277 | 0.15499 | 0.00055954 | No
21/02/2019 | 10:05:54 | AP424E | Urban | Planned |  | 181 | 206 | 0.059608 | 0.00028936 | No
21/02/2019 | 10:12:03 | SB16 | Rural Long | Planned |  | 2 | 92 | 0.0013429 | 1.46e-05 | No
21/02/2019 | 10:33:00 | CM11 | Rural Long | Planned |  | 1 | 127 | 0.00092689 | 7.3e-06 | No
21/02/2019 | 10:43:55 | GU15 | Rural Long | Planned |  | 8 | 158 | 0.0092251 | 5.839e-05 | No
21/02/2019 | 12:12:25 | W20 | Rural Long | Unknown | Unknown | 5 | 100 | 0.0036492 | 3.649e-05 | No
21/02/2019 | 13:15:32 | KA08 | Rural Long | Unknown | Unknown | 2 | 70 | 0.0010218 | 1.46e-05 | No
21/02/2019 | 13:38:28 | GA21 | Rural Long | Planned |  | 1 | 43 | 0.00031383 | 7.3e-06 | No
21/02/2019 | 14:25:34 | HH121F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 527 | 42.7894 | 0.03605 | 0.0008425 | No
21/02/2019 | 14:27:36 | EL01R | Urban | Third Party | Vehicle impact | 24.6666 | 175 | 0.0069009 | 3.943e-05 | No
21/02/2019 | 15:00:47 | HH428F | Urban | Overloads |  | 24.3333 | 279 | 0.010853 | 3.89e-05 | No
21/02/2019 | 15:16:17 | MG03 | Rural Short | Asset failure | LV | 2 | 73 | 0.0010877 | 1.49e-05 | No
21/02/2019 | 16:35:05 | SG10 | Rural Short | Asset failure | LV | 1 | 63 | 0.00046936 | 7.45e-06 | No
21/02/2019 | 18:02:18 | HH121F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 43 | 168 | 0.011549 | 6.874e-05 | No
21/02/2019 | 18:52:33 | MB01 | Rural Long | Unknown | Unknown | 20 | 32 | 0.0046709 | 0.00014597 | No
21/02/2019 | 21:45:55 | AP125D | Urban | Overloads |  | 1 | 151 | 0.0002414 | 1.6e-06 | No
22/02/2019 | 07:37:15 | PA05 | Rural Long | Planned |  | 29 | 7 | 0.0014816 | 0.00021165 | No
22/02/2019 | 08:17:57 | HH177E | Urban | Planned |  | 191 | 382 | 0.11664 | 0.00030535 | No
22/02/2019 | 08:30:36 | MTB52 | Rural Long | Planned |  | 18 | 110 | 0.014451 | 0.00013137 | No
22/02/2019 | 08:45:03 | MG10 | Rural Long | Planned |  | 24 | 227 | 0.039761 | 0.00017516 | No
22/02/2019 | 08:58:55 | NA06 | Rural Long | Overloads |  | 1 | 330 | 0.0024084 | 7.3e-06 | No
22/02/2019 | 09:01:17 | PL20 | Rural Long | Planned |  | 1 | 262 | 0.0019122 | 7.3e-06 | No
22/02/2019 | 09:01:20 | ST12 | Rural Short | Planned |  | 60 | 258 | 0.11533 | 0.00044701 | No
22/02/2019 | 09:12:36 | MT18 | Rural Long | Planned |  | 24 | 119 | 0.020844 | 0.00017516 | No
22/02/2019 | 09:19:35 | ST13 | Rural Short | Planned |  | 2 | 345 | 0.0051406 | 1.49e-05 | No
22/02/2019 | 09:24:24 | NL544B | Urban | Planned |  | 3 | 194 | 0.00093043 | 4.8e-06 | No
22/02/2019 | 09:24:43 | SG14 | Rural Short | Planned |  | 43 | 45 | 0.014416 | 0.00032036 | No
22/02/2019 | 09:26:35 | VH31 | Rural Short | Planned |  | 224 | 340 | 0.5674 | 0.0016688 | No
22/02/2019 | 09:35:34 | LM64 | Rural Long | Planned |  | 21 | 147 | 0.02253 | 0.00015327 | No
22/02/2019 | 09:37:26 | KI31 | Rural Short | Animal | Animal nesting/burrowing, etc and other | 1 | 205 | 0.0015273 | 7.45e-06 | No
22/02/2019 | 09:44:18 | MG37 | Rural Long | Asset failure | LV | 4.6667 | 191 | 0.0065052 | 3.406e-05 | No
22/02/2019 | 09:46:22 | LM52 | Rural Long | Planned |  | 9 | 32 | 0.0021019 | 6.569e-05 | No
22/02/2019 | 09:53:09 | SM216E | Urban | Planned |  | 63 | 243 | 0.024474 | 0.00010072 | No
22/02/2019 | 09:55:25 | SG09 | Rural Short | Planned |  | 139 | 274.3813 | 0.28414 | 0.0010356 | No
22/02/2019 | 09:55:50 | SB17 | Rural Long | Planned |  | 150 | 52 | 0.056927 | 0.0010948 | No
22/02/2019 | 09:59:25 | MG37 | Rural Long | Other |  | 1 | 232 | 0.0016932 | 7.3e-06 | No
22/02/2019 | 10:10:23 | CD26 | Rural Long | Planned |  | 1 | 178 | 0.0012991 | 7.3e-06 | No
22/02/2019 | 10:16:43 | LM13 | Rural Long | Planned |  | 82 | 201 | 0.12029 | 0.00059846 | No
22/02/2019 | 10:25:03 | MB22 | Rural Short | Planned |  | 4 | 11 | 0.00032781 | 2.98e-05 | No
22/02/2019 | 10:30:01 | MV33 | Rural Short | Planned |  | 5 | 104 | 0.0038741 | 3.725e-05 | No
22/02/2019 | 10:30:07 | KI41 | Rural Long | Planned |  | 1 | 63 | 0.0004598 | 7.3e-06 | No
22/02/2019 | 10:30:15 | HH496E | Urban | Planned |  | 3 | 220 | 0.0010551 | 4.8e-06 | No
22/02/2019 | 10:46:44 | CM02 | Rural Long | Planned |  | 42 | 200 | 0.061306 | 0.00030653 | No
22/02/2019 | 10:54:49 | ME347B | Urban | Planned |  | 5 | 87 | 0.00069542 | 7.99e-06 | No
22/02/2019 | 12:39:45 | SA744D | Urban | Asset failure | LV | 7.3333 | 129 | 0.0015123 | 1.172e-05 | No
22/02/2019 | 13:25:04 | KA28 | Rural Long | Unknown | Unknown | 1 | 5 | 3.649e-05 | 7.3e-06 | No
22/02/2019 | 13:42:33 | BU03 | Rural Long | Unknown | Unknown | 1 | 1 | 7.3e-06 | 7.3e-06 | No
22/02/2019 | 13:45:24 | HH429C | Urban | Third Party | Vehicle impact | 1 | 111 | 0.00017745 | 1.6e-06 | No
22/02/2019 | 13:58:15 | NA06 | Rural Long | Planned |  | 4 | 109 | 0.0031821 | 2.919e-05 | No
22/02/2019 | 14:24:12 | SG09 | Rural Short | Planned |  | 1 | 40 | 0.00029801 | 7.45e-06 | No
22/02/2019 | 14:27:15 | GA03 | Rural Long | Overloads |  | 1 | 266 | 0.0019414 | 7.3e-06 | No
22/02/2019 | 14:42:03 | CN73 | Rural Long | Asset failure | HV | 1 | 19 | 0.00013867 | 7.3e-06 | No
22/02/2019 | 18:02:36 | GU21 | Rural Long | Asset failure | LV | 12.3333 | 115 | 0.010351 | 9.001e-05 | No
22/02/2019 | 19:24:01 | MI11 | Rural Long | Unknown | Unknown | 46 | 208 | 0.069831 | 0.00033572 | No
22/02/2019 | 20:54:10 | EL17 | Urban | Asset failure | LV | 2 | 208 | 0.00066505 | 3.2e-06 | No
22/02/2019 | 21:12:45 | HH403A | Urban | Asset failure | LV | 1 | 86 | 0.00013749 | 1.6e-06 | No
22/02/2019 | 22:46:41 | SM126C | Urban | Animal | Animal impact | 53 | 109 | 0.0092356 | 8.473e-05 | No
23/02/2019 | 05:50:03 | KA05 | Rural Long | Asset failure | LV | 10 | 117 | 0.008539 | 7.298e-05 | No
23/02/2019 | 06:36:20 | HH496A | Urban | Unknown | Unknown | 2005 | 28.7307 | 0.092092 | 0.0032053 | No
23/02/2019 | 07:01:37 | MI26 | Rural Long | Unknown | Unknown | 71 | 190 | 0.098455 | 0.00051818 | No
23/02/2019 | 07:20:12 | GA745A | Rural Short | Asset failure | LV | 1 | 498 | 0.0037102 | 7.45e-06 | No
23/02/2019 | 07:30:15 | HH145E | Urban | Unknown | Unknown | 128.0001 | 41.3594 | 0.0084634 | 0.00020463 | No
23/02/2019 | 08:27:29 | HH130D | Urban | Asset failure | LV | 1 | 217 | 0.00034691 | 1.6e-06 | No
23/02/2019 | 08:54:16 | HH177G | Urban | Asset failure | LV | 1 | 222 | 0.00035491 | 1.6e-06 | No
23/02/2019 | 09:26:09 | HH496D | Urban | Planned |  | 89 | 153.382 | 0.021824 | 0.00014228 | No
23/02/2019 | 09:44:37 | AP149E | Urban | Asset failure | LV | 37 | 228 | 0.013486 | 5.915e-05 | No
23/02/2019 | 15:16:38 | NU13 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 176 | 0.0012845 | 7.3e-06 | No
23/02/2019 | 18:22:38 | HH386C | Urban | Vegetation | Grow-in - NSP responsibility | 67 | 361 | 0.038667 | 0.00010711 | No
23/02/2019 | 19:59:28 | AP424C | Urban | Asset failure | LV | 28 | 97 | 0.004342 | 4.476e-05 | No
23/02/2019 | 20:52:30 | HH102C | Urban | Asset failure | LV | 9 | 139 | 0.0019999 | 1.439e-05 | No
24/02/2019 | 00:28:40 | HH121A | Urban | Asset failure | LV | 1 | 363 | 0.00058032 | 1.6e-06 | No
24/02/2019 | 01:26:32 | HH386C | Urban | Asset failure | LV | 22.3333 | 265 | 0.0094615 | 3.57e-05 | No
24/02/2019 | 02:32:45 | HH121A | Urban | Asset failure | LV | 2 | 239 | 0.00076417 | 3.2e-06 | No
24/02/2019 | 07:19:33 | HH428A | Urban | Asset failure | LV | 1 | 125 | 0.00019983 | 1.6e-06 | No
24/02/2019 | 08:02:17 | SSD317 | Rural Short | Asset failure | Zone substation | 1883 | 5 | 0.070143 | 0.014029 | No
24/02/2019 | 08:19:55 | EL02 | Urban | Planned |  | 2 | 240 | 0.00076736 | 3.2e-06 | No
24/02/2019 | 08:21:55 | MV64 | Urban | Asset failure | LV | 1 | 366 | 0.00058512 | 1.6e-06 | No
24/02/2019 | 08:39:13 | SM374C | Urban | Planned |  | 2 | 163 | 0.00052117 | 3.2e-06 | No
24/02/2019 | 08:44:16 | HH130E | Urban | Planned |  | 42 | 172 | 0.011549 | 6.714e-05 | No
24/02/2019 | 09:00:21 | MV62 | Rural Short | Planned |  | 14 | 113 | 0.011786 | 0.0001043 | No
24/02/2019 | 09:22:16 | HH121D | Urban | Planned |  | 46 | 337 | 0.024783 | 7.354e-05 | No
24/02/2019 | 10:32:22 | EL02 | Urban | Overloads |  | 1 | 182 | 0.00029096 | 1.6e-06 | No
24/02/2019 | 14:04:32 | SA33 | Urban | Overloads |  | 1 | 225 | 0.0003597 | 1.6e-06 | No
24/02/2019 | 14:24:51 | MG12 | Rural Long | Unknown | Unknown | 1 | 165 | 0.0012042 | 7.3e-06 | No
24/02/2019 | 15:49:23 | SM349C | Urban | Asset failure | LV | 91 | 225 | 0.032733 | 0.00014548 | No
24/02/2019 | 17:01:43 | HH341H | Urban | Unknown | Unknown | 21.3333 | 65 | 0.0022168 | 3.411e-05 | No
24/02/2019 | 19:08:02 | CN71 | Rural Long | Asset failure | LV | 13 | 228 | 0.021632 | 9.488e-05 | No
24/02/2019 | 19:44:20 | CM28 | Rural Long | Unknown | Unknown | 1 | 184 | 0.0013429 | 7.3e-06 | No
24/02/2019 | 23:00:05 | MV63 | Rural Short | Asset failure | LV | 2 | 186 | 0.0027715 | 1.49e-05 | No
25/02/2019 | 01:37:25 | NL234C | Urban | Asset failure | LV | 1 | 107 | 0.00017106 | 1.6e-06 | No
25/02/2019 | 04:47:09 | EL01N | Urban | Overloads |  | 38.6666 | 287 | 0.017741 | 6.182e-05 | No
25/02/2019 | 07:46:12 | MB42 | Rural Long | Overloads |  | 2 | 216 | 0.0031529 | 1.46e-05 | No
25/02/2019 | 08:04:18 | ST12 | Rural Short | Planned |  | 71 | 253 | 0.13383 | 0.00052896 | No
25/02/2019 | 08:30:45 | HH177F | Urban | Planned |  | 24 | 226 | 0.0086712 | 3.837e-05 | No
25/02/2019 | 09:14:27 | CD01 | Rural Short | Planned |  | 14 | 36 | 0.0037549 | 0.0001043 | No
25/02/2019 | 09:22:53 | GU43 | Rural Long | Planned |  | 13 | 199 | 0.018881 | 9.488e-05 | No
25/02/2019 | 09:29:13 | SG14 | Rural Short | Planned |  | 22 | 220 | 0.036059 | 0.0001639 | No
25/02/2019 | 09:38:29 | SM172B | Urban | Planned |  | 100 | 240 | 0.038368 | 0.00015987 | No
25/02/2019 | 09:44:48 | GA15 | Rural Short | Planned |  | 206 | 93 | 0.14273 | 0.0015347 | No
25/02/2019 | 09:49:12 | CN12 | Rural Long | Planned |  | 4 | 53 | 0.0015473 | 2.919e-05 | No
25/02/2019 | 10:06:41 | HH121B | Urban | Overloads |  | 14.3333 | 94 | 0.0021539 | 2.291e-05 | No
25/02/2019 | 10:07:48 | BM51 | Urban | Planned |  | 50 | 206 | 0.016466 | 7.993e-05 | No
25/02/2019 | 10:10:32 | GU18 | Rural Long | Planned |  | 95 | 246.2316 | 0.17072 | 0.00069334 | No
25/02/2019 | 10:27:02 | MI32 | Rural Long | Asset failure | LV | 1 | 255 | 0.0018611 | 7.3e-06 | No
25/02/2019 | 10:31:03 | CL05 | Rural Long | Planned |  | 57 | 127 | 0.052833 | 0.00041601 | No
25/02/2019 | 10:42:45 | CN76 | Rural Long | Planned |  | 73 | 259 | 0.13799 | 0.00053278 | No
25/02/2019 | 11:35:43 | AP424C | Urban | Overloads |  | 1 | 198 | 0.00031654 | 1.6e-06 | No
25/02/2019 | 11:46:56 | GA15 | Rural Short | Planned |  | 41 | 46 | 0.014051 | 0.00030546 | No
25/02/2019 | 12:12:18 | PL30 | Rural Long | Overloads |  | 2 | 2 | 2.919e-05 | 1.46e-05 | No
25/02/2019 | 12:44:37 | SG12 | Rural Short | Unknown | Unknown | 2 | 98 | 0.0014602 | 1.49e-05 | No
25/02/2019 | 12:57:37 | HH428F | Urban | Vegetation | Grow-in - NSP responsibility | 2238 | 44 | 0.15742 | 0.0035778 | No
25/02/2019 | 13:59:59 | AP344F | Urban | Asset failure | LV | 57 | 54 | 0.0049207 | 9.112e-05 | No
25/02/2019 | 14:06:04 | GA38 | Rural Long | Asset failure | HV | 17 | 139.2941 | 0.017282 | 0.00012407 | No
25/02/2019 | 14:36:58 | AP351E | Urban | Overloads |  | 1 | 559 | 0.00089366 | 1.6e-06 | No
25/02/2019 | 16:14:31 | SM349H | Urban | Overloads |  | 1 | 427 | 0.00068263 | 1.6e-06 | No
25/02/2019 | 17:10:06 | LX43 | Rural Short | Unknown | Unknown | 3.3333 | 118 | 0.0029304 | 2.483e-05 | No
25/02/2019 | 17:42:09 | SM349F | Urban | Asset failure | LV | 1 | 368 | 0.00058831 | 1.6e-06 | No
25/02/2019 | 18:35:22 | SA744C | Urban | Unknown | Unknown | 17 | 303 | 0.0082348 | 2.718e-05 | No
25/02/2019 | 19:11:07 | HH403D | Urban | Unknown | Unknown | 32.3333 | 90 | 0.0046521 | 5.169e-05 | No
25/02/2019 | 19:15:03 | AP424D | Urban | Overloads |  | 56.9999 | 52 | 0.0047385 | 9.112e-05 | No
25/02/2019 | 19:21:42 | AP146C | Urban | Unknown | Unknown | 20.6666 | 62 | 0.0020484 | 3.304e-05 | No
25/02/2019 | 19:35:14 | SM410C | Urban | Unknown | Unknown | 29.3333 | 84 | 0.0039391 | 4.689e-05 | No
25/02/2019 | 19:50:04 | SM411D | Urban | Asset failure | LV | 75 | 197 | 0.02362 | 0.0001199 | No
25/02/2019 | 19:57:20 | EL23 | Urban | Unknown | Unknown | 16.6667 | 140 | 0.0037302 | 2.664e-05 | No
25/02/2019 | 20:04:36 | SM350F | Urban | Other |  | 34 | 306 | 0.016633 | 5.435e-05 | No
25/02/2019 | 20:09:29 | HH341D | Urban | Asset failure | LV | 20 | 94 | 0.0030055 | 3.197e-05 | No
25/02/2019 | 20:24:19 | EL01N | Urban | Asset failure | LV | 1 | 59 | 9.432e-05 | 1.6e-06 | No
25/02/2019 | 21:03:48 | AP226C | Urban | Unknown | Unknown | 37 | 88 | 0.0052053 | 5.915e-05 | No
25/02/2019 | 21:04:57 | EL16 | Urban | Asset failure | HV | 1 | 38 | 6.075e-05 | 1.6e-06 | No
25/02/2019 | 22:23:29 | NL234C | Urban | Asset failure | LV | 70.6667 | 125 | 0.014122 | 0.00011297 | No
25/02/2019 | 22:51:29 | NL111P | Urban | Overloads |  | 1 | 171 | 0.00027337 | 1.6e-06 | No
26/02/2019 | 00:23:59 | PL07 | Urban | Asset failure | HV | 1625 | 233.56 | 0.60675 | 0.0025979 | No
26/02/2019 | 00:32:59 | MI16 | Rural Long | Asset failure | LV | 1 | 170 | 0.0012407 | 7.3e-06 | No
26/02/2019 | 00:51:45 | GA745C | Rural Short | Unknown | Unknown | 1 | 489 | 0.0036431 | 7.45e-06 | No
26/02/2019 | 04:07:40 | CD18 | Rural Long | Asset failure | HV | 24 | 592 | 0.10369 | 0.00017516 | No
26/02/2019 | 08:12:43 | BM55 | Rural Short | Planned |  | 14 | 200 | 0.02086 | 0.0001043 | No
26/02/2019 | 08:39:18 | PA22 | Rural Long | Planned |  | 65 | 210 | 0.099622 | 0.00047439 | No
26/02/2019 | 08:42:20 | SSD165 | Urban | Planned |  | 1 | 52 | 8.313e-05 | 1.6e-06 | No
26/02/2019 | 08:43:15 | VH15 | Rural Short | Planned |  | 272 | 395 | 0.80044 | 0.0020264 | No
26/02/2019 | 08:45:33 | AP214D | Urban | Planned |  | 63 | 17 | 0.0017122 | 0.00010072 | No
26/02/2019 | 08:49:58 | NL111C | Urban | Planned |  | 73 | 283 | 0.033027 | 0.0001167 | No
26/02/2019 | 09:11:49 | EL12 | Urban | Planned |  | 57 | 243 | 0.022143 | 9.112e-05 | No
26/02/2019 | 09:33:19 | HH432B | Urban | Planned |  | 84 | 183 | 0.024575 | 0.00013429 | No
26/02/2019 | 09:38:31 | GA01 | Urban | Planned |  | 20 | 115 | 0.003677 | 3.197e-05 | No
26/02/2019 | 09:49:48 | EL13 | Urban | Third Party | Other | 11 | 48 | 0.0008441 | 1.759e-05 | No
26/02/2019 | 10:10:32 | GA27 | Rural Long | Planned |  | 90 | 80 | 0.052548 | 0.00065685 | No
26/02/2019 | 10:16:10 | EL03 | Urban | Third Party | Other | 7.3333 | 106 | 0.0012427 | 1.172e-05 | No
26/02/2019 | 10:44:16 | MTB54 | Rural Long | Planned |  | 78 | 211 | 0.12012 | 0.00056927 | No
26/02/2019 | 11:34:30 | ST12 | Rural Short | Planned |  | 2 | 200 | 0.0029801 | 1.49e-05 | No
26/02/2019 | 11:41:25 | NA23 | Rural Long | Unknown | Unknown | 1 | 157 | 0.0011458 | 7.3e-06 | No
26/02/2019 | 13:11:24 | SM350E | Urban | Planned |  | 1 | 417 | 0.00066665 | 1.6e-06 | No
26/02/2019 | 14:54:01 | SM410C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2599 | 87.1616 | 0.36215 | 0.004155 | No
26/02/2019 | 15:02:24 | MV61 | Urban | Overloads |  | 1 | 191 | 0.00030535 | 1.6e-06 | No
26/02/2019 | 16:03:31 | M21 | Rural Long | Weather |  | 394 | 28 | 0.080515 | 0.0028756 | No
26/02/2019 | 16:19:11 | SM410D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 61 | 151 | 0.014725 | 9.752e-05 | No
26/02/2019 | 17:15:37 | NL234C | Urban | Asset failure | LV | 35.3333 | 141 | 0.0079646 | 5.649e-05 | No
26/02/2019 | 17:32:38 | SM172E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 80 | 24 | 0.0030695 | 0.00012789 | No
26/02/2019 | 17:51:50 | HH386F | Urban | Overloads |  | 1 | 242 | 0.00038688 | 1.6e-06 | No
26/02/2019 | 18:06:44 | SM172C | Urban | Overloads |  | 68.6666 | 128 | 0.014051 | 0.00010978 | No
26/02/2019 | 18:18:13 | HH102B | Urban | Asset failure | LV | 24.3333 | 106 | 0.0041235 | 3.89e-05 | No
26/02/2019 | 18:45:10 | GA02 | Rural Short | Asset failure | LV | 1 | 214 | 0.0015943 | 7.45e-06 | No
26/02/2019 | 20:29:09 | AP214D | Urban | Asset failure | HV | 111 | 127 | 0.022537 | 0.00017745 | No
26/02/2019 | 21:38:19 | ST35 | Rural Long | Unknown | Unknown | 7 | 410 | 0.020946 | 5.109e-05 | No
26/02/2019 | 23:14:05 | SM349E | Urban | Asset failure | LV | 1 | 128 | 0.00020463 | 1.6e-06 | No
26/02/2019 | 23:19:30 | CD23 | Rural Long | Unknown | Unknown | 37 | 999.0811 | 0.26979 | 0.00027004 | No
27/02/2019 | 00:22:38 | CM25 | Rural Long | Asset failure | HV | 75 | 505 | 0.27642 | 0.00054738 | No
27/02/2019 | 00:49:43 | SM172C | Urban | Unknown | Unknown | 25.3333 | 155 | 0.0062775 | 4.05e-05 | No
27/02/2019 | 00:52:35 | HH145A | Urban | Unknown | Unknown | 290 | 79.2414 | 0.036738 | 0.00046362 | No
27/02/2019 | 01:47:40 | SM126E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 70 | 0.0025739 | 3.677e-05 | No
27/02/2019 | 02:28:50 | GA50 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 28.6666 | 55 | 0.0025206 | 4.583e-05 | No
27/02/2019 | 03:09:11 | CD18 | Rural Long | Unknown | Unknown | 42 | 449.8571 | 0.13789 | 0.00030653 | No
27/02/2019 | 06:41:25 | CN51 | Rural Long | Planned |  | 237 | 95 | 0.16432 | 0.0017297 | No
27/02/2019 | 07:19:08 | ME347A | Urban | Overloads |  | 1 | 193 | 0.00030854 | 1.6e-06 | No
27/02/2019 | 08:01:45 | BM11 | Rural Short | Planned |  | 6 | 248 | 0.011086 | 4.47e-05 | No
27/02/2019 | 08:28:58 | GU15 | Rural Long | Planned |  | 1 | 149 | 0.0010875 | 7.3e-06 | No
27/02/2019 | 08:30:42 | MB81 | Rural Long | Planned |  | 85 | 135 | 0.083748 | 0.00062036 | No
27/02/2019 | 08:45:04 | CM03 | Rural Long | Planned |  | 266 | 360.7519 | 0.70035 | 0.0019414 | No
27/02/2019 | 09:00:27 | SG01 | Rural Short | Planned |  | 16 | 169 | 0.020145 | 0.0001192 | No
27/02/2019 | 09:03:01 | CL23 | Rural Long | Planned |  | 79 | 6 | 0.0034594 | 0.00057657 | No
27/02/2019 | 09:03:28 | SG09 | Rural Short | Planned |  | 86 | 272 | 0.17427 | 0.00064071 | No
27/02/2019 | 09:14:38 | NU23 | Rural Long | Planned |  | 1 | 33 | 0.00024085 | 7.3e-06 | No
27/02/2019 | 09:16:53 | HH107D | Urban | Asset failure | LV | 1 | 164 | 0.00026218 | 1.6e-06 | No
27/02/2019 | 09:32:08 | VH72 | Rural Short | Animal | Animal impact | 49 | 72 | 0.026284 | 0.00036506 | No
27/02/2019 | 10:17:17 | MV31 | Rural Short | Planned |  | 4 | 150 | 0.0044701 | 2.98e-05 | No
27/02/2019 | 10:38:10 | AP424C | Urban | Planned |  | 198 | 16 | 0.0050646 | 0.00031654 | No
27/02/2019 | 10:55:30 | M21 | Rural Long | Unknown | Unknown | 1 | 213 | 0.0015546 | 7.3e-06 | No
27/02/2019 | 11:01:10 | NA08 | Rural Long | Unknown | Unknown | 1 | 157 | 0.0011458 | 7.3e-06 | No
27/02/2019 | 11:01:24 | NA08 | Rural Long | Animal | Animal impact | 1 | 143 | 0.0010437 | 7.3e-06 | No
27/02/2019 | 11:46:57 | AP227A | Urban | Asset failure | LV | 72 | 81 | 0.0093235 | 0.0001151 | No
27/02/2019 | 13:28:52 | SD49200 | Rural Long | Animal | Animal impact | 30 | 102 | 0.022333 | 0.00021895 | No
27/02/2019 | 13:55:40 | NL115F | Urban | Overloads |  | 1 | 166 | 0.00026538 | 1.6e-06 | No
27/02/2019 | 14:09:00 | YK14 | Rural Long | Unknown | Unknown | 1 | 5 | 3.649e-05 | 7.3e-06 | No
27/02/2019 | 14:39:16 | SA711C | Urban | Vegetation | Grow-in - NSP responsibility | 33.3333 | 55 | 0.0029309 | 5.329e-05 | No
27/02/2019 | 14:48:23 | HH107A | Urban | Asset failure | LV | 10 | 120 | 0.0019184 | 1.599e-05 | No
27/02/2019 | 14:56:38 | HH409F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2016 | 61 | 0.1966 | 0.0032229 | No
27/02/2019 | 15:45:59 | NU08 | Rural Long | Unknown | Unknown | 1 | 24 | 0.00017516 | 7.3e-06 | No
27/02/2019 | 16:31:51 | SM137A | Urban | Asset failure | LV | 21 | 64 | 0.0021486 | 3.357e-05 | No
27/02/2019 | 17:37:56 | AP125D | Urban | Unknown | Unknown | 13 | 2 | 4.157e-05 | 2.078e-05 | No
27/02/2019 | 17:53:53 | HH428A | Urban | Asset failure | LV | 1 | 160 | 0.00025579 | 1.6e-06 | No
27/02/2019 | 18:02:43 | SM137A | Urban | Asset failure | LV | 21 | 86 | 0.0028872 | 3.357e-05 | No
27/02/2019 | 18:32:18 | AP214D | Urban | Asset failure | LV | 37 | 96 | 0.0056785 | 5.915e-05 | No
27/02/2019 | 18:55:53 | SM374B | Urban | Asset failure | HV | 1009 | 96.439 | 0.15556 | 0.0016131 | No
27/02/2019 | 23:45:44 | AP139C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 892 | 84.7668 | 0.12088 | 0.001426 | No
27/02/2019 | 23:45:44 | AP139C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 0 | 273 | 0.040152 | 0 | No
28/02/2019 | 01:56:38 | HH341E | Urban | Asset failure | HV | 1628 | 52 | 0.13534 | 0.0026026 | No
28/02/2019 | 02:56:11 | SA520J | Urban | Unknown | Unknown | 3.3333 | 420 | 0.0022381 | 5.33e-06 | No
28/02/2019 | 04:25:27 | GA800A | Rural Short | Asset failure | LV | 1 | 340 | 0.002533 | 7.45e-06 | No
28/02/2019 | 06:00:58 | MG48 | Rural Long | Unknown | Unknown | 101 | 37 | 0.027274 | 0.00073713 | No
28/02/2019 | 07:06:56 | AP139C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 121 | 0.00019344 | 1.6e-06 | No
28/02/2019 | 08:11:37 | SG07 | Rural Short | Planned |  | 81 | 262 | 0.15811 | 0.00060346 | No
28/02/2019 | 08:34:19 | BM43 | Rural Short | Overloads |  | 1 | 403 | 0.0030024 | 7.45e-06 | No
28/02/2019 | 08:45:56 | KI21 | Rural Long | Planned |  | 15 | 321 | 0.035141 | 0.00010948 | No
28/02/2019 | 09:16:59 | HH121C | Urban | Planned |  | 45 | 63 | 0.0045322 | 7.194e-05 | No
28/02/2019 | 09:37:37 | MT18 | Rural Long | Planned |  | 2 | 91 | 0.0013283 | 1.46e-05 | No
28/02/2019 | 09:58:16 | CM25 | Rural Long | Planned |  | 3 | 185 | 0.0040506 | 2.19e-05 | No
28/02/2019 | 10:05:58 | HH121F | Urban | Planned |  | 110 | 51 | 0.0089686 | 0.00017585 | No
28/02/2019 | 10:11:22 | WK72 | Rural Short | Planned |  | 1 | 3 | 2.235e-05 | 7.45e-06 | No
28/02/2019 | 10:16:27 | MG22 | Rural Long | Asset failure | Distribution substation | 849 | 170.1637 | 1.0544 | 0.0061963 | No
28/02/2019 | 10:31:13 | VH12 | Rural Short | Planned |  | 1 | 99 | 0.00073756 | 7.45e-06 | No
28/02/2019 | 10:42:14 | PL34 | Rural Long | Planned |  | 2 | 153 | 0.0022333 | 1.46e-05 | No
28/02/2019 | 10:45:41 | NU24 | Rural Long | Planned |  | 4 | 49 | 0.0014305 | 2.919e-05 | No
28/02/2019 | 10:46:00 | HH121C | Urban | Planned |  | 97 | 48 | 0.0074434 | 0.00015507 | No
28/02/2019 | 10:56:18 | WK72 | Rural Short | Planned |  | 1 | 1 | 7.45e-06 | 7.45e-06 | No
28/02/2019 | 12:39:04 | LX25 | Rural Short | Animal | Animal impact | 1 | 113 | 0.00084187 | 7.45e-06 | No
28/02/2019 | 13:45:27 | MG04 | Rural Short | Unknown | Unknown | 1 | 57 | 0.00042466 | 7.45e-06 | No
28/02/2019 | 15:00:43 | MG22 | Rural Long | Other |  | 2 | 156 | 0.0022771 | 1.46e-05 | No
28/02/2019 | 15:47:34 | HH145B | Urban | Unknown | Unknown | 35.3333 | 120 | 0.0067784 | 5.649e-05 | No
28/02/2019 | 15:56:10 | NL760A | Urban | Third Party | Dig-in | 12 | 139.6667 | 0.0026794 | 1.918e-05 | No
28/02/2019 | 16:54:27 | HH130B | Urban | Overloads |  | 1 | 74 | 0.0001183 | 1.6e-06 | No
28/02/2019 | 17:32:26 | SM410A | Urban | Asset failure | LV | 13 | 285 | 0.0059231 | 2.078e-05 | No
28/02/2019 | 17:45:22 | HH121D | Urban | Asset failure | HV | 68 | 625 | 0.067944 | 0.00010871 | No
28/02/2019 | 18:10:20 | HH409D | Urban | Asset failure | LV | 1 | 531 | 0.0008489 | 1.6e-06 | No
28/02/2019 | 18:20:09 | SSD425 | Urban | Animal | Animal impact | 6860 | 51.8589 | 0.56873 | 0.010967 | No
28/02/2019 | 18:23:01 | AP355F | Urban | Asset failure | LV | 1 | 180 | 0.00028776 | 1.6e-06 | No
28/02/2019 | 18:43:40 | HH177G | Urban | Unknown | Unknown | 21 | 122 | 0.0040958 | 3.357e-05 | No
28/02/2019 | 18:52:31 | HH341G | Urban | Overloads |  | 1 | 275 | 0.00043964 | 1.6e-06 | No
28/02/2019 | 18:52:55 | SB16 | Rural Long | Asset failure | HV | 18 | 97.6111 | 0.012823 | 0.00013137 | No
28/02/2019 | 19:03:46 | AP355A | Urban | Asset failure | LV | 1 | 138 | 0.00022062 | 1.6e-06 | No
28/02/2019 | 22:06:32 | HH102C | Urban | Overloads |  | 1 | 134 | 0.00021422 | 1.6e-06 | No
28/02/2019 | 22:37:45 | AP227D | Urban | Planned |  | 127 | 289 | 0.058676 | 0.00020303 | No
1/03/2019 | 01:16:37 | HH121G | Urban | Unknown | Unknown | 2 | 153 | 0.00048919 | 3.2e-06 | No
1/03/2019 | 01:42:16 | HH121B | Urban | Overloads |  | 1 | 187 | 0.00029895 | 1.6e-06 | No
1/03/2019 | 02:28:59 | HH121B | Urban | Other |  | 1 | 139 | 0.00022222 | 1.6e-06 | No
1/03/2019 | 04:20:34 | HH121D | Urban | Asset failure | LV | 22.3333 | 148 | 0.0052841 | 3.57e-05 | No
1/03/2019 | 07:18:01 | NA04 | Rural Long | Unknown | Unknown | 13 | 127 | 0.01205 | 9.488e-05 | No
1/03/2019 | 08:02:50 | ST44 | Rural Long | Planned |  | 3 | 193 | 0.0042257 | 2.19e-05 | No
1/03/2019 | 08:09:31 | SG10 | Rural Short | Planned |  | 138 | 128 | 0.1316 | 0.0010281 | No
1/03/2019 | 08:11:08 | ME231F | Urban | Planned |  | 1865 | 1 | 0.0029815 | 0.0029815 | No
1/03/2019 | 08:29:37 | BM56 | Rural Short | Planned |  | 12 | 130 | 0.011622 | 8.94e-05 | No
1/03/2019 | 08:51:31 | SM216B | Urban | Planned |  | 1 | 102 | 0.00016306 | 1.6e-06 | No
1/03/2019 | 08:58:18 | MV63 | Rural Short | Planned |  | 10 | 120 | 0.0089402 | 7.45e-05 | No
1/03/2019 | 08:59:20 | HH145C | Urban | Planned |  | 47 | 83 | 0.0062364 | 7.514e-05 | No
1/03/2019 | 09:00:05 | GU43 | Rural Long | Planned |  | 113 | 128 | 0.10556 | 0.00082471 | No
1/03/2019 | 09:05:38 | SM350B | Urban | Planned |  | 95 | 15 | 0.0022781 | 0.00015187 | No
1/03/2019 | 09:17:15 | HK03 | Rural Long | Asset failure | LV | 1 | 337 | 0.0024595 | 7.3e-06 | No
1/03/2019 | 09:36:11 | W28 | Rural Long | Planned |  | 1 | 49 | 0.00035762 | 7.3e-06 | No
1/03/2019 | 10:01:57 | CBD412M | Urban | Asset failure | LV | 10.3333 | 112 | 0.0018502 | 1.652e-05 | No
1/03/2019 | 10:06:01 | NU08 | Rural Long | Third Party | Vehicle impact | 1 | 289 | 0.0021092 | 7.3e-06 | No
1/03/2019 | 10:23:08 | SA12 | Urban | Third Party | Vehicle impact | 1 | 204 | 0.00032613 | 1.6e-06 | No
1/03/2019 | 11:27:40 | MB64 | Rural Long | Third Party | Vehicle impact | 31 | 135 | 0.030544 | 0.00022625 | No
1/03/2019 | 11:31:22 | MG19 | Rural Long | Asset failure | Distribution substation | 214 | 184.4907 | 0.28815 | 0.0015618 | No
1/03/2019 | 11:32:08 | MI32 | Rural Long | Third Party | Dig-in | 4 | 216 | 0.0063058 | 2.919e-05 | No
1/03/2019 | 11:39:41 | HH522C | Urban | Planned |  | 321 | 2 | 0.0010264 | 0.00051317 | No
1/03/2019 | 12:39:06 | AP149A | Urban | Unknown | Unknown | 124 | 121 | 0.023987 | 0.00019824 | No
1/03/2019 | 13:05:46 | MI32 | Rural Long | Unknown | Unknown | 4 | 91 | 0.0026566 | 2.919e-05 | No
1/03/2019 | 13:19:36 | R18 | Rural Long | Third Party | Vehicle impact | 646 | 104.6471 | 0.49338 | 0.0047147 | No
1/03/2019 | 14:19:20 | MG09 | Rural Short | Asset failure | LV | 1 | 60 | 0.00044701 | 7.45e-06 | No
1/03/2019 | 16:26:53 | SA19 | Urban | Overloads |  | 4 | 191 | 0.0012214 | 6.39e-06 | No
1/03/2019 | 17:29:39 | GA15 | Rural Short | Unknown | Unknown | 4.6667 | 182 | 0.0063276 | 3.477e-05 | No
1/03/2019 | 17:57:30 | SM137A | Urban | Overloads |  | 1 | 232 | 0.00037089 | 1.6e-06 | No
1/03/2019 | 18:02:38 | ME427F | Urban | Unknown | Unknown | 32.3333 | 82 | 0.0042386 | 5.169e-05 | No
1/03/2019 | 18:11:54 | HH121B | Urban | Asset failure | LV | 15.6667 | 62 | 0.0015528 | 2.505e-05 | No
1/03/2019 | 18:16:03 | AP214D | Urban | Unknown | Unknown | 36.6666 | 141 | 0.0082651 | 5.862e-05 | No
1/03/2019 | 18:19:55 | AP149E | Urban | Asset failure | LV | 20.6666 | 50 | 0.001652 | 3.304e-05 | No
1/03/2019 | 18:23:47 | AP529A | Urban | Unknown | Unknown | 34.3333 | 52 | 0.0028542 | 5.489e-05 | No
1/03/2019 | 18:26:13 | ME231F | Urban | Unknown | Unknown | 4 | 178 | 0.0011383 | 6.39e-06 | No
1/03/2019 | 18:53:27 | GA53 | Rural Short | Overloads |  | 1 | 181 | 0.0013485 | 7.45e-06 | No
1/03/2019 | 19:18:41 | AP424B | Urban | Asset failure | LV | 41 | 59 | 0.0038672 | 6.555e-05 | No
1/03/2019 | 19:33:00 | HH145B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 231 | 72 | 0.026589 | 0.00036929 | No
1/03/2019 | 19:39:03 | HH102A | Urban | Asset failure | LV | 28.6666 | 174 | 0.0079742 | 4.583e-05 | No
1/03/2019 | 19:49:06 | NL210E | Urban | Unknown | Unknown | 26.3333 | 113 | 0.0047571 | 4.21e-05 | No
1/03/2019 | 19:56:24 | AP355D | Urban | Asset failure | LV | 1 | 163 | 0.00026058 | 1.6e-06 | No
1/03/2019 | 20:47:56 | HH496D | Urban | Asset failure | LV | 1 | 96 | 0.00015347 | 1.6e-06 | No
1/03/2019 | 21:00:34 | AP529E | Urban | Overloads |  | 1 | 80 | 0.00012789 | 1.6e-06 | No
1/03/2019 | 21:27:22 | NL511B | Urban | Unknown | Unknown | 16.6667 | 62 | 0.001652 | 2.664e-05 | No
1/03/2019 | 22:19:27 | EL07 | Urban | Asset failure | LV | 1 | 56 | 8.953e-05 | 1.6e-06 | No
2/03/2019 | 01:44:34 | HH386A | Urban | Animal | Animal nesting/burrowing, etc and other | 19.3333 | 206 | 0.006367 | 3.091e-05 | No
2/03/2019 | 02:02:02 | ST34 | Rural Long | Unknown | Unknown | 2 | 503 | 0.0073421 | 1.46e-05 | No
2/03/2019 | 05:00:25 | HH145C | Urban | Asset failure | LV | 54 | 143 | 0.012345 | 8.633e-05 | No
2/03/2019 | 07:56:05 | EL04 | Urban | Planned |  | 10 | 343.3 | 0.0054883 | 1.599e-05 | No
2/03/2019 | 08:35:13 | PL33 | Rural Long | Unknown | Unknown | 1 | 14 | 0.00010218 | 7.3e-06 | No
2/03/2019 | 10:42:42 | HH403D | Urban | Asset failure | LV | 1 | 207 | 0.00033093 | 1.6e-06 | No
2/03/2019 | 11:15:42 | HH386G | Urban | Third Party | Other | 730 | 77 | 0.089862 | 0.001167 | No
2/03/2019 | 11:16:12 | HH496G | Urban | Asset failure | LV | 1 | 291 | 0.00046521 | 1.6e-06 | No
2/03/2019 | 11:57:29 | HH386A | Urban | Asset failure | LV | 19.3333 | 113 | 0.0034926 | 3.091e-05 | No
2/03/2019 | 12:06:40 | HH386B | Urban | Unknown | Unknown | 19.3333 | 75 | 0.0023181 | 3.091e-05 | No
2/03/2019 | 13:01:55 | AP149D | Urban | Asset failure | LV | 59.9999 | 186 | 0.017841 | 9.592e-05 | No
2/03/2019 | 14:12:31 | SM216A | Urban | Overloads |  | 32.3333 | 80 | 0.0041352 | 5.169e-05 | No
2/03/2019 | 14:45:55 | CV19 | Rural Long | Asset failure | HV | 9 | 377 | 0.024763 | 6.569e-05 | No
2/03/2019 | 16:45:12 | KA22 | Rural Long | Asset failure | LV | 1 | 142 | 0.0010364 | 7.3e-06 | No
2/03/2019 | 16:48:11 | ST22 | Rural Short | Asset failure | HV | 1 | 279 | 0.0020786 | 7.45e-06 | No
2/03/2019 | 17:24:50 | AP214D | Urban | Other |  | 36.6666 | 136 | 0.007972 | 5.862e-05 | No
2/03/2019 | 17:43:25 | SA33 | Urban | Overloads |  | 28 | 139 | 0.006222 | 4.476e-05 | No
2/03/2019 | 17:57:54 | SM179D | Urban | Unknown | Unknown | 43.3333 | 80 | 0.0055421 | 6.928e-05 | No
2/03/2019 | 18:12:22 | HH341H | Urban | Asset failure | LV | 21 | 79 | 0.0026522 | 3.357e-05 | No
2/03/2019 | 18:27:26 | PP03 | Urban | Overloads |  | 1 | 213 | 0.00034052 | 1.6e-06 | No
2/03/2019 | 18:33:11 | PA07 | Rural Long | Other |  | 1 | 238 | 0.001737 | 7.3e-06 | No
2/03/2019 | 18:39:10 | MTB12 | Rural Short | Overloads |  | 14.3333 | 212 | 0.022638 | 0.00010679 | No
2/03/2019 | 18:58:19 | HH102C | Urban | Asset failure | LV | 30 | 104 | 0.0049879 | 4.796e-05 | No
2/03/2019 | 19:02:26 | ME131C | Urban | Asset failure | LV | 57.6666 | 81 | 0.0074674 | 9.219e-05 | No
2/03/2019 | 19:09:33 | HH118D | Urban | Unknown | Unknown | 16 | 139 | 0.0035554 | 2.558e-05 | No
2/03/2019 | 19:31:18 | ST22 | Rural Short | Unknown | Unknown | 1 | 69 | 0.00051406 | 7.45e-06 | No
2/03/2019 | 19:43:08 | SM216F | Urban | Animal | Animal impact | 49.3334 | 242 | 0.019086 | 7.887e-05 | No
2/03/2019 | 19:49:44 | SM349B | Urban | Overloads |  | 30.6666 | 89 | 0.0043633 | 4.903e-05 | No
2/03/2019 | 20:16:47 | HH429C | Urban | Asset failure | LV | 27.6666 | 66 | 0.0029192 | 4.423e-05 | No
3/03/2019 | 03:07:42 | BT02 | Rural Long | Asset failure | HV | 2 | 600 | 0.008758 | 1.46e-05 | No
3/03/2019 | 04:30:25 | HH102D | Urban | Unknown | Unknown | 1802 | 75.2364 | 0.21674 | 0.0028808 | No
3/03/2019 | 06:27:49 | EL17 | Urban | Planned |  | 7 | 208 | 0.0023277 | 1.119e-05 | No
3/03/2019 | 06:56:51 | SA13 | Urban | Asset failure | HV | 1061 | 169.0311 | 0.28671 | 0.0016962 | No
3/03/2019 | 08:45:32 | HH429B | Urban | Asset failure | LV | 1 | 146 | 0.00023341 | 1.6e-06 | No
3/03/2019 | 08:53:57 | NU21 | Rural Long | Overloads |  | 1 | 150 | 0.0010948 | 7.3e-06 | No
3/03/2019 | 09:09:49 | SA16 | Urban | Asset failure | LV | 5 | 269 | 0.0021502 | 7.99e-06 | No
3/03/2019 | 09:21:52 | MV53 | Rural Short | Unknown | Unknown | 1 | 172 | 0.0012814 | 7.45e-06 | No
3/03/2019 | 11:24:40 | MI26 | Rural Long | Asset failure | HV | 28 | 301.3571 | 0.061583 | 0.00020435 | No
3/03/2019 | 13:38:08 | CM04 | Rural Long | Animal | Animal impact | 23 | 126 | 0.021151 | 0.00016786 | No
3/03/2019 | 13:52:09 | EL08G | Urban | Asset failure | LV | 1 | 64 | 0.00010232 | 1.6e-06 | No
3/03/2019 | 14:16:50 | SM216D | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | No
3/03/2019 | 17:17:28 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 243 | 0.0018104 | 7.45e-06 | No
3/03/2019 | 18:44:13 | SM349E | Urban | Asset failure | LV | 1 | 106 | 0.00016946 | 1.6e-06 | No
3/03/2019 | 19:22:36 | NL544B | Urban | Third Party | Other | 1735 | 55 | 0.15255 | 0.0027737 | No
3/03/2019 | 22:41:49 | HH177B | Urban | Asset failure | LV | 1 | 191 | 0.00030535 | 1.6e-06 | No
3/03/2019 | 23:16:46 | CBD412K | CBD | Planned |  | 1 | 31 | 0.0060177 | 0.00019412 | No
3/03/2019 | 23:16:46 | CBD412K | CBD | Planned |  | 0 | 13 | 0.0025235 | 0 | No
4/03/2019 | 02:46:05 | SD34200 | Rural Short | Weather |  | 446 | 248.3543 | 0.82522 | 0.0033228 | No
4/03/2019 | 03:07:32 | SA13 | Urban | Weather |  | 47 | 102 | 0.0076641 | 7.514e-05 | No
4/03/2019 | 03:26:16 | GU41 | Rural Long | Weather |  | 10 | 395 | 0.028828 | 7.298e-05 | No
4/03/2019 | 03:54:30 | GU11 | Rural Long | Unknown | Unknown | 21 | 236 | 0.036171 | 0.00015327 | No
4/03/2019 | 03:55:33 | SD38200 | Rural Long | Weather |  | 16 | 123 | 0.014363 | 0.00011677 | No
4/03/2019 | 03:56:01 | M91 | Rural Long | Unknown | Unknown | 36 | 202 | 0.053074 | 0.00026274 | No
4/03/2019 | 04:07:22 | GU35 | Rural Long | Unknown | Unknown | 102 | 271.0588 | 0.20178 | 0.00074443 | No
4/03/2019 | 04:16:06 | R04 | Rural Long | Weather |  | 38 | 431 | 0.11953 | 0.00027734 | No
4/03/2019 | 04:17:08 | NU22 | Rural Long | Weather |  | 19.3333 | 218 | 0.03076 | 0.0001411 | No
4/03/2019 | 04:27:46 | R14 | Rural Long | Weather |  | 291 | 221.3814 | 0.47017 | 0.0021238 | No
4/03/2019 | 04:29:14 | GU41 | Rural Long | Weather |  | 7.3333 | 517 | 0.02767 | 5.352e-05 | No
4/03/2019 | 04:40:57 | NU14 | Rural Long | Weather |  | 2 | 107 | 0.0015618 | 1.46e-05 | No
4/03/2019 | 04:45:34 | GU36 | Rural Long | Weather |  | 57 | 646.5439 | 0.26897 | 0.00041601 | No
4/03/2019 | 05:04:38 | M01 | Rural Long | Weather |  | 92 | 344.1304 | 0.23107 | 0.00067145 | No
4/03/2019 | 05:10:59 | CL09 | Rural Long | Unknown | Unknown | 166 | 437 | 0.52944 | 0.0012115 | No
4/03/2019 | 06:10:07 | CL05 | Rural Long | Weather |  | 469 | 189.8955 | 0.65 | 0.0034229 | No
4/03/2019 | 06:28:08 | CL09 | Rural Long | Weather |  | 1 | 428 | 0.0031237 | 7.3e-06 | No
4/03/2019 | 06:51:03 | CL27 | Rural Long | Unknown | Unknown | 32 | 238 | 0.055584 | 0.00023355 | No
4/03/2019 | 07:00:03 | BU05 | Rural Long | Weather |  | 86 | 311.5698 | 0.19556 | 0.00062766 | No
4/03/2019 | 07:00:56 | R17 | Rural Long | Weather |  | 73 | 474.7534 | 0.25294 | 0.00053278 | No
4/03/2019 | 07:17:07 | MG06 | Rural Short | Unknown | Unknown | 29 | 120 | 0.025927 | 0.00021605 | No
4/03/2019 | 07:27:14 | GA22 | Rural Short | Planned |  | 1 | 40 | 0.00029801 | 7.45e-06 | No
4/03/2019 | 07:51:21 | KA18 | Rural Long | Unknown | Unknown | 23 | 374 | 0.06278 | 0.00016786 | No
4/03/2019 | 08:04:19 | ST12 | Rural Short | Planned |  | 60 | 414 | 0.18506 | 0.00044701 | No
4/03/2019 | 08:20:12 | ME347G | Urban | Asset failure | LV | 31 | 109 | 0.0054019 | 4.956e-05 | No
4/03/2019 | 08:23:22 | HH341E | Urban | Overloads |  | 1 | 396 | 0.00063308 | 1.6e-06 | No
4/03/2019 | 08:39:39 | R11 | Rural Long | Weather |  | 82 | 294.9024 | 0.17649 | 0.00059846 | No
4/03/2019 | 08:58:55 | EL12 | Urban | Planned |  | 1 | 190 | 0.00030375 | 1.6e-06 | No
4/03/2019 | 09:04:55 | NL234A | Urban | Planned |  | 17 | 9 | 0.0002446 | 2.718e-05 | No
4/03/2019 | 09:08:07 | SD37102 | Rural Long | Asset failure | Subtransmission | 13 | 167 | 0.015845 | 9.488e-05 | No
4/03/2019 | 09:18:50 | HH145B | Urban | Unknown | Unknown | 90 | 157 | 0.022589 | 0.00014388 | No
4/03/2019 | 09:20:17 | SG11 | Rural Short | Planned |  | 6 | 172 | 0.0076885 | 4.47e-05 | No
4/03/2019 | 09:32:03 | HH409A | Urban | Third Party | Vehicle impact | 1 | 153 | 0.0002446 | 1.6e-06 | No
4/03/2019 | 09:36:36 | EL260A | Urban | Animal | Animal impact | 10.6667 | 194 | 0.0033082 | 1.705e-05 | No
4/03/2019 | 09:43:53 | HH121E | Urban | Planned |  | 61 | 187 | 0.018236 | 9.752e-05 | No
4/03/2019 | 09:58:11 | GA22 | Rural Short | Planned |  | 5 | 63 | 0.0023468 | 3.725e-05 | No
4/03/2019 | 10:16:52 | HH130A | Urban | Planned |  | 134 | 157 | 0.033633 | 0.00021422 | No
4/03/2019 | 10:22:12 | HH386B | Urban | Other |  | 1 | 158 | 0.00025259 | 1.6e-06 | No
4/03/2019 | 10:34:17 | SD38100 | Rural Long | Weather |  | 16 | 307.75 | 0.035937 | 0.00011677 | No
4/03/2019 | 10:34:55 | HH121E | Urban | Planned |  | 80 | 64 | 0.0081852 | 0.00012789 | No
4/03/2019 | 10:39:19 | BM21 | Rural Short | Asset failure | LV | 37 | 232 | 0.063952 | 0.00027566 | No
4/03/2019 | 11:09:16 | CL05 | Rural Long | Weather |  | 1 | 423 | 0.0030872 | 7.3e-06 | No
4/03/2019 | 11:32:56 | PA22 | Rural Long | Unknown | Unknown | 15 | 149 | 0.016312 | 0.00010948 | No
4/03/2019 | 11:34:53 | CL05 | Rural Long | Weather |  | 1 | 127 | 0.00092689 | 7.3e-06 | No
4/03/2019 | 12:13:32 | CN32 | Rural Long | Planned |  | 1 | 18 | 0.00013137 | 7.3e-06 | No
4/03/2019 | 12:16:09 | MI20 | Rural Long | Overloads |  | 1 | 140 | 0.0010218 | 7.3e-06 | No
4/03/2019 | 12:59:43 | CL09 | Rural Long | Weather |  | 8.3333 | 83 | 0.005048 | 6.082e-05 | No
4/03/2019 | 13:20:48 | BM13 | Rural Short | Weather |  | 10 | 110 | 0.0081952 | 7.45e-05 | No
4/03/2019 | 14:00:42 | SM374A | Urban | Planned |  | 76 | 16 | 0.001944 | 0.0001215 | No
4/03/2019 | 14:46:45 | AP149B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 56 | 388 | 0.034736 | 8.953e-05 | No
4/03/2019 | 15:26:38 | GA43 | Rural Short | Other |  | 1 | 150 | 0.0011175 | 7.45e-06 | No
4/03/2019 | 16:24:11 | MTB51 | Rural Long | Asset failure | LV | 1 | 221 | 0.0016129 | 7.3e-06 | No
4/03/2019 | 16:40:57 | PA22 | Rural Long | Unknown | Unknown | 12 | 194 | 0.016991 | 8.758e-05 | No
4/03/2019 | 16:52:23 | HH403A | Urban | Asset failure | LV | 83 | 60 | 0.0079614 | 0.00013269 | No
4/03/2019 | 16:58:59 | LX73 | Rural Long | Weather |  | 8 | 334 | 0.019501 | 5.839e-05 | No
4/03/2019 | 17:11:49 | NL544B | Urban | Asset failure | LV | 2 | 225 | 0.0007194 | 3.2e-06 | No
4/03/2019 | 17:19:54 | R17 | Rural Long | Unknown | Unknown | 1 | 37 | 0.00027004 | 7.3e-06 | No
4/03/2019 | 18:05:09 | R14 | Rural Long | Asset failure | Distribution substation | 2 | 499 | 0.0072837 | 1.46e-05 | No
4/03/2019 | 18:05:09 | R14 | Rural Long | Asset failure | Distribution substation | 1 | 112 | 0.00081741 | 7.3e-06 | No
4/03/2019 | 18:14:45 | LX31 | Rural Short | Weather |  | 65.3333 | 568.6327 | 0.27678 | 0.00048674 | No
4/03/2019 | 18:20:41 | LX73 | Rural Long | Weather |  | 13 | 205 | 0.01945 | 9.488e-05 | No
4/03/2019 | 18:34:45 | SM349C | Urban | Third Party | Vehicle impact | 1977 | 206.0116 | 0.65112 | 0.0031606 | No
4/03/2019 | 18:34:45 | SM349C | Urban | Third Party | Vehicle impact | 0 | 5 | 0.0016466 | 0 | No
4/03/2019 | 18:35:38 | W28 | Rural Long | Unknown | Unknown | 16 | 949 | 0.11082 | 0.00011677 | No
4/03/2019 | 19:24:18 | HH432B | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
4/03/2019 | 20:02:28 | SD57100 | Rural Long | Unknown | Unknown | 1 | 156 | 0.0011385 | 7.3e-06 | No
4/03/2019 | 20:36:56 | GU21 | Rural Long | Unknown | Unknown | 12.3333 | 135 | 0.012152 | 9.001e-05 | No
4/03/2019 | 21:57:55 | NL544B | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
5/03/2019 | 07:40:22 | KI56 | Rural Long | Planned |  | 112 | 368 | 0.30081 | 0.00081741 | No
5/03/2019 | 07:55:36 | GU32 | Rural Long | Unknown | Unknown | 1 | 298 | 0.0021749 | 7.3e-06 | No
5/03/2019 | 08:28:57 | CN25 | Rural Long | Planned |  | 59 | 332 | 0.14296 | 0.0004306 | No
5/03/2019 | 08:29:13 | SM216D | Urban | Planned |  | 1 | 370 | 0.00059151 | 1.6e-06 | No
5/03/2019 | 09:06:44 | AP529A | Urban | Planned |  | 98 | 274 | 0.042928 | 0.00015667 | No
5/03/2019 | 09:07:22 | AP425C | Urban | Asset failure | LV | 1 | 233 | 0.00037249 | 1.6e-06 | No
5/03/2019 | 09:15:08 | HH429A | Urban | Planned |  | 121 | 310 | 0.059966 | 0.00019344 | No
5/03/2019 | 09:17:25 | NL234C | Urban | Planned |  | 287 | 339 | 0.15554 | 0.00045882 | No
5/03/2019 | 09:25:41 | M61 | Rural Long | Planned |  | 198 | 268 | 0.38728 | 0.0014451 | No
5/03/2019 | 09:49:22 | SM350C | Urban | Overloads |  | 1 | 410 | 0.00065546 | 1.6e-06 | No
5/03/2019 | 09:55:39 | EL13 | Urban | Animal | Animal impact | 2510 | 42.0653 | 0.16879 | 0.0040127 | No
5/03/2019 | 10:19:46 | AP132D | Urban | Planned |  | 4 | 102 | 0.00065226 | 6.39e-06 | No
5/03/2019 | 10:38:56 | SM216B | Urban | Planned |  | 214 | 249 | 0.085187 | 0.00034212 | No
5/03/2019 | 10:42:05 | MG52 | Rural Short | Third Party | Vehicle impact | 1762 | 210.9376 | 2.769 | 0.013127 | No
5/03/2019 | 10:44:06 | BT27 | Rural Long | Planned |  | 2 | 70 | 0.0010218 | 1.46e-05 | No
5/03/2019 | 10:50:26 | HH121B | Urban | Planned |  | 85 | 43 | 0.0058432 | 0.00013589 | No
5/03/2019 | 10:52:03 | CN77 | Rural Long | Planned |  | 3 | 83.6667 | 0.0018319 | 2.19e-05 | No
5/03/2019 | 11:00:03 | EL20 | Urban | Planned |  | 35 | 128 | 0.0071621 | 5.595e-05 | No
5/03/2019 | 11:12:47 | MI23 | Rural Long | Asset failure | HV | 93 | 141.8602 | 0.096287 | 0.00067875 | No
5/03/2019 | 12:10:03 | HH121C | Urban | Planned |  | 110 | 37 | 0.0065066 | 0.00017585 | No
5/03/2019 | 12:58:08 | NL210B | Urban | Unknown | Unknown | 935 | 1 | 0.0014948 | 0.0014948 | No
5/03/2019 | 12:59:28 | SM216C | Urban | Planned |  | 1 | 100 | 0.00015987 | 1.6e-06 | No
5/03/2019 | 13:20:58 | CN71 | Rural Long | Planned |  | 232 | 145 | 0.24552 | 0.0016932 | No
5/03/2019 | 13:30:35 | YK16 | Rural Long | Asset failure | HV | 1 | 15 | 0.00010948 | 7.3e-06 | No
5/03/2019 | 14:33:17 | CN02 | Rural Long | Weather |  | 13 | 67 | 0.0063568 | 9.488e-05 | No
5/03/2019 | 15:21:16 | HH429A | Urban | Unknown | Unknown | 3.3333 | 131 | 0.00069809 | 5.33e-06 | No
5/03/2019 | 15:26:12 | CL09 | Rural Long | Unknown | Unknown | 2.6667 | 202 | 0.0039314 | 1.946e-05 | No
5/03/2019 | 16:06:21 | G23 | Rural Long | Unknown | Unknown | 107 | 416.271 | 0.32508 | 0.00078092 | No
5/03/2019 | 17:13:10 | HH429A | Urban | Unknown | Unknown | 2 | 26 | 8.313e-05 | 3.2e-06 | No
5/03/2019 | 18:00:54 | MG52 | Rural Short | Overloads |  | 1762 | 6.6084 | 0.08675 | 0.013127 | No
5/03/2019 | 18:11:14 | WK42 | Rural Short | Asset failure | LV | 1 | 93 | 0.00069286 | 7.45e-06 | No
5/03/2019 | 18:14:07 | CM03 | Rural Long | Unknown | Unknown | 646 | 163 | 0.7685 | 0.0047147 | No
5/03/2019 | 18:19:50 | BT06 | Rural Long | Asset failure | LV | 1 | 53 | 0.00038681 | 7.3e-06 | No
5/03/2019 | 20:02:14 | GU36 | Rural Long | Weather |  | 57 | 522.3158 | 0.21729 | 0.00041601 | No
5/03/2019 | 20:02:14 | GU36 | Rural Long | Weather |  | 0 | 244.5862 | 0.10353 | 0 | No
5/03/2019 | 21:40:42 | MB12 | Rural Short | Asset failure | LV | 1 | 85 | 0.00063326 | 7.45e-06 | No
5/03/2019 | 22:12:31 | BT37 | Rural Long | Unknown | Unknown | 1 | 15 | 0.00010948 | 7.3e-06 | No
5/03/2019 | 22:37:38 | NL21 | Urban | Animal | Animal impact | 608 | 87 | 0.084564 | 0.00097199 | No
5/03/2019 | 22:37:38 | MV22 | Rural Short | Animal | Animal impact | 402 | 74 | 0.22163 | 0.002995 | No
5/03/2019 | 23:19:48 | NL234A | Urban | Asset failure | LV | 19.3333 | 131 | 0.0040489 | 3.091e-05 | No
5/03/2019 | 23:57:29 | SD37101 | Rural Long | Asset failure | Subtransmission | 72 | 395.5556 | 0.20786 | 0.00052548 | No
5/03/2019 | 23:57:29 | SD37101 | Rural Long | Asset failure | Subtransmission | 0 | 1 | 0.00027734 | 0 | No
6/03/2019 | 08:10:42 | CN81 | Rural Long | Planned |  | 104 | 514.8462 | 0.39078 | 0.00075903 | No
6/03/2019 | 08:17:51 | AP365E | Urban | Planned |  | 13 | 382 | 0.007939 | 2.078e-05 | No
6/03/2019 | 08:29:16 | ST44 | Rural Long | Planned |  | 10 | 292 | 0.021311 | 7.298e-05 | No
6/03/2019 | 08:47:05 | MV34 | Rural Short | Planned |  | 38 | 3 | 0.00084932 | 0.00028311 | No
6/03/2019 | 08:56:48 | HH409D | Urban | Planned |  | 1 | 343 | 0.00054835 | 1.6e-06 | No
6/03/2019 | 09:14:39 | GA21 | Rural Long | Planned |  | 44 | 198 | 0.063583 | 0.00032113 | No
6/03/2019 | 09:25:57 | AP139B | Urban | Planned |  | 100 | 94 | 0.015028 | 0.00015987 | No
6/03/2019 | 09:33:49 | ME427E | Urban | Planned |  | 68 | 125 | 0.013589 | 0.00010871 | No
6/03/2019 | 09:50:19 | CD17 | Rural Long | Planned |  | 6 | 415 | 0.018173 | 4.379e-05 | No
6/03/2019 | 10:04:09 | SM126D | Urban | Planned |  | 28 | 140 | 0.0062668 | 4.476e-05 | No
6/03/2019 | 10:15:59 | HH121E | Urban | Planned |  | 54 | 169 | 0.01459 | 8.633e-05 | No
6/03/2019 | 10:47:32 | BT02 | Rural Long | Planned |  | 12 | 254 | 0.022245 | 8.758e-05 | No
6/03/2019 | 10:57:25 | GA01 | Urban | Planned |  | 157 | 230 | 0.057728 | 0.00025099 | No
6/03/2019 | 11:00:20 | MB03 | Rural Long | Unknown | Unknown | 1 | 74 | 0.00054008 | 7.3e-06 | No
6/03/2019 | 11:02:23 | SSD397 | Urban | Planned |  | 5 | 214 | 0.0017106 | 7.99e-06 | No
6/03/2019 | 11:14:05 | HH130A | Urban | Planned |  | 131 | 197 | 0.041257 | 0.00020943 | No
6/03/2019 | 11:46:48 | AP355F | Urban | Overloads |  | 1 | 235 | 0.00037569 | 1.6e-06 | No
6/03/2019 | 13:06:42 | HH107C | Urban | Other |  | 1 | 89 | 0.00014228 | 1.6e-06 | No
6/03/2019 | 14:38:01 | YK16 | Rural Long | Animal | Animal impact | 2 | 31 | 0.0004525 | 1.46e-05 | No
6/03/2019 | 14:46:24 | YK16 | Rural Long | Unknown | Unknown | 1 | 20 | 0.00014597 | 7.3e-06 | No
6/03/2019 | 15:20:47 | BM56 | Rural Short | Asset failure | LV | 1 | 1057 | 0.0078748 | 7.45e-06 | No
6/03/2019 | 15:58:03 | ME347B | Urban | Other |  | 1 | 195 | 0.00031174 | 1.6e-06 | No
6/03/2019 | 16:19:44 | SA33 | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
6/03/2019 | 20:05:36 | AP424A | Urban | Asset failure | LV | 1 | 138 | 0.00022062 | 1.6e-06 | No
7/03/2019 | 03:45:55 | AP425D | Urban | Asset failure | HV | 1852 | 151.7559 | 0.44931 | 0.0029607 | No
7/03/2019 | 06:45:23 | SM410B | Urban | Planned |  | 106 | 308 | 0.052194 | 0.00016946 | No
7/03/2019 | 07:48:57 | NL234D | Urban | Other |  | 1 | 146 | 0.00023341 | 1.6e-06 | No
7/03/2019 | 07:56:28 | SA20 | Urban | Asset failure | LV | 2.3333 | 219 | 0.00081692 | 3.73e-06 | No
7/03/2019 | 08:35:44 | MV52 | Rural Short | Planned |  | 4 | 308 | 0.0091786 | 2.98e-05 | No
7/03/2019 | 08:44:24 | KI42 | Rural Long | Planned |  | 2 | 142 | 0.0020727 | 1.46e-05 | No
7/03/2019 | 09:07:57 | GA28 | Rural Long | Planned |  | 204 | 367 | 0.54641 | 0.0014889 | No
7/03/2019 | 09:11:40 | SD37501 | Rural Short | Planned |  | 1 | 382 | 0.002846 | 7.45e-06 | No
7/03/2019 | 09:18:32 | MTB32 | Rural Long | Planned |  | 6 | 304 | 0.013312 | 4.379e-05 | No
7/03/2019 | 09:20:11 | CV02 | Rural Long | Planned |  | 42 | 84.2857 | 0.025836 | 0.00030653 | No
7/03/2019 | 09:21:41 | ST35 | Rural Long | Planned |  | 97 | 285 | 0.20176 | 0.00070794 | No
7/03/2019 | 09:22:12 | ST41 | Rural Long | Planned |  | 2 | 140 | 0.0020435 | 1.46e-05 | No
7/03/2019 | 09:22:18 | EL12 | Urban | Planned |  | 95 | 347 | 0.0527 | 0.00015187 | No
7/03/2019 | 09:28:31 | PA02 | Urban | Planned |  | 9 | 195 | 0.0028057 | 1.439e-05 | No
7/03/2019 | 09:29:19 | BM43 | Rural Short | Planned |  | 7 | 41 | 0.0021382 | 5.215e-05 | No
7/03/2019 | 09:30:04 | MB02 | Rural Long | Planned |  | 13 | 128 | 0.012144 | 9.488e-05 | No
7/03/2019 | 09:35:38 | VH19 | Rural Short | Planned |  | 8 | 172 | 0.010251 | 5.96e-05 | No
7/03/2019 | 09:46:21 | YK02 | Rural Short | Planned |  | 27 | 224 | 0.045059 | 0.00020115 | No
7/03/2019 | 10:06:11 | HH102B | Urban | Planned |  | 135 | 289 | 0.062372 | 0.00021582 | No
7/03/2019 | 10:20:04 | SD32301 | Rural Long | Planned |  | 3 | 186 | 0.0040725 | 2.19e-05 | No
7/03/2019 | 11:05:49 | MB03 | Rural Long | Overloads |  | 1 | 555 | 0.0040506 | 7.3e-06 | No
7/03/2019 | 11:20:19 | SM216E | Urban | Planned |  | 99 | 192 | 0.030388 | 0.00015827 | No
7/03/2019 | 11:45:53 | SM216B | Urban | Planned |  | 113 | 213 | 0.038479 | 0.00018065 | No
7/03/2019 | 12:27:43 | BT02 | Rural Long | Unknown | Unknown | 5.3333 | 234.625 | 0.0091327 | 3.892e-05 | No
7/03/2019 | 13:46:47 | MG04 | Rural Short | Asset failure | LV | 8 | 18 | 0.0010728 | 5.96e-05 | No
7/03/2019 | 14:34:28 | HH496F | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | No
7/03/2019 | 14:43:12 | AP424F | Urban | Planned |  | 198 | 14 | 0.0044315 | 0.00031654 | No
7/03/2019 | 18:16:32 | SM402E | Urban | Asset failure | LV | 1 | 71 | 0.00011351 | 1.6e-06 | No
7/03/2019 | 21:11:56 | CBD366J-GW1 | CBD | Asset failure | HV | 150 | 66.7467 | 1.9435 | 0.029118 | No
7/03/2019 | 21:11:56 | CBD366J-GW1 | Urban | Asset failure | HV | 68 | 245.6029 | 0.026699 | 0.00010871 | No
8/03/2019 | 08:34:25 | GA25 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 271 | 0.002019 | 7.45e-06 | No
8/03/2019 | 08:40:50 | SA17 | Urban | Planned |  | 53 | 104 | 0.0088119 | 8.473e-05 | No
8/03/2019 | 08:43:23 | VH16 | Rural Short | Planned |  | 4 | 316 | 0.009417 | 2.98e-05 | No
8/03/2019 | 08:49:00 | NL115D | Urban | Planned |  | 322 | 207 | 0.10656 | 0.00051477 | No
8/03/2019 | 09:00:00 | MB01 | Rural Long | Planned |  | 2 | 168 | 0.0024522 | 1.46e-05 | No
8/03/2019 | 09:05:13 | BM43 | Rural Short | Planned |  | 26 | 147 | 0.028474 | 0.0001937 | No
8/03/2019 | 09:05:30 | GU43 | Rural Long | Planned |  | 30 | 333 | 0.07291 | 0.00021895 | No
8/03/2019 | 09:10:31 | NL234C | Urban | Planned |  | 55 | 405 | 0.03561 | 8.793e-05 | No
8/03/2019 | 09:14:59 | PL14 | Urban | Planned |  | 4 | 300 | 0.0019184 | 6.39e-06 | No
8/03/2019 | 09:17:31 | NA24 | Rural Long | Planned |  | 1 | 319 | 0.0023282 | 7.3e-06 | No
8/03/2019 | 09:18:19 | GU11 | Rural Long | Planned |  | 21 | 163 | 0.024982 | 0.00015327 | No
8/03/2019 | 09:18:21 | AP149B | Urban | Planned |  | 35 | 174 | 0.0097359 | 5.595e-05 | No
8/03/2019 | 09:30:23 | CV33 | Rural Long | Planned |  | 4 | 216 | 0.0063058 | 2.919e-05 | No
8/03/2019 | 09:37:23 | R02 | Rural Long | Planned |  | 76 | 13.7368 | 0.0076195 | 0.00055467 | No
8/03/2019 | 09:44:13 | ST35 | Rural Long | Planned |  | 205 | 260 | 0.389 | 0.0014962 | No
8/03/2019 | 09:52:04 | AP529A | Urban | Planned |  | 301 | 140 | 0.067368 | 0.0004812 | No
8/03/2019 | 09:54:45 | PA02 | Urban | Planned |  | 131 | 81 | 0.016964 | 0.00020943 | No
8/03/2019 | 10:05:17 | GA49 | Rural Long | Planned |  | 59 | 193 | 0.083106 | 0.0004306 | No
8/03/2019 | 10:14:57 | HH130A | Urban | Planned |  | 86 | 140 | 0.019248 | 0.00013749 | No
8/03/2019 | 10:33:42 | SG14 | Rural Short | Planned |  | 34 | 56 | 0.014185 | 0.00025331 | No
8/03/2019 | 10:47:42 | GA27 | Rural Long | Planned |  | 4 | 71 | 0.0020727 | 2.919e-05 | No
8/03/2019 | 11:01:36 | EL19 | Urban | Third Party | Other | 2 | 37 | 0.0001183 | 3.2e-06 | No
8/03/2019 | 11:03:29 | HH102B | Urban | Planned |  | 59 | 62 | 0.005848 | 9.432e-05 | No
8/03/2019 | 11:04:06 | G04 | Rural Long | Planned |  | 7 | 221 | 0.011291 | 5.109e-05 | No
8/03/2019 | 11:11:46 | SSD132 | Urban | Asset failure | Zone substation | 2681 | 92.8243 | 0.39785 | 0.004286 | No
8/03/2019 | 11:28:06 | HH121E | Urban | Asset failure | LV | 1 | 471 | 0.00075298 | 1.6e-06 | No
8/03/2019 | 13:03:58 | PL08 | Urban | Planned |  | 5 | 66.8 | 0.00053396 | 7.99e-06 | No
8/03/2019 | 13:27:06 | SG14 | Rural Short | Planned |  | 29 | 52 | 0.011235 | 0.00021605 | No
8/03/2019 | 13:39:16 | CL04 | Rural Long | Unknown | Unknown | 1 | 97 | 0.00070794 | 7.3e-06 | No
8/03/2019 | 13:45:07 | CL09 | Rural Long | Unknown | Unknown | 2 | 55 | 0.00080282 | 1.46e-05 | No
8/03/2019 | 15:53:38 | AP132E | Urban | Unknown | Unknown | 1 | 161 | 0.00025739 | 1.6e-06 | No
8/03/2019 | 15:56:59 | SM137A | Urban | Unknown | Unknown | 16 | 76 | 0.001944 | 2.558e-05 | No
8/03/2019 | 17:40:55 | EL13 | Urban | Animal | Animal impact | 2504 | 76.7013 | 0.30704 | 0.0040031 | No
8/03/2019 | 18:49:10 | HH177E | Urban | Third Party | Vehicle impact | 16.3333 | 145 | 0.0037862 | 2.611e-05 | No
9/03/2019 | 00:36:04 | MB12 | Rural Short | Asset failure | LV | 1 | 94 | 0.00070031 | 7.45e-06 | No
9/03/2019 | 03:14:02 | HH432B | Urban | Animal | Animal impact | 42 | 76 | 0.005103 | 6.714e-05 | No
9/03/2019 | 03:15:28 | SM411C | Urban | Animal | Animal impact | 11 | 234 | 0.004115 | 1.759e-05 | No
9/03/2019 | 03:35:09 | HH386C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 39.3334 | 13 | 0.00081746 | 6.288e-05 | No
9/03/2019 | 05:46:21 | KI51 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 38 | 251.1316 | 0.069648 | 0.00027734 | No
9/03/2019 | 06:48:53 | KA10 | Rural Long | Asset failure | HV | 71 | 106 | 0.054927 | 0.00051818 | No
9/03/2019 | 08:57:14 | SA41 | Urban | Third Party | Other | 98 | 6.9592 | 0.0010903 | 0.00015667 | No
9/03/2019 | 09:55:13 | HH341H | Urban | Planned |  | 108 | 475 | 0.082012 | 0.00017266 | No
9/03/2019 | 09:59:20 | NA12 | Rural Long | Third Party | Vehicle impact | 81 | 121 | 0.071531 | 0.00059117 | No
9/03/2019 | 12:04:32 | AP365A | Urban | Asset failure | LV | 1 | 255 | 0.00040766 | 1.6e-06 | No
9/03/2019 | 13:30:58 | HH341H | Urban | Planned |  | 5 | 282 | 0.0022541 | 7.99e-06 | No
9/03/2019 | 14:39:22 | HH409D | Urban | Planned |  | 2484 | 1 | 0.0039711 | 0.0039711 | No
9/03/2019 | 15:09:57 | BM13 | Rural Short | Asset failure | LV | 11 | 204 | 0.016718 | 8.195e-05 | No
9/03/2019 | 21:19:57 | NA04 | Rural Long | Unknown | Unknown | 7.6667 | 220 | 0.01231 | 5.595e-05 | No
10/03/2019 | 08:40:44 | HH177C | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
10/03/2019 | 08:50:51 | EL01Y | Urban | Planned |  | 2 | 108 | 0.00034531 | 3.2e-06 | No
10/03/2019 | 09:12:38 | MT06 | Rural Long | Weather |  | 452 | 99.5796 | 0.3285 | 0.0032988 | No
10/03/2019 | 09:45:04 | MI14 | Rural Long | Weather |  | 696 | 83.0489 | 0.42186 | 0.0050796 | No
10/03/2019 | 10:11:22 | ME347B | Urban | Asset failure | LV | 1 | 164 | 0.00026218 | 1.6e-06 | No
10/03/2019 | 10:16:57 | KA06 | Rural Long | Overloads |  | 1 | 168 | 0.0012261 | 7.3e-06 | No
10/03/2019 | 12:11:53 | SG07 | Rural Short | Asset failure | LV | 1 | 190 | 0.0014155 | 7.45e-06 | No
10/03/2019 | 13:27:14 | SM216A | Urban | Overloads |  | 25.3333 | 360 | 0.01458 | 4.05e-05 | No
10/03/2019 | 13:59:25 | CM03 | Rural Long | Unknown | Unknown | 646 | 70 | 0.33003 | 0.0047147 | No
10/03/2019 | 14:02:18 | SA14 | Urban | Asset failure | HV | 1086 | 127.57 | 0.22148 | 0.0017362 | No
10/03/2019 | 19:20:26 | SA16 | Urban | Overloads |  | 1 | 398 | 0.00063627 | 1.6e-06 | No
10/03/2019 | 20:04:01 | SA744D | Urban | Asset failure | HV | 184 | 263 | 0.077363 | 0.00029416 | No
10/03/2019 | 20:04:01 | SA744D | Urban | Asset failure | HV | 186 | 7 | 0.0020815 | 0.00029735 | No
10/03/2019 | 21:45:27 | HH107D | Urban | Animal | Animal impact | 46 | 137 | 0.010075 | 7.354e-05 | No
11/03/2019 | 04:18:54 | SG13 | Rural Short | Animal | Animal impact | 41 | 294 | 0.089804 | 0.00030546 | No
11/03/2019 | 07:54:25 | MG06 | Rural Short | Unknown | Unknown | 29 | 64 | 0.013827 | 0.00021605 | No
11/03/2019 | 08:34:18 | G12 | Rural Long | Animal | Animal impact | 628 | 191 | 0.87542 | 0.0045834 | No
11/03/2019 | 11:29:45 | ST34 | Rural Long | Overloads |  | 1 | 150 | 0.0010948 | 7.3e-06 | No
11/03/2019 | 11:46:16 | PL07 | Urban | Unknown | Unknown | 1 | 31 | 4.956e-05 | 1.6e-06 | No
11/03/2019 | 13:17:14 | MV61 | Urban | Overloads |  | 1 | 201 | 0.00032133 | 1.6e-06 | No
11/03/2019 | 15:20:56 | GA25 | Rural Short | Asset failure | LV | 1 | 199 | 0.0014826 | 7.45e-06 | No
11/03/2019 | 17:07:22 | NL111C | Urban | Asset failure | LV | 11 | 45 | 0.00079134 | 1.759e-05 | No
11/03/2019 | 18:33:55 | SM410D | Urban | Overloads |  | 1 | 377 | 0.0006027 | 1.6e-06 | No
11/03/2019 | 20:42:00 | SG11 | Rural Short | Asset failure | LV | 1 | 182 | 0.0013559 | 7.45e-06 | No
11/03/2019 | 21:12:54 | SM402D | Urban | Unknown | Unknown | 1595 | 92.2063 | 0.23512 | 0.0025499 | No
11/03/2019 | 21:39:47 | MV14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 169 | 0.0025181 | 1.49e-05 | No
12/03/2019 | 01:19:56 | SM402D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1595 | 99.2063 | 0.25296 | 0.0025499 | No
12/03/2019 | 07:23:48 | HH341B | Urban | Vegetation | Grow-in - NSP responsibility | 15 | 155 | 0.0037169 | 2.398e-05 | No
12/03/2019 | 07:46:53 | SSD165 | Urban | Planned |  | 1 | 4149 | 0.0066329 | 1.6e-06 | No
12/03/2019 | 08:13:42 | KA29 | Rural Long | Asset failure | LV | 1 | 681 | 0.0049702 | 7.3e-06 | No
12/03/2019 | 08:36:01 | HH145C | Urban | Planned |  | 107 | 304 | 0.052002 | 0.00017106 | No
12/03/2019 | 08:52:07 | MV63 | Rural Short | Planned |  | 83 | 144 | 0.089044 | 0.00061836 | No
12/03/2019 | 09:00:06 | SG07 | Rural Short | Planned |  | 13 | 145 | 0.014044 | 9.685e-05 | No
12/03/2019 | 09:22:54 | GA24 | Rural Long | Planned |  | 101 | 215 | 0.15848 | 0.00073713 | No
12/03/2019 | 09:25:05 | ST41 | Rural Long | Planned |  | 17 | 114 | 0.014144 | 0.00012407 | No
12/03/2019 | 09:43:17 | MB25 | Rural Long | Asset failure | LV | 1 | 201 | 0.001467 | 7.3e-06 | No
12/03/2019 | 10:36:16 | HH121B | Urban | Planned |  | 246 | 154 | 0.060564 | 0.00039327 | No
12/03/2019 | 11:56:16 | GU43 | Rural Long | Third Party | Dig-in | 12 | 92 | 0.0080574 | 8.758e-05 | No
12/03/2019 | 12:09:32 | MB25 | Rural Long | Unknown | Unknown | 1 | 11 | 8.028e-05 | 7.3e-06 | No
12/03/2019 | 12:27:29 | HH121B | Urban | Planned |  | 7 | 75 | 0.0008393 | 1.119e-05 | No
12/03/2019 | 13:26:51 | HH121G | Urban | Planned |  | 2 | 49 | 0.00015667 | 3.2e-06 | No
12/03/2019 | 13:55:40 | BT06 | Rural Long | Unknown | Unknown | 1 | 8340 | 0.060868 | 7.3e-06 | No
12/03/2019 | 16:25:10 | CM01 | Rural Long | Third Party | Other | 534 | 74 | 0.2884 | 0.0038973 | No
12/03/2019 | 18:22:48 | BM56 | Rural Short | Planned |  | 762 | 1 | 0.005677 | 0.005677 | No
12/03/2019 | 20:07:38 | SM172F | Urban | Overloads |  | 1 | 200 | 0.00031974 | 1.6e-06 | No
13/03/2019 | 02:24:25 | AP139B | Urban | Animal | Animal impact | 2083 | 64 | 0.21312 | 0.00333 | No
13/03/2019 | 04:32:41 | SA42 | Urban | Other |  | 1 | 775 | 0.001239 | 1.6e-06 | No
13/03/2019 | 08:11:54 | ST21 | Rural Short | Planned |  | 555 | 407.7586 | 1.686 | 0.0041348 | No
13/03/2019 | 08:29:52 | MTB32 | Rural Long | Planned |  | 40 | 460 | 0.13429 | 0.00029193 | No
13/03/2019 | 08:31:31 | KA04 | Rural Long | Planned |  | 161 | 282.9814 | 0.33251 | 0.001175 | No
13/03/2019 | 08:46:04 | KI42 | Rural Long | Planned |  | 216 | 331 | 0.5218 | 0.0015764 | No
13/03/2019 | 09:00:59 | YK17 | Rural Long | Planned |  | 198 | 237 | 0.34248 | 0.0014451 | No
13/03/2019 | 09:17:56 | HH102B | Urban | Third Party | Vehicle impact | 1 | 234 | 0.00037409 | 1.6e-06 | No
13/03/2019 | 09:36:27 | HH429A | Urban | Planned |  | 217 | 174 | 0.060363 | 0.00034691 | No
13/03/2019 | 09:48:16 | MV34 | Rural Short | Planned |  | 61 | 190 | 0.086347 | 0.00045446 | No
13/03/2019 | 09:50:58 | CN42 | Rural Long | Planned |  | 2 | 132 | 0.0019268 | 1.46e-05 | No
13/03/2019 | 10:02:28 | MV14 | Rural Short | Planned |  | 69 | 199 | 0.1023 | 0.00051406 | No
13/03/2019 | 10:04:26 | BM56 | Rural Short | Planned |  | 7 | 75 | 0.0039113 | 5.215e-05 | No
13/03/2019 | 10:06:48 | ST41 | Rural Long | Planned |  | 10 | 167 | 0.012188 | 7.298e-05 | No
13/03/2019 | 10:25:33 | SM126E | Urban | Planned |  | 6 | 1658 | 0.015904 | 9.59e-06 | No
13/03/2019 | 10:35:42 | CM15 | Rural Long | Planned |  | 68 | 166 | 0.082384 | 0.00049629 | No
13/03/2019 | 11:10:42 | PP12 | Rural Long | Planned |  | 30 | 207 | 0.045323 | 0.00021895 | No
13/03/2019 | 12:00:19 | SM126E | Urban | Planned |  | 50 | 73 | 0.0058352 | 7.993e-05 | No
13/03/2019 | 12:13:30 | AP149E | Urban | Other |  | 16 | 28 | 0.00071621 | 2.558e-05 | No
13/03/2019 | 13:18:27 | GU11 | Rural Long | Unknown | Unknown | 2 | 94 | 0.0013721 | 1.46e-05 | No
13/03/2019 | 14:35:41 | NA21 | Rural Long | Third Party | Vehicle impact | 55 | 182.8727 | 0.073407 | 0.00040141 | No
13/03/2019 | 14:49:33 | MI14 | Rural Long | Asset failure | LV | 1 | 129 | 0.00094149 | 7.3e-06 | No
13/03/2019 | 17:27:41 | WK42 | Rural Short | Unknown | Unknown | 87 | 87 | 0.05639 | 0.00064816 | No
14/03/2019 | 03:13:00 | HH107D | Urban | Animal | Animal impact | 46 | 111 | 0.0081628 | 7.354e-05 | No
14/03/2019 | 08:20:37 | LX51 | Rural Short | Planned |  | 200 | 369 | 0.54982 | 0.00149 | No
14/03/2019 | 08:28:05 | ST12 | Rural Short | Planned |  | 56 | 398 | 0.16605 | 0.00041721 | No
14/03/2019 | 08:36:30 | MB63 | Rural Long | Asset failure | LV | 1 | 225 | 0.0016421 | 7.3e-06 | No
14/03/2019 | 08:53:58 | GA53 | Rural Short | Planned |  | 15 | 325.4667 | 0.036372 | 0.00011175 | No
14/03/2019 | 08:55:08 | SD56301 | Urban | Planned |  | 1 | 382 | 0.00061069 | 1.6e-06 | No
14/03/2019 | 09:05:08 | NL111C | Urban | Planned |  | 96 | 273 | 0.041898 | 0.00015347 | No
14/03/2019 | 09:11:58 | MTB32 | Rural Long | Planned |  | 18 | 188 | 0.024698 | 0.00013137 | No
14/03/2019 | 09:12:18 | SA711C | Urban | Asset failure | LV | 1 | 349 | 0.00055794 | 1.6e-06 | No
14/03/2019 | 09:16:59 | YK02 | Rural Short | Planned |  | 22 | 227 | 0.037206 | 0.0001639 | No
14/03/2019 | 09:22:05 | MTB12 | Rural Short | Asset failure | LV | 2 | 177 | 0.0026374 | 1.49e-05 | No
14/03/2019 | 09:25:13 | ST36 | Rural Long | Planned |  | 14 | 114 | 0.011648 | 0.00010218 | No
14/03/2019 | 09:30:33 | GU17 | Rural Long | Planned |  | 8 | 239 | 0.013954 | 5.839e-05 | No
14/03/2019 | 09:39:34 | PL07 | Urban | Planned |  | 15 | 305 | 0.0073139 | 2.398e-05 | No
14/03/2019 | 09:41:14 | VH36 | Rural Short | Planned |  | 10 | 280 | 0.02086 | 7.45e-05 | No
14/03/2019 | 09:44:25 | AP149E | Urban | Planned |  | 1 | 35 | 5.595e-05 | 1.6e-06 | No
14/03/2019 | 09:47:27 | CL23 | Rural Long | Planned |  | 121 | 291 | 0.25698 | 0.0008831 | No
14/03/2019 | 09:52:58 | PP04 | Rural Short | Planned |  | 91 | 301 | 0.20407 | 0.00067796 | No
14/03/2019 | 10:15:15 | HH121B | Urban | Planned |  | 86 | 153 | 0.021035 | 0.00013749 | No
14/03/2019 | 10:19:21 | MB01 | Rural Long | Planned |  | 2 | 117 | 0.0017078 | 1.46e-05 | No
14/03/2019 | 10:23:54 | BT15 | Rural Long | Asset failure | LV | 1 | 374 | 0.0027296 | 7.3e-06 | No
14/03/2019 | 10:48:44 | W17 | Rural Long | Planned |  | 15 | 243 | 0.026602 | 0.00010948 | No
14/03/2019 | 10:51:21 | SM350F | Urban | Planned |  | 45 | 1662 | 0.11956 | 7.194e-05 | No
14/03/2019 | 11:00:26 | HH386A | Urban | Planned |  | 58 | 218 | 0.020214 | 9.272e-05 | No
14/03/2019 | 11:26:53 | SM374E | Urban | Other |  | 26.6666 | 21 | 0.00089526 | 4.263e-05 | No
14/03/2019 | 11:30:46 | AP351C | Urban | Asset failure | LV | 1 | 79 | 0.0001263 | 1.6e-06 | No
14/03/2019 | 11:31:37 | AP351B | Urban | Asset failure | LV | 3 | 77 | 0.00036929 | 4.8e-06 | No
14/03/2019 | 12:27:17 | BT26 | Rural Long | Third Party | Vehicle impact | 66 | 105 | 0.050577 | 0.00048169 | No
14/03/2019 | 12:35:26 | AP227A | Urban | Asset failure | LV | 16.6667 | 124 | 0.0033039 | 2.664e-05 | No
14/03/2019 | 13:17:17 | ME427D | Urban | Asset failure | LV | 1 | 260 | 0.00041566 | 1.6e-06 | No
14/03/2019 | 14:30:58 | KA24 | Rural Long | Asset failure | HV | 2 | 29 | 0.0004233 | 1.46e-05 | No
14/03/2019 | 14:37:20 | M31 | Rural Long | Network business | Switching and protection error | 4 | 52 | 0.001518 | 2.919e-05 | No
14/03/2019 | 18:17:39 | BM34 | Rural Short | Third Party | Vehicle impact | 1 | 238 | 0.0017731 | 7.45e-06 | No
14/03/2019 | 23:30:37 | HH102D | Urban | Unknown | Unknown | 50 | 6 | 0.0004796 | 7.993e-05 | No
15/03/2019 | 06:54:41 | HH177F | Urban | Asset failure | LV | 1.6667 | 120 | 0.00031973 | 2.66e-06 | No
15/03/2019 | 08:48:00 | NL111P | Urban | Planned |  | 174 | 120 | 0.03338 | 0.00027817 | No
15/03/2019 | 08:49:18 | SB21 | Rural Long | Planned |  | 2 | 10 | 0.00014597 | 1.46e-05 | No
15/03/2019 | 08:55:45 | SD38200 | Rural Long | Planned |  | 5 | 194 | 0.0070794 | 3.649e-05 | No
15/03/2019 | 08:56:06 | MTB53 | Rural Long | Planned |  | 232 | 367.2759 | 0.62188 | 0.0016932 | No
15/03/2019 | 08:59:07 | NA13 | Rural Long | Unknown | Unknown | 26 | 460 | 0.087288 | 0.00018976 | No
15/03/2019 | 09:00:15 | R18 | Rural Long | Planned |  | 6 | 14 | 0.00061306 | 4.379e-05 | No
15/03/2019 | 09:04:55 | MTB11 | Rural Short | Planned |  | 177 | 390 | 0.51428 | 0.0013187 | No
15/03/2019 | 09:10:41 | MTB41 | Rural Short | Planned |  | 2 | 204 | 0.0030397 | 1.49e-05 | No
15/03/2019 | 09:15:20 | HH177E | Urban | Asset failure | LV | 2 | 291 | 0.00093043 | 3.2e-06 | No
15/03/2019 | 09:15:46 | SD56301 | Urban | Planned |  | 1 | 322 | 0.00051477 | 1.6e-06 | No
15/03/2019 | 09:16:37 | CL05 | Rural Long | Unknown | Unknown | 1 | 357 | 0.0026055 | 7.3e-06 | No
15/03/2019 | 09:20:58 | CV22 | Rural Long | Planned |  | 1 | 81 | 0.00059117 | 7.3e-06 | No
15/03/2019 | 09:23:07 | VH13 | Rural Short | Planned |  | 28 | 341 | 0.071134 | 0.0002086 | No
15/03/2019 | 09:25:46 | WK33 | Rural Short | Third Party | Vehicle impact | 2 | 220 | 0.0032781 | 1.49e-05 | No
15/03/2019 | 09:29:25 | MG14 | Rural Long | Planned |  | 1 | 132 | 0.00096338 | 7.3e-06 | No
15/03/2019 | 09:31:57 | AP139B | Urban | Asset failure | LV | 13.3333 | 108 | 0.0023021 | 2.132e-05 | No
15/03/2019 | 09:36:42 | BT07 | Rural Long | Planned |  | 1 | 38 | 0.00027734 | 7.3e-06 | No
15/03/2019 | 10:00:36 | MTB41 | Rural Short | Planned |  | 1 | 116 | 0.00086422 | 7.45e-06 | No
15/03/2019 | 10:12:48 | HH121D | Urban | Planned |  | 360 | 257.1583 | 0.148 | 0.00057552 | No
15/03/2019 | 10:14:03 | SA18 | Urban | Planned |  | 152 | 231 | 0.056133 | 0.000243 | No
15/03/2019 | 11:33:18 | SA711C | Urban | Third Party | Vehicle impact | 13.3333 | 172 | 0.0036663 | 2.132e-05 | No
15/03/2019 | 11:47:37 | HH496A | Urban | Planned |  | 157 | 44 | 0.011044 | 0.00025099 | No
15/03/2019 | 12:15:23 | HH177E | Urban | Planned |  | 43 | 30 | 0.0020623 | 6.874e-05 | No
15/03/2019 | 12:39:37 | KI31 | Rural Short | Unknown | Unknown | 66 | 116 | 0.057038 | 0.00049171 | No
15/03/2019 | 13:40:23 | CL05 | Rural Long | Unknown | Unknown | 2 | 7 | 0.00010218 | 1.46e-05 | No
15/03/2019 | 21:36:11 | AP146C | Urban | Asset failure | LV | 1 | 165 | 0.00026378 | 1.6e-06 | No
15/03/2019 | 23:25:37 | MV61 | Urban | Asset failure | LV | 40 | 177 | 0.011319 | 6.395e-05 | No
15/03/2019 | 23:33:07 | HH409E | Urban | Animal | Animal impact | 27 | 118 | 0.0050934 | 4.316e-05 | No
16/03/2019 | 00:45:06 | HH145B | Urban | Asset failure | HV | 393 | 131.173 | 0.082413 | 0.00062828 | No
16/03/2019 | 01:53:03 | HH121B | Urban | Unknown | Unknown | 798 | 129 | 0.16457 | 0.0012757 | No
16/03/2019 | 02:09:55 | HH409E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 168 | 0.00026858 | 1.6e-06 | No
16/03/2019 | 02:15:51 | HH409E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 164 | 0.00026218 | 1.6e-06 | No
16/03/2019 | 03:39:49 | HH409E | Urban | Overloads |  | 1.6667 | 81 | 0.00021582 | 2.66e-06 | No
16/03/2019 | 03:46:46 | HH102D | Urban | Unknown | Unknown | 1802 | 95.8047 | 0.276 | 0.0028808 | No
16/03/2019 | 08:17:32 | AP139B | Urban | Unknown | Unknown | 29 | 464 | 0.021512 | 4.636e-05 | No
16/03/2019 | 10:40:38 | NL115E | Urban | Asset failure | LV | 1 | 362 | 0.00057872 | 1.6e-06 | No
16/03/2019 | 11:21:42 | VH15 | Rural Short | Asset failure | LV | 31.6666 | 99 | 0.023356 | 0.00023592 | No
16/03/2019 | 11:28:41 | KA01 | Rural Short | Asset failure | LV | 35 | 144 | 0.037549 | 0.00026076 | No
16/03/2019 | 11:29:25 | MB23 | Rural Short | Planned |  | 28 | 1337 | 0.2789 | 0.0002086 | No
16/03/2019 | 12:59:46 | EL13 | Urban | Asset failure | LV | 8.6667 | 197 | 0.0027295 | 1.386e-05 | No
16/03/2019 | 14:10:01 | CM16 | Rural Long | Unknown | Unknown | 2 | 9 | 0.00013137 | 1.46e-05 | No
16/03/2019 | 16:09:43 | HH496A | Urban | Asset failure | LV | 1 | 277 | 0.00044283 | 1.6e-06 | No
16/03/2019 | 18:09:18 | EL18 | Urban | Asset failure | LV | 16.3333 | 174 | 0.0045434 | 2.611e-05 | No
16/03/2019 | 18:44:17 | EL07 | Urban | Asset failure | LV | 1 | 208 | 0.00033252 | 1.6e-06 | No
17/03/2019 | 00:08:45 | MTB11 | Rural Short | Third Party | Vehicle impact | 1 | 631 | 0.004701 | 7.45e-06 | No
17/03/2019 | 06:12:10 | KA06 | Rural Long | Asset failure | LV | 1 | 222 | 0.0016202 | 7.3e-06 | No
17/03/2019 | 07:10:23 | SSD338 | Rural Short | Planned |  | 6 | 215 | 0.0096107 | 4.47e-05 | No
17/03/2019 | 08:17:06 | SA520J | Urban | Planned |  | 75 | 41 | 0.0049159 | 0.0001199 | No
17/03/2019 | 09:10:00 | NU25 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 160 | 0.060722 | 0.00037951 | No
17/03/2019 | 09:18:31 | GA26 | Urban | Planned |  | 60 | 356 | 0.034148 | 9.592e-05 | No
17/03/2019 | 09:28:54 | ST12 | Rural Short | Planned |  | 221 | 281 | 0.46266 | 0.0016465 | No
17/03/2019 | 09:29:38 | AP372D | Urban | Planned |  | 93 | 312 | 0.046387 | 0.00014868 | No
17/03/2019 | 09:54:23 | HH177A | Urban | Planned |  | 34 | 234 | 0.012719 | 5.435e-05 | No
17/03/2019 | 12:04:31 | VH21 | Rural Short | Asset failure | LV | 10.3333 | 195 | 0.015012 | 7.698e-05 | No
17/03/2019 | 14:17:11 | NU21 | Rural Long | Third Party | Other | 2328 | 65.5606 | 1.1139 | 0.016991 | No
17/03/2019 | 15:31:39 | HH121C | Urban | Overloads |  | 1 | 173 | 0.00027657 | 1.6e-06 | No
17/03/2019 | 16:26:14 | NL21 | Urban | Asset failure | LV | 1 | 249 | 0.00039807 | 1.6e-06 | No
17/03/2019 | 16:43:37 | MT10 | Rural Long | Asset failure | LV | 15 | 168 | 0.018392 | 0.00010948 | No
18/03/2019 | 06:30:56 | GA22 | Rural Short | Unknown | Unknown | 8.3333 | 149 | 0.0092506 | 6.208e-05 | No
18/03/2019 | 06:52:06 | NL21 | Urban | Planned |  | 66 | 252.7273 | 0.026666 | 0.00010551 | No
18/03/2019 | 06:52:55 | SM349C | Urban | Animal | Animal impact | 9 | 105 | 0.0015107 | 1.439e-05 | No
18/03/2019 | 08:45:38 | MV62 | Rural Short | Planned |  | 1 | 22 | 0.0001639 | 7.45e-06 | No
18/03/2019 | 08:55:19 | VH22 | Rural Short | Planned |  | 1 | 20 | 0.000149 | 7.45e-06 | No
18/03/2019 | 09:07:38 | GA19 | Rural Long | Planned |  | 3 | 221 | 0.0048388 | 2.19e-05 | No
18/03/2019 | 09:20:56 | ST12 | Rural Short | Planned |  | 82 | 153 | 0.09347 | 0.00061091 | No
18/03/2019 | 09:43:45 | AP365E | Urban | Planned |  | 28 | 27 | 0.0012086 | 4.476e-05 | No
18/03/2019 | 09:45:59 | R01 | Rural Long | Planned |  | 12 | 334 | 0.029252 | 8.758e-05 | No
18/03/2019 | 10:10:11 | CL10 | Rural Long | Planned |  | 1 | 90 | 0.00065685 | 7.3e-06 | No
18/03/2019 | 10:30:52 | SD33100 | Rural Long | Planned |  | 3 | 105 | 0.002299 | 2.19e-05 | No
18/03/2019 | 10:38:42 | HH121A | Urban | Planned |  | 215 | 56 | 0.019248 | 0.00034372 | No
18/03/2019 | 10:40:34 | AP365F | Urban | Planned |  | 48 | 14 | 0.0010743 | 7.674e-05 | No
18/03/2019 | 10:48:22 | HH177C | Urban | Planned |  | 78 | 44 | 0.0054867 | 0.0001247 | No
18/03/2019 | 11:32:09 | PL14 | Urban | Asset failure | HV | 71.6667 | 61.493 | 0.0070454 | 0.00011457 | No
18/03/2019 | 11:50:55 | CD17 | Rural Long | Unknown | Unknown | 17 | 161 | 0.019976 | 0.00012407 | No
18/03/2019 | 11:52:30 | VH45 | Rural Short | Planned |  | 51 | 123 | 0.046735 | 0.00037996 | No
18/03/2019 | 11:53:59 | SM172C | Urban | Asset failure | LV | 50.6667 | 470 | 0.03807 | 8.1e-05 | No
18/03/2019 | 13:14:15 | AP425D | Urban | Asset failure | LV | 1 | 69 | 0.00011031 | 1.6e-06 | No
18/03/2019 | 13:14:15 | AP425D | Urban | Asset failure | LV | 1 | 70 | 0.00011191 | 1.6e-06 | No
18/03/2019 | 14:07:40 | AP425D | Urban | Other |  | 1 | 16 | 2.558e-05 | 1.6e-06 | No
18/03/2019 | 14:57:07 | VH12 | Rural Short | Asset failure | LV | 1 | 94 | 0.00070031 | 7.45e-06 | No
18/03/2019 | 15:26:30 | ST21 | Rural Short | Asset failure | LV | 1 | 172 | 0.0012814 | 7.45e-06 | No
18/03/2019 | 15:32:43 | CD15 | Rural Long | Unknown | Unknown | 32 | 119 | 0.027792 | 0.00023355 | No
18/03/2019 | 17:01:56 | MB02 | Rural Long | Unknown | Unknown | 99 | 177 | 0.12789 | 0.00072254 | No
18/03/2019 | 17:38:07 | ST11 | Rural Short | Asset failure | LV | 1 | 924 | 0.0068839 | 7.45e-06 | No
18/03/2019 | 17:46:07 | GA24 | Rural Long | Asset failure | Distribution substation | 103 | 535.8932 | 0.40285 | 0.00075173 | No
18/03/2019 | 19:18:03 | HH177C | Urban | Overloads |  | 1 | 182 | 0.00029096 | 1.6e-06 | No
18/03/2019 | 21:05:08 | AP226C | Urban | Asset failure | LV | 1.6667 | 317 | 0.00084463 | 2.66e-06 | No
19/03/2019 | 01:54:58 | HH121D | Urban | Unknown | Unknown | 3027 | 42.3191 | 0.20479 | 0.0048392 | No
19/03/2019 | 04:15:37 | HH341G | Urban | Animal | Animal impact | 121 | 253 | 0.04894 | 0.00019344 | No
19/03/2019 | 05:02:49 | PP12 | Rural Long | Unknown | Unknown | 77 | 292.0909 | 0.16415 | 0.00056197 | No
19/03/2019 | 08:49:36 | MV53 | Rural Short | Planned |  | 3 | 70 | 0.0015645 | 2.235e-05 | No
19/03/2019 | 08:53:53 | YK12 | Rural Long | Planned |  | 22 | 330 | 0.052986 | 0.00016056 | No
19/03/2019 | 09:00:14 | AP355C | Urban | Planned |  | 112 | 32 | 0.0057297 | 0.00017905 | No
19/03/2019 | 09:04:30 | CD03 | Rural Short | Planned |  | 1 | 46 | 0.00034271 | 7.45e-06 | No
19/03/2019 | 09:13:48 | AP355C | Urban | Planned |  | 30 | 192 | 0.0092084 | 4.796e-05 | No
19/03/2019 | 09:14:08 | BT02 | Rural Long | Planned |  | 8 | 325 | 0.018976 | 5.839e-05 | No
19/03/2019 | 09:16:53 | GA36 | Rural Long | Planned |  | 5 | 157 | 0.0057292 | 3.649e-05 | No
19/03/2019 | 09:26:28 | HH496D | Urban | Planned |  | 147 | 53.0408 | 0.012465 | 0.00023501 | No
19/03/2019 | 09:49:18 | NL115B | Urban | Planned |  | 274 | 318 | 0.1393 | 0.00043804 | No
19/03/2019 | 09:49:31 | MG43 | Rural Short | Planned |  | 99 | 122 | 0.089983 | 0.00073756 | No
19/03/2019 | 10:00:54 | ME200E | Urban | Planned |  | 74 | 144 | 0.017035 | 0.0001183 | No
19/03/2019 | 10:03:03 | HH107B | Urban | Planned |  | 46 | 19 | 0.0013972 | 7.354e-05 | No
19/03/2019 | 10:07:04 | ST11 | Rural Short | Planned |  | 159 | 69 | 0.081736 | 0.0011846 | No
19/03/2019 | 11:00:27 | CM10 | Rural Long | Planned |  | 1 | 82 | 0.00059846 | 7.3e-06 | No
19/03/2019 | 12:03:40 | HH386B | Urban | Asset failure | LV | 1 | 108 | 0.00017266 | 1.6e-06 | No
19/03/2019 | 13:35:35 | GA36 | Rural Long | Planned |  | 1 | 24 | 0.00017516 | 7.3e-06 | No
19/03/2019 | 16:28:09 | HH177B | Urban | Other |  | 2 | 301 | 0.0009624 | 3.2e-06 | No
19/03/2019 | 16:51:16 | PP10 | Urban | Third Party | Other | 1 | 117 | 0.00018704 | 1.6e-06 | No
19/03/2019 | 19:22:40 | ST35 | Rural Long | Unknown | Unknown | 44 | 183 | 0.058766 | 0.00032113 | No
19/03/2019 | 19:26:50 | ST35 | Rural Long | Unknown | Unknown | 1 | 167 | 0.0012188 | 7.3e-06 | No
20/03/2019 | 01:55:20 | AP214D | Urban | Asset failure | LV | 30 | 135 | 0.0064746 | 4.796e-05 | No
20/03/2019 | 04:45:43 | AP149E | Urban | Planned |  | 2034 | 2 | 0.0065034 | 0.0032517 | No
20/03/2019 | 08:25:37 | AP149E | Urban | Planned |  | 13 | 398 | 0.0082715 | 2.078e-05 | No
20/03/2019 | 08:28:43 | SD38100 | Rural Long | Planned |  | 1 | 364 | 0.0026566 | 7.3e-06 | No
20/03/2019 | 08:43:57 | MV14 | Rural Short | Planned |  | 45 | 328 | 0.10996 | 0.00033526 | No
20/03/2019 | 08:57:13 | MV15 | Rural Short | Planned |  | 1 | 366 | 0.0027268 | 7.45e-06 | No
20/03/2019 | 08:57:50 | SA711C | Urban | Planned |  | 287 | 180.6829 | 0.082901 | 0.00045882 | No
20/03/2019 | 09:05:36 | PL04 | Urban | Planned |  | 73 | 340 | 0.039679 | 0.0001167 | No
20/03/2019 | 09:06:03 | MB01 | Rural Long | Unknown | Unknown | 18 | 94 | 0.012349 | 0.00013137 | No
20/03/2019 | 09:11:27 | CL21 | Rural Long | Planned |  | 24 | 9 | 0.0015764 | 0.00017516 | No
20/03/2019 | 09:26:19 | HH432D | Urban | Planned |  | 67 | 12 | 0.0012853 | 0.00010711 | No
20/03/2019 | 09:28:00 | WK42 | Rural Short | Unknown | Unknown | 87 | 42 | 0.027223 | 0.00064816 | No
20/03/2019 | 09:29:09 | AP149E | Urban | Asset failure | LV | 1 | 81 | 0.00012949 | 1.6e-06 | No
20/03/2019 | 09:29:22 | CD03 | Rural Short | Planned |  | 2 | 27 | 0.00040231 | 1.49e-05 | No
20/03/2019 | 09:29:27 | GU41 | Rural Long | Planned |  | 7 | 23 | 0.001175 | 5.109e-05 | No
20/03/2019 | 09:35:11 | AP132D | Urban | Planned |  | 522 | 222 | 0.18526 | 0.00083451 | No
20/03/2019 | 09:35:16 | SM350E | Urban | Planned |  | 71 | 328 | 0.03723 | 0.00011351 | No
20/03/2019 | 09:37:29 | AP424E | Urban | Planned |  | 61 | 1 | 9.752e-05 | 9.752e-05 | No
20/03/2019 | 09:44:18 | YK17 | Rural Long | Planned |  | 149 | 270.7584 | 0.29444 | 0.0010875 | No
20/03/2019 | 09:59:36 | HH522C | Urban | Planned |  | 1 | 73 | 0.0001167 | 1.6e-06 | No
20/03/2019 | 10:06:06 | MB23 | Rural Short | Asset failure | LV | 1 | 317 | 0.0023617 | 7.45e-06 | No
20/03/2019 | 10:08:03 | SM350E | Urban | Planned |  | 450 | 235 | 0.16906 | 0.0007194 | No
20/03/2019 | 10:15:01 | AP424D | Urban | Planned |  | 171 | 280 | 0.076545 | 0.00027337 | No
20/03/2019 | 10:23:15 | HH522C | Urban | Planned |  | 181 | 149 | 0.043115 | 0.00028936 | No
20/03/2019 | 10:34:18 | ST11 | Rural Short | Planned |  | 74 | 254 | 0.14003 | 0.00055131 | No
20/03/2019 | 10:38:13 | MB51 | Rural Long | Planned |  | 1 | 116 | 0.00084661 | 7.3e-06 | No
20/03/2019 | 10:50:34 | ST11 | Rural Short | Planned |  | 2 | 266 | 0.0039635 | 1.49e-05 | No
20/03/2019 | 11:06:00 | HH121B | Urban | Asset failure | LV | 1 | 206 | 0.00032933 | 1.6e-06 | No
20/03/2019 | 11:12:36 | W27 | Rural Long | Unknown | Unknown | 2 | 104 | 0.001518 | 1.46e-05 | No
20/03/2019 | 12:07:15 | HH145B | Urban | Vegetation | Grow-in - NSP responsibility | 25 | 80 | 0.0031973 | 3.997e-05 | No
20/03/2019 | 13:31:53 | MV15 | Rural Short | Asset failure | LV | 2 | 66 | 0.00098342 | 1.49e-05 | No
20/03/2019 | 13:40:40 | CN25 | Rural Long | Unknown | Unknown | 35 | 123 | 0.031419 | 0.00025544 | No
20/03/2019 | 13:56:55 | KA03 | Rural Long | Planned |  | 91 | 39 | 0.025902 | 0.00066415 | No
20/03/2019 | 14:13:28 | HH522A | Urban | Asset failure | LV | 1 | 89 | 0.00014228 | 1.6e-06 | No
20/03/2019 | 15:30:51 | YK24 | Rural Long | Unknown | Unknown | 1 | 29 | 0.00021165 | 7.3e-06 | No
20/03/2019 | 16:10:52 | HH107A | Urban | Asset failure | LV | 1 | 276 | 0.00044123 | 1.6e-06 | No
20/03/2019 | 17:12:12 | NL111C | Urban | Unknown | Unknown | 83 | 204 | 0.027069 | 0.00013269 | No
20/03/2019 | 19:01:35 | HH177G | Urban | Other |  | 21.6666 | 54 | 0.0018705 | 3.464e-05 | No
21/03/2019 | 03:24:58 | AP132B | Urban | Unknown | Unknown | 64 | 11 | 0.0011255 | 0.00010232 | No
21/03/2019 | 08:03:03 | HH145B | Urban | Asset failure | LV | 82 | 79 | 0.010356 | 0.00013109 | No
21/03/2019 | 08:15:10 | LX51 | Rural Short | Planned |  | 41 | 213 | 0.065062 | 0.00030546 | No
21/03/2019 | 08:20:56 | GA33 | Rural Short | Planned |  | 14 | 201 | 0.020965 | 0.0001043 | No
21/03/2019 | 08:43:06 | MV14 | Rural Short | Planned |  | 159 | 117 | 0.1386 | 0.0011846 | No
21/03/2019 | 08:44:00 | EL14 | Urban | Planned |  | 73 | 37 | 0.004318 | 0.0001167 | No
21/03/2019 | 08:46:00 | MTB81 | Rural Short | Planned |  | 337 | 243 | 0.6101 | 0.0025107 | No
21/03/2019 | 09:06:18 | HK02 | Rural Long | Planned |  | 25 | 357 | 0.065138 | 0.00018246 | No
21/03/2019 | 09:11:43 | VH33 | Rural Short | Planned |  | 24 | 301 | 0.05382 | 0.0001788 | No
21/03/2019 | 09:18:05 | NL760B | Urban | Planned |  | 174 | 321 | 0.089292 | 0.00027817 | No
21/03/2019 | 09:18:49 | GU43 | Rural Long | Planned |  | 60 | 344.65 | 0.15092 | 0.0004379 | No
21/03/2019 | 09:23:28 | GA28 | Rural Long | Planned |  | 60 | 237 | 0.10378 | 0.0004379 | No
21/03/2019 | 09:25:19 | SM411C | Urban | Vegetation | Grow-in - NSP responsibility | 43.3333 | 131 | 0.0090751 | 6.928e-05 | No
21/03/2019 | 09:25:47 | MB26 | Rural Long | Unknown | Unknown | 1 | 12 | 8.758e-05 | 7.3e-06 | No
21/03/2019 | 09:30:29 | NL115B | Urban | Planned |  | 3 | 82 | 0.00039327 | 4.8e-06 | No
21/03/2019 | 09:32:42 | VH72 | Rural Short | Planned |  | 8 | 139 | 0.0082846 | 5.96e-05 | No
21/03/2019 | 09:33:09 | GU15 | Rural Long | Planned |  | 85 | 247 | 0.15323 | 0.00062036 | No
21/03/2019 | 09:35:15 | MT01 | Rural Long | Planned |  | 123 | 227.5203 | 0.20424 | 0.0008977 | No
21/03/2019 | 09:36:52 | VH34 | Rural Short | Planned |  | 32 | 180 | 0.042913 | 0.0002384 | No
21/03/2019 | 09:39:56 | SA14 | Urban | Planned |  | 86 | 157 | 0.021585 | 0.00013749 | No
21/03/2019 | 09:41:25 | GA745B | Rural Short | Planned |  | 48 | 267 | 0.095481 | 0.00035761 | No
21/03/2019 | 10:10:00 | AP424E | Urban | Planned |  | 248 | 328 | 0.13004 | 0.00039647 | No
21/03/2019 | 10:40:05 | CM20 | Rural Long | Planned |  | 1 | 229 | 0.0016713 | 7.3e-06 | No
21/03/2019 | 10:45:06 | SA520D | Urban | Asset failure | LV | 1 | 189 | 0.00030215 | 1.6e-06 | No
21/03/2019 | 10:50:29 | SM410B | Urban | Planned |  | 1 | 9 | 1.439e-05 | 1.6e-06 | No
21/03/2019 | 13:03:26 | BT37 | Rural Long | Unknown | Unknown | 3 | 9 | 0.00019706 | 2.19e-05 | No
21/03/2019 | 13:40:49 | NA12 | Rural Long | Asset failure | LV | 6 | 145 | 0.0063495 | 4.379e-05 | No
21/03/2019 | 14:49:37 | VH18 | Rural Short | Asset failure | HV | 2 | 29 | 0.00043211 | 1.49e-05 | No
21/03/2019 | 15:01:00 | CBD27A-NT1-CB4326 | CBD | Asset failure | HV | 2 | 124 | 0.048141 | 0.00038824 | No
21/03/2019 | 15:15:37 | YK18 | Rural Long | Unknown | Unknown | 3 | 18 | 0.00039411 | 2.19e-05 | No
21/03/2019 | 21:23:45 | SM172D | Urban | Asset failure | LV | 47 | 126 | 0.0094673 | 7.514e-05 | No
21/03/2019 | 21:25:37 | SM216C | Urban | Asset failure | LV | 61 | 110 | 0.010727 | 9.752e-05 | No
21/03/2019 | 22:26:00 | SA20 | Urban | Third Party | Vehicle impact | 54 | 217 | 0.018733 | 8.633e-05 | No
22/03/2019 | 00:00:54 | SM374B | Urban | Asset failure | LV | 98 | 49 | 0.0076768 | 0.00015667 | No
22/03/2019 | 07:07:30 | ST35 | Rural Long | Unknown | Unknown | 32 | 188 | 0.043907 | 0.00023355 | No
22/03/2019 | 08:00:20 | AP149E | Urban | Planned |  | 58 | 377 | 0.034957 | 9.272e-05 | No
22/03/2019 | 08:32:32 | SB01 | Rural Long | Planned |  | 1 | 12 | 8.758e-05 | 7.3e-06 | No
22/03/2019 | 08:41:19 | HH121C | Urban | Planned |  | 197 | 76.6802 | 0.02415 | 0.00031494 | No
22/03/2019 | 08:50:35 | KI53 | Rural Long | Unknown | Unknown | 2 | 99 | 0.0014451 | 1.46e-05 | No
22/03/2019 | 08:51:08 | LM11 | Rural Long | Asset failure | LV | 1 | 336 | 0.0024522 | 7.3e-06 | No
22/03/2019 | 08:58:00 | MV14 | Rural Short | Planned |  | 22 | 80 | 0.013112 | 0.0001639 | No
22/03/2019 | 09:06:51 | BT02 | Rural Long | Planned |  | 4 | 164 | 0.0047877 | 2.919e-05 | No
22/03/2019 | 09:08:57 | VH19 | Rural Short | Planned |  | 32 | 295 | 0.070329 | 0.0002384 | No
22/03/2019 | 09:12:20 | AP125D | Urban | Planned |  | 183 | 299 | 0.087475 | 0.00029256 | No
22/03/2019 | 09:13:29 | HH130E | Urban | Planned |  | 41 | 161 | 0.010553 | 6.555e-05 | No
22/03/2019 | 09:16:21 | EL02 | Urban | Planned |  | 180 | 201.9722 | 0.05812 | 0.00028776 | No
22/03/2019 | 09:17:50 | HH148B | Urban | Planned |  | 109 | 70 | 0.012198 | 0.00017426 | No
22/03/2019 | 09:21:37 | ME347C | Urban | Planned |  | 9 | 4 | 5.755e-05 | 1.439e-05 | No
22/03/2019 | 09:33:59 | CV757A | Rural Long | Planned |  | 1 | 46 | 0.00033572 | 7.3e-06 | No
22/03/2019 | 09:39:23 | ME347C | Urban | Planned |  | 3 | 237 | 0.0011367 | 4.8e-06 | No
22/03/2019 | 09:39:37 | MV62 | Rural Short | Planned |  | 324 | 190 | 0.45863 | 0.0024138 | No
22/03/2019 | 09:53:24 | GU43 | Rural Long | Planned |  | 26 | 296 | 0.056168 | 0.00018976 | No
22/03/2019 | 10:16:48 | HH121A / HH409D | Urban | Planned |  | 372 | 101.7016 | 0.060483 | 0.00059471 | No
22/03/2019 | 10:24:18 | MI32 | Rural Long | Planned |  | 55 | 121 | 0.04857 | 0.00040141 | No
22/03/2019 | 10:26:46 | BM12 | Rural Short | Planned |  | 8 | 115 | 0.0068541 | 5.96e-05 | No
22/03/2019 | 12:07:44 | BM34 | Rural Short | Unknown | Unknown | 81.6667 | 104 | 0.063277 | 0.00060843 | No
22/03/2019 | 12:30:18 | WK44 | Rural Short | Unknown | Unknown | 7 | 191 | 0.0099609 | 5.215e-05 | No
22/03/2019 | 12:49:40 | BM13 | Rural Short | Unknown | Unknown | 1 | 74 | 0.00055131 | 7.45e-06 | No
22/03/2019 | 14:07:59 | KA02 | Rural Short | Planned |  | 64 | 12 | 0.0057217 | 0.00047681 | No
22/03/2019 | 20:28:12 | HH403B | Urban | Asset failure | LV | 68 | 107 | 0.011632 | 0.00010871 | No
23/03/2019 | 00:28:07 | AP149D | Urban | Unknown | Unknown | 12.6667 | 167 | 0.0033817 | 2.025e-05 | No
23/03/2019 | 02:02:02 | SG10 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 118 | 0.00087912 | 7.45e-06 | No
23/03/2019 | 07:05:18 | HH130B | Urban | Asset failure | LV | 1 | 242 | 0.00038688 | 1.6e-06 | No
23/03/2019 | 07:09:45 | CM16 | Rural Long | Asset failure | HV | 30 | 100 | 0.021895 | 0.00021895 | No
23/03/2019 | 09:11:25 | NL210D | Urban | Asset failure | LV | 1 | 258 | 0.00041246 | 1.6e-06 | No
23/03/2019 | 13:04:23 | AP149D | Urban | Third Party | Vehicle impact | 24 | 322 | 0.012355 | 3.837e-05 | No
23/03/2019 | 13:05:40 | AP149D | Urban | Third Party | Vehicle impact | 99 | 307 | 0.048589 | 0.00015827 | No
23/03/2019 | 13:06:38 | NL234A | Urban | Asset failure | LV | 25.3333 | 16 | 0.000648 | 4.05e-05 | No
23/03/2019 | 13:07:34 | SG14 | Rural Short | Asset failure | LV | 1 | 224 | 0.0016688 | 7.45e-06 | No
23/03/2019 | 15:26:55 | PP08 | Rural Long | Weather |  | 210.3334 | 166.599 | 0.25574 | 0.0015351 | No
23/03/2019 | 17:10:31 | EL23 | Urban | Animal | Animal impact | 26 | 64 | 0.0026602 | 4.157e-05 | No
23/03/2019 | 20:46:17 | BM44 | Rural Short | Unknown | Unknown | 954 | 172.9748 | 1.2294 | 0.0071074 | No
24/03/2019 | 00:26:26 | MB123 | Rural Long | Asset failure | HV | 75 | 372.4533 | 0.20387 | 0.00054738 | No
24/03/2019 | 02:00:28 | BM57 | Rural Short | Asset failure | HV | 15 | 198 | 0.022127 | 0.00011175 | No
24/03/2019 | 02:54:20 | CN25 | Rural Long | Unknown | Unknown | 86 | 454 | 0.28496 | 0.00062766 | No
24/03/2019 | 05:16:16 | ST14 | Rural Short | Animal | Animal impact | 21 | 498.6667 | 0.078018 | 0.00015645 | No
24/03/2019 | 07:11:21 | HH522A | Urban | Planned |  | 27 | 71 | 0.0030647 | 4.316e-05 | No
24/03/2019 | 07:36:44 | AP373B | Urban | Planned |  | 10 | 352 | 0.0056273 | 1.599e-05 | No
24/03/2019 | 08:16:40 | ME427A | Urban | Planned |  | 8 | 384 | 0.0049111 | 1.279e-05 | No
24/03/2019 | 09:05:56 | AP373B | Urban | Planned |  | 2 | 192 | 0.00061389 | 3.2e-06 | No
24/03/2019 | 09:18:03 | SM126D | Urban | Planned |  | 82 | 228 | 0.029889 | 0.00013109 | No
24/03/2019 | 09:43:14 | HH409C | Urban | Planned |  | 59 | 68 | 0.0064139 | 9.432e-05 | No
24/03/2019 | 10:02:42 | HH409F | Urban | Planned |  | 8 | 57 | 0.000729 | 1.279e-05 | No
24/03/2019 | 10:15:59 | GA26 | Urban | Planned |  | 133 | 241 | 0.051242 | 0.00021262 | No
24/03/2019 | 10:41:14 | KA10 | Rural Long | Planned |  | 2 | 89 | 0.0012991 | 1.46e-05 | No
24/03/2019 | 11:20:42 | PA02 | Urban | Unknown | Unknown | 7.3333 | 136 | 0.0015944 | 1.172e-05 | No
24/03/2019 | 13:27:28 | MV32 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 106 | 82 | 0.064757 | 0.00078972 | No
24/03/2019 | 13:47:52 | CL27 | Rural Long | Asset failure | HV | 32 | 110 | 0.02569 | 0.00023355 | No
24/03/2019 | 15:19:24 | WK41 | Rural Short | Other |  | 1 | 218 | 0.0016241 | 7.45e-06 | No
24/03/2019 | 17:24:47 | NA09 | Rural Long | Asset failure | HV | 204 | 121 | 0.18015 | 0.0014889 | No
24/03/2019 | 18:18:32 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 65 | 0.00048426 | 7.45e-06 | No
24/03/2019 | 18:23:14 | MTB32 | Rural Long | Asset failure | HV | 62 | 794.2097 | 0.35938 | 0.0004525 | No
24/03/2019 | 18:23:14 | MTB32 | Rural Long | Asset failure | HV | 0 | 5 | 0.0019706 | 0 | No
24/03/2019 | 18:43:28 | KI42 | Rural Long | Unknown | Unknown | 184.3333 | 39 | 0.052468 | 0.0013453 | No
24/03/2019 | 18:49:34 | ST36 | Rural Long | Asset failure | HV | 38 | 1125 | 0.312 | 0.00027734 | No
24/03/2019 | 18:49:34 | ST15 | Rural Short | Asset failure | HV | 2 | 145 | 0.0021605 | 1.49e-05 | No
24/03/2019 | 18:49:34 | ST36 | Rural Long | Asset failure | HV | 132.3334 | 139.5995 | 0.13483 | 0.00096581 | No
24/03/2019 | 19:30:11 | MG19 | Rural Long | Asset failure | HV | 38 | 48 | 0.013312 | 0.00027734 | No
24/03/2019 | 19:46:06 | AP344D | Urban | Weather |  | 2343 | 158 | 0.59182 | 0.0037457 | No
24/03/2019 | 19:50:59 | AP372A | Urban | Third Party | Other | 463 | 84 | 0.062176 | 0.00074019 | No
24/03/2019 | 19:57:59 | MV32 | Rural Short | Asset failure | HV | 2 | 69 | 0.0010281 | 1.49e-05 | No
24/03/2019 | 20:32:19 | SG09 | Rural Short | 7 - STPIS Exclusion (3.3)(a) |  | 1 | 98 | 0.00073011 | 7.45e-06 | No
24/03/2019 | 20:54:44 | WK65 | Rural Short | Asset failure | LV | 1 | 249 | 0.0018551 | 7.45e-06 | No
24/03/2019 | 21:28:22 | W25 | Rural Long | Asset failure | HV | 9 | 957 | 0.062861 | 6.569e-05 | No
24/03/2019 | 21:28:22 | W25 | Rural Long | Asset failure | HV | 16 | 38 | 0.0044374 | 0.00011677 | No
24/03/2019 | 21:31:26 | MTB13 | Rural Short | Asset failure | HV | 3668 | 70.6031 | 1.9294 | 0.027327 | No
24/03/2019 | 21:32:08 | ST11 | Rural Short | Asset failure | HV | 201.3334 | 180.1788 | 0.27026 | 0.0015 | No
24/03/2019 | 21:58:24 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 113 | 0.0016837 | 1.49e-05 | No
24/03/2019 | 22:19:31 | HH341D | Urban | Animal | Animal impact | 62 | 86 | 0.0085241 | 9.912e-05 | No
24/03/2019 | 22:34:32 | HH409C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 99 | 176 | 0.027855 | 0.00015827 | No
24/03/2019 | 22:56:12 | SG09 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 20 | 148 | 0.022052 | 0.000149 | No
24/03/2019 | 23:21:35 | MV64 | Urban | Asset failure | LV | 19 | 106 | 0.0032197 | 3.037e-05 | No
25/03/2019 | 00:27:23 | AP424C | Urban | Asset failure | LV | 19.3333 | 92 | 0.0028435 | 3.091e-05 | No
25/03/2019 | 00:41:42 | CBD103C | Urban | Unknown | Unknown | 4.3333 | 169 | 0.0011708 | 6.93e-06 | No
25/03/2019 | 02:03:23 | CD23 | Rural Long | Asset failure | HV | 37 | 876.1081 | 0.23658 | 0.00027004 | No
25/03/2019 | 02:31:26 | YK17 | Rural Long | Unknown | Unknown | 1 | 380 | 0.0027734 | 7.3e-06 | No
25/03/2019 | 02:44:43 | AP529E | Urban | Weather |  | 1 | 85 | 0.00013589 | 1.6e-06 | No
25/03/2019 | 02:52:30 | AP529A | Urban | Asset failure | LV | 34.3333 | 57 | 0.0031286 | 5.489e-05 | No
25/03/2019 | 04:38:39 | MTB14 | Rural Short | 7 - STPIS Exclusion (3.3)(a) |  | 1 | 25 | 0.00018625 | 7.45e-06 | No
25/03/2019 | 04:42:01 | GA26 | Urban | Asset failure | LV | 1 | 225 | 0.0003597 | 1.6e-06 | No
25/03/2019 | 05:11:54 | GA26 | Urban | Asset failure | LV | 6.6667 | 194 | 0.0020676 | 1.066e-05 | No
25/03/2019 | 06:00:20 | MTB14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 678 | 0.0050512 | 7.45e-06 | No
25/03/2019 | 06:01:34 | SG09 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 772 | 0.0057515 | 7.45e-06 | No
25/03/2019 | 07:40:52 | MI08 | Rural Long | Asset failure | LV | 1 | 463 | 0.0033791 | 7.3e-06 | No
25/03/2019 | 07:50:42 | MTB71 | Rural Short | Unknown | Unknown | 205 | 169 | 0.25811 | 0.0015273 | No
25/03/2019 | 07:56:44 | MG32 | Rural Long | Unknown | Unknown | 1 | 124 | 0.00090499 | 7.3e-06 | No
25/03/2019 | 08:08:02 | HH177E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 75 | 40 | 0.004796 | 0.0001199 | No
25/03/2019 | 08:13:13 | ST23 | Rural Short | Planned |  | 183 | 299 | 0.40765 | 0.0013634 | No
25/03/2019 | 08:30:31 | MV53 | Rural Short | Planned |  | 196 | 269.4643 | 0.39348 | 0.0014602 | No
25/03/2019 | 08:53:10 | NA09 | Rural Long | Planned |  | 8 | 417 | 0.024347 | 5.839e-05 | No
25/03/2019 | 09:05:55 | SG11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 564 | 0.012606 | 2.235e-05 | No
25/03/2019 | 09:09:12 | HH118C | Urban | Vegetation | Grow-in - NSP responsibility | 6 | 320 | 0.0030695 | 9.59e-06 | No
25/03/2019 | 09:10:46 | BM21 | Rural Short | Asset failure | LV | 1 | 135 | 0.0010058 | 7.45e-06 | No
25/03/2019 | 09:33:24 | SM350F | Urban | Vegetation | Grow-in - NSP responsibility | 78 | 232 | 0.02893 | 0.0001247 | No
25/03/2019 | 09:35:58 | HH496C | Urban | Planned |  | 140 | 4 | 0.00089526 | 0.00022381 | No
25/03/2019 | 09:54:37 | HH409B | Urban | Unknown | Unknown | 926 | 23.7732 | 0.035193 | 0.0014804 | No
25/03/2019 | 10:01:55 | MV42 | Rural Short | Planned |  | 151 | 415 | 0.46686 | 0.001125 | No
25/03/2019 | 10:02:59 | CM03 | Rural Long | Asset failure | HV | 6 | 132.6667 | 0.0058095 | 4.379e-05 | No
25/03/2019 | 10:11:11 | KA03 | Rural Long | Asset failure | HV | 1099 | 27 | 0.21656 | 0.0080209 | No
25/03/2019 | 10:13:18 | MB32 | Rural Long | Unknown | Unknown | 9 | 196.7778 | 0.012925 | 6.569e-05 | No
25/03/2019 | 10:15:12 | SD38200 | Rural Long | Planned |  | 16 | 225 | 0.026274 | 0.00011677 | No
25/03/2019 | 10:17:04 | SM350A | Urban | Weather |  | 1704 | 81.2793 | 0.22142 | 0.0027241 | No
25/03/2019 | 10:21:10 | G18 | Rural Long | Planned |  | 77 | 307 | 0.17253 | 0.00056197 | No
25/03/2019 | 10:39:09 | HH148D | Urban | Asset failure | LV | 9 | 135 | 0.0019424 | 1.439e-05 | No
25/03/2019 | 11:28:09 | SD54102 | Rural Long | Unknown | Unknown | 37 | 23 | 0.0062109 | 0.00027004 | No
25/03/2019 | 11:59:35 | HH403B | Urban | Planned |  | 44 | 20 | 0.0014068 | 7.034e-05 | No
25/03/2019 | 12:01:51 | SM216A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 354 | 0.00056593 | 1.6e-06 | No
25/03/2019 | 12:29:37 | SA17 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 36 | 130 | 0.0074818 | 5.755e-05 | No
25/03/2019 | 13:05:06 | MTB32 | Rural Long | Unknown | Unknown | 62 | 183 | 0.082807 | 0.0004525 | No
25/03/2019 | 13:38:40 | CL17 | Rural Long | Asset failure | HV | 3.6667 | 90 | 0.0024084 | 2.676e-05 | No
25/03/2019 | 15:34:21 | CBD367R | CBD | Unknown | Unknown | 10 | 307 | 0.59594 | 0.0019412 | No
25/03/2019 | 17:21:02 | AP365E | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 174 | 0.00055634 | 3.2e-06 | No
25/03/2019 | 18:38:55 | SM349A | Urban | Unknown | Unknown | 14 | 154 | 0.0034467 | 2.238e-05 | No
25/03/2019 | 22:29:10 | AP227D | Urban | Planned |  | 16 | 254 | 0.006497 | 2.558e-05 | No
25/03/2019 | 22:29:10 | AP227D | Urban | Planned |  | 4 | 14 | 8.953e-05 | 6.39e-06 | No
25/03/2019 | 23:09:53 | GA26 | Urban | Planned |  | 113 | 249 | 0.044982 | 0.00018065 | No
26/03/2019 | 00:35:33 | G33 | Rural Long | Unknown | Unknown | 8 | 238.5 | 0.013925 | 5.839e-05 | No
26/03/2019 | 08:29:57 | HH428F | Urban | Planned |  | 122 | 267 | 0.052075 | 0.00019504 | No
26/03/2019 | 08:33:16 | MG11 | Rural Short | Planned |  | 40 | 376 | 0.11205 | 0.00029801 | No
26/03/2019 | 08:34:23 | EL09 | Urban | Asset failure | LV | 1 | 151 | 0.0002414 | 1.6e-06 | No
26/03/2019 | 09:26:52 | GA28 | Rural Long | Planned |  | 13 | 66 | 0.006262 | 9.488e-05 | No
26/03/2019 | 09:50:27 | HH145A | Urban | Planned |  | 89 | 245 | 0.034859 | 0.00014228 | No
26/03/2019 | 09:57:47 | HH145A | Urban | Planned |  | 2 | 274 | 0.00087607 | 3.2e-06 | No
26/03/2019 | 10:05:02 | ST11 | Rural Short | Planned |  | 16 | 272.875 | 0.032527 | 0.0001192 | No
26/03/2019 | 10:11:27 | SB01 | Rural Long | Asset failure | LV | 21.6666 | 176 | 0.027831 | 0.00015813 | No
26/03/2019 | 10:29:17 | GA29 | Rural Long | Planned |  | 8 | 121 | 0.0070648 | 5.839e-05 | No
26/03/2019 | 10:43:05 | SM216E | Urban | Planned |  | 261 | 205 | 0.085537 | 0.00041725 | No
26/03/2019 | 11:26:45 | MG32 | Rural Long | Asset failure | HV | 2 | 173 | 0.0025252 | 1.46e-05 | No
26/03/2019 | 11:50:15 | GA28 | Rural Long | Planned |  | 4 | 46 | 0.0013429 | 2.919e-05 | No
26/03/2019 | 12:00:54 | GA36 | Rural Long | Planned |  | 2 | 189 | 0.0027588 | 1.46e-05 | No
26/03/2019 | 12:30:49 | SA744D | Urban | Planned |  | 1 | 124 | 0.00019824 | 1.6e-06 | No
26/03/2019 | 12:45:24 | AP425D | Urban | Asset failure | LV | 1 | 109 | 0.00017426 | 1.6e-06 | No
26/03/2019 | 13:00:31 | GA28 | Rural Long | Planned |  | 5 | 24 | 0.0008758 | 3.649e-05 | No
26/03/2019 | 15:06:34 | KI56 | Rural Long | Asset failure | HV | 7 | 45 | 0.002299 | 5.109e-05 | No
26/03/2019 | 15:21:49 | KI56 | Rural Long | Unknown | Unknown | 7 | 18 | 0.00091959 | 5.109e-05 | No
26/03/2019 | 19:12:35 | CV34 | Rural Long | Asset failure | HV | 17 | 1 | 0.00012407 | 0.00012407 | No
26/03/2019 | 20:41:19 | MI32 | Rural Long | Asset failure | HV | 1223 | 175.0564 | 1.5625 | 0.0089259 | No
26/03/2019 | 21:45:15 | NL451A | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
26/03/2019 | 22:12:35 | BM52 | Urban | Asset failure | LV | 1 | 226 | 0.0003613 | 1.6e-06 | No
26/03/2019 | 22:26:10 | HH429A | Urban | Overloads |  | 1 | 104 | 0.00016626 | 1.6e-06 | No
26/03/2019 | 22:43:07 | AP227D | Urban | Planned |  | 209 | 238 | 0.079521 | 0.00033412 | No
27/03/2019 | 01:13:34 | SD44200 | Rural Short | Animal | Animal impact | 3 | 691 | 0.015444 | 2.235e-05 | No
27/03/2019 | 05:37:39 | GU32 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 9 | 219 | 0.014385 | 6.569e-05 | No
27/03/2019 | 06:12:22 | WHY04 | Urban | Planned |  | 1 | 261 | 0.00041725 | 1.6e-06 | No
27/03/2019 | 06:48:52 | SM350G | Urban | Asset failure | LV | 5.3333 | 311 | 0.0026517 | 8.53e-06 | No
27/03/2019 | 08:10:48 | MV52 | Rural Short | Planned |  | 5 | 139 | 0.0051779 | 3.725e-05 | No
27/03/2019 | 08:16:25 | MV15 | Rural Short | Planned |  | 64 | 254 | 0.12111 | 0.00047681 | No
27/03/2019 | 08:45:17 | GU43 | Rural Long | Planned |  | 201 | 58.7164 | 0.086135 | 0.001467 | No
27/03/2019 | 08:46:49 | MB12 | Rural Short | Planned |  | 85 | 343.2 | 0.21734 | 0.00063326 | No
27/03/2019 | 08:56:50 | AP149F | Urban | Planned |  | 5 | 7 | 5.595e-05 | 7.99e-06 | No
27/03/2019 | 09:04:35 | YK23 | Rural Long | Planned |  | 10 | 354 | 0.025836 | 7.298e-05 | No
27/03/2019 | 09:07:52 | HH177C | Urban | Planned |  | 54 | 82 | 0.0070789 | 8.633e-05 | No
27/03/2019 | 09:16:02 | AP214C | Urban | Planned |  | 2 | 453 | 0.0014484 | 3.2e-06 | No
27/03/2019 | 09:29:25 | AP149F | Urban | Planned |  | 110 | 439 | 0.0772 | 0.00017585 | No
27/03/2019 | 09:30:40 | GA52 | Rural Long | Planned |  | 9 | 101 | 0.0066342 | 6.569e-05 | No
27/03/2019 | 09:37:10 | AP149D | Urban | Overloads |  | 1 | 84 | 0.00013429 | 1.6e-06 | No
27/03/2019 | 10:00:26 | AP132D | Urban | Planned |  | 330 | 370 | 0.1952 | 0.00052756 | No
27/03/2019 | 10:13:31 | VH51 | Rural Short | Animal | Animal impact | 2.6667 | 155 | 0.0030794 | 1.987e-05 | No
27/03/2019 | 10:26:04 | SM350A | Urban | Planned |  | 73 | 14 | 0.0016339 | 0.0001167 | No
27/03/2019 | 10:32:52 | CD15 | Rural Long | Planned |  | 1 | 108 | 0.00078822 | 7.3e-06 | No
27/03/2019 | 10:34:03 | SM350A | Urban | Planned |  | 4 | 392 | 0.0025067 | 6.39e-06 | No
27/03/2019 | 10:35:23 | NU05 | Rural Short | Planned |  | 5 | 190 | 0.0070776 | 3.725e-05 | No
27/03/2019 | 10:41:45 | AP132D | Urban | Planned |  | 1 | 88 | 0.00014068 | 1.6e-06 | No
27/03/2019 | 10:50:37 | MG17 | Rural Long | Animal | Animal impact | 46 | 37.9565 | 0.012743 | 0.00033572 | No
27/03/2019 | 11:03:51 | MV33 | Rural Short | Planned |  | 3 | 123 | 0.0027491 | 2.235e-05 | No
27/03/2019 | 11:07:18 | PL14 | Urban | Planned |  | 102 | 105.5294 | 0.017208 | 0.00016306 | No
27/03/2019 | 11:12:11 | EL10 | Urban | Asset failure | LV | 1 | 129 | 0.00020623 | 1.6e-06 | No
27/03/2019 | 11:42:48 | HH177B | Urban | Planned |  | 50 | 33 | 0.0026378 | 7.993e-05 | No
27/03/2019 | 12:56:02 | EL18 | Urban | Asset failure | LV | 1 | 329 | 0.00052596 | 1.6e-06 | No
27/03/2019 | 13:20:25 | NL511B | Urban | Asset failure | LV | 1 | 93 | 0.00014868 | 1.6e-06 | No
27/03/2019 | 14:06:52 | AP425D | Urban | Asset failure | LV | 1 | 307 | 0.00049079 | 1.6e-06 | No
27/03/2019 | 15:08:06 | R07 | Rural Short | Unknown | Unknown | 61 | 155.5082 | 0.070672 | 0.00045446 | No
27/03/2019 | 17:38:00 | SSD413 | Urban | Network business | Switching and protection error | 1776 | 119 | 0.33787 | 0.0028393 | No
27/03/2019 | 17:38:00 | SSD413 | Rural Short | Network business | Switching and protection error | 27817 | 114.8001 | 23.7913 | 0.20724 | No
27/03/2019 | 17:38:00 | SSD413 | Rural Long | Network business | Switching and protection error | 2281 | 132 | 2.1975 | 0.016648 | No
27/03/2019 | 18:18:31 | M14 | Rural Long | Unknown | Unknown | 1 | 284 | 0.0020727 | 7.3e-06 | No
27/03/2019 | 18:52:58 | NL760B | Urban | Asset failure | LV | 1 | 159 | 0.00025419 | 1.6e-06 | No
27/03/2019 | 19:31:59 | CM22 | Rural Long | Unknown | Unknown | 16 | 1075 | 0.12553 | 0.00011677 | No
27/03/2019 | 19:51:42 | MB28 | Rural Short | Unknown | Unknown | 139 | 95 | 0.098379 | 0.0010356 | No
27/03/2019 | 20:44:13 | SA18 | Urban | Asset failure | HV | 982 | 29.9542 | 0.047025 | 0.0015699 | No
27/03/2019 | 20:44:13 | SA18 | Urban | Asset failure | HV | 0 | 2 | 0.0028936 | 0 | No
27/03/2019 | 21:42:03 | KI31 | Rural Short | Asset failure | LV | 6.3333 | 79 | 0.0037276 | 4.718e-05 | No
28/03/2019 | 05:15:06 | MG37 | Rural Long | Unknown | Unknown | 85 | 27 | 0.01675 | 0.00062036 | No
28/03/2019 | 07:38:31 | MG06 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 378 | 48 | 0.13518 | 0.0028162 | No
28/03/2019 | 08:20:22 | SD38100 | Rural Long | Planned |  | 35 | 369 | 0.094258 | 0.00025544 | No
28/03/2019 | 08:32:07 | GA50 | Urban | Planned |  | 110 | 197 | 0.034643 | 0.00017585 | No
28/03/2019 | 08:34:51 | GA28 | Rural Long | Planned |  | 164 | 307 | 0.36746 | 0.0011969 | No
28/03/2019 | 08:48:13 | MG10 | Rural Long | Planned |  | 23 | 223 | 0.037433 | 0.00016786 | No
28/03/2019 | 09:05:23 | YK16 | Rural Long | Planned |  | 1 | 12 | 8.758e-05 | 7.3e-06 | No
28/03/2019 | 09:07:45 | BT04 | Rural Long | Planned |  | 10 | 346 | 0.025252 | 7.298e-05 | No
28/03/2019 | 09:11:06 | CD03 | Rural Short | Planned |  | 1 | 27 | 0.00020115 | 7.45e-06 | No
28/03/2019 | 09:13:01 | SD38200 | Rural Long | Planned |  | 4 | 321 | 0.0093711 | 2.919e-05 | No
28/03/2019 | 09:18:49 | HH130F | Urban | Planned |  | 2 | 89 | 0.00028456 | 3.2e-06 | No
28/03/2019 | 09:24:40 | M01 | Rural Long | Planned |  | 92 | 1288 | 0.86482 | 0.00067145 | No
28/03/2019 | 09:31:50 | KA03 | Rural Long | Planned |  | 86 | 236 | 0.14813 | 0.00062766 | No
28/03/2019 | 09:32:48 | MTB63 | Rural Short | Planned |  | 219 | 341 | 0.55637 | 0.0016316 | No
28/03/2019 | 09:34:09 | AP424F | Urban | Planned |  | 99 | 287 | 0.045423 | 0.00015827 | No
28/03/2019 | 09:45:10 | W04 | Rural Long | Planned |  | 144 | 314 | 0.33 | 0.001051 | No
28/03/2019 | 09:53:50 | AP226D | Urban | Planned |  | 238 | 478 | 0.18187 | 0.00038048 | No
28/03/2019 | 10:14:12 | MI14 | Rural Long | Planned |  | 3 | 77 | 0.0016859 | 2.19e-05 | No
28/03/2019 | 10:15:08 | VH51 | Rural Short | Planned |  | 86 | 348 | 0.22297 | 0.00064071 | No
28/03/2019 | 10:18:01 | SM349F | Urban | Planned |  | 45 | 269 | 0.019352 | 7.194e-05 | No
28/03/2019 | 10:33:55 | MTB52 | Rural Long | Planned |  | 53 | 145 | 0.056088 | 0.00038681 | No
28/03/2019 | 10:43:05 | EL17 | Urban | Animal | Animal impact | 6 | 115 | 0.0011031 | 9.59e-06 | No
28/03/2019 | 11:15:46 | CN83 | Rural Long | Planned |  | 3 | 51 | 0.0011167 | 2.19e-05 | No
28/03/2019 | 11:35:23 | KI16 | Rural Long | Planned |  | 2 | 62 | 0.00090499 | 1.46e-05 | No
28/03/2019 | 11:51:31 | AP424D | Urban | Other |  | 33.6666 | 69 | 0.0037137 | 5.382e-05 | No
28/03/2019 | 11:57:01 | MG52 | Rural Short | Asset failure | LV | 1 | 185 | 0.0013783 | 7.45e-06 | No
28/03/2019 | 12:15:30 | EL11 | Urban | Unknown | Unknown | 14.6667 | 312 | 0.0073155 | 2.345e-05 | No
28/03/2019 | 12:30:38 | EL19 | Urban | Unknown | Unknown | 15 | 14 | 0.00033572 | 2.398e-05 | No
28/03/2019 | 13:15:40 | AP424D | Urban | Asset failure | LV | 101 | 157 | 0.02535 | 0.00016147 | No
28/03/2019 | 13:50:20 | MV33 | Rural Short | Asset failure | HV | 8 | 40 | 0.002384 | 5.96e-05 | No
28/03/2019 | 13:52:13 | HH409A | Urban | Asset failure | LV | 1 | 596 | 0.00095281 | 1.6e-06 | No
28/03/2019 | 14:06:21 | PL34 | Rural Long | Unknown | Unknown | 246 | 147.9878 | 0.2657 | 0.0017954 | No
28/03/2019 | 14:16:36 | AP424D | Urban | Asset failure | LV | 69 | 104 | 0.011472 | 0.00011031 | No
28/03/2019 | 16:23:08 | ME427A | Urban | Planned |  | 2 | 87 | 0.00027817 | 3.2e-06 | No
28/03/2019 | 16:40:45 | KA03 | Rural Long | Third Party | Vehicle impact | 29 | 31 | 0.0065612 | 0.00021165 | No
28/03/2019 | 19:37:47 | MB34 | Rural Long | Unknown | Unknown | 1 | 12 | 8.758e-05 | 7.3e-06 | No
28/03/2019 | 21:10:04 | ST34 | Rural Long | Asset failure | LV | 2 | 337 | 0.0049191 | 1.46e-05 | No
28/03/2019 | 23:41:51 | HH102B | Urban | Animal | Animal impact | 482 | 38 | 0.029281 | 0.00077056 | No
29/03/2019 | 00:41:51 | MI23 | Rural Long | Asset failure | HV | 93 | 382.0753 | 0.25933 | 0.00067875 | No
29/03/2019 | 01:34:20 | SD54100 | Rural Long | Third Party | Other | 2577 | 84.8739 | 1.5963 | 0.018808 | No
29/03/2019 | 05:08:24 | SA520D | Urban | Asset failure | LV | 56 | 190 | 0.01701 | 8.953e-05 | No
29/03/2019 | 06:36:59 | KI32 | Rural Short | Unknown | Unknown | 22 | 63 | 0.010326 | 0.0001639 | No
29/03/2019 | 07:24:19 | BM34 | Rural Short | Asset failure | HV | 67 | 216 | 0.10782 | 0.00049916 | No
29/03/2019 | 07:58:12 | MTB81 | Rural Short | Planned |  | 132 | 263 | 0.25864 | 0.00098342 | No
29/03/2019 | 08:11:06 | YK11 | Rural Long | Planned |  | 57 | 149 | 0.061985 | 0.00041601 | No
29/03/2019 | 08:37:09 | MG37 | Rural Long | Weather |  | 85 | 73 | 0.045286 | 0.00062036 | No
29/03/2019 | 08:41:20 | HH409F | Urban | Planned |  | 103 | 258 | 0.042483 | 0.00016466 | No
29/03/2019 | 08:51:45 | AP149B | Urban | Third Party | Vehicle impact | 1 | 128 | 0.00020463 | 1.6e-06 | No
29/03/2019 | 08:55:12 | MTB61 | Rural Short | Planned |  | 78 | 285 | 0.16562 | 0.00058111 | No
29/03/2019 | 08:55:35 | GA22 | Rural Short | Planned |  | 43 | 341 | 0.10924 | 0.00032036 | No
29/03/2019 | 09:15:39 | MV22 | Rural Short | Planned |  | 1 | 24 | 0.0001788 | 7.45e-06 | No
29/03/2019 | 09:15:40 | ST11 | Rural Short | Planned |  | 72 | 238 | 0.12767 | 0.00053641 | No
29/03/2019 | 09:23:38 | VH18 | Rural Short | Unknown | Unknown | 148 | 90.7838 | 0.1001 | 0.0011026 | No
29/03/2019 | 09:27:58 | GA23 | Rural Short | Planned |  | 22 | 12 | 0.0019668 | 0.0001639 | No
29/03/2019 | 09:33:50 | SM179B | Urban | Planned |  | 41 | 278 | 0.018222 | 6.555e-05 | No
29/03/2019 | 09:38:44 | SM410A | Urban | Planned |  | 2 | 28 | 8.953e-05 | 3.2e-06 | No
29/03/2019 | 09:45:00 | CN02 | Rural Long | Planned |  | 14 | 142 | 0.014509 | 0.00010218 | No
29/03/2019 | 10:06:50 | W16 | Rural Long | Planned |  | 1 | 52 | 0.00037951 | 7.3e-06 | No
29/03/2019 | 10:13:31 | BM53 | Rural Short | Planned |  | 77 | 174 | 0.099817 | 0.00057366 | No
29/03/2019 | 10:14:43 | SM411E | Urban | Planned |  | 75 | 111 | 0.013309 | 0.0001199 | No
29/03/2019 | 10:14:48 | HH121B | Urban | Planned |  | 1 | 234 | 0.00037409 | 1.6e-06 | No
29/03/2019 | 10:17:46 | MB81 | Rural Long | Unknown | Unknown | 143 | 198 | 0.20665 | 0.0010437 | No
29/03/2019 | 10:20:08 | MT06 | Rural Long | Planned |  | 21 | 6 | 0.00091959 | 0.00015327 | No
29/03/2019 | 10:25:30 | R07 | Rural Short | Planned |  | 2 | 21 | 0.00031291 | 1.49e-05 | No
29/03/2019 | 10:42:34 | G17 | Rural Long | Planned |  | 16 | 176 | 0.020552 | 0.00011677 | No
29/03/2019 | 10:48:58 | GU15 | Rural Long | Planned |  | 8 | 196 | 0.011444 | 5.839e-05 | No
29/03/2019 | 11:03:59 | HH107B | Urban | Animal | Animal impact | 196 | 5 | 0.0015667 | 0.00031334 | No
29/03/2019 | 11:15:42 | HH121B | Urban | Planned |  | 62 | 161 | 0.015958 | 9.912e-05 | No
29/03/2019 | 11:31:23 | GA18 | Rural Long | Unknown | Unknown | 73 | 158.6438 | 0.084522 | 0.00053278 | No
29/03/2019 | 12:02:11 | PL14 | Urban | Unknown | Unknown | 12 | 3 | 5.755e-05 | 1.918e-05 | No
29/03/2019 | 12:12:27 | HH118C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 585 | 34 | 0.031798 | 0.00093522 | No
29/03/2019 | 12:35:57 | SM350E | Urban | Asset failure | LV | 1 | 84 | 0.00013429 | 1.6e-06 | No
29/03/2019 | 12:52:17 | NL760B | Urban | Planned |  | 1 | 31 | 4.956e-05 | 1.6e-06 | No
29/03/2019 | 13:00:58 | AP146E | Urban | Unknown | Unknown | 4 | 503 | 0.0032165 | 6.39e-06 | No
29/03/2019 | 13:05:03 | SD48200 | Rural Long | Planned |  | 471 | 40.9915 | 0.14091 | 0.0034375 | No
29/03/2019 | 13:32:50 | HH341F | Urban | Asset failure | LV | 1 | 315 | 0.00050358 | 1.6e-06 | No
29/03/2019 | 13:53:50 | SA18 | Urban | Planned |  | 77 | 31 | 0.003816 | 0.0001231 | No
29/03/2019 | 14:01:15 | BM34 | Rural Short | Other |  | 2 | 88 | 0.0013112 | 1.49e-05 | No
29/03/2019 | 14:02:04 | GU51 | Urban | Unknown | Unknown | 17 | 53 | 0.0014404 | 2.718e-05 | No
29/03/2019 | 14:05:36 | SM350H | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1946 | 109.1382 | 0.33953 | 0.003111 | No
29/03/2019 | 14:46:40 | KA30 | Rural Short | Unknown | Unknown | 1 | 2 | 1.49e-05 | 7.45e-06 | No
29/03/2019 | 15:05:12 | SA744D | Urban | Asset failure | LV | 1 | 99 | 0.00015827 | 1.6e-06 | No
29/03/2019 | 15:25:24 | NL234A | Urban | Asset failure | LV | 1 | 149 | 0.0002382 | 1.6e-06 | No
29/03/2019 | 15:27:14 | GA25 | Rural Short | Unknown | Unknown | 18 | 181 | 0.024273 | 0.0001341 | No
29/03/2019 | 15:55:26 | M14 | Rural Long | Unknown | Unknown | 13 | 67 | 0.0063568 | 9.488e-05 | No
29/03/2019 | 16:17:20 | PA13 | Rural Long | Unknown | Unknown | 2 | 65 | 0.00094878 | 1.46e-05 | No
29/03/2019 | 16:56:48 | HH177A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 266 | 0.00042525 | 1.6e-06 | No
29/03/2019 | 16:59:02 | NL111P | Urban | Asset failure | LV | 1 | 178 | 0.00028456 | 1.6e-06 | No
29/03/2019 | 17:23:12 | BT04 | Rural Long | Vegetation | Grow-in - NSP responsibility | 1 | 246 | 0.0017954 | 7.3e-06 | No
29/03/2019 | 17:34:56 | CV15 | Rural Long | Asset failure | LV | 2 | 299 | 0.0043644 | 1.46e-05 | No
29/03/2019 | 19:08:50 | SM402C | Urban | Overloads |  | 2 | 158 | 0.00050518 | 3.2e-06 | No
29/03/2019 | 19:16:32 | MT08 | Rural Long | Asset failure | LV | 23 | 90 | 0.015108 | 0.00016786 | No
29/03/2019 | 19:30:14 | AP149B | Urban | Asset failure | LV | 1 | 155 | 0.00024779 | 1.6e-06 | No
29/03/2019 | 20:54:05 | AP355H | Urban | Asset failure | LV | 1 | 152 | 0.000243 | 1.6e-06 | No
29/03/2019 | 22:41:42 | BU10 | Rural Long | Asset failure | LV | 1 | 118 | 0.0008612 | 7.3e-06 | No
29/03/2019 | 23:04:36 | MG46 | Rural Short | Asset failure | HV | 202.9999 | 70 | 0.10587 | 0.0015124 | No
29/03/2019 | 23:04:36 | MG46 | Rural Short | Asset failure | HV | 0 | 72.1724 | 0.10915 | 0 | No
30/03/2019 | 00:58:25 | LM51 | Rural Long | Asset failure | HV | 14 | 607 | 0.062021 | 0.00010218 | No
30/03/2019 | 02:27:14 | WHY17 | Rural Short | Unknown | Unknown | 52 | 297 | 0.11506 | 0.00038741 | No
30/03/2019 | 03:13:41 | HH121B | Urban | Animal | Animal impact | 47 | 449 | 0.033737 | 7.514e-05 | No
30/03/2019 | 07:01:39 | MTB12 | Rural Short | Unknown | Unknown | 146 | 302 | 0.32849 | 0.0010877 | No
30/03/2019 | 07:41:40 | PA07 | Rural Long | Asset failure | LV | 1 | 123 | 0.0008977 | 7.3e-06 | No
30/03/2019 | 08:23:23 | KA10 | Rural Long | Planned |  | 2 | 64 | 0.00093419 | 1.46e-05 | No
30/03/2019 | 08:26:25 | SM126C | Urban | Overloads |  | 1 | 265 | 0.00042365 | 1.6e-06 | No
30/03/2019 | 08:30:44 | SSD541 | Rural Short | Planned |  | 1 | 154 | 0.0011473 | 7.45e-06 | No
30/03/2019 | 08:48:13 | PA18 | Rural Long | Planned |  | 94 | 91 | 0.06243 | 0.00068604 | No
30/03/2019 | 08:48:13 | PA18 | Rural Long | Planned |  | 0 | 85 | 0.058314 | 0 | No
30/03/2019 | 09:14:45 | MG46 | Rural Short | Unknown | Unknown | 329 | 195.5684 | 0.47936 | 0.0024511 | No
30/03/2019 | 10:24:24 | AP355E | Urban | Planned |  | 6 | 1555 | 0.014916 | 9.59e-06 | No
30/03/2019 | 11:16:26 | NL111P | Urban | Asset failure | LV | 12.6667 | 34 | 0.0006885 | 2.025e-05 | No
30/03/2019 | 12:07:15 | AP424B | Urban | Weather |  | 1 | 87 | 0.00013908 | 1.6e-06 | No
30/03/2019 | 12:31:02 | GA43 | Rural Short | Asset failure | LV | 2 | 18 | 0.00026821 | 1.49e-05 | No
30/03/2019 | 13:03:42 | HH341K | Urban | Asset failure | LV | 1 | 367 | 0.00058671 | 1.6e-06 | No
30/03/2019 | 14:03:28 | AP529A | Urban | Asset failure | LV | 1 | 262 | 0.00041885 | 1.6e-06 | No
30/03/2019 | 14:06:58 | AP372A | Urban | Planned |  | 1 | 324 | 0.00051797 | 1.6e-06 | No
30/03/2019 | 14:26:42 | VH10 | Rural Short | Asset failure | LV | 20 | 22 | 0.0032781 | 0.000149 | No
30/03/2019 | 14:31:26 | MG46 | Rural Short | Asset failure | HV | 329 | 69.9392 | 0.17143 | 0.0024511 | No
30/03/2019 | 15:11:21 | MT02 | Rural Long | Asset failure | HV | 135 | 163.1111 | 0.16071 | 0.00098528 | No
30/03/2019 | 23:14:09 | AP125D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2284 | 125.3363 | 0.45765 | 0.0036514 | No
31/03/2019 | 03:35:17 | PP16 | Rural Short | Unknown | Unknown | 74 | 489.3649 | 0.26979 | 0.00055131 | No
31/03/2019 | 05:08:04 | CD17 | Rural Long | Unknown | Unknown | 37 | 260 | 0.07021 | 0.00027004 | No
31/03/2019 | 06:38:27 | R03 | Rural Long | Unknown | Unknown | 6 | 145 | 0.0063495 | 4.379e-05 | No
31/03/2019 | 07:15:32 | MG05 | Rural Long | Other |  | 2.6667 | 75 | 0.0014597 | 1.946e-05 | No
31/03/2019 | 08:38:54 | HH121G | Urban | Asset failure | LV | 1 | 367 | 0.00058671 | 1.6e-06 | No
31/03/2019 | 09:11:24 | SM402D | Urban | Third Party | Vehicle impact | 196 | 230 | 0.072068 | 0.00031334 | No
31/03/2019 | 09:54:43 | HH428D | Urban | Planned |  | 1 | 17 | 2.718e-05 | 1.6e-06 | No
31/03/2019 | 11:34:29 | SD52100 | Rural Long | Asset failure | Subtransmission | 859 | 101.9488 | 0.63914 | 0.0062693 | No
31/03/2019 | 11:42:14 | HH177F | Urban | Asset failure | LV | 18 | 47 | 0.0013525 | 2.878e-05 | No
31/03/2019 | 12:34:35 | SM216B | Urban | Asset failure | HV | 2767 | 96.6021 | 0.42732 | 0.0044235 | No
31/03/2019 | 13:18:14 | CBD412S-GG2 | Urban | Asset failure | HV | 462 | 105.9957 | 0.078287 | 0.00073859 | No
31/03/2019 | 16:52:51 | MG29 | Rural Long | Other |  | 2 | 156 | 0.0022771 | 1.46e-05 | No
31/03/2019 | 17:58:44 | HH341J | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 130 | 0.00020783 | 1.6e-06 | No
31/03/2019 | 18:38:54 | CBD27F | CBD | Other |  | 2.6667 | 133 | 0.068847 | 0.00051765 | No
31/03/2019 | 20:08:54 | MG19 | Rural Long | Asset failure | Distribution substation | 113 | 73.6018 | 0.0607 | 0.00082471 | No
1/04/2019 | 07:31:37 | PP12 | Rural Long | Unknown | Unknown | 3 | 318 | 0.0069626 | 2.19e-05 | No
1/04/2019 | 08:39:21 | SA17 | Urban | Planned |  | 83 | 101 | 0.013402 | 0.00013269 | No
1/04/2019 | 09:08:44 | MV31 | Rural Short | Planned |  | 1 | 138 | 0.0010281 | 7.45e-06 | No
1/04/2019 | 09:09:32 | NL760C | Urban | Unknown | Unknown | 15.6667 | 159 | 0.0039823 | 2.505e-05 | No
1/04/2019 | 09:25:44 | NA36 | Rural Long | Planned |  | 64 | 387 | 0.18077 | 0.00046709 | No
1/04/2019 | 09:30:01 | HH386B | Urban | Planned |  | 73 | 157 | 0.018322 | 0.0001167 | No
1/04/2019 | 09:30:45 | GU13 | Rural Long | Planned |  | 31 | 264 | 0.05973 | 0.00022625 | No
1/04/2019 | 09:34:00 | GA15 | Rural Short | Planned |  | 48 | 259 | 0.09262 | 0.00035761 | No
1/04/2019 | 09:39:58 | GA53 | Rural Short | Planned |  | 17 | 264 | 0.033436 | 0.00012665 | No
1/04/2019 | 10:16:46 | MTB11 | Rural Short | Asset failure | LV | 1 | 146 | 0.0010877 | 7.45e-06 | No
1/04/2019 | 10:29:34 | AP227B / AP227C | Urban | Planned |  | 453 | 1271.6777 | 0.92095 | 0.0007242 | No
1/04/2019 | 10:43:42 | SB17 | Rural Long | Planned |  | 22 | 113 | 0.018144 | 0.00016056 | No
1/04/2019 | 10:51:11 | SA17 | Urban | Network business | Network error | 10.3333 | 15 | 0.00024779 | 1.652e-05 | No
1/04/2019 | 10:52:06 | MG44 | Urban | Other |  | 1 | 137 | 0.00021902 | 1.6e-06 | No
1/04/2019 | 11:10:05 | NL511D | Urban | Asset failure | HV | 38 | 9 | 0.00054675 | 6.075e-05 | No
1/04/2019 | 11:27:17 | W06 | Rural Long | Unknown | Unknown | 2 | 361 | 0.0052694 | 1.46e-05 | No
1/04/2019 | 12:15:59 | NL511D | Urban | Unknown | Unknown | 38 | 2 | 0.0001215 | 6.075e-05 | No
1/04/2019 | 13:23:29 | GA05 | Rural Short | Asset failure | LV | 1 | 116 | 0.00086422 | 7.45e-06 | No
1/04/2019 | 14:00:56 | AP373K | Urban | Asset failure | HV | 152 | 107.3158 | 0.026078 | 0.000243 | No
1/04/2019 | 14:25:12 | SG14 | Rural Short | Animal | Animal nesting/burrowing, etc and other | 16.6667 | 268 | 0.033277 | 0.00012417 | No
1/04/2019 | 16:36:53 | ST11 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 139 | 0.0010356 | 7.45e-06 | No
1/04/2019 | 18:27:59 | EL19 | Urban | Asset failure | LV | 2.6667 | 15 | 6.395e-05 | 4.26e-06 | No
1/04/2019 | 18:36:14 | SG03 | Rural Short | Asset failure | LV | 1 | 109 | 0.00081207 | 7.45e-06 | No
1/04/2019 | 22:02:59 | AP132D | Urban | Overloads |  | 1 | 64 | 0.00010232 | 1.6e-06 | No
1/04/2019 | 22:40:24 | AP227D | Urban | Planned |  | 94 | 308 | 0.046285 | 0.00015028 | No
2/04/2019 | 02:06:51 | R25 | Rural Long | Third Party | Other | 114 | 176.7544 | 0.14706 | 0.00083201 | No
2/04/2019 | 07:51:23 | HH428C | Urban | Asset failure | HV | 1090 | 13.5651 | 0.023638 | 0.0017426 | No
2/04/2019 | 08:05:22 | MTB81 | Rural Short | Planned |  | 3 | 306 | 0.0068392 | 2.235e-05 | No
2/04/2019 | 08:25:49 | WHY02 | Urban | Asset failure | LV | 1 | 139 | 0.00022222 | 1.6e-06 | No
2/04/2019 | 08:30:51 | YK23 | Rural Long | Planned |  | 3 | 210 | 0.0045979 | 2.19e-05 | No
2/04/2019 | 08:39:03 | G14 | Rural Long | Planned |  | 96 | 417 | 0.29217 | 0.00070064 | No
2/04/2019 | 08:44:26 | ST44 | Rural Long | Planned |  | 104 | 165.7308 | 0.12579 | 0.00075903 | No
2/04/2019 | 08:49:24 | SM349A | Urban | Planned |  | 85 | 287 | 0.039 | 0.00013589 | No
2/04/2019 | 08:51:00 | MB12 | Rural Short | Planned |  | 51 | 352 | 0.13375 | 0.00037996 | No
2/04/2019 | 09:01:15 | PL754A | Rural Long | Planned |  | 24 | 343 | 0.06008 | 0.00017516 | No
2/04/2019 | 09:11:05 | WHY04 | Urban | Asset failure | LV | 2 | 185 | 0.00059151 | 3.2e-06 | No
2/04/2019 | 09:12:07 | GA22 | Rural Short | Planned |  | 204 | 361.299 | 0.54911 | 0.0015198 | No
2/04/2019 | 09:16:48 | SD38200 | Rural Long | Planned |  | 2 | 131 | 0.0019122 | 1.46e-05 | No
2/04/2019 | 09:19:50 | NU07 / NU08 | Rural Long | Planned |  | 115 | 119.7478 | 0.10051 | 0.00083931 | No
2/04/2019 | 09:26:32 | NL115B | Urban | Planned |  | 275 | 300 | 0.13189 | 0.00043964 | No
2/04/2019 | 09:57:55 | GA53 | Rural Short | Planned |  | 1 | 98 | 0.00073011 | 7.45e-06 | No
2/04/2019 | 10:27:28 | NL115B | Urban | Planned |  | 1 | 26 | 4.157e-05 | 1.6e-06 | No
2/04/2019 | 10:41:53 | VH18 | Rural Short | Planned |  | 1 | 92 | 0.00068541 | 7.45e-06 | No
2/04/2019 | 11:37:59 | ST11 | Rural Short | Planned |  | 2 | 26 | 0.00038741 | 1.49e-05 | No
2/04/2019 | 12:19:23 | MI08 | Rural Long | Weather |  | 5 | 106 | 0.0038681 | 3.649e-05 | No
2/04/2019 | 14:40:22 | AP132B | Urban | Asset failure | HV | 3 | 1313 | 0.0062972 | 4.8e-06 | No
2/04/2019 | 15:46:35 | HH107B | Urban | Asset failure | LV | 1 | 270 | 0.00043164 | 1.6e-06 | No
2/04/2019 | 19:50:25 | AP373E | Urban | Unknown | Unknown | 219 | 90.7763 | 0.031782 | 0.00035011 | No
2/04/2019 | 19:50:25 | AP373E | Urban | Unknown | Unknown | 0 | 1 | 0.00033892 | 0 | No
2/04/2019 | 23:28:55 | NA06 | Rural Long | Animal | Animal impact | 29 | 106 | 0.022435 | 0.00021165 | No
2/04/2019 | 23:46:06 | HH177E | Urban | Overloads |  | 1 | 658 | 0.0010519 | 1.6e-06 | No
3/04/2019 | 05:06:22 | VH17 | Rural Short | Unknown | Unknown | 31.3333 | 136 | 0.031748 | 0.00023344 | No
3/04/2019 | 08:17:38 | MG43 | Rural Short | Planned |  | 1505 | 517 | 5.7968 | 0.011212 | No
3/04/2019 | 08:28:47 | SD49900 | Rural Short | Planned |  | 3 | 433 | 0.0096777 | 2.235e-05 | No
3/04/2019 | 08:39:04 | HH496G | Urban | Planned |  | 90 | 23.8 | 0.0034244 | 0.00014388 | No
3/04/2019 | 08:39:04 | HH496G | Urban | Planned |  | 0 | 19 | 0.0027337 | 0 | No
3/04/2019 | 09:30:20 | NL111C | Urban | Planned |  | 64 | 259 | 0.0265 | 0.00010232 | No
3/04/2019 | 09:59:00 | SA520F | Urban | Planned |  | 1 | 3062 | 0.0048951 | 1.6e-06 | No
3/04/2019 | 10:10:35 | VH32 | Rural Short | Asset failure | LV | 1 | 182 | 0.0013559 | 7.45e-06 | No
3/04/2019 | 10:18:45 | CV31 | Rural Long | Planned |  | 1 | 135 | 0.00098528 | 7.3e-06 | No
3/04/2019 | 10:19:52 | MV31 | Rural Short | Planned |  | 1 | 86 | 0.00064071 | 7.45e-06 | No
3/04/2019 | 10:59:28 | G23 | Rural Long | Planned |  | 3 | 123 | 0.0026931 | 2.19e-05 | No
3/04/2019 | 12:06:00 | SA36 | Urban | Third Party | Vehicle impact | 14 | 166 | 0.0037153 | 2.238e-05 | No
3/04/2019 | 12:11:02 | AP146A | Urban | Asset failure | HV | 649 | 105.131 | 0.10908 | 0.0010375 | No
3/04/2019 | 12:32:48 | SM411F | Urban | Overloads |  | 1 | 165 | 0.00026378 | 1.6e-06 | No
3/04/2019 | 14:29:33 | MV32 | Rural Short | Unknown | Unknown | 2 | 102 | 0.0015198 | 1.49e-05 | No
3/04/2019 | 14:29:44 | MV32 | Rural Short | Unknown | Unknown | 1 | 93 | 0.00069286 | 7.45e-06 | No
3/04/2019 | 14:47:54 | AP139C | Urban | Unknown | Unknown | 1 | 158 | 0.00025259 | 1.6e-06 | No
3/04/2019 | 17:40:18 | HH522C | Urban | Asset failure | LV | 1 | 132 | 0.00021103 | 1.6e-06 | No
3/04/2019 | 21:42:25 | CBD367S | CBD | Planned |  | 1 | 359 | 0.069688 | 0.00019412 | No
3/04/2019 | 23:19:49 | CBD366S | Urban | Planned |  | 59 | 273 | 0.02575 | 9.432e-05 | No
4/04/2019 | 01:31:38 | MV64 | Urban | Asset failure | LV | 1 | 17 | 2.718e-05 | 1.6e-06 | No
4/04/2019 | 02:38:08 | AP132D | Urban | Animal | Animal impact | 2163 | 60 | 0.20748 | 0.0034579 | No
4/04/2019 | 08:07:32 | MV15 | Rural Short | Planned |  | 15 | 81 | 0.0090519 | 0.00011175 | No
4/04/2019 | 09:07:27 | YK15 | Rural Long | Planned |  | 74 | 322 | 0.1739 | 0.00054008 | No
4/04/2019 | 09:13:11 | VH14 | Rural Short | Planned |  | 39 | 368 | 0.10692 | 0.00029056 | No
4/04/2019 | 09:39:34 | GA22 | Rural Short | Planned |  | 308 | 363 | 0.83296 | 0.0022947 | No
4/04/2019 | 09:40:22 | HH145E | Urban | Unknown | Unknown | 15.6667 | 62 | 0.0015528 | 2.505e-05 | No
4/04/2019 | 09:56:03 | ST11 | Rural Short | Planned |  | 160 | 321 | 0.38264 | 0.001192 | No
4/04/2019 | 09:57:35 | GU31 | Rural Long | Planned |  | 46 | 228 | 0.076545 | 0.00033572 | No
4/04/2019 | 10:03:47 | SD37102 | Rural Long | Planned |  | 101 | 218.3465 | 0.16095 | 0.00073713 | No
4/04/2019 | 10:13:11 | SM410A | Urban | Planned |  | 264 | 155 | 0.065418 | 0.00042205 | No
4/04/2019 | 10:15:37 | HH522B | Urban | Planned |  | 123 | 288.0488 | 0.056641 | 0.00019664 | No
4/04/2019 | 10:22:10 | BM44 | Rural Short | Planned |  | 20 | 47 | 0.0070031 | 0.000149 | No
4/04/2019 | 10:23:06 | EL19 | Urban | Third Party | Other | 2 | 29 | 9.272e-05 | 3.2e-06 | No
4/04/2019 | 10:28:09 | PA24 | Rural Long | Unknown | Unknown | 27 | 138 | 0.027194 | 0.00019706 | No
4/04/2019 | 10:43:25 | GU32 | Rural Long | Planned |  | 2 | 122 | 0.0017808 | 1.46e-05 | No
4/04/2019 | 10:55:10 | MB41 | Rural Long | Planned |  | 14 | 185 | 0.018903 | 0.00010218 | No
4/04/2019 | 11:01:22 | G25 | Rural Long | Planned |  | 107 | 63.5607 | 0.049636 | 0.00078092 | No
4/04/2019 | 12:09:15 | MG43 | Rural Short | Planned |  | 99 | 133 | 0.098096 | 0.00073756 | No
4/04/2019 | 13:25:57 | BT02 | Rural Long | Planned |  | 5 | 78 | 0.0028464 | 3.649e-05 | No
4/04/2019 | 13:56:13 | MTB13 | Rural Short | Third Party | Dig-in | 1269 | 91.0851 | 0.86114 | 0.0094542 | No
4/04/2019 | 13:56:16 | GA01 | Urban | Asset failure | LV | 13 | 141 | 0.0029304 | 2.078e-05 | No
4/04/2019 | 14:06:25 | ME347A | Urban | Asset failure | LV | 31 | 630 | 0.031222 | 4.956e-05 | No
4/04/2019 | 14:19:25 | ME347A | Urban | Asset failure | LV | 26 | 887 | 0.036869 | 4.157e-05 | No
4/04/2019 | 14:37:14 | G25 | Rural Long | Asset failure | HV | 30 | 289 | 0.063277 | 0.00021895 | No
4/04/2019 | 15:02:33 | YK15 | Rural Long | Asset failure | HV | 74 | 63 | 0.034025 | 0.00054008 | No
4/04/2019 | 16:52:03 | NL234E | Urban | Unknown | Unknown | 15 | 97 | 0.0023261 | 2.398e-05 | No
4/04/2019 | 17:28:33 | SA17 | Urban | Overloads |  | 1 | 133 | 0.00021262 | 1.6e-06 | No
4/04/2019 | 19:00:12 | MV14 | Rural Short | Unknown | Unknown | 3 | 322 | 0.0071968 | 2.235e-05 | No
4/04/2019 | 22:39:07 | MB12 | Rural Short | Asset failure | LV | 25 | 103 | 0.019184 | 0.00018625 | No
4/04/2019 | 23:08:08 | AP529E | Urban | Overloads |  | 1 | 119 | 0.00019024 | 1.6e-06 | No
5/04/2019 | 03:34:00 | VH16 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 112.6667 | 359.2367 | 0.30154 | 0.00083938 | No
5/04/2019 | 08:17:52 | EL21 | Urban | Asset failure | HV | 71.6667 | 87.2465 | 0.009996 | 0.00011457 | No
5/04/2019 | 08:35:34 | MTB54 | Rural Long | Planned |  | 245 | 235 | 0.4202 | 0.0017881 | No
5/04/2019 | 08:46:47 | KA28 | Rural Long | Planned |  | 1 | 44 | 0.00032113 | 7.3e-06 | No
5/04/2019 | 09:18:41 | CM25 | Rural Long | Planned |  | 90 | 68 | 0.044666 | 0.00065685 | No
5/04/2019 | 09:28:59 | ST23 | Rural Short | Planned |  | 3 | 124 | 0.0027715 | 2.235e-05 | No
5/04/2019 | 09:36:19 | HH409D | Urban | Planned |  | 101 | 282 | 0.045533 | 0.00016147 | No
5/04/2019 | 09:39:54 | MB81 | Rural Long | Unknown | Unknown | 2 | 53 | 0.00077362 | 1.46e-05 | No
5/04/2019 | 09:42:23 | ST12 | Rural Short | Planned |  | 67 | 51.1493 | 0.025532 | 0.00049916 | No
5/04/2019 | 09:56:10 | ST12 | Rural Short | Planned |  | 1 | 138 | 0.0010281 | 7.45e-06 | No
5/04/2019 | 10:06:10 | AP132D | Urban | Vegetation | Grow-in - NSP responsibility | 2163 | 53.7466 | 0.18585 | 0.0034579 | No
5/04/2019 | 10:09:00 | M13 | Rural Long | Planned |  | 3 | 166 | 0.0036346 | 2.19e-05 | No
5/04/2019 | 10:12:50 | PA24 | Rural Long | Planned |  | 27 | 67 | 0.013203 | 0.00019706 | No
5/04/2019 | 10:13:13 | CD03 | Rural Short | Planned |  | 4 | 160 | 0.0047681 | 2.98e-05 | No
5/04/2019 | 11:08:51 | SM350A | Urban | Planned |  | 91 | 152 | 0.022113 | 0.00014548 | No
5/04/2019 | 11:11:01 | CN32 | Rural Long | Asset failure | LV | 1 | 410 | 0.0029923 | 7.3e-06 | No
5/04/2019 | 11:16:50 | HH121B | Urban | Planned |  | 239 | 202 | 0.077181 | 0.00038208 | No
5/04/2019 | 11:23:14 | YK19 | Rural Long | Unknown | Unknown | 1 | 3 | 2.19e-05 | 7.3e-06 | No
5/04/2019 | 11:24:14 | KA13 | Rural Long | Asset failure | LV | 2.6667 | 107 | 0.0020825 | 1.946e-05 | No
5/04/2019 | 11:35:24 | CN01 | Rural Long | Asset failure | LV | 1 | 287 | 0.0020946 | 7.3e-06 | No
5/04/2019 | 11:50:48 | CBD103B | Urban | Asset failure | LV | 13.3333 | 75 | 0.0015987 | 2.132e-05 | No
5/04/2019 | 12:00:29 | VH10 | Rural Short | Asset failure | LV | 20 | 259 | 0.038592 | 0.000149 | No
5/04/2019 | 12:16:06 | HH118B | Urban | Unknown | Unknown | 9.6667 | 299 | 0.0046207 | 1.545e-05 | No
5/04/2019 | 12:44:31 | PL28 | Rural Long | Asset failure | HV | 95 | 202 | 0.14006 | 0.00069334 | No
5/04/2019 | 12:52:38 | MI23 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 93 | 205.5161 | 0.13949 | 0.00067875 | No
5/04/2019 | 12:56:55 | GU12 | Rural Long | Unknown | Unknown | 115 | 134 | 0.11247 | 0.00083931 | No
5/04/2019 | 13:14:01 | W02 | Rural Long | Unknown | Unknown | 38 | 16 | 0.0044374 | 0.00027734 | No
5/04/2019 | 13:14:48 | SSD188 | Urban | 7 - STPIS Exclusion (3.3)(a) |  | 8972 | 45.5614 | 0.6535 | 0.014343 | No
5/04/2019 | 13:14:48 | SSD188 | Rural Long | 7 - STPIS Exclusion (3.3)(a) |  | 4874 | 48 | 1.7075 | 0.035572 | No
5/04/2019 | 13:22:23 | MT06 | Rural Long | Asset failure | LV | 11.3333 | 57 | 0.0047147 | 8.271e-05 | No
5/04/2019 | 13:29:31 | SA12 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 397 | 40 | 0.025387 | 0.00063467 | No
5/04/2019 | 13:48:54 | SA13 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 823 | 41 | 0.053944 | 0.0013157 | No
5/04/2019 | 13:55:20 | HH118C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1423 | 51.1321 | 0.11632 | 0.0022749 | No
5/04/2019 | 14:12:01 | HH409D | Urban | Unknown | Unknown | 22.3333 | 230 | 0.0082118 | 3.57e-05 | No
5/04/2019 | 14:12:33 | VH21 | Rural Short | Asset failure | LV | 1 | 246 | 0.0018327 | 7.45e-06 | No
5/04/2019 | 14:29:12 | VH22 | Rural Short | Asset failure | HV | 1 | 320 | 0.002384 | 7.45e-06 | No
5/04/2019 | 14:30:59 | HH429B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 153 | 0.0002446 | 1.6e-06 | No
5/04/2019 | 14:48:31 | AP425C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 258 | 0.00041246 | 1.6e-06 | No
5/04/2019 | 14:50:10 | SG08 | Rural Short | Asset failure | LV | 1.6667 | 41 | 0.00050909 | 1.242e-05 | No
5/04/2019 | 15:09:10 | ME131C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2657 | 62 | 0.26336 | 0.0042477 | No
5/04/2019 | 15:34:00 | VH22 | Rural Short | Asset failure | HV | 2 | 261 | 0.003889 | 1.49e-05 | No
5/04/2019 | 15:42:05 | PL07 | Urban | Asset failure | HV | 15 | 203 | 0.004868 | 2.398e-05 | No
5/04/2019 | 15:55:24 | SA20 | Urban | Asset failure | LV | 1 | 502 | 0.00080253 | 1.6e-06 | No
5/04/2019 | 16:00:22 | VH23 | Rural Short | Asset failure | LV | 18.3333 | 118 | 0.016117 | 0.00013659 | No
5/04/2019 | 16:46:06 | HH428A | Urban | Overloads |  | 1 | 218 | 0.00034851 | 1.6e-06 | No
5/04/2019 | 16:48:58 | EL20 | Urban | Asset failure | LV | 2 | 1139 | 0.0036418 | 3.2e-06 | No
5/04/2019 | 16:59:49 | LX41 | Rural Short | Vegetation | Grow-in - NSP responsibility | 1 | 112 | 0.00083442 | 7.45e-06 | No
5/04/2019 | 17:47:55 | MG52 | Rural Short | Asset failure | LV | 1 | 239 | 0.0017806 | 7.45e-06 | No
5/04/2019 | 18:17:01 | NA34 | Rural Long | Asset failure | HV | 150 | 440.7867 | 0.48255 | 0.0010948 | No
5/04/2019 | 18:17:01 | NA34 | Rural Long | Asset failure | HV | 0 | 1 | 0.00032843 | 0 | No
5/04/2019 | 18:18:33 | SA11 | Urban | Asset failure | LV | 1 | 395 | 0.00063148 | 1.6e-06 | No
5/04/2019 | 18:58:31 | HH177E | Urban | Asset failure | LV | 1 | 150 | 0.0002398 | 1.6e-06 | No
5/04/2019 | 19:58:20 | SM179C | Urban | Vegetation | Grow-in - NSP responsibility | 2 | 146 | 0.00046681 | 3.2e-06 | No
5/04/2019 | 20:39:58 | HH177B | Urban | Asset failure | LV | 81 | 88 | 0.011395 | 0.00012949 | No
5/04/2019 | 21:03:33 | SM216B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 118 | 43 | 0.0081117 | 0.00018864 | No
5/04/2019 | 23:04:39 | SM172F | Urban | Asset failure | LV | 1 | 67 | 0.00010711 | 1.6e-06 | No
6/04/2019 | 06:18:02 | CN42 | Rural Long | Asset failure | HV | 28 | 183.5714 | 0.037513 | 0.00020435 | No
6/04/2019 | 07:20:12 | CBD353F | CBD | Planned |  | 1 | 428 | 0.083083 | 0.00019412 | No
6/04/2019 | 08:28:45 | SD34201 | Rural Short | Planned |  | 2 | 161 | 0.0023989 | 1.49e-05 | No
6/04/2019 | 08:41:33 | PP03 | Urban | Asset failure | LV | 1 | 135 | 0.00021582 | 1.6e-06 | No
6/04/2019 | 09:00:00 | SD2011 | Urban | Planned |  | 1 | 11635 | 0.018601 | 1.6e-06 | No
6/04/2019 | 11:29:32 | SA520J | Urban | Asset failure | LV | 18.3333 | 11 | 0.0003224 | 2.931e-05 | No
6/04/2019 | 12:25:18 | AP214B | Urban | Asset failure | LV | 2 | 280 | 0.00089526 | 3.2e-06 | No
6/04/2019 | 13:33:57 | G06 | Rural Long | Asset failure | HV | 1 | 20 | 0.00014597 | 7.3e-06 | No
6/04/2019 | 13:54:49 | SG10 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 90 | 0.00067051 | 7.45e-06 | No
6/04/2019 | 16:30:44 | PP04 | Rural Short | Third Party | Vehicle impact | 54 | 223 | 0.089715 | 0.00040231 | No
6/04/2019 | 16:38:19 | PP09 | Rural Long | Asset failure | LV | 1 | 346 | 0.0025252 | 7.3e-06 | No
7/04/2019 | 03:48:58 | AP214D | Urban | Asset failure | LV | 1 | 291 | 0.00046521 | 1.6e-06 | No
7/04/2019 | 05:05:02 | MTB51 | Rural Long | Third Party | Other | 1082 | 64 | 0.5054 | 0.0078968 | No
7/04/2019 | 05:14:59 | SD35500 | Rural Long | Planned |  | 3622 | 275 | 7.2695 | 0.026435 | No
7/04/2019 | 08:04:07 | HH177G | Urban | Asset failure | LV | 15 | 92 | 0.0022062 | 2.398e-05 | No
7/04/2019 | 08:42:24 | CBD353L | Urban | Planned |  | 53 | 225 | 0.019064 | 8.473e-05 | No
7/04/2019 | 08:42:46 | NL210C | Urban | Unknown | Unknown | 7 | 242 | 0.0027082 | 1.119e-05 | No
7/04/2019 | 08:47:52 | MI32 | Rural Long | Planned |  | 30 | 289 | 0.063277 | 0.00021895 | No
7/04/2019 | 09:27:59 | ST35 | Rural Long | Planned |  | 94 | 219.7234 | 0.15074 | 0.00068604 | No
7/04/2019 | 09:38:58 | GA15 | Rural Short | Vegetation | Grow-in - NSP responsibility | 2 | 149 | 0.0022201 | 1.49e-05 | No
7/04/2019 | 10:42:45 | NA56 | Rural Long | Asset failure | LV | 2 | 176 | 0.002569 | 1.46e-05 | No
7/04/2019 | 11:50:48 | PL07 | Urban | Asset failure | LV | 11.3333 | 126 | 0.0022829 | 1.812e-05 | No
7/04/2019 | 12:06:44 | HH386F | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
7/04/2019 | 15:55:47 | NA56 | Rural Long | Unknown | Unknown | 2 | 29 | 0.0004233 | 1.46e-05 | No
7/04/2019 | 16:29:26 | SM179C | Urban | Vegetation | Grow-in - NSP responsibility | 24.3333 | 153 | 0.0059519 | 3.89e-05 | No
7/04/2019 | 16:33:47 | MG32 | Rural Long | Other |  | 27 | 303 | 0.059708 | 0.00019706 | No
7/04/2019 | 18:35:21 | WK21 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 15 | 390 | 0.043583 | 0.00011175 | No
8/04/2019 | 02:33:41 | AP149D | Urban | Asset failure | LV | 33.6666 | 267 | 0.01437 | 5.382e-05 | No
8/04/2019 | 06:44:28 | SB16 | Rural Long | Unknown | Unknown | 18 | 184 | 0.024172 | 0.00013137 | No
8/04/2019 | 07:18:36 | CD01 | Rural Short | Asset failure | LV | 5 | 79 | 0.0029428 | 3.725e-05 | No
8/04/2019 | 08:23:05 | KI42 | Rural Long | Asset failure | HV | 201 | 35.9652 | 0.05276 | 0.001467 | No
8/04/2019 | 08:56:06 | MTB32 | Rural Long | Planned |  | 10 | 250 | 0.018246 | 7.298e-05 | No
8/04/2019 | 08:56:43 | WK33 | Rural Short | Planned |  | 9 | 341 | 0.022865 | 6.705e-05 | No
8/04/2019 | 09:22:15 | MV31 | Rural Short | Planned |  | 8 | 218 | 0.012993 | 5.96e-05 | No
8/04/2019 | 09:35:08 | GU118 | Rural Long | Planned |  | 1 | 36 | 0.00026274 | 7.3e-06 | No
8/04/2019 | 10:15:06 | GU17 | Rural Long | Planned |  | 1 | 21 | 0.00015327 | 7.3e-06 | No
8/04/2019 | 10:38:34 | PP03 | Urban | Asset failure | LV | 1 | 265 | 0.00042365 | 1.6e-06 | No
8/04/2019 | 10:42:32 | SD49500 | Rural Long | Asset failure | Subtransmission | 690 | 262 | 1.3194 | 0.0050358 | No
8/04/2019 | 10:51:02 | ST13 | Rural Short | Planned |  | 74 | 253 | 0.13948 | 0.00055131 | No
8/04/2019 | 11:40:33 | ST36 | Rural Long | Planned |  | 39 | 171 | 0.048673 | 0.00028464 | No
8/04/2019 | 12:13:53 | MTB61 | Rural Short | Planned |  | 1 | 151 | 0.001125 | 7.45e-06 | No
8/04/2019 | 13:16:32 | NL115E | Urban | Planned |  | 57 | 127 | 0.011573 | 9.112e-05 | No
8/04/2019 | 14:22:40 | GU18 | Rural Long | Unknown | Unknown | 31.6667 | 117 | 0.02704 | 0.00023111 | No
8/04/2019 | 14:30:00 | SM126C | Urban | Asset failure | LV | 1 | 337 | 0.00053875 | 1.6e-06 | No
8/04/2019 | 15:09:13 | NL234A | Urban | Overloads |  | 1 | 174 | 0.00027817 | 1.6e-06 | No
8/04/2019 | 16:53:25 | SM216A | Urban | Asset failure | HV | 19 | 148 | 0.0044955 | 3.037e-05 | No
8/04/2019 | 16:53:25 | SM216A | Urban | Planned |  | 2091 | 1 | 0.0033428 | 0.0033428 | No
8/04/2019 | 17:51:04 | CN03 | Rural Long | Asset failure | HV | 49 | 30 | 0.010729 | 0.00035762 | No
9/04/2019 | 02:24:13 | ME427D | Urban | Overloads |  | 3 | 129 | 0.00061869 | 4.8e-06 | No
9/04/2019 | 04:41:44 | LX71 | Rural Long | Unknown | Unknown | 10 | 402 | 0.029339 | 7.298e-05 | No
9/04/2019 | 05:21:22 | CBD412M | Urban | Unknown | Unknown | 40.6667 | 455 | 0.029581 | 6.501e-05 | No
9/04/2019 | 07:08:29 | BM53 | Rural Short | Unknown | Unknown | 5.3333 | 174 | 0.0069137 | 3.973e-05 | No
9/04/2019 | 08:24:51 | MV63 | Rural Short | Third Party | Vehicle impact | 1 | 188 | 0.0014006 | 7.45e-06 | No
9/04/2019 | 08:30:32 | VH17 | Rural Short | Planned |  | 2 | 428 | 0.0063773 | 1.49e-05 | No
9/04/2019 | 08:30:42 | NL21 | Urban | Planned |  | 1 | 4828 | 0.0077184 | 1.6e-06 | No
9/04/2019 | 08:33:08 | SD40200 | Rural Long | Animal | Animal impact | 112 | 109 | 0.089098 | 0.00081741 | No
9/04/2019 | 09:13:08 | MB34 | Rural Long | Planned |  | 45 | 211 | 0.069298 | 0.00032843 | No
9/04/2019 | 09:26:53 | AP529E | Urban | Planned |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
9/04/2019 | 09:31:46 | CV24 | Rural Long | Planned |  | 2 | 4 | 5.839e-05 | 1.46e-05 | No
9/04/2019 | 09:39:02 | MTB32 | Rural Long | Planned |  | 35 | 270 | 0.068969 | 0.00025544 | No
9/04/2019 | 09:48:46 | EL11 | Urban | Unknown | Unknown | 1 | 99 | 0.00015827 | 1.6e-06 | No
9/04/2019 | 09:50:12 | AP149H | Urban | Planned |  | 68 | 235 | 0.025547 | 0.00010871 | No
9/04/2019 | 10:03:33 | CV24 | Rural Long | Planned |  | 1 | 2 | 1.46e-05 | 7.3e-06 | No
9/04/2019 | 10:25:32 | MI10 | Rural Long | Planned |  | 48 | 283 | 0.099141 | 0.00035032 | No
9/04/2019 | 10:50:30 | EL20 | Urban | Planned |  | 58 | 78 | 0.0072324 | 9.272e-05 | No
9/04/2019 | 11:03:17 | PA15 | Rural Long | Planned |  | 3 | 2 | 4.379e-05 | 2.19e-05 | No
9/04/2019 | 11:09:58 | MG32 | Rural Long | Asset failure | LV | 4 | 24 | 0.00070064 | 2.919e-05 | No
9/04/2019 | 11:35:39 | SA41 | Urban | Planned |  | 4 | 10 | 6.395e-05 | 6.39e-06 | No
9/04/2019 | 11:42:10 | PA15 | Rural Long | Planned |  | 2 | 20 | 0.00029193 | 1.46e-05 | No
9/04/2019 | 11:57:28 | HH409D | Urban | Overloads |  | 1 | 271 | 0.00043324 | 1.6e-06 | No
9/04/2019 | 11:58:21 | HH341C | Urban | Unknown | Unknown | 84 | 387 | 0.05197 | 0.00013429 | No
9/04/2019 | 12:13:30 | LX71 | Rural Long | Unknown | Unknown | 2 | 148 | 0.0021603 | 1.46e-05 | No
9/04/2019 | 12:32:41 | GU31 | Rural Long | Third Party | Vehicle impact | 2 | 83 | 0.0012115 | 1.46e-05 | No
9/04/2019 | 13:49:30 | AP365D1 | Urban | Overloads |  | 2 | 1178 | 0.0037665 | 3.2e-06 | No
9/04/2019 | 14:26:39 | AP227D | Urban | Asset failure | HV | 17.6666 | 82 | 0.0023159 | 2.824e-05 | No
9/04/2019 | 15:14:42 | AP425B | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
9/04/2019 | 15:25:23 | GU21 | Rural Long | Asset failure | LV | 1 | 368 | 0.0026858 | 7.3e-06 | No
9/04/2019 | 16:21:00 | HH177E | Urban | Overloads |  | 1 | 92 | 0.00014708 | 1.6e-06 | No
9/04/2019 | 17:13:45 | ME200G | Urban | Other |  | 96 | 202 | 0.031002 | 0.00015347 | No
9/04/2019 | 17:24:01 | HH148A | Urban | Asset failure | LV | 17.3333 | 209 | 0.0057915 | 2.771e-05 | No
9/04/2019 | 17:37:46 | AP344E | Urban | Unknown | Unknown | 136 | 71 | 0.015437 | 0.00021742 | No
9/04/2019 | 18:15:59 | AP373E | Urban | Unknown | Unknown | 219 | 130.0822 | 0.045543 | 0.00035011 | No
9/04/2019 | 18:25:33 | MB93 | Rural Long | Unknown | Unknown | 29 | 204 | 0.043177 | 0.00021165 | No
9/04/2019 | 19:47:11 | PA02 | Urban | Asset failure | LV | 1 | 166 | 0.00026538 | 1.6e-06 | No
10/04/2019 | 01:43:06 | CM01 | Rural Long | Planned |  | 532 | 3 | 0.011648 | 0.0038827 | No
10/04/2019 | 08:11:30 | YK17 | Rural Long | Planned |  | 594 | 441 | 1.9118 | 0.0043352 | No
10/04/2019 | 08:22:31 | CN24 | Rural Long | Planned |  | 68 | 197 | 0.097769 | 0.00049629 | No
10/04/2019 | 08:29:04 | AP149F / AP424D | Urban | Planned |  | 101 | 549.3762 | 0.088706 | 0.00016147 | No
10/04/2019 | 08:50:07 | EL19 | Urban | Third Party | Other | 2 | 44 | 0.00014068 | 3.2e-06 | No
10/04/2019 | 08:56:14 | MTB51 | Rural Long | Planned |  | 5 | 339 | 0.012371 | 3.649e-05 | No
10/04/2019 | 08:56:36 | MTB41 | Rural Short | Planned |  | 20 | 483 | 0.071968 | 0.000149 | No
10/04/2019 | 09:02:28 | NA27 | Rural Long | Unknown | Unknown | 1 | 21 | 0.00015327 | 7.3e-06 | No
10/04/2019 | 09:13:02 | NL234C | Urban | Planned |  | 120 | 268 | 0.051413 | 0.00019184 | No
10/04/2019 | 09:30:12 | SB18 | Rural Long | Planned |  | 14 | 245 | 0.025033 | 0.00010218 | No
10/04/2019 | 09:34:03 | GU43 | Rural Long | Planned |  | 4 | 38 | 0.0011094 | 2.919e-05 | No
10/04/2019 | 09:44:23 | VH16 | Rural Short | Asset failure | LV | 1 | 317 | 0.0023617 | 7.45e-06 | No
10/04/2019 | 10:10:10 | MTB51 | Rural Long | Planned |  | 51 | 112 | 0.041688 | 0.00037222 | No
10/04/2019 | 10:26:41 | CM15 | Rural Long | Unknown | Unknown | 9 | 128 | 0.0084077 | 6.569e-05 | No
10/04/2019 | 10:30:11 | NL234B | Urban | Planned |  | 54 | 38 | 0.0032805 | 8.633e-05 | No
10/04/2019 | 11:53:51 | G41 | Rural Long | Planned |  | 89 | 271 | 0.17603 | 0.00064955 | No
10/04/2019 | 12:55:25 | WK33 | Rural Short | Asset failure | LV | 2 | 101 | 0.0015049 | 1.49e-05 | No
10/04/2019 | 13:51:25 | CN52 | Rural Long | Unknown | Unknown | 85 | 8 | 0.0049629 | 0.00062036 | No
10/04/2019 | 16:34:52 | SM410C | Urban | Asset failure | LV | 57.3333 | 90 | 0.0082492 | 9.166e-05 | No
10/04/2019 | 18:25:15 | AP424D | Urban | Planned |  | 46 | 45 | 0.0033093 | 7.354e-05 | No
10/04/2019 | 23:00:00 | CBD353A | CBD | Planned |  | 1 | 399 | 0.077453 | 0.00019412 | No
11/04/2019 | 07:49:45 | PA04 | Rural Short | Asset failure | LV | 1 | 91 | 0.00067796 | 7.45e-06 | No
11/04/2019 | 08:04:14 | ST22 | Rural Short | Asset failure | LV | 1.3333 | 336 | 0.0033377 | 9.93e-06 | No
11/04/2019 | 08:14:28 | AP373E | Urban | Unknown | Unknown | 2 | 176 | 0.00056273 | 3.2e-06 | No
11/04/2019 | 08:14:57 | AP373E | Urban | Unknown | Unknown | 1 | 158 | 0.00025259 | 1.6e-06 | No
11/04/2019 | 08:18:10 | G01 | Rural Long | Overloads |  | 1 | 96 | 0.00070064 | 7.3e-06 | No
11/04/2019 | 08:26:24 | KA04 | Rural Long | Planned |  | 69 | 325 | 0.16367 | 0.00050359 | No
11/04/2019 | 08:55:58 | WHY10 | Urban | Unknown | Unknown | 68 | 195 | 0.021198 | 0.00010871 | No
11/04/2019 | 09:04:54 | MB24 | Rural Short | Planned |  | 3 | 23 | 0.00051406 | 2.235e-05 | No
11/04/2019 | 09:09:04 | NL234C | Urban | Planned |  | 371 | 304 | 0.1803 | 0.00059311 | No
11/04/2019 | 09:19:53 | PL07 | Urban | Planned |  | 50 | 316 | 0.025259 | 7.993e-05 | No
11/04/2019 | 09:26:36 | ME200G | Urban | Planned |  | 96 | 265 | 0.04067 | 0.00015347 | No
11/04/2019 | 09:33:12 | EL19 | Urban | Planned |  | 178 | 291 | 0.082808 | 0.00028456 | No
11/04/2019 | 09:33:12 | EL19 | Urban | Planned |  | 2 | 307 | 0.00098159 | 3.2e-06 | No
11/04/2019 | 09:37:08 | SA17 | Urban | Planned |  | 102 | 229 | 0.037342 | 0.00016306 | No
11/04/2019 | 09:46:25 | HH102C | Urban | Planned |  | 3 | 204 | 0.00097839 | 4.8e-06 | No
11/04/2019 | 10:13:32 | W27 | Rural Long | Planned |  | 2 | 64 | 0.00093419 | 1.46e-05 | No
11/04/2019 | 10:19:35 | MTB13 | Rural Short | Planned |  | 2 | 79 | 0.0011771 | 1.49e-05 | No
11/04/2019 | 10:30:52 | AP132D | Urban | Planned |  | 244 | 360 | 0.14043 | 0.00039008 | No
11/04/2019 | 10:32:59 | SM216C | Urban | Planned |  | 406 | 125 | 0.081133 | 0.00064906 | No
11/04/2019 | 10:34:04 | BT02 | Rural Long | Unknown | Unknown | 8 | 179 | 0.010451 | 5.839e-05 | No
11/04/2019 | 10:40:02 | HH496F | Urban | Planned |  | 40 | 65 | 0.0041566 | 6.395e-05 | No
11/04/2019 | 10:40:02 | HH496F | Urban | Planned |  | 44 | 65 | 0.0045722 | 7.034e-05 | No
11/04/2019 | 10:49:27 | YK19 | Rural Long | Planned |  | 5 | 197 | 0.0071889 | 3.649e-05 | No
11/04/2019 | 10:54:58 | SD38200 | Rural Long | Planned |  | 2 | 37 | 0.00054008 | 1.46e-05 | No
11/04/2019 | 10:57:07 | HH177G | Urban | Overloads |  | 1 | 223 | 0.0003565 | 1.6e-06 | No
11/04/2019 | 11:10:21 | ST22 | Rural Short | Unknown | Unknown | 1 | 50 | 0.00037251 | 7.45e-06 | No
11/04/2019 | 11:31:29 | SA16 | Urban | Overloads |  | 1 | 127 | 0.00020303 | 1.6e-06 | No
11/04/2019 | 11:52:43 | SA18 | Urban | Planned |  | 50 | 167 | 0.013349 | 7.993e-05 | No
11/04/2019 | 12:14:34 | NL451C | Urban | Overloads |  | 1 | 119 | 0.00019024 | 1.6e-06 | No
11/04/2019 | 13:05:15 | SD38200 | Rural Long | Planned |  | 2 | 24 | 0.00035032 | 1.46e-05 | No
11/04/2019 | 13:24:03 | VH15 | Rural Short | Third Party | Dig-in | 2067 | 81.3561 | 1.2528 | 0.015399 | No
11/04/2019 | 14:08:31 | CV33 | Rural Long | Planned |  | 19 | 10 | 0.0013867 | 0.00013867 | No
11/04/2019 | 20:45:15 | AP529D | Urban | Asset failure | LV | 1 | 140 | 0.00022381 | 1.6e-06 | No
11/04/2019 | 23:03:29 | NL234D | Urban | Asset failure | LV | 1 | 133 | 0.00021262 | 1.6e-06 | No
12/04/2019 | 00:10:40 | HH403B | Urban | Asset failure | LV | 58 | 117 | 0.010849 | 9.272e-05 | No
12/04/2019 | 02:17:50 | HH428F | Urban | Asset failure | LV | 40 | 77 | 0.0049239 | 6.395e-05 | No
12/04/2019 | 05:02:22 | EL01Y | Urban | Asset failure | HV | 59 | 130.7119 | 0.012329 | 9.432e-05 | No
12/04/2019 | 06:16:02 | HH145D | Urban | Overloads |  | 1 | 279 | 0.00044603 | 1.6e-06 | No
12/04/2019 | 06:52:17 | SA13 | Urban | Planned |  | 62 | 1.5161 | 0.00015028 | 9.912e-05 | No
12/04/2019 | 07:36:07 | MV63 | Rural Short | Unknown | Unknown | 624 | 59.1218 | 0.27485 | 0.0046489 | No
12/04/2019 | 07:44:00 | GU31 | Rural Long | Third Party | Vehicle impact | 2 | 131 | 0.0019122 | 1.46e-05 | No
12/04/2019 | 08:27:06 | GU31 | Rural Long | Third Party | Vehicle impact | 4 | 324 | 0.0094587 | 2.919e-05 | No
12/04/2019 | 08:31:00 | ME427A | Urban | Asset failure | HV | 803 | 132.599 | 0.17022 | 0.0012837 | No
12/04/2019 | 08:55:12 | GA41 | Rural Long | Planned |  | 65 | 386 | 0.18312 | 0.00047439 | No
12/04/2019 | 08:55:55 | MTB22 | Rural Short | Planned |  | 132 | 372 | 0.36583 | 0.00098342 | No
12/04/2019 | 09:02:47 | CM03 | Rural Long | Planned |  | 7 | 96 | 0.0049045 | 5.109e-05 | No
12/04/2019 | 09:06:47 | YK23 | Rural Long | Planned |  | 7 | 249 | 0.012721 | 5.109e-05 | No
12/04/2019 | 09:07:01 | MTB32 | Rural Long | Planned |  | 1 | 100 | 0.00072983 | 7.3e-06 | No
12/04/2019 | 09:30:29 | BM43 | Rural Short | Planned |  | 33 | 129 | 0.031715 | 0.00024585 | No
12/04/2019 | 09:33:01 | AP149F | Urban | Planned |  | 71 | 376 | 0.042678 | 0.00011351 | No
12/04/2019 | 09:34:03 | MTB81 | Rural Short | Planned |  | 3 | 191 | 0.0042689 | 2.235e-05 | No
12/04/2019 | 09:52:01 | PP10 | Urban | Asset failure | LV | 1 | 707 | 0.0011303 | 1.6e-06 | No
12/04/2019 | 10:01:05 | M91 | Rural Long | Asset failure | LV | 1 | 235 | 0.0017151 | 7.3e-06 | No
12/04/2019 | 10:02:42 | CM16 | Rural Long | Planned |  | 3 | 120 | 0.0026274 | 2.19e-05 | No
12/04/2019 | 10:25:40 | AP139C | Urban | Asset failure | LV | 6.6667 | 264 | 0.0028137 | 1.066e-05 | No
12/04/2019 | 10:32:52 | CD03 | Rural Short | Planned |  | 1 | 22 | 0.0001639 | 7.45e-06 | No
12/04/2019 | 10:46:48 | AP149C | Urban | Asset failure | LV | 21.6666 | 339 | 0.011742 | 3.464e-05 | No
12/04/2019 | 10:47:18 | VH15 | Rural Short | Planned |  | 1 | 7310 | 0.054461 | 7.45e-06 | No
12/04/2019 | 11:12:58 | SB17 | Rural Long | Planned |  | 1 | 40 | 0.00029193 | 7.3e-06 | No
12/04/2019 | 11:20:00 | W26 | Rural Long | Planned |  | 2 | 25 | 0.00036492 | 1.46e-05 | No
12/04/2019 | 11:27:24 | SM374A | Urban | Planned |  | 191 | 248 | 0.075726 | 0.00030535 | No
12/04/2019 | 12:25:29 | EL07 | Urban | Asset failure | LV | 1 | 152 | 0.000243 | 1.6e-06 | No
12/04/2019 | 12:46:23 | GA09 | Rural Long | Planned |  | 1 | 140 | 0.0010218 | 7.3e-06 | No
12/04/2019 | 13:30:21 | CM15 | Rural Long | Asset failure | HV | 1 | 20 | 0.00014597 | 7.3e-06 | No
12/04/2019 | 13:49:29 | CL12 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 93 | 0.0013575 | 1.46e-05 | No
12/04/2019 | 14:12:43 | HH107D | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
12/04/2019 | 20:14:47 | SM216C | Urban | Unknown | Unknown | 9 | 344 | 0.0049495 | 1.439e-05 | No
13/04/2019 | 07:31:48 | AP373J | Urban | Planned |  | 1 | 199 | 0.00031814 | 1.6e-06 | No
13/04/2019 | 08:43:46 | MI17 | Rural Long | Planned |  | 25 | 169 | 0.030835 | 0.00018246 | No
13/04/2019 | 11:06:07 | VH21 | Rural Short | Asset failure | LV | 22.6666 | 23 | 0.003884 | 0.00016887 | No
13/04/2019 | 11:44:09 | SM126C | Urban | Third Party | Other | 177 | 141 | 0.039898 | 0.00028297 | No
13/04/2019 | 19:16:38 | NL234A | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | No
13/04/2019 | 21:49:46 | HH121G | Urban | Animal | Animal impact | 940 | 55 | 0.082652 | 0.0015027 | No
14/04/2019 | 05:05:10 | MV12 / MV15 | Urban | Planned |  | 125 | 278 | 0.055554 | 0.00019983 | No
14/04/2019 | 05:05:10 | MV12 / MV15 | Rural Short | Planned |  | 43 | 271 | 0.086817 | 0.00032036 | No
14/04/2019 | 06:06:21 | M21 | Rural Long | Asset failure | HV | 397 | 430.2015 | 1.2465 | 0.0028974 | No
14/04/2019 | 06:21:14 | MV52 | Rural Short | Planned |  | 170 | 124 | 0.15705 | 0.0012665 | No
14/04/2019 | 06:36:38 | AP132E | Urban | Animal | Animal impact | 82 | 151.5366 | 0.019865 | 0.00013109 | No
14/04/2019 | 06:58:16 | HH177C | Urban | Planned |  | 27 | 81 | 0.0034963 | 4.316e-05 | No
14/04/2019 | 07:02:30 | AP425A | Urban | Other |  | 29 | 169 | 0.0078351 | 4.636e-05 | No
14/04/2019 | 07:59:24 | SM410A / SM410B | Urban | Planned |  | 183 | 156.8197 | 0.045879 | 0.00029256 | No
14/04/2019 | 08:10:26 | AP373B | Urban | Planned |  | 10 | 364 | 0.0058192 | 1.599e-05 | No
14/04/2019 | 08:33:43 | SD48100 | Rural Short | Planned |  | 389 | 373 | 1.081 | 0.0028981 | No
14/04/2019 | 08:33:43 | SD48100 | Rural Long | Planned |  | 17 | 376 | 0.046651 | 0.00012407 | No
14/04/2019 | 08:40:51 | HH148A | Urban | Planned |  | 16 | 363 | 0.0092851 | 2.558e-05 | No
14/04/2019 | 08:53:57 | HH130C | Urban | Planned |  | 1 | 446 | 0.00071301 | 1.6e-06 | No
14/04/2019 | 09:20:15 | WHY03 | Urban | Unknown | Unknown | 12.3333 | 117 | 0.0023069 | 1.972e-05 | No
14/04/2019 | 10:35:27 | ST44 | Rural Long | Unknown | Unknown | 3 | 299 | 0.0065466 | 2.19e-05 | No
14/04/2019 | 11:06:09 | HH177E | Urban | Planned |  | 222 | 211 | 0.074885 | 0.00035491 | No
14/04/2019 | 12:07:30 | GU13 | Rural Long | Planned |  | 29 | 1 | 0.00021165 | 0.00021165 | No
14/04/2019 | 15:01:46 | MG06 | Rural Short | Unknown | Unknown | 306.0001 | 101 | 0.23025 | 0.0022798 | No
14/04/2019 | 15:43:22 | WK72 | Rural Short | Unknown | Unknown | 575 | 191.5217 | 0.82045 | 0.0042838 | No
14/04/2019 | 16:50:19 | HH121B | Urban | Asset failure | LV | 4.6667 | 140 | 0.0010445 | 7.46e-06 | No
14/04/2019 | 21:05:05 | HH177E | Urban | Asset failure | LV | 31.6666 | 100 | 0.0050625 | 5.062e-05 | No
14/04/2019 | 22:49:30 | NL511C / NL511D | Urban | Planned |  | 1 | 397 | 0.00063467 | 1.6e-06 | No
14/04/2019 | 22:49:30 | NL511C / NL511D | Urban | Planned |  | 3 | 150 | 0.0007194 | 4.8e-06 | No
15/04/2019 | 04:24:37 | SM350B | Urban | Animal | Animal impact | 1 | 188 | 0.00030055 | 1.6e-06 | No
15/04/2019 | 05:50:25 | ME200G | Urban | Planned |  | 274 | 78 | 0.034167 | 0.00043804 | No
15/04/2019 | 05:59:58 | SM350B | Urban | Animal | Animal impact | 1 | 3 | 4.8e-06 | 1.6e-06 | No
15/04/2019 | 06:13:27 | MV42 | Rural Short | Animal | Animal impact | 2 | 391 | 0.005826 | 1.49e-05 | No
15/04/2019 | 08:00:24 | W19 | Rural Long | Asset failure | HV | 9 | 275 | 0.018063 | 6.569e-05 | No
15/04/2019 | 08:28:46 | MV52 | Rural Short | Planned |  | 36 | 229 | 0.061419 | 0.00026821 | No
15/04/2019 | 08:56:46 | AP529B | Urban | Planned |  | 53 | 93 | 0.0078799 | 8.473e-05 | No
15/04/2019 | 09:09:03 | EL23 | Urban | Planned |  | 70 | 37 | 0.0041406 | 0.00011191 | No
15/04/2019 | 09:16:04 | SD38200 | Rural Long | Planned |  | 8 | 330 | 0.019268 | 5.839e-05 | No
15/04/2019 | 09:17:26 | MV13 | Rural Short | Planned |  | 247 | 141.166 | 0.25977 | 0.0018402 | No
15/04/2019 | 09:17:52 | HH148B | Urban | Planned |  | 1 | 50 | 7.993e-05 | 1.6e-06 | No
15/04/2019 | 09:31:04 | HH341D | Urban | Planned |  | 72 | 198 | 0.022791 | 0.0001151 | No
15/04/2019 | 09:31:17 | MTB51 | Rural Long | Planned |  | 437 | 288 | 0.91854 | 0.0031894 | No
15/04/2019 | 09:42:56 | CM12 | Rural Long | Asset failure | HV | 18 | 84 | 0.011035 | 0.00013137 | No
15/04/2019 | 09:46:34 | CM15 | Rural Long | Unknown | Unknown | 7 | 87 | 0.0044447 | 5.109e-05 | No
15/04/2019 | 09:55:30 | AP227D | Urban | Planned |  | 405 | 234 | 0.15151 | 0.00064746 | No
15/04/2019 | 09:56:09 | NL111C | Urban | Planned |  | 116 | 320 | 0.059343 | 0.00018545 | No
15/04/2019 | 09:57:59 | CL09 | Rural Long | Planned |  | 2 | 45 | 0.00065685 | 1.46e-05 | No
15/04/2019 | 10:16:35 | VH18 | Rural Short | Unknown | Unknown | 23.3333 | 31 | 0.0053889 | 0.00017384 | No
15/04/2019 | 10:17:48 | AP227B | Urban | Planned |  | 1 | 64 | 0.00010232 | 1.6e-06 | No
15/04/2019 | 10:23:55 | HH432F | Urban | Asset failure | LV | 3 | 130 | 0.00062348 | 4.8e-06 | No
15/04/2019 | 10:40:19 | G14 | Rural Long | Planned |  | 17 | 150 | 0.018611 | 0.00012407 | No
15/04/2019 | 10:41:16 | HH432F | Urban | Asset failure | LV | 1 | 112 | 0.00017905 | 1.6e-06 | No
15/04/2019 | 10:52:59 | HH148B | Urban | Planned |  | 1 | 37 | 5.915e-05 | 1.6e-06 | No
15/04/2019 | 10:57:29 | AP149E | Urban | Planned |  | 266 | 35 | 0.014884 | 0.00042525 | No
15/04/2019 | 10:57:41 | MI02 | Rural Short | Asset failure | LV | 54 | 102 | 0.041035 | 0.00040231 | No
15/04/2019 | 11:37:56 | BM57 | Rural Short | Unknown | Unknown | 91 | 12 | 0.0081356 | 0.00067796 | No
15/04/2019 | 11:38:50 | CL05 | Rural Long | Planned |  | 4 | 30 | 0.0008758 | 2.919e-05 | No
15/04/2019 | 12:38:05 | CM11 | Rural Long | Asset failure | HV | 1 | 12 | 8.758e-05 | 7.3e-06 | No
15/04/2019 | 16:37:01 | M91 | Rural Long | Asset failure | LV | 3 | 144 | 0.0031529 | 2.189e-05 | No
15/04/2019 | 19:42:32 | GA745A | Rural Short | Overloads |  | 1 | 170 | 0.0012665 | 7.45e-06 | No
15/04/2019 | 20:38:46 | MG34 | Rural Long | Unknown | Unknown | 21 | 31 | 0.0047512 | 0.00015327 | No
16/04/2019 | 08:23:52 | HH130A | Urban | Planned |  | 71 | 20 | 0.0022701 | 0.00011351 | No
16/04/2019 | 08:45:14 | MG48 | Rural Long | Planned |  | 99 | 237 | 0.17124 | 0.00072254 | No
16/04/2019 | 08:52:56 | PA02 | Urban | Planned |  | 75 | 341 | 0.040886 | 0.0001199 | No
16/04/2019 | 09:08:26 | AP373K | Urban | Asset failure | LV | 1 | 202 | 0.00032293 | 1.6e-06 | No
16/04/2019 | 09:09:10 | GA15 | Rural Short | Planned |  | 25 | 103 | 0.019184 | 0.00018625 | No
16/04/2019 | 09:13:46 | HH428A | Urban | Planned |  | 73 | 418 | 0.048782 | 0.0001167 | No
16/04/2019 | 09:17:54 | GU17 | Rural Long | Planned |  | 153 | 289 | 0.32271 | 0.0011167 | No
16/04/2019 | 09:21:21 | EL11 | Urban | Planned |  | 42 | 369 | 0.024776 | 6.714e-05 | No
16/04/2019 | 09:27:05 | AP226D | Urban | Planned |  | 1 | 51 | 8.153e-05 | 1.6e-06 | No
16/04/2019 | 09:30:15 | VH45 | Rural Short | Planned |  | 134 | 398 | 0.39733 | 0.00099832 | No
16/04/2019 | 09:32:33 | AP149E | Urban | Planned |  | 106 | 435 | 0.073715 | 0.00016946 | No
16/04/2019 | 09:38:19 | CN33 | Rural Long | Planned |  | 14 | 188 | 0.019209 | 0.00010218 | No
16/04/2019 | 09:39:13 | LM41 | Rural Long | Planned |  | 475 | 18 | 0.062401 | 0.0034667 | No
16/04/2019 | 09:40:29 | MTB32 | Rural Long | Planned |  | 122 | 298 | 0.26534 | 0.0008904 | No
16/04/2019 | 09:53:22 | MV41 | Rural Short | Unknown | Unknown | 1 | 146 | 0.0010877 | 7.45e-06 | No
16/04/2019 | 09:57:33 | MV41 | Rural Short | Unknown | Unknown | 1 | 141 | 0.0010505 | 7.45e-06 | No
16/04/2019 | 10:05:11 | CM16 | Rural Long | Asset failure | HV | 26 | 114 | 0.021632 | 0.00018976 | No
16/04/2019 | 11:06:13 | EL15 | Urban | Unknown | Unknown | 297.0001 | 1.3131 | 0.00062348 | 0.00047481 | No
16/04/2019 | 11:06:50 | SM172F | Urban | Planned |  | 166 | 70 | 0.018577 | 0.00026538 | No
16/04/2019 | 11:20:13 | MB01 | Rural Long | Unknown | Unknown | 1 | 122 | 0.0008904 | 7.3e-06 | No
16/04/2019 | 11:57:38 | EL23 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 142 | 0.00022701 | 1.6e-06 | No
16/04/2019 | 13:31:58 | NL511A | Urban | Asset failure | LV | 66 | 70 | 0.0073859 | 0.00010551 | No
16/04/2019 | 13:54:16 | PA02 | Urban | Planned |  | 9 | 1125 | 0.016187 | 1.439e-05 | No
16/04/2019 | 14:05:22 | EL15 | Urban | Unknown | Unknown | 1.3333 | 53 | 0.00011297 | 2.13e-06 | No
16/04/2019 | 14:26:40 | CL08 | Rural Long | Asset failure | HV | 2 | 26 | 0.00037951 | 1.46e-05 | No
16/04/2019 | 15:00:21 | WK51 | Rural Short | Unknown | Unknown | 1 | 365 | 0.0027193 | 7.45e-06 | No
16/04/2019 | 15:38:00 | GA34 | Rural Short | Third Party | Other | 44 | 169.5 | 0.055563 | 0.00032781 | No
16/04/2019 | 15:58:33 | HH145D | Urban | Overloads |  | 1.3333 | 136 | 0.00028989 | 2.13e-06 | No
16/04/2019 | 17:57:28 | SG12 | Rural Short | Asset failure | LV | 2 | 401 | 0.005975 | 1.49e-05 | No
16/04/2019 | 18:17:13 | SM374E | Urban | Asset failure | LV | 1 | 195 | 0.00031174 | 1.6e-06 | No
16/04/2019 | 20:08:36 | SB23 | Rural Long | Asset failure | HV | 57 | 189.7368 | 0.078932 | 0.00041601 | No
16/04/2019 | 20:24:46 | CBD412S | Urban | Planned |  | 156 | 429 | 0.10699 | 0.00024939 | No
16/04/2019 | 20:29:19 | HH107A | Urban | Asset failure | LV | 23 | 21 | 0.00077216 | 3.677e-05 | No
16/04/2019 | 23:10:09 | HH130B | Urban | Planned |  | 10 | 244 | 0.0039008 | 1.599e-05 | No
17/04/2019 | 03:18:27 | SD46200 | Rural Long | Animal | Animal impact | 403.6665 | 109.1338 | 0.32152 | 0.0029461 | No
17/04/2019 | 06:09:26 | MG06 | Rural Short | Unknown | Unknown | 377 | 84 | 0.23593 | 0.0028087 | No
17/04/2019 | 06:13:56 | MG06 | Rural Short | Unknown | Unknown | 377 | 307.3687 | 0.86331 | 0.0028087 | No
17/04/2019 | 06:20:28 | MTB41 | Rural Short | Unknown | Unknown | 41 | 171 | 0.052233 | 0.00030546 | No
17/04/2019 | 08:21:10 | SD37102 | Rural Long | Planned |  | 17 | 385.3529 | 0.047811 | 0.00012407 | No
17/04/2019 | 08:50:00 | PL14 | Urban | Planned |  | 99 | 28.1818 | 0.0044603 | 0.00015827 | No
17/04/2019 | 08:50:00 | PL14 | Urban | Planned |  | 2 | 317 | 0.0010136 | 3.2e-06 | No
17/04/2019 | 08:54:25 | NL111C | Urban | Planned |  | 57 | 310 | 0.028249 | 9.112e-05 | No
17/04/2019 | 09:00:42 | SM179C | Urban | Asset failure | LV | 1 | 54 | 8.633e-05 | 1.6e-06 | No
17/04/2019 | 09:03:45 | SM179C | Urban | Asset failure | LV | 1 | 50 | 7.993e-05 | 1.6e-06 | No
17/04/2019 | 09:06:12 | WHY04 | Urban | Planned |  | 34 | 103 | 0.0055986 | 5.435e-05 | No
17/04/2019 | 09:14:22 | SG03 | Rural Short | Planned |  | 84 | 339 | 0.21215 | 0.00062581 | No
17/04/2019 | 09:16:43 | MTB10 | Urban | Planned |  | 46 | 178 | 0.01309 | 7.354e-05 | No
17/04/2019 | 09:21:51 | MTB81 | Rural Short | Planned |  | 120 | 194 | 0.17344 | 0.00089402 | No
17/04/2019 | 09:29:08 | SG03 | Rural Short | Planned |  | 1 | 399 | 0.0029726 | 7.45e-06 | No
17/04/2019 | 09:32:19 | SA17 | Urban | Planned |  | 180 | 339 | 0.097551 | 0.00028776 | No
17/04/2019 | 09:35:55 | PA02 | Urban | Planned |  | 37 | 213.5676 | 0.012633 | 5.915e-05 | No
17/04/2019 | 09:51:03 | AP227A | Urban | Asset failure | LV | 1 | 175 | 0.00027977 | 1.6e-06 | No
17/04/2019 | 09:58:09 | SG07 | Rural Short | Planned |  | 1 | 20 | 0.000149 | 7.45e-06 | No
17/04/2019 | 10:15:47 | MTB14 | Rural Short | Planned |  | 45 | 235 | 0.078785 | 0.00033526 | No
17/04/2019 | 10:25:37 | MV33 | Rural Short | Planned |  | 15 | 176 | 0.019668 | 0.00011175 | No
17/04/2019 | 11:06:18 | HH148B | Urban | Planned |  | 74 | 162 | 0.019165 | 0.0001183 | No
17/04/2019 | 11:36:26 | SG14 | Rural Short | Planned |  | 46 | 150 | 0.051406 | 0.00034271 | No
17/04/2019 | 12:10:42 | SA16 | Urban | Unknown | Unknown | 19 | 166 | 0.0050422 | 3.037e-05 | No
17/04/2019 | 13:38:14 | NL21 | Urban | Asset failure | LV | 1 | 147 | 0.00023501 | 1.6e-06 | No
17/04/2019 | 13:47:57 | CL06 | Rural Long | Asset failure | HV | 2 | 42 | 0.00061306 | 1.46e-05 | No
17/04/2019 | 17:57:32 | NU19 | Rural Long | Unknown | Unknown | 1 | 122 | 0.0008904 | 7.3e-06 | No
17/04/2019 | 19:48:31 | NA01 | Rural Long | Overloads |  | 1 | 791 | 0.005773 | 7.3e-06 | No
17/04/2019 | 19:50:57 | GU13 | Rural Long | Unknown | Unknown | 29 | 35 | 0.0074078 | 0.00021165 | No
17/04/2019 | 22:18:27 | SM350E | Urban | Asset failure | LV | 26.6666 | 55 | 0.0023447 | 4.263e-05 | No
18/04/2019 | 08:30:29 | KI22 | Rural Long | Planned |  | 16 | 241 | 0.028142 | 0.00011677 | No
18/04/2019 | 08:34:15 | AP125D | Urban | Planned |  | 80 | 71 | 0.0090805 | 0.00012789 | No
18/04/2019 | 08:40:33 | AP424D | Urban | Asset failure | LV | 2 | 285 | 0.00091124 | 3.2e-06 | No
18/04/2019 | 08:41:45 | VH18 | Rural Short | Planned |  | 6 | 288 | 0.012874 | 4.47e-05 | No
18/04/2019 | 08:44:52 | PA14 | Rural Long | Planned |  | 32 | 8 | 0.0018684 | 0.00023355 | No
18/04/2019 | 08:45:42 | CV33 | Rural Long | Unknown | Unknown | 40 | 113 | 0.032988 | 0.00029193 | No
18/04/2019 | 08:46:24 | NA13 | Rural Long | Planned |  | 4 | 25 | 0.00072983 | 2.919e-05 | No
18/04/2019 | 09:05:35 | MTB22 | Rural Short | Planned |  | 19 | 164 | 0.023215 | 0.00014155 | No
18/04/2019 | 09:14:12 | ST35 | Rural Long | Planned |  | 46 | 120 | 0.040287 | 0.00033572 | No
18/04/2019 | 09:14:37 | SA17 | Urban | Planned |  | 8 | 104 | 0.0013301 | 1.279e-05 | No
18/04/2019 | 09:23:19 | HH130B | Urban | Planned |  | 176 | 130 | 0.036578 | 0.00028137 | No
18/04/2019 | 09:26:18 | SM411D | Urban | Overloads |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
18/04/2019 | 09:28:43 | NL760C | Urban | Planned |  | 72 | 284 | 0.03269 | 0.0001151 | No
18/04/2019 | 09:28:44 | ST12 | Rural Short | Planned |  | 2 | 108 | 0.0016092 | 1.49e-05 | No
18/04/2019 | 09:34:15 | ST36 | Rural Long | Planned |  | 55 | 122 | 0.048972 | 0.00040141 | No
18/04/2019 | 09:34:43 | CBD103C | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
18/04/2019 | 09:52:35 | SM410C | Urban | Planned |  | 200 | 354 | 0.11319 | 0.00031974 | No
18/04/2019 | 09:53:45 | SM216C | Urban | Planned |  | 157 | 29 | 0.0072788 | 0.00025099 | No
18/04/2019 | 09:55:23 | CD18 | Rural Long | Planned |  | 40 | 294 | 0.085828 | 0.00029193 | No
18/04/2019 | 10:15:46 | GU13 | Rural Long | Unknown | Unknown | 29 | 141 | 0.029843 | 0.00021165 | No
18/04/2019 | 10:31:33 | GU17 | Rural Long | Asset failure | HV | 6 | 262 | 0.011473 | 4.379e-05 | No
18/04/2019 | 10:32:56 | MTB52 | Rural Long | Planned |  | 69 | 145 | 0.07302 | 0.00050359 | No
18/04/2019 | 10:35:12 | SB18 | Rural Long | Planned |  | 2 | 73 | 0.0010656 | 1.46e-05 | No
18/04/2019 | 10:43:00 | CM16 | Rural Long | Unknown | Unknown | 13 | 166 | 0.01575 | 9.488e-05 | No
18/04/2019 | 10:48:27 | AP125D | Urban | Planned |  | 169 | 166 | 0.044849 | 0.00027018 | No
18/04/2019 | 10:50:32 | CM15 | Rural Long | Unknown | Unknown | 2 | 74 | 0.0010801 | 1.46e-05 | No
18/04/2019 | 12:24:50 | NA32 | Rural Long | Asset failure | HV | 31.6667 | 77 | 0.017796 | 0.00023111 | No
18/04/2019 | 12:50:41 | WK65 | Rural Short | Unknown | Unknown | 1 | 241 | 0.0017955 | 7.45e-06 | No
18/04/2019 | 13:36:11 | EL01P | Urban | Asset failure | HV | 538 | 57.0725 | 0.049087 | 0.00086009 | No
18/04/2019 | 14:00:44 | SD34400 | Rural Long | Unknown | Unknown | 1 | 1 | 7.3e-06 | 7.3e-06 | No
18/04/2019 | 15:30:00 | PL14 | Urban | Planned |  | 2 | 130 | 0.00041566 | 3.2e-06 | No
18/04/2019 | 16:21:42 | SD46201 | Rural Long | Planned |  | 667 | 11 | 0.053548 | 0.004868 | No
18/04/2019 | 17:31:29 | VH18 | Rural Short | Unknown | Unknown | 28 | 66 | 0.013768 | 0.0002086 | No
18/04/2019 | 20:11:59 | VH22 | Rural Short | Unknown | Unknown | 1 | 884 | 0.0065859 | 7.45e-06 | No
18/04/2019 | 20:38:55 | HH118C | Urban | Asset failure | LV | 8.6667 | 210 | 0.0029096 | 1.386e-05 | No
19/04/2019 | 03:19:07 | VH12 | Rural Short | Asset failure | LV | 21.3333 | 297 | 0.047204 | 0.00015894 | No
19/04/2019 | 06:47:40 | ME200A | Urban | Planned |  | 5 | 2004 | 0.016019 | 7.99e-06 | No
19/04/2019 | 08:31:13 | WK65 | Rural Short | Animal | Animal impact | 3.6667 | 401 | 0.010954 | 2.732e-05 | No
19/04/2019 | 10:50:14 | HH341G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 364 | 70 | 0.040734 | 0.00058192 | No
19/04/2019 | 11:37:55 | GA17 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 178 | 0.0012991 | 7.3e-06 | No
19/04/2019 | 12:17:27 | GU33 | Rural Long | Asset failure | HV | 1 | 22 | 0.00016056 | 7.3e-06 | No
19/04/2019 | 20:17:02 | HH121F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 22.6666 | 66 | 0.0023916 | 3.624e-05 | No
19/04/2019 | 22:14:21 | MG17 | Rural Long | Asset failure | LV | 19.6666 | 108 | 0.015502 | 0.00014353 | No
20/04/2019 | 02:49:00 | NL111C | Urban | Asset failure | LV | 1 | 298 | 0.00047641 | 1.6e-06 | No
20/04/2019 | 10:28:41 | R04 | Rural Long | Asset failure | LV | 1 | 281 | 0.0020508 | 7.3e-06 | No
20/04/2019 | 11:22:51 | EL15 | Urban | Vegetation | Grow-in - NSP responsibility | 1.3333 | 204 | 0.00043484 | 2.13e-06 | No
20/04/2019 | 11:44:16 | BM33 | Rural Short | Asset failure | LV | 1 | 123 | 0.00091637 | 7.45e-06 | No
20/04/2019 | 15:19:04 | MI02 | Rural Short | Unknown | Unknown | 1 | 5 | 3.725e-05 | 7.45e-06 | No
20/04/2019 | 16:23:27 | VH21 | Rural Short | Asset failure | LV | 17.6666 | 292 | 0.038433 | 0.00013162 | No
20/04/2019 | 16:58:43 | LM54 | Rural Long | Unknown | Unknown | 3 | 12 | 0.00026274 | 2.19e-05 | No
20/04/2019 | 17:58:51 | SB23 | Rural Long | Unknown | Unknown | 1 | 398 | 0.0029047 | 7.3e-06 | No
20/04/2019 | 18:33:42 | ST23 | Rural Short | Unknown | Unknown | 19 | 164 | 0.023215 | 0.00014155 | No
20/04/2019 | 18:55:04 | SA711C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 19.6666 | 73 | 0.0022952 | 3.144e-05 | No
20/04/2019 | 19:46:17 | AP424E | Urban | Asset failure | LV | 18 | 78 | 0.0022445 | 2.878e-05 | No
20/04/2019 | 21:58:21 | EL01A | Urban | Asset failure | LV | 1 | 91 | 0.00014548 | 1.6e-06 | No
20/04/2019 | 22:13:00 | CV16 | Rural Long | Asset failure | HV | 13 | 959 | 0.090988 | 9.488e-05 | No
20/04/2019 | 22:13:00 | CV16 | Rural Long | Asset failure | HV | 11 | 319 | 0.02561 | 8.028e-05 | No
20/04/2019 | 22:15:50 | CM12 | Rural Long | Unknown | Unknown | 14 | 303 | 0.03096 | 0.00010218 | No
21/04/2019 | 00:27:16 | NU05 | Rural Short | Unknown | Unknown | 2 | 436 | 0.0064965 | 1.49e-05 | No
21/04/2019 | 00:49:04 | KI44 | Rural Long | Unknown | Unknown | 44 | 121 | 0.038856 | 0.00032113 | No
21/04/2019 | 04:58:13 | KI44 | Rural Long | Unknown | Unknown | 44 | 309 | 0.099228 | 0.00032113 | No
21/04/2019 | 07:11:01 | MB23 | Rural Short | Third Party | Vehicle impact | 25 | 273 | 0.050847 | 0.00018625 | No
21/04/2019 | 09:26:06 | KA28 | Rural Long | Unknown | Unknown | 66 | 95.5 | 0.046001 | 0.00048169 | No
21/04/2019 | 09:42:04 | NL111C | Urban | Asset failure | LV | 1 | 127 | 0.00020303 | 1.6e-06 | No
21/04/2019 | 09:52:24 | HH428D | Urban | Asset failure | LV | 80 | 29 | 0.0037089 | 0.00012789 | No
21/04/2019 | 10:07:59 | MB03 | Rural Long | Unknown | Unknown | 32 | 231.5 | 0.054066 | 0.00023355 | No
21/04/2019 | 11:02:47 | R07 | Rural Short | Weather |  | 104 | 255 | 0.19758 | 0.00077482 | No
21/04/2019 | 12:16:19 | MV15 | Rural Short | Asset failure | LV | 66 | 100 | 0.049171 | 0.00049171 | No
21/04/2019 | 14:43:00 | MI08 | Rural Long | Third Party | Other | 1 | 290 | 0.0021165 | 7.3e-06 | No
21/04/2019 | 14:46:01 | CL24 | Rural Long | Unknown | Unknown | 49 | 180.3469 | 0.064495 | 0.00035762 | No
21/04/2019 | 15:54:42 | G25 | Rural Long | Unknown | Unknown | 30 | 848.9667 | 0.18588 | 0.00021895 | No
21/04/2019 | 16:47:40 | HH496A | Urban | Third Party | Other | 1 | 52 | 8.313e-05 | 1.6e-06 | No
21/04/2019 | 16:54:52 | NL234A | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
21/04/2019 | 16:59:17 | G41 | Rural Long | Overloads |  | 2 | 114 | 0.001664 | 1.46e-05 | No
21/04/2019 | 20:56:07 | KI44 | Rural Long | Asset failure | HV | 91 | 202.2967 | 0.13436 | 0.00066415 | No
21/04/2019 | 20:56:07 | KI44 | Rural Long | Asset failure | HV | 0 | 358.0857 | 0.18294 | 0 | No
22/04/2019 | 01:44:38 | HH341E | Urban | Vegetation | Grow-in - NSP responsibility | 30.6666 | 150 | 0.0073539 | 4.903e-05 | No
22/04/2019 | 07:22:16 | GA745C | Rural Short | Unknown | Unknown | 455 | 107 | 0.36271 | 0.0033898 | No
22/04/2019 | 09:09:09 | MG17 | Rural Long | Asset failure | Distribution substation | 80 | 69 | 0.040287 | 0.00058387 | No
22/04/2019 | 14:33:11 | GA40 | Rural Short | Unknown | Unknown | 51 | 224 | 0.085111 | 0.00037996 | No
22/04/2019 | 15:57:34 | HH145A | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 110 | 0.00017585 | 1.6e-06 | No
22/04/2019 | 19:32:00 | MT09 | Rural Long | Asset failure | HV | 9 | 215.4444 | 0.014151 | 6.569e-05 | No
22/04/2019 | 19:43:00 | WK72 | Rural Short | Asset failure | LV | 1 | 127 | 0.00094617 | 7.45e-06 | No
22/04/2019 | 21:46:22 | AP227D | Urban | Asset failure | LV | 32 | 69 | 0.0035299 | 5.116e-05 | No
22/04/2019 | 23:26:03 | SA17 | Urban | Asset failure | LV | 1 | 165 | 0.00026378 | 1.6e-06 | No
23/04/2019 | 00:05:46 | GU13 | Rural Long | Unknown | Unknown | 29 | 211 | 0.044659 | 0.00021165 | No
23/04/2019 | 07:29:44 | SM126E | Urban | Asset failure | LV | 1 | 178 | 0.00028456 | 1.6e-06 | No
23/04/2019 | 08:59:17 | MG32 | Rural Long | Planned |  | 35 | 181 | 0.046235 | 0.00025544 | No
23/04/2019 | 09:09:06 | SD37102 | Rural Long | Planned |  | 15 | 227 | 0.024851 | 0.00010948 | No
23/04/2019 | 09:09:20 | GA15 | Rural Short | Planned |  | 6 | 307 | 0.013723 | 4.47e-05 | No
23/04/2019 | 09:16:12 | SM350F | Urban | Planned |  | 34 | 25 | 0.0013589 | 5.435e-05 | No
23/04/2019 | 09:25:03 | GA03 | Rural Long | Planned |  | 5 | 274 | 0.0099987 | 3.649e-05 | No
23/04/2019 | 09:28:03 | AP125A | Urban | Planned |  | 86 | 162.0233 | 0.022276 | 0.00013749 | No
23/04/2019 | 09:28:03 | AP125A | Urban | Planned |  | 0 | 27 | 0.00341 | 0 | No
23/04/2019 | 09:49:06 | EL12 | Urban | Planned |  | 13 | 309 | 0.0064219 | 2.078e-05 | No
23/04/2019 | 09:51:01 | PA01 | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
23/04/2019 | 09:51:32 | MV33 | Rural Short | Planned |  | 8 | 233 | 0.013887 | 5.96e-05 | No
23/04/2019 | 09:59:20 | PP15 | Rural Long | Planned |  | 1 | 112 | 0.00081741 | 7.3e-06 | No
23/04/2019 | 10:03:26 | CV757A | Rural Long | Planned |  | 44 | 240 | 0.07707 | 0.00032113 | No
23/04/2019 | 10:20:14 | MB43 | Rural Long | Planned |  | 1 | 45 | 0.00032843 | 7.3e-06 | No
23/04/2019 | 10:29:14 | CD23 | Rural Long | Planned |  | 38 | 216 | 0.059905 | 0.00027734 | No
23/04/2019 | 10:40:44 | HH522C | Urban | Planned |  | 144 | 217 | 0.049955 | 0.00023021 | No
23/04/2019 | 10:49:23 | HH522C | Urban | Planned |  | 1 | 81 | 0.00012949 | 1.6e-06 | No
23/04/2019 | 11:07:37 | SG07 | Rural Short | Planned |  | 10 | 18 | 0.001341 | 7.45e-05 | No
23/04/2019 | 11:20:10 | SB18 | Rural Long | Planned |  | 2 | 18 | 0.00026274 | 1.46e-05 | No
23/04/2019 | 11:27:55 | HH107A | Urban | Asset failure | LV | 69 | 62 | 0.0068391 | 0.00011031 | No
23/04/2019 | 12:05:10 | KA27 | Rural Long | Planned |  | 1 | 40 | 0.00029193 | 7.3e-06 | No
23/04/2019 | 12:05:47 | GU13 | Rural Long | Asset failure | HV | 19.3333 | 89 | 0.012558 | 0.0001411 | No
23/04/2019 | 13:43:47 | CV24 | Rural Long | Asset failure | Distribution substation | 74 | 261.7027 | 0.14134 | 0.00054008 | No
23/04/2019 | 14:22:08 | SM350G | Urban | Planned |  | 38 | 20 | 0.001215 | 6.075e-05 | No
23/04/2019 | 15:37:33 | GA25 | Rural Short | Unknown | Unknown | 12.6667 | 58 | 0.0054734 | 9.437e-05 | No
23/04/2019 | 15:38:13 | HH121C | Urban | Asset failure | LV | 18.3333 | 88 | 0.0025792 | 2.931e-05 | No
23/04/2019 | 15:51:25 | GU42 | Rural Long | Asset failure | LV | 1 | 208 | 0.001518 | 7.3e-06 | No
23/04/2019 | 15:55:58 | M11 | Rural Long | Unknown | Unknown | 10.3333 | 100 | 0.0075416 | 7.542e-05 | No
23/04/2019 | 16:36:23 | ME200G | Urban | Asset failure | LV | 10 | 99 | 0.0015827 | 1.599e-05 | No
23/04/2019 | 23:54:48 | NL210D | Urban | Animal | Animal impact | 73 | 133 | 0.015522 | 0.0001167 | No
24/04/2019 | 00:00:44 | CBD103E | Urban | Planned |  | 49 | 29 | 0.0022717 | 7.834e-05 | No
24/04/2019 | 08:11:33 | PA02 | Urban | Planned |  | 66 | 334 | 0.035241 | 0.00010551 | No
24/04/2019 | 08:47:39 | MV52 | Rural Short | Planned |  | 22 | 324 | 0.053105 | 0.0001639 | No
24/04/2019 | 08:51:10 | AP227D | Urban | Asset failure | LV | 49.3334 | 79 | 0.0062306 | 7.887e-05 | No
24/04/2019 | 08:52:58 | SM349F | Urban | Asset failure | LV | 1 | 154 | 0.0002462 | 1.6e-06 | No
24/04/2019 | 08:58:42 | SG09 | Rural Short | Planned |  | 14 | 319 | 0.033272 | 0.0001043 | No
24/04/2019 | 09:02:36 | SM137A | Urban | Planned |  | 3 | 319 | 0.0015299 | 4.8e-06 | No
24/04/2019 | 09:11:14 | MTB32 | Rural Long | Planned |  | 104 | 258 | 0.19583 | 0.00075903 | No
24/04/2019 | 09:12:33 | YK21 | Rural Long | Planned |  | 8 | 172 | 0.010043 | 5.839e-05 | No
24/04/2019 | 09:25:09 | HH429A | Urban | Planned |  | 15 | 94 | 0.0022541 | 2.398e-05 | No
24/04/2019 | 09:30:11 | PL33 | Rural Long | Planned |  | 1094 | 83 | 0.6627 | 0.0079844 | No
24/04/2019 | 09:32:42 | ST51 | Rural Short | Planned |  | 9 | 313 | 0.020987 | 6.705e-05 | No
24/04/2019 | 09:34:01 | HH386B | Urban | Planned |  | 53 | 63 | 0.005338 | 8.473e-05 | No
24/04/2019 | 09:40:01 | BM12 | Rural Short | Planned |  | 87 | 120 | 0.07778 | 0.00064816 | No
24/04/2019 | 09:56:53 | SM350B | Urban | Planned |  | 28 | 309 | 0.013832 | 4.476e-05 | No
24/04/2019 | 10:08:01 | HH432D | Urban | Third Party | Vehicle impact | 58 | 302 | 0.028002 | 9.272e-05 | No
24/04/2019 | 10:13:41 | HH177D | Urban | Planned |  | 182 | 108 | 0.031424 | 0.00029096 | No
24/04/2019 | 10:41:55 | SA42 | Urban | Planned |  | 4 | 66 | 0.00042205 | 6.39e-06 | No
24/04/2019 | 10:47:37 | W24 | Rural Long | Planned |  | 3 | 141 | 0.0030872 | 2.19e-05 | No
24/04/2019 | 12:40:21 | NL451C | Urban | Asset failure | LV | 100 | 117 | 0.018704 | 0.00015987 | No
24/04/2019 | 17:10:55 | SSD522 | Urban | Asset failure | Zone substation | 5411 | 71.3565 | 0.61726 | 0.0086504 | No
24/04/2019 | 20:23:37 | NU27 | Rural Long | Unknown | Unknown | 1 | 112 | 0.00081741 | 7.3e-06 | No
24/04/2019 | 22:06:23 | SM410C | Urban | Asset failure | LV | 105 | 175 | 0.029376 | 0.00016786 | No
25/04/2019 | 01:50:00 | AP424F | Urban | Asset failure | HV | 732 | 137.3607 | 0.16074 | 0.0011702 | No
25/04/2019 | 05:52:31 | KA12 | Rural Long | Asset failure | HV | 13 | 267 | 0.025333 | 9.488e-05 | No
25/04/2019 | 15:33:20 | HH341D | Urban | Asset failure | LV | 1.6667 | 125 | 0.00033306 | 2.66e-06 | No
25/04/2019 | 21:22:32 | SM374E | Urban | Other |  | 1 | 187 | 0.00029895 | 1.6e-06 | No
25/04/2019 | 23:29:44 | AP132D | Urban | Animal | Animal nesting/burrowing, etc and other | 1 | 130 | 0.00020783 | 1.6e-06 | No
26/04/2019 | 08:41:27 | SD38200 | Rural Long | Planned |  | 3 | 204 | 0.0044666 | 2.19e-05 | No
26/04/2019 | 08:49:18 | LX51 | Rural Short | Planned |  | 2 | 155 | 0.0023096 | 1.49e-05 | No
26/04/2019 | 08:49:27 | KI21 | Rural Long | Planned |  | 2 | 231 | 0.0033718 | 1.46e-05 | No
26/04/2019 | 08:56:49 | SA18 | Urban | Planned |  | 31 | 230 | 0.011399 | 4.956e-05 | No
26/04/2019 | 09:03:54 | HH148B | Urban | Planned |  | 1 | 561 | 0.00089686 | 1.6e-06 | No
26/04/2019 | 09:10:22 | MB24 | Rural Short | Planned |  | 5 | 40 | 0.00149 | 3.725e-05 | No
26/04/2019 | 09:13:12 | MG22 | Rural Long | Planned |  | 5 | 102 | 0.0037222 | 3.649e-05 | No
26/04/2019 | 09:21:55 | ST13 | Rural Short | Planned |  | 13 | 69 | 0.0066828 | 9.685e-05 | No
26/04/2019 | 09:30:03 | R30 | Rural Long | Planned |  | 2 | 38 | 0.00055467 | 1.46e-05 | No
26/04/2019 | 09:49:25 | ME231C | Urban | Planned |  | 2 | 198 | 0.00063308 | 3.2e-06 | No
26/04/2019 | 09:58:21 | VH21 | Rural Short | Planned |  | 31 | 27 | 0.0062358 | 0.00023095 | No
26/04/2019 | 10:20:23 | G28 | Rural Long | Asset failure | LV | 2 | 127 | 0.0018538 | 1.46e-05 | No
26/04/2019 | 10:25:22 | NA09 | Rural Long | Planned |  | 2 | 77 | 0.0011239 | 1.46e-05 | No
26/04/2019 | 11:02:05 | G25 | Rural Long | Planned |  | 30 | 146 | 0.031967 | 0.00021895 | No
26/04/2019 | 11:58:37 | VH21 | Rural Short | Planned |  | 83 | 17 | 0.010512 | 0.00061836 | No
26/04/2019 | 12:00:08 | AP146E | Urban | Asset failure | LV | 1 | 130 | 0.00020783 | 1.6e-06 | No
26/04/2019 | 13:20:22 | R01 | Rural Long | Unknown | Unknown | 2 | 57 | 0.00083201 | 1.46e-05 | No
26/04/2019 | 13:32:34 | MG21 | Rural Long | Asset failure | LV | 1 | 81 | 0.00059116 | 7.3e-06 | No
26/04/2019 | 14:43:57 | MG49 | Rural Long | Overloads |  | 1 | 62 | 0.0004525 | 7.3e-06 | No
26/04/2019 | 21:50:11 | BM43 | Rural Short | Unknown | Unknown | 34 | 45 | 0.011399 | 0.00025331 | No
27/04/2019 | 08:40:03 | SG04 | Rural Short | Asset failure | LV | 7.3333 | 361 | 0.019723 | 5.463e-05 | No
27/04/2019 | 12:51:10 | LM33 | Rural Long | Unknown | Unknown | 67 | 146 | 0.071392 | 0.00048899 | No
27/04/2019 | 13:07:31 | SD38100 | Rural Long | Unknown | Unknown | 6 | 5 | 0.00021895 | 4.379e-05 | No
27/04/2019 | 13:53:36 | CBD366N | CBD | Planned |  | 2 | 1290 | 0.50082 | 0.00038824 | No
27/04/2019 | 14:58:57 | AP344D | Urban | Asset failure | LV | 1 | 101 | 0.00016147 | 1.6e-06 | No
27/04/2019 | 21:19:40 | NL234A | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
28/04/2019 | 07:31:19 | CV30 | Rural Long | Unknown | Unknown | 11 | 394 | 0.031631 | 8.028e-05 | No
28/04/2019 | 08:10:29 | WHY05 | Urban | Planned |  | 16 | 300 | 0.0076736 | 2.558e-05 | No
28/04/2019 | 08:43:05 | EL13 | Urban | Planned |  | 11 | 21 | 0.00036929 | 1.759e-05 | No
28/04/2019 | 08:44:27 | ME200F | Urban | Asset failure | HV | 1 | 105 | 0.00016786 | 1.6e-06 | No
28/04/2019 | 08:48:52 | AP227D | Urban | Planned |  | 113 | 281 | 0.050763 | 0.00018065 | No
28/04/2019 | 09:15:09 | GU33 | Rural Long | Planned |  | 1 | 110 | 0.00080282 | 7.3e-06 | No
28/04/2019 | 09:41:11 | KI55 | Rural Long | Unknown | Unknown | 40 | 318.25 | 0.092908 | 0.00029193 | No
28/04/2019 | 10:01:00 | KA12 | Rural Long | Planned |  | 2 | 78 | 0.0011385 | 1.46e-05 | No
28/04/2019 | 10:10:52 | GU33 | Rural Long | Unknown | Unknown | 16 | 22 | 0.002569 | 0.00011677 | No
28/04/2019 | 10:33:06 | NA32 | Rural Long | Unknown | Unknown | 14.3333 | 230 | 0.02406 | 0.00010461 | No
28/04/2019 | 11:21:02 | KA12 | Rural Long | Planned |  | 1 | 73 | 0.00053278 | 7.3e-06 | No
28/04/2019 | 16:20:21 | EL17 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 997 | 73 | 0.11635 | 0.0015939 | No
28/04/2019 | 17:28:02 | PP02 | Urban | Overloads |  | 1 | 148 | 0.0002366 | 1.6e-06 | No
28/04/2019 | 18:29:30 | SM410B | Urban | Overloads |  | 1 | 242 | 0.00038688 | 1.6e-06 | No
28/04/2019 | 18:50:35 | AP146B | Urban | Asset failure | LV | 1 | 95 | 0.00015187 | 1.6e-06 | No
28/04/2019 | 22:11:47 | R03 | Rural Long | Unknown | Unknown | 6 | 144 | 0.0063058 | 4.379e-05 | No
28/04/2019 | 23:14:57 | ME131B | Urban | Planned |  | 304 | 394 | 0.19148 | 0.000486 | No
29/04/2019 | 03:58:52 | GA02 | Rural Short | Asset failure | HV | 712 | 183.493 | 0.97334 | 0.0053045 | No
29/04/2019 | 07:23:44 | GU23 | Rural Long | Animal | Animal impact | 1 | 264 | 0.0019268 | 7.3e-06 | No
29/04/2019 | 08:13:40 | SA14 | Urban | Asset failure | LV | 1 | 323 | 0.00051637 | 1.6e-06 | No
29/04/2019 | 08:33:47 | MG10 | Rural Long | Planned |  | 21 | 171 | 0.026208 | 0.00015327 | No
29/04/2019 | 08:50:31 | MTB33 | Rural Short | Planned |  | 8 | 279 | 0.016629 | 5.96e-05 | No
29/04/2019 | 09:00:53 | NL511B | Urban | Planned |  | 70 | 347 | 0.038832 | 0.00011191 | No
29/04/2019 | 09:20:29 | SB22 | Rural Long | Planned |  | 8 | 191 | 0.011152 | 5.839e-05 | No
29/04/2019 | 09:26:50 | ST51 | Rural Short | Planned |  | 7 | 313 | 0.016323 | 5.215e-05 | No
29/04/2019 | 09:27:52 | MB15 | Rural Short | Planned |  | 1 | 200 | 0.00149 | 7.45e-06 | No
29/04/2019 | 09:32:05 | PL14 | Urban | Planned |  | 2 | 234 | 0.00074818 | 3.2e-06 | No
29/04/2019 | 09:36:56 | SM349E | Urban | Planned |  | 1 | 44 | 7.034e-05 | 1.6e-06 | No
29/04/2019 | 09:45:47 | SM126D | Urban | Planned |  | 62 | 285 | 0.028249 | 9.912e-05 | No
29/04/2019 | 09:48:14 | GU41 | Rural Long | Planned |  | 4 | 212 | 0.006189 | 2.919e-05 | No
29/04/2019 | 10:06:51 | WK11 | Rural Short | Planned |  | 3 | 88 | 0.0019668 | 2.235e-05 | No
29/04/2019 | 10:21:30 | SM350B | Urban | Overloads |  | 1 | 285 | 0.00045562 | 1.6e-06 | No
29/04/2019 | 10:30:00 | AP227B / AP227C | Urban | Planned |  | 354 | 1648.3955 | 0.93288 | 0.00056593 | No
29/04/2019 | 10:32:30 | MTB32 | Rural Long | Planned |  | 14 | 268 | 0.027383 | 0.00010218 | No
29/04/2019 | 10:34:41 | MI20 | Rural Long | Unknown | Unknown | 12 | 109 | 0.0095462 | 8.758e-05 | No
29/04/2019 | 10:35:58 | MB15 | Rural Short | Planned |  | 1 | 90 | 0.00067051 | 7.45e-06 | No
29/04/2019 | 10:53:11 | AP149F | Urban | Asset failure | LV | 35 | 49 | 0.0027417 | 5.595e-05 | No
29/04/2019 | 12:34:00 | CL19 | Rural Long | Third Party | Vehicle impact | 82 | 159.878 | 0.095681 | 0.00059846 | No
29/04/2019 | 13:33:11 | SM216A | Urban | Planned |  | 162 | 1 | 0.00025899 | 0.00025899 | No
29/04/2019 | 13:43:00 | SM349A | Urban | Planned |  | 1 | 30 | 4.796e-05 | 1.6e-06 | No
29/04/2019 | 15:34:18 | NU21 | Rural Long | Asset failure | LV | 3 | 143 | 0.003131 | 2.19e-05 | No
29/04/2019 | 15:50:39 | SD49200 | Rural Long | Unknown | Unknown | 1 | 1189 | 0.0086777 | 7.3e-06 | No
29/04/2019 | 16:15:29 | W02 | Rural Long | Planned |  | 38 | 5 | 0.0013867 | 0.00027734 | No
29/04/2019 | 18:19:10 | W15 | Rural Long | Third Party | Vehicle impact | 53 | 143 | 0.055314 | 0.00038681 | No
29/04/2019 | 18:55:22 | PA22 | Rural Long | Planned |  | 1 | 45 | 0.00032843 | 7.3e-06 | No
29/04/2019 | 20:30:14 | SD34102 | Rural Long | Planned |  | 1 | 20 | 0.00014597 | 7.3e-06 | No
29/04/2019 | 23:14:30 | CBD353L | CBD | Planned |  | 12 | 225.6667 | 0.52567 | 0.0023294 | No
29/04/2019 | 23:14:30 | CBD353L | CBD | Planned |  | 0 | 2 | 0.00038824 | 0 | No
30/04/2019 | 06:20:21 | GA09 | Rural Long | Asset failure | HV | 956 | 62.7008 | 0.43748 | 0.0069772 | No
30/04/2019 | 06:49:39 | NA01 | Rural Long | Asset failure | LV | 1 | 197 | 0.0014378 | 7.3e-06 | No
30/04/2019 | 07:43:05 | VH32 | Rural Short | Asset failure | LV | 1 | 200 | 0.00149 | 7.45e-06 | No
30/04/2019 | 08:16:59 | AP373K | Urban | Unknown | Unknown | 2.3333 | 48 | 0.00017905 | 3.73e-06 | No
30/04/2019 | 08:44:05 | AP125D | Urban | Planned |  | 199 | 237 | 0.075398 | 0.00031814 | No
30/04/2019 | 08:49:47 | SD33200 | Rural Long | Planned |  | 44 | 369 | 0.1185 | 0.00032113 | No
30/04/2019 | 08:58:10 | KA22 | Rural Long | Planned |  | 3 | 137 | 0.0029996 | 2.19e-05 | No
30/04/2019 | 09:05:29 | PL27 | Rural Long | Other |  | 14 | 34 | 0.003474 | 0.00010218 | No
30/04/2019 | 09:13:19 | PL20 | Rural Long | Planned |  | 1 | 13 | 9.488e-05 | 7.3e-06 | No
30/04/2019 | 09:20:32 | CL09 | Rural Long | Planned |  | 15 | 253 | 0.027697 | 0.00010948 | No
30/04/2019 | 09:25:48 | NA13 | Rural Long | Planned |  | 85 | 327 | 0.20286 | 0.00062036 | No
30/04/2019 | 09:30:12 | GA26 | Urban | Planned |  | 194 | 307.9691 | 0.095514 | 0.00031014 | No
30/04/2019 | 09:42:17 | SA32 | Urban | Planned |  | 1 | 18 | 2.878e-05 | 1.6e-06 | No
30/04/2019 | 09:42:58 | MTB32 | Rural Long | Planned |  | 24 | 254 | 0.044491 | 0.00017516 | No
30/04/2019 | 09:45:29 | AP373K | Urban | Asset failure | LV | 1 | 46 | 7.354e-05 | 1.6e-06 | No
30/04/2019 | 09:55:02 | SD32400 | Rural Long | Planned |  | 81 | 309 | 0.18267 | 0.00059117 | No
30/04/2019 | 09:56:18 | AP149F | Urban | Planned |  | 2 | 37 | 0.0001183 | 3.2e-06 | No
30/04/2019 | 10:24:01 | PA02 | Urban | Asset failure | LV | 56 | 91 | 0.0081469 | 8.953e-05 | No
30/04/2019 | 12:26:58 | NL451D | Urban | Planned |  | 171 | 3050 | 0.83379 | 0.00027337 | No
30/04/2019 | 14:13:28 | SA33 | Urban | Third Party | Vehicle impact | 77 | 503 | 0.061918 | 0.0001231 | No
30/04/2019 | 16:46:41 | HH432B | Urban | Overloads |  | 1 | 415 | 0.00066345 | 1.6e-06 | No
30/04/2019 | 17:17:26 | PA22 | Rural Long | Planned |  | 1 | 256 | 0.0018684 | 7.3e-06 | No
30/04/2019 | 20:03:45 | AP125D | Urban | Vegetation | Grow-in - NSP responsibility | 28 | 77 | 0.0034467 | 4.476e-05 | No
30/04/2019 | 20:04:32 | SM172F | Urban | Planned |  | 166 | 2 | 0.00053076 | 0.00026538 | No
30/04/2019 | 20:06:04 | PA14 | Rural Long | Unknown | Unknown | 1 | 49 | 0.00035762 | 7.3e-06 | No
30/04/2019 | 20:10:32 | SA711C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 83 | 162 | 0.021496 | 0.00013269 | No
30/04/2019 | 20:20:11 | HH148A | Urban | Vegetation | Grow-in - NSP responsibility | 610.3336 | 37 | 0.036102 | 0.00097573 | No
30/04/2019 | 20:25:56 | HH409E | Urban | Unknown | Unknown | 21.3333 | 43 | 0.0014665 | 3.411e-05 | No
30/04/2019 | 20:46:10 | KA28 | Rural Long | Asset failure | HV | 66 | 134 | 0.064547 | 0.00048169 | No
30/04/2019 | 21:19:23 | HH148A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 25 | 3.997e-05 | 1.6e-06 | No
30/04/2019 | 21:28:59 | SG07 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1016 | 29.3465 | 0.22213 | 0.0075693 | No
30/04/2019 | 21:41:14 | HH121E | Urban | Unknown | Unknown | 499 | 1 | 0.00079774 | 0.00079774 | No
30/04/2019 | 21:41:14 | HH121E | Urban | Unknown | Unknown | 21 | 172 | 0.0057744 | 3.357e-05 | No
30/04/2019 | 22:00:04 | VH22 | Rural Short | Weather |  | 67 | 136.209 | 0.06799 | 0.00049916 | No
30/04/2019 | 22:14:02 | HH148D | Urban | Animal | Animal impact | 1 | 208 | 0.00033252 | 1.6e-06 | No
1/05/2019 | 00:25:48 | MB28 | Rural Short | Unknown | Unknown | 139 | 170 | 0.17605 | 0.0010356 | No
1/05/2019 | 00:46:02 | SG14 | Rural Short | Weather |  | 146 | 209 | 0.22733 | 0.0010877 | No
1/05/2019 | 01:25:07 | KA28 | Rural Long | Asset failure | HV | 66 | 455.5 | 0.21941 | 0.00048169 | No
1/05/2019 | 02:47:00 | NL21 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 200 | 442.41 | 0.14145 | 0.00031974 | No
1/05/2019 | 03:03:54 | R01 | Rural Long | Asset failure | HV | 106.3334 | 333.3762 | 0.25872 | 0.00077606 | No
1/05/2019 | 03:50:15 | SD41200 | Rural Short | Asset failure | Subtransmission | 6 | 90.5 | 0.0040454 | 4.47e-05 | No
1/05/2019 | 06:43:43 | SG13 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 138 | 0.0010281 | 7.45e-06 | No
1/05/2019 | 06:49:27 | SM179B | Urban | Asset failure | LV | 7 | 287 | 0.0032117 | 1.119e-05 | No
1/05/2019 | 07:24:35 | AP149F | Urban | Asset failure | LV | 42.6666 | 70 | 0.0047747 | 6.821e-05 | No
1/05/2019 | 08:04:34 | HH121A | Urban | Unknown | Unknown | 1 | 177 | 0.00028297 | 1.6e-06 | No
1/05/2019 | 08:24:37 | HH428F | Urban | Unknown | Unknown | 4141 | 66.2142 | 0.43835 | 0.0066201 | No
1/05/2019 | 08:24:46 | EL13 | Urban | Asset failure | LV | 1 | 279 | 0.00044603 | 1.6e-06 | No
1/05/2019 | 08:36:37 | SA38 | Urban | Planned |  | 25 | 379 | 0.015147 | 3.997e-05 | No
1/05/2019 | 08:45:16 | MTB81 | Rural Short | Planned |  | 116 | 168 | 0.14519 | 0.00086422 | No
1/05/2019 | 08:59:44 | SA17 | Urban | Asset failure | LV | 16 | 172 | 0.0043996 | 2.558e-05 | No
1/05/2019 | 09:02:38 | NU32 | Rural Long | Planned |  | 4 | 348 | 0.010159 | 2.919e-05 | No
1/05/2019 | 09:05:50 | W15 | Rural Long | Third Party | Vehicle impact | 53 | 162.0755 | 0.062693 | 0.00038681 | No
1/05/2019 | 09:06:13 | GA02 | Rural Short | Planned |  | 30 | 300 | 0.067051 | 0.0002235 | No
1/05/2019 | 09:12:54 | CV17 | Rural Long | Planned |  | 9 | 79 | 0.0051891 | 6.569e-05 | No
1/05/2019 | 09:17:59 | SM349H | Urban | Overloads |  | 1 | 181 | 0.00028936 | 1.6e-06 | No
1/05/2019 | 09:26:42 | VH44 | Rural Short | Planned |  | 1 | 127 | 0.00094617 | 7.45e-06 | No
1/05/2019 | 09:27:54 | GU17 | Rural Long | Planned |  | 6 | 76 | 0.003328 | 4.379e-05 | No
1/05/2019 | 09:31:00 | SM172F | Urban | Planned |  | 971 | 172 | 0.267 | 0.0015523 | No
1/05/2019 | 09:35:14 | ST11 | Rural Short | Planned |  | 38 | 193 | 0.054639 | 0.00028311 | No
1/05/2019 | 09:38:30 | SM216C | Urban | Planned |  | 50 | 241 | 0.019264 | 7.993e-05 | No
1/05/2019 | 09:45:22 | BU09 | Rural Long | Planned |  | 22 | 49 | 0.0078676 | 0.00016056 | No
1/05/2019 | 09:56:08 | SM349C | Urban | Asset failure | LV | 1 | 324 | 0.00051797 | 1.6e-06 | No
1/05/2019 | 10:02:07 | NU08 | Rural Long | Planned |  | 1 | 40 | 0.00029193 | 7.3e-06 | No
1/05/2019 | 10:03:47 | NL115E | Urban | Asset failure | LV | 1 | 323 | 0.00051637 | 1.6e-06 | No
1/05/2019 | 10:27:47 | MI12 | Rural Long | Planned |  | 75 | 397 | 0.21731 | 0.00054738 | No
1/05/2019 | 11:17:32 | MT11 | Rural Long | Planned |  | 4 | 115 | 0.0033572 | 2.919e-05 | No
1/05/2019 | 11:19:13 | NL210A | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
1/05/2019 | 11:34:57 | NU08 | Rural Long | Asset failure | HV | 100 | 403.3 | 0.29434 | 0.00072983 | No
1/05/2019 | 11:38:45 | NL234C | Urban | Asset failure | LV | 1 | 44 | 7.034e-05 | 1.6e-06 | No
1/05/2019 | 11:54:56 | NL234C | Urban | Asset failure | LV | 1 | 28 | 4.476e-05 | 1.6e-06 | No
1/05/2019 | 13:10:47 | PP04 | Rural Short | Asset failure | LV | 1 | 187 | 0.0013932 | 7.45e-06 | No
1/05/2019 | 13:37:49 | MV14 | Rural Short | Asset failure | HV | 35 | 233.4286 | 0.060868 | 0.00026076 | No
1/05/2019 | 13:42:17 | NL111C | Urban | Planned |  | 14 | 12 | 0.00026858 | 2.238e-05 | No
1/05/2019 | 14:00:20 | PA04 | Rural Short | Asset failure | LV | 1 | 72 | 0.00053641 | 7.45e-06 | No
1/05/2019 | 15:34:34 | MT03 | Rural Long | Third Party | Vehicle impact | 1 | 223 | 0.0016275 | 7.3e-06 | No
1/05/2019 | 15:48:43 | VH23 | Rural Short | Asset failure | LV | 1 | 214 | 0.0015943 | 7.45e-06 | No
1/05/2019 | 15:53:39 | KI32 | Rural Short | Weather |  | 19 | 62 | 0.0087763 | 0.00014155 | No
1/05/2019 | 16:28:27 | SM172F | Urban | Planned |  | 1 | 133 | 0.00021262 | 1.6e-06 | No
1/05/2019 | 17:00:41 | SD35500 | Rural Long | Weather |  | 567 | 230.3386 | 0.95318 | 0.0041382 | No
1/05/2019 | 17:02:06 | VH11 | Urban | Other |  | 1 | 238 | 0.00038048 | 1.6e-06 | No
1/05/2019 | 17:04:09 | PP14 | Rural Long | Asset failure | LV | 2 | 1258 | 0.018363 | 1.46e-05 | No
1/05/2019 | 17:27:28 | HH522B | Urban | Unknown | Unknown | 12 | 126 | 0.0024172 | 1.918e-05 | No
1/05/2019 | 17:30:02 | MT04 | Rural Short | Weather |  | 14 | 153 | 0.015958 | 0.0001043 | No
1/05/2019 | 19:11:27 | NL111C | Urban | Asset failure | LV | 1 | 390 | 0.00062348 | 1.6e-06 | No
1/05/2019 | 19:36:31 | HH121E | Urban | Unknown | Unknown | 14.3333 | 124 | 0.0028414 | 2.291e-05 | No
1/05/2019 | 20:56:08 | SM126B | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
1/05/2019 | 22:42:03 | GA03 | Rural Long | Planned |  | 1 | 65 | 0.00047439 | 7.3e-06 | No
1/05/2019 | 22:58:29 | SM216B | Urban | Planned |  | 270 | 262 | 0.11309 | 0.00043164 | No
1/05/2019 | 23:02:36 | ME231D | Urban | Unknown | Unknown | 1 | 121 | 0.00019344 | 1.6e-06 | No
1/05/2019 | 23:35:12 | SM179A | Urban | Asset failure | LV | 163 | 215 | 0.056026 | 0.00026058 | No
2/05/2019 | 03:43:02 | ME231D | Urban | Asset failure | LV | 1 | 135 | 0.00021582 | 1.6e-06 | No
2/05/2019 | 06:48:10 | NA05 | Rural Long | Unknown | Unknown | 17.6667 | 187 | 0.024111 | 0.00012894 | No
2/05/2019 | 06:51:49 | ME231D | Urban | Unknown | Unknown | 4 | 125 | 0.00079934 | 6.39e-06 | No
2/05/2019 | 08:04:26 | SA38 | Urban | Planned |  | 4 | 341 | 0.0021806 | 6.39e-06 | No
2/05/2019 | 08:07:26 | ST12 | Rural Short | Planned |  | 32 | 194 | 0.046251 | 0.0002384 | No
2/05/2019 | 08:31:29 | NL111B | Urban | Overloads |  | 21 | 399 | 0.013395 | 3.357e-05 | No
2/05/2019 | 08:39:41 | CL09 | Rural Long | Planned |  | 47 | 145 | 0.049738 | 0.00034302 | No
2/05/2019 | 08:51:25 | GU43 | Rural Long | Planned |  | 5 | 16 | 0.00058387 | 3.649e-05 | No
2/05/2019 | 08:51:48 | MTB13 | Rural Short | Planned |  | 153 | 280 | 0.31916 | 0.0011399 | No
2/05/2019 | 08:56:53 | SM349C | Urban | Planned |  | 172 | 305 | 0.083866 | 0.00027497 | No
2/05/2019 | 09:06:32 | SG13 | Rural Short | Planned |  | 38 | 142 | 0.040201 | 0.00028311 | No
2/05/2019 | 09:11:03 | MTB22 | Rural Short | Planned |  | 21 | 349 | 0.054602 | 0.00015645 | No
2/05/2019 | 09:11:26 | MI26 | Rural Long | Planned |  | 13 | 291 | 0.02761 | 9.488e-05 | No
2/05/2019 | 09:15:27 | CL27 | Rural Long | Planned |  | 2 | 98 | 0.0014305 | 1.46e-05 | No
2/05/2019 | 09:25:13 | PP01 | Urban | Asset failure | LV | 1 | 154 | 0.0002462 | 1.6e-06 | No
2/05/2019 | 09:37:15 | EL12 | Urban | Planned |  | 135 | 176 | 0.037985 | 0.00021582 | No
2/05/2019 | 09:39:58 | CM16 | Rural Long | Planned |  | 38 | 221 | 0.061291 | 0.00027734 | No
2/05/2019 | 09:41:21 | HH496F | Urban | Planned |  | 266 | 54.2857 | 0.023085 | 0.00042525 | No
2/05/2019 | 09:43:22 | GU43 | Rural Long | Planned |  | 113 | 217 | 0.17896 | 0.00082471 | No
2/05/2019 | 10:02:40 | SG13 | Rural Short | Planned |  | 127 | 249 | 0.2356 | 0.00094617 | No
2/05/2019 | 10:03:22 | SB01 | Rural Long | Asset failure | LV | 2 | 126 | 0.0018392 | 1.46e-05 | No
2/05/2019 | 10:20:46 | BU01 | Rural Long | Planned |  | 41 | 75 | 0.022442 | 0.00029923 | No
2/05/2019 | 10:44:21 | LM43 | Rural Long | Planned |  | 2 | 79 | 0.0011531 | 1.46e-05 | No
2/05/2019 | 10:45:36 | MB51 | Rural Long | Asset failure | HV | 1 | 79 | 0.00057657 | 7.3e-06 | No
2/05/2019 | 11:23:18 | HH121E | Urban | Unknown | Unknown | 21 | 10 | 0.00033572 | 3.357e-05 | No
2/05/2019 | 12:25:50 | YK03 | Rural Long | Asset failure | HV | 885 | 112.1605 | 0.72445 | 0.006459 | No
2/05/2019 | 12:25:57 | SG13 | Rural Short | Planned |  | 6 | 91 | 0.0040678 | 4.47e-05 | No
2/05/2019 | 12:28:00 | YK03 | Rural Long | Overloads |  | 3 | 140 | 0.0030653 | 2.19e-05 | No
2/05/2019 | 13:15:48 | MV34 | Rural Short | Third Party | Vehicle impact | 17.3333 | 55 | 0.0071025 | 0.00012914 | No
2/05/2019 | 13:22:17 | BU01 | Rural Long | Planned |  | 40 | 24 | 0.0070064 | 0.00029193 | No
2/05/2019 | 15:56:44 | MV34 | Rural Short | Asset failure | LV | 1 | 115 | 0.00085677 | 7.45e-06 | No
2/05/2019 | 16:10:03 | MI08 | Rural Long | Asset failure | LV | 9.6667 | 45 | 0.0031748 | 7.055e-05 | No
2/05/2019 | 16:22:55 | HH177G | Urban | Asset failure | LV | 1 | 247 | 0.00039487 | 1.6e-06 | No
2/05/2019 | 17:43:08 | AP149F | Urban | Weather |  | 1 | 118 | 0.00018864 | 1.6e-06 | No
2/05/2019 | 17:46:22 | HH429B | Urban | Weather |  | 1 | 134 | 0.00021422 | 1.6e-06 | No
2/05/2019 | 18:31:29 | HH386C | Urban | Asset failure | LV | 1 | 242 | 0.00038688 | 1.6e-06 | No
2/05/2019 | 18:47:01 | AP424C | Urban | Asset failure | LV | 1 | 129 | 0.00020623 | 1.6e-06 | No
2/05/2019 | 19:18:41 | SM216D | Urban | Asset failure | LV | 1 | 91 | 0.00014548 | 1.6e-06 | No
2/05/2019 | 19:52:33 | AP149B | Urban | Asset failure | LV | 8.3333 | 70 | 0.00093256 | 1.332e-05 | No
2/05/2019 | 20:12:19 | SA520E | Urban | Asset failure | LV | 23 | 70 | 0.0025739 | 3.677e-05 | No
2/05/2019 | 23:43:05 | SD49500 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 688 | 449 | 2.2545 | 0.0050213 | No
3/05/2019 | 02:44:48 | MG46 | Rural Short | Unknown | Unknown | 327 | 149 | 0.36299 | 0.0024362 | No
3/05/2019 | 05:37:36 | NL451C | Urban | Asset failure | LV | 48 | 256 | 0.019645 | 7.674e-05 | No
3/05/2019 | 06:07:58 | NL111B | Urban | Overloads |  | 1 | 373 | 0.00059631 | 1.6e-06 | No
3/05/2019 | 06:15:56 | SM411A | Urban | Unknown | Unknown | 43.3333 | 153 | 0.010599 | 6.928e-05 | No
3/05/2019 | 08:30:51 | SG13 | Rural Short | Unknown | Unknown | 3.6667 | 103 | 0.0028137 | 2.732e-05 | No
3/05/2019 | 08:46:10 | SA38 | Urban | Planned |  | 4 | 355 | 0.0022701 | 6.39e-06 | No
3/05/2019 | 08:56:25 | GU32 | Rural Long | Planned |  | 24 | 330 | 0.057803 | 0.00017516 | No
3/05/2019 | 09:06:25 | GA35 | Rural Long | Planned |  | 3 | 110 | 0.0024084 | 2.19e-05 | No
3/05/2019 | 09:15:57 | MB28 | Rural Short | Planned |  | 40 | 257 | 0.076588 | 0.00029801 | No
3/05/2019 | 09:16:53 | MTB53 | Rural Long | Planned |  | 13 | 334 | 0.031689 | 9.488e-05 | No
3/05/2019 | 09:26:30 | HH130A | Urban | Planned |  | 52 | 260 | 0.021614 | 8.313e-05 | No
3/05/2019 | 09:26:37 | AP132D | Urban | Planned |  | 183 | 341 | 0.099762 | 0.00029256 | No
3/05/2019 | 09:26:50 | GA39 | Rural Long | Planned |  | 36 | 54 | 0.014188 | 0.00026274 | No
3/05/2019 | 09:31:21 | MV41 | Rural Short | Planned |  | 3 | 288 | 0.0064369 | 2.235e-05 | No
3/05/2019 | 09:33:23 | SG10 | Rural Short | Planned |  | 126 | 231 | 0.21684 | 0.00093872 | No
3/05/2019 | 09:40:02 | LX21 | Rural Short | Planned |  | 2 | 260 | 0.0038741 | 1.49e-05 | No
3/05/2019 | 10:05:00 | HH496C | Urban | Planned |  | 140 | 140 | 0.031334 | 0.00022381 | No
3/05/2019 | 10:06:13 | MTB51 | Rural Long | Planned |  | 9 | 203 | 0.013334 | 6.569e-05 | No
3/05/2019 | 10:09:33 | SM179A | Urban | Planned |  | 1 | 58 | 9.272e-05 | 1.6e-06 | No
3/05/2019 | 10:32:21 | CM11 | Rural Long | Planned |  | 25 | 139 | 0.025362 | 0.00018246 | No
3/05/2019 | 11:29:19 | CL03 | Rural Long | Planned |  | 1 | 213 | 0.0015546 | 7.3e-06 | No
3/05/2019 | 11:43:23 | GA35 | Rural Long | Planned |  | 1 | 58 | 0.0004233 | 7.3e-06 | No
3/05/2019 | 14:03:19 | SG13 | Rural Short | Third Party | Other | 265 | 87 | 0.17176 | 0.0019743 | No
3/05/2019 | 14:21:02 | BT03 | Rural Long | Animal | Animal impact | 349 | 43 | 0.10953 | 0.0025471 | No
3/05/2019 | 14:31:58 | YK04 | Rural Short | Asset failure | HV | 13 | 40 | 0.0038741 | 9.685e-05 | No
3/05/2019 | 14:53:20 | MT09 | Rural Long | Unknown | Unknown | 65 | 222.9385 | 0.10576 | 0.00047439 | No
3/05/2019 | 16:39:11 | HH107B | Urban | Asset failure | LV | 1 | 77 | 0.0001231 | 1.6e-06 | No
3/05/2019 | 17:37:26 | HH107A | Urban | Overloads |  | 1 | 264 | 0.00042205 | 1.6e-06 | No
3/05/2019 | 18:02:50 | ME131A | Urban | Asset failure | LV | 50 | 137 | 0.010951 | 7.993e-05 | No
3/05/2019 | 19:14:07 | HH121E | Urban | Asset failure | LV | 1 | 145 | 0.00023181 | 1.6e-06 | No
3/05/2019 | 19:52:05 | SA16 | Urban | Asset failure | LV | 1 | 179 | 0.00028616 | 1.6e-06 | No
3/05/2019 | 22:57:32 | AP132E | Urban | Unknown | Unknown | 81 | 112.2099 | 0.01453 | 0.00012949 | No
4/05/2019 | 00:56:54 | MT09 | Rural Long | Asset failure | HV | 65 | 509 | 0.24147 | 0.00047439 | No
4/05/2019 | 01:43:32 | AP365F | Urban | Asset failure | LV | 74 | 87 | 0.010292 | 0.0001183 | No
4/05/2019 | 03:15:57 | AP132E | Urban | Weather |  | 81 | 110 | 0.014244 | 0.00012949 | No
4/05/2019 | 06:28:31 | VH18 | Rural Short | Asset failure | HV | 16 | 315 | 0.037549 | 0.0001192 | No
4/05/2019 | 08:11:49 | NU04 | Rural Short | Animal | Animal impact | 33 | 214 | 0.052613 | 0.00024585 | No
4/05/2019 | 08:13:25 | MV63 | Rural Short | Asset failure | LV | 2 | 245 | 0.0036506 | 1.49e-05 | No
4/05/2019 | 08:15:59 | NL210A | Urban | Asset failure | LV | 1 | 274 | 0.00043804 | 1.6e-06 | No
4/05/2019 | 08:18:10 | EL23 | Urban | Unknown | Unknown | 25 | 181 | 0.007234 | 3.997e-05 | No
4/05/2019 | 08:38:51 | HH130A | Urban | Asset failure | LV | 7 | 84 | 0.00094002 | 1.119e-05 | No
4/05/2019 | 10:39:43 | GA26 | Urban | Asset failure | LV | 1 | 180 | 0.00028776 | 1.6e-06 | No
4/05/2019 | 10:44:24 | AP139C | Urban | Asset failure | LV | 1 | 200 | 0.00031974 | 1.6e-06 | No
4/05/2019 | 11:10:24 | AP373C | Urban | Planned |  | 1 | 119 | 0.00019024 | 1.6e-06 | No
4/05/2019 | 12:23:50 | R09 | Rural Long | Unknown | Unknown | 1.6667 | 18 | 0.00021895 | 1.216e-05 | No
4/05/2019 | 13:11:16 | SD37402 | Rural Long | Weather |  | 1894 | 107 | 1.4791 | 0.013823 | No
4/05/2019 | 14:10:53 | CBD412B | Urban | Third Party | Vehicle impact | 1 | 122 | 0.00019504 | 1.6e-06 | No
4/05/2019 | 15:18:49 | PA02 | Urban | Vegetation | Grow-in - NSP responsibility | 58 | 76 | 0.007047 | 9.272e-05 | No
4/05/2019 | 20:23:28 | MB44 | Rural Long | Unknown | Unknown | 2 | 15 | 0.00021895 | 1.46e-05 | No
4/05/2019 | 23:22:08 | AP424A | Urban | Asset failure | LV | 15.3333 | 773 | 0.018949 | 2.451e-05 | No
5/05/2019 | 00:32:39 | AP146B | Urban | Asset failure | LV | 2 | 151 | 0.0004828 | 3.2e-06 | No
5/05/2019 | 06:57:10 | HH386D | Urban | Asset failure | LV | 14.3333 | 155 | 0.0035517 | 2.291e-05 | No
5/05/2019 | 08:23:04 | BM53 | Rural Short | Planned |  | 84 | 406 | 0.25408 | 0.00062581 | No
5/05/2019 | 08:32:16 | SM216B | Urban | Planned |  | 16 | 82 | 0.0020975 | 2.558e-05 | No
5/05/2019 | 08:34:00 | MTB14 | Rural Short | Planned |  | 2 | 341 | 0.005081 | 1.49e-05 | No
5/05/2019 | 08:40:00 | GU36 | Rural Long | Planned |  | 1 | 126 | 0.00091959 | 7.3e-06 | No
5/05/2019 | 08:42:03 | SM410C | Urban | Planned |  | 126 | 275 | 0.055394 | 0.00020143 | No
5/05/2019 | 08:44:11 | SM349F | Urban | Planned |  | 1 | 370 | 0.00059151 | 1.6e-06 | No
5/05/2019 | 09:00:39 | AP355F | Urban | Planned |  | 44 | 249 | 0.017515 | 7.034e-05 | No
5/05/2019 | 09:09:43 | SD37102 | Rural Long | Planned |  | 11 | 236 | 0.018946 | 8.028e-05 | No
5/05/2019 | 09:25:59 | HH386C | Urban | Planned |  | 133 | 183 | 0.03891 | 0.00021262 | No
5/05/2019 | 10:38:39 | SM410C | Urban | Planned |  | 1 | 110 | 0.00017585 | 1.6e-06 | No
5/05/2019 | 14:17:05 | MI02 | Rural Short | Unknown | Unknown | 8 | 58 | 0.0034569 | 5.96e-05 | No
5/05/2019 | 16:03:15 | CM11 | Rural Long | Planned |  | 15 | 75 | 0.0082106 | 0.00010948 | No
5/05/2019 | 17:11:34 | NU25 | Rural Long | Asset failure | LV | 1 | 109 | 0.00079552 | 7.3e-06 | No
5/05/2019 | 17:33:36 | HH428B | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
5/05/2019 | 21:24:59 | SA17 | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
5/05/2019 | 21:59:54 | AP149D | Urban | Unknown | Unknown | 34 | 62 | 0.00337 | 5.435e-05 | No
6/05/2019 | 08:06:28 | KI31 | Rural Short | Overloads |  | 1 | 143 | 0.0010654 | 7.45e-06 | No
6/05/2019 | 08:28:46 | ST11 | Rural Short | Animal | Animal impact | 5 | 324 | 0.012069 | 3.725e-05 | No
6/05/2019 | 08:41:57 | NA02 | Rural Long | Planned |  | 3 | 400.6667 | 0.0087726 | 2.19e-05 | No
6/05/2019 | 08:51:14 | AP125C | Urban | Planned |  | 67 | 347 | 0.037168 | 0.00010711 | No
6/05/2019 | 09:14:40 | HH121D | Urban | Asset failure | LV | 1 | 121 | 0.00019344 | 1.6e-06 | No
6/05/2019 | 09:18:41 | MB25 | Rural Long | Planned |  | 68 | 217 | 0.10769 | 0.00049629 | No
6/05/2019 | 09:20:08 | LX21 | Rural Short | Planned |  | 2 | 275 | 0.0040976 | 1.49e-05 | No
6/05/2019 | 09:20:26 | SD37102 | Rural Long | Planned |  | 4 | 224 | 0.0065393 | 2.919e-05 | No
6/05/2019 | 09:26:18 | SA19 | Urban | Planned |  | 52 | 117 | 0.0097263 | 8.313e-05 | No
6/05/2019 | 09:28:09 | MV33 | Rural Short | Planned |  | 6 | 119 | 0.0053194 | 4.47e-05 | No
6/05/2019 | 09:31:05 | ST36 | Rural Long | Planned |  | 11 | 192 | 0.015414 | 8.028e-05 | No
6/05/2019 | 09:37:45 | SM349F | Urban | Planned |  | 1 | 462 | 0.00073859 | 1.6e-06 | No
6/05/2019 | 09:46:48 | W06 | Rural Long | Planned |  | 3 | 81 | 0.0017735 | 2.19e-05 | No
6/05/2019 | 09:49:36 | AP149F | Urban | Asset failure | LV | 85.3334 | 164 | 0.022373 | 0.00013642 | No
6/05/2019 | 09:51:09 | PP09 | Rural Long | Planned |  | 74 | 238 | 0.12854 | 0.00054008 | No
6/05/2019 | 10:05:51 | GA35 | Rural Long | Planned |  | 2 | 242 | 0.0035324 | 1.46e-05 | No
6/05/2019 | 10:58:21 | EL19 | Urban | Planned |  | 166 | 150 | 0.039807 | 0.00026538 | No
6/05/2019 | 12:13:58 | SA19 | Urban | Planned |  | 101 | 58 | 0.009365 | 0.00016147 | No
6/05/2019 | 12:41:04 | MV33 | Rural Short | Planned |  | 8 | 30 | 0.001788 | 5.96e-05 | No
6/05/2019 | 12:47:05 | HK05 | Rural Long | Unknown | Unknown | 57 | 77 | 0.032032 | 0.00041601 | No
6/05/2019 | 14:11:56 | M93 | Rural Long | Asset failure | Distribution substation | 50 | 194.84 | 0.0711 | 0.00036492 | No
6/05/2019 | 15:06:07 | CBD103A | Urban | Asset failure | HV | 1263 | 145.7451 | 0.29428 | 0.0020191 | No
6/05/2019 | 15:45:20 | HH341E | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
6/05/2019 | 16:58:22 | LX21 | Rural Short | Animal | Animal impact | 166.3334 | 119.6834 | 0.14831 | 0.0012392 | No
6/05/2019 | 16:59:15 | NL511B | Urban | Asset failure | LV | 1 | 94 | 0.00015028 | 1.6e-06 | No
6/05/2019 | 17:05:56 | SM349F | Urban | Planned |  | 71 | 1 | 0.00011351 | 0.00011351 | No
6/05/2019 | 20:01:10 | AP372D | Urban | Asset failure | HV | 11 | 59 | 0.0010375 | 1.759e-05 | No
6/05/2019 | 20:19:33 | NL234C | Urban | Unknown | Unknown | 17.6666 | 82 | 0.0023159 | 2.824e-05 | No
7/05/2019 | 00:42:28 | ME231B | Urban | Overloads |  | 1 | 110 | 0.00017585 | 1.6e-06 | No
7/05/2019 | 04:17:22 | SM349C | Urban | Animal | Animal impact | 9 | 96 | 0.0013813 | 1.439e-05 | No
7/05/2019 | 08:16:18 | GA53 | Rural Short | Asset failure | LV | 1 | 121 | 0.00090147 | 7.45e-06 | No
7/05/2019 | 09:11:38 | GA800A | Rural Short | Planned |  | 11 | 49 | 0.0040156 | 8.195e-05 | No
7/05/2019 | 09:22:53 | SM216A | Urban | Planned |  | 121 | 273 | 0.052809 | 0.00019344 | No
7/05/2019 | 09:23:39 | NU19 | Rural Long | Planned |  | 5 | 66 | 0.0024084 | 3.649e-05 | No
7/05/2019 | 09:25:56 | HH496G | Urban | Planned |  | 10 | 17 | 0.00027177 | 1.599e-05 | No
7/05/2019 | 09:32:12 | W18 | Rural Long | Planned |  | 5 | 200 | 0.0072983 | 3.649e-05 | No
7/05/2019 | 09:32:31 | CN83 | Rural Long | Planned |  | 24 | 195 | 0.034156 | 0.00017516 | No
7/05/2019 | 09:45:56 | NL111C | Urban | Planned |  | 83 | 169 | 0.022425 | 0.00013269 | No
7/05/2019 | 09:46:07 | SM216C | Urban | Planned |  | 3 | 14 | 6.714e-05 | 4.8e-06 | No
7/05/2019 | 10:01:10 | GA36 | Rural Long | Unknown | Unknown | 1 | 142 | 0.0010364 | 7.3e-06 | No
7/05/2019 | 10:06:25 | CN27 | Rural Long | Other |  | 1 | 125 | 0.00091229 | 7.3e-06 | No
7/05/2019 | 10:17:08 | EL20 | Urban | Planned |  | 36 | 257 | 0.014791 | 5.755e-05 | No
7/05/2019 | 10:27:14 | PA11 | Rural Long | Unknown | Unknown | 89 | 205 | 0.13316 | 0.00064955 | No
7/05/2019 | 11:08:57 | GU32 | Rural Long | Planned |  | 3 | 31 | 0.00067875 | 2.19e-05 | No
7/05/2019 | 11:25:22 | CV19 | Rural Long | Planned |  | 1 | 97 | 0.00070794 | 7.3e-06 | No
7/05/2019 | 12:08:30 | AP355H | Urban | Asset failure | LV | 3.3333 | 188 | 0.0010018 | 5.33e-06 | No
7/05/2019 | 12:48:28 | SM216C | Urban | Planned |  | 3 | 149 | 0.00071461 | 4.8e-06 | No
7/05/2019 | 12:58:33 | MG17 | Rural Long | Asset failure | HV | 21 | 250 | 0.038316 | 0.00015327 | No
7/05/2019 | 15:40:57 | GA43 | Rural Short | Unknown | Unknown | 4.6667 | 65 | 0.0022599 | 3.477e-05 | No
7/05/2019 | 15:52:25 | HH428B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 163 | 0.00026058 | 1.6e-06 | No
7/05/2019 | 16:01:28 | NU27 | Rural Long | Unknown | Unknown | 1 | 195 | 0.0014232 | 7.3e-06 | No
7/05/2019 | 16:07:42 | NU31 | Rural Long | Unknown | Unknown | 2 | 88 | 0.0012845 | 1.46e-05 | No
7/05/2019 | 16:08:32 | NL511A | Urban | Overloads |  | 1 | 169 | 0.00027018 | 1.6e-06 | No
7/05/2019 | 16:16:45 | NU31 | Rural Long | Weather |  | 1 | 94 | 0.00068604 | 7.3e-06 | No
7/05/2019 | 16:25:01 | AP373A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 246 | 61.8171 | 0.024311 | 0.00039327 | No
7/05/2019 | 16:25:27 | AP373A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 23.6667 | 60 | 0.0022701 | 3.784e-05 | No
7/05/2019 | 16:50:42 | SA744D | Urban | Asset failure | LV | 1 | 128 | 0.00020463 | 1.6e-06 | No
7/05/2019 | 17:03:06 | NL234C | Urban | Unknown | Unknown | 29.6666 | 43 | 0.0020394 | 4.743e-05 | No
7/05/2019 | 17:44:12 | AP214D | Urban | Asset failure | HV | 84 | 192 | 0.025783 | 0.00013429 | No
7/05/2019 | 17:55:56 | HH177D | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
7/05/2019 | 17:59:11 | MB12 | Rural Short | Other |  | 1 | 226 | 0.0016837 | 7.45e-06 | No
7/05/2019 | 18:05:05 | R08 | Rural Long | Asset failure | LV | 2 | 248 | 0.00362 | 1.46e-05 | No
7/05/2019 | 18:30:20 | GU43 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 149 | 117 | 0.12723 | 0.0010875 | No
7/05/2019 | 18:41:09 | HH177B | Urban | Unknown | Unknown | 1 | 166 | 0.00026538 | 1.6e-06 | No
7/05/2019 | 19:09:28 | ME427D | Urban | Asset failure | LV | 1 | 300 | 0.0004796 | 1.6e-06 | No
7/05/2019 | 19:10:15 | AP373A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 239 | 0.00038208 | 1.6e-06 | No
7/05/2019 | 22:28:34 | MG39 | Rural Short | Weather |  | 657 | 264.2451 | 1.2934 | 0.0048947 | No
7/05/2019 | 22:28:34 | MG39 | Rural Short | Weather |  | 0 | 2.2465 | 0.027633 | 0 | No
7/05/2019 | 22:30:51 | CN01 | Rural Long | Asset failure | LV | 1 | 154 | 0.0011239 | 7.3e-06 | No
8/05/2019 | 03:19:33 | SM137A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1843 | 112.5491 | 0.33161 | 0.0029464 | No
8/05/2019 | 07:08:45 | CN71 | Rural Long | Planned |  | 1 | 18 | 0.00013137 | 7.3e-06 | No
8/05/2019 | 07:31:52 | VH32 | Rural Short | Overloads |  | 1 | 163 | 0.0012144 | 7.45e-06 | No
8/05/2019 | 08:33:33 | EL17 | Urban | Planned |  | 27 | 87 | 0.0037553 | 4.316e-05 | No
8/05/2019 | 08:59:26 | SA34 | Urban | Planned |  | 24 | 197 | 0.0075585 | 3.837e-05 | No
8/05/2019 | 09:03:24 | SG04 | Rural Short | Planned |  | 50 | 330 | 0.12293 | 0.00037251 | No
8/05/2019 | 09:11:51 | SM216G | Urban | Asset failure | LV | 74 | 143 | 0.016917 | 0.0001183 | No
8/05/2019 | 09:12:22 | MTB71 | Rural Short | Planned |  | 66 | 308 | 0.15145 | 0.00049171 | No
8/05/2019 | 09:20:27 | CN83 | Rural Long | Planned |  | 53 | 313 | 0.12107 | 0.00038681 | No
8/05/2019 | 09:21:54 | PA13 | Rural Long | Planned |  | 237 | 264 | 0.45664 | 0.0017297 | No
8/05/2019 | 09:22:40 | SA38 | Urban | Planned |  | 4 | 314 | 0.0020079 | 6.39e-06 | No
8/05/2019 | 09:43:28 | BM12 | Rural Short | Planned |  | 5 | 49 | 0.0018253 | 3.725e-05 | No
8/05/2019 | 09:44:23 | M13 | Rural Long | Planned |  | 38 | 16 | 0.0044374 | 0.00027734 | No
8/05/2019 | 09:57:26 | MT26 | Rural Long | Planned |  | 53 | 253 | 0.097863 | 0.00038681 | No
8/05/2019 | 10:20:39 | CV24 | Rural Long | Planned |  | 1 | 267 | 0.0019487 | 7.3e-06 | No
8/05/2019 | 10:32:27 | G25 | Rural Long | Planned |  | 1 | 195 | 0.0014232 | 7.3e-06 | No
8/05/2019 | 11:59:00 | EL17 | Urban | Planned |  | 10 | 63 | 0.0010072 | 1.599e-05 | No
8/05/2019 | 12:08:10 | NL451C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2440 | 43.5898 | 0.17003 | 0.0039008 | No
8/05/2019 | 14:06:19 | EL15 | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 193 | 0.00061709 | 3.2e-06 | No
8/05/2019 | 15:23:49 | HH145A | Urban | Overloads |  | 1 | 224 | 0.0003581 | 1.6e-06 | No
8/05/2019 | 15:35:55 | NL234A | Urban | Asset failure | LV | 1 | 119 | 0.00019024 | 1.6e-06 | No
8/05/2019 | 15:48:28 | PA15 | Rural Long | Unknown | Unknown | 73 | 47 | 0.025041 | 0.00053278 | No
8/05/2019 | 16:27:49 | W32 | Rural Long | Unknown | Unknown | 10 | 394 | 0.028755 | 7.298e-05 | No
8/05/2019 | 16:53:50 | SM350E | Urban | Asset failure | LV | 72 | 67 | 0.007712 | 0.0001151 | No
8/05/2019 | 20:48:59 | HH432B | Urban | Overloads |  | 1 | 173 | 0.00027657 | 1.6e-06 | No
9/05/2019 | 00:36:56 | CBD353N | CBD | Planned |  | 22 | 141 | 0.60215 | 0.0042706 | No
9/05/2019 | 06:13:05 | W01 | Rural Long | Asset failure | LV | 1 | 434 | 0.0031675 | 7.3e-06 | No
9/05/2019 | 06:42:08 | SG09 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 21 | 105 | 0.016428 | 0.00015645 | No
9/05/2019 | 06:53:22 | YK19 | Rural Long | Asset failure | HV | 55 | 159 | 0.063824 | 0.00040141 | No
9/05/2019 | 08:34:32 | AP227A | Urban | Planned |  | 47 | 47 | 0.0035315 | 7.514e-05 | No
9/05/2019 | 08:37:50 | WHY08 | Urban | Planned |  | 51 | 277 | 0.022584 | 8.153e-05 | No
9/05/2019 | 08:52:15 | HH130B | Urban | Planned |  | 86 | 210 | 0.028872 | 0.00013749 | No
9/05/2019 | 08:58:20 | NL759B | Urban | Planned |  | 2 | 61 | 0.00019504 | 3.2e-06 | No
9/05/2019 | 09:18:10 | NL210A | Urban | Planned |  | 19 | 219 | 0.0066521 | 3.037e-05 | No
9/05/2019 | 09:23:05 | BT02 | Rural Long | Planned |  | 8 | 140 | 0.0081741 | 5.839e-05 | No
9/05/2019 | 09:25:42 | AP424A | Urban | Planned |  | 1 | 279 | 0.00044603 | 1.6e-06 | No
9/05/2019 | 09:45:39 | GA21 | Rural Long | Planned |  | 2 | 63 | 0.00091959 | 1.46e-05 | No
9/05/2019 | 09:49:14 | W20 | Rural Long | Planned |  | 17 | 322 | 0.039951 | 0.00012407 | No
9/05/2019 | 09:57:50 | AP424E | Urban | Planned |  | 1 | 247 | 0.00039487 | 1.6e-06 | No
9/05/2019 | 10:08:06 | MT01 | Rural Long | Planned |  | 8 | 51 | 0.0029777 | 5.839e-05 | No
9/05/2019 | 10:17:30 | PA14 | Rural Long | Planned |  | 31 | 5 | 0.0011312 | 0.00022625 | No
9/05/2019 | 10:18:27 | GA36 | Rural Long | Planned |  | 2 | 19 | 0.00027734 | 1.46e-05 | No
9/05/2019 | 10:34:13 | R09 | Rural Long | Unknown | Unknown | 1.6667 | 151 | 0.0018368 | 1.216e-05 | No
9/05/2019 | 10:50:00 | SM172F | Urban | Weather |  | 1964 | 91 | 0.28572 | 0.0031398 | No
9/05/2019 | 10:50:50 | R21 | Rural Long | Planned |  | 2 | 156 | 0.0022771 | 1.46e-05 | No
9/05/2019 | 11:02:46 | MV64 | Urban | Animal | Animal impact | 1 | 363 | 0.00058032 | 1.6e-06 | No
9/05/2019 | 11:56:22 | SA36 | Urban | Third Party | Vehicle impact | 2.6667 | 51 | 0.00021742 | 4.26e-06 | No
9/05/2019 | 13:14:51 | ME116A | Urban | Asset failure | LV | 15.3333 | 110 | 0.0026964 | 2.451e-05 | No
9/05/2019 | 13:16:20 | HH403B | Urban | Asset failure | LV | 1 | 405 | 0.00064746 | 1.6e-06 | No
9/05/2019 | 13:55:31 | SB01 | Rural Long | Asset failure | Distribution substation | 52 | 251 | 0.095258 | 0.00037951 | No
9/05/2019 | 14:08:33 | MG43 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1512 | 20 | 0.22529 | 0.011265 | No
9/05/2019 | 14:27:57 | R09 | Rural Long | Unknown | Unknown | 1.6667 | 221 | 0.0026882 | 1.216e-05 | No
9/05/2019 | 14:53:39 | HH432C | Urban | Asset failure | LV | 1 | 648 | 0.0010359 | 1.6e-06 | No
9/05/2019 | 15:21:05 | SM410C | Urban | Weather |  | 29.6666 | 84 | 0.0039839 | 4.743e-05 | No
9/05/2019 | 15:57:56 | SA17 | Urban | Asset failure | LV | 1 | 94 | 0.00015028 | 1.6e-06 | No
9/05/2019 | 17:09:13 | EL02 | Urban | Overloads |  | 1 | 137 | 0.00021902 | 1.6e-06 | No
9/05/2019 | 17:35:41 | SM411E | Urban | Asset failure | LV | 1 | 240 | 0.00038368 | 1.6e-06 | No
9/05/2019 | 17:48:01 | SM349E | Urban | Asset failure | LV | 25.6666 | 78 | 0.0032005 | 4.103e-05 | No
9/05/2019 | 18:02:57 | M81 | Rural Long | Asset failure | LV | 1 | 50 | 0.00036492 | 7.3e-06 | No
9/05/2019 | 18:05:00 | AP373E | Urban | Unknown | Unknown | 225 | 145.2 | 0.052229 | 0.0003597 | No
9/05/2019 | 18:51:58 | BM44 | Rural Short | Unknown | Unknown | 26 | 115 | 0.022276 | 0.0001937 | No
9/05/2019 | 20:47:09 | HH341E | Urban | Overloads |  | 1 | 211 | 0.00033732 | 1.6e-06 | No
9/05/2019 | 21:36:13 | AP226A | Urban | Asset failure | LV | 28 | 139 | 0.006222 | 4.476e-05 | No
9/05/2019 | 21:48:46 | SM216G | Urban | Asset failure | LV | 1 | 223 | 0.0003565 | 1.6e-06 | No
9/05/2019 | 23:55:21 | AP227D | Urban | Planned |  | 141 | 257 | 0.057931 | 0.00022541 | No
10/05/2019 | 00:06:11 | NL511A | Urban | Asset failure | LV | 1 | 118 | 0.00018864 | 1.6e-06 | No
10/05/2019 | 00:38:01 | BM33 | Rural Short | Unknown | Unknown | 5 | 16 | 0.00059601 | 3.725e-05 | No
10/05/2019 | 04:07:27 | SSD440 | Rural Short | Asset failure | Zone substation | 133 | 503 | 0.49841 | 0.00099087 | No
10/05/2019 | 04:07:27 | SSD440 | Rural Long | Asset failure | Zone substation | 252 | 504 | 0.92695 | 0.0018392 | No
10/05/2019 | 06:02:45 | MG46 | Rural Short | Asset failure | LV | 2 | 119 | 0.0017731 | 1.49e-05 | No
10/05/2019 | 06:39:01 | MB23 | Rural Short | Animal | Animal impact | 831 | 99 | 0.61292 | 0.0061911 | No
10/05/2019 | 07:51:57 | CN81 | Rural Long | Asset failure | LV | 12 | 176 | 0.015414 | 8.758e-05 | No
10/05/2019 | 08:30:56 | WHY03 | Urban | Asset failure | LV | 1 | 166 | 0.00026538 | 1.6e-06 | No
10/05/2019 | 08:41:44 | SA17 / SA18 | Urban | Planned |  | 94 | 268.3191 | 0.040322 | 0.00015028 | No
10/05/2019 | 08:50:07 | PL33 | Rural Long | Planned |  | 1 | 275 | 0.002007 | 7.3e-06 | No
10/05/2019 | 08:53:02 | NU19 | Rural Long | Planned |  | 51 | 323 | 0.12023 | 0.00037222 | No
10/05/2019 | 08:56:43 | VH44 | Rural Short | Planned |  | 1 | 253 | 0.0018849 | 7.45e-06 | No
10/05/2019 | 09:00:54 | SG04 | Rural Short | Planned |  | 16 | 234 | 0.027893 | 0.0001192 | No
10/05/2019 | 09:04:48 | SG02 | Rural Short | Planned |  | 86 | 449 | 0.28768 | 0.00064071 | No
10/05/2019 | 09:07:37 | GA22 | Rural Short | Planned |  | 176 | 296.8182 | 0.3892 | 0.0013112 | No
10/05/2019 | 09:09:19 | SD34300 | Rural Short | Planned |  | 134 | 9.1045 | 0.0090892 | 0.00099832 | No
10/05/2019 | 09:12:13 | SM349D | Urban | Asset failure | LV | 1 | 366 | 0.00058512 | 1.6e-06 | No
10/05/2019 | 09:20:56 | SG07 | Rural Short | Planned |  | 10 | 217 | 0.016167 | 7.45e-05 | No
10/05/2019 | 09:26:45 | CN24 | Rural Long | Asset failure | LV | 1 | 350 | 0.0025544 | 7.3e-06 | No
10/05/2019 | 09:48:36 | ST13 | Rural Short | Planned |  | 19 | 171 | 0.024206 | 0.00014155 | No
10/05/2019 | 09:56:35 | SM216C | Urban | Third Party | Other | 3002 | 3 | 0.014398 | 0.0047992 | No
10/05/2019 | 10:16:19 | SG13 | Rural Short | Planned |  | 93 | 218 | 0.15104 | 0.00069286 | No
10/05/2019 | 10:16:25 | LX25 | Rural Short | Unknown | Unknown | 12.3333 | 101 | 0.0092804 | 9.189e-05 | No
10/05/2019 | 10:25:51 | HH386B | Urban | Asset failure | Distribution substation | 71 | 168 | 0.019069 | 0.00011351 | No
10/05/2019 | 10:42:25 | HH145B / HH496A | Urban | Planned |  | 514 | 8.1654 | 0.0067096 | 0.00082172 | No
10/05/2019 | 12:06:00 | SM216A | Urban | Asset failure | HV | 32 | 189 | 0.0096688 | 5.116e-05 | No
10/05/2019 | 12:19:08 | M21 | Rural Long | Asset failure | HV | 396 | 160.2197 | 0.46306 | 0.0028901 | No
10/05/2019 | 12:45:07 | SD31200 | Rural Long | Unknown | Unknown | 2 | 161 | 0.0023501 | 1.46e-05 | No
10/05/2019 | 13:37:04 | LX41 | Rural Short | Asset failure | LV | 1 | 121 | 0.00090147 | 7.45e-06 | No
10/05/2019 | 14:50:15 | AP149C | Urban | Third Party | Vehicle impact | 1 | 206 | 0.00032933 | 1.6e-06 | No
10/05/2019 | 16:03:14 | MTB13 | Rural Short | Unknown | Unknown | 1 | 1 | 7.45e-06 | 7.45e-06 | No
10/05/2019 | 17:29:59 | NL115D | Urban | Asset failure | LV | 1 | 214 | 0.00034212 | 1.6e-06 | No
10/05/2019 | 17:33:31 | SM179C | Urban | Asset failure | LV | 1 | 267 | 0.00042685 | 1.6e-06 | No
10/05/2019 | 17:35:22 | MT11 | Rural Long | Overloads |  | 3 | 315 | 0.0068969 | 2.19e-05 | No
10/05/2019 | 18:42:36 | GA02 | Rural Short | Unknown | Unknown | 1664 | 4.5192 | 0.056025 | 0.012397 | No
10/05/2019 | 21:22:28 | NL210E | Urban | Asset failure | HV | 60 | 49 | 0.0047001 | 9.592e-05 | No
10/05/2019 | 21:26:50 | VH22 | Rural Short | Overloads |  | 1 | 226 | 0.0016837 | 7.45e-06 | No
10/05/2019 | 22:48:08 | HH107B | Urban | Third Party | Vehicle impact | 66 | 160 | 0.016882 | 0.00010551 | No
10/05/2019 | 23:47:05 | BM52 | Urban | Overloads |  | 1 | 910 | 0.0014548 | 1.6e-06 | No
11/05/2019 | 00:28:16 | CL06 | Rural Long | Third Party | Vehicle impact | 337 | 156.3976 | 0.38467 | 0.0024595 | No
11/05/2019 | 06:46:10 | PA14 | Rural Long | Unknown | Unknown | 1 | 104 | 0.00075903 | 7.3e-06 | No
11/05/2019 | 08:33:00 | CBD155B-AMP-IMFC | CBD | Unknown | Unknown | 41 | 396.9512 | 3.1593 | 0.0079588 | No
11/05/2019 | 10:05:49 | SD59100 | Rural Long | Unknown | Unknown | 1 | 25 | 0.00018246 | 7.3e-06 | No
11/05/2019 | 10:12:28 | CN24 | Rural Long | Asset failure | LV | 1 | 335 | 0.0024449 | 7.3e-06 | No
11/05/2019 | 11:36:04 | PP03 | Urban | Overloads |  | 1 | 212 | 0.00033892 | 1.6e-06 | No
11/05/2019 | 11:41:10 | SM126D | Urban | Overloads |  | 1 | 369 | 0.00058991 | 1.6e-06 | No
11/05/2019 | 15:07:51 | SSD528 | Rural Short | Unknown | Unknown | 2 | 3099 | 0.046176 | 1.49e-05 | No
11/05/2019 | 15:50:31 | SM349C | Urban | Asset failure | LV | 1 | 264 | 0.00042205 | 1.6e-06 | No
11/05/2019 | 19:16:20 | SM126C | Urban | Asset failure | LV | 1 | 335 | 0.00053556 | 1.6e-06 | No
11/05/2019 | 19:21:52 | EL01B | Urban | Asset failure | LV | 1 | 81 | 0.00012949 | 1.6e-06 | No
11/05/2019 | 20:16:59 | KA02 | Rural Short | Asset failure | LV | 1 | 174 | 0.0012963 | 7.45e-06 | No
11/05/2019 | 21:21:26 | ME347A | Urban | Asset failure | LV | 1 | 107 | 0.00017106 | 1.6e-06 | No
11/05/2019 | 22:02:17 | WHY10 | Urban | Asset failure | LV | 16.6667 | 84 | 0.0022381 | 2.664e-05 | No
11/05/2019 | 23:30:38 | ME347G | Urban | Planned |  | 1 | 302 | 0.0004828 | 1.6e-06 | No
12/05/2019 | 04:22:49 | CN31 | Rural Long | Asset failure | HV | 2 | 803 | 0.011721 | 1.46e-05 | No
12/05/2019 | 06:50:48 | MV33 | Rural Short | Unknown | Unknown | 3.6667 | 334 | 0.009124 | 2.732e-05 | No
12/05/2019 | 08:10:31 | CBD412A | CBD | Planned |  | 152 | 2 | 0.059012 | 0.029506 | No
12/05/2019 | 08:10:31 | CBD412A | CBD | Planned |  | 0 | 1 | 0.029506 | 0 | No
12/05/2019 | 08:10:31 | CBD412A | Urban | Planned |  | 6 | 2 | 1.918e-05 | 9.59e-06 | No
12/05/2019 | 08:10:31 | CBD412A | Urban | Planned |  | 0 | 1 | 9.59e-06 | 0 | No
12/05/2019 | 08:29:48 | EL02 / EL22 | Urban | Planned |  | 11 | 138.1818 | 0.00243 | 1.759e-05 | No
12/05/2019 | 08:50:01 | NL210D | Urban | Planned |  | 5 | 261 | 0.0020863 | 7.99e-06 | No
12/05/2019 | 08:54:31 | GU42 | Rural Long | Planned |  | 6 | 259 | 0.011342 | 4.379e-05 | No
12/05/2019 | 09:03:04 | CBD412H | Urban | Planned |  | 7 | 183 | 0.0020479 | 1.119e-05 | No
12/05/2019 | 09:47:12 | HH121E | Urban | Overloads |  | 1 | 376 | 0.0006011 | 1.6e-06 | No
12/05/2019 | 12:58:22 | EL260A | Urban | Unknown | Unknown | 10 | 93 | 0.0014868 | 1.599e-05 | No
12/05/2019 | 15:59:25 | EL11 | Urban | Asset failure | HV | 11 | 88.6364 | 0.0015587 | 1.759e-05 | No
12/05/2019 | 15:59:58 | WK43 | Rural Short | Unknown | Unknown | 45 | 180.9111 | 0.060652 | 0.00033526 | No
12/05/2019 | 17:04:44 | MV52 | Rural Short | Asset failure | LV | 1 | 251 | 0.00187 | 7.45e-06 | No
12/05/2019 | 17:31:11 | CV28 | Rural Long | Asset failure | HV | 19 | 449 | 0.062262 | 0.00013867 | No
12/05/2019 | 17:36:42 | VH33 | Rural Short | Asset failure | LV | 2 | 490 | 0.0073012 | 1.49e-05 | No
12/05/2019 | 20:07:34 | AP226D | Urban | Animal | Animal impact | 1 | 111 | 0.00017745 | 1.6e-06 | No
12/05/2019 | 21:26:35 | AP149E | Urban | Overloads |  | 1 | 105 | 0.00016786 | 1.6e-06 | No
12/05/2019 | 22:21:06 | HH341B | Urban | Asset failure | LV | 1 | 293 | 0.00046841 | 1.6e-06 | No
12/05/2019 | 22:44:12 | ME116D | Urban | Unknown | Unknown | 29.3333 | 116 | 0.0054398 | 4.689e-05 | No
12/05/2019 | 22:54:37 | ME131A | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
13/05/2019 | 05:20:31 | CBD103E | Urban | Unknown | Unknown | 530.6669 | 7.0025 | 0.0059407 | 0.00084836 | No
13/05/2019 | 07:23:22 | WK65 | Rural Short | Asset failure | LV | 1 | 205 | 0.0015273 | 7.45e-06 | No
13/05/2019 | 07:27:17 | G17 | Rural Long | Unknown | Unknown | 14 | 763 | 0.077961 | 0.00010218 | No
13/05/2019 | 07:54:56 | EL19 | Urban | Unknown | Unknown | 313.0001 | 11.7987 | 0.0059039 | 0.00050039 | No
13/05/2019 | 08:50:11 | HH130B | Urban | Planned |  | 216 | 145 | 0.05007 | 0.00034531 | No
13/05/2019 | 09:03:35 | MI32 | Rural Long | Planned |  | 4 | 236 | 0.0068896 | 2.919e-05 | No
13/05/2019 | 09:24:49 | GA745A / GA02 | Rural Short | Planned |  | 389 | 261.0617 | 0.75658 | 0.0028981 | No
13/05/2019 | 09:25:57 | ST35 | Rural Long | Planned |  | 1 | 40 | 0.00029193 | 7.3e-06 | No
13/05/2019 | 09:26:24 | KA14 | Rural Long | Planned |  | 1 | 38 | 0.00027734 | 7.3e-06 | No
13/05/2019 | 09:30:21 | AP227D | Urban | Planned |  | 123 | 262 | 0.051519 | 0.00019664 | No
13/05/2019 | 09:34:03 | GA29 | Rural Long | Asset failure | LV | 1 | 132 | 0.00096338 | 7.3e-06 | No
13/05/2019 | 09:35:45 | HH522B | Urban | Planned |  | 82 | 246 | 0.032248 | 0.00013109 | No
13/05/2019 | 10:15:04 | MTB22 | Rural Short | Planned |  | 53 | 250 | 0.098714 | 0.00039486 | No
13/05/2019 | 10:26:02 | ME200G | Urban | Planned |  | 146 | 74 | 0.017272 | 0.00023341 | No
13/05/2019 | 10:32:01 | GA25 | Rural Short | Network business | Network error | 3 | 57 | 0.001274 | 2.235e-05 | No
13/05/2019 | 10:59:36 | AP355E | Urban | Third Party | Vehicle impact | 1 | 491 | 0.00078495 | 1.6e-06 | No
13/05/2019 | 11:16:00 | CBD366M-GW2 | CBD | Asset failure | HV | 39 | 176 | 1.3324 | 0.0075706 | No
13/05/2019 | 12:16:28 | GA25 | Rural Short | Planned |  | 3 | 1546 | 0.034554 | 2.235e-05 | No
13/05/2019 | 12:35:20 | GU32 | Rural Long | Planned |  | 2 | 31 | 0.0004525 | 1.46e-05 | No
13/05/2019 | 12:47:14 | SM350F | Urban | Planned |  | 77 | 95 | 0.011694 | 0.0001231 | No
13/05/2019 | 15:37:31 | LX71 | Rural Long | Third Party | Vehicle impact | 24 | 274.2917 | 0.048045 | 0.00017516 | No
13/05/2019 | 16:22:05 | SA20 | Urban | Asset failure | LV | 1 | 199 | 0.00031814 | 1.6e-06 | No
13/05/2019 | 19:06:49 | NL210C | Urban | Vegetation | Grow-in - NSP responsibility | 18 | 162 | 0.0046617 | 2.878e-05 | No
13/05/2019 | 19:44:05 | SM411E | Urban | Asset failure | LV | 1 | 207 | 0.00033093 | 1.6e-06 | No
13/05/2019 | 20:25:15 | AP424E | Urban | Overloads |  | 1 | 340 | 0.00054355 | 1.6e-06 | No
13/05/2019 | 22:15:49 | WK43 | Rural Short | Asset failure | Distribution substation | 45 | 311.3333 | 0.10438 | 0.00033526 | No
13/05/2019 | 22:46:46 | HH145A | Urban | Asset failure | LV | 1 | 246 | 0.00039327 | 1.6e-06 | No
13/05/2019 | 22:48:37 | SA32 | Urban | Unknown | Unknown | 24.6667 | 99 | 0.003904 | 3.943e-05 | No
14/05/2019 | 05:05:05 | SA32 | Urban | Asset failure | LV | 1 | 229 | 0.0003661 | 1.6e-06 | No
14/05/2019 | 06:53:27 | SM350C | Urban | Planned |  | 1 | 13 | 2.078e-05 | 1.6e-06 | No
14/05/2019 | 07:00:31 | SM126B | Urban | Overloads |  | 1 | 200 | 0.00031974 | 1.6e-06 | No
14/05/2019 | 07:28:59 | HH145B / HH496A | Urban | Planned |  | 144 | 68.5208 | 0.015774 | 0.00023021 | No
14/05/2019 | 07:28:59 | HH145B / HH496A | Urban | Planned |  | 0 | 1 | 0.00021902 | 0 | No
14/05/2019 | 08:02:47 | CL06 | Rural Long | Planned |  | 131 | 724.0153 | 0.69222 | 0.00095608 | No
14/05/2019 | 08:23:24 | GU43 | Rural Long | Planned |  | 3 | 413 | 0.0090426 | 2.19e-05 | No
14/05/2019 | 08:31:07 | PA02 | Urban | Planned |  | 9 | 173 | 0.0024891 | 1.439e-05 | No
14/05/2019 | 08:48:48 | SM402D | Urban | Planned |  | 150 | 59 | 0.014148 | 0.0002398 | No
14/05/2019 | 08:51:27 | SD34102 | Rural Long | Planned |  | 2 | 187 | 0.0027296 | 1.46e-05 | No
14/05/2019 | 09:09:27 | SB22 | Rural Long | Planned |  | 17 | 258 | 0.032011 | 0.00012407 | No
14/05/2019 | 09:30:32 | AP146B | Urban | Planned |  | 48 | 358 | 0.027472 | 7.674e-05 | No
14/05/2019 | 09:54:49 | NA51 | Rural Long | Planned |  | 1 | 193 | 0.0014086 | 7.3e-06 | No
14/05/2019 | 10:13:11 | MG45 | Urban | Asset failure | LV | 1 | 373 | 0.00059631 | 1.6e-06 | No
14/05/2019 | 10:58:35 | YK17 | Rural Long | Planned |  | 66 | 88 | 0.042389 | 0.00048169 | No
14/05/2019 | 10:58:58 | CBD27B | CBD | Third Party | Vehicle impact | 1 | 196 | 0.038047 | 0.00019412 | No
14/05/2019 | 11:18:24 | SA20 | Urban | Asset failure | LV | 1 | 378 | 0.0006043 | 1.6e-06 | No
14/05/2019 | 11:28:04 | NU05 | Rural Short | Planned |  | 3 | 163 | 0.0036431 | 2.235e-05 | No
14/05/2019 | 11:37:20 | MG24 | Rural Short | Planned |  | 2 | 197 | 0.0029354 | 1.49e-05 | No
14/05/2019 | 11:37:47 | LX51 | Rural Short | Asset failure | LV | 1 | 144 | 0.0010728 | 7.45e-06 | No
14/05/2019 | 11:54:02 | NL234A | Urban | Asset failure | LV | 17.3333 | 145 | 0.004018 | 2.771e-05 | No
14/05/2019 | 12:14:11 | WHY08 | Urban | Asset failure | LV | 25.3333 | 137 | 0.0055485 | 4.05e-05 | No
14/05/2019 | 12:16:51 | EL23 | Urban | Unknown | Unknown | 664 | 9.0783 | 0.0096368 | 0.0010615 | No
14/05/2019 | 13:15:50 | KA32 | Rural Long | Third Party | Vehicle impact | 35 | 84.2 | 0.021508 | 0.00025544 | No
14/05/2019 | 14:08:50 | HH177E | Urban | Asset failure | LV | 1 | 143 | 0.00022861 | 1.6e-06 | No
14/05/2019 | 14:14:16 | AP355F | Urban | Asset failure | LV | 2 | 365 | 0.001167 | 3.2e-06 | No
14/05/2019 | 15:15:43 | SM172F | Urban | Third Party | Vehicle impact | 1 | 107 | 0.00017106 | 1.6e-06 | No
14/05/2019 | 15:53:50 | CL09 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 75 | 0.0010948 | 1.46e-05 | No
14/05/2019 | 17:20:48 | HH428D | Urban | Asset failure | LV | 61 | 38 | 0.0037057 | 9.752e-05 | No
14/05/2019 | 17:49:55 | BM31 | Rural Short | Planned |  | 454 | 14 | 0.047353 | 0.0033824 | No
14/05/2019 | 18:19:00 | HH130A | Urban | Asset failure | HV | 3653 | 133.6805 | 0.78069 | 0.00584 | No
14/05/2019 | 19:19:31 | EL10 | Urban | Asset failure | LV | 1 | 149 | 0.0002382 | 1.6e-06 | No
14/05/2019 | 22:01:19 | CBD412H | Urban | Planned |  | 7 | 3223 | 0.036068 | 1.119e-05 | No
15/05/2019 | 06:20:22 | MI33 | Rural Long | Asset failure | HV | 50 | 540.58 | 0.19727 | 0.00036492 | No
15/05/2019 | 08:49:40 | W29 | Rural Long | Planned |  | 18 | 280 | 0.036784 | 0.00013137 | No
15/05/2019 | 08:58:04 | SA13 | Urban | Planned |  | 83 | 338 | 0.044849 | 0.00013269 | No
15/05/2019 | 08:58:49 | HH409C | Urban | Planned |  | 77 | 346 | 0.042592 | 0.0001231 | No
15/05/2019 | 09:16:16 | MV12 | Urban | Planned |  | 4 | 12 | 7.674e-05 | 6.39e-06 | No
15/05/2019 | 09:24:40 | MTB61 | Rural Short | Planned |  | 117 | 383 | 0.33385 | 0.00087167 | No
15/05/2019 | 09:25:56 | WHY14 | Urban | Planned |  | 106 | 286 | 0.048465 | 0.00016946 | No
15/05/2019 | 09:35:11 | CM05 | Rural Long | Planned |  | 4 | 346 | 0.010101 | 2.919e-05 | No
15/05/2019 | 09:40:07 | SA31 | Urban | Planned |  | 107 | 1547 | 0.26463 | 0.00017106 | No
15/05/2019 | 10:05:18 | YK23 | Rural Long | Planned |  | 117 | 281 | 0.23995 | 0.00085391 | No
15/05/2019 | 11:04:22 | ME347C | Urban | Planned |  | 1 | 210 | 0.00033572 | 1.6e-06 | No
15/05/2019 | 11:10:28 | NL511A | Urban | Planned |  | 96 | 92 | 0.01412 | 0.00015347 | No
15/05/2019 | 11:18:49 | WK72 | Rural Short | Third Party | Vehicle impact | 572 | 106.3322 | 0.45313 | 0.0042615 | No
15/05/2019 | 11:57:31 | EL14 | Urban | Asset failure | LV | 1 | 138 | 0.00022062 | 1.6e-06 | No
15/05/2019 | 11:58:17 | SM350E | Urban | Planned |  | 1 | 186 | 0.00029735 | 1.6e-06 | No
15/05/2019 | 12:00:32 | MG03 | Rural Short | Animal | Animal impact | 1 | 79 | 0.00058856 | 7.45e-06 | No
15/05/2019 | 12:04:18 | GA28 | Rural Long | Planned |  | 1 | 1 | 7.3e-06 | 7.3e-06 | No
15/05/2019 | 12:56:09 | VH33 | Rural Short | Unknown | Unknown | 136 | 3.3971 | 0.003442 | 0.0010132 | No
15/05/2019 | 13:01:05 | SM349F | Urban | Asset failure | LV | 142 | 78 | 0.017707 | 0.00022701 | No
15/05/2019 | 13:42:39 | KI55 | Rural Long | Unknown | Unknown | 1 | 27 | 0.00019706 | 7.3e-06 | No
15/05/2019 | 17:16:29 | CN31 | Rural Long | Asset failure | HV | 16 | 657.875 | 0.076822 | 0.00011677 | No
15/05/2019 | 18:08:43 | PA02 | Urban | Asset failure | LV | 1 | 131 | 0.00020943 | 1.6e-06 | No
15/05/2019 | 18:35:55 | G32 | Rural Long | Asset failure | LV | 2 | 388 | 0.0056635 | 1.46e-05 | No
15/05/2019 | 20:15:32 | SM349H | Urban | Asset failure | LV | 1 | 92 | 0.00014708 | 1.6e-06 | No
15/05/2019 | 20:28:44 | NL115B | Urban | Asset failure | LV | 1 | 148 | 0.0002366 | 1.6e-06 | No
16/05/2019 | 05:57:47 | HH121E | Urban | Other |  | 1 | 124 | 0.00019824 | 1.6e-06 | No
16/05/2019 | 07:41:13 | NA04 | Rural Long | Unknown | Unknown | 13 | 99 | 0.009393 | 9.488e-05 | No
16/05/2019 | 08:11:53 | MTB13 | Rural Short | Planned |  | 68 | 158 | 0.080044 | 0.00050661 | No
16/05/2019 | 08:34:30 | VH33 | Rural Short | Asset failure | LV | 2 | 159 | 0.0023691 | 1.49e-05 | No
16/05/2019 | 08:45:13 | W20 | Rural Long | Planned |  | 5 | 278 | 0.010145 | 3.649e-05 | No
16/05/2019 | 08:48:20 | NU19 | Rural Long | Planned |  | 5 | 324 | 0.011823 | 3.649e-05 | No
16/05/2019 | 09:00:16 | AP132D | Urban | Planned |  | 168 | 67.8393 | 0.01822 | 0.00026858 | No
16/05/2019 | 09:23:49 | GA36 | Rural Long | Planned |  | 3 | 160 | 0.0035032 | 2.19e-05 | No
16/05/2019 | 09:40:18 | AP351E | Urban | Planned |  | 1 | 65 | 0.00010391 | 1.6e-06 | No
16/05/2019 | 09:43:54 | MB81 | Rural Long | Planned |  | 56 | 279 | 0.11403 | 0.00040871 | No
16/05/2019 | 09:50:16 | YK17 | Rural Long | Planned |  | 48 | 287 | 0.10054 | 0.00035032 | No
16/05/2019 | 09:54:09 | SD34102 | Rural Long | Planned |  | 1 | 60 | 0.0004379 | 7.3e-06 | No
16/05/2019 | 09:59:03 | GA02 | Rural Short | Animal | Animal impact | 49 | 112 | 0.040886 | 0.00036506 | No
16/05/2019 | 10:04:22 | NL234C | Urban | Planned |  | 41 | 343 | 0.022482 | 6.555e-05 | No
16/05/2019 | 10:06:15 | SA744C | Urban | Asset failure | LV | 1 | 176 | 0.00028137 | 1.6e-06 | No
16/05/2019 | 10:32:21 | PL07 | Urban | Planned |  | 44 | 5 | 0.00035171 | 7.034e-05 | No
16/05/2019 | 10:37:52 | SM216A / SM216B | Urban | Planned |  | 173 | 276.5665 | 0.07649 | 0.00027657 | No
16/05/2019 | 10:40:43 | GA27 | Rural Long | Planned |  | 3 | 130 | 0.0028464 | 2.19e-05 | No
16/05/2019 | 12:41:43 | GA47 | Rural Long | Planned |  | 52 | 79 | 0.029982 | 0.00037951 | No
16/05/2019 | 16:12:18 | SA16 | Urban | Asset failure | LV | 1 | 53 | 8.473e-05 | 1.6e-06 | No
16/05/2019 | 17:12:52 | HH107B | Urban | Asset failure | LV | 33 | 82 | 0.004326 | 5.276e-05 | No
16/05/2019 | 17:52:43 | NL451C | Urban | Asset failure | LV | 1 | 189 | 0.00030215 | 1.6e-06 | No
16/05/2019 | 17:54:13 | NA52 | Rural Long | Asset failure | LV | 13.3333 | 184 | 0.017905 | 9.731e-05 | No
16/05/2019 | 18:41:49 | SM411E | Urban | Overloads |  | 1 | 226 | 0.0003613 | 1.6e-06 | No
16/05/2019 | 23:25:21 | AP227D | Urban | Planned |  | 85 | 270 | 0.03669 | 0.00013589 | No
17/05/2019 | 08:33:33 | MTB12 | Rural Short | Planned |  | 177 | 382.3729 | 0.50423 | 0.0013187 | No
17/05/2019 | 08:37:53 | AP227A | Urban | Planned |  | 77 | 111 | 0.013664 | 0.0001231 | No
17/05/2019 | 08:56:30 | VH12 | Rural Short | Planned |  | 1 | 366 | 0.0027268 | 7.45e-06 | No
17/05/2019 | 08:58:43 | NL544B | Urban | Planned |  | 176 | 317 | 0.089193 | 0.00028137 | No
17/05/2019 | 09:02:34 | BT27 | Rural Long | Unknown | Unknown | 14 | 83 | 0.0084807 | 0.00010218 | No
17/05/2019 | 09:05:22 | AP227A | Urban | Planned |  | 227 | 129 | 0.046814 | 0.0003629 | No
17/05/2019 | 09:09:19 | GA48 | Rural Short | Planned |  | 1 | 322 | 0.0023989 | 7.45e-06 | No
17/05/2019 | 09:11:13 | AP132D | Urban | Planned |  | 256 | 112.4766 | 0.046032 | 0.00040926 | No
17/05/2019 | 09:17:19 | CN25 | Rural Long | Planned |  | 1 | 21 | 0.00015327 | 7.3e-06 | No
17/05/2019 | 09:22:20 | SG04 | Rural Short | Planned |  | 11 | 192 | 0.015735 | 8.195e-05 | No
17/05/2019 | 09:35:52 | SM216D | Urban | Asset failure | LV | 112 | 311 | 0.055685 | 0.00017905 | No
17/05/2019 | 09:38:33 | PL07 | Urban | Planned |  | 15 | 65 | 0.0015587 | 2.398e-05 | No
17/05/2019 | 09:45:07 | ME116A | Urban | Planned |  | 1 | 14699 | 0.023499 | 1.6e-06 | No
17/05/2019 | 09:45:51 | GA41 | Rural Long | Planned |  | 64 | 254 | 0.11864 | 0.00046709 | No
17/05/2019 | 09:55:39 | HH428C | Urban | Planned |  | 22 | 147 | 0.0051701 | 3.517e-05 | No
17/05/2019 | 10:26:32 | AP355E | Urban | Planned |  | 165 | 85 | 0.022421 | 0.00026378 | No
17/05/2019 | 10:27:15 | G08 | Rural Long | Planned |  | 77 | 239 | 0.13431 | 0.00056197 | No
17/05/2019 | 10:37:41 | HH121D | Urban | Planned |  | 165 | 110 | 0.029016 | 0.00026378 | No
17/05/2019 | 10:52:47 | MTB13 | Rural Short | Asset failure | LV | 26 | 80 | 0.015496 | 0.0001937 | No
17/05/2019 | 10:58:23 | CN74 | Rural Long | Planned |  | 1 | 73 | 0.00053278 | 7.3e-06 | No
17/05/2019 | 12:07:33 | KA14 | Rural Long | Unknown | Unknown | 16 | 94 | 0.010977 | 0.00011677 | No
17/05/2019 | 12:12:48 | AP227C | Urban | Planned |  | 1 | 16 | 2.558e-05 | 1.6e-06 | No
17/05/2019 | 12:54:26 | AP146B | Urban | Planned |  | 2 | 129 | 0.00041246 | 3.2e-06 | No
17/05/2019 | 14:03:36 | HH409C | Urban | Asset failure | LV | 1 | 211 | 0.00033732 | 1.6e-06 | No
17/05/2019 | 14:24:04 | SM349F | Urban | Asset failure | LV | 1 | 93 | 0.00014868 | 1.6e-06 | No
17/05/2019 | 15:15:31 | PL07 | Urban | Asset failure | LV | 1 | 187 | 0.00029895 | 1.6e-06 | No
17/05/2019 | 15:40:08 | NU02 | Rural Long | Overloads |  | 1 | 124 | 0.00090499 | 7.3e-06 | No
17/05/2019 | 17:25:22 | AP227A | Urban | Overloads |  | 1 | 388 | 0.00062029 | 1.6e-06 | No
17/05/2019 | 18:12:20 | MG07 | Rural Short | Asset failure | LV | 35 | 176 | 0.045893 | 0.00026076 | No
17/05/2019 | 19:41:40 | AP132D | Urban | Other |  | 48.6667 | 194 | 0.015094 | 7.78e-05 | No
17/05/2019 | 19:42:05 | AP132D | Urban | Asset failure | HV | 137 | 189 | 0.041394 | 0.00021902 | No
17/05/2019 | 20:30:22 | AP132D | Urban | Unknown | Unknown | 647 | 123 | 0.12722 | 0.0010343 | No
17/05/2019 | 21:37:38 | MV63 | Rural Short | Asset failure | LV | 1 | 4 | 2.98e-05 | 7.45e-06 | No
17/05/2019 | 23:02:14 | AP132D | Urban | Asset failure | LV | 19.3333 | 129 | 0.0039871 | 3.091e-05 | No
18/05/2019 | 04:23:00 | SD1608 | Rural Short | Asset failure | Subtransmission | 1381 | 709 | 7.2947 | 0.010289 | No
18/05/2019 | 04:23:00 | SD1608 | Rural Long | Asset failure | Subtransmission | 2108 | 296.6471 | 4.5639 | 0.015385 | No
18/05/2019 | 06:48:00 | SD44300 | Rural Short | Planned |  | 1584 | 14 | 0.16521 | 0.011801 | No
18/05/2019 | 06:48:00 | SD44300 | Rural Long | Planned |  | 1183 | 14 | 0.12088 | 0.0086339 | No
18/05/2019 | 08:00:38 | NL234D | Urban | Asset failure | LV | 13.6667 | 192 | 0.0041949 | 2.185e-05 | No
18/05/2019 | 09:52:48 | PA15 | Rural Long | Unknown | Unknown | 73 | 205 | 0.10922 | 0.00053278 | No
18/05/2019 | 11:08:31 | W30 | Rural Short | Unknown | Unknown | 63 | 325.1905 | 0.15263 | 0.00046936 | No
18/05/2019 | 11:24:48 | MT12 | Rural Long | Asset failure | HV | 2 | 59 | 0.0008612 | 1.46e-05 | No
18/05/2019 | 11:51:59 | NL760C | Urban | Asset failure | LV | 70 | 28 | 0.0031334 | 0.00011191 | No
18/05/2019 | 13:46:51 | PL803C | Urban | Asset failure | LV | 2 | 261 | 0.00083451 | 3.2e-06 | No
18/05/2019 | 15:34:51 | MV31 | Rural Short | Unknown | Unknown | 6 | 341 | 0.015243 | 4.47e-05 | No
18/05/2019 | 15:38:58 | MTB32 | Rural Long | Overloads |  | 2 | 208 | 0.0030361 | 1.46e-05 | No
18/05/2019 | 15:42:47 | EL09 | Urban | Asset failure | LV | 1 | 286 | 0.00045722 | 1.6e-06 | No
18/05/2019 | 16:41:29 | CD16 | Rural Short | Weather |  | 66 | 1105.8788 | 0.54377 | 0.00049171 | No
18/05/2019 | 17:21:40 | SB23 | Rural Long | Weather |  | 57 | 657.8421 | 0.27367 | 0.00041601 | No
18/05/2019 | 17:34:40 | SB20 | Rural Long | Weather |  | 11 | 1935.8182 | 0.15541 | 8.028e-05 | No
18/05/2019 | 18:41:48 | SA11 | Urban | Overloads |  | 1 | 190 | 0.00030375 | 1.6e-06 | No
18/05/2019 | 18:47:49 | W04 | Rural Long | Weather |  | 1 | 2793 | 0.020384 | 7.3e-06 | No
18/05/2019 | 19:00:18 | W08 | Rural Short | Weather |  | 1 | 2795 | 0.020823 | 7.45e-06 | No
18/05/2019 | 19:55:04 | SB21 | Rural Long | Weather |  | 79 | 876.4304 | 0.50532 | 0.00057657 | No
18/05/2019 | 20:21:00 | SB19 | Rural Long | Unknown | Unknown | 25 | 2687 | 0.49027 | 0.00018246 | No
18/05/2019 | 20:34:09 | YK19 | Rural Long | Weather |  | 55 | 836.4364 | 0.33575 | 0.00040141 | No
18/05/2019 | 20:37:54 | PL33 | Rural Long | Weather |  | 1104 | 1017.1413 | 8.1955 | 0.0080574 | No
18/05/2019 | 20:37:54 | PL33 | Rural Long | Weather |  | 0 | 2 | 0.0015764 | 0 | No
18/05/2019 | 22:55:12 | CV32 | Rural Long | Weather |  | 68 | 668.5294 | 0.33178 | 0.00049629 | No
18/05/2019 | 22:55:12 | CV32 | Rural Long | Weather |  | 0 | 1 | 8.758e-05 | 0 | No
18/05/2019 | 23:13:00 | CV15 | Rural Long | Weather |  | 41 | 2067.6585 | 0.61871 | 0.00029923 | No
18/05/2019 | 23:33:20 | CM16 | Rural Long | Weather |  | 87 | 1712.8276 | 1.0876 | 0.00063496 | No
18/05/2019 | 23:33:20 | CM16 | Rural Long | Weather |  | 0 | 8 | 0.0012845 | 0 | No
18/05/2019 | 23:33:20 | CM16 | Rural Long | Weather |  | 0 | 140 | 0.0020435 | 0 | No
18/05/2019 | 23:43:07 | SSD188 | Urban | 5 - STPIS Exclusion (3.3)(a) |  | 8974 | 10 | 0.14347 | 0.014347 | No
18/05/2019 | 23:43:07 | SSD188 | Rural Long | 5 - STPIS Exclusion (3.3)(a) |  | 4787 | 10 | 0.34937 | 0.034937 | No
18/05/2019 | 23:54:08 | SM411E | Urban | Asset failure | LV | 1 | 750 | 0.001199 | 1.6e-06 | No
19/05/2019 | 00:00:00 | HH148C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 103 | 63 | 0.010374 | 0.00016466 | No
19/05/2019 | 00:01:44 | YK12 | Rural Long | Unknown | Unknown | 34 | 746 | 0.18512 | 0.00024814 | No
19/05/2019 | 00:02:32 | CM10 | Rural Long | Unknown | Unknown | 23 | 1073.6087 | 0.18022 | 0.00016786 | No
19/05/2019 | 00:40:15 | CM27 | Rural Long | Weather |  | 45 | 2681.5333 | 0.88068 | 0.00032843 | No
19/05/2019 | 00:41:32 | PL31 | Urban | Weather |  | 4941 | 630 | 4.9764 | 0.007899 | No
19/05/2019 | 00:44:28 | PL34 | Rural Long | Weather |  | 2 | 2668 | 0.038944 | 1.46e-05 | No
19/05/2019 | 01:16:37 | CM21 | Rural Long | Unknown | Unknown | 63 | 1130 | 0.51957 | 0.0004598 | No
19/05/2019 | 01:49:00 | CV03 | Rural Short | Asset failure | HV | 62 | 1395.7097 | 0.64469 | 0.00046191 | No
19/05/2019 | 02:39:00 | SD44300 | Rural Short | Weather |  | 1584 | 142 | 1.6757 | 0.011801 | No
19/05/2019 | 02:39:00 | SD44300 | Rural Long | Weather |  | 2286 | 43.1675 | 0.72021 | 0.016684 | No
19/05/2019 | 02:39:20 | KI57 | Rural Short | Weather |  | 165 | 421.5515 | 0.5182 | 0.0012293 | No
19/05/2019 | 02:48:23 | CM26 | Rural Long | Weather |  | 5 | 2794.6 | 0.10198 | 3.649e-05 | No
19/05/2019 | 05:45:39 | CM25 | Rural Long | Weather |  | 74 | 1025.9865 | 0.55411 | 0.00054008 | No
19/05/2019 | 07:27:12 | SM402D | Urban | Planned |  | 62 | 125 | 0.01239 | 9.912e-05 | No
19/05/2019 | 07:41:07 | NA05 | Rural Long | Planned |  | 1 | 302 | 0.0022041 | 7.3e-06 | No
19/05/2019 | 08:00:40 | WK31 | Rural Short | Planned |  | 28 | 406 | 0.084693 | 0.0002086 | No
19/05/2019 | 08:16:24 | MG04 | Rural Short | Planned |  | 91 | 246 | 0.16678 | 0.00067796 | No
19/05/2019 | 08:24:54 | KI21 | Rural Long | Weather |  | 13.6667 | 1135 | 0.11321 | 9.974e-05 | No
19/05/2019 | 08:31:12 | HH432E | Urban | Planned |  | 3 | 236 | 0.0011319 | 4.8e-06 | No
19/05/2019 | 08:38:04 | HH409B | Urban | Planned |  | 1 | 144 | 0.00023021 | 1.6e-06 | No
19/05/2019 | 08:40:14 | GA02 | Rural Short | Animal | Animal impact | 49 | 126 | 0.045997 | 0.00036506 | No
19/05/2019 | 08:42:00 | VH10 | Rural Short | Planned |  | 1 | 369 | 0.0027491 | 7.45e-06 | No
19/05/2019 | 08:44:02 | KI54 | Rural Long | Weather |  | 109 | 925.7431 | 0.73645 | 0.00079552 | No
19/05/2019 | 08:54:06 | CD17 | Rural Long | Weather |  | 37 | 356 | 0.096134 | 0.00027004 | No
19/05/2019 | 08:56:18 | ST35 | Rural Long | Planned |  | 23 | 222 | 0.037265 | 0.00016786 | No
19/05/2019 | 09:00:50 | ME116C | Urban | Planned |  | 153 | 243 | 0.059437 | 0.0002446 | No
19/05/2019 | 09:14:00 | VH10 | Rural Short | Planned |  | 324 | 491 | 1.1852 | 0.0024138 | No
19/05/2019 | 09:51:34 | ST36 | Rural Long | Planned |  | 1 | 299 | 0.0021822 | 7.3e-06 | No
19/05/2019 | 10:30:57 | VH18 | Rural Short | Unknown | Unknown | 4 | 103 | 0.0030695 | 2.98e-05 | No
19/05/2019 | 10:32:24 | ST23 | Rural Short | Weather |  | 21 | 118 | 0.018461 | 0.00015645 | No
19/05/2019 | 10:33:39 | EL25 | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 106 | 0.00016946 | 1.6e-06 | No
19/05/2019 | 10:53:03 | YK21 | Rural Long | Asset failure | LV | 1 | 191 | 0.001394 | 7.3e-06 | No
19/05/2019 | 11:53:58 | MT02 | Rural Long | Unknown | Unknown | 129 | 1016.186 | 0.95672 | 0.00094149 | No
19/05/2019 | 12:42:02 | PL11 | Rural Long | Unknown | Unknown | 68 | 38.1471 | 0.018932 | 0.00049629 | No
19/05/2019 | 13:37:50 | W17 | Rural Long | Weather |  | 47 | 216 | 0.074093 | 0.00034302 | No
19/05/2019 | 13:45:04 | VH10 | Rural Short | Planned |  | 1 | 66 | 0.00049171 | 7.45e-06 | No
19/05/2019 | 13:57:49 | SB21 | Rural Long | Overloads |  | 1 | 2667 | 0.019465 | 7.3e-06 | No
19/05/2019 | 14:12:40 | HH522C | Urban | Asset failure | LV | 74 | 34 | 0.0040223 | 0.0001183 | No
19/05/2019 | 14:35:00 | CV15 | Rural Long | Weather |  | 58 | 1225 | 0.51855 | 0.0004233 | No
19/05/2019 | 14:43:43 | CV05 | Rural Long | Unknown | Unknown | 57 | 29 | 0.012064 | 0.00041601 | No
19/05/2019 | 14:54:56 | SM349H | Urban | Unknown | Unknown | 1038.6672 | 5.3851 | 0.0089419 | 0.0016605 | No
19/05/2019 | 16:13:04 | VH10 | Rural Short | Planned |  | 1 | 150 | 0.0011175 | 7.45e-06 | No
19/05/2019 | 16:22:02 | KI43 | Rural Long | Third Party | Vehicle impact | 72 | 563 | 0.29585 | 0.00052548 | No
19/05/2019 | 16:33:53 | SB18 | Rural Long | Unknown | Unknown | 41 | 529.1707 | 0.15834 | 0.00029923 | No
19/05/2019 | 16:33:53 | SB18 | Rural Long | Unknown | Unknown | 0 | 142.5294 | 0.017684 | 0 | No
19/05/2019 | 16:35:58 | SM179D | Urban | Overloads |  | 1 | 287 | 0.00045882 | 1.6e-06 | No
19/05/2019 | 16:45:50 | CD15 | Rural Long | Weather |  | 33 | 101.6364 | 0.024479 | 0.00024085 | No
19/05/2019 | 17:00:55 | SSD457 | Rural Short | 5 - STPIS Exclusion (3.3)(a) |  | 3174 | 107 | 2.5302 | 0.023647 | No
19/05/2019 | 17:00:55 | SSD457 | Rural Long | 5 - STPIS Exclusion (3.3)(a) |  | 6897 | 107 | 5.386 | 0.050337 | No
19/05/2019 | 17:02:17 | W27 | Rural Long | Weather |  | 73 | 617.5068 | 0.32899 | 0.00053278 | No
19/05/2019 | 17:02:17 | W27 | Rural Long | Weather |  | 0 | 73 | 0.0042622 | 0 | No
19/05/2019 | 17:27:07 | BU08 | Rural Long | Unknown | Unknown | 19 | 353 | 0.04895 | 0.00013867 | No
19/05/2019 | 18:00:26 | NL451A | Urban | Asset failure | HV | 2095 | 169.5518 | 0.56787 | 0.0033492 | No
19/05/2019 | 18:00:26 | NL451A | Urban | Asset failure | HV | 0 | 9 | 0.027093 | 0 | No
19/05/2019 | 18:11:59 | W23 | Rural Long | Weather |  | 15 | 98 | 0.010729 | 0.00010948 | No
19/05/2019 | 19:01:43 | HH145A | Urban | Asset failure | LV | 1 | 95 | 0.00015187 | 1.6e-06 | No
19/05/2019 | 19:17:20 | PP12 | Rural Long | Unknown | Unknown | 22 | 298 | 0.047848 | 0.00016056 | No
19/05/2019 | 19:17:51 | CM15 | Rural Long | Weather |  | 29 | 1799.5862 | 0.38089 | 0.00021165 | No
19/05/2019 | 19:32:24 | KA28 | Rural Long | Weather |  | 27 | 1015 | 0.20001 | 0.00019706 | No
19/05/2019 | 20:04:19 | GU14 | Rural Long | Asset failure | LV | 1 | 386 | 0.0028172 | 7.3e-06 | No
19/05/2019 | 20:11:10 | SD59100 | Rural Long | Weather |  | 3 | 856 | 0.018742 | 2.19e-05 | No
19/05/2019 | 20:21:30 | GA22 | Rural Short | Unknown | Unknown | 13 | 287.9231 | 0.027886 | 9.685e-05 | No
19/05/2019 | 20:24:43 | MB03 | Rural Long | Weather |  | 98 | 278 | 0.19884 | 0.00071524 | No
19/05/2019 | 20:38:51 | SD36300 | Rural Long | Unknown | Unknown | 732 | 198 | 1.0578 | 0.0053424 | No
19/05/2019 | 20:56:19 | R04 | Rural Long | Unknown | Unknown | 39 | 322 | 0.091653 | 0.00028464 | No
19/05/2019 | 22:22:59 | PA23 | Rural Long | Weather |  | 88 | 634 | 0.40719 | 0.00064225 | No
19/05/2019 | 23:04:33 | NL760C | Urban | Overloads |  | 1 | 614 | 0.00098159 | 1.6e-06 | No
19/05/2019 | 23:54:37 | WK61 | Rural Short | Weather |  | 28 | 178 | 0.037132 | 0.0002086 | No
20/05/2019 | 01:18:18 | BU08 | Rural Long | Weather |  | 48 | 1249.25 | 0.43764 | 0.00035032 | No
20/05/2019 | 02:10:49 | R09 | Rural Long | Unknown | Unknown | 1.6667 | 15 | 0.00018246 | 1.216e-05 | No
20/05/2019 | 03:04:31 | LX25 | Rural Short | Weather |  | 17 | 429 | 0.054334 | 0.00012665 | No
20/05/2019 | 06:30:21 | SD54300 | Rural Long | Weather |  | 1 | 213 | 0.0015546 | 7.3e-06 | No
20/05/2019 | 06:56:59 | HK03 | Rural Long | Weather |  | 19 | 286 | 0.039659 | 0.00013867 | No
20/05/2019 | 07:01:49 | SD54300 | Rural Long | Weather |  | 1 | 186 | 0.0013575 | 7.3e-06 | No
20/05/2019 | 07:39:23 | SD32200 | Rural Long | Weather |  | 1 | 424 | 0.0030945 | 7.3e-06 | No
20/05/2019 | 08:44:54 | GU42 | Rural Long | Planned |  | 1 | 359 | 0.0026201 | 7.3e-06 | No
20/05/2019 | 08:53:18 | AP214A | Urban | Asset failure | LV | 25 | 89 | 0.003557 | 3.997e-05 | No
20/05/2019 | 09:14:38 | EL13 | Urban | Planned |  | 1 | 312 | 0.00049879 | 1.6e-06 | No
20/05/2019 | 09:18:37 | G18 | Rural Long | Weather |  | 77 | 272.4026 | 0.15308 | 0.00056197 | No
20/05/2019 | 09:22:59 | SM411E | Urban | Overloads |  | 1 | 113 | 0.00018065 | 1.6e-06 | No
20/05/2019 | 09:24:38 | GA22 | Rural Short | Unknown | Unknown | 293 | 5.5461 | 0.012106 | 0.0021829 | No
20/05/2019 | 09:25:58 | NL234C | Urban | Planned |  | 1 | 42 | 6.714e-05 | 1.6e-06 | No
20/05/2019 | 09:30:58 | MV34 | Rural Short | Planned |  | 1 | 200 | 0.00149 | 7.45e-06 | No
20/05/2019 | 09:54:16 | SA11 | Urban | Planned |  | 41 | 72 | 0.0047193 | 6.555e-05 | No
20/05/2019 | 10:02:25 | CM12 | Rural Long | Unknown | Unknown | 74 | 90 | 0.048607 | 0.00054008 | No
20/05/2019 | 10:18:19 | NL234C | Urban | Planned |  | 57 | 259 | 0.023601 | 9.112e-05 | No
20/05/2019 | 10:32:51 | HH177G | Urban | Asset failure | LV | 63 | 154 | 0.01551 | 0.00010072 | No
20/05/2019 | 10:44:44 | SA14 | Urban | Asset failure | LV | 16 | 130 | 0.0033252 | 2.558e-05 | No
20/05/2019 | 10:51:11 | MG10 | Rural Long | Asset failure | Distribution substation | 402 | 75.107 | 0.22036 | 0.0029339 | No
20/05/2019 | 10:59:26 | SA20 | Urban | Asset failure | LV | 1 | 156 | 0.00024939 | 1.6e-06 | No
20/05/2019 | 11:12:05 | MG22 | Rural Long | Asset failure | LV | 53 | 107 | 0.041389 | 0.00038681 | No
20/05/2019 | 11:14:46 | PL24 | Rural Long | Unknown | Unknown | 56 | 253.7679 | 0.10372 | 0.00040871 | No
20/05/2019 | 12:08:11 | CM12 | Rural Long | Other |  | 18 | 587.1667 | 0.077136 | 0.00013137 | No
20/05/2019 | 12:12:47 | SA11 | Urban | Planned |  | 225 | 105 | 0.037769 | 0.0003597 | No
20/05/2019 | 12:40:45 | PL23 | Rural Long | Asset failure | HV | 38 | 279.7895 | 0.077596 | 0.00027734 | No
20/05/2019 | 12:56:04 | W31 | Rural Short | Weather |  | 29 | 293.2759 | 0.063364 | 0.00021605 | No
20/05/2019 | 13:19:02 | CM12 | Rural Long | Weather |  | 18 | 457.8889 | 0.060153 | 0.00013137 | No
20/05/2019 | 14:20:31 | NL451C | Urban | Overloads |  | 1 | 440 | 0.00070342 | 1.6e-06 | No
20/05/2019 | 14:27:30 | PL01 | Urban | Asset failure | LV | 1 | 417 | 0.00066665 | 1.6e-06 | No
20/05/2019 | 16:08:36 | W27 | Rural Long | Weather |  | 2 | 2 | 2.919e-05 | 1.46e-05 | No
20/05/2019 | 16:10:42 | MB81 | Rural Long | Unknown | Unknown | 1 | 23 | 0.00016786 | 7.3e-06 | No
20/05/2019 | 19:05:17 | MV62 | Rural Short | Unknown | Unknown | 4 | 339 | 0.010102 | 2.98e-05 | No
20/05/2019 | 21:10:14 | NL115D | Urban | Asset failure | LV | 12.6667 | 95 | 0.0019237 | 2.025e-05 | No
20/05/2019 | 22:03:58 | CBD353L | CBD | Planned |  | 1 | 229 | 0.044453 | 0.00019412 | No
20/05/2019 | 23:18:51 | AP227D | Urban | Planned |  | 25 | 288 | 0.01151 | 3.997e-05 | No
21/05/2019 | 03:42:55 | EL01N | Urban | Third Party | Other | 1 | 82 | 0.00013109 | 1.6e-06 | No
21/05/2019 | 06:42:08 | SD38200 | Rural Long | Animal | Animal impact | 2 | 425 | 0.0062036 | 1.46e-05 | No
21/05/2019 | 06:42:21 | SD38200 | Rural Long | Animal | Animal impact | 1 | 452 | 0.0032988 | 7.3e-06 | No
21/05/2019 | 07:48:14 | NL210D | Urban | Unknown | Unknown | 1 | 166 | 0.00026538 | 1.6e-06 | No
21/05/2019 | 08:42:18 | HH341E | Urban | Asset failure | LV | 14.3333 | 198 | 0.004537 | 2.291e-05 | No
21/05/2019 | 09:09:36 | SM349H | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 169 | 0.00027018 | 1.6e-06 | No
21/05/2019 | 09:10:27 | WK61 | Rural Short | Planned |  | 4 | 119 | 0.0035463 | 2.98e-05 | No
21/05/2019 | 09:17:32 | NL111C | Urban | Planned |  | 73 | 276 | 0.03221 | 0.0001167 | No
21/05/2019 | 09:25:34 | SG14 | Rural Short | Planned |  | 26 | 295 | 0.057143 | 0.0001937 | No
21/05/2019 | 09:31:42 | SM179C | Urban | Planned |  | 1 | 31 | 4.956e-05 | 1.6e-06 | No
21/05/2019 | 09:37:31 | SA13 | Urban | Planned |  | 357 | 251 | 0.14325 | 0.00057073 | No
21/05/2019 | 09:47:02 | LX21 | Rural Short | Unknown | Unknown | 1 | 275 | 0.0020488 | 7.45e-06 | No
21/05/2019 | 09:53:59 | AP226E | Urban | Planned |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
21/05/2019 | 09:55:17 | M21 | Rural Long | Asset failure | LV | 1 | 104 | 0.00075903 | 7.3e-06 | No
21/05/2019 | 10:08:35 | SD34102 | Rural Long | Planned |  | 23 | 90.7391 | 0.015232 | 0.00016786 | No
21/05/2019 | 10:20:42 | MTB71 | Rural Short | Planned |  | 2 | 79 | 0.0011771 | 1.49e-05 | No
21/05/2019 | 10:27:56 | W01 | Rural Long | Weather |  | 2 | 365 | 0.0053278 | 1.46e-05 | No
21/05/2019 | 11:14:21 | LX43 | Rural Short | Asset failure | LV | 1 | 67 | 0.00049916 | 7.45e-06 | No
21/05/2019 | 11:18:33 | W32 | Rural Long | Weather |  | 19 | 142 | 0.019691 | 0.00013867 | No
21/05/2019 | 11:44:25 | NL115D | Urban | Asset failure | LV | 25.3333 | 181 | 0.0073305 | 4.05e-05 | No
21/05/2019 | 12:04:17 | HH177E | Urban | Overloads |  | 1 | 127 | 0.00020303 | 1.6e-06 | No
21/05/2019 | 12:15:02 | EL19 | Urban | Weather |  | 2 | 18 | 5.755e-05 | 3.2e-06 | No
21/05/2019 | 12:36:36 | YK17 | Rural Long | Planned |  | 1 | 178 | 0.0012991 | 7.3e-06 | No
21/05/2019 | 13:15:07 | GA03 | Rural Long | Planned |  | 1 | 40 | 0.00029193 | 7.3e-06 | No
21/05/2019 | 14:26:42 | M51 | Rural Short | Asset failure | LV | 7 | 98 | 0.0051108 | 5.215e-05 | No
21/05/2019 | 14:40:57 | BM13 | Rural Short | Unknown | Unknown | 2 | 179 | 0.0026672 | 1.49e-05 | No
21/05/2019 | 19:31:51 | ME131C | Urban | Asset failure | LV | 19.6666 | 158 | 0.0049676 | 3.144e-05 | No
21/05/2019 | 20:53:53 | HH177F | Urban | Overloads |  | 1 | 81 | 0.00012949 | 1.6e-06 | No
21/05/2019 | 21:13:41 | SM172B | Urban | Asset failure | LV | 146 | 70 | 0.016338 | 0.00023341 | No
21/05/2019 | 21:45:11 | CBD366J | CBD | Planned |  | 22 | 2 | 0.0085412 | 0.0042706 | No
21/05/2019 | 21:45:11 | CBD366J | CBD | Planned |  | 0 | 1 | 0.0042706 | 0 | No
21/05/2019 | 21:45:11 | CBD366J | Urban | Planned |  | 5 | 2 | 1.599e-05 | 7.99e-06 | No
21/05/2019 | 21:45:11 | CBD366J | Urban | Planned |  | 0 | 1 | 7.99e-06 | 0 | No
21/05/2019 | 21:52:48 | NA06 | Rural Long | Asset failure | HV | 26.6667 | 308 | 0.059944 | 0.00019462 | No
21/05/2019 | 21:52:48 | NA06 | Rural Long | Asset failure | HV | 0 | 47 | 0.0091473 | 0 | No
22/05/2019 | 05:54:13 | HH121F | Urban | Asset failure | LV | 1 | 188 | 0.00030055 | 1.6e-06 | No
22/05/2019 | 06:08:35 | YK22 | Rural Short | Weather |  | 59.3334 | 152.8483 | 0.067565 | 0.00044204 | No
22/05/2019 | 06:28:00 | NL115C | Urban | Asset failure | HV | 794 | 85.0906 | 0.10801 | 0.0012694 | No
22/05/2019 | 08:57:06 | EL11 | Urban | Planned |  | 15 | 341 | 0.0081772 | 2.398e-05 | No
22/05/2019 | 09:15:33 | LX48 | Rural Short | Asset failure | LV | 2 | 379 | 0.0056472 | 1.49e-05 | No
22/05/2019 | 09:21:10 | GA39 | Rural Long | Planned |  | 2 | 59 | 0.0008612 | 1.46e-05 | No
22/05/2019 | 09:27:40 | PA02 | Urban | Planned |  | 84 | 321 | 0.043107 | 0.00013429 | No
22/05/2019 | 09:42:32 | HH121B | Urban | Overloads |  | 1 | 192 | 0.00030695 | 1.6e-06 | No
22/05/2019 | 09:45:32 | SM349E | Urban | Overloads |  | 1 | 114 | 0.00018225 | 1.6e-06 | No
22/05/2019 | 10:04:23 | SM410C | Urban | Planned |  | 173 | 297 | 0.082142 | 0.00027657 | No
22/05/2019 | 10:25:54 | CN33 | Rural Long | Planned |  | 15 | 246.5333 | 0.026989 | 0.00010948 | No
22/05/2019 | 10:28:54 | SD34102 | Rural Long | Planned |  | 7 | 27.4286 | 0.0014013 | 5.109e-05 | No
22/05/2019 | 10:39:15 | SM216A | Urban | Planned |  | 65 | 222 | 0.023069 | 0.00010391 | No
22/05/2019 | 10:45:47 | SB18 | Rural Long | Weather |  | 41 | 150.2195 | 0.04495 | 0.00029923 | No
22/05/2019 | 10:58:58 | YK03 | Rural Long | Planned |  | 42 | 147 | 0.04506 | 0.00030653 | No
22/05/2019 | 12:06:18 | MG17 | Rural Long | Overloads |  | 33 | 172 | 0.041425 | 0.00024085 | No
22/05/2019 | 12:21:08 | EL15 | Urban | Unknown | Unknown | 2 | 283 | 0.00090485 | 3.2e-06 | No
22/05/2019 | 12:43:42 | MG17 | Rural Long | Unknown | Unknown | 33 | 116 | 0.027938 | 0.00024085 | No
22/05/2019 | 12:44:24 | NL115E | Urban | Planned |  | 1 | 83 | 0.00013269 | 1.6e-06 | No
22/05/2019 | 15:48:29 | MG07 | Rural Short | Planned |  | 306 | 15 | 0.034196 | 0.0022798 | No
22/05/2019 | 16:12:00 | NL234C | Urban | Asset failure | LV | 1 | 137 | 0.00021902 | 1.6e-06 | No
22/05/2019 | 16:14:45 | NL234C | Urban | Asset failure | LV | 1 | 135 | 0.00021582 | 1.6e-06 | No
22/05/2019 | 18:43:06 | HH432F | Urban | Asset failure | LV | 1 | 177 | 0.00028297 | 1.6e-06 | No
22/05/2019 | 18:51:05 | BM13 | Rural Short | Asset failure | LV | 1 | 176 | 0.0013112 | 7.45e-06 | No
23/05/2019 | 00:23:55 | MTB21 | Rural Short | Unknown | Unknown | 38 | 422 | 0.11947 | 0.00028311 | No
23/05/2019 | 01:18:44 | EL08G | Urban | Asset failure | LV | 1 | 196 | 0.00031334 | 1.6e-06 | No
23/05/2019 | 08:01:49 | AP149B | Urban | Asset failure | LV | 1 | 420 | 0.00067144 | 1.6e-06 | No
23/05/2019 | 08:13:26 | AP344E | Urban | Third Party | Vehicle impact | 18.6666 | 72 | 0.0021486 | 2.984e-05 | No
23/05/2019 | 08:35:56 | AP425B | Urban | Planned |  | 61 | 334 | 0.032571 | 9.752e-05 | No
23/05/2019 | 08:49:40 | AP227A | Urban | Planned |  | 1 | 221 | 0.00035331 | 1.6e-06 | No
23/05/2019 | 09:00:15 | HH177C | Urban | Planned |  | 24 | 165 | 0.0063307 | 3.837e-05 | No
23/05/2019 | 09:05:41 | MTB11 | Rural Short | Planned |  | 28 | 260 | 0.054237 | 0.0002086 | No
23/05/2019 | 09:08:58 | AP365E | Urban | Planned |  | 77 | 321 | 0.039514 | 0.0001231 | No
23/05/2019 | 09:13:28 | EL09 | Urban | Planned |  | 247 | 324.0526 | 0.12796 | 0.00039487 | No
23/05/2019 | 09:42:21 | MV34 | Rural Short | Planned |  | 12 | 320 | 0.028609 | 8.94e-05 | No
23/05/2019 | 09:45:15 | VH72 | Rural Short | Planned |  | 9 | 340 | 0.022797 | 6.705e-05 | No
23/05/2019 | 10:10:59 | SB18 | Rural Long | Unknown | Unknown | 41 | 40 | 0.011969 | 0.00029923 | No
23/05/2019 | 10:16:04 | GU42 | Rural Long | Asset failure | LV | 1 | 117 | 0.00085391 | 7.3e-06 | No
23/05/2019 | 10:19:14 | GA27 | Rural Long | Planned |  | 26 | 36 | 0.0068312 | 0.00018976 | No
23/05/2019 | 10:47:19 | SG13 | Rural Short | Asset failure | LV | 1 | 92 | 0.00068541 | 7.45e-06 | No
23/05/2019 | 11:13:20 | MTB52 | Rural Long | Planned |  | 53 | 150 | 0.058022 | 0.00038681 | No
23/05/2019 | 11:14:59 | SM349D | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
23/05/2019 | 11:18:48 | LX54 | Rural Short | Animal | Animal impact | 10 | 288 | 0.021456 | 7.45e-05 | No
23/05/2019 | 11:25:04 | SB03 | Rural Long | Asset failure | HV | 3 | 37 | 0.00081012 | 2.19e-05 | No
23/05/2019 | 11:45:18 | SD34102 | Rural Long | Planned |  | 1 | 106 | 0.00077362 | 7.3e-06 | No
23/05/2019 | 11:49:11 | MB44 | Rural Long | Planned |  | 1 | 60 | 0.0004379 | 7.3e-06 | No
23/05/2019 | 11:57:35 | MT15 | Rural Long | Planned |  | 1 | 104 | 0.00075903 | 7.3e-06 | No
23/05/2019 | 12:30:35 | W20 | Rural Long | Third Party | Vehicle impact | 5 | 285 | 0.0104 | 3.649e-05 | No
23/05/2019 | 12:30:50 | MTB52 | Rural Long | Asset failure | LV | 2 | 72 | 0.001051 | 1.46e-05 | No
23/05/2019 | 12:45:28 | GA27 | Rural Long | Planned |  | 23 | 47 | 0.0078895 | 0.00016786 | No
23/05/2019 | 13:34:03 | HH341B | Urban | Third Party | Vehicle impact | 15 | 490 | 0.01175 | 2.398e-05 | No
23/05/2019 | 13:39:21 | AP132C | Urban | Third Party | Vehicle impact | 2 | 101 | 0.00032293 | 3.2e-06 | No
23/05/2019 | 14:02:58 | SM216G | Urban | Overloads |  | 2 | 216 | 0.00069063 | 3.2e-06 | No
23/05/2019 | 15:01:43 | MTB41 | Rural Short | Planned |  | 1 | 52 | 0.00038741 | 7.45e-06 | No
23/05/2019 | 15:58:44 | ME116A | Urban | Asset failure | LV | 1 | 236 | 0.00037729 | 1.6e-06 | No
23/05/2019 | 16:09:07 | MTB53 | Rural Long | Overloads |  | 1 | 298 | 0.0021749 | 7.3e-06 | No
23/05/2019 | 16:27:20 | G16 | Rural Long | Asset failure | LV | 2 | 105 | 0.0015326 | 1.46e-05 | No
23/05/2019 | 17:10:41 | G16 | Rural Long | Unknown | Unknown | 2 | 21 | 0.00030653 | 1.46e-05 | No
23/05/2019 | 19:58:29 | ST36 | Rural Long | Asset failure | LV | 1.6667 | 164 | 0.0019949 | 1.216e-05 | No
23/05/2019 | 19:58:59 | SSD532 | Rural Long | Asset failure | Zone substation | 1113 | 292 | 2.3719 | 0.008123 | No
24/05/2019 | 00:15:40 | SA20 | Urban | Asset failure | LV | 23.3333 | 140 | 0.0052223 | 3.73e-05 | No
24/05/2019 | 01:37:07 | CM25 | Rural Long | Weather |  | 97 | 702.7732 | 0.49752 | 0.00070794 | No
24/05/2019 | 05:15:45 | ME347C | Urban | Asset failure | HV | 2624 | 95.979 | 0.40262 | 0.0041949 | No
24/05/2019 | 05:51:38 | CM25 | Rural Long | Weather |  | 3 | 457 | 0.010006 | 2.19e-05 | No
24/05/2019 | 08:43:23 | AP227A | Urban | Planned |  | 1 | 292 | 0.00046681 | 1.6e-06 | No
24/05/2019 | 08:52:44 | NL111C | Urban | Planned |  | 1 | 359 | 0.00057392 | 1.6e-06 | No
24/05/2019 | 08:56:48 | NL111C | Urban | Planned |  | 44 | 290 | 0.020399 | 7.034e-05 | No
24/05/2019 | 09:00:35 | CL05 | Rural Long | Planned |  | 1 | 22 | 0.00016056 | 7.3e-06 | No
24/05/2019 | 09:07:34 | MV32 | Rural Short | Planned |  | 20 | 328 | 0.048873 | 0.000149 | No
24/05/2019 | 09:10:11 | MTB21 | Rural Short | Planned |  | 52 | 354 | 0.13714 | 0.00038741 | No
24/05/2019 | 09:17:17 | PA02 | Urban | Planned |  | 164 | 210 | 0.055058 | 0.00026218 | No
24/05/2019 | 09:21:50 | KA22 | Rural Long | Asset failure | LV | 1 | 339 | 0.0024741 | 7.3e-06 | No
24/05/2019 | 09:25:25 | NU24 | Rural Long | Planned |  | 2 | 171 | 0.002496 | 1.46e-05 | No
24/05/2019 | 09:28:24 | KI55 | Rural Long | Planned |  | 1 | 151 | 0.0011021 | 7.3e-06 | No
24/05/2019 | 09:36:50 | SM126D | Urban | Planned |  | 249 | 213 | 0.084789 | 0.00039807 | No
24/05/2019 | 09:45:53 | SM410B | Urban | Planned |  | 109 | 249 | 0.04339 | 0.00017426 | No
24/05/2019 | 09:55:58 | SA18 | Urban | Planned |  | 119 | 315 | 0.059926 | 0.00019024 | No
24/05/2019 | 09:59:17 | ME347C | Urban | Asset failure | LV | 1 | 431 | 0.00068903 | 1.6e-06 | No
24/05/2019 | 10:00:37 | PP08 | Rural Long | Planned |  | 1 | 77 | 0.00056197 | 7.3e-06 | No
24/05/2019 | 10:03:29 | SD49900 | Rural Short | Asset failure | Subtransmission | 3 | 276 | 0.0061687 | 2.235e-05 | No
24/05/2019 | 10:06:35 | MI15 | Rural Long | Planned |  | 24 | 9 | 0.0015764 | 0.00017516 | No
24/05/2019 | 10:08:48 | MI22 | Rural Long | Planned |  | 174 | 148 | 0.18795 | 0.0012699 | No
24/05/2019 | 10:09:53 | NL115C | Urban | Asset failure | LV | 1 | 441 | 0.00070502 | 1.6e-06 | No
24/05/2019 | 10:49:08 | SG08 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 197 | 97.7259 | 0.14343 | 0.0014677 | No
24/05/2019 | 11:50:00 | NL234B | Urban | Planned |  | 2 | 38 | 0.0001215 | 3.2e-06 | No
24/05/2019 | 12:34:42 | MTB21 | Rural Short | Planned |  | 2 | 143 | 0.0021307 | 1.49e-05 | No
24/05/2019 | 12:35:02 | HH432D | Urban | Planned |  | 22 | 54 | 0.0018992 | 3.517e-05 | No
24/05/2019 | 13:02:28 | W06 | Rural Long | Unknown | Unknown | 2 | 4271 | 0.062342 | 1.46e-05 | No
24/05/2019 | 14:42:54 | SM126D | Urban | Other |  | 16 | 54 | 0.0013813 | 2.558e-05 | No
24/05/2019 | 16:28:33 | EL10 | Urban | Asset failure | LV | 1 | 167 | 0.00026698 | 1.6e-06 | No
24/05/2019 | 17:17:07 | SA16 | Urban | Third Party | Vehicle impact | 79 | 359 | 0.04534 | 0.0001263 | No
24/05/2019 | 17:18:52 | SA520G | Urban | Planned |  | 1 | 291 | 0.00046521 | 1.6e-06 | No
24/05/2019 | 17:47:27 | SA16 | Urban | Unknown | Unknown | 79 | 250 | 0.031574 | 0.0001263 | No
24/05/2019 | 20:05:53 | HH121C | Urban | Asset failure | LV | 1 | 212 | 0.00033892 | 1.6e-06 | No
24/05/2019 | 20:36:41 | CD23 | Rural Long | Unknown | Unknown | 2 | 892 | 0.01302 | 1.46e-05 | No
24/05/2019 | 20:41:01 | HH121C | Urban | Asset failure | LV | 1 | 205 | 0.00032773 | 1.6e-06 | No
24/05/2019 | 20:59:46 | CD23 | Rural Long | Asset failure | HV | 3 | 882 | 0.019311 | 2.19e-05 | No
24/05/2019 | 22:36:30 | SG12 | Rural Short | Unknown | Unknown | 254 | 57 | 0.10786 | 0.0018923 | No
25/05/2019 | 06:20:21 | MV15 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1099 | 124.8389 | 1.0221 | 0.0081877 | No
25/05/2019 | 08:52:05 | W16 | Rural Long | Weather |  | 24 | 537.3333 | 0.094119 | 0.00017516 | No
25/05/2019 | 08:52:30 | SG12 | Rural Short | Asset failure | HV | 544 | 148.7463 | 0.60285 | 0.0040529 | No
25/05/2019 | 09:22:11 | SM349B | Urban | Planned |  | 92 | 185 | 0.027209 | 0.00014708 | No
25/05/2019 | 09:28:53 | SM350F | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 34 | 286 | 0.015546 | 5.435e-05 | No
25/05/2019 | 09:34:55 | ST11 | Rural Short | Asset failure | LV | 1 | 207 | 0.0015422 | 7.45e-06 | No
25/05/2019 | 10:33:59 | VH12 | Rural Short | Asset failure | LV | 1 | 569 | 0.0042391 | 7.45e-06 | No
25/05/2019 | 10:52:45 | W08 | Rural Short | Asset failure | HV | 62.3333 | 273.0053 | 0.12678 | 0.00046439 | No
25/05/2019 | 11:06:47 | HH121C | Urban | Asset failure | LV | 10 | 62 | 0.00099118 | 1.599e-05 | No
25/05/2019 | 11:35:13 | NL451A | Urban | Unknown | Unknown | 5.6667 | 250 | 0.0022648 | 9.06e-06 | No
25/05/2019 | 11:39:41 | SB23 | Rural Long | Unknown | Unknown | 57 | 1030.6667 | 0.42876 | 0.00041601 | No
25/05/2019 | 16:38:40 | SM350H | Urban | Vegetation | Grow-in - NSP responsibility | 388 | 84 | 0.052104 | 0.00062029 | No
25/05/2019 | 17:00:21 | YK23 | Rural Long | Overloads |  | 11 | 126 | 0.010115 | 8.028e-05 | No
25/05/2019 | 17:31:51 | KA03 | Rural Long | Asset failure | HV | 2 | 119 | 0.001737 | 1.46e-05 | No
25/05/2019 | 18:34:17 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 177 | 0.0013187 | 7.45e-06 | No
25/05/2019 | 20:04:01 | SM216B | Urban | Other |  | 36 | 163 | 0.009381 | 5.755e-05 | No
25/05/2019 | 20:32:24 | HH121A | Urban | Asset failure | LV | 1 | 237 | 0.00037889 | 1.6e-06 | No
25/05/2019 | 21:04:08 | EL01A | Urban | Asset failure | LV | 9 | 152 | 0.002187 | 1.439e-05 | No
25/05/2019 | 22:15:46 | KA10 | Rural Long | Unknown | Unknown | 25 | 49 | 0.0089405 | 0.00018246 | No
25/05/2019 | 22:48:02 | HH341D | Urban | Animal | Animal impact | 165 | 72 | 0.018992 | 0.00026378 | No
25/05/2019 | 23:30:51 | EL09 | Urban | Third Party | Other | 1 | 6 | 9.59e-06 | 1.6e-06 | No
26/05/2019 | 00:04:26 | MB22 | Rural Short | Asset failure | LV | 12 | 86 | 0.0076885 | 8.94e-05 | No
26/05/2019 | 05:23:37 | SM216B | Urban | Asset failure | LV | 37.3333 | 249 | 0.014861 | 5.968e-05 | No
26/05/2019 | 07:54:47 | SM137A | Urban | Planned |  | 470 | 212 | 0.15929 | 0.00075138 | No
26/05/2019 | 08:09:04 | WK31 | Rural Short | Planned |  | 38 | 349.9474 | 0.099072 | 0.00028311 | No
26/05/2019 | 08:17:14 | EL17 | Urban | Planned |  | 23 | 344 | 0.012649 | 3.677e-05 | No
26/05/2019 | 08:27:08 | AP355E | Urban | Planned |  | 164 | 167 | 0.043785 | 0.00026218 | No
26/05/2019 | 08:30:22 | EL17 | Urban | Planned |  | 1 | 71 | 0.00011351 | 1.6e-06 | No
26/05/2019 | 08:47:49 | VH16 | Rural Short | Planned |  | 1 | 500 | 0.0037251 | 7.45e-06 | No
26/05/2019 | 08:49:36 | BT03 | Rural Long | Planned |  | 55 | 255 | 0.10236 | 0.00040141 | No
26/05/2019 | 08:54:41 | VH10 | Rural Short | Planned |  | 157 | 380 | 0.44448 | 0.0011697 | No
26/05/2019 | 08:55:21 | NL234C | Urban | Planned |  | 1 | 2 | 3.2e-06 | 1.6e-06 | No
26/05/2019 | 09:02:52 | ST35 | Rural Long | Planned |  | 16 | 133 | 0.015531 | 0.00011677 | No
26/05/2019 | 09:17:56 | HH341E | Urban | Planned |  | 314 | 237 | 0.11897 | 0.00050198 | No
26/05/2019 | 10:15:11 | HH341K | Urban | Planned |  | 1 | 47 | 7.514e-05 | 1.6e-06 | No
26/05/2019 | 11:25:29 | HH341K | Urban | Planned |  | 1 | 2 | 3.2e-06 | 1.6e-06 | No
26/05/2019 | 13:14:43 | NU13 | Rural Long | Animal | Animal impact | 2.6667 | 173 | 0.003367 | 1.946e-05 | No
26/05/2019 | 16:33:32 | SM349H | Urban | Asset failure | LV | 2 | 331 | 0.0010583 | 3.2e-06 | No
26/05/2019 | 16:52:54 | MB22 | Rural Short | Weather |  | 1157 | 192.9386 | 1.6631 | 0.0086198 | No
26/05/2019 | 17:08:08 | SA520J | Urban | Planned |  | 5 | 1 | 7.99e-06 | 7.99e-06 | No
26/05/2019 | 18:10:18 | MG14 | Rural Long | Unknown | Unknown | 2 | 17 | 0.00024814 | 1.46e-05 | No
26/05/2019 | 22:15:59 | CBD366P | Urban | Planned |  | 1 | 254 | 0.00040606 | 1.6e-06 | No
26/05/2019 | 23:49:07 | HH341A | Urban | Planned |  | 4 | 185 | 0.001183 | 6.39e-06 | No
27/05/2019 | 00:27:51 | MG34 | Rural Long | Unknown | Unknown | 207 | 114.2609 | 0.17262 | 0.0015108 | No
27/05/2019 | 02:16:04 | NL210E | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 621 | 90 | 0.08935 | 0.00099278 | No
27/05/2019 | 05:41:34 | AP226E | Urban | Asset failure | LV | 29.3333 | 159 | 0.0074562 | 4.689e-05 | No
27/05/2019 | 06:12:36 | SM172E | Urban | Overloads |  | 1 | 328 | 0.00052436 | 1.6e-06 | No
27/05/2019 | 07:22:48 | AP373E | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 243 | 0.00038848 | 1.6e-06 | No
27/05/2019 | 08:02:58 | CL09 | Rural Long | Planned |  | 44 | 427 | 0.13712 | 0.00032113 | No
27/05/2019 | 08:53:11 | SA14 | Urban | Planned |  | 51 | 206 | 0.016796 | 8.153e-05 | No
27/05/2019 | 08:55:39 | KA02 | Rural Short | Planned |  | 66 | 14 | 0.0068839 | 0.00049171 | No
27/05/2019 | 08:58:41 | HH428A | Urban | Planned |  | 133 | 296 | 0.062937 | 0.00021262 | No
27/05/2019 | 09:08:48 | NA01 | Rural Long | Planned |  | 92 | 387 | 0.25985 | 0.00067145 | No
27/05/2019 | 09:10:25 | AP149D | Urban | Planned |  | 56 | 217 | 0.019427 | 8.953e-05 | No
27/05/2019 | 09:11:44 | HH107B | Urban | Planned |  | 1 | 366 | 0.00058512 | 1.6e-06 | No
27/05/2019 | 09:30:06 | KI12 | Rural Long | Planned |  | 4 | 273 | 0.0079698 | 2.919e-05 | No
27/05/2019 | 09:34:33 | SA744C | Urban | Planned |  | 12 | 323 | 0.0061965 | 1.918e-05 | No
27/05/2019 | 09:55:01 | AP226E | Urban | Planned |  | 76 | 131 | 0.015916 | 0.0001215 | No
27/05/2019 | 09:55:43 | BM13 | Rural Short | Planned |  | 9 | 224 | 0.015019 | 6.705e-05 | No
27/05/2019 | 10:05:24 | SM137A | Urban | Planned |  | 181 | 73 | 0.021123 | 0.00028936 | No
27/05/2019 | 10:05:56 | CN27 | Rural Long | Planned |  | 60 | 287 | 0.12568 | 0.0004379 | No
27/05/2019 | 10:07:12 | SD36400 | Rural Long | Asset failure | Subtransmission | 1827 | 258 | 3.4402 | 0.013334 | No
27/05/2019 | 10:08:54 | SB21 | Rural Long | Weather |  | 7 | 71 | 0.0036273 | 5.109e-05 | No
27/05/2019 | 10:22:51 | AP355F | Urban | Asset failure | LV | 14.6667 | 24 | 0.00056273 | 2.345e-05 | No
27/05/2019 | 10:25:47 | M61 | Rural Long | Planned |  | 35 | 128 | 0.032697 | 0.00025544 | No
27/05/2019 | 11:10:26 | KA21 | Rural Long | Planned |  | 1 | 23 | 0.00016786 | 7.3e-06 | No
27/05/2019 | 11:19:08 | SA14 | Urban | Planned |  | 37 | 106 | 0.00627 | 5.915e-05 | No
27/05/2019 | 12:08:02 | BM51 | Urban | Asset failure | LV | 1 | 372 | 0.00059471 | 1.6e-06 | No
27/05/2019 | 12:08:59 | SM172C | Urban | Asset failure | HV | 93 | 113 | 0.0168 | 0.00014868 | No
27/05/2019 | 12:30:09 | SM172C | Urban | Unknown | Unknown | 93 | 52 | 0.0077312 | 0.00014868 | No
27/05/2019 | 13:19:37 | SA14 | Urban | Planned |  | 1 | 46 | 7.354e-05 | 1.6e-06 | No
27/05/2019 | 13:30:25 | BM15 | Rural Short | Asset failure | LV | 1 | 204 | 0.0015198 | 7.45e-06 | No
27/05/2019 | 13:31:31 | HH130A | Urban | Asset failure | LV | 16.3333 | 146 | 0.0038123 | 2.611e-05 | No
27/05/2019 | 15:20:44 | MV22 | Rural Short | Asset failure | HV | 400 | 52.165 | 0.15545 | 0.0029801 | No
27/05/2019 | 16:05:59 | W23 | Rural Long | Unknown | Unknown | 11 | 60 | 0.0048169 | 8.028e-05 | No
27/05/2019 | 16:49:10 | MG34 | Rural Long | Unknown | Unknown | 207 | 96 | 0.14503 | 0.0015108 | No
27/05/2019 | 17:24:40 | NL210C | Urban | Asset failure | LV | 4 | 182 | 0.0011638 | 6.39e-06 | No
27/05/2019 | 22:03:00 | MG34 | Rural Long | Asset failure | HV | 270 | 43.8444 | 0.086398 | 0.0019706 | No
27/05/2019 | 22:06:43 | HH409B | Urban | Planned |  | 19 | 451 | 0.013699 | 3.037e-05 | No
28/05/2019 | 00:05:28 | MV22 | Rural Short | Asset failure | HV | 400 | 114.5175 | 0.34127 | 0.0029801 | No
28/05/2019 | 00:05:28 | MV22 | Rural Short | Planned |  | 0 | 461 | 0.020607 | 0 | No
28/05/2019 | 07:17:45 | SM216E | Urban | Asset failure | LV | 7.6667 | 122 | 0.0014953 | 1.226e-05 | No
28/05/2019 | 08:44:57 | ME347A | Urban | Planned |  | 112 | 327 | 0.05855 | 0.00017905 | No
28/05/2019 | 08:48:52 | SD34102 | Rural Long | Planned |  | 64 | 326 | 0.15227 | 0.00046709 | No
28/05/2019 | 08:58:36 | MV34 | Rural Short | Planned |  | 414 | 235 | 0.72483 | 0.0030844 | No
28/05/2019 | 09:01:58 | MTB71 | Rural Short | Planned |  | 206 | 316 | 0.48497 | 0.0015347 | No
28/05/2019 | 09:02:54 | MTB21 | Rural Short | Planned |  | 75 | 303.4 | 0.16953 | 0.00055876 | No
28/05/2019 | 09:09:49 | NA12 | Rural Long | Asset failure | HV | 1 | 118 | 0.0008612 | 7.3e-06 | No
28/05/2019 | 09:25:24 | WK65 | Rural Short | Asset failure | LV | 2 | 140 | 0.002086 | 1.49e-05 | No
28/05/2019 | 09:31:31 | AP226D | Urban | Planned |  | 106 | 311 | 0.052702 | 0.00016946 | No
28/05/2019 | 09:36:24 | W29 | Rural Long | Planned |  | 36 | 324 | 0.085128 | 0.00026274 | No
28/05/2019 | 09:44:16 | ST36 | Rural Long | Unknown | Unknown | 423 | 107.5768 | 0.33211 | 0.0030872 | No
28/05/2019 | 09:45:43 | ME347A | Urban | Planned |  | 1 | 286 | 0.00045722 | 1.6e-06 | No
28/05/2019 | 10:00:59 | SA11 | Urban | Planned |  | 382 | 240 | 0.14657 | 0.00061069 | No
28/05/2019 | 10:01:00 | AP226D | Urban | Planned |  | 1 | 391 | 0.00062508 | 1.6e-06 | No
28/05/2019 | 10:08:07 | SA32 | Urban | Planned |  | 130 | 319 | 0.066297 | 0.00020783 | No
28/05/2019 | 10:16:40 | R11 | Rural Long | Asset failure | LV | 1.3333 | 239 | 0.0023257 | 9.73e-06 | No
28/05/2019 | 10:18:08 | HH432C | Urban | Asset failure | LV | 34 | 155 | 0.008425 | 5.435e-05 | No
28/05/2019 | 10:18:42 | HH432C | Urban | Asset failure | LV | 24 | 152 | 0.005832 | 3.837e-05 | No
28/05/2019 | 12:08:42 | HH386B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1082.3339 | 48 | 0.083054 | 0.0017303 | No
28/05/2019 | 12:41:59 | SM410B | Urban | Asset failure | LV | 52 | 88 | 0.0073155 | 8.313e-05 | No
28/05/2019 | 13:52:04 | SD31200 | Rural Long | Asset failure | Subtransmission | 1 | 323 | 0.0023574 | 7.3e-06 | No
28/05/2019 | 14:12:09 | HH145B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 173 | 0.00027657 | 1.6e-06 | No
28/05/2019 | 14:16:57 | LM43 | Rural Long | Unknown | Unknown | 101 | 503 | 0.37078 | 0.00073713 | No
28/05/2019 | 15:18:22 | EL20 | Urban | Vegetation | Grow-in - NSP responsibility | 779 | 86.4737 | 0.10769 | 0.0012454 | No
28/05/2019 | 15:31:46 | NL115E | Urban | Asset failure | LV | 42 | 193 | 0.012959 | 6.714e-05 | No
28/05/2019 | 15:41:04 | GA13 | Rural Long | Unknown | Unknown | 2 | 224 | 0.0032697 | 1.46e-05 | No
28/05/2019 | 16:14:15 | CL27 | Rural Long | Unknown | Unknown | 2 | 18 | 0.00026274 | 1.46e-05 | No
28/05/2019 | 19:34:48 | EL20 | Urban | Unknown | Unknown | 2 | 110 | 0.00035171 | 3.2e-06 | No
28/05/2019 | 20:20:55 | MG17 | Rural Long | Asset failure | HV | 253 | 208.3202 | 0.38466 | 0.0018465 | No
28/05/2019 | 20:20:55 | MG17 | Rural Long | Asset failure | HV | 0 | 5 | 0.0064225 | 0 | No
28/05/2019 | 21:16:32 | NL234C | Urban | Asset failure | LV | 32 | 109 | 0.0055762 | 5.116e-05 | No
28/05/2019 | 21:16:37 | NL210C | Urban | Animal | Animal impact | 61 | 117 | 0.01141 | 9.752e-05 | No
28/05/2019 | 22:02:47 | CBD412A | CBD | Planned |  | 2 | 289 | 0.1122 | 0.00038824 | No
29/05/2019 | 00:38:00 | LM43 | Rural Long | Asset failure | HV | 101 | 714.413 | 0.52662 | 0.00073713 | No
29/05/2019 | 04:39:23 | HH145A | Urban | Unknown | Unknown | 289 | 129 | 0.0596 | 0.00046202 | No
29/05/2019 | 04:56:35 | ST36 | Rural Long | Asset failure | HV | 58 | 301.7586 | 0.12774 | 0.0004233 | No
29/05/2019 | 06:20:31 | AP125D | Urban | Asset failure | LV | 15.6667 | 184 | 0.0046084 | 2.505e-05 | No
29/05/2019 | 06:24:36 | MI08 | Rural Long | Asset failure | HV | 1129 | 188.3454 | 1.5519 | 0.0082398 | No
29/05/2019 | 07:01:14 | MI31 | Rural Long | Asset failure | HV | 48 | 384.1667 | 0.13458 | 0.00035032 | No
29/05/2019 | 07:44:33 | NL111P | Urban | Asset failure | LV | 79 | 195 | 0.024628 | 0.0001263 | No
29/05/2019 | 08:02:19 | NA01 | Rural Long | Vegetation | Grow-in - NSP responsibility | 1 | 212 | 0.0015473 | 7.3e-06 | No
29/05/2019 | 08:21:25 | HH341H | Urban | Asset failure | LV | 14.3333 | 132 | 0.0030247 | 2.291e-05 | No
29/05/2019 | 08:40:04 | SG08 | Rural Short | Planned |  | 5 | 193 | 0.0071894 | 3.725e-05 | No
29/05/2019 | 08:44:47 | SD34102 | Rural Long | Planned |  | 64 | 232 | 0.10837 | 0.00046709 | No
29/05/2019 | 08:55:05 | SA16 | Urban | Vegetation | Grow-in - NSP responsibility | 23 | 47 | 0.0017282 | 3.677e-05 | No
29/05/2019 | 09:12:19 | AP149F | Urban | Planned |  | 54 | 417 | 0.035999 | 8.633e-05 | No
29/05/2019 | 09:12:33 | GA800A | Rural Short | Planned |  | 217 | 250.6267 | 0.40518 | 0.0016167 | No
29/05/2019 | 09:29:04 | YK16 | Rural Long | Planned |  | 33 | 134 | 0.032273 | 0.00024085 | No
29/05/2019 | 09:30:12 | EL20 | Urban | Planned |  | 5 | 435 | 0.0034771 | 7.99e-06 | No
29/05/2019 | 09:31:22 | BU08 | Rural Long | Asset failure | HV | 2 | 28 | 0.00040871 | 1.46e-05 | No
29/05/2019 | 09:35:34 | NL111Q | Urban | Asset failure | LV | 1 | 189 | 0.00030215 | 1.6e-06 | No
29/05/2019 | 09:37:18 | GA28 | Rural Long | Planned |  | 203 | 344 | 0.50966 | 0.0014816 | No
29/05/2019 | 09:41:14 | W29 | Rural Long | Planned |  | 12 | 334 | 0.029252 | 8.758e-05 | No
29/05/2019 | 09:45:30 | MB93 | Rural Long | Planned |  | 23 | 104 | 0.017458 | 0.00016786 | No
29/05/2019 | 09:51:42 | SA31 | Urban | Asset failure | LV | 1 | 264 | 0.00042205 | 1.6e-06 | No
29/05/2019 | 09:54:15 | HK05 | Rural Long | Planned |  | 3 | 166 | 0.0036346 | 2.19e-05 | No
29/05/2019 | 10:14:00 | MTB81 | Rural Short | Planned |  | 275 | 20.28 | 0.041549 | 0.0020488 | No
29/05/2019 | 10:22:23 | CV15 | Rural Long | Planned |  | 29 | 127 | 0.02688 | 0.00021165 | No
29/05/2019 | 10:22:30 | MG17 | Rural Long | Asset failure | HV | 82 | 156.6341 | 0.09374 | 0.00059846 | No
29/05/2019 | 10:41:52 | G31 | Rural Long | Planned |  | 2 | 69 | 0.0010072 | 1.46e-05 | No
29/05/2019 | 10:59:35 | MG06 | Rural Short | Asset failure | Distribution substation | 148 | 110 | 0.12129 | 0.0011026 | No
29/05/2019 | 11:03:04 | CN25 | Rural Long | Asset failure | HV | 59 | 131.322 | 0.056548 | 0.0004306 | No
29/05/2019 | 11:15:03 | BT02 | Rural Long | Planned |  | 12 | 164 | 0.014363 | 8.758e-05 | No
29/05/2019 | 11:58:50 | NU11 | Rural Long | Third Party | Vehicle impact | 1 | 143 | 0.0010437 | 7.3e-06 | No
29/05/2019 | 12:50:36 | SA11 | Urban | Asset failure | LV | 7 | 243 | 0.0027193 | 1.119e-05 | No
29/05/2019 | 12:58:14 | AP146B | Urban | Planned |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
29/05/2019 | 12:59:49 | KI31 | Rural Short | Planned |  | 2 | 61 | 0.00090892 | 1.49e-05 | No
29/05/2019 | 13:10:15 | NL511A | Urban | Asset failure | LV | 1 | 205 | 0.00032773 | 1.6e-06 | No
29/05/2019 | 13:36:51 | R02 | Rural Long | Planned |  | 10 | 2 | 0.00014597 | 7.298e-05 | No
29/05/2019 | 13:40:32 | YK16 | Rural Long | Planned |  | 1 | 19 | 0.00013867 | 7.3e-06 | No
29/05/2019 | 13:42:00 | SD44302 | Rural Short | Weather |  | 1584 | 6 | 0.070806 | 0.011801 | No
29/05/2019 | 13:42:00 | SD44302 | Rural Long | Weather |  | 2286 | 111.2695 | 1.8564 | 0.016684 | No
29/05/2019 | 14:06:00 | SSD116 | Urban | Network business | Switching and protection error | 4783 | 4 | 0.030586 | 0.0076465 | No
29/05/2019 | 14:22:01 | R09 | Rural Long | Asset failure | LV | 5 | 489 | 0.017844 | 3.649e-05 | No
29/05/2019 | 14:39:34 | VH17 | Rural Short | Unknown | Unknown | 278 | 202.964 | 0.42037 | 0.0020711 | No
29/05/2019 | 15:10:57 | HH118C | Urban | Other |  | 70 | 89 | 0.0099597 | 0.00011191 | No
29/05/2019 | 16:41:10 | BU06 | Rural Long | Unknown | Unknown | 275 | 14 | 0.028099 | 0.002007 | No
29/05/2019 | 16:54:22 | HH107B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 252 | 0.00040287 | 1.6e-06 | No
29/05/2019 | 17:47:06 | SM216G | Urban | Asset failure | LV | 36.3333 | 92 | 0.0053438 | 5.809e-05 | No
29/05/2019 | 18:27:58 | ME427E | Urban | Overloads |  | 32 | 37 | 0.0018928 | 5.116e-05 | No
29/05/2019 | 18:52:38 | SM349D | Urban | Overloads |  | 1 | 173 | 0.00027657 | 1.6e-06 | No
29/05/2019 | 19:06:14 | SM410A | Urban | Asset failure | LV | 2 | 109 | 0.00034851 | 3.2e-06 | No
29/05/2019 | 19:29:54 | R09 | Rural Long | Overloads |  | 5 | 13 | 0.00047439 | 3.649e-05 | No
29/05/2019 | 19:46:42 | NL511B | Urban | Asset failure | LV | 1 | 72 | 0.0001151 | 1.6e-06 | No
29/05/2019 | 20:07:10 | HH432B | Urban | Overloads |  | 1 | 166 | 0.00026538 | 1.6e-06 | No
29/05/2019 | 21:02:02 | NU04 | Rural Short | Asset failure | LV | 1 | 180 | 0.001341 | 7.45e-06 | No
29/05/2019 | 22:03:26 | ME200G | Urban | Asset failure | LV | 1 | 141 | 0.00022541 | 1.6e-06 | No
29/05/2019 | 22:53:25 | VH17 | Rural Short | Unknown | Unknown | 212 | 341.6321 | 0.53958 | 0.0015794 | No
29/05/2019 | 22:53:25 | VH17 | Rural Short | Unknown | Unknown | 0 | 40.9867 | 0.045804 | 0 | No
29/05/2019 | 22:57:51 | HH409B | Urban | Planned |  | 100 | 383 | 0.061229 | 0.00015987 | No
30/05/2019 | 00:27:04 | SA18 | Urban | Asset failure | LV | 24.3333 | 105 | 0.0040846 | 3.89e-05 | No
30/05/2019 | 07:25:03 | LX31 | Rural Short | Asset failure | LV | 2 | 612 | 0.009119 | 1.49e-05 | No
30/05/2019 | 07:43:19 | HH130A | Urban | Overloads |  | 1 | 122 | 0.00019504 | 1.6e-06 | No
30/05/2019 | 08:02:18 | SA20 | Urban | Asset failure | Distribution substation | 557 | 90.7163 | 0.080779 | 0.00089046 | No
30/05/2019 | 08:07:20 | MTB82 | Rural Short | Asset failure | LV | 1 | 427 | 0.0031812 | 7.45e-06 | No
30/05/2019 | 08:13:06 | HH145B | Urban | Asset failure | LV | 1 | 168 | 0.00026858 | 1.6e-06 | No
30/05/2019 | 08:17:57 | LX54 | Rural Short | Planned |  | 2 | 392 | 0.0058409 | 1.49e-05 | No
30/05/2019 | 08:25:48 | AP149H | Urban | Asset failure | LV | 1 | 363 | 0.00058032 | 1.6e-06 | No
30/05/2019 | 08:29:36 | AP372F | Urban | Asset failure | LV | 1 | 239 | 0.00038208 | 1.6e-06 | No
30/05/2019 | 08:37:51 | MG51 | Rural Long | Unknown | Unknown | 15 | 84 | 0.0091959 | 0.00010948 | No
30/05/2019 | 08:53:07 | WHY06 | Urban | Planned |  | 160 | 239.9062 | 0.061365 | 0.00025579 | No
30/05/2019 | 09:06:47 | ME427E | Urban | Planned |  | 100 | 217 | 0.034691 | 0.00015987 | No
30/05/2019 | 09:07:39 | AP373D | Urban | Planned |  | 15 | 270 | 0.0064746 | 2.398e-05 | No
30/05/2019 | 09:25:00 | SD34102 | Rural Long | Planned |  | 78 | 296 | 0.1685 | 0.00056927 | No
30/05/2019 | 11:00:18 | NU31 | Rural Long | Planned |  | 1 | 87 | 0.00063496 | 7.3e-06 | No
30/05/2019 | 11:57:24 | MV62 | Rural Short | Overloads |  | 1 | 161 | 0.0011995 | 7.45e-06 | No
30/05/2019 | 12:00:21 | PL34 | Rural Long | Planned |  | 1 | 147 | 0.0010729 | 7.3e-06 | No
30/05/2019 | 12:08:43 | SD48100 | Rural Short | Third Party | Vehicle impact | 230 | 1 | 0.0017135 | 0.0017135 | No
30/05/2019 | 13:04:38 | NL234C | Urban | Overloads |  | 2 | 207 | 0.00066185 | 3.2e-06 | No
30/05/2019 | 13:41:11 | HH107D | Urban | Asset failure | LV | 1 | 296 | 0.00047321 | 1.6e-06 | No
30/05/2019 | 13:41:39 | NA24 | Rural Long | Planned |  | 1 | 26 | 0.00018976 | 7.3e-06 | No
30/05/2019 | 14:31:46 | SG12 | Rural Short | Planned |  | 12 | 32 | 0.0028609 | 8.94e-05 | No
30/05/2019 | 14:35:14 | GA27 | Rural Long | Asset failure | LV | 1 | 463 | 0.0033791 | 7.3e-06 | No
30/05/2019 | 16:13:48 | HH130A | Urban | Asset failure | LV | 1 | 235 | 0.00037569 | 1.6e-06 | No
30/05/2019 | 17:12:03 | SA20 | Urban | Asset failure | LV | 1 | 174 | 0.00027817 | 1.6e-06 | No
30/05/2019 | 17:21:53 | HH429C | Urban | Asset failure | LV | 17.6666 | 236 | 0.0066654 | 2.824e-05 | No
30/05/2019 | 17:51:48 | WHY02 | Urban | Asset failure | LV | 1 | 144 | 0.00023021 | 1.6e-06 | No
30/05/2019 | 17:56:28 | PL07 | Urban | Asset failure | LV | 1 | 104 | 0.00016626 | 1.6e-06 | No
30/05/2019 | 19:21:39 | HH130B | Urban | Overloads |  | 1 | 151 | 0.0002414 | 1.6e-06 | No
30/05/2019 | 19:26:18 | GU32 | Rural Long | Overloads |  | 1 | 353 | 0.0025763 | 7.3e-06 | No
30/05/2019 | 20:03:38 | SM402B | Urban | Asset failure | LV | 99 | 68 | 0.010762 | 0.00015827 | No
30/05/2019 | 20:20:30 | MTB81 | Rural Short | Asset failure | LV | 10.6667 | 185 | 0.014702 | 7.947e-05 | No
30/05/2019 | 20:57:41 | CM22 | Rural Long | Asset failure | HV | 38 | 468.3421 | 0.12989 | 0.00027734 | No
30/05/2019 | 21:36:43 | SM216B | Urban | Asset failure | LV | 16 | 109 | 0.0027881 | 2.558e-05 | No
30/05/2019 | 22:50:00 | HH409B | Urban | Planned |  | 46 | 402 | 0.029563 | 7.354e-05 | No
30/05/2019 | 23:08:44 | NU34 | Rural Long | Unknown | Unknown | 22.3333 | 170 | 0.027709 | 0.000163 | No
31/05/2019 | 00:32:00 | MB22 | Rural Short | Planned |  | 112 | 93 | 0.077601 | 0.00083442 | No
31/05/2019 | 08:20:41 | HH121C | Urban | Third Party | Vehicle impact | 37 | 754 | 0.0446 | 5.915e-05 | No
31/05/2019 | 08:41:28 | NA10 | Rural Long | Asset failure | HV | 1 | 5898 | 0.043046 | 7.3e-06 | No
31/05/2019 | 08:47:03 | SG07 | Rural Short | Planned |  | 55 | 3 | 0.0012293 | 0.00040976 | No
31/05/2019 | 09:03:45 | SA36 | Urban | Planned |  | 17 | 272.2353 | 0.0073987 | 2.718e-05 | No
31/05/2019 | 09:08:05 | SD34102 | Rural Long | Planned |  | 81 | 278.4074 | 0.16458 | 0.00059117 | No
31/05/2019 | 09:12:31 | NU05 | Rural Short | Planned |  | 44 | 202 | 0.066217 | 0.00032781 | No
31/05/2019 | 09:15:15 | SM172C | Urban | Planned |  | 165 | 295 | 0.077816 | 0.00026378 | No
31/05/2019 | 09:21:34 | MT09 | Rural Long | Planned |  | 2 | 72 | 0.001051 | 1.46e-05 | No
31/05/2019 | 09:26:05 | GA22 | Rural Short | Planned |  | 142 | 305 | 0.32267 | 0.0010579 | No
31/05/2019 | 09:30:26 | NU05 | Rural Short | Planned |  | 2 | 337 | 0.0050214 | 1.49e-05 | No
31/05/2019 | 09:33:07 | HH121C | Urban | Third Party | Vehicle impact | 52 | 513 | 0.042646 | 8.313e-05 | No
31/05/2019 | 09:38:06 | CV08 | Rural Long | Planned |  | 1 | 248 | 0.00181 | 7.3e-06 | No
31/05/2019 | 09:41:08 | CD22 | Rural Long | Planned |  | 9 | 222 | 0.014582 | 6.569e-05 | No
31/05/2019 | 09:43:46 | MG24 | Rural Short | Unknown | Unknown | 19 | 114 | 0.016137 | 0.00014155 | No
31/05/2019 | 09:49:05 | ST12 | Rural Short | Planned |  | 23 | 314 | 0.053805 | 0.00017135 | No
31/05/2019 | 09:51:31 | NU05 | Rural Short | Planned |  | 1 | 316 | 0.0023543 | 7.45e-06 | No
31/05/2019 | 09:55:22 | ST42 | Rural Long | Planned |  | 75 | 112 | 0.061306 | 0.00054738 | No
31/05/2019 | 09:55:59 | ME116A | Urban | Planned |  | 121 | 76 | 0.014701 | 0.00019344 | No
31/05/2019 | 09:56:08 | SM349H | Urban | Overloads |  | 1 | 174 | 0.00027817 | 1.6e-06 | No
31/05/2019 | 10:00:05 | MTB63 | Rural Short | Planned |  | 70 | 249 | 0.12986 | 0.00052151 | No
31/05/2019 | 10:05:13 | AP125D | Urban | Planned |  | 357 | 207 | 0.11814 | 0.00057073 | No
31/05/2019 | 10:20:14 | HH130G | Urban | Planned |  | 79 | 18 | 0.0022733 | 0.0001263 | No
31/05/2019 | 10:31:57 | G14 | Rural Long | Planned |  | 1 | 53 | 0.00038681 | 7.3e-06 | No
31/05/2019 | 10:35:34 | SM216C | Urban | Planned |  | 346 | 107 | 0.059186 | 0.00055314 | No
31/05/2019 | 10:45:59 | NA01 | Rural Long | Unknown | Unknown | 87 | 24 | 0.015239 | 0.00063496 | No
31/05/2019 | 10:52:09 | G04 | Rural Long | Planned |  | 4 | 82 | 0.0023938 | 2.919e-05 | No
31/05/2019 | 12:02:30 | AP125D | Urban | Animal | Animal impact | 2287 | 39 | 0.14259 | 0.0036562 | No
31/05/2019 | 12:12:07 | MTB32 | Rural Long | Planned |  | 27 | 116 | 0.022858 | 0.00019706 | No
31/05/2019 | 12:12:17 | GA01 | Urban | Asset failure | LV | 1 | 225 | 0.0003597 | 1.6e-06 | No
31/05/2019 | 12:37:56 | LX43 | Rural Short | Asset failure | LV | 1 | 252 | 0.0018774 | 7.45e-06 | No
31/05/2019 | 12:56:08 | HH148C | Urban | Planned |  | 70 | 68 | 0.0076097 | 0.00011191 | No
31/05/2019 | 13:10:58 | MG44 | Urban | Asset failure | LV | 1 | 227 | 0.0003629 | 1.6e-06 | No
31/05/2019 | 14:12:54 | W27 | Rural Long | Asset failure | HV | 1 | 13 | 9.488e-05 | 7.3e-06 | No
31/05/2019 | 15:40:13 | MI32 | Rural Long | Asset failure | LV | 1 | 145 | 0.0010583 | 7.3e-06 | No
31/05/2019 | 17:16:53 | MT12 | Rural Long | Unknown | Unknown | 2 | 40 | 0.00058387 | 1.46e-05 | No
31/05/2019 | 17:26:28 | MV32 | Rural Short | Weather |  | 13 | 274 | 0.026537 | 9.685e-05 | No
31/05/2019 | 18:15:54 | M21 | Rural Long | Asset failure | LV | 1 | 195 | 0.0014232 | 7.3e-06 | No
31/05/2019 | 18:28:13 | KI32 | Rural Short | Weather |  | 1 | 216 | 0.0016092 | 7.45e-06 | No
31/05/2019 | 20:14:47 | CM12 | Rural Long | Third Party | Vehicle impact | 1 | 140 | 0.0010218 | 7.3e-06 | No
31/05/2019 | 20:36:23 | SM172A | Urban | Overloads |  | 1 | 107 | 0.00017106 | 1.6e-06 | No
31/05/2019 | 23:06:32 | G17 | Rural Long | Asset failure | LV | 1 | 884 | 0.0064517 | 7.3e-06 | No
1/06/2019 | 00:12:05 | KA15 | Rural Long | Asset failure | HV | 59 | 478.5254 | 0.20605 | 0.0004306 | No
1/06/2019 | 08:20:31 | GA745B | Rural Short | Asset failure | LV | 6.6667 | 165 | 0.0081952 | 4.967e-05 | No
1/06/2019 | 08:56:08 | NL111B | Urban | Planned |  | 2 | 231 | 0.00073859 | 3.2e-06 | No
1/06/2019 | 09:24:19 | SG11 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 258 | 0.0019221 | 7.45e-06 | No
1/06/2019 | 09:50:09 | HK02 | Rural Long | Unknown | Unknown | 21 | 15 | 0.002299 | 0.00015327 | No
1/06/2019 | 12:27:05 | SA17 | Urban | Asset failure | LV | 1 | 278 | 0.00044443 | 1.6e-06 | No
1/06/2019 | 13:22:18 | AP424C | Urban | Asset failure | LV | 61 | 479 | 0.046712 | 9.752e-05 | No
1/06/2019 | 13:22:35 | HH177E | Urban | Overloads |  | 1 | 156 | 0.00024939 | 1.6e-06 | No
1/06/2019 | 14:20:26 | NU04 | Rural Short | Unknown | Unknown | 12.3333 | 134 | 0.012313 | 9.189e-05 | No
1/06/2019 | 16:12:10 | HH496G | Urban | Asset failure | LV | 1 | 61 | 9.752e-05 | 1.6e-06 | No
1/06/2019 | 21:08:17 | SM216B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2832 | 68.8333 | 0.31164 | 0.0045274 | No
1/06/2019 | 21:45:28 | AP355H | Urban | Other |  | 33.3333 | 95 | 0.0050625 | 5.329e-05 | No
1/06/2019 | 22:43:55 | VH31 | Rural Short | Asset failure | LV | 18.6667 | 34 | 0.0047284 | 0.00013907 | No
2/06/2019 | 06:18:28 | KA04 | Rural Long | Asset failure | LV | 29.3333 | 301 | 0.064439 | 0.00021408 | No
2/06/2019 | 07:38:24 | ME200A | Urban | Planned |  | 43 | 184 | 0.012649 | 6.874e-05 | No
2/06/2019 | 08:01:25 | SD40600 | Rural Long | Planned |  | 2003 | 386 | 5.6428 | 0.014619 | No
2/06/2019 | 08:20:40 | ME200G | Urban | Planned |  | 276 | 201 | 0.088688 | 0.00044123 | No
2/06/2019 | 08:26:03 | SD34102 | Rural Long | Planned |  | 1019 | 357 | 2.655 | 0.007437 | No
2/06/2019 | 08:30:31 | ST35 | Rural Long | Planned |  | 229 | 31 | 0.051811 | 0.0016713 | No
2/06/2019 | 08:41:45 | PL04 | Urban | Planned |  | 8 | 452 | 0.0057808 | 1.279e-05 | No
2/06/2019 | 09:05:06 | CM25 | Rural Long | Asset failure | HV | 1 | 340 | 0.0024814 | 7.3e-06 | No
2/06/2019 | 09:16:43 | BT03 | Rural Long | Planned |  | 8 | 93 | 0.00543 | 5.839e-05 | No
2/06/2019 | 09:43:02 | SM410B | Urban | Planned |  | 248 | 244 | 0.096739 | 0.00039647 | No
2/06/2019 | 17:14:51 | MT03 | Rural Long | Third Party | Vehicle impact | 20 | 67 | 0.0097798 | 0.00014597 | No
2/06/2019 | 17:30:46 | NL760B | Urban | Overloads |  | 1 | 293 | 0.00046841 | 1.6e-06 | No
2/06/2019 | 18:01:10 | NL210E | Urban | Asset failure | LV | 11 | 82 | 0.001442 | 1.759e-05 | No
2/06/2019 | 19:51:09 | CV16 | Rural Long | Asset failure | LV | 2 | 261 | 0.0038097 | 1.46e-05 | No
2/06/2019 | 21:45:09 | CBD353L | CBD | Planned |  | 1 | 225 | 0.043677 | 0.00019412 | No
2/06/2019 | 22:27:12 | CBD353T | CBD | Planned |  | 1 | 1742 | 0.33815 | 0.00019412 | No
2/06/2019 | 22:39:34 | HH341G | Urban | Planned |  | 6 | 262 | 0.0025131 | 9.59e-06 | No
2/06/2019 | 23:48:17 | HH432F | Urban | Third Party | Vehicle impact | 89 | 332 | 0.047238 | 0.00014228 | No
3/06/2019 | 00:28:32 | HH121A | Urban | Unknown | Unknown | 1 | 190 | 0.00030375 | 1.6e-06 | No
3/06/2019 | 07:07:34 | HH102B | Urban | Asset failure | LV | 1 | 192 | 0.00030695 | 1.6e-06 | No
3/06/2019 | 07:58:44 | SM126C | Urban | Asset failure | LV | 1 | 365 | 0.00058352 | 1.6e-06 | No
3/06/2019 | 08:31:02 | KI11 | Rural Long | Weather |  | 1 | 259 | 0.0018903 | 7.3e-06 | No
3/06/2019 | 08:44:43 | SM179B | Urban | Asset failure | LV | 55 | 64 | 0.0056273 | 8.793e-05 | No
3/06/2019 | 09:02:34 | SM179A | Urban | Planned |  | 73 | 359 | 0.041896 | 0.0001167 | No
3/06/2019 | 09:05:37 | VH72 | Rural Short | Asset failure | LV | 1 | 176 | 0.0013112 | 7.45e-06 | No
3/06/2019 | 09:15:44 | M13 | Rural Long | Planned |  | 1 | 119 | 0.0008685 | 7.3e-06 | No
3/06/2019 | 09:19:32 | MT03 | Rural Long | Third Party | Vehicle impact | 20 | 315 | 0.04598 | 0.00014597 | No
3/06/2019 | 09:30:03 | MG17 | Rural Long | Planned |  | 2 | 125 | 0.0018246 | 1.46e-05 | No
3/06/2019 | 09:36:00 | GA28 | Rural Long | Planned |  | 190 | 271 | 0.37579 | 0.0013867 | No
3/06/2019 | 09:53:20 | NU12 | Rural Long | Asset failure | LV | 1 | 265 | 0.0019341 | 7.3e-06 | No
3/06/2019 | 10:01:49 | ST36 | Rural Long | Planned |  | 29 | 214 | 0.045293 | 0.00021165 | No
3/06/2019 | 10:11:33 | NL234C | Urban | Planned |  | 58 | 286 | 0.026519 | 9.272e-05 | No
3/06/2019 | 10:17:28 | AP214A | Urban | Asset failure | LV | 1 | 66 | 0.00010551 | 1.6e-06 | No
3/06/2019 | 10:52:49 | GU35 | Rural Long | Asset failure | HV | 90 | 12.5444 | 0.0082398 | 0.00065685 | No
3/06/2019 | 10:56:46 | SG09 | Rural Short | Planned |  | 32 | 170 | 0.040529 | 0.0002384 | No
3/06/2019 | 11:39:12 | AP365E | Urban | Asset failure | LV | 98 | 49 | 0.0076768 | 0.00015667 | No
3/06/2019 | 12:13:06 | MB44 | Rural Long | Planned |  | 2 | 77 | 0.0011239 | 1.46e-05 | No
3/06/2019 | 12:15:05 | VH44 | Rural Short | Planned |  | 1 | 29 | 0.00021605 | 7.45e-06 | No
3/06/2019 | 12:20:28 | HH118E | Urban | Asset failure | HV | 1102 | 82.8294 | 0.14592 | 0.0017617 | No
3/06/2019 | 12:35:55 | MG17 | Rural Long | Planned |  | 1 | 55 | 0.00040141 | 7.3e-06 | No
3/06/2019 | 13:02:14 | MB01 | Rural Long | Third Party | Vehicle impact | 13 | 62 | 0.0058825 | 9.488e-05 | No
3/06/2019 | 13:10:43 | ST36 | Rural Long | Planned |  | 1 | 56 | 0.00040871 | 7.3e-06 | No
3/06/2019 | 13:27:52 | BU06 | Rural Long | Unknown | Unknown | 1 | 56 | 0.00040871 | 7.3e-06 | No
3/06/2019 | 15:38:09 | HH428E | Urban | Asset failure | LV | 1 | 198 | 0.00031654 | 1.6e-06 | No
3/06/2019 | 16:19:09 | SM349B | Urban | Asset failure | LV | 137 | 168 | 0.036795 | 0.00021902 | No
3/06/2019 | 16:23:35 | NA35 | Rural Short | Asset failure | Distribution substation | 25 | 1347.6 | 0.251 | 0.00018625 | No
3/06/2019 | 16:25:42 | SSD242 | Rural Long | Animal | Animal impact | 791 | 129.5272 | 0.74776 | 0.005773 | No
3/06/2019 | 17:34:41 | ME427D | Urban | Asset failure | LV | 1 | 167 | 0.00026698 | 1.6e-06 | No
3/06/2019 | 17:40:01 | ME116B | Urban | Asset failure | LV | 1 | 369 | 0.00058991 | 1.6e-06 | No
3/06/2019 | 18:22:41 | MTB81 | Rural Short | Animal | Animal impact | 2 | 139 | 0.0020711 | 1.49e-05 | No
3/06/2019 | 19:16:54 | EL14 | Urban | Asset failure | LV | 1 | 129 | 0.00020623 | 1.6e-06 | No
3/06/2019 | 19:31:26 | PP04 | Rural Short | Overloads |  | 14 | 121 | 0.012621 | 0.0001043 | No
3/06/2019 | 19:52:57 | HH386F | Urban | Asset failure | LV | 1 | 224 | 0.0003581 | 1.6e-06 | No
3/06/2019 | 20:46:13 | SM350D | Urban | Unknown | Unknown | 22 | 100 | 0.0035171 | 3.517e-05 | No
3/06/2019 | 20:54:28 | HH341G | Urban | Asset failure | LV | 37 | 58 | 0.0034308 | 5.915e-05 | No
3/06/2019 | 21:25:58 | CBD353L | CBD | Planned |  | 1 | 341 | 0.066194 | 0.00019412 | No
3/06/2019 | 22:05:45 | ME200E | Urban | Planned |  | 212 | 79.9245 | 0.027088 | 0.00033892 | No
3/06/2019 | 22:05:45 | ME200E | Urban | Planned |  | 0 | 6 | 0.0013237 | 0 | No
3/06/2019 | 22:48:07 | GA52 | Rural Long | Unknown | Unknown | 1 | 306 | 0.0022333 | 7.3e-06 | No
4/06/2019 | 05:28:51 | NL451E | Urban | Asset failure | LV | 1 | 336 | 0.00053715 | 1.6e-06 | No
4/06/2019 | 08:00:09 | GA05 | Rural Short | Asset failure | LV | 2 | 133 | 0.0019817 | 1.49e-05 | No
4/06/2019 | 08:20:43 | GA53 | Rural Short | Planned |  | 1 | 6 | 4.47e-05 | 7.45e-06 | No
4/06/2019 | 08:21:59 | SA20 | Urban | Planned |  | 297 | 128 | 0.060775 | 0.00047481 | No
4/06/2019 | 08:40:28 | CD03 | Rural Short | Planned |  | 73 | 420 | 0.22842 | 0.00054386 | No
4/06/2019 | 09:25:28 | AP424C | Urban | Planned |  | 66 | 195 | 0.020575 | 0.00010551 | No
4/06/2019 | 09:27:25 | CV18 | Rural Short | Planned |  | 62 | 345 | 0.15936 | 0.00046191 | No
4/06/2019 | 09:44:16 | VH22 | Rural Short | Planned |  | 79 | 177 | 0.10418 | 0.00058856 | No
4/06/2019 | 09:53:50 | HH341F | Urban | Other |  | 24.6667 | 104 | 0.0041011 | 3.943e-05 | No
4/06/2019 | 10:05:32 | NL544B | Urban | Planned |  | 2 | 243 | 0.00077696 | 3.2e-06 | No
4/06/2019 | 10:25:37 | PL07 | Urban | Planned |  | 23 | 224 | 0.0082364 | 3.677e-05 | No
4/06/2019 | 10:45:29 | YK08 | Rural Long | Asset failure | HV | 1 | 68 | 0.00049629 | 7.3e-06 | No
4/06/2019 | 11:24:38 | EL10 | Urban | Asset failure | LV | 1 | 142 | 0.00022701 | 1.6e-06 | No
4/06/2019 | 11:52:57 | HH409B | Urban | Asset failure | LV | 38 | 113 | 0.0068647 | 6.075e-05 | No
4/06/2019 | 12:27:03 | WHY11 | Urban | Asset failure | HV | 1 | 109 | 0.00017426 | 1.6e-06 | No
4/06/2019 | 12:35:54 | BT04 | Rural Long | Asset failure | HV | 14 | 202 | 0.02064 | 0.00010218 | No
4/06/2019 | 13:07:01 | MT14 | Rural Short | Third Party | Vehicle impact | 1 | 91 | 0.00067796 | 7.45e-06 | No
4/06/2019 | 13:07:05 | SM374B | Urban | Asset failure | LV | 37 | 156 | 0.0092275 | 5.915e-05 | No
4/06/2019 | 13:36:00 | NL210D | Urban | Animal | Animal impact | 1353 | 202.8788 | 0.43883 | 0.002163 | No
4/06/2019 | 13:41:29 | GA47 | Rural Long | Unknown | Unknown | 52 | 199.6346 | 0.075764 | 0.00037951 | No
4/06/2019 | 16:27:14 | NL511A | Urban | Overloads |  | 1 | 166 | 0.00026538 | 1.6e-06 | No
4/06/2019 | 16:58:53 | SM402D | Urban | Overloads |  | 1 | 206 | 0.00032933 | 1.6e-06 | No
4/06/2019 | 17:21:35 | MI11 | Rural Long | Asset failure | HV | 50 | 542.14 | 0.19784 | 0.00036492 | No
4/06/2019 | 17:21:35 | MI11 | Rural Long | Asset failure | HV | 0 | 2 | 0.00048169 | 0 | No
4/06/2019 | 17:59:49 | HH341E | Urban | Asset failure | LV | 19.3333 | 171 | 0.0052852 | 3.091e-05 | No
4/06/2019 | 19:30:55 | HH118C | Urban | Asset failure | LV | 31 | 59 | 0.002924 | 4.956e-05 | No
4/06/2019 | 20:08:23 | CN24 | Rural Long | Asset failure | HV | 107 | 147.4486 | 0.11515 | 0.00078092 | No
4/06/2019 | 20:18:01 | AP214B | Urban | Overloads |  | 1 | 101 | 0.00016147 | 1.6e-06 | No
4/06/2019 | 21:12:49 | AP355E | Urban | Overloads |  | 1 | 118 | 0.00018864 | 1.6e-06 | No
4/06/2019 | 22:47:20 | EL11 | Urban | Asset failure | LV | 1 | 44 | 7.034e-05 | 1.6e-06 | No
5/06/2019 | 02:58:49 | HH177C | Urban | Overloads |  | 1 | 83 | 0.00013269 | 1.6e-06 | No
5/06/2019 | 05:05:24 | SA13 | Urban | Asset failure | HV | 1063 | 2 | 0.0033988 | 0.0016994 | No
5/06/2019 | 06:01:38 | ST22 | Rural Short | Asset failure | LV | 1 | 244 | 0.0018178 | 7.45e-06 | No
5/06/2019 | 06:42:36 | HH428F | Urban | Asset failure | LV | 1 | 196 | 0.00031334 | 1.6e-06 | No
5/06/2019 | 07:15:23 | NU20 | Rural Long | Asset failure | LV | 10.6667 | 172 | 0.01339 | 7.785e-05 | No
5/06/2019 | 08:05:19 | KI16 | Rural Long | Planned |  | 107 | 40.2523 | 0.031434 | 0.00078092 | No
5/06/2019 | 08:15:25 | AP365E | Urban | Planned |  | 58 | 521 | 0.048309 | 9.272e-05 | No
5/06/2019 | 08:27:29 | GA03 | Rural Long | Planned |  | 158 | 387.0253 | 0.44629 | 0.0011531 | No
5/06/2019 | 09:04:06 | PA04 | Rural Short | Planned |  | 180 | 339 | 0.45461 | 0.001341 | No
5/06/2019 | 09:07:55 | HH409D | Urban | Planned |  | 80 | 190 | 0.0243 | 0.00012789 | No
5/06/2019 | 09:12:55 | HH386D | Urban | Planned |  | 1 | 322 | 0.00051477 | 1.6e-06 | No
5/06/2019 | 09:15:36 | SG07 | Rural Short | Planned |  | 49 | 355 | 0.1296 | 0.00036506 | No
5/06/2019 | 09:25:10 | CM15 | Rural Long | Planned |  | 67 | 198 | 0.09682 | 0.00048899 | No
5/06/2019 | 09:25:39 | NL234C | Urban | Planned |  | 1 | 346 | 0.00055314 | 1.6e-06 | No
5/06/2019 | 09:28:47 | AP226D | Urban | Planned |  | 84 | 451 | 0.060564 | 0.00013429 | No
5/06/2019 | 09:29:25 | ME231A | Urban | Planned |  | 350 | 302.0686 | 0.16902 | 0.00055954 | No
5/06/2019 | 09:30:12 | WK11 | Rural Short | Planned |  | 2 | 11 | 0.0001639 | 1.49e-05 | No
5/06/2019 | 09:30:13 | R25 | Rural Long | Planned |  | 1 | 99 | 0.00072254 | 7.3e-06 | No
5/06/2019 | 09:30:32 | NL234C | Urban | Planned |  | 208 | 279 | 0.092774 | 0.00033252 | No
5/06/2019 | 09:30:51 | SG09 | Rural Short | Planned |  | 64 | 347 | 0.16545 | 0.00047681 | No
5/06/2019 | 09:37:44 | SM410A | Urban | Planned |  | 167 | 224 | 0.059803 | 0.00026698 | No
5/06/2019 | 09:41:59 | VH23 | Rural Short | Planned |  | 85 | 14 | 0.0088657 | 0.00063326 | No
5/06/2019 | 09:50:15 | HH386D | Urban | Planned |  | 1 | 285 | 0.00045562 | 1.6e-06 | No
5/06/2019 | 09:59:05 | EL17 | Urban | Planned |  | 7 | 249 | 0.0027865 | 1.119e-05 | No
5/06/2019 | 10:05:08 | SM126C | Urban | Asset failure | LV | 1 | 307 | 0.00049079 | 1.6e-06 | No
5/06/2019 | 10:09:31 | HH386G | Urban | Asset failure | LV | 67 | 207 | 0.022172 | 0.00010711 | No
5/06/2019 | 10:23:36 | SM374A | Urban | Planned |  | 153 | 177 | 0.043294 | 0.0002446 | No
5/06/2019 | 10:48:54 | HH386D | Urban | Planned |  | 102 | 122 | 0.019894 | 0.00016306 | No
5/06/2019 | 10:51:35 | HH341B | Urban | Unknown | Unknown | 16.6667 | 98 | 0.0026112 | 2.664e-05 | No
5/06/2019 | 10:55:16 | EL02 | Urban | Planned |  | 73 | 97.0959 | 0.011331 | 0.0001167 | No
5/06/2019 | 11:21:47 | EL01R | Urban | Third Party | Other | 1 | 69 | 0.00011031 | 1.6e-06 | No
5/06/2019 | 11:31:22 | WK31 | Rural Short | Planned |  | 3 | 9 | 0.00020115 | 2.235e-05 | No
5/06/2019 | 11:48:27 | SM172A | Urban | Asset failure | LV | 4 | 372 | 0.0023788 | 6.39e-06 | No
5/06/2019 | 12:17:24 | CM16 | Rural Long | Asset failure | Distribution substation | 87 | 383 | 0.24319 | 0.00063496 | No
5/06/2019 | 14:15:47 | WK51 | Rural Short | Planned |  | 6 | 12 | 0.00053641 | 4.47e-05 | No
5/06/2019 | 14:28:55 | AP146B | Urban | Overloads |  | 1 | 174 | 0.00027817 | 1.6e-06 | No
5/06/2019 | 14:54:04 | HH386F | Urban | Overloads |  | 1 | 174 | 0.00027817 | 1.6e-06 | No
5/06/2019 | 15:05:27 | SA14 | Urban | Asset failure | LV | 1 | 233 | 0.00037249 | 1.6e-06 | No
5/06/2019 | 17:44:51 | HH148B | Urban | Asset failure | LV | 25.3333 | 49 | 0.0019845 | 4.05e-05 | No
5/06/2019 | 18:36:44 | HH121A | Urban | Asset failure | Distribution substation | 68 | 243 | 0.026417 | 0.00010871 | No
5/06/2019 | 19:25:01 | HH522C | Urban | Overloads |  | 26.3333 | 168 | 0.0070725 | 4.21e-05 | No
5/06/2019 | 20:12:15 | SM411A | Urban | Asset failure | LV | 1 | 151 | 0.0002414 | 1.6e-06 | No
5/06/2019 | 20:18:29 | SM350E | Urban | Asset failure | LV | 21 | 102 | 0.0034244 | 3.357e-05 | No
5/06/2019 | 20:39:40 | NL234A | Urban | Asset failure | LV | 29 | 55 | 0.0025499 | 4.636e-05 | No
5/06/2019 | 20:49:11 | AP424E | Urban | Asset failure | HV | 2123 | 31.968 | 0.1085 | 0.003394 | No
5/06/2019 | 22:40:54 | CBD366H | CBD | Planned |  | 1 | 5082 | 0.98651 | 0.00019412 | No
6/06/2019 | 03:39:12 | SD31400 | Rural Long | Asset failure | Subtransmission | 676 | 388.5237 | 1.9169 | 0.0049337 | No
6/06/2019 | 07:07:36 | GA01 | Urban | Planned |  | 32 | 100 | 0.0051158 | 5.116e-05 | No
6/06/2019 | 08:17:00 | GA11 | Rural Short | Planned |  | 1 | 15 | 0.00011175 | 7.45e-06 | No
6/06/2019 | 08:45:51 | WHY14 | Urban | Planned |  | 106 | 130 | 0.02203 | 0.00016946 | No
6/06/2019 | 08:54:46 | SD34102 | Rural Long | Planned |  | 2 | 285 | 0.0041601 | 1.46e-05 | No
6/06/2019 | 08:57:08 | GU43 | Rural Long | Planned |  | 58 | 304 | 0.12868 | 0.0004233 | No
6/06/2019 | 09:08:16 | GA53 | Rural Short | Planned |  | 65 | 201.3846 | 0.097522 | 0.00048426 | No
6/06/2019 | 09:10:18 | AP149B | Urban | Planned |  | 50 | 178 | 0.014228 | 7.993e-05 | No
6/06/2019 | 09:11:37 | GA53 | Rural Short | Planned |  | 5 | 89 | 0.0033153 | 3.725e-05 | No
6/06/2019 | 09:15:11 | AP344D | Urban | Planned |  | 1 | 56 | 8.953e-05 | 1.6e-06 | No
6/06/2019 | 09:20:28 | NL111C | Urban | Planned |  | 98 | 255 | 0.039951 | 0.00015667 | No
6/06/2019 | 09:20:30 | AP344D | Urban | Planned |  | 48 | 129 | 0.009899 | 7.674e-05 | No
6/06/2019 | 09:22:15 | GA27 | Rural Long | Planned |  | 14 | 95.7143 | 0.0097798 | 0.00010218 | No
6/06/2019 | 09:22:41 | BT06 | Rural Long | Planned |  | 6 | 343 | 0.01502 | 4.379e-05 | No
6/06/2019 | 09:24:35 | AP344D | Urban | Planned |  | 2 | 46 | 0.00014708 | 3.2e-06 | No
6/06/2019 | 09:30:45 | PA03 | Urban | Planned |  | 2 | 240 | 0.00076736 | 3.2e-06 | No
6/06/2019 | 09:30:47 | AP149F | Urban | Planned |  | 55 | 218 | 0.019168 | 8.793e-05 | No
6/06/2019 | 09:38:43 | NL544B | Urban | Planned |  | 90 | 381 | 0.054819 | 0.00014388 | No
6/06/2019 | 10:05:27 | AP227B | Urban | Planned |  | 261 | 290 | 0.121 | 0.00041725 | No
6/06/2019 | 10:14:08 | GU17 | Rural Long | Planned |  | 18 | 118 | 0.015502 | 0.00013137 | No
6/06/2019 | 10:17:36 | AP149D | Urban | Planned |  | 1 | 166 | 0.00026538 | 1.6e-06 | No
6/06/2019 | 10:25:03 | VH18 | Rural Short | Planned |  | 1 | 173 | 0.0012889 | 7.45e-06 | No
6/06/2019 | 10:38:49 | CV29 | Rural Long | Planned |  | 2 | 63 | 0.00091959 | 1.46e-05 | No
6/06/2019 | 11:34:27 | CD03 | Rural Short | Planned |  | 73 | 233 | 0.12672 | 0.00054386 | No
6/06/2019 | 11:34:49 | AP149F | Urban | Planned |  | 1 | 283 | 0.00045243 | 1.6e-06 | No
6/06/2019 | 13:51:21 | HH496C | Urban | Unknown | Unknown | 1 | 161 | 0.00025739 | 1.6e-06 | No
6/06/2019 | 14:42:19 | HH432E | Urban | Asset failure | LV | 24.6667 | 113 | 0.004456 | 3.943e-05 | No
6/06/2019 | 16:52:25 | HH496C | Urban | Asset failure | LV | 15 | 428 | 0.010263 | 2.398e-05 | No
6/06/2019 | 18:46:26 | G38 | Rural Long | Unknown | Unknown | 19 | 281 | 0.038966 | 0.00013867 | No
6/06/2019 | 19:33:21 | SM411B | Urban | Asset failure | LV | 1 | 167 | 0.00026698 | 1.6e-06 | No
6/06/2019 | 20:34:40 | SM350A | Urban | Asset failure | LV | 23 | 40 | 0.0014708 | 3.677e-05 | No
6/06/2019 | 22:58:51 | SM216G | Urban | Asset failure | LV | 87 | 92 | 0.012796 | 0.00013908 | No
6/06/2019 | 23:39:51 | EL01C | Urban | Unknown | Unknown | 42 | 39 | 0.0026186 | 6.714e-05 | No
7/06/2019 | 06:29:01 | AP226C | Urban | Asset failure | LV | 1 | 243 | 0.00038848 | 1.6e-06 | No
7/06/2019 | 08:49:06 | HH409D | Urban | Planned |  | 112 | 11 | 0.0019696 | 0.00017905 | No
7/06/2019 | 08:57:40 | HH118D | Urban | Other |  | 24.3333 | 103 | 0.0040068 | 3.89e-05 | No
7/06/2019 | 08:57:47 | MB17 | Rural Short | Other |  | 29.6667 | 17 | 0.0037574 | 0.00022102 | No
7/06/2019 | 09:00:19 | EL03 | Urban | Planned |  | 158 | 80 | 0.020207 | 0.00025259 | No
7/06/2019 | 09:07:18 | SG07 | Rural Short | Planned |  | 146 | 105 | 0.11421 | 0.0010877 | No
7/06/2019 | 09:09:45 | NL111C | Urban | Planned |  | 141 | 286 | 0.064468 | 0.00022541 | No
7/06/2019 | 09:16:11 | MG05 | Rural Long | Planned |  | 12 | 335 | 0.029339 | 8.758e-05 | No
7/06/2019 | 09:18:24 | ST16 | Rural Short | Planned |  | 44 | 74 | 0.024258 | 0.00032781 | No
7/06/2019 | 09:30:27 | SM216A | Urban | Planned |  | 113 | 263 | 0.047511 | 0.00018065 | No
7/06/2019 | 09:34:31 | PA02 | Urban | Planned |  | 58 | 166 | 0.015392 | 9.272e-05 | No
7/06/2019 | 09:41:55 | MTB12 | Rural Short | Planned |  | 1 | 192 | 0.0014304 | 7.45e-06 | No
7/06/2019 | 09:50:14 | AP125C | Urban | Planned |  | 56 | 259 | 0.023187 | 8.953e-05 | No
7/06/2019 | 10:19:01 | ME231A | Urban | Planned |  | 244 | 113 | 0.044079 | 0.00039008 | No
7/06/2019 | 10:21:06 | ME347A | Urban | Planned |  | 93 | 158 | 0.023491 | 0.00014868 | No
7/06/2019 | 10:31:29 | SG01 | Rural Short | Planned |  | 41 | 56 | 0.017106 | 0.00030546 | No
7/06/2019 | 10:34:46 | SD35200 | Rural Long | Planned |  | 22 | 91 | 0.014611 | 0.00016056 | No
7/06/2019 | 11:50:04 | HH409B | Urban | Planned |  | 19 | 549 | 0.016676 | 3.037e-05 | No
7/06/2019 | 12:47:36 | HH409B | Urban | Third Party | Vehicle impact | 66 | 391 | 0.041255 | 0.00010551 | No
7/06/2019 | 13:24:24 | M41 | Rural Long | Asset failure | LV | 1 | 138 | 0.0010072 | 7.3e-06 | No
7/06/2019 | 15:35:50 | SM410C | Urban | Asset failure | LV | 48 | 181 | 0.013889 | 7.674e-05 | No
7/06/2019 | 17:56:51 | HH145A | Urban | Overloads |  | 1 | 230 | 0.0003677 | 1.6e-06 | No
7/06/2019 | 18:27:24 | SM179A | Urban | Asset failure | LV | 27.6667 | 116 | 0.0051307 | 4.423e-05 | No
7/06/2019 | 19:03:36 | SM411F | Urban | Overloads |  | 1 | 125 | 0.00019983 | 1.6e-06 | No
7/06/2019 | 19:36:54 | SM410C | Urban | Planned |  | 72 | 190 | 0.02187 | 0.0001151 | No
7/06/2019 | 20:36:58 | SM179A | Urban | Asset failure | LV | 27.6667 | 76 | 0.0033615 | 4.423e-05 | No
7/06/2019 | 22:42:16 | MI19 | Rural Long | Asset failure | Distribution substation | 90 | 391.2444 | 0.25699 | 0.00065685 | No
8/06/2019 | 00:44:53 | SA33 | Urban | Third Party | Vehicle impact | 84 | 558 | 0.074933 | 0.00013429 | No
8/06/2019 | 00:45:28 | SA33 | Urban | Third Party | Vehicle impact | 78 | 562 | 0.07008 | 0.0001247 | No
8/06/2019 | 02:05:00 | SA33 | Urban | Third Party | Vehicle impact | 0 | 470 | 0.058607 | 0 | No
8/06/2019 | 03:01:12 | EL260A | Urban | Asset failure | HV | 3001 | 25.7194 | 0.12339 | 0.0047976 | No
8/06/2019 | 07:03:46 | HH522C | Urban | Overloads |  | 14 | 390 | 0.0087288 | 2.238e-05 | No
8/06/2019 | 08:04:22 | HH107B | Urban | Planned |  | 122 | 324 | 0.063192 | 0.00019504 | No
8/06/2019 | 08:22:29 | ME131A | Urban | Unknown | Unknown | 1 | 127 | 0.00020303 | 1.6e-06 | No
8/06/2019 | 08:57:35 | MB24 | Rural Short | Other |  | 1 | 204 | 0.0015198 | 7.45e-06 | No
8/06/2019 | 10:11:35 | SA33 | Urban | Other |  | 84 | 118 | 0.015846 | 0.00013429 | No
8/06/2019 | 10:23:17 | SA33 | Urban | Other |  | 78 | 107 | 0.013343 | 0.0001247 | No
8/06/2019 | 11:12:18 | MV64 | Urban | Asset failure | LV | 1 | 616 | 0.00098478 | 1.6e-06 | No
8/06/2019 | 13:05:13 | MTB13 | Rural Short | Overloads |  | 1 | 154 | 0.0011473 | 7.45e-06 | No
8/06/2019 | 16:59:43 | NL234A | Urban | Asset failure | LV | 2 | 208 | 0.00066505 | 3.2e-06 | No
8/06/2019 | 17:58:20 | HH409B | Urban | Asset failure | LV | 2 | 112 | 0.0003581 | 3.2e-06 | No
8/06/2019 | 19:44:19 | AP149B | Urban | Other |  | 1 | 64 | 0.00010232 | 1.6e-06 | No
8/06/2019 | 19:50:29 | HH145B | Urban | Unknown | Unknown | 35.3333 | 85 | 0.0048014 | 5.649e-05 | No
8/06/2019 | 21:05:04 | VH23 | Rural Short | Asset failure | LV | 18.3333 | 126 | 0.01721 | 0.00013659 | No
8/06/2019 | 21:55:03 | MT08 | Rural Long | Asset failure | LV | 19 | 131 | 0.018166 | 0.00013867 | No
9/06/2019 | 04:16:55 | GA09 | Rural Long | Animal | Animal impact | 8 | 129 | 0.0075319 | 5.839e-05 | No
9/06/2019 | 07:09:51 | AP373C | Urban | Planned |  | 157 | 153 | 0.038402 | 0.00025099 | No
9/06/2019 | 09:26:31 | BS0211 | Rural Long | Planned |  | 5 | 292 | 0.010656 | 3.649e-05 | No
9/06/2019 | 10:42:37 | ME131C | Urban | Asset failure | LV | 22.3333 | 139 | 0.0049628 | 3.57e-05 | No
9/06/2019 | 12:29:52 | HH386D | Urban | Other |  | 15.3333 | 169 | 0.0041427 | 2.451e-05 | No
9/06/2019 | 16:11:30 | CN21 | Rural Long | Asset failure | HV | 114 | 106.4912 | 0.088602 | 0.00083201 | No
9/06/2019 | 16:24:12 | AP139B | Urban | Asset failure | LV | 24.6667 | 63 | 0.0024843 | 3.943e-05 | No
9/06/2019 | 16:25:34 | AP146A | Urban | Overloads |  | 1 | 112 | 0.00017905 | 1.6e-06 | No
9/06/2019 | 16:48:24 | KA02 | Rural Short | Asset failure | LV | 22 | 152 | 0.024913 | 0.0001639 | No
9/06/2019 | 17:26:52 | MTB82 | Rural Short | Asset failure | LV | 1 | 1490 | 0.011101 | 7.45e-06 | No
9/06/2019 | 18:42:14 | SM216G | Urban | Asset failure | LV | 1 | 253 | 0.00040446 | 1.6e-06 | No
9/06/2019 | 19:07:01 | SM126D | Urban | Overloads |  | 1 | 268 | 0.00042844 | 1.6e-06 | No
9/06/2019 | 19:31:36 | VH31 | Rural Short | Asset failure | LV | 1 | 350 | 0.0026076 | 7.45e-06 | No
9/06/2019 | 21:14:20 | SG02 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 724 | 136.5939 | 0.73678 | 0.0053939 | No
9/06/2019 | 21:24:35 | HH121D | Urban | Asset failure | LV | 1 | 225 | 0.0003597 | 1.6e-06 | No
9/06/2019 | 22:38:14 | KI55 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 73 | 881 | 0.46938 | 0.00053278 | No
9/06/2019 | 22:38:48 | KI42 | Rural Long | Unknown | Unknown | 143 | 723 | 0.75457 | 0.0010437 | No
9/06/2019 | 23:24:39 | KI42 | Rural Long | Asset failure | HV | 242 | 549.6405 | 0.97077 | 0.0017662 | No
9/06/2019 | 23:26:23 | NL111C | Urban | Asset failure | LV | 1 | 157 | 0.00025099 | 1.6e-06 | No
10/06/2019 | 00:06:51 | CN42 | Rural Long | Asset failure | Distribution substation | 28 | 190.0714 | 0.038842 | 0.00020435 | No
10/06/2019 | 01:23:38 | MB26 | Rural Long | Overloads |  | 1 | 875 | 0.006386 | 7.3e-06 | No
10/06/2019 | 01:44:15 | NU33 | Rural Long | Unknown | Unknown | 5.3333 | 740 | 0.028804 | 3.892e-05 | No
10/06/2019 | 01:50:36 | MTB54 | Rural Long | Asset failure | HV | 246 | 390.4024 | 0.70093 | 0.0017954 | No
10/06/2019 | 02:39:57 | AP132A | Urban | Third Party | Vehicle impact | 1.3333 | 133 | 0.0002835 | 2.13e-06 | No
10/06/2019 | 03:37:49 | NL111C | Urban | Asset failure | LV | 1 | 278 | 0.00044443 | 1.6e-06 | No
10/06/2019 | 03:56:34 | AP424C | Urban | Overloads |  | 1 | 430 | 0.00068743 | 1.6e-06 | No
10/06/2019 | 07:05:27 | NL544A | Urban | Asset failure | LV | 1 | 28 | 4.476e-05 | 1.6e-06 | No
10/06/2019 | 07:33:50 | SM350F | Urban | Overloads |  | 1 | 312 | 0.00049879 | 1.6e-06 | No
10/06/2019 | 09:01:48 | VH32 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 3 | 253 | 0.0056547 | 2.235e-05 | No
10/06/2019 | 09:34:10 | SM179B | Urban | Asset failure | LV | 12.3333 | 578 | 0.011396 | 1.972e-05 | No
10/06/2019 | 10:01:36 | SM411D | Urban | Asset failure | LV | 1 | 388 | 0.00062029 | 1.6e-06 | No
10/06/2019 | 11:20:10 | AP355E | Urban | Other |  | 6 | 176 | 0.0016882 | 9.59e-06 | No
10/06/2019 | 11:21:30 | MI13 | Rural Long | Asset failure | HV | 1 | 478 | 0.0034886 | 7.3e-06 | No
10/06/2019 | 12:18:35 | KI54 | Rural Long | Asset failure | HV | 1 | 138 | 0.0010072 | 7.3e-06 | No
10/06/2019 | 12:31:56 | SA744D | Urban | Asset failure | LV | 1 | 254 | 0.00040606 | 1.6e-06 | No
10/06/2019 | 14:28:44 | HH496A | Urban | Asset failure | LV | 14.3333 | 104 | 0.0023831 | 2.291e-05 | No
10/06/2019 | 15:10:29 | SA41 | Urban | Asset failure | LV | 1.3333 | 175 | 0.00037302 | 2.13e-06 | No
10/06/2019 | 15:45:26 | KI53 | Rural Long | Unknown | Unknown | 1 | 29 | 0.00021165 | 7.3e-06 | No
10/06/2019 | 16:34:09 | AP149E | Urban | Third Party | Vehicle impact | 3 | 315 | 0.0015107 | 4.8e-06 | No
10/06/2019 | 17:47:31 | AP149E | Urban | Third Party | Vehicle impact | 2 | 209 | 0.00066825 | 3.2e-06 | No
10/06/2019 | 19:27:12 | NL21 | Urban | Asset failure | HV | 262 | 121.3969 | 0.050847 | 0.00041885 | No
10/06/2019 | 22:05:26 | SA520D | Urban | Asset failure | LV | 1 | 84 | 0.00013429 | 1.6e-06 | No
10/06/2019 | 23:24:00 | VH23 | Rural Short | Planned |  | 334 | 428 | 1.065 | 0.0024883 | No
10/06/2019 | 23:58:34 | SA520D | Urban | Asset failure | LV | 17.6667 | 134 | 0.0037846 | 2.824e-05 | No
11/06/2019 | 04:56:49 | SA520D | Urban | Asset failure | LV | 35.3333 | 589 | 0.033271 | 5.649e-05 | No
11/06/2019 | 05:52:22 | KI55 | Rural Long | Unknown | Unknown | 73 | 423 | 0.22537 | 0.00053278 | No
11/06/2019 | 05:58:24 | M13 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 61 | 0.02315 | 0.00037951 | No
11/06/2019 | 08:24:51 | KI42 | Rural Long | Third Party | Other | 216 | 82.7778 | 0.13049 | 0.0015764 | No
11/06/2019 | 08:43:53 | BM15 | Rural Short | Planned |  | 9 | 116 | 0.007778 | 6.705e-05 | No
11/06/2019 | 08:49:26 | MTB33 | Rural Short | Asset failure | LV | 1 | 129 | 0.00096107 | 7.45e-06 | No
11/06/2019 | 08:58:27 | NL234C | Urban | Planned |  | 96 | 293 | 0.044968 | 0.00015347 | No
11/06/2019 | 09:10:55 | HH145D | Urban | Planned |  | 36 | 169 | 0.0097263 | 5.755e-05 | No
11/06/2019 | 10:00:37 | SG04 | Rural Short | Planned |  | 44 | 143 | 0.046876 | 0.00032781 | No
11/06/2019 | 10:06:51 | HH341H | Urban | Asset failure | LV | 1 | 81 | 0.00012949 | 1.6e-06 | No
11/06/2019 | 10:10:38 | SM349A | Urban | Planned |  | 1 | 204 | 0.00032613 | 1.6e-06 | No
11/06/2019 | 10:14:43 | MG22 | Rural Long | Asset failure | LV | 1 | 133 | 0.00097068 | 7.3e-06 | No
11/06/2019 | 10:19:05 | SA11 | Urban | Planned |  | 1 | 63 | 0.00010072 | 1.6e-06 | No
11/06/2019 | 10:23:12 | G21 | Rural Long | Unknown | Unknown | 1 | 179 | 0.0013064 | 7.3e-06 | No
11/06/2019 | 10:54:47 | NL234A | Urban | Unknown | Unknown | 225 | 109 | 0.039207 | 0.0003597 | No
11/06/2019 | 11:17:48 | BT18 | Rural Long | Planned |  | 2 | 122 | 0.0017808 | 1.46e-05 | No
11/06/2019 | 11:27:51 | G17 | Rural Long | Planned |  | 123 | 190.0569 | 0.17061 | 0.0008977 | No
11/06/2019 | 11:40:56 | HH177C | Urban | Asset failure | LV | 66 | 299 | 0.031548 | 0.00010551 | No
11/06/2019 | 12:56:29 | MI20 | Rural Long | Asset failure | LV | 1 | 71 | 0.00051818 | 7.3e-06 | No
11/06/2019 | 13:08:41 | SM216A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 2096 | 61 | 0.2044 | 0.0033508 | No
11/06/2019 | 15:08:04 | SA20 | Urban | Unknown | Unknown | 14 | 50 | 0.0011191 | 2.238e-05 | No
11/06/2019 | 19:01:21 | ME347G | Urban | Asset failure | LV | 61 | 86 | 0.0083867 | 9.752e-05 | No
11/06/2019 | 20:54:44 | SA20 | Urban | Asset failure | LV | 1 | 73 | 0.0001167 | 1.6e-06 | No
11/06/2019 | 21:20:40 | NL210B | Urban | Asset failure | LV | 1 | 101 | 0.00016147 | 1.6e-06 | No
11/06/2019 | 21:22:36 | W17 | Rural Long | Weather |  | 31 | 154.3871 | 0.03493 | 0.00022625 | No
11/06/2019 | 22:26:48 | CV25 | Rural Long | Unknown | Unknown | 55 | 527.1091 | 0.21159 | 0.00040141 | No
11/06/2019 | 23:49:12 | KA12 | Rural Long | Weather |  | 49 | 589.7143 | 0.21089 | 0.00035762 | No
12/06/2019 | 00:17:24 | ST12 | Rural Short | Unknown | Unknown | 20 | 202 | 0.030099 | 0.000149 | No
12/06/2019 | 00:50:53 | SD38100 | Rural Long | Unknown | Unknown | 5 | 367 | 0.013392 | 3.649e-05 | No
12/06/2019 | 01:06:00 | M21 | Rural Long | Weather |  | 94 | 338 | 0.23188 | 0.00068604 | No
12/06/2019 | 01:51:48 | MB83 | Rural Long | Weather |  | 52 | 626.3846 | 0.23772 | 0.00037951 | No
12/06/2019 | 02:18:53 | CBD353P | CBD | Weather |  | 1 | 284 | 0.05513 | 0.00019412 | No
12/06/2019 | 03:19:02 | SD38100 | Rural Long | Weather |  | 64 | 412 | 0.19244 | 0.00046709 | No
12/06/2019 | 04:40:09 | CL05 | Rural Long | Unknown | Unknown | 26.3333 | 223 | 0.042858 | 0.00019219 | No
12/06/2019 | 05:06:24 | HH148D | Urban | Weather |  | 6 | 241 | 0.0023117 | 9.59e-06 | No
12/06/2019 | 05:32:35 | CBD103A | Urban | Asset failure | LV | 30.3333 | 531 | 0.02575 | 4.849e-05 | No
12/06/2019 | 06:52:07 | MTB11 | Rural Short | Asset failure | LV | 1 | 108 | 0.00080462 | 7.45e-06 | No
12/06/2019 | 06:52:52 | NL210B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 55 | 404 | 0.035523 | 8.793e-05 | No
12/06/2019 | 07:03:39 | AP424E | Urban | Asset failure | LV | 58 | 261 | 0.024201 | 9.272e-05 | No
12/06/2019 | 07:17:39 | MTB52 | Rural Long | Asset failure | LV | 1 | 170 | 0.0012407 | 7.3e-06 | No
12/06/2019 | 07:23:07 | KI55 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 73 | 163.2329 | 0.086967 | 0.00053278 | No
12/06/2019 | 08:00:46 | HH428A | Urban | Asset failure | LV | 63 | 158 | 0.015913 | 0.00010072 | No
12/06/2019 | 08:05:44 | ST12 | Rural Short | Unknown | Unknown | 2 | 195 | 0.0029056 | 1.49e-05 | No
12/06/2019 | 08:33:21 | SA520D | Urban | Unknown | Unknown | 17.6667 | 403 | 0.011382 | 2.824e-05 | No
12/06/2019 | 08:56:04 | AP351B | Urban | Planned |  | 243.6668 | 4.0944 | 0.0015949 | 0.00038954 | No
12/06/2019 | 09:04:03 | ST11 | Rural Short | Planned |  | 8 | 201 | 0.01198 | 5.96e-05 | No
12/06/2019 | 09:28:13 | M71 | Rural Long | Planned |  | 3 | 129 | 0.0028245 | 2.19e-05 | No
12/06/2019 | 09:38:24 | SM179C | Urban | Asset failure | LV | 81 | 183 | 0.023697 | 0.00012949 | No
12/06/2019 | 10:00:57 | EL01Q | Urban | Asset failure | LV | 20.6667 | 274 | 0.0090528 | 3.304e-05 | No
12/06/2019 | 10:22:02 | GU11 | Rural Long | Unknown | Unknown | 2 | 230 | 0.0033572 | 1.46e-05 | No
12/06/2019 | 10:23:05 | MB63 | Rural Long | Planned |  | 29 | 200 | 0.04233 | 0.00021165 | No
12/06/2019 | 10:30:25 | ST51 | Rural Short | Planned |  | 4 | 104 | 0.0030993 | 2.98e-05 | No
12/06/2019 | 10:50:40 | SM179C | Urban | Asset failure | LV | 36 | 96 | 0.005525 | 5.755e-05 | No
12/06/2019 | 11:00:31 | PL30 | Rural Long | Unknown | Unknown | 1 | 10 | 7.298e-05 | 7.3e-06 | No
12/06/2019 | 11:30:36 | KA04 | Rural Long | Unknown | Unknown | 10 | 25 | 0.0018246 | 7.298e-05 | No
12/06/2019 | 11:58:34 | ME347F | Urban | Asset failure | LV | 52 | 139 | 0.011555 | 8.313e-05 | No
12/06/2019 | 12:09:44 | ME131C | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 377 | 0.0006027 | 1.6e-06 | No
12/06/2019 | 12:54:39 | ST51 | Rural Short | Planned |  | 1 | 114 | 0.00084932 | 7.45e-06 | No
12/06/2019 | 13:20:43 | SM126C | Urban | Asset failure | Distribution substation | 583.3333 | 118.0149 | 0.11006 | 0.00093256 | No
12/06/2019 | 14:45:49 | GU13 | Rural Long | Animal | Animal impact | 10 | 119 | 0.008685 | 7.298e-05 | No
12/06/2019 | 14:51:12 | EL11 | Urban | Asset failure | LV | 1 | 622 | 0.00099438 | 1.6e-06 | No
12/06/2019 | 15:26:01 | EL01X | Urban | Asset failure | LV | 1 | 140 | 0.00022381 | 1.6e-06 | No
12/06/2019 | 15:41:09 | EL09 | Urban | Asset failure | LV | 1 | 324 | 0.00051797 | 1.6e-06 | No
12/06/2019 | 15:43:38 | LX43 | Rural Short | Asset failure | LV | 1 | 117 | 0.00087167 | 7.45e-06 | No
12/06/2019 | 17:08:43 | MG10 | Rural Long | Other |  | 1 | 260 | 0.0018976 | 7.3e-06 | No
12/06/2019 | 17:30:23 | NL511B | Urban | Asset failure | LV | 69 | 77 | 0.0084938 | 0.00011031 | No
12/06/2019 | 18:19:30 | EL01Q | Urban | Asset failure | LV | 31 | 965 | 0.047824 | 4.956e-05 | No
12/06/2019 | 18:33:23 | EL13 | Urban | Unknown | Unknown | 68.6667 | 17 | 0.0018662 | 0.00010978 | No
12/06/2019 | 18:53:25 | HH177G | Urban | Asset failure | LV | 1 | 277 | 0.00044283 | 1.6e-06 | No
12/06/2019 | 19:03:12 | AP424F | Urban | Asset failure | LV | 31 | 68 | 0.00337 | 4.956e-05 | No
12/06/2019 | 19:10:58 | BT03 | Rural Long | Asset failure | HV | 1 | 59 | 0.0004306 | 7.3e-06 | No
12/06/2019 | 19:18:57 | HH177C | Urban | Other |  | 1 | 262 | 0.00041885 | 1.6e-06 | No
12/06/2019 | 19:46:36 | AP355F | Urban | Asset failure | LV | 1 | 880 | 0.0014068 | 1.6e-06 | No
12/06/2019 | 20:22:15 | SG14 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 52 | 246 | 0.095302 | 0.00038741 | No
12/06/2019 | 20:23:05 | SM349F | Urban | Asset failure | LV | 1 | 291 | 0.00046521 | 1.6e-06 | No
13/06/2019 | 04:30:16 | SA11 | Urban | Asset failure | LV | 1 | 458 | 0.00073219 | 1.6e-06 | No
13/06/2019 | 06:20:15 | AP227C | Urban | Unknown | Unknown | 22.3333 | 170 | 0.0060696 | 3.57e-05 | No
13/06/2019 | 08:37:13 | AP132D | Urban | Planned |  | 295 | 336 | 0.15846 | 0.00047161 | No
13/06/2019 | 08:49:16 | BM56 | Rural Short | Planned |  | 32 | 174 | 0.041482 | 0.0002384 | No
13/06/2019 | 09:05:26 | EL19 | Urban | Planned |  | 42 | 343 | 0.023031 | 6.714e-05 | No
13/06/2019 | 09:05:35 | AP344F | Urban | Planned |  | 2 | 257 | 0.00082172 | 3.2e-06 | No
13/06/2019 | 09:09:18 | KI54 | Rural Long | Planned |  | 1 | 179 | 0.0013064 | 7.3e-06 | No
13/06/2019 | 09:12:10 | GU36 | Rural Long | Planned |  | 2 | 143 | 0.0020873 | 1.46e-05 | No
13/06/2019 | 09:12:58 | NL544B | Urban | Planned |  | 66 | 268 | 0.028277 | 0.00010551 | No
13/06/2019 | 09:18:17 | YK19 | Rural Long | Planned |  | 6 | 291 | 0.012743 | 4.379e-05 | No
13/06/2019 | 09:27:39 | W29 | Rural Long | Planned |  | 36 | 206 | 0.054124 | 0.00026274 | No
13/06/2019 | 09:41:39 | NU13 | Rural Long | Planned |  | 58 | 277 | 0.11726 | 0.0004233 | No
13/06/2019 | 10:31:39 | HH409E | Urban | Asset failure | LV | 20.6667 | 84 | 0.0027753 | 3.304e-05 | No
13/06/2019 | 10:43:22 | SM216B | Urban | Planned |  | 130 | 215 | 0.044683 | 0.00020783 | No
13/06/2019 | 10:45:28 | AP424E | Urban | Overloads |  | 1 | 154 | 0.0002462 | 1.6e-06 | No
13/06/2019 | 10:56:16 | WK31 | Rural Short | Planned |  | 2 | 35 | 0.00052151 | 1.49e-05 | No
13/06/2019 | 11:35:17 | MTB11 | Rural Short | Unknown | Unknown | 6 | 97 | 0.004336 | 4.47e-05 | No
13/06/2019 | 11:44:42 | NL115F | Urban | Overloads |  | 1 | 153 | 0.0002446 | 1.6e-06 | No
13/06/2019 | 11:53:04 | SD32200 | Rural Long | Planned |  | 3 | 49 | 0.0010729 | 2.19e-05 | No
13/06/2019 | 12:19:35 | GU31 | Rural Long | Other |  | 1 | 165 | 0.0012042 | 7.3e-06 | No
13/06/2019 | 12:59:53 | SM349D | Urban | Planned |  | 2 | 21 | 6.714e-05 | 3.2e-06 | No
13/06/2019 | 13:37:23 | EL10 | Urban | Overloads |  | 19.6667 | 73 | 0.0022952 | 3.144e-05 | No
13/06/2019 | 15:00:30 | HH130F | Urban | Overloads |  | 1 | 122 | 0.00019504 | 1.6e-06 | No
13/06/2019 | 15:02:00 | HH496A | Urban | Asset failure | LV | 1 | 202 | 0.00032293 | 1.6e-06 | No
13/06/2019 | 16:17:14 | CV18 | Rural Short | Unknown | Unknown | 20 | 86 | 0.012814 | 0.000149 | No
13/06/2019 | 17:31:48 | SA711C | Urban | Unknown | Unknown | 54 | 77 | 0.0066473 | 8.633e-05 | No
13/06/2019 | 17:52:59 | NU33 | Rural Long | Asset failure | HV | 489 | 131.6667 | 0.4699 | 0.0035689 | No
13/06/2019 | 17:55:14 | HH341E | Urban | Asset failure | LV | 39 | 309 | 0.019266 | 6.235e-05 | No
13/06/2019 | 18:03:15 | SM126C | Urban | Planned |  | 794 | 40.9547 | 0.051986 | 0.0012694 | No
13/06/2019 | 18:13:38 | AP424E | Urban | Asset failure | LV | 34 | 164 | 0.0089142 | 5.435e-05 | No
13/06/2019 | 20:14:26 | HH341G | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 44 | 118 | 0.0083003 | 7.034e-05 | No
13/06/2019 | 21:29:35 | AP139C | Urban | Asset failure | LV | 1 | 117 | 0.00018704 | 1.6e-06 | No
13/06/2019 | 22:26:09 | VH11 | Urban | Planned |  | 1 | 406 | 0.00064906 | 1.6e-06 | No
13/06/2019 | 23:04:35 | EL17 | Urban | Unknown | Unknown | 1 | 31 | 4.956e-05 | 1.6e-06 | No
14/06/2019 | 05:00:14 | AP355C | Urban | Unknown | Unknown | 10.3333 | 255 | 0.0042125 | 1.652e-05 | No
14/06/2019 | 07:46:25 | ME200C | Urban | Other |  | 2 | 84 | 0.00026858 | 3.2e-06 | No
14/06/2019 | 08:04:53 | AP355B | Urban | Unknown | Unknown | 1 | 74 | 0.0001183 | 1.6e-06 | No
14/06/2019 | 08:22:11 | BM31 | Rural Short | Planned |  | 437 | 105.7849 | 0.34441 | 0.0032557 | No
14/06/2019 | 08:38:00 | PA24 | Rural Long | Planned |  | 26 | 218 | 0.041367 | 0.00018976 | No
14/06/2019 | 08:38:56 | HH130B | Urban | Planned |  | 215 | 314 | 0.10793 | 0.00034372 | No
14/06/2019 | 08:57:42 | KI13 | Rural Long | Planned |  | 1 | 27 | 0.00019706 | 7.3e-06 | No
14/06/2019 | 09:01:43 | AP227B | Urban | Planned |  | 192 | 274 | 0.084103 | 0.00030695 | No
14/06/2019 | 09:03:58 | SG13 | Rural Short | Planned |  | 1 | 278 | 0.0020711 | 7.45e-06 | No
14/06/2019 | 09:09:23 | GU13 | Rural Long | Planned |  | 17 | 211 | 0.026179 | 0.00012407 | No
14/06/2019 | 09:11:41 | ST51 | Rural Short | Unknown | Unknown | 19 | 33 | 0.0046712 | 0.00014155 | No
14/06/2019 | 09:18:02 | NL544B | Urban | Planned |  | 90 | 377 | 0.054243 | 0.00014388 | No
14/06/2019 | 09:24:27 | ME427E | Urban | Planned |  | 72 | 39 | 0.0044891 | 0.0001151 | No
14/06/2019 | 09:41:14 | SM216A | Urban | Planned |  | 143 | 261 | 0.059667 | 0.00022861 | No
14/06/2019 | 09:42:54 | CL13 | Rural Long | Planned |  | 2 | 187 | 0.0027296 | 1.46e-05 | No
14/06/2019 | 09:43:23 | ME427A | Urban | Planned |  | 1 | 44 | 7.034e-05 | 1.6e-06 | No
14/06/2019 | 10:09:17 | CD23 | Rural Long | Planned |  | 1 | 31 | 0.00022625 | 7.3e-06 | No
14/06/2019 | 10:09:34 | SM410C | Urban | Planned |  | 708 | 266 | 0.30108 | 0.0011319 | No
14/06/2019 | 10:14:28 | SM410C | Urban | Planned |  | 89 | 269 | 0.038274 | 0.00014228 | No
14/06/2019 | 10:20:38 | MTB61 | Rural Short | Planned |  | 10 | 85 | 0.0063326 | 7.45e-05 | No
14/06/2019 | 10:38:06 | HH121G | Urban | Planned |  | 93 | 29 | 0.0043116 | 0.00014868 | No
14/06/2019 | 10:55:01 | CD23 | Rural Long | Planned |  | 1 | 32 | 0.00023355 | 7.3e-06 | No
14/06/2019 | 11:49:19 | EL03 | Urban | Asset failure | LV | 100 | 64 | 0.010232 | 0.00015987 | No
14/06/2019 | 12:14:47 | HH102B | Urban | Planned |  | 62 | 123 | 0.012191 | 9.912e-05 | No
14/06/2019 | 12:39:17 | MI16 | Rural Long | Asset failure | LV | 1 | 73 | 0.00053278 | 7.3e-06 | No
14/06/2019 | 12:48:59 | CV25 | Rural Long | Unknown | Unknown | 4 | 69 | 0.0020143 | 2.919e-05 | No
14/06/2019 | 13:13:00 | SM126A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 471 | 171.2611 | 0.12896 | 0.00075298 | No
14/06/2019 | 13:24:03 | SM126A | Urban | Vegetation | Grow-in - NSP responsibility | 60 | 230 | 0.022062 | 9.592e-05 | No
14/06/2019 | 15:15:30 | AP355C | Urban | Unknown | Unknown | 10.3333 | 113 | 0.0018667 | 1.652e-05 | No
14/06/2019 | 16:41:50 | CM05 | Rural Long | Asset failure | LV | 49 | 292 | 0.10442 | 0.00035762 | No
14/06/2019 | 17:05:20 | SM179A | Urban | Asset failure | LV | 47 | 45 | 0.0033812 | 7.514e-05 | No
14/06/2019 | 17:22:01 | GU43 | Rural Long | Unknown | Unknown | 1 | 1067 | 0.0077873 | 7.3e-06 | No
14/06/2019 | 17:58:00 | AP424E | Urban | Asset failure | LV | 1 | 245 | 0.00039168 | 1.6e-06 | No
14/06/2019 | 18:08:51 | ME131B | Urban | Asset failure | LV | 48.3333 | 52 | 0.004018 | 7.727e-05 | No
14/06/2019 | 19:01:14 | HH496G | Urban | Asset failure | LV | 15.6667 | 267 | 0.0066873 | 2.505e-05 | No
14/06/2019 | 23:26:34 | HH522B | Urban | Asset failure | LV | 1 | 109 | 0.00017426 | 1.6e-06 | No
15/06/2019 | 05:01:12 | AP139C | Urban | Asset failure | LV | 2 | 326 | 0.0010423 | 3.2e-06 | No
15/06/2019 | 06:11:21 | SM172C | Urban | Asset failure | LV | 1 | 345 | 0.00055154 | 1.6e-06 | No
15/06/2019 | 07:11:10 | EL10 | Urban | Unknown | Unknown | 48.6667 | 86 | 0.006691 | 7.78e-05 | No
15/06/2019 | 07:55:39 | SM374A | Urban | Overloads |  | 3.3333 | 187 | 0.00099651 | 5.33e-06 | No
15/06/2019 | 08:07:52 | AP424E | Urban | Asset failure | LV | 1 | 165 | 0.00026378 | 1.6e-06 | No
15/06/2019 | 09:13:56 | MV62 | Rural Short | Unknown | Unknown | 14 | 114 | 0.01189 | 0.0001043 | No
15/06/2019 | 12:35:11 | SM349H | Urban | Asset failure | LV | 64 | 92 | 0.009413 | 0.00010232 | No
15/06/2019 | 12:42:00 | ME200A | Urban | Overloads |  | 1 | 215 | 0.00034372 | 1.6e-06 | No
15/06/2019 | 15:11:01 | EL20 | Urban | Unknown | Unknown | 39 | 65 | 0.0040526 | 6.235e-05 | No
15/06/2019 | 15:11:01 | EL20 | Urban | Planned |  | 739 | 1 | 0.0011814 | 0.0011814 | No
15/06/2019 | 15:22:25 | SM374B | Urban | Asset failure | LV | 88 | 109 | 0.015334 | 0.00014068 | No
15/06/2019 | 17:17:36 | ME131E | Urban | Asset failure | LV | 2 | 154 | 0.00049239 | 3.2e-06 | No
15/06/2019 | 22:09:52 | SM411A | Urban | Animal | Animal impact | 1 | 163 | 0.00026058 | 1.6e-06 | No
16/06/2019 | 05:43:24 | VH11 | Urban | Planned |  | 239 | 175 | 0.066865 | 0.00038208 | No
16/06/2019 | 07:53:05 | CBD412H | Urban | Planned |  | 7 | 374 | 0.0041853 | 1.119e-05 | No
16/06/2019 | 08:07:33 | SD34405 | Rural Long | Planned |  | 248 | 383.9113 | 0.69487 | 0.00181 | No
16/06/2019 | 08:21:36 | ST11 | Rural Short | Planned |  | 455 | 363.6615 | 1.2327 | 0.0033898 | No
16/06/2019 | 08:26:08 | PL04 | Urban | Planned |  | 8 | 384 | 0.0049111 | 1.279e-05 | No
16/06/2019 | 08:34:56 | SA14 | Urban | Planned |  | 15 | 246 | 0.0058991 | 2.398e-05 | No
16/06/2019 | 08:38:41 | NL115C | Urban | Asset failure | HV | 597 | 150.0503 | 0.14321 | 0.00095441 | No
16/06/2019 | 09:00:53 | SA520J | Urban | Planned |  | 5 | 102.2 | 0.00081692 | 7.99e-06 | No
16/06/2019 | 09:13:27 | NL544B | Urban | Planned |  | 66 | 484 | 0.051068 | 0.00010551 | No
16/06/2019 | 09:51:57 | AP425C | Urban | Third Party | Other | 28 | 68 | 0.0030439 | 4.476e-05 | No
16/06/2019 | 10:20:27 | AP425C | Urban | Animal | Animal impact | 1 | 56 | 8.953e-05 | 1.6e-06 | No
16/06/2019 | 11:58:26 | SM179A | Urban | Asset failure | LV | 3.3333 | 218 | 0.0011617 | 5.33e-06 | No
16/06/2019 | 12:46:25 | M21 | Rural Long | Unknown | Unknown | 2 | 11 | 0.00016056 | 1.46e-05 | No
16/06/2019 | 13:04:39 | SM126D | Urban | Asset failure | HV | 225 | 200.2133 | 0.072017 | 0.0003597 | No
16/06/2019 | 14:35:15 | AP355C | Urban | Unknown | Unknown | 10.3333 | 179 | 0.002957 | 1.652e-05 | No
16/06/2019 | 16:32:42 | HH121D | Urban | Asset failure | LV | 1 | 105 | 0.00016786 | 1.6e-06 | No
16/06/2019 | 18:03:25 | NU02 | Rural Long | Asset failure | HV | 195 | 336.4 | 0.47876 | 0.0014232 | No
16/06/2019 | 18:16:39 | AP529C | Urban | Asset failure | LV | 10.3333 | 67 | 0.0011068 | 1.652e-05 | No
16/06/2019 | 18:48:45 | AP529D | Urban | Asset failure | LV | 10.6667 | 152 | 0.002592 | 1.705e-05 | No
16/06/2019 | 19:46:11 | GA01 | Urban | Asset failure | LV | 1 | 150 | 0.0002398 | 1.6e-06 | No
16/06/2019 | 20:58:06 | HH341H | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 107 | 0.00017106 | 1.6e-06 | No
16/06/2019 | 21:09:57 | ME347C | Urban | Asset failure | LV | 44.6667 | 151 | 0.010783 | 7.141e-05 | No
17/06/2019 | 00:30:20 | HH145B | Urban | Asset failure | LV | 1 | 86 | 0.00013749 | 1.6e-06 | No
17/06/2019 | 03:48:27 | KI21 | Rural Long | Unknown | Unknown | 15 | 197 | 0.021567 | 0.00010948 | No
17/06/2019 | 05:05:20 | CL04 | Rural Long | Asset failure | HV | 178 | 232.691 | 0.30229 | 0.0012991 | No
17/06/2019 | 05:32:17 | AP355C | Urban | Asset failure | LV | 10.3333 | 207 | 0.0034196 | 1.652e-05 | No
17/06/2019 | 06:50:16 | KI21 | Rural Long | Unknown | Unknown | 1 | 45 | 0.00032843 | 7.3e-06 | No
17/06/2019 | 08:29:15 | VH11 | Urban | Planned |  | 158 | 427 | 0.10786 | 0.00025259 | No
17/06/2019 | 08:34:41 | EL06H10 | Urban | Planned |  | 1 | 550 | 0.00087927 | 1.6e-06 | No
17/06/2019 | 09:04:05 | AP227B | Urban | Planned |  | 99 | 332 | 0.052545 | 0.00015827 | No
17/06/2019 | 09:18:55 | SG12 | Rural Short | Planned |  | 8 | 307 | 0.018298 | 5.96e-05 | No
17/06/2019 | 09:20:58 | YK15 | Rural Long | Planned |  | 75 | 1 | 0.00054738 | 0.00054738 | No
17/06/2019 | 09:26:18 | AP214D | Urban | Planned |  | 1 | 110 | 0.00017585 | 1.6e-06 | No
17/06/2019 | 09:34:20 | AP214B | Urban | Planned |  | 1 | 79 | 0.0001263 | 1.6e-06 | No
17/06/2019 | 09:37:40 | VH22 | Rural Short | Planned |  | 72 | 316 | 0.16951 | 0.00053641 | No
17/06/2019 | 09:46:47 | VH14 | Rural Short | Planned |  | 1 | 299 | 0.0022276 | 7.45e-06 | No
17/06/2019 | 09:53:30 | AP372A | Urban | Planned |  | 141 | 212 | 0.047788 | 0.00022541 | No
17/06/2019 | 10:02:58 | NL115C | Urban | Asset failure | LV | 1 | 124 | 0.00019824 | 1.6e-06 | No
17/06/2019 | 10:06:16 | SD32400 | Rural Long | Planned |  | 4 | 361 | 0.010539 | 2.919e-05 | No
17/06/2019 | 10:31:09 | VH21 | Rural Short | Asset failure | LV | 20.3333 | 65 | 0.0098466 | 0.00015149 | No
17/06/2019 | 10:51:34 | CV29 | Rural Long | Planned |  | 8 | 126 | 0.0073567 | 5.839e-05 | No
17/06/2019 | 10:58:34 | YK19 | Rural Long | Planned |  | 55 | 1 | 0.00040141 | 0.00040141 | No
17/06/2019 | 11:03:39 | HH409F | Urban | Asset failure | LV | 1 | 395 | 0.00063148 | 1.6e-06 | No
17/06/2019 | 11:04:13 | BM31 | Rural Short | Unknown | Unknown | 1 | 343 | 0.0025554 | 7.45e-06 | No
17/06/2019 | 11:15:37 | CBD103G | Urban | Asset failure | LV | 4 | 67 | 0.00042844 | 6.39e-06 | No
17/06/2019 | 11:28:14 | EL01R | Urban | Asset failure | LV | 1 | 72 | 0.0001151 | 1.6e-06 | No
17/06/2019 | 11:50:18 | GU43 | Rural Long | Planned |  | 1 | 4 | 2.919e-05 | 7.3e-06 | No
17/06/2019 | 11:51:55 | PP01 | Urban | Asset failure | LV | 1 | 467 | 0.00074658 | 1.6e-06 | No
17/06/2019 | 12:05:52 | BT04 | Rural Long | Planned |  | 2 | 92 | 0.0013429 | 1.46e-05 | No
17/06/2019 | 12:17:02 | LX76 | Rural Long | Unknown | Unknown | 2 | 62 | 0.00090499 | 1.46e-05 | No
17/06/2019 | 12:22:56 | AP214B | Urban | Planned |  | 1 | 58 | 9.272e-05 | 1.6e-06 | No
17/06/2019 | 12:44:23 | MB62 | Rural Long | Asset failure | HV | 7 | 76 | 0.0038827 | 5.109e-05 | No
17/06/2019 | 13:21:22 | HH341H | Urban | Asset failure | LV | 1 | 345 | 0.00055154 | 1.6e-06 | No
17/06/2019 | 14:47:38 | HH386G | Urban | Asset failure | LV | 1 | 307 | 0.00049079 | 1.6e-06 | No
17/06/2019 | 15:20:26 | MI20 | Rural Long | Asset failure | LV | 1 | 184 | 0.0013429 | 7.3e-06 | No
17/06/2019 | 16:53:32 | MV62 | Rural Short | Asset failure | LV | 11.6667 | 168 | 0.014602 | 8.692e-05 | No
17/06/2019 | 17:15:49 | MI05 | Rural Long | Planned |  | 1 | 23 | 0.00016786 | 7.3e-06 | No
17/06/2019 | 19:10:20 | SM410C | Urban | Asset failure | LV | 1 | 154 | 0.0002462 | 1.6e-06 | No
17/06/2019 | 19:40:07 | R21 | Rural Long | Overloads |  | 1 | 242 | 0.0017662 | 7.3e-06 | No
17/06/2019 | 20:06:30 | NL111Q | Urban | Overloads |  | 1 | 131 | 0.00020943 | 1.6e-06 | No
17/06/2019 | 23:48:41 | HH496D | Urban | Third Party | Vehicle impact | 1 | 348 | 0.00055634 | 1.6e-06 | No
18/06/2019 | 02:25:23 | SM410D | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 1910 | 68 | 0.20764 | 0.0030535 | No
18/06/2019 | 03:12:55 | HH177E | Urban | Planned |  | 1 | 234 | 0.00037409 | 1.6e-06 | No
18/06/2019 | 05:55:29 | SM349F / NL111A / NL451A | Urban | Planned |  | 698 | 209.3152 | 0.23357 | 0.0011159 | No
18/06/2019 | 08:21:34 | GA05 | Rural Short | Planned |  | 62 | 384 | 0.17737 | 0.00046191 | No
18/06/2019 | 08:33:50 | VH11 / VH12 | Urban | Planned |  | 181 | 260 | 0.075234 | 0.00028936 | No
18/06/2019 | 08:33:50 | VH11 / VH12 | Rural Short | Planned |  | 92 | 260 | 0.17821 | 0.00068541 | No
18/06/2019 | 08:51:58 | SD35500 | Rural Long | Planned |  | 482 | 400.9295 | 1.4104 | 0.0035178 | No
18/06/2019 | 08:54:51 | VH12 | Rural Short | Planned |  | 1 | 23 | 0.00017135 | 7.45e-06 | No
18/06/2019 | 08:55:48 | MG10 | Rural Long | Planned |  | 2 | 139 | 0.0020289 | 1.46e-05 | No
18/06/2019 | 09:12:20 | CV33 | Rural Long | Planned |  | 40 | 114 | 0.03328 | 0.00029193 | No
18/06/2019 | 09:22:38 | MB91 | Rural Long | Planned |  | 1 | 261 | 0.0019049 | 7.3e-06 | No
18/06/2019 | 09:38:22 | AP424E | Urban | Planned |  | 61 | 243 | 0.023697 | 9.752e-05 | No
18/06/2019 | 09:53:29 | W29 | Rural Long | Planned |  | 10 | 129 | 0.0094149 | 7.298e-05 | No
18/06/2019 | 10:35:45 | MG05 | Rural Long | Other |  | 1 | 77 | 0.00056197 | 7.3e-06 | No
18/06/2019 | 10:39:59 | SM126B | Urban | Other |  | 1 | 238 | 0.00038048 | 1.6e-06 | No
18/06/2019 | 10:40:47 | GA50 | Urban | Asset failure | LV | 16.3333 | 339 | 0.0088519 | 2.611e-05 | No
18/06/2019 | 10:49:31 | AP226C | Urban | Animal | Animal impact | 1 | 140 | 0.00022381 | 1.6e-06 | No
18/06/2019 | 12:14:07 | AP425D | Urban | Asset failure | LV | 1 | 144 | 0.00023021 | 1.6e-06 | No
18/06/2019 | 12:29:34 | BT06 | Rural Long | Planned |  | 2 | 104 | 0.001518 | 1.46e-05 | No
18/06/2019 | 13:00:50 | BM56 | Rural Short | Unknown | Unknown | 15 | 133 | 0.014863 | 0.00011175 | No
18/06/2019 | 13:30:02 | MTB21 | Rural Short | Unknown | Unknown | 4 | 190 | 0.0056621 | 2.98e-05 | No
18/06/2019 | 16:27:56 | PL07 | Urban | Unknown | Unknown | 1 | 68 | 0.00010871 | 1.6e-06 | No
18/06/2019 | 17:47:05 | SA744D | Urban | Asset failure | LV | 44 | 92 | 0.0064714 | 7.034e-05 | No
18/06/2019 | 18:39:03 | HH121C | Urban | Asset failure | LV | 21 | 62 | 0.0020815 | 3.357e-05 | No
18/06/2019 | 19:01:07 | NL115E | Urban | Asset failure | LV | 1 | 97 | 0.00015507 | 1.6e-06 | No
18/06/2019 | 19:44:37 | GA800A | Rural Short | Asset failure | HV | 281 | 103.605 | 0.2169 | 0.0020935 | No
18/06/2019 | 19:46:31 | HH429B | Urban | Asset failure | LV | 18.6667 | 68 | 0.0020292 | 2.984e-05 | No
18/06/2019 | 19:50:19 | SM137B | Urban | Asset failure | LV | 62 | 68 | 0.00674 | 9.912e-05 | No
18/06/2019 | 21:13:25 | SM216C | Urban | Asset failure | LV | 4.3333 | 70 | 0.00048493 | 6.93e-06 | No
18/06/2019 | 23:09:36 | SA18 | Urban | Unknown | Unknown | 24 | 83 | 0.0031846 | 3.837e-05 | No
19/06/2019 | 05:21:51 | WHY07 | Urban | Asset failure | HV | 154 | 423.039 | 0.10415 | 0.0002462 | No
19/06/2019 | 08:15:43 | HH522C | Urban | Other |  | 27.3333 | 383 | 0.016736 | 4.37e-05 | No
19/06/2019 | 08:16:54 | HH522B | Urban | Planned |  | 1 | 391 | 0.00062508 | 1.6e-06 | No
19/06/2019 | 08:34:07 | LM53 | Rural Long | Planned |  | 7 | 377 | 0.01926 | 5.109e-05 | No
19/06/2019 | 08:41:32 | AP424E | Urban | Planned |  | 261 | 1210.9349 | 0.50527 | 0.00041725 | No
19/06/2019 | 08:41:32 | AP424E | Urban | Planned |  | 0 | 66 | 0.017304 | 0 | No
19/06/2019 | 08:42:21 | SM350A | Urban | Vegetation | Grow-in - NSP responsibility | 15 | 56 | 0.0013429 | 2.398e-05 | No
19/06/2019 | 08:58:56 | YK29 | Rural Long | Planned |  | 131 | 204 | 0.19504 | 0.00095608 | No
19/06/2019 | 08:59:42 | BM12 | Rural Short | Planned |  | 9 | 182 | 0.012203 | 6.705e-05 | No
19/06/2019 | 09:15:37 | EL02 | Urban | Planned |  | 1 | 276 | 0.00044123 | 1.6e-06 | No
19/06/2019 | 09:24:56 | GA43 | Rural Short | Planned |  | 9 | 267 | 0.017903 | 6.705e-05 | No
19/06/2019 | 09:26:05 | W20 | Rural Long | Planned |  | 14 | 313 | 0.031981 | 0.00010218 | No
19/06/2019 | 09:46:04 | MV42 | Rural Short | Asset failure | LV | 1 | 161 | 0.0011995 | 7.45e-06 | No
19/06/2019 | 09:56:02 | SSD235 | Rural Short | Planned |  | 1825 | 1 | 0.013597 | 0.013597 | No
19/06/2019 | 09:56:02 | SSD235 | Rural Long | Planned |  | 492 | 1 | 0.0035908 | 0.0035908 | No
19/06/2019 | 10:05:05 | SG10 | Rural Short | Planned |  | 210 | 218 | 0.34107 | 0.0015645 | No
19/06/2019 | 10:10:38 | SM349A | Urban | Planned |  | 2 | 125 | 0.00039967 | 3.2e-06 | No
19/06/2019 | 10:11:15 | SM216G | Urban | Planned |  | 1 | 101 | 0.00016147 | 1.6e-06 | No
19/06/2019 | 10:11:44 | NL544B | Urban | Planned |  | 66 | 235 | 0.024795 | 0.00010551 | No
19/06/2019 | 10:18:36 | AP529E | Urban | Planned |  | 658 | 311 | 0.32715 | 0.0010519 | No
19/06/2019 | 10:35:54 | SM349A | Urban | Planned |  | 2 | 103 | 0.00032933 | 3.2e-06 | No
19/06/2019 | 10:38:44 | SM216G | Urban | Planned |  | 232 | 144 | 0.053409 | 0.00037089 | No
19/06/2019 | 11:01:00 | G21 | Rural Long | Planned |  | 2 | 299 | 0.0043644 | 1.46e-05 | No
19/06/2019 | 11:04:16 | MV62 | Rural Short | Planned |  | 5 | 81 | 0.0030173 | 3.725e-05 | No
19/06/2019 | 11:05:31 | SM216G | Urban | Planned |  | 1 | 52 | 8.313e-05 | 1.6e-06 | No
19/06/2019 | 11:15:47 | ST22 | Rural Short | Unknown | Unknown | 7 | 63 | 0.0032855 | 5.215e-05 | No
19/06/2019 | 11:16:44 | ST22 | Rural Short | Unknown | Unknown | 3 | 153 | 0.0034196 | 2.235e-05 | No
19/06/2019 | 11:26:16 | ME231B | Urban | Planned |  | 1 | 84 | 0.00013429 | 1.6e-06 | No
19/06/2019 | 11:38:04 | SA36 | Urban | Planned |  | 1 | 20 | 3.197e-05 | 1.6e-06 | No
19/06/2019 | 12:21:47 | SM349A | Urban | Planned |  | 2 | 427 | 0.0013653 | 3.2e-06 | No
19/06/2019 | 12:30:38 | YK28 | Rural Long | Planned |  | 10 | 50 | 0.0036492 | 7.298e-05 | No
19/06/2019 | 12:35:15 | ST12 | Rural Short | Unknown | Unknown | 2 | 35 | 0.00052151 | 1.49e-05 | No
19/06/2019 | 12:41:49 | SD38100 | Rural Long | Planned |  | 21 | 36 | 0.0055175 | 0.00015327 | No
19/06/2019 | 12:46:00 | ST22 | Rural Short | Weather |  | 1 | 92 | 0.00068541 | 7.45e-06 | No
19/06/2019 | 13:17:30 | EL23 | Urban | Unknown | Unknown | 667 | 31 | 0.033056 | 0.0010663 | No
19/06/2019 | 13:29:09 | HH148C | Urban | Asset failure | LV | 1 | 173 | 0.00027657 | 1.6e-06 | No
19/06/2019 | 15:09:04 | MB31 | Rural Long | Unknown | Unknown | 2 | 244 | 0.0035616 | 1.46e-05 | No
19/06/2019 | 16:38:42 | VH32 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 136 | 83 | 0.084097 | 0.0010132 | No
19/06/2019 | 18:22:31 | HH522C | Urban | Asset failure | LV | 1 | 485 | 0.00077536 | 1.6e-06 | No
19/06/2019 | 18:58:01 | SM374A | Urban | Asset failure | LV | 20 | 93 | 0.0029735 | 3.197e-05 | No
19/06/2019 | 19:07:28 | VH14 | Rural Short | Unknown | Unknown | 5 | 290 | 0.010803 | 3.725e-05 | No
19/06/2019 | 20:11:54 | EL01M | Urban | Asset failure | LV | 1 | 345 | 0.00055154 | 1.6e-06 | No
19/06/2019 | 20:48:34 | EL10 | Urban | Asset failure | LV | 1 | 384 | 0.00061389 | 1.6e-06 | No
19/06/2019 | 22:58:55 | SM216B | Urban | Planned |  | 163 | 349 | 0.090944 | 0.00026058 | No
19/06/2019 | 23:21:08 | YK23 | Rural Long | Asset failure | HV | 165 | 187.4242 | 0.2257 | 0.0012042 | No
20/06/2019 | 05:55:44 | GA02 | Rural Short | Unknown | Unknown | 2 | 170 | 0.002533 | 1.49e-05 | No
20/06/2019 | 07:06:18 | SA14 | Urban | Asset failure | LV | 1 | 153 | 0.0002446 | 1.6e-06 | No
20/06/2019 | 08:30:17 | MG05 | Rural Long | Planned |  | 6 | 108 | 0.0047293 | 4.379e-05 | No
20/06/2019 | 08:31:14 | SD35500 | Rural Long | Planned |  | 436 | 367.945 | 1.1708 | 0.0031821 | No
20/06/2019 | 08:52:47 | MB28 | Rural Short | Planned |  | 40 | 253.35 | 0.0755 | 0.00029801 | No
20/06/2019 | 08:53:28 | LX51 | Rural Short | Planned |  | 4 | 294 | 0.0087614 | 2.98e-05 | No
20/06/2019 | 08:55:45 | PL33 | Rural Long | Planned |  | 1092 | 400.4835 | 3.1918 | 0.0079698 | No
20/06/2019 | 08:59:59 | SD38200 | Rural Long | Planned |  | 32 | 217 | 0.05068 | 0.00023355 | No
20/06/2019 | 09:02:49 | SM349A | Urban | Asset failure | LV | 96 | 52 | 0.0079806 | 0.00015347 | No
20/06/2019 | 09:12:14 | NA06 | Rural Long | Asset failure | LV | 19 | 249 | 0.034528 | 0.00013867 | No
20/06/2019 | 09:12:35 | VH17 | Rural Short | Asset failure | LV | 4 | 209 | 0.0062283 | 2.98e-05 | No
20/06/2019 | 09:14:19 | MI08 | Rural Long | Planned |  | 123 | 281 | 0.25225 | 0.0008977 | No
20/06/2019 | 09:27:25 | AP529E | Urban | Planned |  | 199 | 102 | 0.03245 | 0.00031814 | No
20/06/2019 | 09:34:30 | SM216E | Urban | Planned |  | 25 | 298 | 0.01191 | 3.997e-05 | No
20/06/2019 | 09:37:51 | CM03 | Rural Long | Planned |  | 51 | 124.4118 | 0.046308 | 0.00037222 | No
20/06/2019 | 09:38:35 | MTB32 | Rural Long | Planned |  | 144 | 291 | 0.30583 | 0.001051 | No
20/06/2019 | 09:45:03 | NL111Q | Urban | Overloads |  | 1 | 164 | 0.00026218 | 1.6e-06 | No
20/06/2019 | 09:50:59 | MV33 | Rural Short | Planned |  | 2 | 61 | 0.00090892 | 1.49e-05 | No
20/06/2019 | 10:30:48 | HH522C | Urban | Asset failure | LV | 1 | 292 | 0.00046681 | 1.6e-06 | No
20/06/2019 | 10:32:06 | MTB32 | Rural Long | Planned |  | 32 | 41 | 0.0095754 | 0.00023355 | No
20/06/2019 | 10:36:29 | HH130F | Urban | Planned |  | 154 | 127.4156 | 0.031369 | 0.0002462 | No
20/06/2019 | 10:54:39 | CV753A | Rural Long | Planned |  | 125 | 203 | 0.1852 | 0.00091229 | No
20/06/2019 | 11:13:27 | MB28 | Rural Short | Unknown | Unknown | 57 | 67 | 0.028452 | 0.00042466 | No
20/06/2019 | 12:08:08 | KI45 | Rural Long | Planned |  | 2 | 26 | 0.00037951 | 1.46e-05 | No
20/06/2019 | 13:34:56 | SM410B | Urban | Asset failure | LV | 35 | 111 | 0.0062109 | 5.595e-05 | No
20/06/2019 | 14:28:36 | AP214A | Urban | Asset failure | LV | 27.3333 | 143 | 0.0062487 | 4.37e-05 | No
20/06/2019 | 15:00:35 | MTB33 | Rural Short | Asset failure | LV | 1 | 224 | 0.0016688 | 7.45e-06 | No
20/06/2019 | 16:35:46 | MG10 | Rural Long | Asset failure | HV | 4 | 13 | 0.00037951 | 2.919e-05 | No
20/06/2019 | 16:50:14 | AP424B | Urban | Asset failure | LV | 2 | 119 | 0.00038048 | 3.2e-06 | No
20/06/2019 | 16:59:15 | NU01 | Rural Short | Unknown | Unknown | 8 | 65 | 0.0038741 | 5.96e-05 | No
20/06/2019 | 17:42:30 | KA05 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 15.3333 | 43 | 0.004812 | 0.00011191 | No
20/06/2019 | 17:55:48 | KA05 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 23 | 28 | 0.0047001 | 0.00016786 | No
20/06/2019 | 17:56:17 | HH145D | Urban | Asset failure | LV | 1 | 288 | 0.00046042 | 1.6e-06 | No
20/06/2019 | 18:51:55 | HH121G | Urban | Asset failure | LV | 1 | 415 | 0.00066345 | 1.6e-06 | No
20/06/2019 | 20:15:28 | GA50 | Urban | Asset failure | LV | 1 | 204 | 0.00032613 | 1.6e-06 | No
20/06/2019 | 20:43:40 | HH341D | Urban | Overloads |  | 1 | 412 | 0.00065865 | 1.6e-06 | No
20/06/2019 | 23:21:25 | NA01 | Rural Long | Unknown | Unknown | 1 | 191 | 0.001394 | 7.3e-06 | No
21/06/2019 | 07:37:30 | AP344B | Urban | Animal | Animal impact | 34.6667 | 370 | 0.020506 | 5.542e-05 | No
21/06/2019 | 08:19:33 | AP226E | Urban | Planned |  | 2 | 450 | 0.0014388 | 3.2e-06 | No
21/06/2019 | 08:44:50 | BM31 | Rural Short | Planned |  | 437 | 24.222 | 0.07886 | 0.0032557 | No
21/06/2019 | 09:01:17 | HH145E | Urban | Planned |  | 88 | 139.5455 | 0.019632 | 0.00014068 | No
21/06/2019 | 09:04:55 | MI26 | Rural Long | Planned |  | 72 | 50.7778 | 0.026683 | 0.00052548 | No
21/06/2019 | 09:06:12 | AP227B | Urban | Planned |  | 123 | 280 | 0.055058 | 0.00019664 | No
21/06/2019 | 09:33:24 | KA10 | Rural Long | Planned |  | 1 | 101 | 0.00073713 | 7.3e-06 | No
21/06/2019 | 09:41:41 | NL511A | Urban | Planned |  | 72 | 247 | 0.028431 | 0.0001151 | No
21/06/2019 | 10:15:50 | KA10 | Rural Long | Planned |  | 1 | 169 | 0.0012334 | 7.3e-06 | No
21/06/2019 | 10:18:44 | MG43 | Rural Short | Planned |  | 1 | 77 | 0.00057366 | 7.45e-06 | No
21/06/2019 | 10:24:10 | CM01 | Rural Long | Animal | Animal impact | 527 | 88 | 0.33847 | 0.0038462 | No
21/06/2019 | 10:28:19 | MV63 | Rural Short | Unknown | Unknown | 22.6667 | 49 | 0.0082746 | 0.00016887 | No
21/06/2019 | 10:55:35 | YK24 | Rural Long | Planned |  | 2 | 15 | 0.00021895 | 1.46e-05 | No
21/06/2019 | 11:38:33 | KA10 | Rural Long | Planned |  | 1 | 73 | 0.00053278 | 7.3e-06 | No
21/06/2019 | 12:39:11 | LM33 | Rural Long | Unknown | Unknown | 2 | 37 | 0.00054008 | 1.46e-05 | No
21/06/2019 | 12:39:41 | BT18 | Rural Long | Planned |  | 42 | 128 | 0.039236 | 0.00030653 | No
21/06/2019 | 13:50:39 | SG13 | Rural Short | Asset failure | LV | 1 | 267 | 0.0019892 | 7.45e-06 | No
21/06/2019 | 16:02:20 | NA20 | Rural Long | Asset failure | LV | 2 | 147 | 0.0021457 | 1.46e-05 | No
21/06/2019 | 16:27:51 | MG03 | Rural Short | Asset failure | HV | 24 | 101 | 0.018059 | 0.0001788 | No
21/06/2019 | 16:34:00 | SD40800 | Rural Long | Network business | Switching and protection error | 1414 | 139.9547 | 1.4443 | 0.01032 | No
21/06/2019 | 18:45:56 | NL111Q | Urban | Overloads |  | 1 | 251 | 0.00040127 | 1.6e-06 | No
21/06/2019 | 19:14:41 | ST21 | Rural Short | Animal | Animal impact | 10 | 179 | 0.013336 | 7.45e-05 | No
21/06/2019 | 21:18:44 | PP16 | Rural Short | Asset failure | HV | 74 | 837.0135 | 0.46145 | 0.00055131 | No
21/06/2019 | 21:49:55 | CD01 | Rural Short | Asset failure | LV | 13.3333 | 109 | 0.010828 | 9.934e-05 | No
21/06/2019 | 22:56:40 | MI01 | Rural Long | Other |  | 1 | 183 | 0.0013356 | 7.3e-06 | No
22/06/2019 | 07:26:54 | G14 | Rural Long | Unknown | Unknown | 13 | 428 | 0.040608 | 9.488e-05 | No
22/06/2019 | 07:27:22 | HH148B | Urban | Planned |  | 1 | 317 | 0.00050678 | 1.6e-06 | No
22/06/2019 | 09:47:10 | MV53 | Rural Short | Asset failure | LV | 2 | 317 | 0.0047234 | 1.49e-05 | No
22/06/2019 | 09:57:25 | HH177F | Urban | Asset failure | LV | 1 | 248 | 0.00039647 | 1.6e-06 | No
22/06/2019 | 10:35:26 | BM11 | Rural Short | Asset failure | LV | 4 | 521 | 0.015526 | 2.98e-05 | No
22/06/2019 | 10:36:56 | AP214A | Urban | Overloads |  | 1 | 140 | 0.00022381 | 1.6e-06 | No
22/06/2019 | 10:50:38 | AP149B | Urban | Overloads |  | 1 | 88 | 0.00014068 | 1.6e-06 | No
22/06/2019 | 12:13:35 | BM11 | Rural Short | Asset failure | LV | 1 | 113 | 0.00084187 | 7.45e-06 | No
22/06/2019 | 12:34:16 | SM126E | Urban | Asset failure | LV | 15.6667 | 147 | 0.0036818 | 2.505e-05 | No
22/06/2019 | 12:47:54 | MB13 | Rural Short | Asset failure | LV | 1 | 174 | 0.0012963 | 7.45e-06 | No
22/06/2019 | 12:55:44 | HH145A | Urban | Asset failure | LV | 1 | 218 | 0.00034851 | 1.6e-06 | No
22/06/2019 | 20:12:17 | NL760B | Urban | Asset failure | LV | 3.6667 | 102 | 0.0005979 | 5.86e-06 | No
22/06/2019 | 20:35:46 | KA04 | Rural Long | Unknown | Unknown | 28 | 78 | 0.01594 | 0.00020435 | No
22/06/2019 | 21:11:27 | SG14 | Rural Short | Planned |  | 30 | 112 | 0.025032 | 0.0002235 | No
22/06/2019 | 23:12:04 | VH45 | Rural Short | Unknown | Unknown | 27.6667 | 157 | 0.032361 | 0.00020612 | No
22/06/2019 | 23:44:56 | VH45 | Rural Short | Overloads |  | 2 | 132 | 0.0019668 | 1.49e-05 | No
23/06/2019 | 00:54:01 | LX43 | Rural Short | Planned |  | 197 | 231 | 0.33903 | 0.0014677 | No
23/06/2019 | 05:42:06 | EL10 | Urban | Overloads |  | 1 | 346 | 0.00055314 | 1.6e-06 | No
23/06/2019 | 06:06:46 | VH22 | Rural Short | Planned |  | 1396 | 224.0888 | 2.3306 | 0.0104 | No
23/06/2019 | 06:11:27 | SM349A | Urban | Asset failure | LV | 25.3333 | 156 | 0.006318 | 4.05e-05 | No
23/06/2019 | 06:59:57 | SA17 | Urban | Overloads |  | 1 | 207 | 0.00033093 | 1.6e-06 | No
23/06/2019 | 07:30:08 | MB03 | Rural Long | Unknown | Unknown | 32 | 185 | 0.043206 | 0.00023355 | No
23/06/2019 | 07:57:28 | HH432B | Urban | Unknown | Unknown | 27.3333 | 138 | 0.0060302 | 4.37e-05 | No
23/06/2019 | 08:13:26 | KA04 | Rural Long | Asset failure | LV | 6.6667 | 234 | 0.011385 | 4.866e-05 | No
23/06/2019 | 08:24:24 | SD35100 | Rural Long | Planned |  | 1 | 253 | 0.0018465 | 7.3e-06 | No
23/06/2019 | 09:13:57 | AP149C | Urban | Asset failure | LV | 1 | 338 | 0.00054035 | 1.6e-06 | No
23/06/2019 | 09:27:31 | MG52 | Rural Short | Asset failure | Distribution substation | 2 | 273 | 0.0040678 | 1.49e-05 | No
23/06/2019 | 11:02:39 | SM179D | Urban | Asset failure | LV | 81 | 113 | 0.014633 | 0.00012949 | No
23/06/2019 | 12:03:04 | VH22 | Rural Short | Planned |  | 345 | 234 | 0.60145 | 0.0025703 | No
23/06/2019 | 16:14:13 | NL511A | Urban | Asset failure | LV | 25.3333 | 107 | 0.0043335 | 4.05e-05 | No
23/06/2019 | 18:01:33 | SSD405 | Rural Long | Planned |  | 5268 | 27 | 1.0381 | 0.038448 | No
23/06/2019 | 18:17:04 | SM410A | Urban | Asset failure | LV | 26.6667 | 173 | 0.0073752 | 4.263e-05 | No
23/06/2019 | 18:35:51 | AP344D | Urban | Asset failure | LV | 15 | 388 | 0.0093043 | 2.398e-05 | No
23/06/2019 | 18:40:44 | HH341H | Urban | Unknown | Unknown | 42 | 62 | 0.004163 | 6.714e-05 | No
23/06/2019 | 18:42:10 | MB03 | Rural Long | Unknown | Unknown | 32 | 183 | 0.042739 | 0.00023355 | No
23/06/2019 | 18:48:39 | SM137B | Urban | Asset failure | LV | 27 | 130 | 0.0056114 | 4.316e-05 | No
23/06/2019 | 19:28:32 | AP149E | Urban | Asset failure | LV | 29.3333 | 165 | 0.0077376 | 4.689e-05 | No
23/06/2019 | 23:17:56 | MV61 | Urban | Asset failure | HV | 1961 | 128.1719 | 0.40182 | 0.003135 | No
23/06/2019 | 23:17:56 | MV62 | Rural Short | Asset failure | HV | 0 | 1 | 0.0075693 | 0 | No
23/06/2019 | 23:17:56 | MV62 | Rural Short | Asset failure | HV | 2082 | 114.8482 | 1.7814 | 0.015511 | No
24/06/2019 | 05:58:51 | ME231D | Urban | Asset failure | LV | 1 | 332 | 0.00053076 | 1.6e-06 | No
24/06/2019 | 07:04:23 | AP372F | Urban | Asset failure | LV | 1 | 236 | 0.00037729 | 1.6e-06 | No
24/06/2019 | 07:15:29 | AP214C | Urban | Asset failure | LV | 1 | 271 | 0.00043324 | 1.6e-06 | No
24/06/2019 | 08:16:08 | CL09 | Rural Long | Planned |  | 3 | 171 | 0.0037441 | 2.19e-05 | No
24/06/2019 | 08:18:11 | HH341D | Urban | Planned |  | 75 | 150 | 0.017985 | 0.0001199 | No
24/06/2019 | 08:27:32 | SM410D | Urban | Asset failure | LV | 61 | 43 | 0.0041933 | 9.752e-05 | No
24/06/2019 | 08:39:03 | VH22 | Rural Short | Planned |  | 192 | 423 | 0.60507 | 0.0014304 | No
24/06/2019 | 08:53:44 | HH341D | Urban | Asset failure | LV | 1.6667 | 181 | 0.00048227 | 2.66e-06 | No
24/06/2019 | 09:00:12 | HH522C | Urban | Planned |  | 1 | 365 | 0.00058352 | 1.6e-06 | No
24/06/2019 | 09:05:58 | MB12 | Rural Short | Planned |  | 38 | 11 | 0.0031142 | 0.00028311 | No
24/06/2019 | 09:10:57 | GA53 | Rural Short | Planned |  | 2 | 233 | 0.0034718 | 1.49e-05 | No
24/06/2019 | 09:12:19 | SA744D | Urban | Unknown | Unknown | 18.6667 | 132 | 0.0039391 | 2.984e-05 | No
24/06/2019 | 09:20:25 | VH22 | Rural Short | Planned |  | 1 | 395 | 0.0029428 | 7.45e-06 | No
24/06/2019 | 09:22:00 | HH130C | Urban | Planned |  | 309 | 187 | 0.092376 | 0.00049399 | No
24/06/2019 | 09:24:10 | PA07 | Rural Long | Planned |  | 47 | 94 | 0.032244 | 0.00034302 | No
24/06/2019 | 09:24:38 | NL760C | Urban | Planned |  | 1 | 341 | 0.00054515 | 1.6e-06 | No
24/06/2019 | 09:26:18 | KI12 | Rural Long | Planned |  | 3 | 195 | 0.0042695 | 2.19e-05 | No
24/06/2019 | 09:27:16 | KA03 | Rural Long | Asset failure | LV | 11.3333 | 126 | 0.010422 | 8.271e-05 | No
24/06/2019 | 09:33:09 | ME347C | Urban | Asset failure | LV | 1 | 300 | 0.0004796 | 1.6e-06 | No
24/06/2019 | 09:44:56 | VH22 | Rural Short | Planned |  | 19 | 369 | 0.052233 | 0.00014155 | No
24/06/2019 | 09:48:13 | VH21 | Rural Short | Planned |  | 1 | 519 | 0.0038666 | 7.45e-06 | No
24/06/2019 | 10:03:29 | NL544B | Urban | Planned |  | 766 | 338 | 0.41391 | 0.0012246 | No
24/06/2019 | 10:03:51 | PP03 | Urban | Planned |  | 77 | 308 | 0.037914 | 0.0001231 | No
24/06/2019 | 10:10:26 | NL760C | Urban | Planned |  | 111 | 263 | 0.04667 | 0.00017745 | No
24/06/2019 | 10:22:59 | GA05 | Rural Short | Planned |  | 3 | 289 | 0.0064593 | 2.235e-05 | No
24/06/2019 | 10:25:48 | YK24 | Rural Long | Planned |  | 111 | 1 | 0.00081012 | 0.00081012 | No
24/06/2019 | 10:27:29 | SM216C | Urban | Planned |  | 68 | 227 | 0.024677 | 0.00010871 | No
24/06/2019 | 10:31:07 | PL07 | Urban | Planned |  | 429 | 138.7692 | 0.095172 | 0.00068583 | No
24/06/2019 | 10:33:44 | VH45 | Rural Short | Planned |  | 1 | 324 | 0.0024138 | 7.45e-06 | No
24/06/2019 | 10:38:38 | HH432B | Urban | Planned |  | 9 | 292 | 0.0042013 | 1.439e-05 | No
24/06/2019 | 11:04:03 | VH21 | Rural Short | Planned |  | 291 | 382 | 0.82817 | 0.002168 | No
24/06/2019 | 11:13:51 | NL760C | Urban | Unknown | Unknown | 1 | 256 | 0.00040926 | 1.6e-06 | No
24/06/2019 | 11:22:26 | MTB41 | Rural Short | Unknown | Unknown | 2 | 85 | 0.0012665 | 1.49e-05 | No
24/06/2019 | 11:22:26 | MTB41 | Rural Short | Unknown | Unknown | 5.3333 | 86 | 0.0034171 | 3.973e-05 | No
24/06/2019 | 13:10:35 | EL02 | Urban | Unknown | Unknown | 1 | 70 | 0.00011191 | 1.6e-06 | No
24/06/2019 | 13:55:35 | PL33 | Rural Long | Planned |  | 1 | 63 | 0.0004598 | 7.3e-06 | No
24/06/2019 | 14:42:43 | VH23 | Rural Short | Asset failure | LV | 1 | 179 | 0.0013336 | 7.45e-06 | No
24/06/2019 | 15:40:34 | SM179B | Urban | Third Party | Vehicle impact | 2 | 453 | 0.0014484 | 3.2e-06 | No
24/06/2019 | 16:04:40 | HH341E | Urban | Unknown | Unknown | 191 | 449 | 0.1371 | 0.00030535 | No
24/06/2019 | 17:18:20 | SM172A | Urban | Asset failure | LV | 1 | 259 | 0.00041406 | 1.6e-06 | No
24/06/2019 | 17:28:23 | HH130C | Urban | Asset failure | LV | 22 | 115 | 0.0040447 | 3.517e-05 | No
24/06/2019 | 17:38:56 | NL451C | Urban | Asset failure | LV | 10 | 506 | 0.0080893 | 1.599e-05 | No
24/06/2019 | 18:04:31 | ME347C | Urban | Overloads |  | 1 | 489 | 0.00078175 | 1.6e-06 | No
24/06/2019 | 18:16:06 | SM349F | Urban | Overloads |  | 3096 | 9.3437 | 0.046246 | 0.0049495 | No
24/06/2019 | 18:43:24 | MB03 | Rural Long | Unknown | Unknown | 32 | 246 | 0.057453 | 0.00023355 | No
24/06/2019 | 20:40:04 | HH107B | Urban | Asset failure | LV | 1 | 117 | 0.00018704 | 1.6e-06 | No
24/06/2019 | 21:41:20 | SM179C | Urban | Overloads |  | 1 | 197 | 0.00031494 | 1.6e-06 | No
24/06/2019 | 23:04:48 | HH121D | Urban | Asset failure | LV | 1 | 160 | 0.00025579 | 1.6e-06 | No
24/06/2019 | 23:10:05 | SM402B | Urban | Planned |  | 19 | 289 | 0.0087783 | 3.037e-05 | No
25/06/2019 | 00:03:37 | HH429B | Urban | Overloads |  | 29.6667 | 141 | 0.0066873 | 4.743e-05 | No
25/06/2019 | 02:01:35 | WHY07 | Urban | Asset failure | LV | 1 | 437 | 0.00069862 | 1.6e-06 | No
25/06/2019 | 08:13:15 | PL33 | Rural Long | Planned |  | 19 | 341 | 0.047286 | 0.00013867 | No
25/06/2019 | 08:25:29 | SD34400 | Rural Long | Planned |  | 173 | 367 | 0.46338 | 0.0012626 | No
25/06/2019 | 08:52:14 | SD35500 | Rural Long | Planned |  | 334 | 372.5509 | 0.90815 | 0.0024376 | No
25/06/2019 | 08:52:41 | CD03 | Rural Short | Planned |  | 73 | 344 | 0.18709 | 0.00054386 | No
25/06/2019 | 08:54:43 | SA711C | Urban | Planned |  | 100 | 292 | 0.046681 | 0.00015987 | No
25/06/2019 | 09:01:46 | NL511A | Urban | Planned |  | 113 | 287 | 0.051847 | 0.00018065 | No
25/06/2019 | 09:03:47 | HH130C | Urban | Planned |  | 162 | 87 | 0.022532 | 0.00025899 | No
25/06/2019 | 09:03:51 | MG05 | Rural Long | Planned |  | 91 | 335 | 0.22249 | 0.00066415 | No
25/06/2019 | 09:06:01 | HH341D | Urban | Planned |  | 2 | 37 | 0.0001183 | 3.2e-06 | No
25/06/2019 | 09:11:01 | HH496F | Urban | Planned |  | 268 | 64.3843 | 0.027585 | 0.00042844 | No
25/06/2019 | 09:20:22 | HH341D | Urban | Planned |  | 1 | 42 | 6.714e-05 | 1.6e-06 | No
25/06/2019 | 09:22:12 | BU07 | Rural Long | Planned |  | 1 | 1425 | 0.0104 | 7.3e-06 | No
25/06/2019 | 09:26:06 | WHY09 | Urban | Planned |  | 15 | 246 | 0.0058991 | 2.398e-05 | No
25/06/2019 | 09:34:34 | NL544B | Urban | Planned |  | 766 | 361 | 0.44208 | 0.0012246 | No
25/06/2019 | 09:37:11 | NL759B | Urban | Planned |  | 3 | 3092.3333 | 0.014831 | 4.8e-06 | No
25/06/2019 | 09:49:53 | SA14 | Urban | Planned |  | 1 | 25 | 3.997e-05 | 1.6e-06 | No
25/06/2019 | 09:50:46 | SA14 | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
25/06/2019 | 09:56:45 | HH341D | Urban | Planned |  | 409 | 269 | 0.17589 | 0.00065386 | No
25/06/2019 | 10:11:32 | HH341D | Urban | Planned |  | 1 | 94 | 0.00015028 | 1.6e-06 | No
25/06/2019 | 10:48:03 | HH341D | Urban | Planned |  | 2 | 72 | 0.00023021 | 3.2e-06 | No
25/06/2019 | 11:25:20 | SA711C | Urban | Planned |  | 1 | 34 | 5.435e-05 | 1.6e-06 | No
25/06/2019 | 11:42:41 | HH386E | Urban | Third Party | Vehicle impact | 833 | 112.5906 | 0.14994 | 0.0013317 | No
25/06/2019 | 11:44:20 | SA14 | Urban | Planned |  | 45 | 159 | 0.011439 | 7.194e-05 | No
25/06/2019 | 12:14:38 | SM349A | Urban | Other |  | 21.3333 | 21 | 0.00071621 | 3.411e-05 | No
25/06/2019 | 12:50:45 | HH130C | Urban | Planned |  | 5 | 69 | 0.00055154 | 7.99e-06 | No
25/06/2019 | 13:09:33 | HH403B | Urban | Asset failure | LV | 63 | 87 | 0.0087623 | 0.00010072 | No
25/06/2019 | 13:39:02 | HH428B | Urban | Overloads |  | 1 | 164 | 0.00026218 | 1.6e-06 | No
25/06/2019 | 13:50:52 | SA38 | Urban | Unknown | Unknown | 3 | 428 | 0.0020527 | 4.8e-06 | No
25/06/2019 | 14:12:30 | HH102A | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 4 | 78 | 0.00049879 | 6.39e-06 | No
25/06/2019 | 14:13:03 | LM61 | Rural Long | Asset failure | HV | 1 | 86 | 0.00062766 | 7.3e-06 | No
25/06/2019 | 14:45:19 | SG04 | Rural Short | Third Party | Vehicle impact | 95 | 160.4526 | 0.11356 | 0.00070776 | No
25/06/2019 | 15:34:37 | EL01P | Urban | Asset failure | LV | 1 | 254 | 0.00040606 | 1.6e-06 | No
25/06/2019 | 17:57:29 | EL12 | Urban | Unknown | Unknown | 1 | 8286 | 0.013247 | 1.6e-06 | No
25/06/2019 | 17:58:08 | CM21 | Rural Long | Unknown | Unknown | 1 | 340 | 0.0024814 | 7.3e-06 | No
25/06/2019 | 18:23:28 | HH121D | Urban | Asset failure | LV | 1 | 188 | 0.00030055 | 1.6e-06 | No
25/06/2019 | 19:23:19 | AP355A | Urban | Overloads |  | 1 | 190 | 0.00030375 | 1.6e-06 | No
25/06/2019 | 19:33:24 | HH177D | Urban | Asset failure | LV | 39 | 91 | 0.0056737 | 6.235e-05 | No
25/06/2019 | 22:56:04 | CBD103B | Urban | Asset failure | LV | 51 | 400 | 0.032613 | 8.153e-05 | No
26/06/2019 | 08:02:32 | VH22 | Rural Short | Planned |  | 1280 | 452 | 4.3104 | 0.0095362 | No
26/06/2019 | 08:48:26 | AP424E | Urban | Planned |  | 138 | 3085 | 0.6806 | 0.00022062 | No
26/06/2019 | 08:56:42 | PL11 | Rural Long | Planned |  | 99 | 2 | 0.0014451 | 0.00072254 | No
26/06/2019 | 09:00:39 | NU13 | Rural Long | Planned |  | 26 | 389 | 0.073815 | 0.00018976 | No
26/06/2019 | 09:05:43 | SA14 | Urban | Planned |  | 90 | 153 | 0.022014 | 0.00014388 | No
26/06/2019 | 09:16:26 | MTB41 | Rural Short | Unknown | Unknown | 1 | 101 | 0.00075247 | 7.45e-06 | No
26/06/2019 | 09:16:26 | MTB41 | Rural Short | Unknown | Unknown | 5.3333 | 105 | 0.0041721 | 3.973e-05 | No
26/06/2019 | 09:27:41 | GU41 | Rural Long | Planned |  | 3 | 216 | 0.0047293 | 2.19e-05 | No
26/06/2019 | 09:35:14 | NL115C | Urban | Overloads |  | 1 | 109 | 0.00017426 | 1.6e-06 | No
26/06/2019 | 09:38:32 | NL544B | Urban | Planned |  | 766 | 318 | 0.38942 | 0.0012246 | No
26/06/2019 | 09:50:58 | YK19 | Rural Long | Planned |  | 1 | 134 | 0.00097798 | 7.3e-06 | No
26/06/2019 | 09:53:18 | MTB52 | Rural Long | Planned |  | 234 | 233 | 0.39792 | 0.0017078 | No
26/06/2019 | 10:24:24 | LX43 | Rural Short | Planned |  | 21 | 220 | 0.03442 | 0.00015645 | No
26/06/2019 | 10:43:42 | KA03 | Rural Long | Planned |  | 159 | 92 | 0.10676 | 0.0011604 | No
26/06/2019 | 10:54:49 | ME131E | Urban | Third Party | Vehicle impact | 736 | 81.9837 | 0.096464 | 0.0011766 | No
26/06/2019 | 11:03:28 | ME131E | Urban | Third Party | Vehicle impact | 614 | 91 | 0.089324 | 0.00098159 | No
26/06/2019 | 11:15:31 | AP139B | Urban | Unknown | Unknown | 196 | 255.9286 | 0.080193 | 0.00031334 | No
26/06/2019 | 12:45:52 | ME131E | Urban | Third Party | Vehicle impact | 73 | 123 | 0.014354 | 0.0001167 | No
26/06/2019 | 13:57:18 | CD02 | Rural Long | Third Party | Vehicle impact | 5.6667 | 1088 | 0.044997 | 4.136e-05 | No
26/06/2019 | 15:11:11 | SM179B | Urban | Overloads |  | 1 | 386 | 0.00061709 | 1.6e-06 | No
26/06/2019 | 15:31:49 | GA15 | Rural Short | Unknown | Unknown | 3 | 110 | 0.0024585 | 2.235e-05 | No
26/06/2019 | 16:05:02 | NA01 | Rural Long | Network business | Network error | 1 | 159 | 0.0011604 | 7.3e-06 | No
26/06/2019 | 16:52:42 | SM216C | Urban | Asset failure | LV | 22 | 37 | 0.0013013 | 3.517e-05 | No
26/06/2019 | 17:28:08 | HH121B | Urban | Asset failure | LV | 1 | 180 | 0.00028776 | 1.6e-06 | No
26/06/2019 | 18:08:28 | AP425D | Urban | Asset failure | LV | 1 | 133 | 0.00021262 | 1.6e-06 | No
26/06/2019 | 20:01:48 | GU15 | Rural Long | Asset failure | HV | 95.3333 | 603 | 0.41955 | 0.00069577 | No
26/06/2019 | 20:01:48 | GU15 | Rural Long | Asset failure | HV | 3.3333 | 215 | 0.0052305 | 2.433e-05 | No
26/06/2019 | 20:14:56 | SM126D | Urban | Asset failure | LV | 20.3333 | 231 | 0.007509 | 3.251e-05 | No
26/06/2019 | 20:38:44 | SA12 | Urban | Asset failure | LV | 1 | 148 | 0.0002366 | 1.6e-06 | No
26/06/2019 | 21:40:46 | HH177B | Urban | Unknown | Unknown | 174 | 88.1379 | 0.024517 | 0.00027817 | No
27/06/2019 | 01:05:22 | MTB21 | Rural Short | Unknown | Unknown | 30 | 166 | 0.037102 | 0.0002235 | No
27/06/2019 | 07:38:56 | NU05 | Rural Short | Unknown | Unknown | 3 | 167 | 0.0037325 | 2.235e-05 | No
27/06/2019 | 07:59:37 | PL33 | Rural Long | Planned |  | 1092 | 431.0696 | 3.4355 | 0.0079698 | No
27/06/2019 | 08:25:09 | VH22 | Rural Short | Planned |  | 111 | 413 | 0.34154 | 0.00082697 | No
27/06/2019 | 08:30:49 | SD35500 | Rural Long | Planned |  | 324 | 275 | 0.65028 | 0.0023647 | No
27/06/2019 | 08:39:57 | SM216D | Urban | Planned |  | 1 | 429 | 0.00068583 | 1.6e-06 | No
27/06/2019 | 08:47:26 | VH10 | Rural Short | Planned |  | 1 | 7 | 5.215e-05 | 7.45e-06 | No
27/06/2019 | 09:04:01 | AP355A / AP372F | Urban | Planned |  | 283 | 322.0071 | 0.14568 | 0.00045243 | No
27/06/2019 | 09:10:00 | VH11 | Urban | Planned |  | 192 | 283 | 0.086866 | 0.00030695 | No
27/06/2019 | 09:17:38 | HH130E | Urban | Planned |  | 80 | 278 | 0.035555 | 0.00012789 | No
27/06/2019 | 09:21:04 | SM349D | Urban | Planned |  | 2 | 209 | 0.00066825 | 3.2e-06 | No
27/06/2019 | 09:32:32 | HH118D | Urban | Asset failure | LV | 9 | 166 | 0.0023884 | 1.439e-05 | No
27/06/2019 | 09:33:52 | SA38 | Urban | Unknown | Unknown | 1 | 116 | 0.00018545 | 1.6e-06 | No
27/06/2019 | 09:55:19 | HH107A | Urban | Asset failure | LV | 43 | 155 | 0.010655 | 6.874e-05 | No
27/06/2019 | 10:34:00 | BM56 | Rural Short | Planned |  | 1 | 199 | 0.0014826 | 7.45e-06 | No
27/06/2019 | 10:46:36 | EL23 | Urban | Unknown | Unknown | 667 | 9.4213 | 0.010046 | 0.0010663 | No
27/06/2019 | 10:49:00 | GU31 | Rural Long | Planned |  | 91 | 177 | 0.11755 | 0.00066415 | No
27/06/2019 | 11:30:08 | SB22 | Rural Long | Planned |  | 3 | 88 | 0.0019268 | 2.19e-05 | No
27/06/2019 | 13:06:00 | CD24 | Rural Long | Unknown | Unknown | 8 | 54 | 0.0031529 | 5.839e-05 | No
27/06/2019 | 13:39:10 | HH102D | Urban | Third Party | Dig-in | 42 | 38 | 0.0025515 | 6.714e-05 | No
27/06/2019 | 13:50:28 | BU09 | Rural Long | Unknown | Unknown | 2 | 20 | 0.00029193 | 1.46e-05 | No
27/06/2019 | 14:49:52 | PL803C | Urban | Unknown | Unknown | 1 | 173 | 0.00027657 | 1.6e-06 | No
27/06/2019 | 15:35:01 | G06 | Rural Long | Unknown | Unknown | 56 | 100 | 0.040871 | 0.00040871 | No
27/06/2019 | 16:09:25 | EL11 | Urban | Asset failure | LV | 1 | 87 | 0.00013908 | 1.6e-06 | No
27/06/2019 | 16:24:52 | VH22 | Rural Short | Unknown | Unknown | 7.6667 | 53 | 0.0030272 | 5.712e-05 | No
27/06/2019 | 16:50:11 | VH22 | Rural Short | Planned |  | 1 | 71 | 0.00052896 | 7.45e-06 | No
27/06/2019 | 16:57:09 | EL260C | Urban | Third Party | Vehicle impact | 14 | 102 | 0.0022829 | 2.238e-05 | No
27/06/2019 | 19:11:49 | MV64 | Urban | Asset failure | LV | 1 | 257 | 0.00041086 | 1.6e-06 | No
27/06/2019 | 22:50:00 | VH11 | Urban | Planned |  | 1 | 336 | 0.00053715 | 1.6e-06 | No
28/06/2019 | 07:56:27 | SA38 | Urban | Planned |  | 1 | 280 | 0.00044763 | 1.6e-06 | No
28/06/2019 | 08:06:51 | HH177G | Urban | Asset failure | LV | 1 | 390 | 0.00062348 | 1.6e-06 | No
28/06/2019 | 08:19:30 | BM31 | Rural Short | Planned |  | 33 | 374 | 0.09195 | 0.00024585 | No
28/06/2019 | 08:48:54 | MI20 | Rural Long | Planned |  | 42 | 218 | 0.066824 | 0.00030653 | No
28/06/2019 | 09:04:12 | HH145D | Urban | Planned |  | 427 | 410 | 0.27988 | 0.00068263 | No
28/06/2019 | 09:18:56 | MV62 | Rural Short | Planned |  | 33 | 214 | 0.052613 | 0.00024585 | No
28/06/2019 | 09:19:27 | PL04 | Urban | Planned |  | 84 | 279 | 0.037467 | 0.00013429 | No
28/06/2019 | 09:25:21 | NL760A | Urban | Third Party | Dig-in | 4 | 332 | 0.002123 | 6.39e-06 | No
28/06/2019 | 09:26:11 | KI11 | Rural Long | Animal | Animal impact | 1 | 216 | 0.0015764 | 7.3e-06 | No
28/06/2019 | 09:32:30 | MTB11 | Rural Short | Planned |  | 41 | 277 | 0.084611 | 0.00030546 | No
28/06/2019 | 09:35:45 | SM349F | Urban | Planned |  | 1 | 144 | 0.00023021 | 1.6e-06 | No
28/06/2019 | 09:44:38 | GU42 | Rural Long | Planned |  | 100 | 249 | 0.18173 | 0.00072983 | No
28/06/2019 | 10:02:22 | VH11 | Urban | Planned |  | 1 | 89 | 0.00014228 | 1.6e-06 | No
28/06/2019 | 10:03:53 | MV62 | Rural Short | Planned |  | 1 | 338 | 0.0025181 | 7.45e-06 | No
28/06/2019 | 10:08:20 | BT04 | Rural Long | Planned |  | 2 | 52 | 0.00075903 | 1.46e-05 | No
28/06/2019 | 10:17:29 | VH11 | Urban | Planned |  | 107 | 31 | 0.0053028 | 0.00017106 | No
28/06/2019 | 10:42:47 | SM216B | Urban | Planned |  | 34 | 216 | 0.011741 | 5.435e-05 | No
28/06/2019 | 10:47:13 | AP149H | Urban | Planned |  | 1 | 296 | 0.00047321 | 1.6e-06 | No
28/06/2019 | 11:04:02 | YK19 | Rural Long | Planned |  | 55 | 51 | 0.020472 | 0.00040141 | No
28/06/2019 | 11:07:08 | HH428A | Urban | Planned |  | 86 | 56 | 0.0076992 | 0.00013749 | No
28/06/2019 | 11:10:12 | AP149H | Urban | Planned |  | 51 | 38 | 0.0030982 | 8.153e-05 | No
28/06/2019 | 12:07:41 | HH130A | Urban | Asset failure | LV | 23.6667 | 313 | 0.011842 | 3.784e-05 | No
28/06/2019 | 12:22:05 | HH177G | Urban | Overloads |  | 1 | 357 | 0.00057073 | 1.6e-06 | No
28/06/2019 | 13:12:12 | VH12 | Rural Short | Planned |  | 51 | 186 | 0.070672 | 0.00037996 | No
28/06/2019 | 14:02:45 | NL210D | Urban | Planned |  | 25 | 5 | 0.00019983 | 3.997e-05 | No
28/06/2019 | 15:06:54 | HH386E | Urban | Third Party | Vehicle impact | 56 | 370 | 0.033125 | 8.953e-05 | No
28/06/2019 | 17:16:31 | NU21 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 11.3333 | 261 | 0.021588 | 8.271e-05 | No
28/06/2019 | 17:52:24 | MV64 | Urban | Asset failure | LV | 1 | 161 | 0.00025739 | 1.6e-06 | No
28/06/2019 | 18:15:19 | AP149A | Urban | Asset failure | LV | 3 | 249 | 0.0011942 | 4.8e-06 | No
28/06/2019 | 18:40:08 | SM411E | Urban | Asset failure | LV | 1 | 225 | 0.0003597 | 1.6e-06 | No
29/06/2019 | 03:09:55 | NL111C | Urban | Asset failure | LV | 18 | 204 | 0.0058703 | 2.878e-05 | No
29/06/2019 | 04:30:15 | SM126A | Urban | Weather |  | 873 | 126.6025 | 0.17669 | 0.0013956 | No
29/06/2019 | 05:38:25 | MT01 | Rural Long | Asset failure | LV | 7 | 327 | 0.016706 | 5.109e-05 | No
29/06/2019 | 05:41:58 | MV33 | Rural Short | Asset failure | HV | 30.6667 | 416 | 0.095044 | 0.00022847 | No
29/06/2019 | 07:39:26 | HH496C | Urban | Asset failure | LV | 15 | 296 | 0.0070981 | 2.398e-05 | No
29/06/2019 | 07:41:53 | CM20 | Rural Long | Asset failure | HV | 10 | 130 | 0.0094878 | 7.298e-05 | No
29/06/2019 | 07:41:54 | CM20 | Rural Long | Asset failure | HV | 1 | 145 | 0.0010583 | 7.3e-06 | No
29/06/2019 | 08:09:11 | LX54 | Rural Short | Unknown | Unknown | 10 | 125 | 0.0093127 | 7.45e-05 | No
29/06/2019 | 08:29:52 | NA13 | Rural Long | Unknown | Unknown | 26 | 212 | 0.040228 | 0.00018976 | No
29/06/2019 | 08:38:37 | EL13 | Urban | Asset failure | LV | 5.6667 | 143 | 0.0012955 | 9.06e-06 | No
29/06/2019 | 08:39:19 | NL21 | Urban | Asset failure | LV | 1.3333 | 248 | 0.00052863 | 2.13e-06 | No
29/06/2019 | 08:46:20 | SD54102 | Rural Long | Planned |  | 2039 | 359 | 5.3424 | 0.014881 | No
29/06/2019 | 08:58:10 | VH12 | Rural Short | Asset failure | LV | 21 | 341 | 0.053351 | 0.00015645 | No
29/06/2019 | 09:20:00 | CBD103E | Urban | Planned |  | 1 | 1811 | 0.0028952 | 1.6e-06 | No
29/06/2019 | 11:40:23 | SA744D | Urban | Asset failure | LV | 71 | 73 | 0.0082859 | 0.00011351 | No
29/06/2019 | 12:33:32 | MTB21 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 1247 | 71 | 0.65961 | 0.0092903 | No
29/06/2019 | 12:40:39 | MTB52 | Rural Long | Vegetation | Blow-in/Fall-in - NSP responsibility | 1 | 137 | 0.00099987 | 7.3e-06 | No
29/06/2019 | 12:41:35 | SD41300 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 71 | 0.0010579 | 1.49e-05 | No
29/06/2019 | 12:44:45 | MTB13 | Rural Short | Planned |  | 34 | 402.4412 | 0.10194 | 0.00025331 | No
29/06/2019 | 12:59:54 | AP227A | Urban | Vegetation | Grow-in - NSP responsibility | 22.3333 | 360 | 0.012853 | 3.57e-05 | No
29/06/2019 | 13:02:57 | SG12 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 37.3333 | 122 | 0.033933 | 0.00027814 | No
29/06/2019 | 13:05:42 | SM410B | Urban | Asset failure | LV | 47 | 82 | 0.0061613 | 7.514e-05 | No
29/06/2019 | 13:08:19 | SM410B | Urban | Asset failure | LV | 16 | 98 | 0.0025067 | 2.558e-05 | No
29/06/2019 | 13:15:19 | SM216C | Urban | Asset failure | LV | 1 | 63 | 0.00010072 | 1.6e-06 | No
29/06/2019 | 14:08:01 | SB21 | Rural Long | Weather |  | 79 | 244.5949 | 0.14103 | 0.00057657 | No
29/06/2019 | 14:50:11 | HH130B | Urban | Vegetation | Grow-in - NSP responsibility | 1 | 214 | 0.00034212 | 1.6e-06 | No
29/06/2019 | 15:00:24 | NA33 | Rural Long | Weather |  | 0 | 2.8943 | 0.010393 | 0 | No
29/06/2019 | 15:19:18 | NL451C | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 999 | 90 | 0.14374 | 0.0015971 | No
29/06/2019 | 15:22:50 | NL115C | Urban | Overloads |  | 1 | 277 | 0.00044283 | 1.6e-06 | No
29/06/2019 | 15:36:33 | SM410B | Urban | Vegetation | Blow-in/Fall-in - NSP responsibility | 6 | 115 | 0.0011031 | 9.59e-06 | No
29/06/2019 | 15:36:52 | HH496G | Urban | Asset failure | LV | 1 | 326 | 0.00052117 | 1.6e-06 | No
29/06/2019 | 16:12:14 | SA36 | Urban | Asset failure | LV | 2 | 393 | 0.0012566 | 3.2e-06 | No
29/06/2019 | 17:59:46 | ME427E | Urban | Asset failure | LV | 40.3333 | 255 | 0.016442 | 6.448e-05 | No
29/06/2019 | 18:15:59 | ME116A | Urban | Asset failure | HV | 10.6667 | 150 | 0.0025579 | 1.705e-05 | No
29/06/2019 | 18:20:41 | AP226E | Urban | Asset failure | LV | 1 | 281 | 0.00044923 | 1.6e-06 | No
29/06/2019 | 19:17:59 | HH107C | Urban | Asset failure | LV | 1 | 205 | 0.00032773 | 1.6e-06 | No
29/06/2019 | 20:25:58 | MTB21 | Rural Short | Vegetation | Blow-in/Fall-in - NSP responsibility | 2 | 81 | 0.0012069 | 1.49e-05 | No
29/06/2019 | 22:00:54 | AP424E | Urban | Asset failure | LV | 1 | 823 | 0.0013157 | 1.6e-06 | No
29/06/2019 | 22:24:22 | CM28 | Rural Long | Asset failure | HV | 59 | 462.3729 | 0.1991 | 0.0004306 | No
29/06/2019 | 23:19:30 | HH522C | Urban | Asset failure | LV | 1 | 122 | 0.00019504 | 1.6e-06 | No
29/06/2019 | 23:39:39 | AP425C | Urban | Overloads |  | 1 | 199 | 0.00031814 | 1.6e-06 | No
29/06/2019 | 23:58:08 | PL04 | Urban | Asset failure | HV | 1 | 920 | 0.0014708 | 1.6e-06 | No
30/06/2019 | 00:14:41 | NL111C | Urban | Asset failure | LV | 1 | 113 | 0.00018065 | 1.6e-06 | No
30/06/2019 | 04:48:52 | SM216B | Urban | Asset failure | LV | 32 | 368 | 0.018826 | 5.116e-05 | No
30/06/2019 | 04:59:47 | GU43 | Rural Long | Third Party | Vehicle impact | 8 | 601 | 0.03509 | 5.839e-05 | No
30/06/2019 | 05:00:08 | GU43 | Rural Long | Asset failure | HV | 5 | 592 | 0.021603 | 3.649e-05 | No
30/06/2019 | 08:23:31 | ME200D | Urban | Planned |  | 86 | 216.1512 | 0.029718 | 0.00013749 | No
30/06/2019 | 08:26:12 | SD34102 | Rural Long | Planned |  | 145 | 332 | 0.35134 | 0.0010583 | No
30/06/2019 | 08:58:03 | AP132E | Urban | Planned |  | 1 | 334 | 0.00053396 | 1.6e-06 | No
30/06/2019 | 09:09:34 | GA08 | Rural Long | Planned |  | 104 | 144 | 0.1093 | 0.00075903 | No
30/06/2019 | 09:25:36 | PL04 | Urban | Planned |  | 23 | 353 | 0.01298 | 3.677e-05 | No
30/06/2019 | 09:46:41 | MTB52 | Rural Long | Planned |  | 123 | 307 | 0.27559 | 0.0008977 | No
30/06/2019 | 09:57:07 | KI56 | Rural Long | Asset failure | LV | 1 | 198 | 0.0014451 | 7.3e-06 | No
30/06/2019 | 10:42:26 | BT12 | Rural Long | Third Party | Vehicle impact | 43 | 160 | 0.050213 | 0.00031383 | No
30/06/2019 | 11:26:19 | SM350C | Urban | Overloads |  | 1 | 325 | 0.00051957 | 1.6e-06 | No
30/06/2019 | 14:12:22 | SA520D | Urban | Overloads |  | 1 | 250 | 0.00039967 | 1.6e-06 | No
30/06/2019 | 14:21:43 | SM349H | Urban | Asset failure | LV | 28.6667 | 69 | 0.0031622 | 4.583e-05 | No
30/06/2019 | 15:41:19 | MV62 | Rural Short | Unknown | Unknown | 13 | 128 | 0.012397 | 9.685e-05 | No
30/06/2019 | 16:10:59 | MV33 | Rural Short | Unknown | Unknown | 43 | 18 | 0.0057664 | 0.00032036 | No
30/06/2019 | 16:52:49 | SM350H | Urban | Asset failure | LV | 15.6667 | 48 | 0.0012022 | 2.505e-05 | No
30/06/2019 | 17:44:41 | YK23 | Rural Long | Asset failure | HV | 801 | 192.8689 | 1.1275 | 0.005846 | No
30/06/2019 | 17:56:13 | AP146B | Urban | Other |  | 1 | 47 | 7.514e-05 | 1.6e-06 | No
30/06/2019 | 18:04:24 | HH118A | Urban | Overloads |  | 1 | 155 | 0.00024779 | 1.6e-06 | No
30/06/2019 | 18:40:55 | MG11 | Rural Short | Unknown | Unknown | 80 | 64.9625 | 0.038718 | 0.00059601 | No
30/06/2019 | 19:17:35 | VH16 | Rural Short | Asset failure | LV | 1 | 333 | 0.0024809 | 7.45e-06 | No
30/06/2019 | 19:30:33 | AP424F | Urban | Asset failure | LV | 1 | 116 | 0.00018545 | 1.6e-06 | No
Contents
Instructions
Mark selection CONFIDENTIAL
Return selection to
NON-CONFIDENTIAL
Return selection to NON-AMENDED
Mark selection as AMENDED
FOR AMENDED SUBMISSIONS ONLY

## Amendments
This sheet may be used to identify amendments made to data resubmitted to the AER.
NSP data amendments
Worksheet | Table | Comments
Contents
Instructions