## Instructions
Electricity Distribution Network Service Provider
Category Analysis RIN
This template is to be used by SA Power Networks to fulfil its reporting obligations to the AER.
INSTRUCTIONS
GENERAL | Complete the Business & other details worksheet before entering data or values in any other worksheets. The Business & other details worksheet is linked to other worksheets within the workbook and automatically generates certain column headings and conditional formatting.
CONFIDENTIAL INFORMATION | Please use the macro at the top of each worksheet to identify confidential information in the confidential workbook.
-Do this by selecting the cell or cells that contain confidential information and then run the CONFIDENTIAL macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as confidential. -To reverse this, select the cell or cells and run the NON-CONFIDENTIAL macro.
PROTECTED (SOCI) INFORMATION | Please use the macro at the top of each worksheet to identify information in the confidential workbook that is protected information under the SOCI Act. All information marked Protected (SOCI) is also deemed to be confidential information.
-Do this by selecting the cell or cells that contain protected information and then run the PROTECTED (SOCI) macro. This will format the cells a specific colour that is identified by the AER's database which in turn marks that information as protected.. -To reverse this, select the cell or cells and run the NON-PROTECTED macro.
RESPONSES | Please return two (2) files to the AER: CONSOLIDATED (2 files) 1. A confidential version which must contain a complete set of all responses with confidential information marked using the Mark selection CONFIDENTIAL macro and which has been completed using the locked template file provided by the AER. 2. A public version with confidential information either removed completely or aggregated in some form. The public version must include the confidential markings to identify where confidential information has been removed from the file. Use the drop down box on the Business and other details worksheet to identify the file Confidentiality Status as either 'Confidential', or ‘Public’. Use the drop down box on the Business and other details worksheet to identify the file Data Quality as 'Consolidated'. If there is no confidential information reported in the workbook, the Consolidated Confidential file does NOT have to be submitted.
ORDER OF MAGNITUDE | All amounts are to be unrounded and reported on a one for one basis: that is 1000 is to be entered as '1000'.
INPUT / NON-INPUT CELLS
Yellow = Input cell (mandatory)
Darker yellow = input cell (mandatory)
Orange = input cell (if data available)
Grey = Not applicable/No inputs required
PLEASE DO NOT ENTER TEXT into cells that require numbers (including 'numbers stored as text')
CONFIDENTIAL
NON-CONFIDENTIAL
Protected (SOCI)
NON-Protected

## CONTENTS
CATEGORY ANALYSIS
SA Power Networks
2023-24
CONTENTS
| TEMPLATE DATE | MAY 2024
| SUBMISSION | Business & other details
| EXPENDITURE | 2.1 Expenditure summary
2.2 Repex
2.3(a) Augex
2.3(b) Augex
2.5 Connections
2.6 Non-network
2.7 Vegetation management
2.8 Maintenance
2.9 Emergency Response
2.10 Overheads
2.10(A) Overheads
2.11 Labour
2.12 Input tables
| SERVICE | 6.3 Sustained interruptions
| ALTERNATIVE CONTROL | 4.1 Public lighting
4.2 Metering
4.3 Fee-based services
4.4 Quoted services
| NETWORK | 5.2 Asset Age Profile
5.3 MD - Network level
5.4 MD & utilisation-Spatial

## Business & other details
CATEGORY ANALYSIS
SA Power Networks
2023-24
BUSINESS & OTHER DETAILS
INSTRUCTIONS
Complete the following business details regulatory template before entering data or values in any other regulatory template. This regulatory template is linked to other cells within the spreadsheet and automatically generates column headings and conditional formatting to distinguish business specific input and non-input cells.
SUBMISSION PARTICULARS INPUT SHEET
ENTITY DETAILS
Business Name
| Short name |  |  | SA Power Networks
| ACN/ABN |  |  | 13332330749
| Business Address | [6 empty] | Postal Address
| Address 1 |  |  | 1 Anzac Highway |  |  | Address 1 | GPO Box 77
| Address 2 | [5 empty] | Address 2
| Suburb |  |  | KESWICK |  |  | Suburb | ADELAIDE
| State |  |  | SA | Post code |  | State | SA | Post code
`
REGULATORY CONTROL PERIODS
|  | ANNUAL RINS | Commencing year | 2023-24
|  |  | Ending year | 2023-24
SUBMISSION DETAILS
|  |  | RIN type | Category Analysis
|  |  | Source | Reporting
|  | THIS FILE | Data Quality | Consolidated
|  |  | Confidentiality Status | Public
|  |  | Amended RIN Amendment Reason | .
|  |  | Submission Date | 2024-10-31
Contents
Instructions

## 2.1 Expenditure summary
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.1 EXPENDITURE SUMMARY & RECONCILIATION
TEMPLATE DATE - MAY 2024
There are SIX tables on this worksheet. Each has been grouped for ease of navigation.
2.1.1 - STANDARD CONTROL SERVICES CAPEX
EXPENDITURE $
2023-24
Replacement expenditure | 166066374.5
Connections | 109907943.14
Augmentation Expenditure | 69262165.3
Non-network | 105994933.57
Capitalised network overheads | 6010405.08
Capitalised corporate overheads | -5513938.15
Metering
Public Lighting
balancing item
capcons (included in the above) | 65661242.01
TOTAL GROSS CAPEX (including capcons) | 451727883.44
2.1.2 - STANDARD CONTROL SERVICES OPEX
EXPENDITURE $
2023-24
Vegetation management | 48803791.87
Maintenance | 47818734.02
Emergency response | 49454136.63
Non-network | 68788105.11
Network overheads | 93928378.12
Corporate overheads | 112929729.43
Metering
Public Lighting
balancing item | -74885873.33
TOTAL OPEX | 346837001.85
2.1.3 - ALTERNATIVE CONTROL SERVICES CAPEX
EXPENDITURE $
2023-24
Connections | 0
Capitalised network overheads | 115985.98
Capitalised corporate overheads | -58121.68
Metering | 0
Public lighting | 6540631.35
Fee and quoted | 0
balancing item
TOTAL CAPEX | 6598495.65
2.1.4 - ALTERNATIVE CONTROL SERVICES OPEX
EXPENDITURE $
2023-24
Connections | 77492818.79
Network overheads | 2114865.09
Corporate overheads | 10341644.81
Metering | 6449588.82
Public lighting | 9682944.71
Fee and quoted | 40564237.14
balancing item
TOTAL OPEX | 146646099.36
2.1.5 - DUAL FUNCTION ASSETS CAPEX
EXPENDITURE $
2023-24
Replacement expenditure
Connections
Augmentation Expenditure
Non-network
Capitalised network overheads
Capitalised corporate overheads
balancing item
capcons (included in the above)
TOTAL GROSS CAPEX (including capcons) | 0
2.1.6 - DUAL FUNCTION ASSETS OPEX
EXPENDITURE $
2023-24
Vegetation management
Maintenance
Emergency response
Non-network
Network overheads
Corporate overheads
balancing item
TOTAL OPEX | 0
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.2 Repex
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.2 REPEX
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet. Each has been grouped for ease of navigation.
2.2.1 - REPLACEMENT EXPENDITURE, VOLUMES AND ASSET FAILURES BY ASSET CATEGORY
|  |  | EXPENDITURE | ASSET REPLACEMENTS | ASSET FAILURES
|  |  | $ | (number of assets or KM) | (number of assets or KM)
ASSET GROUP | ASSET CATEGORY |  | 2023-24 | 2023-24 | 2023-24
POLES BY: HIGHEST OPERATING VOLTAGE; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole
| ˂ = 1 kV; Wood |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; Wood |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Wood |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Wood |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; Wood |  | 0 | 0 | 0
| > 132 kV; Wood |  | 0 | 0 | 0
| ˂ = 1 kV; Concrete |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; Concrete |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Concrete |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Concrete |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; Concrete |  | 0 | 0 | 0
| > 132 kV; Concrete |  | 0 | 0 | 0
| ˂ = 1 kV; Steel |  | 0 | 0 | 0
| > 1 kV & < = 11 kV; Steel |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV; Steel |  | 0 | 0 | 0
| > 22 kV & < = 66 kV; Steel |  | 0 | 0 | 0
| > 66 kV & < = 132 kV; Steel |  | 0 | 0 | 0
| > 132 kV; Steel |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
POLE TOP STRUCTURES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 6678099.74 | 11605 | 1917
| > 1 kV & < = 11 kV |  | 13144636.87 | 7826 | 1457
| ˃ 11 kV & < = 22 kV |  | 3583383.43 | 2264 | 276
| > 22 kV & < = 66 kV |  | 2894782.07 | 1843 | 142
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV |  | 450719.45 | 1 | 850
| > 1 kV & < = 11 kV |  | 7637599.72 | 83 | 229
| ˃ 11 kV & < = 22 kV ; SWER |  | 484522.02 | 16 | 107
| ˃ 11 kV & < = 22 kV ; Single-Phase |  | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase |  | 0 | 0 | 0
| > 22 kV & < = 66 kV |  | 2333261.24 | 7 | 18
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV |  | 1182267.09 | 1 | 655
| > 1 kV & < = 11 kV |  | 10468027.88 | 11 | 55
| > 11 kV & < = 22 kV |  | 0 | 0 | 1
| > 22 kV & < = 33 kV |  | 20018.32 | 0 | 4
| > 33 kV & < = 66 kV |  | 30591.87 | 0 | 0
| > 66 kV & < = 132 kV |  | 0 | 0 | 0
| > 132 kV |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type |  | 8016911.56 | 3392 | 3799
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type |  | 0 | 0 | 0
| ˂ = 11 kV ; Residential ; Complex Type |  | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type |  | 890767.95 | 377 | 422
| ˂ = 11 kV ; Subdivision ; Complex Type |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision |  | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial |  | 0 | 0 | 0
| > 132 kV ; Subdivision |  | 0 | 0 | 0
| Other |  | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 1219339.8 | 142 | 116
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 75869.51 | 3 | 5
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 84227.03 | 1
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 61252.14 | 5 | 7
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 1143172.68 | 62 | 65
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase |  | 163899.73 | 1
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase |  | 590818.27 | 2
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase |  | 825775.68 | 1
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase |  | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  | 1604230.89 | 10 | 7
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase |  | 1359559.77 | 2
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase |  | 105708.09 | 1 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA |  | 976611.64 | 2 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA |  | 4110474.58 | 3 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA |  | 19461.31 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA |  |  | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA |  |  | 0 | 0
| Other |  |  | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE ; SWITCH FUNCTION | ˂ = 11 kV ; FUSE |  |  | 0 | 0
| ˂ = 11 kV ; Switch |  | 4060112.03 | 70 | 30
| ˂ = 11 kV ; Circuit Breaker |  | 8341622.4 | 4 | 0
| > 11 kV & < = 22 kV ; Switch |  |  | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker |  |  | 0 | 0
| > 22 kV & < = 33 kV ; Switch |  | 1004585.18 | 7 | 1
| > 22 kV & < = 33 kV ; Circuit Breaker |  | 1234685.69 | 4 | 0
| > 33 kV & < = 66 kV ; Switch |  | 1393562.52 | 19 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker |  | 15268292.95 | 17 | 1
| > 66 kV & < = 132 kV ; Switch |  |  | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker |  |  | 0 | 0
| > 132 kV ; Switch |  |  | 0 | 0
| > 132 kV ; Circuit Breaker |  |  | 0 | 0
| Other |  |  | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION | Luminaires ; Major Road
Luminaires ; Minor Road
Brackets ; Major Road
Brackets ; Minor Road
Lamps ; Major Road
Lamps ; Minor Road
Poles / Columns ; Major Road
Poles / Columns ; Minor Road
Other
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices |  | 11638495.45 | 117 | 14
Local Network Wiring Assets
| Communications Network Assets |  | 5097017.89 | 171 | 0
| Master Station Assets |  | 1084379.81 | 8 | 0
| Communications Site Infrastructure |  | 105537.59 | 0 | 0
| Communications Linear Assets |  | 1718330.22 | 4.5 | 0
AFLC
Other
OTHER BY: DNSP DEFINED | < = 1 kV; stobie pole |  | 8084266.75 | 414 | 263
| > 1 kV & < = 11 kV; stobie pole |  | 11373422.41 | 340 | 76
| > 11 kV & < = 22 kV; stobie pole |  | 3131992.2 | 170 | 15
| > 22 kV & < = 66 kV; stobie pole |  | 1165691.78 | 23 | 1
| > 66 kV & < = 132 kV; stobie pole |  | 0 | 0 | 0
| > 132 kV; stobie pole |  | 0 | 0 | 0
| Pole REFURBISHED; STOBIE Pole |  | 4970117.47 | 3579 | 0
| Pole Mounted ;> = 22 kV & < = 33 kV ; < = 60kVA; DISTRIBUTION TRANSFORMER |  | 222803.76 | 13 | 3
| Pole Mounted ;> = 22 kV & < = 33 kV ; > 60 KVA AND < = 600 KVA; DISTRIBUTION TRANSFORMER |  | 32943.62 | 1 | 7
| Kiosk Mounted; > = 22 kV & < = 33 kV ; DISTRIBUTION TRANSFORMER |  | 0 | 0 | 0
| Voltage regulator; DISTRIBUTION TRANSFORMER |  | 1082333.3 | 13 | 16
| Recloser ;SWITCHGEAR |  | 3278586.24 | 75 | 74
| Sectionalizer ;SWITCHGEAR |  | 192098.32 | 0 | 29
| >= 11 kV & < = 22 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR |  | 3457704.34 | 21 | 4
| > 22 kV & < = 33 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR |  | 0 | 0 | 0
| OTHER - Distribution |  | 398104.42 | 0 | 0
| OTHER - Non Category Substation asset replacement/refurbishment |  | 3480794.33 | 48 | 1
| Pipework Bus Substation Replacements |  | 3027129.81 | 2 | 0
| > = 11 kV ; Circuit Breaker REFURBISHED |  | 86526.54 | 3 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker REFURBISHED |  | 25428.9 | 1 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker REFURBISHED |  | 10185 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ? 22 kV ; > 600 kVA ; Multiple Phase REFURBISHED |  | 0 | 0 | 0
| GROUND OUTDOOR / INDOOR CHAMBER MOUNTED ; > = 22 kV & < = 33 kV ; < = 15 MVA REFURBISHED |  | 0 | 0 | 0
| GROUND OUTDOOR / INDOOR CHAMBER MOUNTED ; > 33 kV & < = 66 kV ; < = 15 MVA REFURBISHED |  | 803690.22 | 3 | 0
| GROUND OUTDOOR / INDOOR CHAMBER MOUNTED ; > 33 kV & < = 66 kV ; > 15 MVA AND < = 40 MVA REFURBISHED |  | 93389.93 | 1 | 0
| GROUND OUTDOOR / INDOOR CHAMBER MOUNTED ; > = 22 kV & < = 33 kV ; > 15 MVA AND < = 40 MVA REFURBISHED |  | 46553.07 | 0 | 0
2.2.2 - SELECTED ASSET CHARACTERISTICS
|  |  | ASSET VOLUMES CURRENTLY IN COMMISSION | ASSET REPLACEMENTS
ASSET GROUP | METRIC | UNITS | 2023-24 | 2023-24
TOTAL POLES BY: FEEDER TYPE | Total CBD poles | Number | 268 | 1
| Total urban poles | Number | 197470.47 | 419
| Total rural long poles | Number | 331612.83 | 340
| Total rural short poles | Number | 96642.7 | 187
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH BY FEEDER TYPE | Conductors CBD | KM | 64.83 | 0
| Conductors urban | KM | 54109.88 | 10.67
| Conductors rural long | KM | 87446.64 | 65.4
| Conductors rural short | KM | 30871.64 | 31.03
OVERHEAD CONDUCTORS BY: CONDUCTOR LENGTH MATERIAL TYPE | OH conductor LV ABC | KM | 8062.26 | 1.08
| OH conductor steel | KM | 41195.28 | 23.6
| OH conductor ACSR | KM | 38533.41 | -6.05
| OH conductor AAAC | KM | 6166.9 | 78.9
| OH conductor AAC | KM | 33614.83 | 8.97
| OH conductor HDBC | KM | 44920.31 | 0.6
| Other | KM | 0 | 0
UNDERGROUND CABLES BY: CABLE LENGTH BY FEEDER TYPE | Cable CBD | KM | 308.11 | 1.57
| Cable urban | KM | 11839.34 | 10.04
| Cable rural long | KM | 3565.45 | 0.05
| Cable rural short | KM | 4081.1 | 0.08
TRANSFORMERS BY: TOTAL MVA | Total MVA replaced | MVA | 0 | 89.66
| Total MVA disposed of | MVA | 0 | 34.18
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.3(a) Augex
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.3 AUGEX PROJECT DATA
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet - each has been 'grouped' for easy navigation. Both ROWS and COLUMNS have been grouped.
2.3.1 - AUGEX ASSET DATA - SUBTRANSMISSION SUBSTATIONS, SWITCHING STATIONS AND ZONE SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE $ | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
SUBSTATION ID | SUBSTATION TYPE (drop down) | PROJECT ID | PROJECT TYPE (drop down) | PROJECT TRIGGER (drop down) | VOLTAGE (KV) | SUBSTATION RATING NORMAL CYCLIC (MVA) |  | SUBSTATION RATING N-1 EMERGENCY (MVA) |  | TRANSFORMERS |  |  | SWITCHGEAR |  | CAPACITORS |  |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | PRE | POST | PRE | POST | UNITS ADDED | MVA ADDED | EXPENDITURE $ | UNITS ADDED | EXPENDITURE $ | MVAR ADDED | EXPENDITURE $ |  |  | EXPENDITURE $ | VOLUME | EXPENDITURE $ | EXPENDITURE $ |  |  |  | EXPENDITURE $ |  |  | EXPENDITURE $
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
|  | Non material projects - [actual] | [21 empty] | 19472582.27
AUG232_1 | AUG232_2 | AUG232_3 | AUG232_4 | AUG232_5 | AUG232_6 | ED_AUG232_00001 | ED_AUG232_00002 | ED_AUG232_00003 | ED_AUG232_00004 | ED_AUG232_00005 | ED_AUG232_00006 | ED_AUG232_00007 | ED_AUG232_00008 | ED_AUG232_00009 | ED_AUG232_00010 | ED_AUG232_00011 | ED_AUG232_00012 | ED_AUG232_00013 | ED_AUG232_00014 | ED_AUG232_00015 | ED_AUG232_00016 | ED_AUG232_00017 | ED_AUG232_00018 | ED_AUG232_00019 | ED_AUG232_00020 | ED_AUG232_00021
2.3.2 - AUGEX ASSET DATA - SUBTRANSMISSION LINES
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON A PROJECT CLOSE BASIS.
PROJECT DESCRIPTION AND CHANGES | [9 empty] | PLANT AND EQUIPMENT EXPENDITURE AND VOLUME | [11 empty] | OTHER EXPENDITURE |  | TOTAL DIRECT EXPENDITURE $ | YEARS INCURRED | ALL RELATED PARTY CONTRACTS |  | ALL NON RELATED PARTY CONTRACTS | LAND AND EASEMENTS
LINE ID | PROJECT ID | PROJECT TYPE | PROJECT TRIGGER |  | VOLTAGE (KV) | ROUTE LINE LENGTH ADDED |  |  |  | POLES/TOWERS (INCLUDING STRUCTURES, AND CIVIL WORKS) |  |  | OVERHEAD LINES |  |  | UNDERGROUND CABLES |  |  | OTHER PLANT ITEM | INSTALLATION (LABOUR) |  | CIVIL WORKS | OTHER DIRECT |  |  | RELATED PARTY MARGINS | TOTAL |  | LAND PURCHASE | EASEMENTS
[6 empty] | KM ADDED |  |  |  | POLES/TOWERS ADDED | POLES/TOWERS UPGRADED | EXPENDITURE $ | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE $ | CIRCUIT KM ADDED | CIRCUIT KM UPGRADED | EXPENDITURE $ | EXPENDITURE $ | VOLUME | EXPENDITURE $ | EXPENDITURE $ |  |  |  | EXPENDITURE $ |  |  | EXPENDITURE $
[24 empty] | 0 | [6 empty] | New line on new route - single circuit
[24 empty] | 0 | [6 empty] | New line on new route - dual circuit
[24 empty] | 0 | [6 empty] | New line on new route - other
[24 empty] | 0 | [6 empty] | Line rebuild over existing route - single circuit
[24 empty] | 0 | [6 empty] | Line rebuild over existing route - dual circuit
[24 empty] | 0 | [6 empty] | Reconductor - Single circuit
[24 empty] | 0 | [6 empty] | Reconductor - Dual circuit
[24 empty] | 0 | [6 empty] | Reconductor - Other
[24 empty] | 0 | [6 empty] | Line upgrade - raising/retensoring
[24 empty] | 0 | [6 empty] | Line upgrade - voltage upgrade
[24 empty] | 0 | [6 empty] | Line upgrade - capacity
[24 empty] | 0 | [6 empty] | String spare circuit
[24 empty] | 0 | [6 empty] | Other
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
| Non material projects - [actual] | [22 empty] | 1432930.45
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.3(b) Augex
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.3 AUGEX DATA
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet. Each has been grouped for ease of navigation.
2.3.3 - AUGEX DATA - HV/LV FEEDERS AND DISTRIBUTION SUBSTATIONS
NOTE: DNSP MUST PROVIDE EXPENDITURE INFORMATION ON AN AS INCURRED BASIS.
DESCRIPTOR METRICS
PROJECT TYPE |  | UNITS ADDED 0's | UNITS UPGRADED 0's
| UNITS | 2023-24 | 2023-24
HV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0 | 0
HV Feeder Augmentations - Underground Cables | Circuit line length in km | 0 | 0
LV Feeder Augmentations - Overhead Lines | Circuit line length in km | 0.23 | 1.99
LV Feeder Augmentations - Underground Cables | Circuit line length in km | 0.37 | 0.17
Distribution Substation Augmentations - Pole Mounted | Number | 73 | 75
Distribution Substation Augmentations - Ground Mounted | Number | 1 | 0
Distribution Substation Augmentations - Indoor | Number | 0 | 0
COST METRICS
TOTAL DIRECT EXPENDITURE - Project Type |  | EXPENDITURE $
2023-24
HV Feeder Augmentations - Overhead Lines |  | 0
HV Feeder Augmentations - Underground Cables |  | 6979945.67
HV Feeder Non-Material Projects |  | 21960745.29
LV Feeder Augmentations - Overhead Lines |  | 873151.49
LV Feeder Augmentations - Underground Cables |  | 332072.68
LV Feeder Non-Material Projects |  | 326962.45
Distribution Substation Augmentations - Pole Mounted |  | 567688.29
Distribution Substation Augmentations - Ground Mounted |  | 0
Distribution Substation Augmentations - Indoor |  | 19872.72
2.3.4 - AUGEX DATA - TOTAL EXPENDITURE
AUGMENTATION CAPEX (As incurred) |  | EXPENDITURE $
2023-24
Subtransmission Substations, Switching Stations, Zone Substations |  | 35936617.71
Subtransmission Lines |  | 2090444.41
HV Feeders |  | 29103435.41
HV Feeders - Land Purchases and Easements |  | 0
Distribution Substations |  | 590865.09
Distribution Substations - Land Purchases And Easements
LV Feeders |  | 1540802.69
LV Feeders - Land Purchases And Easements
Other Assets
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.5 Connections
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.5 CONNECTIONS
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet. Each has been grouped for ease of navigation.
2.5.1 - DESCRIPTOR METRICS
<<<GROUP-ROW>>>
VOLUMES AND EXPENDITURE
CONNECTION SUBCATEGORY | DESCRIPTOR METRIC | UNITS | 2023-24
RESIDENTIAL | Underground connections | 0's | 6786
| Overhead connections | 0's | 52
| Distribution substation installed | MVA added | 7
| Distribution substations installed | 0's | 122
| Distribution substation installed | total spend $ | 2964761
| Augmentation HV | net circuit km added | 2
| Augmentation HV | total spend $ | 387439
| Augmentation LV | net circuit km added | 3
| Augmentation LV | total spend $ | 788204.45
| Mean days to connect residential customer with LV single phase connection | 0's | 8.8
| Volume of GSL breaches for residential customers | 0's | 365
| Volume of customer complaints relating to connection services | 0's | 131
| GSL payments | $0s | 107185
COMMERCIAL/INDUSTRIAL | Underground connections | 0's | 624
| Overhead connections | 0's | 54
| Distribution substation installed | MVA added | 112
| Distribution substations installed | 0's | 255
| Distribution substation installed | total spend $ | 14306617.89
| Augmentation HV | net circuit km added | 32
| Augmentation HV | total spend $ | 8262033.15
| Augmentation LV | net circuit km added | 11
| Augmentation LV | total spend $ | 5110611.51
SUBDIVISION | Underground connections | 0's | 225
| Overhead connections | 0's | 34
| Distribution substation installed | MVA added | 15
| Distribution substations installed | 0's | 57
| Distribution substation installed | total spend $ | 2499878.74
| Augmentation HV | net circuit km added | 7
| Augmentation HV | total spend $ | 1711005.37
| Augmentation LV | net circuit km added | 6
| Augmentation LV | total spend $ | 2132592.14
| Cost per lot ($) | $0s | 2106
EMBEDDED GENERATION | Underground connections | 0's | 209
| Overhead connections | 0's | 18
| Distribution substation installed | MVA added | 0
| Distribution substations installed | 0's | 1
| Distribution substation installed | total spend $ | 0
| Augmentation HV | net circuit km added | 2
| Augmentation HV | total spend $ | 0
| Augmentation LV | net circuit km added | 0
| Augmentation LV | total spend $ | 0
2.5.2 - COST METRICS BY CONNECTION CLASSIFICATION
|  | EXPENDITURE $ | VOLUMES 0's
CONNECTION SUBCATEGORY | CONNECTION CLASSIFICATION | 2023-24 | 2023-24
RESIDENTIAL | Simple connection LV | 14842192.52 | 6844
| Complex connection LV | 7042290.35 | 301
| Complex connection HV | 0 | 0
COMMERCIAL/INDUSTRIAL | Simple connection LV | 4179772.84 | 678
| Complex connection HV (customer connected at LV, minor HV works) | 29080558.76 | 348
| Complex connection HV (customer connected at LV, upstream asset works) | 17996771.48 | 45
| Complex connection HV (customer connected at HV) | 22387925.65 | 4
| Complex connection sub-transmission | 121877.62 | 0
SUBDIVISION | Complex connection LV | 3131340.92 | 76
| Complex connection HV (no upstream asset works) | 7347504.93 | 112
| Complex connection HV (with upstream asset works) | 3777708.09 | 74
EMBEDDED GENERATION | Simple connection LV | 0 | 0
| Complex connection HV (small capacity) | 0 | 191
| Complex connection HV (large capacity) | 0 | 36
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.6 Non-network
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.6 NON NETWORK EXPENDITURE
TEMPLATE DATE - MAY 2024
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation.
2.6.1 - NON-NETWORK EXPENDITURE
EXPENDITURE $
SERVICE SUBCATEGORY | ASSET CATEGORY |  |  | 2023-24
OPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 4650139.37
| Recurrent expenditure |  |  | 35963575.05
| Non-recurrent expenditure |  |  | 664889.64
MOTOR VEHICLES | Car |  |  | 366144
| Light commercial vehicle |  |  | 4700831
| Elevated work platform (LCV) |  |  | 0
| Elevated work platform (HCV) |  |  | 5918023
| Heavy commercial vehicle |  |  | 1174958
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 6510061
OTHER | Other expenditure |  |  | 8839484.24
OTHER - DNSP nominated | TEC Vehicles |  |  | 3443025
| Cranes |  |  | 1746232
| Trailers |  |  | 1668046
| Other Commercial Vehicles |  |  | 360729
| Network Telephony |  |  | 1621452.24
CAPEX
IT & COMMUNICATIONS | Client device expenditure |  |  | 4073220.34
| Recurrent expenditure |  |  | 20278362.92
| Non-recurrent expenditure |  |  | 15773377.82
MOTOR VEHICLES | Car |  |  | 2893436
| Light commercial vehicle |  |  | 11586544
Elevated work platform (LCV)
| Elevated work platform (HCV) |  |  | 8616178
| Heavy commercial vehicle |  |  | 1266695
BUILDINGS AND PROPERTY | Total buildings and property expenditure |  |  | 14029077
OTHER | Other expenditure |  |  | 27478041.83
OTHER - DNSP nominated | TEC Vehicles |  |  | 2310373
| Cranes |  |  | 3846706
| Trailers |  |  | 1352606
| Other Commercial Vehicles |  |  | 192304
| OT Cyber Security Zone |  |  | 1798986.96
| ADMS DERMS |  |  | 1516221.14
| ADMS 3.9 Upgrade |  |  | 2008014.64
| DET Customer Sys 2023 |  |  | 1014947.64
| DER Operational Sys 2023/24 |  |  | 2399073.27
| Non-Network Telecommuniations |  |  | 1209718.1
| Non-Network Plant and Tools and Other Network Strategic |  |  | 9829091.08
2.6.2 - ANNUAL DESCRIPTOR METRICS - IT & COMMUNICATIONS EXPENDITURE
VOLUMES 0's
NON-NETWORK CATEGORY | DESCRIPTOR METRIC |  |  | 2023-24
IT & COMMUNICATIONS | Employee numbers |  |  | 2016
| User numbers |  |  | 2903
| Number of devices |  |  | 6884
2.6.3 - ANNUAL DESCRIPTOR METRICS - MOTOR VEHICLES
VOLUMES / %
NON-NETWORK CATEGORY | ASSET CATEGORY | DESCRIPTOR METRIC | UNITS | 2023-24
MOTOR VEHICLES | CAR | Average kilometres travelled | km | 11230
|  | Number purchased | 0's | 31
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 114
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 88.4%
| LIGHT COMMERCIAL VEHICLE | Average kilometres travelled | km | 16581
|  | Number purchased | 0's | 163
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 602
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 88.4%
| ELEVATED WORK PLATFORM (LCV) | Average kilometres travelled | km | 0
|  | Number purchased | 0's | 0
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 0
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 0%
| ELEVATED WORK PLATFORM (HCV) | Average kilometres travelled | km | 15064
|  | Number purchased | 0's | 17
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 154
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 88.4%
| HEAVY COMMERCIAL VEHICLE | Average kilometres travelled | km | 8684
|  | Number purchased | 0's | 10
|  | Number leased | 0's | 0
|  | Number in fleet | 0's | 70
|  | Proportion of total fleet expenditure allocated as regulatory expenditure | (per cent) | 88.4%
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.7 Vegetation management
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.7 VEGETATION MANAGEMENT
TEMPLATE DATE - MAY 2024
There are THREE tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation.
Please enter a description for each Zone in table 2.7.1 - Urban and CBD. The zone description will then autopopulate in tables 2.7.1 - Rural and 2.7.2.
` | 2.7.1 - DESCRIPTOR METRICS BY ZONE
URBAN AND CBD
2023-24
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
RURAL
2023-24
| ZONES | ASSET | UNITS
| ZONE 1 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 2 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 3 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 4 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 5 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 6 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 7 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 8 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 9 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 10 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 11 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 12 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 13 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 14 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 15 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 16 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 17 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
| ZONE 18 | Route line length within zone | km
|  | Number of maintenance spans | 0's
|  | Total length of maintenance spans | km
|  | Length of vegetation corridors | km
|  | Average number of trees per maintenance span | 0's
|  | Average frequency of cutting cycle | years
2.7.2 - EXPENDITURE METRICS BY ZONE
EXPENDITURE $
| ZONES | SERVICE SUBCATEGORY |  | 2023-24
| ZONE 1 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 2 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 3 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 4 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 5 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 6 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 7 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 8 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 9 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 10 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 11 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 12 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 13 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 14 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 15 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 16 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 17 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
| ZONE 18 | Tree trimming (excluding hazard trees)
Hazard tree cutting
Ground clearance
Vegetation corridor clearance
Inspection
Audit
Contractor liaison expenditure
Tree replacement program costs
Other vegetation management costs not specified in sheet
2.7.3 - DESCRIPTOR METRICS ACROSS ALL ZONES - UNPLANNED VEGETATION EVENTS
VOLUMES 0's
| DESCRIPTOR METRIC |  |  | 2023-24
| Number of fire starts caused by vegetation grow-ins (NSP responsibility) |  |  | 2
| Number of fire starts caused by vegetation blow-ins and fall-ins (NSP responsibility) |  |  | 10
| Number of fire starts caused by vegetation grow-ins (other party responsibility) |  |  | 0
| Number of fire starts caused by vegetation blow-ins and fall-ins (other party responsibility) |  |  | 0
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.8 Maintenance
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.8 MAINTENANCE
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet. Each has been grouped for ease of navigation.
2.8.1 - DESCRIPTOR METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
|  |  |  | ASSET QUANTITY 0's |  | AVERAGE AGE OF ASSET GROUP | INSPECTION CYCLE (YEARS) | MAINTENANCE CYCLE (YEARS)
|  |  |  | AT YEAR END | INSPECTED / MAINTAINED
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2023-24 | 2023-24 | 2023-24
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 625990 | 114633 | 50 | 5 | 0
| Service lines | Number of customers | Number | 864390 | 0 | 29 | 5 | 0
Pole inspection and treatment | All poles | Number of poles | Number | 625990 | 114633 | 50 | 5 | 0
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 64750 | 51786 | 57 | 5 | 0
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 19602 | 0 | 27 | 0 | 0
| 33 KV and above | Length (KM) | KM | 192 | 12 | 45 | 0.5 | 0
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 308 | 12 | 45 | 0 | 0
| Non-CBD | Length (KM) | KM | 19486 | 0 | 27 | 0 | 0
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 78085 | 14290 | 30 | 5 | 0
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 10814 | 1400 | 15 | 1 | 0
| Distribution substation - other equipment | Earth mat | Number | 0 | 0 | 0 | 0 | 0
| Distribution substation - property | Number of distribution substation properties maintained | Number | 15193 | 20 | 26 | 0 | 0
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 717 | 557 | 33.5 | 0.5 | 6
| Transformers - distribution | Number of distribution transformers within zone substation | Number | 393 | 0 | 20 | 0.5 | 0
| Transformers - HV | Number of HV transformers | Number | 0 | 0 | 0 | 0 | 0
| Zone substation - other equipment |  | Number | 397 | 255 | 9.5 | 0.5 | 10
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 406 | 2026 | 48 | 0.5 | 5
Public lighting maintenance | Minor roads | Number of public lights maintained | Number | 0 | 0 | 0 | 0 | 0
| Major roads | Number of public lights maintained | Number | 0 | 0 | 0 | 0 | 0
SCADA & network control maintenance | SCADA & network control | Number of systems | Number | 455 | 0 | 13.3 | 0 | 0
Protection systems maintenance | Protection systems | Number of systems | Number | 5438 | 493 | 28.5 | 0.5 | 5
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets |  | Number | 0 | 0 | 0 | 0 | 0
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 7797 | 665 | 13 | 1.5 | 1.5
Ground clearance - access tracks | Access tracks | Number | Number | 0 | 0 | 0 | 0 | 0
Other | Substation asset inspection | Number of sites | Number | 397 | 750 | 48 | 0.5 | 0
| Zone substation equipment maintenance (switchgear) | Number of CBs and disconnectors | Number | 5835 | 494 | 33.8 | 0.5 | 5
| Numbers of signages and IDs replaced | No. of sites | Number | 78085 | 2213 | 0 | 0 | 0
| Power Station Maintenance, Asset Records Feeder Diagram Maintenance, Compliance Audting, Asset Location Services, Customer Service Penalties | Units not quoted as various UOM | Number | 0 | 0 | 0 | 0 | 0
2.8.2 - COST METRICS FOR ROUTINE AND NON-ROUTINE MAINTENANCE
EXPENDITURE $
|  |  |  | ROUTINE MAINTENANCE | NON-ROUTINE MAINTENANCE
MAINTENANCE ACTIVITY | MAINTENANCE ASSET CATEGORY | ASSET QUANTITY | Units | 2023-24 | 2023-24
Pole top, overhead line & service line maintenance | Pole tops and overhead lines | Number of poles | Number | 1834511.39 | 2802997.09
| Service lines | Number of customers | Number
Pole inspection and treatment | All poles | Number of poles | Number | 8069461.67 | 412147.41
Overhead asset inspection | All overhead assets | Line patrolled (route KM) | KM | 6261436.77 | 182793.01
Network underground cable maintenance: by voltage | LV - 11 to 22 KV | Length (KM) | KM | 597480.99 | 294300.14
| 33 KV and above | Length (KM) | KM | 110069.11 | 309704.61
Network underground cable maintenance: by location | Cbd | Length (KM) | KM | 707550.1 | 604004.75
| Non-CBD | Length (KM) | KM
Distribution substation equipment & property maintenance | Distribution substation transformers | Number of installed transformers | Number | 24174.61 | 473545.37
| Distribution substation switchgear (within-substations and stand-alone switchgear) | Number of switches | Number | 746603.95 | 76678.09
| Distribution substation - other equipment | Earth mat | Number
| Distribution substation - property | Number of distribution substation properties maintained | Number | 0 | 51452.07
Zone substation equipment maintenance | Transformers - zone substation | Number | Number | 3917659.62 | 1190941.84
| Transformers - distribution | Number of distribution transformers within zone substation | Number
| Transformers - HV | Number of HV transformers | Number
| Zone substation - other equipment |  | Number | 1853610.08 | 744008.46
Zone substation property maintenance | All zone substation properties | Number of zone substation properties maintained | Number | 1862876.44 | 2548901.87
Public lighting maintenance | Minor roads | Number of public lights maintained | Number
| Major roads | Number of public lights maintained | Number
SCADA & network control maintenance | SCADA & network control | Number of systems | Number |  | 238921.28
Protection systems maintenance | Protection systems | Number of systems | Number | 1656644.56 | 106121.37
Subtransmission asset maintenance | Subtransmission asset maintenance - for DNSPs with dual function assets |  | Number
Various assets | includes rates, electricity, communications equip, metering | Various | Number | 699103.85 | 5398664.37
Ground clearance - access tracks | Access tracks | Number | Number
Other | Substation asset inspection | Number of sites |  | 684520.06
| Zone substation equipment maintenance (switchgear) | Number of CBs and disconnectors |  | 2617684.11 | 1043595.76
| Numbers of signages and IDs replaced | No. of sites |  |  | 236806.84
| Power Station Maintenance, Asset Records Feeder Diagram Maintenance, Compliance Audting, Asset Location Services, Customer Service Penalties | Units not quoted as various UOM |  | 771317.24
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.9 Emergency Response
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.9 EMERGENCY RESPONSE
TEMPLATE DATE - MAY 2024
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation.
2.9.1 - EMERGENCY RESPONSE EXPENDITURE (OPEX)
EXPENDITURE $
2023-24
(A) TOTAL EMERGENCY RESPONSE EXPENDITURE
Total Expenditure | 49454137
(B) MAJOR EVENTS O&M EXPENDITURE
(C) MAJOR EVENT DAYS O&M EXPENDITURE
02/10/2023 | 83699
28/11/2023 | 852636
8/12/2023 | 394661
11/12/2023 | 1098389
28/12/2023 | 236137
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.10 Overheads
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.10 OVERHEADS
TEMPLATE DATE - MAY 2024
Please note. This worksheet 2.10 Overheads is the original worksheet. We have also included a different version of the Overheads template (worksheet 2.10A Overheads) which collects the information in a different way. SA Power Networks is not obliged to complete worksheet 2.10A. However, the AER would prefer to collect Overheads information as presented in the revised worksheet 2.10A Overheads. If SA Power Networks is prepared to complete worksheet 2.10A in lieu of the original worksheet 2.10 Overheads, please indicate that choice by selecting from the drop down list at the right. SA Power Networks is only required to complete one version of the Overheads worksheet in order to comply with the Category Analysis RIN. |  | Choose Response drop down selection
Worksheet 2.10A
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation.
Instructions Please enter a description for each expenditure category as currently reported under SA Power Networks's annual RIN.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE $
2023-24
NETWORK OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED NETWORK OVERHEADS
Standard Control Services
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE $
2023-24
CORPORATE OVERHEADS
Standard Control Services
Alternative Control Services
Negotiated Services | Total
Unregulated Services | Total
CAPITALISED CORPORATE OVERHEADS
Standard Control Services
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.10(A) Overheads
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.10(A) OVERHEADS
TEMPLATE DATE - MAY 2024
This worksheet may be completed on a voluntary basis. Please see worksheet 2.10 for an explanation of Overheads reporting options.
There are TWO tables on this worksheet. Each has been grouped (and sub-grouped) for ease of navigation.
2.10.1 - NETWORK OVERHEADS EXPENDITURE
EXPENDITURE $
2023-24
OPEX
Standard Control Services | Total | 93928378.12
Alternative Control Services | Total | 2114865.09
CAPEX
Standard Control Services | Total | 6010405.08
Alternative Control Services | Total | 115985.98
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 0
Unregulated Services | Total | 36162.18
2.10.2 - CORPORATE OVERHEADS EXPENDITURE
EXPENDITURE $
2023-24
OPEX
Standard Control Services | Total | 112929729.43
Alternative Control Services | Total | 10341644.81
CAPEX
Standard Control Services | Total | -5513938.15
Alternative Control Services | Total | -58121.68
OTHER DISTRIBUTION SERVICES
Negotiated Services | Total | 0
Unregulated Services | Total | 897362.07
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.11 Labour
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.11 LABOUR
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet. Each has been grouped for ease of navigation.
2.11.1 - COST METRICS PER ANNUM
|  | ASL 0's | TOTAL LABOUR EXPENDITURE $ | AVERAGE PRODUCTIVE WORK HOURS PER ASL 0's | STAND-DOWN OCCURENCES PER ASL 0's
|  | 2023-24 | 2023-24 | 2023-24 | 2023-24
INTERNAL LABOUR EXPENDITURE
CORPORATE OVERHEADS | Executive manager
Senior manager
Manager
Professional
Semi professional
Support staff
Intern, junior staff, apprentice
NETWORK OVERHEADS | Executive manager
Senior manager
Manager
Professional
Semi professional
Support staff
Intern, junior staff, apprentice
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker
Skilled non electical worker
Apprentice
Unskilled worker
2.11.2 - DESCRIPTOR METRICS
|  | ORDINARY TIME 0's |  | OVERTIME 0's
|  | PER ASL | HOURLY RATE PER ASL | PER ASL | HOURLY RATE PER ASL
|  | 2023-24 | 2023-24 | 2023-24 | 2023-24
AVERAGE PRODUCTIVE WORK HOURS PER ASL
CORPORATE OVERHEADS | Executive manager
Senior manager
Manager
Professional
Semi professional
Support staff
Intern, junior staff, apprentice
NETWORK OVERHEADS | Executive manager
Senior manager
Manager
Professional
Semi professional
Support staff
Intern, junior staff, apprentice
TOTAL DIRECT NETWORK LABOUR | Skilled electrical worker
Skilled non electical worker
Apprentice
Unskilled worker
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 2.12 Input tables
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
2.12 INPUT TABLES
TEMPLATE DATE - MAY 2024
There is ONE table on this worksheet. It has been sub-grouped for ease of navigation.
2.12.1 - INPUT TABLES
|  | DIRECT MATERIAL EXPENDITURE | DIRECT LABOUR EXPENDITURE | CONTRACT EXPENDITURE | OTHER EXPENDITURE | RELATED PARTY CONTRACT EXPENDITURE | RELATED PARTY CONTRACT MARGIN EXPENDITURE
EXPENDITURE $
|  | 2023-24 | 2023-24 | 2023-24 | 2023-24 | 2023-24 | 2023-24
VEGETATION MANAGEMENT | ZONE 1
ZONE 2
ZONE 3
ZONE 4
ZONE 5
ZONE 6
ZONE 7
ZONE 8
ZONE 9
ZONE 10
ZONE 11
ZONE 12
ZONE 13
ZONE 14
ZONE 15
ZONE 16
ZONE 17
ZONE 18
ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 4005 | 1518358 | 265884 | 3258
| Pole inspection and treatment | 3708 | 111168 | 6846758 | 380
| Overhead asset inspection | 151562 | 2401729 | 3183399 | 9839
| Network underground cable maintenance | 1255 | 544285 | 124862 | 16952
| Distribution substation equipment & property maintenance | 118517 | 460898 | 142888 | 25364
| Zone substation equipment maintenance | 585502 | 3521648 | 1269381 | 189420
| Zone substation property maintenance | 18072 | 379275 | 1226299 | 40880
| Public lighting maintenance | 0 | 0 | 0 | 0
| Scada & network control maintenance | 0 | 0 | 0 | 0
| Protection systems maintenance | 17466 | 1189666 | 322444 | 74913
| Subtransmission asset maintenance - for dnsps with dual function assets | 0 | 0 | 0 | 0
| Other | 449483 | 3198132 | 862709 | 122761
NON-ROUTINE MAINTENANCE | Pole top, overhead line & service line maintenance | 75345 | 2147432 | 182576 | 368113
| Pole inspection and treatment | 18738 | 106430 | 233461 | 15757
| Overhead asset inspection | 42714 | 125277 | 9617 | 3629
| Network underground cable maintenance | 130148 | 358591 | 84939 | 16588
| Distribution substation equipment & property maintenance | 17202 | 214273 | 297757 | 24283
| Zone substation equipment maintenance | 84433 | 1182415 | 498191 | 89329
| Zone substation property maintenance | 295212 | 791238 | 1210516 | 56137
| Public lighting maintenance | 0 | 0 | 0 | 0
| SCADA & network control maintenance | 944 | 37466 | 168803 | 4404
| Protection systems maintenance | 287 | 93316 | 7165 | 4193
| Subtransmission asset maintenance - for DNSP with dual function assets | 0 | 0 | 0 | 0
| Other | 110116 | 1949746 | 3887879 | 102471
OVERHEADS | Network overheads | 2697333 | 56566888 | 11067181 | 28194678
| Corporate overheads | 543400 | 56474585 | 214223 | 60200749
AUGMENTATION | Subtransmission substations, switching stations, zone substations | 6673711 | 20358665 | 6337011 | 2041965
| Subtransmission lines | 766650 | 1078119 | 169499 | 62126
| HV feeders | 6737881 | 10327819 | 9733500 | 1497438
| Distribution substations | 179354 | 271474 | 94405 | 37807
| LV feeders | 467703 | 707925 | 246180 | 98588
| Other assets | 0 | 0 | 0 | 0
CONNECTIONS | Simple and complex customer connections | 28384736 | 45884559 | 21719471 | 2487985
EMERGENCY RESPONSE | Major storms | 2244989 | 28187508 | 11805349 | 2354077
| Major event days | 0 | 0 | 0 | 0
PUBLIC LIGHTING | All public lighting services | 2901716 | 3880530 | 5638981 | 547052
METERING | All metering services | 278 | 883676 | 3782836 | 4449
FEE-BASED SERVICES | All fee-based services | 1992377 | 9376123 | 4749395 | 630188
QUOTED SERVICES | All quoted services | 2571750 | 12102651 | 6130493 | 813444
REPLACEMENT | Poles | 10476189 | 5299287 | 10422407 | 1487053
| Pole top structures | 15392819 | 5989294 | 2772595 | 1869384
| Overhead conductors | 4421028 | 1827658 | 3846384 | 427016
| Underground cables | 4588599 | 2590897 | 3847750 | 289507
| Service lines | 5119991 | 1649110 | 1457380 | 535697
| Transformers | 6033892 | 5388216 | 2395521 | 565320
| Switchgear | 12821999 | 14824049 | 9134190 | 661211
| Public lighting | 0 | 0 | 0 | 0 | 0 | 0
| SCADA network control and protection systems | 3790928 | 12246602 | 2906577 | 409467
| Other | 1949058 | 2635810 | 2002236 | 119025
NON-NETWORK EXPENDITURE | IT and communications | 2736299 | 26114489 | (114,424) | 52505508
| Motor vehicles | 37976176 | 4580526 | 6583265 | 2302864
| Buildings and property | 59862 | 1687033 | 1847725 | 16874613
| Other | 2693288 | 8131475 | (1,213,715) | 7678547
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 4.1 Public lighting
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
4.1 PUBLIC LIGHTING
TEMPLATE DATE - MAY 2024
There are THREE tables on this worksheet. Each has been grouped for ease of navigation.
4.1.1 - DESCRIPTOR METRICS OVER YEAR
VOLUME 0's
| LIGHT TYPE |  | 2023-24
POPULATION OF LIGHTS | Council Floodlights CLER |  | 31
| Council Floodlights SLUoS |  | 600
| Council Lights CLER |  | 4469
| Council Lights Energy Only |  | 14285
| Council Lights SLUoS |  | 58572
| Council Lights PLC |  | 74053
| Council Lights TFI |  | 3441
| Council Lights SAPN |  | 53934
DIT Floodlights CLER
| DIT Floodlights SLUoS |  | 7
| DIT Lights CLER |  | 13506
| DIT Lights PLC |  | 4257
| DIT Lights SAPN |  | 2902
| DIT Lights SLUoS |  | 6534
| Private Lights CLER |  | 42
| Private Floodlights SECHID |  | 906
| Private Lights SLUoS |  | 190
| Private Lights SAPN |  | 111
| Private Lights Energy |  | 122
| Private Floodlights SECLED |  | 42
| DIT Lights Energy Only |  | 5991
| DIT SLO Reporting |  | 2267
| DIT Lights TFI |  | 21
| Council SLO Reporting |  | 263
| Council Floodlights Energy Only |  | 15
| Council Floodlights PLC |  | 45
| Council Floodlights SAPN |  | 15
| Private Floodlights SLUoS |  | 16
| Council Floodlights SECHID |  | 10
| Council Floodlights SECLED |  | 5
4.1.2 - DESCRIPTOR METRICS ANNUALLY
VOLUMES & EXPENDITURE
SERVICE/SERVICE QUALITY | DESCRIPTOR METRIC | UNITS | 2023-24
LIGHT INSTALLATION | Major road light installation | 0's | 346
| Minor road light installation | 0's | 295
| Number of poles installed | 0's | 67
| Total cost | $0s | 1816012.93
LIGHT REPLACEMENT | Major road light replacement | 0's | 819
| Minor road light replacement | 0's | 2419
| Number of poles replaced | 0's | 71
| Total cost | $0s | 4724618.42
LIGHT MAINTENANCE | Major road light maintenance | 0's | 12442
| Minor road light maintenance | 0's | 14499
| Number of poles installed | 0's | 95
| Total cost | $0s | 9682944.71
QUALITY OF SUPPLY | Mean days to rectify/replace public lighting assets | days | 14
| GSO breaches | 0's | 4775
| GSL payments | $0s | 561175
| Customer complaints | 0's | 235
4.1.3 - COST METRICS
AVERAGE UNIT COST ($)
ACTIVITY TYPE | LIGHT TYPE |  | 2023-24
LIGHT INSTALLATION | LED17 |  | 677.95
| LED24 |  | 777.57
| LED60 |  | 1978.54
| LED80 |  | 2027.13
| LED150 |  | 2031.73
LIGHT REPLACEMENT | LED17 |  | 296
| LED80 |  | 330
| F42 |  | 262
| LED29 |  | 156
| S100 |  | 176
| LED150 |  | 400
| LED60 |  | 442
| LED22 |  | 256
| S150 |  | 314
LED100
| LED105 |  | 954
LED120
| S250 |  | 249
| M80 |  | 167
| S360F |  | 660
| S50 |  | 432
| F40 |  | 982
LED117
| LED198 |  | 828
| LED23 |  | 356
L55
| L90 |  | 301
LED20
| LED34 |  | 242
M125
| S400F |  | 458
| LED24 |  | 225
| M250 |  | 1048
L135
| L18 |  | 194
| L26 |  | 373
| MH250 |  | 1048
| S400 |  | 179
| LED35 |  | 253
| S70 |  | 105
| MH100 |  | 482
| LED42 |  | 384
| LED165 |  | 52
| LED180 F |  | 689
| M250 F |  | 59
LIGHT MAINTENANCE | LED17 |  | 219
| F42 |  | 184
| S50 |  | 172
| M80 |  | 254
| S100 |  | 162
| S150 |  | 167
| LED80 |  | 254
| S250 |  | 162
| F40 |  | 292
| M250 |  | 296
| LED29 |  | 277
| L90 |  | 197
| L18 |  | 226
| M50 |  | 240
| LED150 |  | 178
| LED22 |  | 209
| M400 |  | 328
| L26 |  | 363
LED60
| LED105 |  | 228
| LED100 |  | 152
| L55 |  | 244
| LED120 |  | 148
| S360 F |  | 348
| LED198 |  | 158
| S70 |  | 171
| L135 |  | 146
| F14X2 |  | 117
| S400 |  | 288
| M400 F |  | 233
| MH250 |  | 346
| M1000 F |  | 694
| LED23 |  | 175
| MH400 |  | 602
LED30
| MH150 |  | 379
M125
| MH100 |  | 482
| LED117 |  | 362
| LED165 |  | 52
| LED35 |  | 152
LED175
| LED24 |  | 215
F40X2
| LED72 |  | 351
M100
| M250 F |  | 59
F8X2
M400x2
| LED34 |  | 212
| LED42 |  | 384
| S400 F |  | 601
| M1000 F |  | 135
| LED180 F |  | 87
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 4.2 Metering
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
4.2 METERING
TEMPLATE DATE - MAY 2024
There are TWO tables on this worksheet. Each has been grouped for ease of navigation.
4.2.1 - METERING DESCRIPTOR METRIC
VOLUMES 0's
Asset Category | Asset Subcategory | 2023-24
Meter Type 4 | Single phase meter population | 0
| Multi phase meter population | 0
| Current transformer connected meter population | 0
| Direct connect meter population | 0
Meter Type 5 | Single phase meter population | 199
| Multi phase meter population | 4872
| Current transformer connected meter population | 2283
| Direct connect meter population | 2788
Meter Type 6 | Single phase meter population | 487045
| Multi phase meter population | 109690
| Current transformer connected meter population | 48
| Direct connect meter population | 596687
4.2.2 - COST METRICS
|  | VOLUMES 0's | EXPENDITURE $
Service Subcategory | Meter Type | 2023-24 | 2023-24
Meter purchase | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter testing | Meter Type 4 | 0 | 0
| Meter Type 5 | 92 | 21362
| Meter Type 6 | 2788 | 1209709
Meter investigation | Meter Type 4 | 196 | 50183
| Meter Type 5 | 23 | 5786
| Meter Type 6 | 1002 | 246482
Scheduled meter reading | Meter Type 4
Meter Type 5
Meter Type 6
Special meter reading | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
New meter installation | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter replacement | Meter Type 4 | 0 | 0
| Meter Type 5 | 0 | 0
| Meter Type 6 | 0 | 0
Meter maintenance | Meter Type 4 | 874 | 514306
| Meter Type 5 | 0 | 740
| Meter Type 6 | 0 | 0
Remote meter reading | Meter Type 4 | 0 | 0
Remote meter re-configuration | Meter Type 4 | 0 | 0
Other metering | Meter Type 4
| Meter Type 5 |  | 6980
| Meter Type 6 |  | 821338
Meter Type 7
IT infrastructure capex | Meter Type 4 |  | 0
IT infrastructure opex | Meter Type 4 |  | 0
Communications infrastructure capex | Meter Type 4 |  | 0
Communications infrastructure opex | Meter Type 4 |  | 0
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 4.3 Fee-based services
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
4.3 ANCILLARY SERVICES - FEE BASED SERVICES
TEMPLATE DATE - MAY 2024
4.3.1 - COST METRICS FOR FEE-BASED SERVICES
|  | EXPENDITURE $ |  | VOLUMES 0's
SERVICE | SERVICE SUBCATEGORY | 2023-24 |  | 2023-24
Common Fee-Based Services | Energisation | 0 | ED_FEE431_00001 | 0
| De-energisation | 0 | ED_FEE431_00002 | 0
| Re-energisation | 0 | ED_FEE431_00003 | 0
Miscellaneous Fee-Based Services | Access Permits, oversight and facilitation - Standard Charge Network Access Permit (8am - 3pm) | 970236 | ED_FEE431_00004 | 1028
| Access Permits, oversight and facilitation - Standard NAP Extended daytime hours (6am - 6pm) (Weekdays) | 241892 | ED_FEE431_00005 | 140
| Access Permits, oversight and facilitation - Emergency NAP / Weekends / Night shift | 258719 | ED_FEE431_00006 | 107
| Access Permits, oversight and facilitation - Network access management fee - cancellation | 14943 | ED_FEE431_00007 | 34
| Network safety services - Temporary line covering (eg tiger tails) | 189209 | ED_FEE431_00008 | 179
| Inspection and auditing services - Site Inspection | 0 | ED_FEE431_00009 | 0
| Inspection and auditing services - Re-inspection for compliance | 977583 | ED_FEE431_00010 | 2803
| Inspection and auditing services - Re-inspection for compliance > 3hrs | 0 | ED_FEE431_00011 | 0
| Inspection and auditing services - Re-inspection for compliance - after hours | 0 | ED_FEE431_00012 | 0
| Security Lighting - HID <=400W | 193730 | ED_FEE431_00013 | 826
| Security Lighting - HID >400W | 36588 | ED_FEE431_00014 | 156
| Security Lighting - LED <=200W | 0 | ED_FEE431_00015 | 45
| Security Lighting - LED >200W | 0 | ED_FEE431_00016 | 0
| Location of underground mains - provision of plans from office | 5776 | ED_FEE431_00017 | 45
| Asset information request | 0 | ED_FEE431_00018 | 0
| Asset info request - Ground level transformers (site visit to open and visually see equipment) | 0 | ED_FEE431_00019 | 0
| Swing & Sag Calculations up to 11kV | 22320 | ED_FEE431_00020 | 11
| Swing & Sag Calculations > 11kV | 8115 | ED_FEE431_00021 | 3
| Meter test - single phase | 28983 | ED_FEE431_00022 | 275
| Meter test - additional single-phase meter | 0 | ED_FEE431_00023 | 0
| Meter test - three-phase | 0 | ED_FEE431_00024 | 0
| Meter test - additional three phase meter | 0 | ED_FEE431_00025 | 0
| Priority or out of hour appointment - less than 3 hours | 264402 | ED_FEE431_00026 | 1385
| Charge for Meter Test (where an appointment has been requested by the customer's retailer) where SAPN is MC | 0 | ED_FEE431_00027 | 0
| Meter inspection fee | 18941 | ED_FEE431_00028 | 401
| Meter inspection fee - each additional meter | 0 | ED_FEE431_00029 | 0
| Meter Inspection Fee (where an appointment has been requested by the customer's retailer) | 0 | ED_FEE431_00030 | 0
| Special meter read visit - normal hours | 440414 | ED_FEE431_00031 | 34310
| Special meter read visit - after hours | 0 | ED_FEE431_00032 | 0
| Special Read / Disco / Reco - Cancellation | 150543 | ED_FEE431_00033 | 14918
| Meter read - subsequent attempt | 0 | ED_FEE431_00034 | 0
| Permanent abolishment of LV service | 1801336 | ED_FEE431_00035 | 2977
| Retailer fee - disconnection & reconnection - Disconnection at meter | 1407920 | ED_FEE431_00036 | 36826
| Retailer fee - disconnection & reconnection - reconnection at meter | 3754968 | ED_FEE431_00037 | 98234
| Retailer fee - disconnection & reconnection - reconnect meter after hours | 666127 | ED_FEE431_00038 | 7785
| Retailer fee - disconnection & reconnection O/head - truck attendance | 949736 | ED_FEE431_00039 | 1246
| Third party requested outage for purpose of replacing a meter | 614233 | ED_FEE431_00040 | 2089
| Temporary supply -overhead or underground on existing pole | 108760 | ED_FEE431_00041 | 87
| Temporary supply - Existing pit/pillar | 25703 | ED_FEE431_00042 | 51
| Temporary disconnect and reconnect - customer requested - truck attendance | 287987 | ED_FEE431_00043 | 346
| Temporary disconnect and reconnect - customer requested - single person crew | 540858 | ED_FEE431_00044 | 2034
| Connections specification fee - $0-$200k project | 348952 | ED_FEE431_00045 | 147
| Connections specification fee - >$200k project | 129904 | ED_FEE431_00046 | 31
| Excess kVAr incentive | 0 | ED_FEE431_00047 | 280
| Solar installation enquiry - single phase | 0 | ED_FEE431_00048 | 0
| Solar installation enquiry - three-phase | 0 | ED_FEE431_00049 | 0
| Alter/relocate/replace of overhead/underground service | 1361285 | ED_FEE431_00050 | 877
| Multiphase upgrade - O/under or O/head | 707998 | ED_FEE431_00051 | 679
| Multiphase upgrade - existing service pit/pillar | 73586 | ED_FEE431_00052 | 113
| Additional service for a duplex split (existing metered strata title split into two Torrens titles, no additional load) | 12579 | ED_FEE431_00053 | 8
| Embedded generation firm offer - >30kW-200kW | 1093168 | ED_FEE431_00054 | 192
ED_FEE431_00055
ED_FEE431_00056
ED_FEE431_00057
ED_FEE431_00058
ED_FEE431_00059
ED_FEE431_00060
ED_FEE431_00061
ED_FEE431_00062
ED_FEE431_00063
ED_FEE431_00064
ED_FEE431_00065
ED_FEE431_00066
ED_FEE431_00067
ED_FEE431_00068
ED_FEE431_00069
ED_FEE431_00070
ED_FEE431_00071
ED_FEE431_00072
ED_FEE431_00073
ED_FEE431_00074
ED_FEE431_00075
ED_FEE431_00076
ED_FEE431_00077
ED_FEE431_00078
ED_FEE431_00079
ED_FEE431_00080
ED_FEE431_00081
ED_FEE431_00082
ED_FEE431_00083
ED_FEE431_00084
ED_FEE431_00085
ED_FEE431_00086
ED_FEE431_00087
ED_FEE431_00088
ED_FEE431_00089
ED_FEE431_00090
ED_FEE431_00091
ED_FEE431_00092
ED_FEE431_00093
ED_FEE431_00094
ED_FEE431_00095
ED_FEE431_00096
ED_FEE431_00097
ED_FEE431_00098
ED_FEE431_00099
ED_FEE431_00100
ED_FEE431_00101
ED_FEE431_00102
ED_FEE431_00103
ED_FEE431_00104
ED_FEE431_00105
ED_FEE431_00106
ED_FEE431_00107
ED_FEE431_00108
ED_FEE431_00109
ED_FEE431_00110
ED_FEE431_00111
ED_FEE431_00112
ED_FEE431_00113
ED_FEE431_00114
ED_FEE431_00115
ED_FEE431_00116
ED_FEE431_00117
ED_FEE431_00118
ED_FEE431_00119
ED_FEE431_00120
ED_FEE431_00121
ED_FEE431_00122
ED_FEE431_00123
ED_FEE431_00124
ED_FEE431_00125
ED_FEE431_00126
ED_FEE431_00127
ED_FEE431_00128
ED_FEE431_00129
ED_FEE431_00130
ED_FEE431_00131
ED_FEE431_00132
ED_FEE431_00133
ED_FEE431_00134
ED_FEE431_00135
ED_FEE431_00136
ED_FEE431_00137
ED_FEE431_00138
ED_FEE431_00139
ED_FEE431_00140
ED_FEE431_00141
ED_FEE431_00142
ED_FEE431_00143
ED_FEE431_00144
ED_FEE431_00145
ED_FEE431_00146
ED_FEE431_00147
ED_FEE431_00148
ED_FEE431_00149
ED_FEE431_00150
ED_FEE431_00151
ED_FEE431_00152
ED_FEE431_00153
ED_FEE431_00154
ED_FEE431_00155
ED_FEE431_00156
ED_FEE431_00157
ED_FEE431_00158
ED_FEE431_00159
ED_FEE431_00160
ED_FEE431_00161
ED_FEE431_00162
ED_FEE431_00163
ED_FEE431_00164
ED_FEE431_00165
ED_FEE431_00166
ED_FEE431_00167
ED_FEE431_00168
ED_FEE431_00169
ED_FEE431_00170
ED_FEE431_00171
ED_FEE431_00172
ED_FEE431_00173
ED_FEE431_00174
ED_FEE431_00175
ED_FEE431_00176
ED_FEE431_00177
ED_FEE431_00178
ED_FEE431_00179
ED_FEE431_00180
ED_FEE431_00181
ED_FEE431_00182
ED_FEE431_00183
ED_FEE431_00184
ED_FEE431_00185
ED_FEE431_00186
ED_FEE431_00187
ED_FEE431_00188
ED_FEE431_00189
ED_FEE431_00190
ED_FEE431_00191
ED_FEE431_00192
ED_FEE431_00193
ED_FEE431_00194
ED_FEE431_00195
ED_FEE431_00196
ED_FEE431_00197
ED_FEE431_00198
ED_FEE431_00199
ED_FEE431_00200
ED_FEE431_00201
ED_FEE431_00202
ED_FEE431_00203
ED_FEE431_00204
ED_FEE431_00205
ED_FEE431_00206
ED_FEE431_00207
ED_FEE431_00208
ED_FEE431_00209
ED_FEE431_00210
ED_FEE431_00211
ED_FEE431_00212
ED_FEE431_00213
ED_FEE431_00214
ED_FEE431_00215
ED_FEE431_00216
ED_FEE431_00217
ED_FEE431_00218
ED_FEE431_00219
ED_FEE431_00220
ED_FEE431_00221
ED_FEE431_00222
ED_FEE431_00223
ED_FEE431_00224
ED_FEE431_00225
ED_FEE431_00226
ED_FEE431_00227
ED_FEE431_00228
ED_FEE431_00229
ED_FEE431_00230
ED_FEE431_00231
ED_FEE431_00232
ED_FEE431_00233
ED_FEE431_00234
ED_FEE431_00235
ED_FEE431_00236
ED_FEE431_00237
ED_FEE431_00238
ED_FEE431_00239
ED_FEE431_00240
ED_FEE431_00241
ED_FEE431_00242
ED_FEE431_00243
ED_FEE431_00244
ED_FEE431_00245
ED_FEE431_00246
ED_FEE431_00247
ED_FEE431_00248
ED_FEE431_00249
ED_FEE431_00250
ED_FEE431_00251
ED_FEE431_00252
ED_FEE431_00253
ED_FEE431_00254
ED_FEE431_00255
ED_FEE431_00256
ED_FEE431_00257
ED_FEE431_00258
ED_FEE431_00259
ED_FEE431_00260
ED_FEE431_00261
ED_FEE431_00262
ED_FEE431_00263
ED_FEE431_00264
ED_FEE431_00265
ED_FEE431_00266
ED_FEE431_00267
ED_FEE431_00268
ED_FEE431_00269
ED_FEE431_00270
ED_FEE431_00271
ED_FEE431_00272
ED_FEE431_00273
ED_FEE431_00274
ED_FEE431_00275
ED_FEE431_00276
ED_FEE431_00277
ED_FEE431_00278
ED_FEE431_00279
ED_FEE431_00280
ED_FEE431_00281
ED_FEE431_00282
ED_FEE431_00283
ED_FEE431_00284
ED_FEE431_00285
ED_FEE431_00286
ED_FEE431_00287
ED_FEE431_00288
ED_FEE431_00289
ED_FEE431_00290
ED_FEE431_00291
ED_FEE431_00292
ED_FEE431_00293
ED_FEE431_00294
ED_FEE431_00295
ED_FEE431_00296
ED_FEE431_00297
ED_FEE431_00298
ED_FEE431_00299
ED_FEE431_00300
ED_FEE431_00301
ED_FEE431_00302
ED_FEE431_00303
ED_FEE431_00304
ED_FEE431_00305
ED_FEE431_00306
ED_FEE431_00307
ED_FEE431_00308
ED_FEE431_00309
ED_FEE431_00310
ED_FEE431_00311
ED_FEE431_00312
ED_FEE431_00313
ED_FEE431_00314
ED_FEE431_00315
ED_FEE431_00316
ED_FEE431_00317
ED_FEE431_00318
ED_FEE431_00319
ED_FEE431_00320
ED_FEE431_00321
ED_FEE431_00322
ED_FEE431_00323
ED_FEE431_00324
ED_FEE431_00325
ED_FEE431_00326
ED_FEE431_00327
ED_FEE431_00328
ED_FEE431_00329
ED_FEE431_00330
ED_FEE431_00331
ED_FEE431_00332
ED_FEE431_00333
ED_FEE431_00334
ED_FEE431_00335
ED_FEE431_00336
ED_FEE431_00337
ED_FEE431_00338
ED_FEE431_00339
ED_FEE431_00340
ED_FEE431_00341
ED_FEE431_00342
ED_FEE431_00343
ED_FEE431_00344
ED_FEE431_00345
ED_FEE431_00346
ED_FEE431_00347
ED_FEE431_00348
ED_FEE431_00349
ED_FEE431_00350
ED_FEE431_00351
ED_FEE431_00352
ED_FEE431_00353
ED_FEE431_00354
ED_FEE431_00355
ED_FEE431_00356
ED_FEE431_00357
ED_FEE431_00358
ED_FEE431_00359
ED_FEE431_00360
ED_FEE431_00361
ED_FEE431_00362
ED_FEE431_00363
ED_FEE431_00364
ED_FEE431_00365
ED_FEE431_00366
ED_FEE431_00367
ED_FEE431_00368
ED_FEE431_00369
ED_FEE431_00370
ED_FEE431_00371
ED_FEE431_00372
ED_FEE431_00373
ED_FEE431_00374
ED_FEE431_00375
ED_FEE431_00376
ED_FEE431_00377
ED_FEE431_00378
ED_FEE431_00379
ED_FEE431_00380
ED_FEE431_00381
ED_FEE431_00382
ED_FEE431_00383
ED_FEE431_00384
ED_FEE431_00385
ED_FEE431_00386
ED_FEE431_00387
ED_FEE431_00388
ED_FEE431_00389
ED_FEE431_00390
ED_FEE431_00391
ED_FEE431_00392
ED_FEE431_00393
ED_FEE431_00394
ED_FEE431_00395
ED_FEE431_00396
ED_FEE431_00397
ED_FEE431_00398
ED_FEE431_00399
ED_FEE431_00400
ED_FEE431_00401
ED_FEE431_00402
ED_FEE431_00403
ED_FEE431_00404
ED_FEE431_00405
ED_FEE431_00406
ED_FEE431_00407
ED_FEE431_00408
ED_FEE431_00409
ED_FEE431_00410
ED_FEE431_00411
ED_FEE431_00412
ED_FEE431_00413
ED_FEE431_00414
ED_FEE431_00415
ED_FEE431_00416
ED_FEE431_00417
ED_FEE431_00418
ED_FEE431_00419
ED_FEE431_00420
ED_FEE431_00421
ED_FEE431_00422
ED_FEE431_00423
ED_FEE431_00424
ED_FEE431_00425
ED_FEE431_00426
ED_FEE431_00427
ED_FEE431_00428
ED_FEE431_00429
ED_FEE431_00430
ED_FEE431_00431
ED_FEE431_00432
ED_FEE431_00433
ED_FEE431_00434
ED_FEE431_00435
ED_FEE431_00436
ED_FEE431_00437
ED_FEE431_00438
ED_FEE431_00439
ED_FEE431_00440
ED_FEE431_00441
ED_FEE431_00442
ED_FEE431_00443
ED_FEE431_00444
ED_FEE431_00445
ED_FEE431_00446
ED_FEE431_00447
ED_FEE431_00448
ED_FEE431_00449
ED_FEE431_00450
ED_FEE431_00451
ED_FEE431_00452
ED_FEE431_00453
ED_FEE431_00454
ED_FEE431_00455
ED_FEE431_00456
ED_FEE431_00457
ED_FEE431_00458
ED_FEE431_00459
ED_FEE431_00460
ED_FEE431_00461
ED_FEE431_00462
ED_FEE431_00463
ED_FEE431_00464
ED_FEE431_00465
ED_FEE431_00466
ED_FEE431_00467
ED_FEE431_00468
ED_FEE431_00469
ED_FEE431_00470
ED_FEE431_00471
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 4.4 Quoted services
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
4.4 ANCILLARY SERVICES - QUOTED SERVICES
TEMPLATE DATE - MAY 2024
4.4.1 - COST METRICS FOR QUOTED SERVICES
|  | EXPENDITURE $ |  | VOLUMES 0's
SERVICE | SERVICE SUBCATEGORY | 2023-24 |  | 2023-24
Quoted Services | Network access request - complex | 1351929 | ED_QUO441_00001 | 685
| High Load Escorts | 445087 | ED_QUO441_00002 | 200
| Works & Design Compliance | 385183 | ED_QUO441_00003 | 251
| Specification re-compliance | 0 | ED_QUO441_00004 | 0
| Security light installation / upgrade | 26120 | ED_QUO441_00005 | 8
| Location of underground mains at the request of a customer | 2127 | ED_QUO441_00006 | 4
| Other data requests | 4733 | ED_QUO441_00007 | 0
| Meter reconfiguration | 0 | ED_QUO441_00008 | 0
| Charge for meter removal | 275 | ED_QUO441_00009 | 4
| Other metering services | 0 | ED_QUO441_00010 | 0
| Retailer fee - Temporary isolation of customer's LV supply >100Amp | 0 | ED_QUO441_00011 | 0
| Retailer Initiated Alteration Bypass Fee - Urban | 11039 | ED_QUO441_00012 | 46
| Retailer Initiated Alteration Bypass Fee - Rural | 6662 | ED_QUO441_00013 | 20
| Temporary supply - New pole required | 0 | ED_QUO441_00014 | 0
| Temporary supply - New pit/pillar required | 0 | ED_QUO441_00015 | 0
| Temporary isolation of customer's LV supply >100Amp capacity | 0 | ED_QUO441_00016 | 0
| Wasted Visit - Meter Provider Non-Attendance | 0 | ED_QUO441_00017 | 0
| Wasted Visit - Scheduled Customer Connection Appointment | 114371 | ED_QUO441_00018 | 944
| Late Cancellation of Connection Appointment | 21460 | ED_QUO441_00019 | 339
| Embedded generation services | 4183882 | ED_QUO441_00020 | 289
| Asset relocation services | 14260361 | ED_QUO441_00021 | 366
| Back-up feeder charge | 0 | ED_QUO441_00022 | 114
| All other connections, no additional load | 3328 | ED_QUO441_00023 | 1
| Training | 102773 | ED_QUO441_00024 | 135
| Material Sales | 0 | ED_QUO441_00025 | 0
| Customer funded public light installations | 1937410 | ED_QUO441_00026 | 5396
ED_QUO441_00027
ED_QUO441_00028
ED_QUO441_00029
ED_QUO441_00030
ED_QUO441_00031
ED_QUO441_00032
ED_QUO441_00033
ED_QUO441_00034
ED_QUO441_00035
ED_QUO441_00036
ED_QUO441_00037
ED_QUO441_00038
ED_QUO441_00039
ED_QUO441_00040
ED_QUO441_00041
ED_QUO441_00042
ED_QUO441_00043
ED_QUO441_00044
ED_QUO441_00045
ED_QUO441_00046
ED_QUO441_00047
ED_QUO441_00048
ED_QUO441_00049
ED_QUO441_00050
ED_QUO441_00051
ED_QUO441_00052
ED_QUO441_00053
ED_QUO441_00054
ED_QUO441_00055
ED_QUO441_00056
ED_QUO441_00057
ED_QUO441_00058
ED_QUO441_00059
ED_QUO441_00060
ED_QUO441_00061
ED_QUO441_00062
ED_QUO441_00063
ED_QUO441_00064
ED_QUO441_00065
ED_QUO441_00066
ED_QUO441_00067
ED_QUO441_00068
ED_QUO441_00069
ED_QUO441_00070
ED_QUO441_00071
ED_QUO441_00072
ED_QUO441_00073
ED_QUO441_00074
ED_QUO441_00075
ED_QUO441_00076
ED_QUO441_00077
ED_QUO441_00078
ED_QUO441_00079
ED_QUO441_00080
ED_QUO441_00081
ED_QUO441_00082
ED_QUO441_00083
ED_QUO441_00084
ED_QUO441_00085
ED_QUO441_00086
ED_QUO441_00087
ED_QUO441_00088
ED_QUO441_00089
ED_QUO441_00090
ED_QUO441_00091
ED_QUO441_00092
ED_QUO441_00093
ED_QUO441_00094
ED_QUO441_00095
ED_QUO441_00096
ED_QUO441_00097
ED_QUO441_00098
ED_QUO441_00099
ED_QUO441_00100
ED_QUO441_00101
ED_QUO441_00102
ED_QUO441_00103
ED_QUO441_00104
ED_QUO441_00105
ED_QUO441_00106
ED_QUO441_00107
ED_QUO441_00108
ED_QUO441_00109
ED_QUO441_00110
ED_QUO441_00111
ED_QUO441_00112
ED_QUO441_00113
ED_QUO441_00114
ED_QUO441_00115
ED_QUO441_00116
ED_QUO441_00117
ED_QUO441_00118
ED_QUO441_00119
ED_QUO441_00120
ED_QUO441_00121
ED_QUO441_00122
ED_QUO441_00123
ED_QUO441_00124
ED_QUO441_00125
ED_QUO441_00126
ED_QUO441_00127
ED_QUO441_00128
ED_QUO441_00129
ED_QUO441_00130
ED_QUO441_00131
ED_QUO441_00132
ED_QUO441_00133
ED_QUO441_00134
ED_QUO441_00135
ED_QUO441_00136
ED_QUO441_00137
ED_QUO441_00138
ED_QUO441_00139
ED_QUO441_00140
ED_QUO441_00141
ED_QUO441_00142
ED_QUO441_00143
ED_QUO441_00144
ED_QUO441_00145
ED_QUO441_00146
ED_QUO441_00147
ED_QUO441_00148
ED_QUO441_00149
ED_QUO441_00150
ED_QUO441_00151
ED_QUO441_00152
ED_QUO441_00153
ED_QUO441_00154
ED_QUO441_00155
ED_QUO441_00156
ED_QUO441_00157
ED_QUO441_00158
ED_QUO441_00159
ED_QUO441_00160
ED_QUO441_00161
ED_QUO441_00162
ED_QUO441_00163
ED_QUO441_00164
ED_QUO441_00165
ED_QUO441_00166
ED_QUO441_00167
ED_QUO441_00168
ED_QUO441_00169
ED_QUO441_00170
ED_QUO441_00171
ED_QUO441_00172
ED_QUO441_00173
ED_QUO441_00174
ED_QUO441_00175
ED_QUO441_00176
ED_QUO441_00177
ED_QUO441_00178
ED_QUO441_00179
ED_QUO441_00180
ED_QUO441_00181
ED_QUO441_00182
ED_QUO441_00183
ED_QUO441_00184
ED_QUO441_00185
ED_QUO441_00186
ED_QUO441_00187
ED_QUO441_00188
ED_QUO441_00189
ED_QUO441_00190
ED_QUO441_00191
ED_QUO441_00192
ED_QUO441_00193
ED_QUO441_00194
ED_QUO441_00195
ED_QUO441_00196
ED_QUO441_00197
ED_QUO441_00198
ED_QUO441_00199
ED_QUO441_00200
ED_QUO441_00201
ED_QUO441_00202
ED_QUO441_00203
ED_QUO441_00204
ED_QUO441_00205
ED_QUO441_00206
ED_QUO441_00207
ED_QUO441_00208
ED_QUO441_00209
ED_QUO441_00210
ED_QUO441_00211
ED_QUO441_00212
ED_QUO441_00213
ED_QUO441_00214
ED_QUO441_00215
ED_QUO441_00216
ED_QUO441_00217
ED_QUO441_00218
ED_QUO441_00219
ED_QUO441_00220
ED_QUO441_00221
ED_QUO441_00222
ED_QUO441_00223
ED_QUO441_00224
ED_QUO441_00225
ED_QUO441_00226
ED_QUO441_00227
ED_QUO441_00228
ED_QUO441_00229
ED_QUO441_00230
ED_QUO441_00231
ED_QUO441_00232
ED_QUO441_00233
ED_QUO441_00234
ED_QUO441_00235
ED_QUO441_00236
ED_QUO441_00237
ED_QUO441_00238
ED_QUO441_00239
ED_QUO441_00240
ED_QUO441_00241
ED_QUO441_00242
ED_QUO441_00243
ED_QUO441_00244
ED_QUO441_00245
ED_QUO441_00246
ED_QUO441_00247
ED_QUO441_00248
ED_QUO441_00249
ED_QUO441_00250
ED_QUO441_00251
ED_QUO441_00252
ED_QUO441_00253
ED_QUO441_00254
ED_QUO441_00255
ED_QUO441_00256
ED_QUO441_00257
ED_QUO441_00258
ED_QUO441_00259
ED_QUO441_00260
ED_QUO441_00261
ED_QUO441_00262
ED_QUO441_00263
ED_QUO441_00264
ED_QUO441_00265
ED_QUO441_00266
ED_QUO441_00267
ED_QUO441_00268
ED_QUO441_00269
ED_QUO441_00270
ED_QUO441_00271
ED_QUO441_00272
ED_QUO441_00273
ED_QUO441_00274
ED_QUO441_00275
ED_QUO441_00276
ED_QUO441_00277
ED_QUO441_00278
ED_QUO441_00279
ED_QUO441_00280
ED_QUO441_00281
ED_QUO441_00282
ED_QUO441_00283
ED_QUO441_00284
ED_QUO441_00285
ED_QUO441_00286
ED_QUO441_00287
ED_QUO441_00288
ED_QUO441_00289
ED_QUO441_00290
ED_QUO441_00291
ED_QUO441_00292
ED_QUO441_00293
ED_QUO441_00294
ED_QUO441_00295
ED_QUO441_00296
ED_QUO441_00297
ED_QUO441_00298
ED_QUO441_00299
ED_QUO441_00300
ED_QUO441_00301
ED_QUO441_00302
ED_QUO441_00303
ED_QUO441_00304
ED_QUO441_00305
ED_QUO441_00306
ED_QUO441_00307
ED_QUO441_00308
ED_QUO441_00309
ED_QUO441_00310
ED_QUO441_00311
ED_QUO441_00312
ED_QUO441_00313
ED_QUO441_00314
ED_QUO441_00315
ED_QUO441_00316
ED_QUO441_00317
ED_QUO441_00318
ED_QUO441_00319
ED_QUO441_00320
ED_QUO441_00321
ED_QUO441_00322
ED_QUO441_00323
ED_QUO441_00324
ED_QUO441_00325
ED_QUO441_00326
ED_QUO441_00327
ED_QUO441_00328
ED_QUO441_00329
ED_QUO441_00330
ED_QUO441_00331
ED_QUO441_00332
ED_QUO441_00333
ED_QUO441_00334
ED_QUO441_00335
ED_QUO441_00336
ED_QUO441_00337
ED_QUO441_00338
ED_QUO441_00339
ED_QUO441_00340
ED_QUO441_00341
ED_QUO441_00342
ED_QUO441_00343
ED_QUO441_00344
ED_QUO441_00345
ED_QUO441_00346
ED_QUO441_00347
ED_QUO441_00348
ED_QUO441_00349
ED_QUO441_00350
ED_QUO441_00351
ED_QUO441_00352
ED_QUO441_00353
ED_QUO441_00354
ED_QUO441_00355
ED_QUO441_00356
ED_QUO441_00357
ED_QUO441_00358
ED_QUO441_00359
ED_QUO441_00360
ED_QUO441_00361
ED_QUO441_00362
ED_QUO441_00363
ED_QUO441_00364
ED_QUO441_00365
ED_QUO441_00366
ED_QUO441_00367
ED_QUO441_00368
ED_QUO441_00369
ED_QUO441_00370
ED_QUO441_00371
ED_QUO441_00372
ED_QUO441_00373
ED_QUO441_00374
ED_QUO441_00375
ED_QUO441_00376
ED_QUO441_00377
ED_QUO441_00378
ED_QUO441_00379
ED_QUO441_00380
ED_QUO441_00381
ED_QUO441_00382
ED_QUO441_00383
ED_QUO441_00384
ED_QUO441_00385
ED_QUO441_00386
ED_QUO441_00387
ED_QUO441_00388
ED_QUO441_00389
ED_QUO441_00390
ED_QUO441_00391
ED_QUO441_00392
ED_QUO441_00393
ED_QUO441_00394
ED_QUO441_00395
ED_QUO441_00396
ED_QUO441_00397
ED_QUO441_00398
ED_QUO441_00399
ED_QUO441_00400
ED_QUO441_00401
ED_QUO441_00402
ED_QUO441_00403
ED_QUO441_00404
ED_QUO441_00405
ED_QUO441_00406
ED_QUO441_00407
ED_QUO441_00408
ED_QUO441_00409
ED_QUO441_00410
ED_QUO441_00411
ED_QUO441_00412
ED_QUO441_00413
ED_QUO441_00414
ED_QUO441_00415
ED_QUO441_00416
ED_QUO441_00417
ED_QUO441_00418
ED_QUO441_00419
ED_QUO441_00420
ED_QUO441_00421
ED_QUO441_00422
ED_QUO441_00423
ED_QUO441_00424
ED_QUO441_00425
ED_QUO441_00426
ED_QUO441_00427
ED_QUO441_00428
ED_QUO441_00429
ED_QUO441_00430
ED_QUO441_00431
ED_QUO441_00432
ED_QUO441_00433
ED_QUO441_00434
ED_QUO441_00435
ED_QUO441_00436
ED_QUO441_00437
ED_QUO441_00438
ED_QUO441_00439
ED_QUO441_00440
ED_QUO441_00441
ED_QUO441_00442
ED_QUO441_00443
ED_QUO441_00444
ED_QUO441_00445
ED_QUO441_00446
ED_QUO441_00447
ED_QUO441_00448
ED_QUO441_00449
ED_QUO441_00450
ED_QUO441_00451
ED_QUO441_00452
ED_QUO441_00453
ED_QUO441_00454
ED_QUO441_00455
ED_QUO441_00456
ED_QUO441_00457
ED_QUO441_00458
ED_QUO441_00459
ED_QUO441_00460
ED_QUO441_00461
ED_QUO441_00462
ED_QUO441_00463
ED_QUO441_00464
ED_QUO441_00465
ED_QUO441_00466
ED_QUO441_00467
ED_QUO441_00468
ED_QUO441_00469
ED_QUO441_00470
ED_QUO441_00471
ED_QUO441_00472
ED_QUO441_00473
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 5.2 Asset Age Profile
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
5.2 ASSET AGE PROFILE
TEMPLATE DATE - MAY 2024
There is ONE table on this worksheet. Both the ROWS and COLUMNS have been 'grouped' for easy navigation. See the Instructions sheet on how to group or ungroup data.
5.2.1 - ASSET AGE PROFILE
|  | ECONOMIC LIFE (YEARS) |  | INSTALLED ASSETS -˃ QUANTITY CURRENTLY IN COMMISSION BY YEAR
ASSET GROUP | ASSET CATEGORY | MEAN | STANDARD DEVIATION | 2023-24 | 2022-23 | 2021-22 | 2020-21 | 2019-20 | 2018-19 | 2017-18 | 2016-17 | 2015-16 | 2014-15 | 2013-14 | 2012-13 | 2011-12 | 2010-11 | 2009-10 | 2008-09 | 2007-08 | 2006-07 | 2005-06 | 2004-05 | 2003-04 | 2002-03 | 2001-02 | 2000-01 | 1999-00 | 1998-99 | 1997-98 | 1996-97 | 1995-96 | 1994-95 | 1993-94 | 1992-93 | 1991-92 | 1990-91 | 1989-90 | 1988-89 | 1987-88 | 1986-87 | 1985-86 | 1984-85 | 1983-84 | 1982-83 | 1981-82 | 1980-81 | 1979-80 | 1978-79 | 1977-78 | 1976-77 | 1975-76 | 1974-75 | 1973-74 | 1972-73 | 1971-72 | 1970-71 | 1969-70 | 1968-69 | 1967-68 | 1966-67 | 1965-66 | 1964-65 | 1963-64 | 1962-63 | 1961-62 | 1960-61 | 1959-60 | 1958-59 | 1957-58 | 1956-57 | 1955-56 | 1954-55 | 1953-54 | 1952-53 | 1951-52 | 1950-51 | 1949-50 | 1948-49 | 1947-48 | 1946-47 | 1945-46 | 1944-45 | 1943-44 | 1942-43 | 1941-42 | 1940-41 | 1939-40 | 1938-39 | 1937-38 | 1936-37 | 1935-36 | 1934-35 | 1933-34 | 1932-33 | 1931-32 | 1930-31 | 1929-30 | 1928-29 | 1927-28 | 1926-27 | 1925-26 | 1924-25 | 1923-24 | 1922-23 | 1921-22 | 1920-21 | 1919-20 | 1918-19 | 1917-18 | 1916-17 | 1915-16 | 1914-15 | 1913-14 | 1912-13 | 1911-12 | 1910-11
POLES BY: HIGHEST OPERATING VOLTAGE; MATERIAL TYPE; STAKING (IF WOOD) | Staking of a wooden pole
˂ = 1 kV; Wood
> 1 kV & < = 11 kV; Wood
˃ 11 kV & < = 22 kV; Wood
> 22 kV & < = 66 kV; Wood
> 66 kV & < = 132 kV; Wood
> 132 kV; Wood
˂ = 1 kV; Concrete
> 1 kV & < = 11 kV; Concrete
˃ 11 kV & < = 22 kV; Concrete
> 22 kV & < = 66 kV; Concrete
> 66 kV & < = 132 kV; Concrete
> 132 kV; Concrete
˂ = 1 kV; Steel
> 1 kV & < = 11 kV; Steel
˃ 11 kV & < = 22 kV; Steel
> 22 kV & < = 66 kV; Steel
> 66 kV & < = 132 kV; Steel
> 132 kV; Steel
Other
OVERHEAD CONDUCTORS BY: HIGHEST OPERATING VOLTAGE; NUMBER OF PHASES (AT HV) | ˂ = 1 kV | 54.91 | 7.41 | 3.318 | 12.59 | 12.36 | 9.4 | 14.06 | 40.57 | 38 | 63 | 96 | 131 | 203 | 227 | 238 | 148 | 133 | 125 | 133 | 45 | 111 | 84 | 59 | 60 | 58 | 77 | 196 | 7 | 129 | 4 | 217 | 108 | 155 | 28 | 307 | 366 | 336 | 360 | 214 | 356 | 493 | 392 | 519 | 524 | 436 | 500 | 768 | 373 | 551 | 1115 | 784 | 1253 | 1138 | 1665 | 626 | 1588 | 2278 | 1046 | 3192 | 1177 | 2822 | 3314 | 3695 | 3483 | 3357 | 4291 | 3571 | 2638 | 2937 | 2584 | 1498 | 4989 | 2840 | 1413 | 563 | 26 | 113 | 19 | 26 | 198 | 149 | 207 | 73 | 128 | 135 | 125 | 741 | 432 | 394 | 409 | 308 | 432 | 145 | 34 | 11 | 1 | 2
| > 1 kV & < = 11 kV | 51.17 | 7.15 | 82.5035 | 69.5 | 146.45 | 129 | 84.9 | 66.38 | 45 | 64 | 42 | 100 | 125 | 54 | 78 | 181 | 132 | 107 | 186 | 56 | 144 | 89 | 56 | 82 | 68 | 84 | 296 | 4 | 406 | 4 | 496 | 210 | 486 | 35 | 576 | 410 | 520 | 543 | 375 | 472 | 595 | 444 | 528 | 449 | 468 | 718 | 1019 | 454 | 567 | 1110 | 852 | 959 | 1033 | 1238 | 634 | 1355 | 2145 | 1744 | 2813 | 1091 | 2023 | 2198 | 1753 | 2409 | 1969 | 2431 | 1776 | 1093 | 1175 | 1357 | 1277 | 3169 | 1340 | 797 | 262 | 9 | 134 | 2 | 10 | 105 | 68 | 74 | 32 | 33 | 33 | 46 | 258 | 87 | 98 | 90 | 68 | 89 | 32 | 10 | 3 | 1 | 1
| ˃ 11 kV & < = 22 kV ; SWER | 51.94 | 7.21 | 16.1 | 2.95 | 7.01 | 17 | 17.2 | 3.63 | 12 | 14 | 11 | 16 | 25 | 14 | 21 | 24 | 21 | 19 | 32 | 19 | 35 | 38 | 16 | 27 | 18 | 34 | 91 | 1 | 95 | 1 | 100 | 100 | 127 | 2 | 165 | 95 | 178 | 111 | 141 | 122 | 113 | 117 | 113 | 95 | 312 | 197 | 331 | 157 | 171 | 515 | 401 | 935 | 721 | 902 | 277 | 844 | 1751 | 959 | 2575 | 769 | 2032 | 1966 | 1911 | 2078 | 1871 | 1487 | 1297 | 1085 | 507 | 225 | 153 | 199 | 83 | 47 | 10 | 1 | 10 | 0 | 4 | 5 | 1 | 9 | 2 | 4 | 10 | 4 | 21 | 3 | 12 | 6 | 6 | 5 | 2 | 1 | 0 | 0 | 1
| ˃ 11 kV & < = 22 kV ; Single-Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˃ 11 kV & < = 22 kV ; Multiple-Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 66 kV | 51.18 | 7.15 | 7.4 | 46.56 | 13.4 | 3 | 50.19 | 0.53 | 15 | 27 | 11 | 14 | 39 | 16 | 15 | 125 | 86 | 79 | 71 | 32 | 24 | 49 | 87 | 24 | 23 | 24 | 152 | 1 | 196 | 5 | 210 | 52 | 79 | 1 | 223 | 188 | 209 | 92 | 67 | 147 | 176 | 193 | 153 | 72 | 22 | 90 | 154 | 50 | 48 | 301 | 634 | 510 | 56 | 531 | 147 | 257 | 524 | 283 | 518 | 216 | 821 | 795 | 843 | 774 | 383 | 970 | 602 | 393 | 214 | 405 | 402 | 824 | 390 | 190 | 88 | 49 | 20 | 0 | 6 | 79 | 47 | 73 | 23 | 54 | 53 | 35 | 114 | 67 | 44 | 28 | 12 | 20 | 79 | 5 | 1 | 0 | 0
| > 66 kV & < = 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UNDERGROUND CABLES BY: HIGHEST OPERATING VOLTAGE | ˂ = 1 kV | 24.77 | 4.98 | 1.1 | 1.33 | 1.37 | 2.16 | 2.56 | 5.08 | 272.16 | 22.45 | 53.24 | 251.98 | 364.11 | 380.49 | 461.42 | 612.4 | 637.37 | 796.36 | 477.17 | 456.06 | 915.35 | 690.39 | 394.87 | 283.94 | 472.93 | 247.04 | 324.35 | 256.99 | 265.13 | 149.47 | 250.82 | 387.12 | 447.45 | 343.91 | 433.79 | 369.18 | 282.7 | 250.35 | 236.94 | 350.37 | 408.34 | 309.07 | 139.48 | 132.62 | 108.86 | 121.48 | 94.48 | 175.99 | 289 | 270.12 | 281.22 | 203.35 | 73.54 | 55.07 | 31.45 | 26.13 | 27.84 | 5.89 | 12.29 | 8.83 | 12.52 | 11.48 | 5.84 | 9.03 | 1.12 | 0.41 | 11.07 | 0.63 | 1.36 | 0.94 | 47.71 | 68.63 | 0.04 | 0 | 0 | 0 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 1 kV & < = 11 kV | 25.24 | 5.02 | 11.17 | 12.97 | 6.89 | 5 | 2.33 | 3.09 | 43.74 | 13.53 | 22.81 | 59.52 | 78.98 | 72.46 | 102.8 | 173.16 | 132.79 | 143.61 | 90.13 | 111.58 | 180.21 | 172.03 | 124.95 | 110.36 | 115.35 | 101.43 | 111.32 | 147.23 | 108.74 | 341.03 | 132.11 | 164.65 | 89.74 | 103.88 | 291.72 | 124.16 | 79.69 | 57.65 | 59.46 | 48.31 | 177.75 | 42.11 | 16.56 | 8.27 | 4.55 | 27.16 | 2.86 | 1.87 | 2.9 | 3.77 | 70.77 | 0.59 | 258.67 | 0.47 | 1.77 | 1.47 | 50.79 | 0.21 | 2.51 | 0.09 | 1.53 | 2.53 | 0.26 | 0.05 | 0.12 | 0.15 | 0 | 0 | 0.07 | 0.26 | 0.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV | 52.36 | 7.24 | 0 | 0 | 0 | 0 | 0 | 0.09 | 1.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 0.74 | 0 | 3.5 | 0.1 | 0 | 1.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0.39 | 1.48 | 0.63 | 2.26 | 0.72 | 1.39 | 1.59 | 2.83 | 3.37 | 3.73 | 0.17 | 4.16 | 1.15 | 7.8 | 8.42 | 3.61 | 7.38 | 1.79 | 2.08 | 2.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV | 44.52 | 6.67 | 0 | 0 | 0 | 0 | 0.04 | 0.12 | 0.03 | 0 | 0.45 | 0.26 | 0.02 | 0.42 | 0 | 19.67 | 0.52 | 3.14 | 0.95 | 0.26 | 1.66 | 0 | 0.62 | 4.04 | 0 | 0 | 1.23 | 0.71 | 0.47 | 0 | 0.38 | 0 | 2.27 | 0 | 0 | 0.86 | 0.34 | 0 | 1.83 | 0.93 | 1.68 | 0 | 0.1 | 1.13 | 0 | 0 | 1.48 | 0 | 1.65 | 0 | 0.89 | 1.14 | 0 | 0 | 0 | 0.49 | 60.92 | 0.07 | 0.09 | 0.26 | 0.21 | 0.09 | 0 | 0.16 | 0.2 | 0 | 2.37 | 0 | 0 | 0.04 | 19.13 | 0 | 0 | 0.02 | 0 | 0.21 | 4.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV | 39.03 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.17 | 0 | 0 | 0 | 0 | 6.57 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0.09 | 0.41 | 0.05 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 0 | 0.08 | 2.84 | 0 | 0 | 17.48 | 0 | 0 | 0 | 0 | 0 | 0.41 | 0 | 1.03 | 0 | 0 | 4.68 | 0 | 3.7 | 0.66 | 0 | 0 | 0.33 | 0 | 1.87 | 0.12 | 5.99 | 0.27 | 1.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SERVICE LINES BY: CONNECTION VOLTAGE; CUSTOMER TYPE; CONNECTION COMPLEXITY | ˂ = 11 kV ; Residential ; Simple Type | 28.55 | 5.34 | 14114 | 12651 | 16060 | 15819 | 22223 | 28821 | 22773 | 18846 | 18759 | 13148 | 13315 | 5803 | 6454 | 7928 | 8539 | 8756 | 8607 | 8302 | 8357 | 8631 | 9607 | 11477 | 13145 | 14986 | 14238 | 11711 | 10625 | 10196 | 11618 | 14504 | 15997 | 16273 | 16491 | 15826 | 15392 | 15612 | 16043 | 16566 | 16276 | 16247 | 15054 | 12707 | 11648 | 10039 | 7843 | 6923 | 7564 | 11936 | 15690 | 15583 | 16689 | 14094 | 13375 | 6878 | 5972 | 5949 | 6744 | 6745 | 6723 | 3868 | 1895 | 1896 | 4775 | 3860 | 741 | 740 | 369 | 369 | 85 | 85 | 30 | 30 | 25 | 25 | 15 | 15 | 7 | 7 | 2 | 2 | 1 | 1 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Simple Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Residential ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 26.8 | 5.18 | 2002 | 1804 | 2055 | 1915 | 2508 | 3235 | 2658 | 2087 | 2160 | 1958 | 1709 | 901 | 864 | 844 | 831 | 868 | 891 | 909 | 956 | 922 | 1349 | 1740 | 2211 | 2454 | 2137 | 2025 | 1860 | 2012 | 2191 | 2126 | 1954 | 1909 | 1980 | 2048 | 2354 | 2413 | 2354 | 2505 | 2251 | 1849 | 1836 | 1854 | 1736 | 1608 | 1305 | 1070 | 1020 | 1111 | 1213 | 1197 | 1229 | 1100 | 1214 | 572 | 739 | 733 | 817 | 818 | 920 | 275 | 98 | 98 | 121 | 80 | 23 | 22 | 11 | 11 | 4 | 4 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Subdivision ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TRANSFORMERS BY: MOUNTING TYPE; HIGHEST OPERATING VOLTAGE; AMPERE RATING; NUMBER OF PHASES (AT LV) | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 32.48 | 5.7 | 147 | 142 | 226 | 284 | 212 | 234 | 724 | 269 | 205 | 235 | 539 | 444 | 469 | 578 | 511 | 531 | 473 | 535 | 505 | 528 | 485 | 462 | 586 | 492 | 613 | 607 | 432 | 557 | 547 | 759 | 1109 | 766 | 704 | 962 | 1080 | 743 | 763 | 766 | 728 | 768 | 704 | 859 | 729 | 710 | 653 | 622 | 553 | 448 | 514 | 679 | 458 | 406 | 411 | 393 | 638 | 447 | 348 | 292 | 352 | 351 | 310 | 329 | 404 | 205 | 191 | 153 | 19 | 3 | 4 | 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 59.46 | 7.71 | 3 | 2 | 2 | 3 | 11 | 5 | 16 | 12 | 6 | 3 | 9 | 13 | 29 | 22 | 22 | 21 | 12 | 15 | 16 | 14 | 11 | 11 | 9 | 22 | 12 | 18 | 6 | 7 | 8 | 7 | 25 | 8 | 6 | 17 | 9 | 7 | 10 | 12 | 13 | 8 | 8 | 4 | 6 | 7 | 3 | 8 | 2 | 5 | 3 | 8 | 7 | 2 | 1 | 5 | 0 | 4 | 8 | 2 | 4 | 2 | 5 | 3 | 4 | 0 | 3 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 12.04 | 3.47 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 34.7 | 5.89 | 8 | 15 | 21 | 12 | 9 | 23 | 92 | 32 | 18 | 22 | 33 | 40 | 63 | 60 | 44 | 82 | 62 | 67 | 97 | 82 | 86 | 96 | 97 | 154 | 225 | 226 | 179 | 155 | 159 | 228 | 248 | 239 | 235 | 306 | 368 | 284 | 207 | 229 | 210 | 233 | 220 | 214 | 279 | 243 | 222 | 190 | 187 | 159 | 189 | 202 | 158 | 170 | 104 | 111 | 129 | 126 | 76 | 64 | 67 | 65 | 47 | 41 | 23 | 13 | 7 | 6 | 3 | 11 | 14 | 9 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 25.38 | 5.04 | 117 | 189 | 189 | 180 | 113 | 156 | 495 | 156 | 64 | 98 | 349 | 364 | 438 | 517 | 680 | 614 | 586 | 570 | 593 | 536 | 519 | 498 | 369 | 796 | 411 | 358 | 293 | 247 | 150 | 288 | 281 | 307 | 274 | 320 | 369 | 303 | 293 | 325 | 271 | 317 | 300 | 294 | 331 | 226 | 222 | 176 | 188 | 167 | 153 | 172 | 139 | 122 | 103 | 117 | 92 | 98 | 76 | 76 | 70 | 74 | 50 | 36 | 13 | 6 | 4 | 7 | 4 | 4 | 16 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 24.78 | 4.98 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 30.57 | 5.53 | 1 | 3 | 1 | 7 | 7 | 1 | 2 | 0 | 0 | 1 | 4 | 2 | 11 | 6 | 1 | 3 | 11 | 7 | 14 | 9 | 3 | 9 | 11 | 4 | 5 | 18 | 7 | 10 | 10 | 27 | 17 | 23 | 15 | 32 | 19 | 27 | 19 | 54 | 75 | 23 | 15 | 6 | 2 | 8 | 3 | 11 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 29.63 | 5.44 | 2 | 0 | 0 | 0 | 0 | 0 | 14 | 1 | 0 | 0 | 2 | 2 | 0 | 2 | 10 | 3 | 0 | 2 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 2 | 4 | 6 | 2 | 2 | 9 | 1 | 4 | 25 | 18 | 8 | 9 | 0 | 0 | 6 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 14 | 3.74 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 28.63 | 5.35 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 0 | 1 | 0 | 1 | 2 | 2 | 1 | 2 | 3 | 1 | 8 | 5 | 2 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 26.2 | 5.12 | 11 | 150 | 189 | 226 | 151 | 203 | 214 | 48 | 7 | 107 | 228 | 234 | 354 | 342 | 392 | 412 | 349 | 296 | 425 | 308 | 266 | 249 | 283 | 191 | 191 | 208 | 244 | 220 | 134 | 257 | 309 | 268 | 311 | 305 | 330 | 325 | 246 | 293 | 440 | 370 | 246 | 148 | 165 | 132 | 125 | 133 | 210 | 237 | 195 | 161 | 90 | 51 | 27 | 19 | 5 | 4 | 3 | 3 | 10 | 7 | 1 | 6 | 3 | 1 | 2 | 0 | 0 | 1 | 3 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 20.59 | 4.54 | 2 | 62 | 85 | 72 | 90 | 75 | 45 | 18 | 1 | 18 | 36 | 68 | 87 | 76 | 72 | 64 | 82 | 80 | 94 | 75 | 63 | 63 | 51 | 55 | 67 | 71 | 60 | 57 | 37 | 43 | 34 | 39 | 54 | 33 | 40 | 21 | 22 | 25 | 42 | 28 | 7 | 10 | 20 | 7 | 7 | 7 | 5 | 8 | 0 | 2 | 4 | 1 | 2 | 2 | 1 | 3 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 59.46 | 7.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 59.46 | 7.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 62.61 | 7.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 4 | 2 | 0 | 2 | 0 | 4 | 1 | 2 | 1 | 2 | 2 | 3 | 0 | 2 | 2 | 2 | 0 | 8 | 1 | 1 | 1 | 3 | 1 | 2 | 5 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 62.61 | 7.91 | 4 | 0 | 3 | 1 | 2 | 4 | 7 | 10 | 8 | 6 | 2 | 7 | 12 | 7 | 6 | 3 | 2 | 4 | 1 | 2 | 5 | 3 | 10 | 8 | 0 | 0 | 3 | 0 | 1 | 0 | 1 | 0 | 11 | 1 | 3 | 0 | 17 | 0 | 7 | 0 | 9 | 14 | 0 | 0 | 1 | 3 | 0 | 3 | 5 | 10 | 0 | 1 | 0 | 3 | 15 | 2 | 1 | 11 | 7 | 0 | 2 | 5 | 3 | 2 | 0 | 2 | 5 | 1 | 4 | 2 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 62.61 | 7.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 62.61 | 7.91 | 2 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 4 | 3 | 1 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 1 | 2 | 1 | 2 | 4 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 9 | 6 | 3 | 7 | 5 | 4 | 16 | 5 | 12 | 4 | 0 | 2 | 2 | 0 | 2 | 4 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 61.28 | 7.83 | 3 | 0 | 1 | 1 | 5 | 1 | 1 | 0 | 0 | 3 | 5 | 1 | 11 | 4 | 4 | 5 | 2 | 4 | 2 | 6 | 2 | 5 | 4 | 4 | 0 | 1 | 0 | 0 | 2 | 0 | 3 | 0 | 2 | 4 | 1 | 3 | 0 | 1 | 4 | 0 | 2 | 3 | 2 | 0 | 4 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 6 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SWITCHGEAR BY: HIGHEST OPERATING VOLTAGE; SWITCH FUNCTION | ˂ = 11 kV ; Fuse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Switch | 77.16 | 8.78 | 22 | 6 | 2 | 3 | 13 | 31 | 10 | 21 | 6 | 0 | 18 | 38 | 20 | 6 | 12 | 16 | 13 | 3 | 2 | 1 | 4 | 0 | 4 | 1 | 0 | 0 | 0 | 1 | 13 | 6 | 0 | 0 | 10 | 7 | 1 | 9 | 3 | 19 | 0 | 21 | 25 | 20 | 11 | 15 | 20 | 2 | 28 | 18 | 29 | 9 | 5 | 60 | 31 | 86 | 120 | 80 | 79 | 92 | 117 | 19 | 37 | 9 | 0 | 2 | 4 | 5 | 4 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ˂ = 11 kV ; Circuit Breaker | 51.65 | 7.19 | 9 | 18 | 12 | 24 | 8 | 20 | 49 | 7 | 20 | 27 | 28 | 64 | 134 | 35 | 20 | 32 | 10 | 32 | 13 | 12 | 17 | 29 | 31 | 8 | 4 | 32 | 11 | 10 | 0 | 0 | 6 | 4 | 9 | 20 | 28 | 0 | 26 | 0 | 31 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 38 | 41 | 40 | 28 | 11 | 76 | 64 | 2 | 78 | 6 | 0 | 0 | 0 | 0 | 6 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Switch | 37.89 | 6.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 11 kV & < = 22 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Switch | 74.62 | 8.64 | 34 | 31 | 12 | 10 | 9 | 62 | 5 | 22 | 18 | 7 | 58 | 48 | 35 | 34 | 39 | 19 | 1 | 11 | 17 | 15 | 14 | 7 | 5 | 12 | 4 | 0 | 0 | 1 | 8 | 8 | 0 | 3 | 23 | 12 | 0 | 5 | 0 | 7 | 3 | 4 | 10 | 5 | 7 | 11 | 21 | 13 | 1 | 0 | 4 | 2 | 16 | 24 | 6 | 6 | 7 | 76 | 39 | 60 | 48 | 20 | 11 | 4 | 0 | 0 | 0 | 0 | 22 | 8 | 26 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; Circuit Breaker | 59.48 | 7.71 | 1 | 0 | 7 | 0 | 3 | 17 | 11 | 0 | 11 | 1 | 11 | 20 | 20 | 14 | 8 | 5 | 5 | 8 | 7 | 11 | 7 | 7 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 0 | 0 | 1 | 2 | 0 | 9 | 0 | 2 | 19 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Switch | 74.62 | 8.64 | 33 | 12 | 9 | 1 | 4 | 10 | 5 | 1 | 19 | 35 | 58 | 70 | 75 | 79 | 69 | 25 | 24 | 17 | 22 | 13 | 7 | 20 | 20 | 12 | 3 | 2 | 13 | 0 | 12 | 0 | 0 | 0 | 17 | 13 | 4 | 2 | 25 | 9 | 4 | 6 | 21 | 5 | 0 | 0 | 8 | 4 | 10 | 18 | 6 | 3 | 0 | 12 | 21 | 77 | 68 | 36 | 46 | 41 | 99 | 34 | 59 | 22 | 22 | 4 | 0 | 30 | 31 | 0 | 32 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 33 kV & < = 66 kV ; Circuit Breaker | 60.84 | 7.8 | 23 | 5 | 8 | 2 | 10 | 8 | 8 | 9 | 8 | 10 | 11 | 14 | 40 | 40 | 30 | 15 | 23 | 16 | 18 | 12 | 2 | 12 | 10 | 8 | 5 | 2 | 6 | 1 | 2 | 1 | 0 | 0 | 2 | 8 | 0 | 13 | 6 | 4 | 2 | 12 | 11 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 8 | 19 | 6 | 2 | 1 | 0 | 13 | 4 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 3 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 66 kV & < = 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PUBLIC LIGHTING BY: ASSET TYPE; LIGHTING OBLIGATION | Luminaires ; Major Road
Luminaires ; Minor Road
Brackets ; Major Road
Brackets ; Minor Road
Lamps ; Major Road
Lamps ; Minor Road
Poles / Columns ; Major Road
Poles / Columns ; Minor Road
Other
SCADA, NETWORK CONTROL AND PROTECTION SYSTEMS BY: FUNCTION | Field Devices | 28.52 | 7.57 | 352 | 251 | 136 | 118 | 143 | 161 | 159 | 140 | 126 | 152 | 187 | 204 | 220 | 199 | 151 | 106 | 73 | 70 | 57 | 53 | 55 | 51 | 39 | 33 | 35 | 28 | 28 | 20 | 16 | 22 | 26 | 71 | 106 | 117 | 114 | 109 | 105 | 78 | 63 | 67 | 65 | 54 | 40 | 23 | 18 | 26 | 36 | 35 | 39 | 37 | 30 | 42 | 64 | 85 | 80 | 77 | 76 | 47 | 45 | 56 | 54 | 43 | 20 | 9 | 16 | 22 | 24 | 17 | 8 | 5 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Local Network Wiring Assets
| Communications Network Assets | 10 | 3.2 | 317 | 170 | 384 | 1069 | 837 | 168 | 154 | 142 | 156 | 124 | 115 | 131 | 124 | 103 | 129 | 72 | 63 | 240 | 188 | 42 | 35 | 0 | 18 | 0 | 0 | 1 | 12 | 0 | 3 | 14 | 3 | 24 | 1 | 2 | 4 | 0 | 0 | 0 | 7 | 1 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Master Station Assets | 13.26 | 6.93 | 26 | 18 | 14 | 1 | 16 | 30 | 10 | 9 | 12 | 33 | 23 | 22 | 14 | 8 | 18 | 18 | 16 | 24 | 34 | 29 | 28 | 14 | 22 | 0 | 16
| Communications Site Infrastructure | 25 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 7 | 1 | 5 | 8 | 5 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 4 | 1 | 7 | 0 | 3 | 1 | 1 | 0 | 0 | 6 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Communications Linear Assets | 32.5 | 5.7 | 24.45 | 34.7 | 44.17 | 10.16 | 4.45 | 6.7 | 6.67 | 17.89 | 117.51 | 92.93 | 91.68 | 210.03 | 203.94 | 183.9 | 177.16 | 171.12 | 157.9 | 178.8 | 152.2 | 148.37 | 161.4 | 90.8 | 82.03 | 26.63 | 25.21 | 23.31 | 24.55 | 8.74 | 1.46 | 2.91 | 4.37 | 4.37 | 7.28 | 26.22 | 4.37 | 7.28 | 5.83 | 5.83 | 2.91 | 2.91 | 11.65 | 8.74 | 10.2 | 2.91 | 5.83 | 17.48 | 17.48 | 13.11 | 8.74 | 1.46 | 0 | 1.46 | 15.95 | 29.13 | 28.63 | 17.05 | 19.91 | 13.11 | 28.25 | 7.28 | 1.46 | 13.11 | 0 | 7.28 | 0 | 1.46 | 7.28 | 5.83 | 11.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AFLC
Other
OTHER BY: DNSP DEFINED | < = 1 kV; stobie pole | 55.88 | 7.48 | 414 | 411 | 338 | 380 | 212 | 418 | 569 | 1074 | 68 | 65 | 90 | 99 | 44 | 84 | 64 | 56 | 724 | 280 | 677 | 419 | 277 | 405 | 311 | 513 | 1317 | 44 | 558 | 30 | 1202 | 553 | 743 | 22 | 1549 | 1787 | 1461 | 1576 | 875 | 1446 | 1719 | 1621 | 2263 | 1863 | 1426 | 2097 | 2430 | 1545 | 1770 | 3369 | 2820 | 3826 | 3503 | 5542 | 1931 | 5368 | 6418 | 3411 | 8373 | 3637 | 7673 | 9077 | 10588 | 9837 | 9464 | 12630 | 9923 | 8473 | 9790 | 7997 | 3296 | 13151 | 7397 | 4015 | 1516 | 39 | 347 | 51 | 81 | 398 | 377 | 538 | 201 | 165 | 373 | 399 | 1980 | 1183 | 1076 | 1101 | 849 | 1241 | 333 | 79 | 35 | 3 | 5
| > 1 kV & < = 11 kV; stobie pole | 48.57 | 6.97 | 340 | 128 | 264 | 361 | 637 | 1704 | 1037 | 677 | 1694 | 1824 | 1941 | 2124 | 882 | 456 | 352 | 436 | 1091 | 371 | 811 | 664 | 431 | 480 | 457 | 566 | 1688 | 40 | 1726 | 32 | 1982 | 1031 | 2016 | 24 | 3040 | 2074 | 2749 | 2757 | 1704 | 2556 | 3398 | 2560 | 3091 | 2595 | 2367 | 2945 | 4384 | 2107 | 2635 | 4687 | 3899 | 4518 | 4787 | 5787 | 2431 | 6401 | 7166 | 4829 | 10247 | 3321 | 7314 | 7268 | 6823 | 7092 | 6701 | 7166 | 5879 | 3258 | 3444 | 3887 | 2740 | 8598 | 4225 | 2185 | 781 | 30 | 357 | 13 | 33 | 383 | 249 | 267 | 123 | 94 | 153 | 156 | 950 | 435 | 430 | 427 | 329 | 429 | 158 | 41 | 9 | 2 | 7
| > 11 kV & < = 22 kV; stobie pole | 51.77 | 7.2 | 170 | 81 | 148 | 11 | 99 | 198 | 321 | 282 | 227 | 232 | 178 | 179 | 99 | 57 | 60 | 74 | 253 | 130 | 210 | 204 | 115 | 167 | 110 | 199 | 495 | 13 | 409 | 17 | 681 | 581 | 739 | 15 | 1075 | 658 | 898 | 981 | 539 | 907 | 909 | 742 | 771 | 685 | 1133 | 1029 | 1453 | 526 | 874 | 1994 | 1943 | 3543 | 2609 | 3674 | 1079 | 3458 | 5838 | 3546 | 8814 | 2583 | 6422 | 7013 | 6400 | 6089 | 5938 | 4797 | 3881 | 3325 | 1863 | 647 | 376 | 390 | 191 | 103 | 23 | 3 | 26 | 1 | 5 | 10 | 3 | 25 | 3 | 8 | 15 | 10 | 42 | 9 | 29 | 10 | 12 | 10 | 5 | 3 | 0 | 0 | 2
| > 22 kV & < = 66 kV; stobie pole | 51.7 | 7.19 | 23 | 13 | 31 | 96 | 19 | 50 | 52 | 36 | 15 | 36 | 35 | 26 | 108 | 39 | 17 | 29 | 248 | 112 | 80 | 136 | 207 | 102 | 81 | 112 | 413 | 9 | 549 | 251 | 228 | 143 | 329 | 6 | 578 | 576 | 410 | 444 | 213 | 541 | 567 | 532 | 408 | 209 | 104 | 516 | 435 | 143 | 199 | 947 | 881 | 467 | 213 | 851 | 372 | 559 | 1115 | 822 | 1514 | 762 | 1569 | 1638 | 1784 | 1576 | 828 | 1594 | 1127 | 748 | 481 | 927 | 794 | 1526 | 776 | 400 | 163 | 58 | 42 | 0 | 13 | 72 | 205 | 199 | 33 | 63 | 107 | 64 | 214 | 134 | 90 | 62 | 43 | 63 | 85 | 16 | 1 | 0 | 0
| > 66 kV & < = 132 kV; stobie pole | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 132 kV; stobie pole | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole REFURBISHED; STOBIE Pole | 6.32 | 2.51 | 3579 | 5157 | 4669 | 3560 | 3148 | 2818 | 6112 | 4102 | 2676 | 3717 | 2563 | 3210 | 3005 | 1811 | 917 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ;> = 22 kV & < = 33 kV ; < = 60kVA | 27.74 | 5.27 | 15 | 19 | 13 | 22 | 17 | 18 | 39 | 5 | 9 | 6 | 26 | 17 | 48 | 42 | 29 | 25 | 17 | 19 | 29 | 20 | 23 | 21 | 26 | 19 | 23 | 30 | 21 | 18 | 33 | 44 | 19 | 32 | 35 | 23 | 39 | 29 | 19 | 40 | 18 | 23 | 24 | 24 | 19 | 22 | 10 | 14 | 10 | 15 | 16 | 9 | 12 | 9 | 7 | 12 | 30 | 7 | 16 | 26 | 5 | 8 | 8 | 17 | 3 | 2 | 4 | 0 | 5 | 14 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ;> = 22 kV & < = 33 kV ; > 60 KVA AND < = 600 KVA | 23.97 | 4.9 | 5 | 12 | 9 | 11 | 1 | 7 | 36 | 13 | 3 | 3 | 16 | 22 | 20 | 26 | 27 | 14 | 23 | 19 | 20 | 8 | 17 | 18 | 19 | 10 | 18 | 11 | 5 | 11 | 12 | 24 | 14 | 23 | 25 | 9 | 7 | 14 | 9 | 5 | 5 | 10 | 10 | 4 | 6 | 6 | 7 | 3 | 3 | 3 | 2 | 3 | 7 | 2 | 2 | 3 | 3 | 3 | 1 | 1 | 3 | 6 | 6 | 1 | 0 | 2 | 1 | 1 | 4 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pole Mounted ; > = 22 kV & < = 33 kV ; > 600 kVA | 20.83 | 4.56 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Kiosk Mounted; > = 22 kV & < = 33 kV ; | 16.68 | 4.08 | 0 | 1 | 2 | 12 | 5 | 0 | 2 | 1 | 0 | 2 | 4 | 0 | 2 | 0 | 6 | 4 | 3 | 3 | 2 | 9 | 2 | 4 | 3 | 2 | 6 | 8 | 4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Voltage Regulator: TRANSFORMER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Recloser ;SWITCHGEAR | 9.36 | 3.06 | 147 | 110 | 102 | 110 | 96 | 123 | 174 | 136 | 126 | 120 | 71 | 64 | 45 | 9 | 12 | 11 | 2 | 4 | 26 | 14 | 7 | 1 | 2 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sectionalizer ;SWITCHGEAR | 23.88 | 4.89 | 8 | 38 | 54 | 51 | 34 | 2 | 0 | 26 | 11 | 5 | 21 | 14 | 42 | 24 | 20 | 14 | 14 | 18 | 11 | 28 | 17 | 1 | 13 | 6 | 3 | 2 | 9 | 20 | 17 | 15 | 17 | 9 | 18 | 21 | 17 | 7 | 16 | 25 | 18 | 3 | 6 | 2 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| >= 11 kV & < = 22 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR | 12.96 | 3.6 | 65 | 241 | 314 | 300 | 278 | 313 | 320 | 301 | 285 | 270 | 344 | 272 | 408 | 490 | 447 | 443 | 433 | 335 | 539 | 321 | 285 | 250 | 146 | 47 | 23 | 74 | 52 | 346 | 2 | 2 | 0 | 0 | 383 | 6 | 1 | 5 | 1 | 3 | 117 | 0 | 0 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 54 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 1 | 1 | 3 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| > 22 kV & < = 33 kV ; LOAD BREAK SWITCH; GROUND LEVEL (Switching Cubicle);SWITCHGEAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pipework Switchyard Substations | 51 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 2 | 4 | 3 | 3 | 3 | 3 | 10 | 3 | 1 | 2 | 1 | 2 | 0 | 0 | 1 | 1 | 2 | 3 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 5.3 MD - Network level
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
5.3 MAXIMUM DEMAND AT NETWORK LEVEL
TEMPLATE DATE - MAY 2024
5.3.1 - RAW AND WEATHER CORRECTED COINCIDENT MD AT NETWORK LEVEL (Summed at transmission connection point)
| UNIT | 2023-24
Raw network coincident MD | MW | 2437
Date MD occurred |  | 11/03/2024
Half hour time period MD occurred |  | 19:00:00
Winter/summer peaking |  | Summer
Embedded generation | MW | 98
Weather corrected (10% POE) network coincident MD | MW | 3127
Weather corrected (50% POE) network coincident MD | MW | 2838
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 5.4 MD & utilisation-Spatial
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
5.4 MAXIMUM DEMAND AND UTILISATION AT SPATIAL LEVEL
TEMPLATE DATE - MAY 2024
There is ONE table on this worksheet. It has two sub-tables based on the Network Level. Each sub-table has been grouped for ease of navigation. See the Instructions sheet on how to group or ungroup data.
5.4.1 NON-COINCIDENT & COINCIDENT MAXIMUM DEMAND
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2023-24
SUBTRANSMISSION SUBSTATION | ACR 66kV | Substation Rating | MVA | Non-Coincident | 525
|  |  |  | Coincident | 525
|  | Raw Adjusted MD | MW | Non-Coincident | 173.049
|  |  |  | Coincident | 107.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 176.193
|  |  |  | Coincident | 107.771
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 7.4
|  |  |  | Coincident | 0.628
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 200.071
|  |  |  | Coincident | 123.951
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 203.706
|  |  |  | Coincident | 124.599
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 185.174
|  |  |  | Coincident | 114.722
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 188.538
|  |  |  | Coincident | 115.322
| Angas Creek 33kV | Substation Rating | MVA | Non-Coincident | 53.9
|  |  |  | Coincident | 53.9
|  | Raw Adjusted MD | MW | Non-Coincident | 17.221
|  |  |  | Coincident | 15.85
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.606
|  |  |  | Coincident | 16.143
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.002
|  |  |  | Coincident | 1.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.661
|  |  |  | Coincident | 16.255
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.056
|  |  |  | Coincident | 16.556
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.916
|  |  |  | Coincident | 14.649
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.272
|  |  |  | Coincident | 14.92
| Ardrossan West 33kV | Substation Rating | MVA | Non-Coincident | 62
|  |  |  | Coincident | 62
|  | Raw Adjusted MD | MW | Non-Coincident | 12.118
|  |  |  | Coincident | 11.899
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.212
|  |  |  | Coincident | 11.995
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.244
|  |  |  | Coincident | 0.547
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.562
|  |  |  | Coincident | 9.389
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.636
|  |  |  | Coincident | 9.465
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.441
|  |  |  | Coincident | 8.288
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.506
|  |  |  | Coincident | 8.355
| Baroota 33kV | Substation Rating | MVA | Non-Coincident | 11.8
|  |  |  | Coincident | 11.8
|  | Raw Adjusted MD | MW | Non-Coincident | 7.32
|  |  |  | Coincident | 2.084
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.332
|  |  |  | Coincident | 2.124
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 5.332
|  |  |  | Coincident | 4.73
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.763
|  |  |  | Coincident | 6.099
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.778
|  |  |  | Coincident | 6.217
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.942
|  |  |  | Coincident | 5.528
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.956
|  |  |  | Coincident | 5.635
| Berri 66kV | Substation Rating | MVA | Non-Coincident | 190
|  |  |  | Coincident | 190
|  | Raw Adjusted MD | MW | Non-Coincident | 88.8
|  |  |  | Coincident | 79.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 91.373
|  |  |  | Coincident | 82.096
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 7.3
|  |  |  | Coincident | 3.313
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 89.073
|  |  |  | Coincident | 79.674
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 91.654
|  |  |  | Coincident | 82.349
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 81.427
|  |  |  | Coincident | 72.835
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 83.787
|  |  |  | Coincident | 75.28
| Blanche 33kV | Substation Rating | MVA | Non-Coincident | 126.3
|  |  |  | Coincident | 126.3
|  | Raw Adjusted MD | MW | Non-Coincident | 32.19
|  |  |  | Coincident | 32.19
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.658
|  |  |  | Coincident | 33.658
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.025
|  |  |  | Coincident | 1.025
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.197
|  |  |  | Coincident | 35.197
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.802
|  |  |  | Coincident | 36.802
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.157
|  |  |  | Coincident | 32.157
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.624
|  |  |  | Coincident | 33.624
| Brinkworth 33kV | Substation Rating | MVA | Non-Coincident | 24.6
|  |  |  | Coincident | 24.6
|  | Raw Adjusted MD | MW | Non-Coincident | 4.419
|  |  |  | Coincident | 3.96
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.471
|  |  |  | Coincident | 4.039
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.097
|  |  |  | Coincident | 0.216
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.884
|  |  |  | Coincident | 4.376
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.941
|  |  |  | Coincident | 4.463
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.465
|  |  |  | Coincident | 4.001
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.517
|  |  |  | Coincident | 4.081
| Clare North 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 10.726
|  |  |  | Coincident | 9.942
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.896
|  |  |  | Coincident | 10.134
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.321
|  |  |  | Coincident | 0.467
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.682
|  |  |  | Coincident | 11.755
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.884
|  |  |  | Coincident | 11.982
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.608
|  |  |  | Coincident | 10.76
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.793
|  |  |  | Coincident | 10.968
| Dalrymple 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 7.206
|  |  |  | Coincident | 5.566
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.224
|  |  |  | Coincident | 5.572
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.4
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.134
|  |  |  | Coincident | 5.51
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.151
|  |  |  | Coincident | 5.516
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.407
|  |  |  | Coincident | 4.949
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.422
|  |  |  | Coincident | 4.954
| Davenport West 33kV | Substation Rating | MVA | Non-Coincident | 120
|  |  |  | Coincident | 120
|  | Raw Adjusted MD | MW | Non-Coincident | 27.711
|  |  |  | Coincident | 22.892
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.246
|  |  |  | Coincident | 23.491
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.826
|  |  |  | Coincident | 1.196
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.501
|  |  |  | Coincident | 26.849
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 33.129
|  |  |  | Coincident | 27.551
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.029
|  |  |  | Coincident | 23.981
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.59
|  |  |  | Coincident | 24.609
| Dorrien 33kV | Substation Rating | MVA | Non-Coincident | 216
|  |  |  | Coincident | 216
|  | Raw Adjusted MD | MW | Non-Coincident | 55.638
|  |  |  | Coincident | 48.351
|  | Raw Adjusted MD | MVA | Non-Coincident | 58.449
|  |  |  | Coincident | 50.255
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.903
|  |  |  | Coincident | 4.031
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 63.695
|  |  |  | Coincident | 57.523
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 66.913
|  |  |  | Coincident | 59.788
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 57.429
|  |  |  | Coincident | 51.865
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 60.331
|  |  |  | Coincident | 53.907
| Florieton SWER 19kV | Substation Rating | MVA | Non-Coincident | 0.15
|  |  |  | Coincident | 0.15
|  | Raw Adjusted MD | MW | Non-Coincident | 0.031
|  |  |  | Coincident | 0.021
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.064
|  |  |  | Coincident | 0.06
|  | Date MD occurred |  | Non-Coincident | 20/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.029
|  |  |  | Coincident | 0.02
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.061
|  |  |  | Coincident | 0.057
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.028
|  |  |  | Coincident | 0.019
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.057
|  |  |  | Coincident | 0.054
| Hummocks 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 12.498
|  |  |  | Coincident | 7.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.267
|  |  |  | Coincident | 7.478
|  | Date MD occurred |  | Non-Coincident | 08/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.207
|  |  |  | Coincident | 5.118
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.679
|  |  |  | Coincident | 13.113
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.582
|  |  |  | Coincident | 13.832
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.402
|  |  |  | Coincident | 11.973
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.227
|  |  |  | Coincident | 12.629
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Kadina East 33kV | Substation Rating | MVA | Non-Coincident | 120
|  |  |  | Coincident | 120
|  | Raw Adjusted MD | MW | Non-Coincident | 25.527
|  |  |  | Coincident | 21.769
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.215
|  |  |  | Coincident | 22.792
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.966
|  |  |  | Coincident | 2.889
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.414
|  |  |  | Coincident | 26.797
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.207
|  |  |  | Coincident | 28.056
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.148
|  |  |  | Coincident | 23.822
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.853
|  |  |  | Coincident | 24.941
| Kanmantoo 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.448
|  |  |  | Coincident | 1.226
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.46
|  |  |  | Coincident | 1.226
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.108
|  |  |  | Coincident | 0.091
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.405
|  |  |  | Coincident | 1.189
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.417
|  |  |  | Coincident | 1.189
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.271
|  |  |  | Coincident | 1.076
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.282
|  |  |  | Coincident | 1.076
| Keith 33kV | Substation Rating | MVA | Non-Coincident | 58.9
|  |  |  | Coincident | 58.9
|  | Raw Adjusted MD | MW | Non-Coincident | 15.83
|  |  |  | Coincident | 13.961
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.109
|  |  |  | Coincident | 14.391
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 6.294
|  |  |  | Coincident | 1.347
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.251
|  |  |  | Coincident | 17.969
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.887
|  |  |  | Coincident | 18.522
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.496
|  |  |  | Coincident | 16.411
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.99
|  |  |  | Coincident | 16.916
| Kincraig 33kV | Substation Rating | MVA | Non-Coincident | 51.6
|  |  |  | Coincident | 51.6
|  | Raw Adjusted MD | MW | Non-Coincident | 16.362
|  |  |  | Coincident | 15.526
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.637
|  |  |  | Coincident | 15.702
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.761
|  |  |  | Coincident | 0.639
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.963
|  |  |  | Coincident | 18.943
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.299
|  |  |  | Coincident | 19.158
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.872
|  |  |  | Coincident | 16.959
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.173
|  |  |  | Coincident | 17.151
| Leigh Creek South 33kV | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 0.852
|  |  |  | Coincident | 0.495
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.857
|  |  |  | Coincident | 0.547
|  | Date MD occurred |  | Non-Coincident | 06/12/2023
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.082
|  |  |  | Coincident | 0.034
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.042
|  |  |  | Coincident | 0.605
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.048
|  |  |  | Coincident | 0.669
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.95
|  |  |  | Coincident | 0.552
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.955
|  |  |  | Coincident | 0.61
| Mannum 33kV | Substation Rating | MVA | Non-Coincident | 40
|  |  |  | Coincident | 40
|  | Raw Adjusted MD | MW | Non-Coincident | 12.802
|  |  |  | Coincident | 12.656
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.917
|  |  |  | Coincident | 12.757
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.498
|  |  |  | Coincident | 0.674
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.042
|  |  |  | Coincident | 12.979
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.159
|  |  |  | Coincident | 13.083
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.772
|  |  |  | Coincident | 11.715
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.878
|  |  |  | Coincident | 11.809
| Metro East 66kV | Substation Rating | MVA | Non-Coincident | 1650
|  |  |  | Coincident | 1650
|  | Raw Adjusted MD | MW | Non-Coincident | 607.553
|  |  |  | Coincident | 543.836
|  | Raw Adjusted MD | MVA | Non-Coincident | 630.321
|  |  |  | Coincident | 554.361
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 73.618
|  |  |  | Coincident | 20.361
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 654.741
|  |  |  | Coincident | 583.039
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 679.277
|  |  |  | Coincident | 594.324
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 602.523
|  |  |  | Coincident | 536.54
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 625.102
|  |  |  | Coincident | 546.924
| Metro North 66kV | Substation Rating | MVA | Non-Coincident | 870
|  |  |  | Coincident | 870
|  | Raw Adjusted MD | MW | Non-Coincident | 289.571
|  |  |  | Coincident | 254.345
|  | Raw Adjusted MD | MVA | Non-Coincident | 291.511
|  |  |  | Coincident | 255.776
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 68.673
|  |  |  | Coincident | 20.493
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 340.809
|  |  |  | Coincident | 292.18
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 343.092
|  |  |  | Coincident | 293.824
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 319.743
|  |  |  | Coincident | 274.12
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 321.885
|  |  |  | Coincident | 275.663
| Metro South 66kV | Substation Rating | MVA | Non-Coincident | 1527
|  |  |  | Coincident | 1527
|  | Raw Adjusted MD | MW | Non-Coincident | 541.991
|  |  |  | Coincident | 541.991
|  | Raw Adjusted MD | MVA | Non-Coincident | 542.072
|  |  |  | Coincident | 548.673
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 88.192
|  |  |  | Coincident | 54.328
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 675.422
|  |  |  | Coincident | 657.395
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 675.523
|  |  |  | Coincident | 665.499
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 601.443
|  |  |  | Coincident | 585.39
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 601.533
|  |  |  | Coincident | 592.607
| Metro West 66kV | Substation Rating | MVA | Non-Coincident | 885
|  |  |  | Coincident | 885
|  | Raw Adjusted MD | MW | Non-Coincident | 366.016
|  |  |  | Coincident | 343.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 367.08
|  |  |  | Coincident | 356.485
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 43.169
|  |  |  | Coincident | 13.052
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 435.554
|  |  |  | Coincident | 409.229
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 436.82
|  |  |  | Coincident | 425.256
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 393.715
|  |  |  | Coincident | 369.919
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 394.859
|  |  |  | Coincident | 384.406
| Mobilong 33kV | Substation Rating | MVA | Non-Coincident | 114.3
|  |  |  | Coincident | 114.3
|  | Raw Adjusted MD | MW | Non-Coincident | 34.999
|  |  |  | Coincident | 30.885
|  | Raw Adjusted MD | MVA | Non-Coincident | 36.188
|  |  |  | Coincident | 31.76
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.737
|  |  |  | Coincident | 1.68
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.136
|  |  |  | Coincident | 32.017
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.364
|  |  |  | Coincident | 32.924
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.017
|  |  |  | Coincident | 29.254
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 34.139
|  |  |  | Coincident | 30.083
| Mount Barker 66kV | Substation Rating | MVA | Non-Coincident | 361.6
|  |  |  | Coincident | 361.6
|  | Raw Adjusted MD | MW | Non-Coincident | 87.593
|  |  |  | Coincident | 82.699
|  | Raw Adjusted MD | MVA | Non-Coincident | 89.541
|  |  |  | Coincident | 84.39
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 5.476
|  |  |  | Coincident | 5.476
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 94.693
|  |  |  | Coincident | 89.403
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 96.799
|  |  |  | Coincident | 91.231
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 83.336
|  |  |  | Coincident | 78.68
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 85.19
|  |  |  | Coincident | 80.289
| Mount Gambier 33kV | Substation Rating | MVA | Non-Coincident | 63.3
|  |  |  | Coincident | 63.3
|  | Raw Adjusted MD | MW | Non-Coincident | 20.482
|  |  |  | Coincident | 16.713
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.404
|  |  |  | Coincident | 17.005
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.141
|  |  |  | Coincident | 0.595
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.837
|  |  |  | Coincident | 18.634
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.865
|  |  |  | Coincident | 18.96
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.792
|  |  |  | Coincident | 16.966
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.728
|  |  |  | Coincident | 17.262
| Mount Gunson 33kV | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 0.095
|  |  |  | Coincident | 0.049
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.115
|  |  |  | Coincident | 0.221
|  | Date MD occurred |  | Non-Coincident | 03/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.074
|  |  |  | Coincident | 0.038
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.09
|  |  |  | Coincident | 0.173
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.067
|  |  |  | Coincident | 0.035
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.081
|  |  |  | Coincident | 0.156
| Neuroodla 33kV | Substation Rating | MVA | Non-Coincident | 10
|  |  |  | Coincident | 10
|  | Raw Adjusted MD | MW | Non-Coincident | 0.919
|  |  |  | Coincident | 0.772
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.929
|  |  |  | Coincident | 0.793
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.025
|  |  |  | Coincident | 0.025
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.056
|  |  |  | Coincident | 0.887
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.068
|  |  |  | Coincident | 0.911
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.949
|  |  |  | Coincident | 0.797
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.96
|  |  |  | Coincident | 0.819
| North West Bend 66kV | Substation Rating | MVA | Non-Coincident | 73.6
|  |  |  | Coincident | 73.6
|  | Raw Adjusted MD | MW | Non-Coincident | 20.529
|  |  |  | Coincident | 17.758
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.318
|  |  |  | Coincident | 18.493
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 0:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 1.21
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.689
|  |  |  | Coincident | 19.626
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.561
|  |  |  | Coincident | 20.438
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.462
|  |  |  | Coincident | 18.565
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.287
|  |  |  | Coincident | 19.333
| Penola West 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 8.068
|  |  |  | Coincident | 7.713
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.424
|  |  |  | Coincident | 8.055
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.084
|  |  |  | Coincident | 0.187
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.869
|  |  |  | Coincident | 7.523
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.217
|  |  |  | Coincident | 7.856
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.183
|  |  |  | Coincident | 6.867
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.501
|  |  |  | Coincident | 7.172
| Port Lincoln Terminal 33kV | Substation Rating | MVA | Non-Coincident | 101.4
|  |  |  | Coincident | 101.4
|  | Raw Adjusted MD | MW | Non-Coincident | 29.657
|  |  |  | Coincident | 26.388
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.892
|  |  |  | Coincident | 28.319
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.595
|  |  |  | Coincident | 1.33
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.236
|  |  |  | Coincident | 27.793
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.537
|  |  |  | Coincident | 29.827
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.028
|  |  |  | Coincident | 24.938
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.195
|  |  |  | Coincident | 26.763
| Port Pirie Bungama 33kV | Substation Rating | MVA | Non-Coincident | 192
|  |  |  | Coincident | 192
|  | Raw Adjusted MD | MW | Non-Coincident | 59.088
|  |  |  | Coincident | 49.606
|  | Raw Adjusted MD | MVA | Non-Coincident | 59.781
|  |  |  | Coincident | 50.48
|  | Date MD occurred |  | Non-Coincident | 12/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.578
|  |  |  | Coincident | 2.428
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 58.515
|  |  |  | Coincident | 49.125
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.201
|  |  |  | Coincident | 49.99
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 55.247
|  |  |  | Coincident | 46.382
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 55.895
|  |  |  | Coincident | 47.199
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Snuggery Rural 33kV | Substation Rating | MVA | Non-Coincident | 28.8
|  |  |  | Coincident | 28.8
|  | Raw Adjusted MD | MW | Non-Coincident | 11.673
|  |  |  | Coincident | 11.673
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.743
|  |  |  | Coincident | 11.743
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.583
|  |  |  | Coincident | 0.583
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.781
|  |  |  | Coincident | 13.781
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.864
|  |  |  | Coincident | 13.864
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.361
|  |  |  | Coincident | 12.361
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.435
|  |  |  | Coincident | 12.435
| Stony Point 11kV | Substation Rating | MVA | Non-Coincident | 2.5
|  |  |  | Coincident | 2.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.121
|  |  |  | Coincident | 0.095
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.123
|  |  |  | Coincident | 0.095
|  | Date MD occurred |  | Non-Coincident | 12/12/2023
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.004
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.138
|  |  |  | Coincident | 0.108
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.14
|  |  |  | Coincident | 0.108
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.129
|  |  |  | Coincident | 0.102
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.132
|  |  |  | Coincident | 0.102
| Tailem Bend 33kV | Substation Rating | MVA | Non-Coincident | 60
|  |  |  | Coincident | 60
|  | Raw Adjusted MD | MW | Non-Coincident | 24.202
|  |  |  | Coincident | 22.324
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.795
|  |  |  | Coincident | 23.656
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.238
|  |  |  | Coincident | 2.601
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.906
|  |  |  | Coincident | 23.7
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 24.491
|  |  |  | Coincident | 25.114
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.524
|  |  |  | Coincident | 22.33
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.076
|  |  |  | Coincident | 23.663
| Templers 33kV | Substation Rating | MVA | Non-Coincident | 147.6
|  |  |  | Coincident | 147.6
|  | Raw Adjusted MD | MW | Non-Coincident | 28.531
|  |  |  | Coincident | 26.652
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.063
|  |  |  | Coincident | 27.017
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.915
|  |  |  | Coincident | 1.337
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 33.929
|  |  |  | Coincident | 31.695
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.561
|  |  |  | Coincident | 32.129
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.562
|  |  |  | Coincident | 28.549
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.131
|  |  |  | Coincident | 28.94
| Waterloo 33kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 7.946
|  |  |  | Coincident | 7.925
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.005
|  |  |  | Coincident | 7.979
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.386
|  |  |  | Coincident | 0.386
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.934
|  |  |  | Coincident | 8.91
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.001
|  |  |  | Coincident | 8.971
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.069
|  |  |  | Coincident | 8.047
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.129
|  |  |  | Coincident | 8.102
| Whyalla Central 33kV | Substation Rating | MVA | Non-Coincident | 240
|  |  |  | Coincident | 240
|  | Raw Adjusted MD | MW | Non-Coincident | 66.635
|  |  |  | Coincident | 55.537
|  | Raw Adjusted MD | MVA | Non-Coincident | 72.999
|  |  |  | Coincident | 60.778
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.948
|  |  |  | Coincident | 1.602
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 70.166
|  |  |  | Coincident | 58.48
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 76.867
|  |  |  | Coincident | 63.999
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 67.239
|  |  |  | Coincident | 56.04
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 73.661
|  |  |  | Coincident | 61.329
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Wudinna 66kV | Substation Rating | MVA | Non-Coincident | 50
|  |  |  | Coincident | 50
|  | Raw Adjusted MD | MW | Non-Coincident | 15
|  |  |  | Coincident | 10.979
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.028
|  |  |  | Coincident | 11.013
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.006
|  |  |  | Coincident | 0.662
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.949
|  |  |  | Coincident | 10.942
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.977
|  |  |  | Coincident | 10.976
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.372
|  |  |  | Coincident | 9.788
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.397
|  |  |  | Coincident | 9.818
| Yadnarie 66kV | Substation Rating | MVA | Non-Coincident | 46.4
|  |  |  | Coincident | 46.4
|  | Raw Adjusted MD | MW | Non-Coincident | 7.607
|  |  |  | Coincident | 6.869
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.942
|  |  |  | Coincident | 7.311
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.151
|  |  |  | Coincident | 0.337
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.414
|  |  |  | Coincident | 7.598
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.785
|  |  |  | Coincident | 8.087
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.559
|  |  |  | Coincident | 6.826
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.893
|  |  |  | Coincident | 7.265
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
NETWORK LEVEL | SUBSTATION | FORECASTING ELEMENTS | UNIT | MAX DEMAND | 2023-24
ZONE SUBSTATION | CBD 33kV | Substation Rating | MVA | Non-Coincident | 82.2
|  |  |  | Coincident | 82.2
|  | Raw Adjusted MD | MW | Non-Coincident | 11.708
|  |  |  | Coincident | 11.708
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.901
|  |  |  | Coincident | 11.901
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 13/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 13:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.144
|  |  |  | Coincident | 0.144
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.256
|  |  |  | Coincident | 13.256
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.475
|  |  |  | Coincident | 13.475
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.509
|  |  |  | Coincident | 12.509
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.716
|  |  |  | Coincident | 12.716
| Coromandel Place 11kV | Substation Rating | MVA | Non-Coincident | 92.039
|  |  |  | Coincident | 92.039
|  | Raw Adjusted MD | MW | Non-Coincident | 49.159
|  |  |  | Coincident | 49.047
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.893
|  |  |  | Coincident | 49.79
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 13/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 13:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.769
|  |  |  | Coincident | 0.763
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.688
|  |  |  | Coincident | 50.573
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 51.445
|  |  |  | Coincident | 51.338
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 47.709
|  |  |  | Coincident | 47.601
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 48.421
|  |  |  | Coincident | 48.321
| East Terrace 11kV | Substation Rating | MVA | Non-Coincident | 77.84
|  |  |  | Coincident | 77.84
|  | Raw Adjusted MD | MW | Non-Coincident | 27.602
|  |  |  | Coincident | 26.888
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.268
|  |  |  | Coincident | 27.52
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 13/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30:00
|  |  |  | Coincident | 13:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.819
|  |  |  | Coincident | 2.362
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.899
|  |  |  | Coincident | 30.1
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.645
|  |  |  | Coincident | 30.807
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.521
|  |  |  | Coincident | 27.783
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.209
|  |  |  | Coincident | 28.436
| Hindley Street 11kV | Substation Rating | MVA | Non-Coincident | 79.988
|  |  |  | Coincident | 79.988
|  | Raw Adjusted MD | MW | Non-Coincident | 42.183
|  |  |  | Coincident | 41.647
|  | Raw Adjusted MD | MVA | Non-Coincident | 42.632
|  |  |  | Coincident | 42.633
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 13/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00:00
|  |  |  | Coincident | 13:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.137
|  |  |  | Coincident | 1.344
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 44.883
|  |  |  | Coincident | 44.313
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.361
|  |  |  | Coincident | 45.363
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.843
|  |  |  | Coincident | 41.311
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.288
|  |  |  | Coincident | 42.29
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Whitmore Square 11kV | Substation Rating | MVA | Non-Coincident | 79.217
|  |  |  | Coincident | 79.217
|  | Raw Adjusted MD | MW | Non-Coincident | 36.702
|  |  |  | Coincident | 35.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.337
|  |  |  | Coincident | 36.239
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 13/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30:00
|  |  |  | Coincident | 13:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.571
|  |  |  | Coincident | 2.793
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.614
|  |  |  | Coincident | 38.456
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.299
|  |  |  | Coincident | 39.114
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.152
|  |  |  | Coincident | 35.095
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.777
|  |  |  | Coincident | 35.696
| Birdwood 11kV | Substation Rating | MVA | Non-Coincident | 3.895
|  |  |  | Coincident | 3.895
|  | Raw Adjusted MD | MW | Non-Coincident | 2.744
|  |  |  | Coincident | 2.613
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.746
|  |  |  | Coincident | 2.616
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.072
|  |  |  | Coincident | 0.16
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.133
|  |  |  | Coincident | 2.984
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.135
|  |  |  | Coincident | 2.988
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.945
|  |  |  | Coincident | 2.805
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.947
|  |  |  | Coincident | 2.808
| Chain of Ponds 11kV | Substation Rating | MVA | Non-Coincident | 0.618
|  |  |  | Coincident | 0.618
|  | Raw Adjusted MD | MW | Non-Coincident | 0.334
|  |  |  | Coincident | 0.287
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.34
|  |  |  | Coincident | 0.292
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.096
|  |  |  | Coincident | 0.019
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.453
|  |  |  | Coincident | 0.39
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.462
|  |  |  | Coincident | 0.396
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.426
|  |  |  | Coincident | 0.366
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.434
|  |  |  | Coincident | 0.373
| Deloraine 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.281
|  |  |  | Coincident | 0.224
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.281
|  |  |  | Coincident | 0.224
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.018
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.312
|  |  |  | Coincident | 0.248
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.313
|  |  |  | Coincident | 0.248
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.285
|  |  |  | Coincident | 0.227
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.285
|  |  |  | Coincident | 0.227
| Forreston 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.773
|  |  |  | Coincident | 0.711
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.811
|  |  |  | Coincident | 0.76
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.046
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.818
|  |  |  | Coincident | 0.752
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.857
|  |  |  | Coincident | 0.804
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.733
|  |  |  | Coincident | 0.674
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.769
|  |  |  | Coincident | 0.721
| Gumeracha 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 01/11/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
| Gumeracha Weir 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.087
|  |  |  | Coincident | 0.074
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.087
|  |  |  | Coincident | 0.076
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.008
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.161
|  |  |  | Coincident | 0.138
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.163
|  |  |  | Coincident | 0.142
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.146
|  |  |  | Coincident | 0.125
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.147
|  |  |  | Coincident | 0.128
| Gumhaven 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.04
|  |  |  | Coincident | 0.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.041
|  |  |  | Coincident | 0.041
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.049
|  |  |  | Coincident | 0.049
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.05
|  |  |  | Coincident | 0.05
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.046
|  |  |  | Coincident | 0.046
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.047
|  |  |  | Coincident | 0.047
| Hermitage 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.153
|  |  |  | Coincident | 0.122
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.153
|  |  |  | Coincident | 0.122
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.008
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.165
|  |  |  | Coincident | 0.132
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.165
|  |  |  | Coincident | 0.132
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.142
|  |  |  | Coincident | 0.113
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.143
|  |  |  | Coincident | 0.114
| Houghton 7.6kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.861
|  |  |  | Coincident | 1.732
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.935
|  |  |  | Coincident | 1.796
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.136
|  |  |  | Coincident | 0.136
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.875
|  |  |  | Coincident | 1.745
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.809
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.677
|  |  |  | Coincident | 1.561
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.744
|  |  |  | Coincident | 1.618
| Kersbrook 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.479
|  |  |  | Coincident | 0.444
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.482
|  |  |  | Coincident | 0.448
|  | Date MD occurred |  | Non-Coincident | 04/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.006
|  |  |  | Coincident | 0.026
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.529
|  |  |  | Coincident | 0.49
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.533
|  |  |  | Coincident | 0.495
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.465
|  |  |  | Coincident | 0.431
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.468
|  |  |  | Coincident | 0.435
| Lobethal 11kV | Substation Rating | MVA | Non-Coincident | 13.4
|  |  |  | Coincident | 13.4
|  | Raw Adjusted MD | MW | Non-Coincident | 7.016
|  |  |  | Coincident | 6.38
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.299
|  |  |  | Coincident | 6.67
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.004
|  |  |  | Coincident | 0.387
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.71
|  |  |  | Coincident | 6.102
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.981
|  |  |  | Coincident | 6.379
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.245
|  |  |  | Coincident | 5.679
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.498
|  |  |  | Coincident | 5.937
| Mount Pleasant 11kV | Substation Rating | MVA | Non-Coincident | 3.7
|  |  |  | Coincident | 3.7
|  | Raw Adjusted MD | MW | Non-Coincident | 2.115
|  |  |  | Coincident | 2.027
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.118
|  |  |  | Coincident | 2.031
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.05
|  |  |  | Coincident | 0.112
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.168
|  |  |  | Coincident | 2.078
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.171
|  |  |  | Coincident | 2.083
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.953
|  |  |  | Coincident | 1.872
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.956
|  |  |  | Coincident | 1.876
| Ardrossan 11kV | Substation Rating | MVA | Non-Coincident | 3.687
|  |  |  | Coincident | 3.687
|  | Raw Adjusted MD | MW | Non-Coincident | 2.152
|  |  |  | Coincident | 2.079
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.185
|  |  |  | Coincident | 2.111
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.046
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.03
|  |  |  | Coincident | 1.961
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.061
|  |  |  | Coincident | 1.992
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.77
|  |  |  | Coincident | 1.71
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.797
|  |  |  | Coincident | 1.736
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Black Point 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.34
|  |  |  | Coincident | 0.34
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.343
|  |  |  | Coincident | 0.343
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.007
|  |  |  | Coincident | 0.007
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.337
|  |  |  | Coincident | 0.337
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.34
|  |  |  | Coincident | 0.34
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.304
|  |  |  | Coincident | 0.304
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.307
|  |  |  | Coincident | 0.307
| Curramulka 7.6kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.14
|  |  |  | Coincident | 0.14
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.141
|  |  |  | Coincident | 0.141
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.148
|  |  |  | Coincident | 0.148
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.149
|  |  |  | Coincident | 0.149
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.134
|  |  |  | Coincident | 0.134
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.135
|  |  |  | Coincident | 0.135
| Curramulka South 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.038
|  |  |  | Coincident | 0.038
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.038
|  |  |  | Coincident | 0.038
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.029
|  |  |  | Coincident | 0.029
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.029
|  |  |  | Coincident | 0.029
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.026
|  |  |  | Coincident | 0.026
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.026
|  |  |  | Coincident | 0.026
| James Well 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.21
|  |  |  | Coincident | 0.21
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.212
|  |  |  | Coincident | 0.212
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.007
|  |  |  | Coincident | 0.007
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.247
|  |  |  | Coincident | 0.247
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.249
|  |  |  | Coincident | 0.249
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.228
|  |  |  | Coincident | 0.228
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.23
|  |  |  | Coincident | 0.23
| Maitland 11kV | Substation Rating | MVA | Non-Coincident | 6.469
|  |  |  | Coincident | 6.469
|  | Raw Adjusted MD | MW | Non-Coincident | 4.021
|  |  |  | Coincident | 3.92
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.037
|  |  |  | Coincident | 3.931
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002
|  |  |  | Coincident | 0.084
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.901
|  |  |  | Coincident | 3.803
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.917
|  |  |  | Coincident | 3.814
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.458
|  |  |  | Coincident | 3.372
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.472
|  |  |  | Coincident | 3.381
| Minlaton 11kV | Substation Rating | MVA | Non-Coincident | 2.587
|  |  |  | Coincident | 2.587
|  | Raw Adjusted MD | MW | Non-Coincident | 1.867
|  |  |  | Coincident | 1.813
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.966
|  |  |  | Coincident | 1.908
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.042
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.952
|  |  |  | Coincident | 1.895
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.055
|  |  |  | Coincident | 1.995
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.857
|  |  |  | Coincident | 1.803
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.955
|  |  |  | Coincident | 1.898
| Port Julia 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.24
|  |  |  | Coincident | 0.133
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.252
|  |  |  | Coincident | 0.14
|  | Date MD occurred |  | Non-Coincident | 02/11/2023
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.194
|  |  |  | Coincident | 0.008
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.338
|  |  |  | Coincident | 0.188
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.356
|  |  |  | Coincident | 0.197
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.311
|  |  |  | Coincident | 0.172
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.327
|  |  |  | Coincident | 0.181
| Port Vincent 11kV | Substation Rating | MVA | Non-Coincident | 2.656
|  |  |  | Coincident | 2.656
|  | Raw Adjusted MD | MW | Non-Coincident | 1.358
|  |  |  | Coincident | 1.358
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.386
|  |  |  | Coincident | 1.386
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.026
|  |  |  | Coincident | 0.026
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.498
|  |  |  | Coincident | 1.498
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.529
|  |  |  | Coincident | 1.529
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.397
|  |  |  | Coincident | 1.397
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.426
|  |  |  | Coincident | 1.426
| Baroota Town 11kV | Substation Rating | MVA | Non-Coincident | 0.713
|  |  |  | Coincident | 0.713
|  | Raw Adjusted MD | MW | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.196
|  |  |  | Coincident | 0.196
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.211
|  |  |  | Coincident | 0.211
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.213
|  |  |  | Coincident | 0.213
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.182
|  |  |  | Coincident | 0.182
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.184
|  |  |  | Coincident | 0.184
| Booleroo Centre 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.456
|  |  |  | Coincident | 0.411
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.491
|  |  |  | Coincident | 0.442
|  | Date MD occurred |  | Non-Coincident | 12/02/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.15
|  |  |  | Coincident | 0.009
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.444
|  |  |  | Coincident | 0.4
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.478
|  |  |  | Coincident | 0.43
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.417
|  |  |  | Coincident | 0.376
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.448
|  |  |  | Coincident | 0.404
| Bungama Napperby 11kV | Substation Rating | MVA | Non-Coincident | 1.296
|  |  |  | Coincident | 1.296
|  | Raw Adjusted MD | MW | Non-Coincident | 0.935
|  |  |  | Coincident | 0.926
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.006
|  |  |  | Coincident | 0.996
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.021
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.741
|  |  |  | Coincident | 0.734
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.797
|  |  |  | Coincident | 0.79
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.709
|  |  |  | Coincident | 0.702
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.762
|  |  |  | Coincident | 0.755
| Fullerville 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.07
|  |  |  | Coincident | 0.07
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.07
|  |  |  | Coincident | 0.07
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.073
|  |  |  | Coincident | 0.073
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.073
|  |  |  | Coincident | 0.073
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.065
|  |  |  | Coincident | 0.065
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.065
|  |  |  | Coincident | 0.065
| Melrose 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.314
|  |  |  | Coincident | 0.278
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.33
|  |  |  | Coincident | 0.292
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.326
|  |  |  | Coincident | 0.289
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.344
|  |  |  | Coincident | 0.304
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.304
|  |  |  | Coincident | 0.269
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.32
|  |  |  | Coincident | 0.283
| Orroroo 11kV | Substation Rating | MVA | Non-Coincident | 2.588
|  |  |  | Coincident | 2.588
|  | Raw Adjusted MD | MW | Non-Coincident | 1.108
|  |  |  | Coincident | 1.025
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.124
|  |  |  | Coincident | 1.039
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.012
|  |  |  | Coincident | 0.027
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.078
|  |  |  | Coincident | 0.996
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.093
|  |  |  | Coincident | 1.011
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.969
|  |  |  | Coincident | 0.896
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.983
|  |  |  | Coincident | 0.909
| Port Germein 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.879
|  |  |  | Coincident | 0.841
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.88
|  |  |  | Coincident | 0.843
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.018
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.777
|  |  |  | Coincident | 0.744
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.779
|  |  |  | Coincident | 0.746
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.685
|  |  |  | Coincident | 0.655
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.686
|  |  |  | Coincident | 0.657
| Telowie 11kV | Substation Rating | MVA | Non-Coincident | 1.235
|  |  |  | Coincident | 1.235
|  | Raw Adjusted MD | MW | Non-Coincident | 0.544
|  |  |  | Coincident | 0.5
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.545
|  |  |  | Coincident | 0.501
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.012
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.536
|  |  |  | Coincident | 0.493
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.538
|  |  |  | Coincident | 0.494
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.475
|  |  |  | Coincident | 0.437
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.476
|  |  |  | Coincident | 0.438
| Wilmington 11kV | Substation Rating | MVA | Non-Coincident | 2.565
|  |  |  | Coincident | 2.565
|  | Raw Adjusted MD | MW | Non-Coincident | 0.733
|  |  |  | Coincident | 0.707
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.733
|  |  |  | Coincident | 0.708
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.019
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.806
|  |  |  | Coincident | 0.777
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.806
|  |  |  | Coincident | 0.778
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.726
|  |  |  | Coincident | 0.7
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.726
|  |  |  | Coincident | 0.701
| Wirrabara Forest 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.36
|  |  |  | Coincident | 0.344
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.364
|  |  |  | Coincident | 0.35
|  | Date MD occurred |  | Non-Coincident | 08/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.388
|  |  |  | Coincident | 0.37
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.392
|  |  |  | Coincident | 0.377
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.372
|  |  |  | Coincident | 0.356
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.376
|  |  |  | Coincident | 0.362
| Wirrabara South 11kV | Substation Rating | MVA | Non-Coincident | 0.13
|  |  |  | Coincident | 0.13
|  | Raw Adjusted MD | MW | Non-Coincident | 0.05
|  |  |  | Coincident | 0.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.05
|  |  |  | Coincident | 0.05
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.052
|  |  |  | Coincident | 0.052
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.052
|  |  |  | Coincident | 0.052
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.046
|  |  |  | Coincident | 0.046
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.046
|  |  |  | Coincident | 0.046
| Wongyarra 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.1
|  |  |  | Coincident | 0.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.1
|  |  |  | Coincident | 0.1
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.104
|  |  |  | Coincident | 0.104
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.104
|  |  |  | Coincident | 0.104
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.093
|  |  |  | Coincident | 0.093
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.093
|  |  |  | Coincident | 0.093
| Berri 11kV | Substation Rating | MVA | Non-Coincident | 27.706
|  |  |  | Coincident | 27.706
|  | Raw Adjusted MD | MW | Non-Coincident | 9.67
|  |  |  | Coincident | 9.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.812
|  |  |  | Coincident | 9.754
|  | Date MD occurred |  | Non-Coincident | 22/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.576
|  |  |  | Coincident | 0.576
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.415
|  |  |  | Coincident | 11.368
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.583
|  |  |  | Coincident | 11.514
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.851
|  |  |  | Coincident | 9.81
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.996
|  |  |  | Coincident | 9.936
| Glossop 11kV | Substation Rating | MVA | Non-Coincident | 15.145
|  |  |  | Coincident | 15.145
|  | Raw Adjusted MD | MW | Non-Coincident | 10.241
|  |  |  | Coincident | 9.678
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.772
|  |  |  | Coincident | 10.108
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.106
|  |  |  | Coincident | 0.259
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.241
|  |  |  | Coincident | 10.623
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.824
|  |  |  | Coincident | 11.096
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.574
|  |  |  | Coincident | 9.993
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.122
|  |  |  | Coincident | 10.437
| Loveday 11kV | Substation Rating | MVA | Non-Coincident | 20.681
|  |  |  | Coincident | 20.681
|  | Raw Adjusted MD | MW | Non-Coincident | 9.529
|  |  |  | Coincident | 8.969
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.041
|  |  |  | Coincident | 9.416
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.281
|  |  |  | Coincident | 0.768
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.871
|  |  |  | Coincident | 10.232
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.456
|  |  |  | Coincident | 10.743
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.237
|  |  |  | Coincident | 9.635
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.787
|  |  |  | Coincident | 10.116
| Loxton 11kV | Substation Rating | MVA | Non-Coincident | 21.954
|  |  |  | Coincident | 21.954
|  | Raw Adjusted MD | MW | Non-Coincident | 12.992
|  |  |  | Coincident | 12.525
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.528
|  |  |  | Coincident | 13.028
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.773
|  |  |  | Coincident | 0.417
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 12.356
|  |  |  | Coincident | 11.911
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 12.866
|  |  |  | Coincident | 12.39
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.613
|  |  |  | Coincident | 11.195
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.092
|  |  |  | Coincident | 11.645
| Lyrup 11kV | Substation Rating | MVA | Non-Coincident | 8.877
|  |  |  | Coincident | 8.877
|  | Raw Adjusted MD | MW | Non-Coincident | 5.1
|  |  |  | Coincident | 2.593
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.181
|  |  |  | Coincident | 2.631
|  | Date MD occurred |  | Non-Coincident | 13/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 8:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.587
|  |  |  | Coincident | 0.125
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.567
|  |  |  | Coincident | 2.83
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.655
|  |  |  | Coincident | 2.872
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.158
|  |  |  | Coincident | 2.622
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.239
|  |  |  | Coincident | 2.661
| Paringa 11kV | Substation Rating | MVA | Non-Coincident | 3.563
|  |  |  | Coincident | 3.563
|  | Raw Adjusted MD | MW | Non-Coincident | 2.174
|  |  |  | Coincident | 2.142
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.187
|  |  |  | Coincident | 2.156
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.201
|  |  |  | Coincident | 0.109
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.438
|  |  |  | Coincident | 2.402
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.453
|  |  |  | Coincident | 2.417
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.206
|  |  |  | Coincident | 2.173
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.219
|  |  |  | Coincident | 2.187
| Paringa 33kV | Substation Rating | MVA | Non-Coincident | 34.643
|  |  |  | Coincident | 34.643
|  | Raw Adjusted MD | MW | Non-Coincident | 13.15
|  |  |  | Coincident | 9.05
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.504
|  |  |  | Coincident | 9.303
|  | Date MD occurred |  | Non-Coincident | 08/12/2023
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 10:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.068
|  |  |  | Coincident | 0.208
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.714
|  |  |  | Coincident | 9.438
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.083
|  |  |  | Coincident | 9.702
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.244
|  |  |  | Coincident | 9.114
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.6
|  |  |  | Coincident | 9.369
| Pyap 11kV | Substation Rating | MVA | Non-Coincident | 15.17
|  |  |  | Coincident | 15.17
|  | Raw Adjusted MD | MW | Non-Coincident | 8.318
|  |  |  | Coincident | 7.233
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.432
|  |  |  | Coincident | 7.33
|  | Date MD occurred |  | Non-Coincident | 04/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.351
|  |  |  | Coincident | 0.351
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.993
|  |  |  | Coincident | 7.82
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.116
|  |  |  | Coincident | 7.925
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.17
|  |  |  | Coincident | 7.104
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.282
|  |  |  | Coincident | 7.2
| Renmark 11kV | Substation Rating | MVA | Non-Coincident | 29.903
|  |  |  | Coincident | 29.903
|  | Raw Adjusted MD | MW | Non-Coincident | 16.793
|  |  |  | Coincident | 16.793
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.951
|  |  |  | Coincident | 16.951
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.209
|  |  |  | Coincident | 1.209
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.643
|  |  |  | Coincident | 18.643
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.818
|  |  |  | Coincident | 18.818
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.406
|  |  |  | Coincident | 16.406
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.56
|  |  |  | Coincident | 16.56
| Woolpunda 11kV | Substation Rating | MVA | Non-Coincident | 19.018
|  |  |  | Coincident | 19.018
|  | Raw Adjusted MD | MW | Non-Coincident | 7.622
|  |  |  | Coincident | 6.394
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.053
|  |  |  | Coincident | 6.707
|  | Date MD occurred |  | Non-Coincident | 22/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.305
|  |  |  | Coincident | 0.029
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.983
|  |  |  | Coincident | 6.696
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.434
|  |  |  | Coincident | 7.024
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.633
|  |  |  | Coincident | 6.402
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.064
|  |  |  | Coincident | 6.716
| Allendale East 11kV | Substation Rating | MVA | Non-Coincident | 7.104
|  |  |  | Coincident | 7.104
|  | Raw Adjusted MD | MW | Non-Coincident | 3.369
|  |  |  | Coincident | 2.967
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.548
|  |  |  | Coincident | 3.133
|  | Date MD occurred |  | Non-Coincident | 04/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 1:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.097
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.846
|  |  |  | Coincident | 3.387
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.051
|  |  |  | Coincident | 3.577
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.597
|  |  |  | Coincident | 3.168
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.789
|  |  |  | Coincident | 3.345
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Glencoe 11kV | Substation Rating | MVA | Non-Coincident | 2.1
|  |  |  | Coincident | 2.1
|  | Raw Adjusted MD | MW | Non-Coincident | 0.963
|  |  |  | Coincident | 0.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.021
|  |  |  | Coincident | 0.676
|  | Date MD occurred |  | Non-Coincident | 03/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 2:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.038
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.043
|  |  |  | Coincident | 0.683
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.106
|  |  |  | Coincident | 0.732
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.972
|  |  |  | Coincident | 0.636
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.03
|  |  |  | Coincident | 0.682
| Kongorong 11kV | Substation Rating | MVA | Non-Coincident | 1.33
|  |  |  | Coincident | 1.33
|  | Raw Adjusted MD | MW | Non-Coincident | 0.738
|  |  |  | Coincident | 0.738
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.758
|  |  |  | Coincident | 0.758
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.021
|  |  |  | Coincident | 0.021
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.673
|  |  |  | Coincident | 0.673
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.691
|  |  |  | Coincident | 0.691
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.627
|  |  |  | Coincident | 0.627
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.644
|  |  |  | Coincident | 0.644
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Mount Gambier North 11kV | Substation Rating | MVA | Non-Coincident | 17.813
|  |  |  | Coincident | 17.813
|  | Raw Adjusted MD | MW | Non-Coincident | 8.9
|  |  |  | Coincident | 7.658
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.127
|  |  |  | Coincident | 7.833
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.071
|  |  |  | Coincident | 0.301
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.075
|  |  |  | Coincident | 9.529
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.357
|  |  |  | Coincident | 9.746
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.801
|  |  |  | Coincident | 8.433
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.051
|  |  |  | Coincident | 8.626
| Mount Gambier West 11kV | Substation Rating | MVA | Non-Coincident | 25.636
|  |  |  | Coincident | 25.636
|  | Raw Adjusted MD | MW | Non-Coincident | 12.972
|  |  |  | Coincident | 12.378
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.108
|  |  |  | Coincident | 12.681
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.578
|  |  |  | Coincident | 0.491
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.892
|  |  |  | Coincident | 15.164
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.058
|  |  |  | Coincident | 15.535
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.484
|  |  |  | Coincident | 13.821
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.636
|  |  |  | Coincident | 14.159
| Mount Schank 11kV | Substation Rating | MVA | Non-Coincident | 3.942
|  |  |  | Coincident | 3.942
|  | Raw Adjusted MD | MW | Non-Coincident | 2.528
|  |  |  | Coincident | 1.586
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.814
|  |  |  | Coincident | 1.787
|  | Date MD occurred |  | Non-Coincident | 09/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 5:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.041
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.58
|  |  |  | Coincident | 1.618
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.872
|  |  |  | Coincident | 1.824
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.485
|  |  |  | Coincident | 1.559
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.767
|  |  |  | Coincident | 1.757
| Tantanoola 11kV | Substation Rating | MVA | Non-Coincident | 1.425
|  |  |  | Coincident | 1.425
|  | Raw Adjusted MD | MW | Non-Coincident | 0.478
|  |  |  | Coincident | 0.434
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.525
|  |  |  | Coincident | 0.452
|  | Date MD occurred |  | Non-Coincident | 22/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 8:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.092
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.508
|  |  |  | Coincident | 0.461
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.557
|  |  |  | Coincident | 0.48
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.471
|  |  |  | Coincident | 0.428
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.517
|  |  |  | Coincident | 0.445
| Brinkworth Town 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.689
|  |  |  | Coincident | 0.658
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.692
|  |  |  | Coincident | 0.662
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.018
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.782
|  |  |  | Coincident | 0.747
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.786
|  |  |  | Coincident | 0.751
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.72
|  |  |  | Coincident | 0.687
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.723
|  |  |  | Coincident | 0.692
| Collinsfield 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 0.556
|  |  |  | Coincident | 0.508
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.558
|  |  |  | Coincident | 0.508
|  | Date MD occurred |  | Non-Coincident | 08/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.049
|  |  |  | Coincident | 0.01
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.529
|  |  |  | Coincident | 0.484
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.531
|  |  |  | Coincident | 0.484
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.494
|  |  |  | Coincident | 0.451
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.496
|  |  |  | Coincident | 0.451
| Georgetown 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.151
|  |  |  | Coincident | 0.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.152
|  |  |  | Coincident | 0.131
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.179
|  |  |  | Coincident | 0.154
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.18
|  |  |  | Coincident | 0.155
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.162
|  |  |  | Coincident | 0.139
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.163
|  |  |  | Coincident | 0.14
| Gulnare 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.1
|  |  |  | Coincident | 0.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.101
|  |  |  | Coincident | 0.101
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.123
|  |  |  | Coincident | 0.123
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.125
|  |  |  | Coincident | 0.125
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.111
|  |  |  | Coincident | 0.111
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.113
|  |  |  | Coincident | 0.113
| Halbury 11kV | Substation Rating | MVA | Non-Coincident | 0.41
|  |  |  | Coincident | 0.41
|  | Raw Adjusted MD | MW | Non-Coincident | 0.05
|  |  |  | Coincident | 0.038
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.05
|  |  |  | Coincident | 0.038
|  | Date MD occurred |  | Non-Coincident | 27/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.072
|  |  |  | Coincident | 0.054
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.072
|  |  |  | Coincident | 0.054
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.065
|  |  |  | Coincident | 0.049
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.065
|  |  |  | Coincident | 0.049
| Hoyleton 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.102
|  |  |  | Coincident | 0.09
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.102
|  |  |  | Coincident | 0.09
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.006
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.086
|  |  |  | Coincident | 0.076
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.086
|  |  |  | Coincident | 0.076
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.079
|  |  |  | Coincident | 0.069
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.079
|  |  |  | Coincident | 0.069
| Kybunga 11kV | Substation Rating | MVA | Non-Coincident | 0.13
|  |  |  | Coincident | 0.13
|  | Raw Adjusted MD | MW | Non-Coincident | 0.065
|  |  |  | Coincident | 0.042
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.067
|  |  |  | Coincident | 0.042
|  | Date MD occurred |  | Non-Coincident | 08/12/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.019
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.076
|  |  |  | Coincident | 0.049
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.079
|  |  |  | Coincident | 0.05
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.069
|  |  |  | Coincident | 0.045
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.072
|  |  |  | Coincident | 0.045
| Spalding 11kV | Substation Rating | MVA | Non-Coincident | 1.235
|  |  |  | Coincident | 1.235
|  | Raw Adjusted MD | MW | Non-Coincident | 0.977
|  |  |  | Coincident | 0.872
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.977
|  |  |  | Coincident | 0.872
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.019
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.931
|  |  |  | Coincident | 0.831
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.931
|  |  |  | Coincident | 0.831
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.871
|  |  |  | Coincident | 0.777
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.871
|  |  |  | Coincident | 0.777
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Burra TF2 11kV | Substation Rating | MVA | Non-Coincident | 3.7
|  |  |  | Coincident | 3.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.97
|  |  |  | Coincident | 1.609
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.974
|  |  |  | Coincident | 1.609
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 4:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.058
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.936
|  |  |  | Coincident | 1.581
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.94
|  |  |  | Coincident | 1.581
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.762
|  |  |  | Coincident | 1.439
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.766
|  |  |  | Coincident | 1.439
| Clare 11kV | Substation Rating | MVA | Non-Coincident | 13.155
|  |  |  | Coincident | 13.155
|  | Raw Adjusted MD | MW | Non-Coincident | 7.792
|  |  |  | Coincident | 7.736
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.948
|  |  |  | Coincident | 7.901
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.143
|  |  |  | Coincident | 0.259
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.491
|  |  |  | Coincident | 9.423
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.681
|  |  |  | Coincident | 9.624
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.646
|  |  |  | Coincident | 8.584
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.82
|  |  |  | Coincident | 8.768
| Edithburgh 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.507
|  |  |  | Coincident | 1.291
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.523
|  |  |  | Coincident | 1.306
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.041
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.469
|  |  |  | Coincident | 1.259
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.486
|  |  |  | Coincident | 1.274
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.402
|  |  |  | Coincident | 1.201
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.418
|  |  |  | Coincident | 1.216
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Marion Bay 11kV | Substation Rating | MVA | Non-Coincident | 1.425
|  |  |  | Coincident | 1.425
|  | Raw Adjusted MD | MW | Non-Coincident | 0.626
|  |  |  | Coincident | 0.6
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.627
|  |  |  | Coincident | 0.601
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.025
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.605
|  |  |  | Coincident | 0.58
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.607
|  |  |  | Coincident | 0.581
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.535
|  |  |  | Coincident | 0.513
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.537
|  |  |  | Coincident | 0.514
| Port Giles 11kV | Substation Rating | MVA | Non-Coincident | 3.563
|  |  |  | Coincident | 3.563
|  | Raw Adjusted MD | MW | Non-Coincident | 1.488
|  |  |  | Coincident | 0.228
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.565
|  |  |  | Coincident | 0.229
|  | Date MD occurred |  | Non-Coincident | 07/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 8:30:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.072
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.357
|  |  |  | Coincident | 0.208
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.427
|  |  |  | Coincident | 0.209
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.288
|  |  |  | Coincident | 0.197
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.354
|  |  |  | Coincident | 0.198
| Stansbury 11kV | Substation Rating | MVA | Non-Coincident | 1.805
|  |  |  | Coincident | 1.805
|  | Raw Adjusted MD | MW | Non-Coincident | 1.332
|  |  |  | Coincident | 1.332
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.402
|  |  |  | Coincident | 1.402
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.016
|  |  |  | Coincident | 1.016
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.069
|  |  |  | Coincident | 1.069
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.974
|  |  |  | Coincident | 0.974
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.025
|  |  |  | Coincident | 1.025
| Warooka 11kV | Substation Rating | MVA | Non-Coincident | 6.442
|  |  |  | Coincident | 6.442
|  | Raw Adjusted MD | MW | Non-Coincident | 1.892
|  |  |  | Coincident | 1.615
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.909
|  |  |  | Coincident | 1.63
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.348
|  |  |  | Coincident | 2.004
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.369
|  |  |  | Coincident | 2.023
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.095
|  |  |  | Coincident | 1.788
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.114
|  |  |  | Coincident | 1.805
| Yorketown 11kV | Substation Rating | MVA | Non-Coincident | 2.597
|  |  |  | Coincident | 2.597
|  | Raw Adjusted MD | MW | Non-Coincident | 1.275
|  |  |  | Coincident | 1.185
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.343
|  |  |  | Coincident | 1.247
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.138
|  |  |  | Coincident | 1.057
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.198
|  |  |  | Coincident | 1.113
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.109
|  |  |  | Coincident | 1.03
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.167
|  |  |  | Coincident | 1.084
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Port Augusta 11kV | Substation Rating | MVA | Non-Coincident | 28.5
|  |  |  | Coincident | 28.5
|  | Raw Adjusted MD | MW | Non-Coincident | 12.52
|  |  |  | Coincident | 12.42
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.748
|  |  |  | Coincident | 12.65
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.127
|  |  |  | Coincident | 0.229
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.964
|  |  |  | Coincident | 13.853
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.218
|  |  |  | Coincident | 14.109
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.428
|  |  |  | Coincident | 12.329
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.655
|  |  |  | Coincident | 12.557
| Port Augusta West TF1 11kV | Substation Rating | MVA | Non-Coincident | 15.1
|  |  |  | Coincident | 15.1
|  | Raw Adjusted MD | MW | Non-Coincident | 4.801
|  |  |  | Coincident | 4.798
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.839
|  |  |  | Coincident | 4.841
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.061
|  |  |  | Coincident | 0.111
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.64
|  |  |  | Coincident | 5.636
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.684
|  |  |  | Coincident | 5.686
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.021
|  |  |  | Coincident | 5.017
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.059
|  |  |  | Coincident | 5.062
| Port Augusta West TF2 11kV | Substation Rating | MVA | Non-Coincident | 17.1
|  |  |  | Coincident | 17.1
|  | Raw Adjusted MD | MW | Non-Coincident | 3.277
|  |  |  | Coincident | 3.145
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.32
|  |  |  | Coincident | 3.193
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.053
|  |  |  | Coincident | 0.097
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.317
|  |  |  | Coincident | 3.183
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.36
|  |  |  | Coincident | 3.232
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.954
|  |  |  | Coincident | 2.835
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.993
|  |  |  | Coincident | 2.879
| Quorn 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.58
|  |  |  | Coincident | 1.519
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.589
|  |  |  | Coincident | 1.528
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.031
|  |  |  | Coincident | 0.056
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.874
|  |  |  | Coincident | 1.802
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.886
|  |  |  | Coincident | 1.814
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.661
|  |  |  | Coincident | 1.597
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.671
|  |  |  | Coincident | 1.608
| Stirling North 1 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 1.342
|  |  |  | Coincident | 1.263
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.525
|  |  |  | Coincident | 1.435
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.052
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.419
|  |  |  | Coincident | 1.336
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.613
|  |  |  | Coincident | 1.518
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.345
|  |  |  | Coincident | 1.266
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.529
|  |  |  | Coincident | 1.439
| Stirling North 2 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.731
|  |  |  | Coincident | 1.593
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.749
|  |  |  | Coincident | 1.61
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.028
|  |  |  | Coincident | 0.05
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.793
|  |  |  | Coincident | 1.649
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.812
|  |  |  | Coincident | 1.668
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.582
|  |  |  | Coincident | 1.455
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.598
|  |  |  | Coincident | 1.471
| Angaston 11kV | Substation Rating | MVA | Non-Coincident | 28.909
|  |  |  | Coincident | 28.909
|  | Raw Adjusted MD | MW | Non-Coincident | 14.292
|  |  |  | Coincident | 13.385
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.862
|  |  |  | Coincident | 14.023
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.213
|  |  |  | Coincident | 1.085
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.178
|  |  |  | Coincident | 14.214
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.783
|  |  |  | Coincident | 14.892
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.235
|  |  |  | Coincident | 13.331
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.802
|  |  |  | Coincident | 13.967
| Barossa South TF1 11kV | Substation Rating | MVA | Non-Coincident | 8.906
|  |  |  | Coincident | 8.906
|  | Raw Adjusted MD | MW | Non-Coincident | 2.33
|  |  |  | Coincident | 1.995
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.334
|  |  |  | Coincident | 1.995
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.335
|  |  |  | Coincident | 0.117
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.637
|  |  |  | Coincident | 2.258
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.641
|  |  |  | Coincident | 2.258
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.395
|  |  |  | Coincident | 2.051
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.399
|  |  |  | Coincident | 2.051
| Barossa South TF2 11kV | Substation Rating | MVA | Non-Coincident | 8.645
|  |  |  | Coincident | 8.645
|  | Raw Adjusted MD | MW | Non-Coincident | 3.585
|  |  |  | Coincident | 3.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.951
|  |  |  | Coincident | 3.526
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.231
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.661
|  |  |  | Coincident | 3.166
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.035
|  |  |  | Coincident | 3.601
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.417
|  |  |  | Coincident | 2.954
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.765
|  |  |  | Coincident | 3.36
| Dorrien TF4 11kV | Substation Rating | MVA | Non-Coincident | 14.6
|  |  |  | Coincident | 14.6
|  | Raw Adjusted MD | MW | Non-Coincident | 7.3
|  |  |  | Coincident | 6.803
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.561
|  |  |  | Coincident | 7.112
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.336
|  |  |  | Coincident | 0.765
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.886
|  |  |  | Coincident | 8.281
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.204
|  |  |  | Coincident | 8.657
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.911
|  |  |  | Coincident | 7.373
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.194
|  |  |  | Coincident | 7.707
| Dorrien TF5 11kV | Substation Rating | MVA | Non-Coincident | 16.1
|  |  |  | Coincident | 16.1
|  | Raw Adjusted MD | MW | Non-Coincident | 4.707
|  |  |  | Coincident | 4.578
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.927
|  |  |  | Coincident | 4.867
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.202
|  |  |  | Coincident | 0.461
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.254
|  |  |  | Coincident | 5.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.499
|  |  |  | Coincident | 5.432
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.76
|  |  |  | Coincident | 4.629
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.982
|  |  |  | Coincident | 4.921
| Gomersal North 11kV | Substation Rating | MVA | Non-Coincident | 0.713
|  |  |  | Coincident | 0.713
|  | Raw Adjusted MD | MW | Non-Coincident | 0.229
|  |  |  | Coincident | 0.027
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.234
|  |  |  | Coincident | 0.028
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.012
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.286
|  |  |  | Coincident | 0.034
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.293
|  |  |  | Coincident | 0.035
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.244
|  |  |  | Coincident | 0.029
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.25
|  |  |  | Coincident | 0.03
| Lyndoch 11kV | Substation Rating | MVA | Non-Coincident | 4.6
|  |  |  | Coincident | 4.6
|  | Raw Adjusted MD | MW | Non-Coincident | 2.857
|  |  |  | Coincident | 2.356
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.953
|  |  |  | Coincident | 2.451
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.31
|  |  |  | Coincident | 0.31
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.927
|  |  |  | Coincident | 2.414
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.025
|  |  |  | Coincident | 2.511
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.61
|  |  |  | Coincident | 2.153
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.698
|  |  |  | Coincident | 2.239
| Lyndoch South 7.6kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.266
|  |  |  | Coincident | 0.137
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.273
|  |  |  | Coincident | 0.143
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.024
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.27
|  |  |  | Coincident | 0.139
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.277
|  |  |  | Coincident | 0.146
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.246
|  |  |  | Coincident | 0.127
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.253
|  |  |  | Coincident | 0.133
| Nuriootpa 11kV | Substation Rating | MVA | Non-Coincident | 13.7
|  |  |  | Coincident | 13.7
|  | Raw Adjusted MD | MW | Non-Coincident | 8.377
|  |  |  | Coincident | 8.159
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.495
|  |  |  | Coincident | 8.302
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.39
|  |  |  | Coincident | 0.889
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.578
|  |  |  | Coincident | 10.302
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.726
|  |  |  | Coincident | 10.483
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.285
|  |  |  | Coincident | 9.042
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.415
|  |  |  | Coincident | 9.201
| Sandy Creek 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.156
|  |  |  | Coincident | 1.535
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.2
|  |  |  | Coincident | 1.592
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.047
|  |  |  | Coincident | 0.281
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.601
|  |  |  | Coincident | 1.851
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.654
|  |  |  | Coincident | 1.921
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.33
|  |  |  | Coincident | 1.658
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.378
|  |  |  | Coincident | 1.721
| Stockwell TF1 11kV | Substation Rating | MVA | Non-Coincident | 8.906
|  |  |  | Coincident | 8.906
|  | Raw Adjusted MD | MW | Non-Coincident | 2.406
|  |  |  | Coincident | 1.839
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.435
|  |  |  | Coincident | 1.859
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.05
|  |  |  | Coincident | 0.255
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.777
|  |  |  | Coincident | 2.122
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.811
|  |  |  | Coincident | 2.146
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.473
|  |  |  | Coincident | 1.89
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.503
|  |  |  | Coincident | 1.911
| Stockwell TF2 11kV | Substation Rating | MVA | Non-Coincident | 8.7
|  |  |  | Coincident | 8.7
|  | Raw Adjusted MD | MW | Non-Coincident | 4.462
|  |  |  | Coincident | 4.113
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.464
|  |  |  | Coincident | 4.133
|  | Date MD occurred |  | Non-Coincident | 07/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:30:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.076
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.482
|  |  |  | Coincident | 5.052
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.485
|  |  |  | Coincident | 5.077
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.994
|  |  |  | Coincident | 4.602
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.996
|  |  |  | Coincident | 4.625
| Williamstown 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.976
|  |  |  | Coincident | 0.622
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.027
|  |  |  | Coincident | 0.655
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.017
|  |  |  | Coincident | 0.087
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.941
|  |  |  | Coincident | 0.6
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.99
|  |  |  | Coincident | 0.632
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.892
|  |  |  | Coincident | 0.569
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.939
|  |  |  | Coincident | 0.599
| Williamstown South 11kV | Substation Rating | MVA | Non-Coincident | 4.94
|  |  |  | Coincident | 4.94
|  | Raw Adjusted MD | MW | Non-Coincident | 1.668
|  |  |  | Coincident | 1.346
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.669
|  |  |  | Coincident | 1.346
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.051
|  |  |  | Coincident | 0.26
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.796
|  |  |  | Coincident | 2.256
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.798
|  |  |  | Coincident | 2.257
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.347
|  |  |  | Coincident | 1.894
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.349
|  |  |  | Coincident | 1.895
| Balaklava 7.6kV | Substation Rating | MVA | Non-Coincident | 5.127
|  |  |  | Coincident | 5.127
|  | Raw Adjusted MD | MW | Non-Coincident | 2.579
|  |  |  | Coincident | 2.161
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.604
|  |  |  | Coincident | 2.186
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 08/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.076
|  |  |  | Coincident | 2.578
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.106
|  |  |  | Coincident | 2.608
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.675
|  |  |  | Coincident | 2.242
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.702
|  |  |  | Coincident | 2.268
| Dowlingville 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.019
|  |  |  | Coincident | 0.009
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.019
|  |  |  | Coincident | 0.009
|  | Date MD occurred |  | Non-Coincident | 17/11/2023
|  |  |  | Coincident | 08/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 2:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.034
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.034
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.031
|  |  |  | Coincident | 0.015
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.032
|  |  |  | Coincident | 0.015
| Ninnes 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 1.03
|  |  |  | Coincident | 1.03
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.045
|  |  |  | Coincident | 1.045
|  | Date MD occurred |  | Non-Coincident | 08/03/2024
|  |  |  | Coincident | 08/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.11
|  |  |  | Coincident | 1.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.127
|  |  |  | Coincident | 1.127
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.993
|  |  |  | Coincident | 0.993
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.007
|  |  |  | Coincident | 1.007
| Paskeville 11kV | Substation Rating | MVA | Non-Coincident | 1.229
|  |  |  | Coincident | 1.229
|  | Raw Adjusted MD | MW | Non-Coincident | 0.222
|  |  |  | Coincident | 0.162
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.224
|  |  |  | Coincident | 0.168
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 08/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.272
|  |  |  | Coincident | 0.198
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.274
|  |  |  | Coincident | 0.205
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.248
|  |  |  | Coincident | 0.181
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.25
|  |  |  | Coincident | 0.187
| Port Clinton 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.554
|  |  |  | Coincident | 0.272
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.568
|  |  |  | Coincident | 0.279
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 08/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.488
|  |  |  | Coincident | 0.24
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.501
|  |  |  | Coincident | 0.246
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.463
|  |  |  | Coincident | 0.227
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.475
|  |  |  | Coincident | 0.233
| Kadina 11kV | Substation Rating | MVA | Non-Coincident | 17.36
|  |  |  | Coincident | 17.36
|  | Raw Adjusted MD | MW | Non-Coincident | 7.737
|  |  |  | Coincident | 7.251
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.809
|  |  |  | Coincident | 7.349
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.003
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.854
|  |  |  | Coincident | 8.298
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.938
|  |  |  | Coincident | 8.41
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.947
|  |  |  | Coincident | 7.448
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.022
|  |  |  | Coincident | 7.549
| Moonta 11kV | Substation Rating | MVA | Non-Coincident | 12.8
|  |  |  | Coincident | 12.8
|  | Raw Adjusted MD | MW | Non-Coincident | 10.416
|  |  |  | Coincident | 10.416
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.501
|  |  |  | Coincident | 10.501
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.004
|  |  |  | Coincident | 0.004
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.507
|  |  |  | Coincident | 10.507
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.592
|  |  |  | Coincident | 10.592
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.305
|  |  |  | Coincident | 9.305
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.381
|  |  |  | Coincident | 9.381
| Wallaroo 11kV | Substation Rating | MVA | Non-Coincident | 17.813
|  |  |  | Coincident | 17.813
|  | Raw Adjusted MD | MW | Non-Coincident | 8.372
|  |  |  | Coincident | 8.372
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.458
|  |  |  | Coincident | 8.458
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.003
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.685
|  |  |  | Coincident | 9.685
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.784
|  |  |  | Coincident | 9.784
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.628
|  |  |  | Coincident | 8.628
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.716
|  |  |  | Coincident | 8.716
| Bordertown 11kV | Substation Rating | MVA | Non-Coincident | 14.182
|  |  |  | Coincident | 14.182
|  | Raw Adjusted MD | MW | Non-Coincident | 7.835
|  |  |  | Coincident | 5.345
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.863
|  |  |  | Coincident | 5.442
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.501
|  |  |  | Coincident | -0.004\
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.641
|  |  |  | Coincident | 5.505
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.679
|  |  |  | Coincident | 5.605
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.798
|  |  |  | Coincident | 5.069
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.833
|  |  |  | Coincident | 5.161
| Keith 11kV | Substation Rating | MVA | Non-Coincident | 16.59
|  |  |  | Coincident | 16.59
|  | Raw Adjusted MD | MW | Non-Coincident | 4.354
|  |  |  | Coincident | 3.936
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.597
|  |  |  | Coincident | 4.118
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.258
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.88
|  |  |  | Coincident | 4.412
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.152
|  |  |  | Coincident | 4.615
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.457
|  |  |  | Coincident | 4.029
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.706
|  |  |  | Coincident | 4.215
| Kumorna 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.49
|  |  |  | Coincident | 0.101
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.552
|  |  |  | Coincident | 0.14
|  | Date MD occurred |  | Non-Coincident | 29/12/2023
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 22:00:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.536
|  |  |  | Coincident | 0.111
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.604
|  |  |  | Coincident | 0.153
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.467
|  |  |  | Coincident | 0.096
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.527
|  |  |  | Coincident | 0.134
| Padthaway 11kV | Substation Rating | MVA | Non-Coincident | 13.628
|  |  |  | Coincident | 13.628
|  | Raw Adjusted MD | MW | Non-Coincident | 2.965
|  |  |  | Coincident | 2.213
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.037
|  |  |  | Coincident | 2.267
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.936
|  |  |  | Coincident | 2.191
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.007
|  |  |  | Coincident | 2.244
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.794
|  |  |  | Coincident | 2.085
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.861
|  |  |  | Coincident | 2.136
| Tintinara 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.848
|  |  |  | Coincident | 0.809
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.848
|  |  |  | Coincident | 0.809
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.927
|  |  |  | Coincident | 0.885
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.927
|  |  |  | Coincident | 0.885
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.84
|  |  |  | Coincident | 0.802
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.84
|  |  |  | Coincident | 0.802
| Inverness 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.655
|  |  |  | Coincident | 0.061
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.788
|  |  |  | Coincident | 0.08
|  | Date MD occurred |  | Non-Coincident | 02/11/2023
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 5:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.253
|  |  |  | Coincident | 0.023
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.304
|  |  |  | Coincident | 0.031
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.224
|  |  |  | Coincident | 0.021
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.27
|  |  |  | Coincident | 0.028
| Kingston SE 11kV | Substation Rating | MVA | Non-Coincident | 3.869
|  |  |  | Coincident | 3.869
|  | Raw Adjusted MD | MW | Non-Coincident | 3.186
|  |  |  | Coincident | 2.42
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.187
|  |  |  | Coincident | 2.422
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.067
|  |  |  | Coincident | 0.177
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.253
|  |  |  | Coincident | 2.471
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.254
|  |  |  | Coincident | 2.473
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.975
|  |  |  | Coincident | 2.26
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.976
|  |  |  | Coincident | 2.262
| Lucindale 11kV | Substation Rating | MVA | Non-Coincident | 3.597
|  |  |  | Coincident | 3.597
|  | Raw Adjusted MD | MW | Non-Coincident | 0.869
|  |  |  | Coincident | 0.75
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.881
|  |  |  | Coincident | 0.757
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.045
|  |  |  | Coincident | 0.053
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.119
|  |  |  | Coincident | 0.966
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.134
|  |  |  | Coincident | 0.974
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.029
|  |  |  | Coincident | 0.888
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.043
|  |  |  | Coincident | 0.896
| Naracoorte 11kV | Substation Rating | MVA | Non-Coincident | 29.838
|  |  |  | Coincident | 29.838
|  | Raw Adjusted MD | MW | Non-Coincident | 8.81
|  |  |  | Coincident | 7.889
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.935
|  |  |  | Coincident | 8.458
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.174
|  |  |  | Coincident | 0.463
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.735
|  |  |  | Coincident | 9.612
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.887
|  |  |  | Coincident | 10.305
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.312
|  |  |  | Coincident | 8.338
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.444
|  |  |  | Coincident | 8.939
| Naracoorte East 11kV | Substation Rating | MVA | Non-Coincident | 17.7
|  |  |  | Coincident | 17.7
|  | Raw Adjusted MD | MW | Non-Coincident | 3.96
|  |  |  | Coincident | 2.581
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.315
|  |  |  | Coincident | 2.924
|  | Date MD occurred |  | Non-Coincident | 24/01/2024
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 8:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.353
|  |  |  | Coincident | 0.06
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.462
|  |  |  | Coincident | 2.908
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.861
|  |  |  | Coincident | 3.294
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.248
|  |  |  | Coincident | 2.769
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.628
|  |  |  | Coincident | 3.136
| Copley Nepabunna 33kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.226
|  |  |  | Coincident | 0.198
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.229
|  |  |  | Coincident | 0.2
|  | Date MD occurred |  | Non-Coincident | 10/12/2023
|  |  |  | Coincident | 06/12/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 7:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.057
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.218
|  |  |  | Coincident | 0.191
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.22
|  |  |  | Coincident | 0.193
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.214
|  |  |  | Coincident | 0.187
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.216
|  |  |  | Coincident | 0.189
| Leigh Creek South 11kV | Substation Rating | MVA | Non-Coincident | 3.3
|  |  |  | Coincident | 3.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.859
|  |  |  | Coincident | 0.859
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.864
|  |  |  | Coincident | 0.864
|  | Date MD occurred |  | Non-Coincident | 06/12/2023
|  |  |  | Coincident | 06/12/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015
|  |  |  | Coincident | 0.015
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.957
|  |  |  | Coincident | 0.957
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.963
|  |  |  | Coincident | 0.963
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.876
|  |  |  | Coincident | 0.876
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.881
|  |  |  | Coincident | 0.881
| Belvedere Road 7.6kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.103
|  |  |  | Coincident | 0.091
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.106
|  |  |  | Coincident | 0.096
|  | Date MD occurred |  | Non-Coincident | 14/02/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 8:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.006
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.139
|  |  |  | Coincident | 0.123
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.142
|  |  |  | Coincident | 0.129
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.124
|  |  |  | Coincident | 0.11
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.127
|  |  |  | Coincident | 0.115
| Caloote 11kV | Substation Rating | MVA | Non-Coincident | 3.922
|  |  |  | Coincident | 3.922
|  | Raw Adjusted MD | MW | Non-Coincident | 1.583
|  |  |  | Coincident | 1.583
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.632
|  |  |  | Coincident | 1.632
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.032
|  |  |  | Coincident | 0.032
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.676
|  |  |  | Coincident | 1.676
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.728
|  |  |  | Coincident | 1.728
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.53
|  |  |  | Coincident | 1.53
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.577
|  |  |  | Coincident | 1.577
| Cambrai 11kV | Substation Rating | MVA | Non-Coincident | 1.296
|  |  |  | Coincident | 1.296
|  | Raw Adjusted MD | MW | Non-Coincident | 0.628
|  |  |  | Coincident | 0.547
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.629
|  |  |  | Coincident | 0.548
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.017
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.81
|  |  |  | Coincident | 0.706
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.812
|  |  |  | Coincident | 0.707
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.739
|  |  |  | Coincident | 0.644
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.741
|  |  |  | Coincident | 0.645
| Mannum Town 7.6kV | Substation Rating | MVA | Non-Coincident | 6.163
|  |  |  | Coincident | 6.163
|  | Raw Adjusted MD | MW | Non-Coincident | 4.279
|  |  |  | Coincident | 4.279
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.338
|  |  |  | Coincident | 4.338
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.088
|  |  |  | Coincident | 0.088
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.56
|  |  |  | Coincident | 4.56
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.623
|  |  |  | Coincident | 4.623
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.022
|  |  |  | Coincident | 4.022
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.078
|  |  |  | Coincident | 4.078
| Nildottie 11kV | Substation Rating | MVA | Non-Coincident | 4.4
|  |  |  | Coincident | 4.4
|  | Raw Adjusted MD | MW | Non-Coincident | 1.655
|  |  |  | Coincident | 1.506
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.663
|  |  |  | Coincident | 1.506
|  | Date MD occurred |  | Non-Coincident | 16/01/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 14:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.339
|  |  |  | Coincident | 0.012
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.795
|  |  |  | Coincident | 1.633
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.804
|  |  |  | Coincident | 1.633
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.751
|  |  |  | Coincident | 1.593
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.759
|  |  |  | Coincident | 1.593
| Palmer 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.01
|  |  |  | Coincident | 0.01
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.01
|  |  |  | Coincident | 0.01
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.003
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.023
|  |  |  | Coincident | 0.023
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.023
|  |  |  | Coincident | 0.023
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.022
|  |  |  | Coincident | 0.022
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.022
|  |  |  | Coincident | 0.022
| Pellaring Flat 11kV | Substation Rating | MVA | Non-Coincident | 0.13
|  |  |  | Coincident | 0.13
|  | Raw Adjusted MD | MW | Non-Coincident | 0.092
|  |  |  | Coincident | 0.092
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.093
|  |  |  | Coincident | 0.093
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.089
|  |  |  | Coincident | 0.089
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.09
|  |  |  | Coincident | 0.09
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.079
|  |  |  | Coincident | 0.079
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.08
|  |  |  | Coincident | 0.08
| Punyelroo 11kV | Substation Rating | MVA | Non-Coincident | 1.33
|  |  |  | Coincident | 1.33
|  | Raw Adjusted MD | MW | Non-Coincident | 0.302
|  |  |  | Coincident | 0.302
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.306
|  |  |  | Coincident | 0.306
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.221
|  |  |  | Coincident | 0.221
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.223
|  |  |  | Coincident | 0.223
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.204
|  |  |  | Coincident | 0.204
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.207
|  |  |  | Coincident | 0.207
| Teal Flat 11kV | Substation Rating | MVA | Non-Coincident | 7.766
|  |  |  | Coincident | 7.766
|  | Raw Adjusted MD | MW | Non-Coincident | 1.921
|  |  |  | Coincident | 1.471
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.022
|  |  |  | Coincident | 1.548
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 22:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.03
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.167
|  |  |  | Coincident | 1.658
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.281
|  |  |  | Coincident | 1.746
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.029
|  |  |  | Coincident | 1.553
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.136
|  |  |  | Coincident | 1.635
| Walker Flat 11kV | Substation Rating | MVA | Non-Coincident | 2.85
|  |  |  | Coincident | 2.85
|  | Raw Adjusted MD | MW | Non-Coincident | 1.248
|  |  |  | Coincident | 1.206
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.264
|  |  |  | Coincident | 1.221
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.247
|  |  |  | Coincident | 1.204
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.263
|  |  |  | Coincident | 1.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.146
|  |  |  | Coincident | 1.107
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.16
|  |  |  | Coincident | 1.121
| Burnside 11kV | Substation Rating | MVA | Non-Coincident | 30.5
|  |  |  | Coincident | 30.5
|  | Raw Adjusted MD | MW | Non-Coincident | 10.955
|  |  |  | Coincident | 9.38
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.066
|  |  |  | Coincident | 9.491
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.203
|  |  |  | Coincident | 1.634
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.079
|  |  |  | Coincident | 11.199
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.211
|  |  |  | Coincident | 11.332
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.578
|  |  |  | Coincident | 9.913
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.694
|  |  |  | Coincident | 10.031
| Campbelltown 11kV | Substation Rating | MVA | Non-Coincident | 73.859
|  |  |  | Coincident | 73.859
|  | Raw Adjusted MD | MW | Non-Coincident | 47.61
|  |  |  | Coincident | 42.103
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.106
|  |  |  | Coincident | 42.882
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.017
|  |  |  | Coincident | 6.334
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 57.071
|  |  |  | Coincident | 50.47
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 57.664
|  |  |  | Coincident | 51.402
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 50.758
|  |  |  | Coincident | 44.887
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 51.286
|  |  |  | Coincident | 45.717
| Clearview 11kV | Substation Rating | MVA | Non-Coincident | 26.597
|  |  |  | Coincident | 26.597
|  | Raw Adjusted MD | MW | Non-Coincident | 22.871
|  |  |  | Coincident | 18.528
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.944
|  |  |  | Coincident | 18.62
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.973
|  |  |  | Coincident | 3.495
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.08
|  |  |  | Coincident | 22.747
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.169
|  |  |  | Coincident | 22.861
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.757
|  |  |  | Coincident | 20.056
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.836
|  |  |  | Coincident | 20.156
| Golden Grove 11kV | Substation Rating | MVA | Non-Coincident | 87.663
|  |  |  | Coincident | 87.663
|  | Raw Adjusted MD | MW | Non-Coincident | 37.104
|  |  |  | Coincident | 30.092
|  | Raw Adjusted MD | MVA | Non-Coincident | 37.497
|  |  |  | Coincident | 30.59
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.703
|  |  |  | Coincident | 6.678
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 50.407
|  |  |  | Coincident | 40.881
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 50.942
|  |  |  | Coincident | 41.557
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 44.725
|  |  |  | Coincident | 36.273
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 45.199
|  |  |  | Coincident | 36.873
| Harrow 11kV | Substation Rating | MVA | Non-Coincident | 30.491
|  |  |  | Coincident | 30.491
|  | Raw Adjusted MD | MW | Non-Coincident | 18.679
|  |  |  | Coincident | 15.538
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.959
|  |  |  | Coincident | 15.871
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.314
|  |  |  | Coincident | 2.52
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.8
|  |  |  | Coincident | 18.967
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.142
|  |  |  | Coincident | 19.372
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.19
|  |  |  | Coincident | 16.796
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.493
|  |  |  | Coincident | 17.155
| Hillcrest 11kV | Substation Rating | MVA | Non-Coincident | 59.685
|  |  |  | Coincident | 59.685
|  | Raw Adjusted MD | MW | Non-Coincident | 30.8
|  |  |  | Coincident | 27.585
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.121
|  |  |  | Coincident | 28.078
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.44
|  |  |  | Coincident | 4.191
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.569
|  |  |  | Coincident | 34.543
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.971
|  |  |  | Coincident | 35.161
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 34.82
|  |  |  | Coincident | 31.186
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.183
|  |  |  | Coincident | 31.743
| Holden Hill 11kV | Substation Rating | MVA | Non-Coincident | 46.713
|  |  |  | Coincident | 46.713
|  | Raw Adjusted MD | MW | Non-Coincident | 31.461
|  |  |  | Coincident | 30.403
|  | Raw Adjusted MD | MVA | Non-Coincident | 31.771
|  |  |  | Coincident | 30.937
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.373
|  |  |  | Coincident | 4.373
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 39.658
|  |  |  | Coincident | 38.325
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.048
|  |  |  | Coincident | 38.997
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.652
|  |  |  | Coincident | 34.453
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.003
|  |  |  | Coincident | 35.058
| Hope Valley 11kV | Substation Rating | MVA | Non-Coincident | 29.1
|  |  |  | Coincident | 29.1
|  | Raw Adjusted MD | MW | Non-Coincident | 14.6
|  |  |  | Coincident | 11.81
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.793
|  |  |  | Coincident | 12.048
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.487
|  |  |  | Coincident | 3.884
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.578
|  |  |  | Coincident | 16.059
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.837
|  |  |  | Coincident | 16.383
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.152
|  |  |  | Coincident | 14.069
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.379
|  |  |  | Coincident | 14.353
| Ingle Farm 11kV | Substation Rating | MVA | Non-Coincident | 54.435
|  |  |  | Coincident | 54.435
|  | Raw Adjusted MD | MW | Non-Coincident | 30.532
|  |  |  | Coincident | 27.053
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.79
|  |  |  | Coincident | 27.431
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.527
|  |  |  | Coincident | 5.006
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 35.758
|  |  |  | Coincident | 31.683
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.061
|  |  |  | Coincident | 32.127
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.655
|  |  |  | Coincident | 28.934
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.932
|  |  |  | Coincident | 29.339
| Kent Town 11kV | Substation Rating | MVA | Non-Coincident | 57.503
|  |  |  | Coincident | 57.503
|  | Raw Adjusted MD | MW | Non-Coincident | 24.425
|  |  |  | Coincident | 23.145
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.301
|  |  |  | Coincident | 23.832
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.77
|  |  |  | Coincident | 1.89
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.196
|  |  |  | Coincident | 27.666
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.243
|  |  |  | Coincident | 28.486
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.809
|  |  |  | Coincident | 24.457
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 26.735
|  |  |  | Coincident | 25.182
| Kilburn South 11kV | Substation Rating | MVA | Non-Coincident | 36.1
|  |  |  | Coincident | 36.1
|  | Raw Adjusted MD | MW | Non-Coincident | 13.49
|  |  |  | Coincident | 10.985
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.739
|  |  |  | Coincident | 11.215
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.651
|  |  |  | Coincident | 1.674
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.104
|  |  |  | Coincident | 13.113
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.401
|  |  |  | Coincident | 13.388
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.523
|  |  |  | Coincident | 11.827
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.792
|  |  |  | Coincident | 12.074
| Linden Park 11kV | Substation Rating | MVA | Non-Coincident | 55.666
|  |  |  | Coincident | 55.666
|  | Raw Adjusted MD | MW | Non-Coincident | 31.903
|  |  |  | Coincident | 30.607
|  | Raw Adjusted MD | MVA | Non-Coincident | 32.422
|  |  |  | Coincident | 31.231
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 6.348
|  |  |  | Coincident | 4.464
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.507
|  |  |  | Coincident | 35.024
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.101
|  |  |  | Coincident | 35.738
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.547
|  |  |  | Coincident | 31.225
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.077
|  |  |  | Coincident | 31.862
| North Adelaide 11kV | Substation Rating | MVA | Non-Coincident | 70.118
|  |  |  | Coincident | 70.118
|  | Raw Adjusted MD | MW | Non-Coincident | 16.86
|  |  |  | Coincident | 16.8
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.461
|  |  |  | Coincident | 17.472
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.328
|  |  |  | Coincident | 1.18
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.192
|  |  |  | Coincident | 20.12
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.911
|  |  |  | Coincident | 20.926
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.922
|  |  |  | Coincident | 17.859
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.561
|  |  |  | Coincident | 18.573
| Northfield 11kV | Substation Rating | MVA | Non-Coincident | 26.532
|  |  |  | Coincident | 26.532
|  | Raw Adjusted MD | MW | Non-Coincident | 17.571
|  |  |  | Coincident | 14.557
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.004
|  |  |  | Coincident | 15.138
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.007
|  |  |  | Coincident | 2.579
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.495
|  |  |  | Coincident | 16.98
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.001
|  |  |  | Coincident | 17.657
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.432
|  |  |  | Coincident | 15.271
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.887
|  |  |  | Coincident | 15.88
| Norwood 11kV | Substation Rating | MVA | Non-Coincident | 85.597
|  |  |  | Coincident | 85.597
|  | Raw Adjusted MD | MW | Non-Coincident | 48.793
|  |  |  | Coincident | 47.794
|  | Raw Adjusted MD | MVA | Non-Coincident | 49.487
|  |  |  | Coincident | 47.878
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.765
|  |  |  | Coincident | 6.147
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 63.94
|  |  |  | Coincident | 62.63
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 64.85
|  |  |  | Coincident | 62.741
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 56.464
|  |  |  | Coincident | 55.307
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 57.267
|  |  |  | Coincident | 55.405
| Prospect 11kV | Substation Rating | MVA | Non-Coincident | 50.616
|  |  |  | Coincident | 50.616
|  | Raw Adjusted MD | MW | Non-Coincident | 24.561
|  |  |  | Coincident | 20.793
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.764
|  |  |  | Coincident | 21.1
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.824
|  |  |  | Coincident | 6.664
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.092
|  |  |  | Coincident | 27.595
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.358
|  |  |  | Coincident | 28.003
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.264
|  |  |  | Coincident | 25.163
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.507
|  |  |  | Coincident | 25.535
| Tea Tree Gully 11kV | Substation Rating | MVA | Non-Coincident | 49.863
|  |  |  | Coincident | 49.863
|  | Raw Adjusted MD | MW | Non-Coincident | 27.248
|  |  |  | Coincident | 23.407
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.395
|  |  |  | Coincident | 23.605
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.446
|  |  |  | Coincident | 4.251
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.861
|  |  |  | Coincident | 29.947
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 35.049
|  |  |  | Coincident | 30.201
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.424
|  |  |  | Coincident | 26.995
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 31.593
|  |  |  | Coincident | 27.223
| Woodforde 11kV | Substation Rating | MVA | Non-Coincident | 47.683
|  |  |  | Coincident | 47.683
|  | Raw Adjusted MD | MW | Non-Coincident | 29.684
|  |  |  | Coincident | 24.829
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.076
|  |  |  | Coincident | 25.182
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 17:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.547
|  |  |  | Coincident | 4.395
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 38.125
|  |  |  | Coincident | 31.889
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 38.628
|  |  |  | Coincident | 32.342
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 33.414
|  |  |  | Coincident | 27.949
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 33.855
|  |  |  | Coincident | 28.346
| Angle Vale 11kV | Substation Rating | MVA | Non-Coincident | 59.549
|  |  |  | Coincident | 59.549
|  | Raw Adjusted MD | MW | Non-Coincident | 21.11
|  |  |  | Coincident | 21.11
|  | Raw Adjusted MD | MVA | Non-Coincident | 21.438
|  |  |  | Coincident | 21.438
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.395
|  |  |  | Coincident | 0.395
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.577
|  |  |  | Coincident | 21.577
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.912
|  |  |  | Coincident | 21.912
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.902
|  |  |  | Coincident | 19.902
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.211
|  |  |  | Coincident | 20.211
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Direk 11kV | Substation Rating | MVA | Non-Coincident | 55.421
|  |  |  | Coincident | 55.421
|  | Raw Adjusted MD | MW | Non-Coincident | 21.655
|  |  |  | Coincident | 21.505
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.003
|  |  |  | Coincident | 21.87
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.305
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 23.267
|  |  |  | Coincident | 23.106
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 23.641
|  |  |  | Coincident | 23.498
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.861
|  |  |  | Coincident | 21.71
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.213
|  |  |  | Coincident | 22.078
| Edinburgh 11kV | Substation Rating | MVA | Non-Coincident | 57.058
|  |  |  | Coincident | 57.058
|  | Raw Adjusted MD | MW | Non-Coincident | 7.667
|  |  |  | Coincident | 7.537
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.731
|  |  |  | Coincident | 7.578
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.247
|  |  |  | Coincident | 0.093
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.379
|  |  |  | Coincident | 9.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.457
|  |  |  | Coincident | 9.27
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.592
|  |  |  | Coincident | 8.446
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.663
|  |  |  | Coincident | 8.492
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Elizabeth Downs 11kV | Substation Rating | MVA | Non-Coincident | 59.745
|  |  |  | Coincident | 59.745
|  | Raw Adjusted MD | MW | Non-Coincident | 35.611
|  |  |  | Coincident | 33.601
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.839
|  |  |  | Coincident | 33.799
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 5.163
|  |  |  | Coincident | 0.543
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.007
|  |  |  | Coincident | 44.355
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 47.309
|  |  |  | Coincident | 44.616
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.864
|  |  |  | Coincident | 39.502
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.132
|  |  |  | Coincident | 39.734
| Elizabeth Heights 11kV | Substation Rating | MVA | Non-Coincident | 27.565
|  |  |  | Coincident | 27.565
|  | Raw Adjusted MD | MW | Non-Coincident | 16.159
|  |  |  | Coincident | 15.857
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.227
|  |  |  | Coincident | 15.93
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.007
|  |  |  | Coincident | 0.267
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.372
|  |  |  | Coincident | 19.01
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.454
|  |  |  | Coincident | 19.098
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.398
|  |  |  | Coincident | 17.073
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.472
|  |  |  | Coincident | 17.152
| Elizabeth South 11kV | Substation Rating | MVA | Non-Coincident | 25.338
|  |  |  | Coincident | 25.338
|  | Raw Adjusted MD | MW | Non-Coincident | 8.769
|  |  |  | Coincident | 8.577
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.841
|  |  |  | Coincident | 8.65
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.097
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.068
|  |  |  | Coincident | 9.847
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.151
|  |  |  | Coincident | 9.932
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.236
|  |  |  | Coincident | 9.033
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.312
|  |  |  | Coincident | 9.111
| Evanston 11kV | Substation Rating | MVA | Non-Coincident | 57.668
|  |  |  | Coincident | 57.668
|  | Raw Adjusted MD | MW | Non-Coincident | 35.658
|  |  |  | Coincident | 35.658
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.917
|  |  |  | Coincident | 35.917
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.647
|  |  |  | Coincident | 1.647
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 42.068
|  |  |  | Coincident | 42.068
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 42.374
|  |  |  | Coincident | 42.374
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 38.101
|  |  |  | Coincident | 38.101
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 38.378
|  |  |  | Coincident | 38.378
| Evanston 33kV | Substation Rating | MVA | Non-Coincident | 11.875
|  |  |  | Coincident | 11.875
|  | Raw Adjusted MD | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 01/11/2023
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.082
|  |  |  | Coincident | 0.082
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.08
|  |  |  | Coincident | 0.08
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
| Parafield Gardens 11kV | Substation Rating | MVA | Non-Coincident | 74.497
|  |  |  | Coincident | 74.497
|  | Raw Adjusted MD | MW | Non-Coincident | 24.99
|  |  |  | Coincident | 24.99
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.105
|  |  |  | Coincident | 25.105
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.463
|  |  |  | Coincident | 0.463
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.608
|  |  |  | Coincident | 32.608
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.758
|  |  |  | Coincident | 32.758
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 28.803
|  |  |  | Coincident | 28.803
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.935
|  |  |  | Coincident | 28.935
| Paralowie 11kV | Substation Rating | MVA | Non-Coincident | 27.613
|  |  |  | Coincident | 27.613
|  | Raw Adjusted MD | MW | Non-Coincident | 17.358
|  |  |  | Coincident | 16.707
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.626
|  |  |  | Coincident | 16.874
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.006
|  |  |  | Coincident | 0.225
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.159
|  |  |  | Coincident | 18.44
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.455
|  |  |  | Coincident | 18.625
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.863
|  |  |  | Coincident | 17.193
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.139
|  |  |  | Coincident | 17.365
| Penfield 11kV | Substation Rating | MVA | Non-Coincident | 50.64
|  |  |  | Coincident | 50.64
|  | Raw Adjusted MD | MW | Non-Coincident | 16.805
|  |  |  | Coincident | 15.205
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.599
|  |  |  | Coincident | 15.427
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 8.411
|  |  |  | Coincident | 0.272
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.025
|  |  |  | Coincident | 18.118
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.97
|  |  |  | Coincident | 18.383
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.196
|  |  |  | Coincident | 16.464
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.056
|  |  |  | Coincident | 16.705
| Salisbury 11kV | Substation Rating | MVA | Non-Coincident | 71.319
|  |  |  | Coincident | 71.319
|  | Raw Adjusted MD | MW | Non-Coincident | 48.665
|  |  |  | Coincident | 48.665
|  | Raw Adjusted MD | MVA | Non-Coincident | 48.737
|  |  |  | Coincident | 48.737
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.73
|  |  |  | Coincident | 0.73
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 59.837
|  |  |  | Coincident | 59.837
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 59.926
|  |  |  | Coincident | 59.926
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 54.094
|  |  |  | Coincident | 54.094
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 54.174
|  |  |  | Coincident | 54.174
| Smithfield West 11kV | Substation Rating | MVA | Non-Coincident | 37.7
|  |  |  | Coincident | 37.7
|  | Raw Adjusted MD | MW | Non-Coincident | 24.645
|  |  |  | Coincident | 24.405
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.648
|  |  |  | Coincident | 24.411
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.009
|  |  |  | Coincident | 0.367
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.439
|  |  |  | Coincident | 28.163
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.443
|  |  |  | Coincident | 28.169
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.853
|  |  |  | Coincident | 25.601
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.856
|  |  |  | Coincident | 25.607
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Two Wells 11kV | Substation Rating | MVA | Non-Coincident | 16.3
|  |  |  | Coincident | 16.3
|  | Raw Adjusted MD | MW | Non-Coincident | 7.899
|  |  |  | Coincident | 4.078
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.902
|  |  |  | Coincident | 4.08
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 15:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.692
|  |  |  | Coincident | 4.168
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.504
|  |  |  | Coincident | 8.605
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.507
|  |  |  | Coincident | 8.609
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.638
|  |  |  | Coincident | 7.822
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.641
|  |  |  | Coincident | 7.825
| Virginia 11kV | Substation Rating | MVA | Non-Coincident | 14.8
|  |  |  | Coincident | 14.8
|  | Raw Adjusted MD | MW | Non-Coincident | 7.317
|  |  |  | Coincident | 6.636
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.565
|  |  |  | Coincident | 6.837
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.408
|  |  |  | Coincident | 0.151
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.611
|  |  |  | Coincident | 6.902
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.869
|  |  |  | Coincident | 7.112
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.971
|  |  |  | Coincident | 6.322
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.207
|  |  |  | Coincident | 6.513
| Aldinga 11kV | Substation Rating | MVA | Non-Coincident | 32.639
|  |  |  | Coincident | 32.639
|  | Raw Adjusted MD | MW | Non-Coincident | 17.546
|  |  |  | Coincident | 15.242
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.688
|  |  |  | Coincident | 15.355
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.407
|  |  |  | Coincident | 0.407
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.968
|  |  |  | Coincident | 15.609
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.114
|  |  |  | Coincident | 15.725
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.949
|  |  |  | Coincident | 13.855
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.078
|  |  |  | Coincident | 13.957
| American River 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.446
|  |  |  | Coincident | 0.396
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.447
|  |  |  | Coincident | 0.398
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.012
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.293
|  |  |  | Coincident | 0.26
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.294
|  |  |  | Coincident | 0.261
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.283
|  |  |  | Coincident | 0.251
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.284
|  |  |  | Coincident | 0.252
| Ascot Park 11kV | Substation Rating | MVA | Non-Coincident | 23.9
|  |  |  | Coincident | 23.9
|  | Raw Adjusted MD | MW | Non-Coincident | 19.42
|  |  |  | Coincident | 16.17
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.503
|  |  |  | Coincident | 16.243
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.287
|  |  |  | Coincident | 0.34
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.646
|  |  |  | Coincident | 17.191
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.734
|  |  |  | Coincident | 17.268
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.071
|  |  |  | Coincident | 15.047
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.148
|  |  |  | Coincident | 15.115
| Blackwood 11kV | Substation Rating | MVA | Non-Coincident | 57.883
|  |  |  | Coincident | 57.883
|  | Raw Adjusted MD | MW | Non-Coincident | 22.613
|  |  |  | Coincident | 22.613
|  | Raw Adjusted MD | MVA | Non-Coincident | 22.754
|  |  |  | Coincident | 22.754
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.518
|  |  |  | Coincident | 0.518
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 26.202
|  |  |  | Coincident | 26.202
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 26.365
|  |  |  | Coincident | 26.365
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 23.191
|  |  |  | Coincident | 23.191
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 23.335
|  |  |  | Coincident | 23.335
| Cape Jervis 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.617
|  |  |  | Coincident | 0.453
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.62
|  |  |  | Coincident | 0.455
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.02
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.306
|  |  |  | Coincident | 0.224
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.307
|  |  |  | Coincident | 0.225
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.289
|  |  |  | Coincident | 0.212
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.291
|  |  |  | Coincident | 0.213
| Cape Jervis 33kV | Substation Rating | MVA | Non-Coincident | 54.4
|  |  |  | Coincident | 54.4
|  | Raw Adjusted MD | MW | Non-Coincident | 7.767
|  |  |  | Coincident | 7.025
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.865
|  |  |  | Coincident | 13.341
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 28.859
|  |  |  | Coincident | -0.030\
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.237
|  |  |  | Coincident | 5.267
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.518
|  |  |  | Coincident | 10.002
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.525
|  |  |  | Coincident | 4.625
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.772
|  |  |  | Coincident | 8.782
| Clarence Gardens 11kV | Substation Rating | MVA | Non-Coincident | 37
|  |  |  | Coincident | 37
|  | Raw Adjusted MD | MW | Non-Coincident | 15.401
|  |  |  | Coincident | 15.401
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.527
|  |  |  | Coincident | 15.527
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.28
|  |  |  | Coincident | 0.28
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.116
|  |  |  | Coincident | 18.116
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.265
|  |  |  | Coincident | 18.265
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.1
|  |  |  | Coincident | 16.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.232
|  |  |  | Coincident | 16.232
| Clarendon 11kV | Substation Rating | MVA | Non-Coincident | 8.7
|  |  |  | Coincident | 8.7
|  | Raw Adjusted MD | MW | Non-Coincident | 2.847
|  |  |  | Coincident | 2.847
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.995
|  |  |  | Coincident | 2.995
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.077
|  |  |  | Coincident | 0.077
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.891
|  |  |  | Coincident | 2.891
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.041
|  |  |  | Coincident | 3.041
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.557
|  |  |  | Coincident | 2.557
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.69
|  |  |  | Coincident | 2.69
| Cudmore Park 11kV | Substation Rating | MVA | Non-Coincident | 24.65
|  |  |  | Coincident | 24.65
|  | Raw Adjusted MD | MW | Non-Coincident | 10.553
|  |  |  | Coincident | 7.48
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.981
|  |  |  | Coincident | 7.52
|  | Date MD occurred |  | Non-Coincident | 08/12/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 12:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 5.489
|  |  |  | Coincident | 0.183
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.009
|  |  |  | Coincident | 7.094
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.416
|  |  |  | Coincident | 7.132
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.187
|  |  |  | Coincident | 6.512
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.56
|  |  |  | Coincident | 6.547
| Glenelg North 11kV | Substation Rating | MVA | Non-Coincident | 27.913
|  |  |  | Coincident | 27.913
|  | Raw Adjusted MD | MW | Non-Coincident | 17.941
|  |  |  | Coincident | 17.046
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.226
|  |  |  | Coincident | 17.317
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.321
|  |  |  | Coincident | 0.214
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.957
|  |  |  | Coincident | 18.962
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.274
|  |  |  | Coincident | 19.262
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.772
|  |  |  | Coincident | 16.886
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.055
|  |  |  | Coincident | 17.154
| Goolwa 11kV | Substation Rating | MVA | Non-Coincident | 33.671
|  |  |  | Coincident | 33.671
|  | Raw Adjusted MD | MW | Non-Coincident | 15.711
|  |  |  | Coincident | 11.689
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.806
|  |  |  | Coincident | 11.748
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.383
|  |  |  | Coincident | 0.383
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.187
|  |  |  | Coincident | 11.3
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.279
|  |  |  | Coincident | 11.357
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.566
|  |  |  | Coincident | 9.349
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.642
|  |  |  | Coincident | 9.396
| Hackham 11kV | Substation Rating | MVA | Non-Coincident | 31.6
|  |  |  | Coincident | 31.6
|  | Raw Adjusted MD | MW | Non-Coincident | 13.385
|  |  |  | Coincident | 13.375
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.414
|  |  |  | Coincident | 13.409
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.007
|  |  |  | Coincident | 0.317
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.918
|  |  |  | Coincident | 15.906
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.952
|  |  |  | Coincident | 15.946
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.066
|  |  |  | Coincident | 14.055
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.096
|  |  |  | Coincident | 14.091
| Happy Valley 11kV | Substation Rating | MVA | Non-Coincident | 59.671
|  |  |  | Coincident | 59.671
|  | Raw Adjusted MD | MW | Non-Coincident | 28.154
|  |  |  | Coincident | 28.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 28.371
|  |  |  | Coincident | 28.349
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.385
|  |  |  | Coincident | 0.619
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.698
|  |  |  | Coincident | 34.668
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.966
|  |  |  | Coincident | 34.938
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.461
|  |  |  | Coincident | 30.435
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.696
|  |  |  | Coincident | 30.672
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Hay Flat 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.084
|  |  |  | Coincident | 0.078
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.085
|  |  |  | Coincident | 0.078
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.091
|  |  |  | Coincident | 0.085
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.093
|  |  |  | Coincident | 0.085
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.081
|  |  |  | Coincident | 0.075
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.082
|  |  |  | Coincident | 0.075
| Keswick 11kV | Substation Rating | MVA | Non-Coincident | 50.567
|  |  |  | Coincident | 50.567
|  | Raw Adjusted MD | MW | Non-Coincident | 25.62
|  |  |  | Coincident | 19.376
|  | Raw Adjusted MD | MVA | Non-Coincident | 26.741
|  |  |  | Coincident | 19.681
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.066
|  |  |  | Coincident | 0.232
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 29.541
|  |  |  | Coincident | 22.341
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.833
|  |  |  | Coincident | 22.692
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 26.851
|  |  |  | Coincident | 20.307
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 28.026
|  |  |  | Coincident | 20.626
| Kingscote 11kV | Substation Rating | MVA | Non-Coincident | 8.5
|  |  |  | Coincident | 8.5
|  | Raw Adjusted MD | MW | Non-Coincident | 2.967
|  |  |  | Coincident | 2.716
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.97
|  |  |  | Coincident | 2.811
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.791
|  |  |  | Coincident | 0.051
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.341
|  |  |  | Coincident | 1.062
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.343
|  |  |  | Coincident | 1.099
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.223
|  |  |  | Coincident | 1.008
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.225
|  |  |  | Coincident | 1.044
| Kingswood 11kV | Substation Rating | MVA | Non-Coincident | 69.116
|  |  |  | Coincident | 69.116
|  | Raw Adjusted MD | MW | Non-Coincident | 38.331
|  |  |  | Coincident | 38.331
|  | Raw Adjusted MD | MVA | Non-Coincident | 38.934
|  |  |  | Coincident | 38.934
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.61
|  |  |  | Coincident | 0.61
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 47.554
|  |  |  | Coincident | 47.554
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 48.302
|  |  |  | Coincident | 48.302
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 41.933
|  |  |  | Coincident | 41.933
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.593
|  |  |  | Coincident | 42.593
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Lower Mitcham 11kV | Substation Rating | MVA | Non-Coincident | 25.742
|  |  |  | Coincident | 25.742
|  | Raw Adjusted MD | MW | Non-Coincident | 15.483
|  |  |  | Coincident | 15.483
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.609
|  |  |  | Coincident | 15.609
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.29
|  |  |  | Coincident | 0.29
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.47
|  |  |  | Coincident | 19.47
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 19.628
|  |  |  | Coincident | 19.628
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.136
|  |  |  | Coincident | 17.136
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.276
|  |  |  | Coincident | 17.276
| MacGillivray 11kV | Substation Rating | MVA | Non-Coincident | 2.398
|  |  |  | Coincident | 2.398
|  | Raw Adjusted MD | MW | Non-Coincident | 1.632
|  |  |  | Coincident | 1.558
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.637
|  |  |  | Coincident | 1.564
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.029
|  |  |  | Coincident | 0.029
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.401
|  |  |  | Coincident | 1.337
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.405
|  |  |  | Coincident | 1.343
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.302
|  |  |  | Coincident | 1.242
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.306
|  |  |  | Coincident | 1.248
| McLaren Flat TF1 11kV | Substation Rating | MVA | Non-Coincident | 15.4
|  |  |  | Coincident | 15.4
|  | Raw Adjusted MD | MW | Non-Coincident | 7.254
|  |  |  | Coincident | 6.925
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.481
|  |  |  | Coincident | 7.117
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.285
|  |  |  | Coincident | 0.127
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.226
|  |  |  | Coincident | 6.898
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.452
|  |  |  | Coincident | 7.089
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.449
|  |  |  | Coincident | 6.157
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.651
|  |  |  | Coincident | 6.327
| McLaren Flat TF2 11kV | Substation Rating | MVA | Non-Coincident | 16
|  |  |  | Coincident | 16
|  | Raw Adjusted MD | MW | Non-Coincident | 2.485
|  |  |  | Coincident | 2.067
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.583
|  |  |  | Coincident | 2.158
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.038
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.165
|  |  |  | Coincident | 1.801
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.251
|  |  |  | Coincident | 1.88
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.979
|  |  |  | Coincident | 1.646
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.057
|  |  |  | Coincident | 1.719
| McLaren Vale 11kV | Substation Rating | MVA | Non-Coincident | 5.395
|  |  |  | Coincident | 5.395
|  | Raw Adjusted MD | MW | Non-Coincident | 2.178
|  |  |  | Coincident | 1.979
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.293
|  |  |  | Coincident | 2.083
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.046
|  |  |  | Coincident | 0.046
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.635
|  |  |  | Coincident | 2.395
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.774
|  |  |  | Coincident | 2.521
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.505
|  |  |  | Coincident | 2.276
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.637
|  |  |  | Coincident | 2.396
| McLaren Vale Vineyard 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.15
|  |  |  | Coincident | 0.139
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.152
|  |  |  | Coincident | 0.139
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.177
|  |  |  | Coincident | 0.164
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.179
|  |  |  | Coincident | 0.164
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.155
|  |  |  | Coincident | 0.145
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.158
|  |  |  | Coincident | 0.145
| Morphett Vale East 11kV | Substation Rating | MVA | Non-Coincident | 57.35
|  |  |  | Coincident | 57.35
|  | Raw Adjusted MD | MW | Non-Coincident | 24.873
|  |  |  | Coincident | 24.546
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.956
|  |  |  | Coincident | 24.655
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.668
|  |  |  | Coincident | 0.668
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 31.193
|  |  |  | Coincident | 30.782
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 31.296
|  |  |  | Coincident | 30.92
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.708
|  |  |  | Coincident | 27.343
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.8
|  |  |  | Coincident | 27.465
| Morphettville 11kV | Substation Rating | MVA | Non-Coincident | 29.8
|  |  |  | Coincident | 29.8
|  | Raw Adjusted MD | MW | Non-Coincident | 14.986
|  |  |  | Coincident | 14.986
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.084
|  |  |  | Coincident | 15.334
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.116
|  |  |  | Coincident | 0.306
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.517
|  |  |  | Coincident | 21.517
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.658
|  |  |  | Coincident | 22.017
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.272
|  |  |  | Coincident | 19.272
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.398
|  |  |  | Coincident | 19.72
| Myponga 11kV | Substation Rating | MVA | Non-Coincident | 13.261
|  |  |  | Coincident | 13.261
|  | Raw Adjusted MD | MW | Non-Coincident | 5.667
|  |  |  | Coincident | 5.166
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.897
|  |  |  | Coincident | 5.359
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.122
|  |  |  | Coincident | 0.122
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.696
|  |  |  | Coincident | 5.192
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.927
|  |  |  | Coincident | 5.386
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.246
|  |  |  | Coincident | 4.782
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.459
|  |  |  | Coincident | 4.961
| Noarlunga Centre 11kV | Substation Rating | MVA | Non-Coincident | 28.272
|  |  |  | Coincident | 28.272
|  | Raw Adjusted MD | MW | Non-Coincident | 13.884
|  |  |  | Coincident | 12.548
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.331
|  |  |  | Coincident | 12.66
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.662
|  |  |  | Coincident | 0.182
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.055
|  |  |  | Coincident | 16.318
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.637
|  |  |  | Coincident | 16.464
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.76
|  |  |  | Coincident | 14.244
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.267
|  |  |  | Coincident | 14.371
| North Unley 11kV | Substation Rating | MVA | Non-Coincident | 26.008
|  |  |  | Coincident | 26.008
|  | Raw Adjusted MD | MW | Non-Coincident | 13.315
|  |  |  | Coincident | 11.42
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.634
|  |  |  | Coincident | 11.511
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.035
|  |  |  | Coincident | 0.178
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.219
|  |  |  | Coincident | 14.768
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 17.631
|  |  |  | Coincident | 14.886
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.136
|  |  |  | Coincident | 12.982
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.498
|  |  |  | Coincident | 13.085
| Oaklands 11kV | Substation Rating | MVA | Non-Coincident | 58.069
|  |  |  | Coincident | 58.069
|  | Raw Adjusted MD | MW | Non-Coincident | 33.025
|  |  |  | Coincident | 33.025
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.433
|  |  |  | Coincident | 33.433
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.538
|  |  |  | Coincident | 0.538
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 40.062
|  |  |  | Coincident | 40.062
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 40.558
|  |  |  | Coincident | 40.558
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 35.276
|  |  |  | Coincident | 35.276
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 35.712
|  |  |  | Coincident | 35.712
| Panorama 11kV | Substation Rating | MVA | Non-Coincident | 58.509
|  |  |  | Coincident | 58.509
|  | Raw Adjusted MD | MW | Non-Coincident | 20.9
|  |  |  | Coincident | 20.9
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.972
|  |  |  | Coincident | 20.972
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.365
|  |  |  | Coincident | 0.365
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.226
|  |  |  | Coincident | 25.226
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.313
|  |  |  | Coincident | 25.313
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.52
|  |  |  | Coincident | 22.52
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.597
|  |  |  | Coincident | 22.597
| Penneshaw 11kV | Substation Rating | MVA | Non-Coincident | 2.715
|  |  |  | Coincident | 2.715
|  | Raw Adjusted MD | MW | Non-Coincident | 0.754
|  |  |  | Coincident | 0.676
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.755
|  |  |  | Coincident | 0.677
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.013
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.799
|  |  |  | Coincident | 0.716
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.8
|  |  |  | Coincident | 0.718
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.717
|  |  |  | Coincident | 0.643
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.718
|  |  |  | Coincident | 0.644
| Plympton 11kV | Substation Rating | MVA | Non-Coincident | 28.429
|  |  |  | Coincident | 28.429
|  | Raw Adjusted MD | MW | Non-Coincident | 18.085
|  |  |  | Coincident | 17.772
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.25
|  |  |  | Coincident | 17.939
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.239
|  |  |  | Coincident | 0.288
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.348
|  |  |  | Coincident | 20.979
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 21.543
|  |  |  | Coincident | 21.175
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.229
|  |  |  | Coincident | 18.896
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.404
|  |  |  | Coincident | 19.073
| Port Noarlunga 11kV | Substation Rating | MVA | Non-Coincident | 58.045
|  |  |  | Coincident | 58.045
|  | Raw Adjusted MD | MW | Non-Coincident | 27.495
|  |  |  | Coincident | 27.44
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.522
|  |  |  | Coincident | 27.487
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.012
|  |  |  | Coincident | 0.579
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 30.167
|  |  |  | Coincident | 30.106
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 30.196
|  |  |  | Coincident | 30.157
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 27.027
|  |  |  | Coincident | 26.973
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 27.053
|  |  |  | Coincident | 27.019
| Port Stanvac 11kV | Substation Rating | MVA | Non-Coincident | 56.195
|  |  |  | Coincident | 56.195
|  | Raw Adjusted MD | MW | Non-Coincident | 27.627
|  |  |  | Coincident | 27.627
|  | Raw Adjusted MD | MVA | Non-Coincident | 27.883
|  |  |  | Coincident | 28.076
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 6.515
|  |  |  | Coincident | 0.563
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 32.607
|  |  |  | Coincident | 29.998
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 32.909
|  |  |  | Coincident | 30.485
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 29.211
|  |  |  | Coincident | 26.874
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 29.482
|  |  |  | Coincident | 27.31
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Rapid Bay 11kV | Substation Rating | MVA | Non-Coincident | 0.41
|  |  |  | Coincident | 0.41
|  | Raw Adjusted MD | MW | Non-Coincident | 0.036
|  |  |  | Coincident | 0.018
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.036
|  |  |  | Coincident | 0.018
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 2:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.038
|  |  |  | Coincident | 0.019
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.038
|  |  |  | Coincident | 0.019
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.033
|  |  |  | Coincident | 0.017
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.034
|  |  |  | Coincident | 0.017
| Salt Cliffs 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.126
|  |  |  | Coincident | 0.117
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.128
|  |  |  | Coincident | 0.117
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.013
|  |  |  | Coincident | 0.006
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.116
|  |  |  | Coincident | 0.107
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.117
|  |  |  | Coincident | 0.107
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.108
|  |  |  | Coincident | 0.101
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.11
|  |  |  | Coincident | 0.101
| Seacombe 11kV | Substation Rating | MVA | Non-Coincident | 59.87
|  |  |  | Coincident | 59.87
|  | Raw Adjusted MD | MW | Non-Coincident | 35.573
|  |  |  | Coincident | 35.127
|  | Raw Adjusted MD | MVA | Non-Coincident | 35.83
|  |  |  | Coincident | 35.387
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.468
|  |  |  | Coincident | 0.656
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.082
|  |  |  | Coincident | 40.566
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 41.378
|  |  |  | Coincident | 40.866
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 36.38
|  |  |  | Coincident | 35.923
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 36.642
|  |  |  | Coincident | 36.189
| Seaford 11kV | Substation Rating | MVA | Non-Coincident | 16.7
|  |  |  | Coincident | 16.7
|  | Raw Adjusted MD | MW | Non-Coincident | 6.739
|  |  |  | Coincident | 6.66
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.774
|  |  |  | Coincident | 6.694
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.034
|  |  |  | Coincident | 3.034
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.589
|  |  |  | Coincident | 10.589
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.645
|  |  |  | Coincident | 10.645
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.311
|  |  |  | Coincident | 9.311
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.359
|  |  |  | Coincident | 9.359
| Second Valley 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.252
|  |  |  | Coincident | 0.164
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.265
|  |  |  | Coincident | 0.173
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.013
|  |  |  | Coincident | 0.013
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.275
|  |  |  | Coincident | 0.179
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.289
|  |  |  | Coincident | 0.188
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.249
|  |  |  | Coincident | 0.162
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.262
|  |  |  | Coincident | 0.171
| Sheidow Park 11kV | Substation Rating | MVA | Non-Coincident | 35.372
|  |  |  | Coincident | 35.372
|  | Raw Adjusted MD | MW | Non-Coincident | 24.11
|  |  |  | Coincident | 24.099
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.282
|  |  |  | Coincident | 24.296
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.01
|  |  |  | Coincident | 0.477
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 27.937
|  |  |  | Coincident | 27.924
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.137
|  |  |  | Coincident | 28.153
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 24.329
|  |  |  | Coincident | 24.318
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 24.503
|  |  |  | Coincident | 24.517
| Square Water Hole 11kV | Substation Rating | MVA | Non-Coincident | 7.125
|  |  |  | Coincident | 7.125
|  | Raw Adjusted MD | MW | Non-Coincident | 3.81
|  |  |  | Coincident | 3.545
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.913
|  |  |  | Coincident | 3.661
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.106
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.622
|  |  |  | Coincident | 3.37
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.72
|  |  |  | Coincident | 3.481
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.361
|  |  |  | Coincident | 3.127
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.451
|  |  |  | Coincident | 3.229
| Tonsley Park 11kV | Substation Rating | MVA | Non-Coincident | 39.831
|  |  |  | Coincident | 39.831
|  | Raw Adjusted MD | MW | Non-Coincident | 16.918
|  |  |  | Coincident | 15.618
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.194
|  |  |  | Coincident | 15.674
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.022
|  |  |  | Coincident | 0.206
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.748
|  |  |  | Coincident | 16.384
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.037
|  |  |  | Coincident | 16.443
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.013
|  |  |  | Coincident | 14.783
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.274
|  |  |  | Coincident | 14.836
| Victor Harbor 11kV | Substation Rating | MVA | Non-Coincident | 59.755
|  |  |  | Coincident | 59.755
|  | Raw Adjusted MD | MW | Non-Coincident | 24.795
|  |  |  | Coincident | 21.58
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.842
|  |  |  | Coincident | 21.619
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.573
|  |  |  | Coincident | 0.573
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.178
|  |  |  | Coincident | 21.913
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.226
|  |  |  | Coincident | 21.953
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 21.783
|  |  |  | Coincident | 18.958
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 21.824
|  |  |  | Coincident | 18.992
| Willunga 11kV | Substation Rating | MVA | Non-Coincident | 6.9
|  |  |  | Coincident | 6.9
|  | Raw Adjusted MD | MW | Non-Coincident | 3.651
|  |  |  | Coincident | 3.634
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.683
|  |  |  | Coincident | 3.667
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002
|  |  |  | Coincident | 0.117
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.505
|  |  |  | Coincident | 3.488
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.536
|  |  |  | Coincident | 3.52
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.134
|  |  |  | Coincident | 3.12
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.162
|  |  |  | Coincident | 3.148
| Willunga 33kV | Substation Rating | MVA | Non-Coincident | 9.75
|  |  |  | Coincident | 9.75
|  | Raw Adjusted MD | MW | Non-Coincident | 2.517
|  |  |  | Coincident | 2.316
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.566
|  |  |  | Coincident | 2.366
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.05
|  |  |  | Coincident | 0.05
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.877
|  |  |  | Coincident | 2.647
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.932
|  |  |  | Coincident | 2.704
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.509
|  |  |  | Coincident | 2.308
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.557
|  |  |  | Coincident | 2.358
| Wirrina Cove 11kV | Substation Rating | MVA | Non-Coincident | 1.95
|  |  |  | Coincident | 1.95
|  | Raw Adjusted MD | MW | Non-Coincident | 0.632
|  |  |  | Coincident | 0.588
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.641
|  |  |  | Coincident | 0.588
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.016
|  |  |  | Coincident | 0.007
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.728
|  |  |  | Coincident | 0.677
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.739
|  |  |  | Coincident | 0.677
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.652
|  |  |  | Coincident | 0.606
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.661
|  |  |  | Coincident | 0.606
| Yankalilla 11kV | Substation Rating | MVA | Non-Coincident | 16.5
|  |  |  | Coincident | 16.5
|  | Raw Adjusted MD | MW | Non-Coincident | 7.203
|  |  |  | Coincident | 5.12
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.323
|  |  |  | Coincident | 5.205
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.003
|  |  |  | Coincident | 0.161
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.364
|  |  |  | Coincident | 4.523
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.469
|  |  |  | Coincident | 4.598
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.258
|  |  |  | Coincident | 4.448
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.362
|  |  |  | Coincident | 4.522
| Yankalilla 33kV | Substation Rating | MVA | Non-Coincident | 17.813
|  |  |  | Coincident | 17.813
|  | Raw Adjusted MD | MW | Non-Coincident | 1.301
|  |  |  | Coincident | 0.7
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.301
|  |  |  | Coincident | 0.707
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.028
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.391
|  |  |  | Coincident | 0.749
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.391
|  |  |  | Coincident | 0.757
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.266
|  |  |  | Coincident | 0.682
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.266
|  |  |  | Coincident | 0.689
| Yankalilla Hill 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.126
|  |  |  | Coincident | 0.117
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.128
|  |  |  | Coincident | 0.117
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.127
|  |  |  | Coincident | 0.118
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.129
|  |  |  | Coincident | 0.118
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.113
|  |  |  | Coincident | 0.105
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.115
|  |  |  | Coincident | 0.105
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Athol Park 11kV | Substation Rating | MVA | Non-Coincident | 25.976
|  |  |  | Coincident | 25.976
|  | Raw Adjusted MD | MW | Non-Coincident | 16.03
|  |  |  | Coincident | 15.122
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.379
|  |  |  | Coincident | 15.481
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.269
|  |  |  | Coincident | 0.315
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.009
|  |  |  | Coincident | 15.102
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.357
|  |  |  | Coincident | 15.46
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.759
|  |  |  | Coincident | 13.923
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.08
|  |  |  | Coincident | 14.253
| Blackpool 11kV | Substation Rating | MVA | Non-Coincident | 34.664
|  |  |  | Coincident | 34.664
|  | Raw Adjusted MD | MW | Non-Coincident | 12.508
|  |  |  | Coincident | 10.336
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.553
|  |  |  | Coincident | 10.389
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.234
|  |  |  | Coincident | 0.234
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.07
|  |  |  | Coincident | 12.453
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.125
|  |  |  | Coincident | 12.517
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.389
|  |  |  | Coincident | 11.064
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.438
|  |  |  | Coincident | 11.12
| Cavan 11kV | Substation Rating | MVA | Non-Coincident | 56.653
|  |  |  | Coincident | 56.653
|  | Raw Adjusted MD | MW | Non-Coincident | 28.065
|  |  |  | Coincident | 26.75
|  | Raw Adjusted MD | MVA | Non-Coincident | 29.257
|  |  |  | Coincident | 27.358
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.083
|  |  |  | Coincident | 0.384
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.577
|  |  |  | Coincident | 32.957
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 36.045
|  |  |  | Coincident | 33.706
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 31.432
|  |  |  | Coincident | 29.959
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.767
|  |  |  | Coincident | 30.64
| Cheltenham 11kV | Substation Rating | MVA | Non-Coincident | 30.7
|  |  |  | Coincident | 30.7
|  | Raw Adjusted MD | MW | Non-Coincident | 9.94
|  |  |  | Coincident | 9.04
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.964
|  |  |  | Coincident | 9.067
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.356
|  |  |  | Coincident | 0.159
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 11.503
|  |  |  | Coincident | 10.461
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 11.531
|  |  |  | Coincident | 10.492
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 10.316
|  |  |  | Coincident | 9.382
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 10.341
|  |  |  | Coincident | 9.41
| Cheltenham 33kV | Substation Rating | MVA | Non-Coincident | 33.1
|  |  |  | Coincident | 33.1
|  | Raw Adjusted MD | MW | Non-Coincident | 3.014
|  |  |  | Coincident | 1.876
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.177
|  |  |  | Coincident | 1.992
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.123
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.132
|  |  |  | Coincident | 1.949
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.302
|  |  |  | Coincident | 2.07
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.058
|  |  |  | Coincident | 1.903
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.224
|  |  |  | Coincident | 2.021
| Croydon 11kV | Substation Rating | MVA | Non-Coincident | 58.499
|  |  |  | Coincident | 58.499
|  | Raw Adjusted MD | MW | Non-Coincident | 20.08
|  |  |  | Coincident | 19.931
|  | Raw Adjusted MD | MVA | Non-Coincident | 20.331
|  |  |  | Coincident | 20.276
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.006
|  |  |  | Coincident | 0.293
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 22.352
|  |  |  | Coincident | 22.186
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.632
|  |  |  | Coincident | 22.57
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 20.063
|  |  |  | Coincident | 19.914
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 20.315
|  |  |  | Coincident | 20.26
| Croydon Park 11kV | Substation Rating | MVA | Non-Coincident | 27.255
|  |  |  | Coincident | 27.255
|  | Raw Adjusted MD | MW | Non-Coincident | 14.393
|  |  |  | Coincident | 14.296
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.538
|  |  |  | Coincident | 14.472
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.218
|  |  |  | Coincident | 0.258
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.612
|  |  |  | Coincident | 16.5
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.779
|  |  |  | Coincident | 16.703
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 15.046
|  |  |  | Coincident | 14.945
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 15.198
|  |  |  | Coincident | 15.129
| Findon 11kV | Substation Rating | MVA | Non-Coincident | 24.821
|  |  |  | Coincident | 24.821
|  | Raw Adjusted MD | MW | Non-Coincident | 15.959
|  |  |  | Coincident | 14.13
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.035
|  |  |  | Coincident | 14.201
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.495
|  |  |  | Coincident | 0.222
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 18.234
|  |  |  | Coincident | 16.145
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.321
|  |  |  | Coincident | 16.226
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.488
|  |  |  | Coincident | 14.599
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.567
|  |  |  | Coincident | 14.672
| Flinders Park 11kV | Substation Rating | MVA | Non-Coincident | 29.4
|  |  |  | Coincident | 29.4
|  | Raw Adjusted MD | MW | Non-Coincident | 18.028
|  |  |  | Coincident | 16.348
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.201
|  |  |  | Coincident | 16.531
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.258
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.235
|  |  |  | Coincident | 18.35
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.43
|  |  |  | Coincident | 18.555
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.996
|  |  |  | Coincident | 16.319
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.169
|  |  |  | Coincident | 16.502
| Fulham Gardens 11kV | Substation Rating | MVA | Non-Coincident | 55.671
|  |  |  | Coincident | 55.671
|  | Raw Adjusted MD | MW | Non-Coincident | 32.998
|  |  |  | Coincident | 28.197
|  | Raw Adjusted MD | MVA | Non-Coincident | 33.497
|  |  |  | Coincident | 28.607
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.494
|  |  |  | Coincident | 0.494
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 36.861
|  |  |  | Coincident | 31.498
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 37.418
|  |  |  | Coincident | 31.956
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 32.175
|  |  |  | Coincident | 27.493
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 32.661
|  |  |  | Coincident | 27.893
| Glanville 11kV | Substation Rating | MVA | Non-Coincident | 23.943
|  |  |  | Coincident | 23.943
|  | Raw Adjusted MD | MW | Non-Coincident | 14.359
|  |  |  | Coincident | 11.284
|  | Raw Adjusted MD | MVA | Non-Coincident | 14.409
|  |  |  | Coincident | 11.314
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.249
|  |  |  | Coincident | 0.249
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 16.446
|  |  |  | Coincident | 12.924
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.503
|  |  |  | Coincident | 12.959
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.389
|  |  |  | Coincident | 11.307
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.439
|  |  |  | Coincident | 11.338
| Henley South 11kV | Substation Rating | MVA | Non-Coincident | 57.075
|  |  |  | Coincident | 57.075
|  | Raw Adjusted MD | MW | Non-Coincident | 30.078
|  |  |  | Coincident | 25.515
|  | Raw Adjusted MD | MVA | Non-Coincident | 30.406
|  |  |  | Coincident | 25.801
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.079
|  |  |  | Coincident | 0.483
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 34.613
|  |  |  | Coincident | 29.363
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 34.99
|  |  |  | Coincident | 29.692
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 30.412
|  |  |  | Coincident | 25.798
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 30.743
|  |  |  | Coincident | 26.087
| Kilburn 11kV | Substation Rating | MVA | Non-Coincident | 85.054
|  |  |  | Coincident | 85.054
|  | Raw Adjusted MD | MW | Non-Coincident | 37.778
|  |  |  | Coincident | 21.85
|  | Raw Adjusted MD | MVA | Non-Coincident | 40.723
|  |  |  | Coincident | 23.566
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 8:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 3.942
|  |  |  | Coincident | 2.498
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 41.912
|  |  |  | Coincident | 26.459
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 45.179
|  |  |  | Coincident | 28.538
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 39.454
|  |  |  | Coincident | 24.907
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 42.529
|  |  |  | Coincident | 26.864
| Kilburn Bus A CMP 11kV | Substation Rating | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MW | Non-Coincident | 8.3
|  |  |  | Coincident | 4.294
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.021
|  |  |  | Coincident | 4.667
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 9:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.723
|  |  |  | Coincident | 5.03
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.568
|  |  |  | Coincident | 5.468
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.033
|  |  |  | Coincident | 4.674
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.819
|  |  |  | Coincident | 5.08
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Kilkenny 11kV | Substation Rating | MVA | Non-Coincident | 55.517
|  |  |  | Coincident | 55.517
|  | Raw Adjusted MD | MW | Non-Coincident | 17.037
|  |  |  | Coincident | 17.037
|  | Raw Adjusted MD | MVA | Non-Coincident | 17.945
|  |  |  | Coincident | 17.945
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.172
|  |  |  | Coincident | 0.172
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.847
|  |  |  | Coincident | 17.847
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.798
|  |  |  | Coincident | 18.798
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.798
|  |  |  | Coincident | 16.798
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 17.693
|  |  |  | Coincident | 17.693
| Largs North 11kV | Substation Rating | MVA | Non-Coincident | 35.526
|  |  |  | Coincident | 35.526
|  | Raw Adjusted MD | MW | Non-Coincident | 13.361
|  |  |  | Coincident | 11.053
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.47
|  |  |  | Coincident | 11.151
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.238
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.987
|  |  |  | Coincident | 13.225
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.118
|  |  |  | Coincident | 13.342
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.205
|  |  |  | Coincident | 11.751
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.321
|  |  |  | Coincident | 11.855
| Lefevre 11kV | Substation Rating | MVA | Non-Coincident | 74.58
|  |  |  | Coincident | 74.58
|  | Raw Adjusted MD | MW | Non-Coincident | 9.51
|  |  |  | Coincident | 7.555
|  | Raw Adjusted MD | MVA | Non-Coincident | 9.784
|  |  |  | Coincident | 7.705
|  | Date MD occurred |  | Non-Coincident | 22/02/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 9:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.11
|  |  |  | Coincident | 0.007
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.972
|  |  |  | Coincident | 7.922
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.259
|  |  |  | Coincident | 8.079
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.322
|  |  |  | Coincident | 7.406
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.591
|  |  |  | Coincident | 7.553
| New Osborne 11kV | Substation Rating | MVA | Non-Coincident | 12.5
|  |  |  | Coincident | 12.5
|  | Raw Adjusted MD | MW | Non-Coincident | 0.345
|  |  |  | Coincident | 0.019
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.349
|  |  |  | Coincident | 0.019
|  | Date MD occurred |  | Non-Coincident | 17/01/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.025
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.025
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.024
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.024
|  |  |  | Coincident | 0.001
| New Richmond 11kV | Substation Rating | MVA | Non-Coincident | 51.334
|  |  |  | Coincident | 51.334
|  | Raw Adjusted MD | MW | Non-Coincident | 24.575
|  |  |  | Coincident | 22.952
|  | Raw Adjusted MD | MVA | Non-Coincident | 24.902
|  |  |  | Coincident | 23.355
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.763
|  |  |  | Coincident | 0.341
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 28.197
|  |  |  | Coincident | 26.334
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 28.572
|  |  |  | Coincident | 26.797
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 25.215
|  |  |  | Coincident | 23.55
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 25.551
|  |  |  | Coincident | 23.963
| Port Adelaide 11kV | Substation Rating | MVA | Non-Coincident | 33.192
|  |  |  | Coincident | 33.192
|  | Raw Adjusted MD | MW | Non-Coincident | 11.147
|  |  |  | Coincident | 10.982
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.305
|  |  |  | Coincident | 11.288
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.397
|  |  |  | Coincident | 0.177
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.034
|  |  |  | Coincident | 12.841
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.218
|  |  |  | Coincident | 13.199
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.8
|  |  |  | Coincident | 11.625
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 11.967
|  |  |  | Coincident | 11.95
| Port Adelaide North 11kV | Substation Rating | MVA | Non-Coincident | 49.029
|  |  |  | Coincident | 49.029
|  | Raw Adjusted MD | MW | Non-Coincident | 14.746
|  |  |  | Coincident | 6.183
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.479
|  |  |  | Coincident | 6.67
|  | Date MD occurred |  | Non-Coincident | 05/02/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 9:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 2.481
|  |  |  | Coincident | 0.116
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.279
|  |  |  | Coincident | 6.406
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 16.039
|  |  |  | Coincident | 6.911
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 14.185
|  |  |  | Coincident | 5.947
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 14.891
|  |  |  | Coincident | 6.417
| Queenstown 11kV | Substation Rating | MVA | Non-Coincident | 22.831
|  |  |  | Coincident | 22.831
|  | Raw Adjusted MD | MW | Non-Coincident | 12.86
|  |  |  | Coincident | 11.02
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.075
|  |  |  | Coincident | 11.211
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.23
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.778
|  |  |  | Coincident | 12.663
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.025
|  |  |  | Coincident | 12.883
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.094
|  |  |  | Coincident | 11.22
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.312
|  |  |  | Coincident | 11.415
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Thebarton 11kV | Substation Rating | MVA | Non-Coincident | 53.718
|  |  |  | Coincident | 53.718
|  | Raw Adjusted MD | MW | Non-Coincident | 18.59
|  |  |  | Coincident | 16.892
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.333
|  |  |  | Coincident | 17.237
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 4.784
|  |  |  | Coincident | 0.273
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 19.497
|  |  |  | Coincident | 17.716
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.276
|  |  |  | Coincident | 18.078
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 17.426
|  |  |  | Coincident | 15.834
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.122
|  |  |  | Coincident | 16.157
| Woodville 11kV | Substation Rating | MVA | Non-Coincident | 27.265
|  |  |  | Coincident | 27.265
|  | Raw Adjusted MD | MW | Non-Coincident | 8.425
|  |  |  | Coincident | 7.848
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.636
|  |  |  | Coincident | 8.097
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.275
|  |  |  | Coincident | 0.123
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 9.19
|  |  |  | Coincident | 8.561
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 9.42
|  |  |  | Coincident | 8.832
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.357
|  |  |  | Coincident | 7.784
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.566
|  |  |  | Coincident | 8.031
| Woodville 33kV | Substation Rating | MVA | Non-Coincident | 33.9
|  |  |  | Coincident | 33.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Raw Adjusted MD | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Date MD occurred |  | Non-Coincident | 01/11/2023
|  |  |  | Coincident | 12/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0
|  |  |  | Coincident | 0
| Monarto Central 11kV | Substation Rating | MVA | Non-Coincident | 8.7
|  |  |  | Coincident | 8.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.761
|  |  |  | Coincident | 0.988
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.802
|  |  |  | Coincident | 1.008
|  | Date MD occurred |  | Non-Coincident | 08/12/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 10:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.264
|  |  |  | Coincident | 0.011
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.956
|  |  |  | Coincident | 1.098
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.002
|  |  |  | Coincident | 1.12
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.824
|  |  |  | Coincident | 1.023
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.866
|  |  |  | Coincident | 1.044
| Monarto South 11kV | Substation Rating | MVA | Non-Coincident | 14.9
|  |  |  | Coincident | 14.9
|  | Raw Adjusted MD | MW | Non-Coincident | 3.755
|  |  |  | Coincident | 3.412
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.885
|  |  |  | Coincident | 3.543
|  | Date MD occurred |  | Non-Coincident | 21/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.036
|  |  |  | Coincident | 0.067
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.119
|  |  |  | Coincident | 3.742
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.261
|  |  |  | Coincident | 3.887
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.764
|  |  |  | Coincident | 3.42
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.894
|  |  |  | Coincident | 3.552
| Murray Bridge North 11kV | Substation Rating | MVA | Non-Coincident | 26.105
|  |  |  | Coincident | 26.105
|  | Raw Adjusted MD | MW | Non-Coincident | 11.474
|  |  |  | Coincident | 11.168
|  | Raw Adjusted MD | MVA | Non-Coincident | 11.773
|  |  |  | Coincident | 11.47
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.233
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.321
|  |  |  | Coincident | 12.966
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.668
|  |  |  | Coincident | 13.316
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 11.913
|  |  |  | Coincident | 11.595
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.222
|  |  |  | Coincident | 11.908
| Murray Bridge South 11kV | Substation Rating | MVA | Non-Coincident | 28.411
|  |  |  | Coincident | 28.411
|  | Raw Adjusted MD | MW | Non-Coincident | 13.739
|  |  |  | Coincident | 13.3
|  | Raw Adjusted MD | MVA | Non-Coincident | 13.859
|  |  |  | Coincident | 13.434
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.642
|  |  |  | Coincident | 0.287
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 15.232
|  |  |  | Coincident | 14.746
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 15.366
|  |  |  | Coincident | 14.894
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 13.486
|  |  |  | Coincident | 13.055
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 13.604
|  |  |  | Coincident | 13.187
| Mypolonga 11kV | Substation Rating | MVA | Non-Coincident | 5.063
|  |  |  | Coincident | 5.063
|  | Raw Adjusted MD | MW | Non-Coincident | 2.666
|  |  |  | Coincident | 2.527
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.763
|  |  |  | Coincident | 2.63
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.051
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.845
|  |  |  | Coincident | 2.697
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.949
|  |  |  | Coincident | 2.807
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.64
|  |  |  | Coincident | 2.502
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.736
|  |  |  | Coincident | 2.604
| Aldgate 11kV | Substation Rating | MVA | Non-Coincident | 12.581
|  |  |  | Coincident | 12.581
|  | Raw Adjusted MD | MW | Non-Coincident | 5.444
|  |  |  | Coincident | 5.37
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.444
|  |  |  | Coincident | 5.37
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.771
|  |  |  | Coincident | 0.151
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.306
|  |  |  | Coincident | 6.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.306
|  |  |  | Coincident | 6.22
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.792
|  |  |  | Coincident | 5.713
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.792
|  |  |  | Coincident | 5.713
| Balhannah 33kV | Substation Rating | MVA | Non-Coincident | 35.554
|  |  |  | Coincident | 35.554
|  | Raw Adjusted MD | MW | Non-Coincident | 18.963
|  |  |  | Coincident | 18.963
|  | Raw Adjusted MD | MVA | Non-Coincident | 19.514
|  |  |  | Coincident | 19.514
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.564
|  |  |  | Coincident | 0.564
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.965
|  |  |  | Coincident | 17.965
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.487
|  |  |  | Coincident | 18.487
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.123
|  |  |  | Coincident | 16.123
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.592
|  |  |  | Coincident | 16.592
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Brukunga 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.4
|  |  |  | Coincident | 0.376
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.4
|  |  |  | Coincident | 0.376
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.01
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.357
|  |  |  | Coincident | 0.335
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.357
|  |  |  | Coincident | 0.335
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.313
|  |  |  | Coincident | 0.294
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.313
|  |  |  | Coincident | 0.294
| Hahndorf 11kV | Substation Rating | MVA | Non-Coincident | 6.9
|  |  |  | Coincident | 6.9
|  | Raw Adjusted MD | MW | Non-Coincident | 4.025
|  |  |  | Coincident | 4.025
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.082
|  |  |  | Coincident | 4.082
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.131
|  |  |  | Coincident | 0.131
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.802
|  |  |  | Coincident | 4.802
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.871
|  |  |  | Coincident | 4.871
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.332
|  |  |  | Coincident | 4.332
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.394
|  |  |  | Coincident | 4.394
| Langhorne Creek 11kV | Substation Rating | MVA | Non-Coincident | 6.855
|  |  |  | Coincident | 6.855
|  | Raw Adjusted MD | MW | Non-Coincident | 3.17
|  |  |  | Coincident | 2.976
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.376
|  |  |  | Coincident | 3.155
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.058
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.559
|  |  |  | Coincident | 3.341
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.79
|  |  |  | Coincident | 3.541
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.187
|  |  |  | Coincident | 2.992
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.395
|  |  |  | Coincident | 3.172
| Meadows 11kV | Substation Rating | MVA | Non-Coincident | 7.112
|  |  |  | Coincident | 7.112
|  | Raw Adjusted MD | MW | Non-Coincident | 5.259
|  |  |  | Coincident | 5.259
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.399
|  |  |  | Coincident | 5.399
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.183
|  |  |  | Coincident | 0.183
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.279
|  |  |  | Coincident | 5.279
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.42
|  |  |  | Coincident | 5.42
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.855
|  |  |  | Coincident | 4.855
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.984
|  |  |  | Coincident | 4.984
| Milang 11kV | Substation Rating | MVA | Non-Coincident | 6.812
|  |  |  | Coincident | 6.812
|  | Raw Adjusted MD | MW | Non-Coincident | 3.589
|  |  |  | Coincident | 2.675
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.697
|  |  |  | Coincident | 2.725
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.07
|  |  |  | Coincident | 0.07
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.179
|  |  |  | Coincident | 2.369
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.275
|  |  |  | Coincident | 2.413
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.84
|  |  |  | Coincident | 2.116
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.925
|  |  |  | Coincident | 2.156
| Mount Barker 11kV | Substation Rating | MVA | Non-Coincident | 72.738
|  |  |  | Coincident | 72.738
|  | Raw Adjusted MD | MW | Non-Coincident | 25.34
|  |  |  | Coincident | 25.34
|  | Raw Adjusted MD | MVA | Non-Coincident | 25.383
|  |  |  | Coincident | 25.383
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.697
|  |  |  | Coincident | 0.697
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 25.782
|  |  |  | Coincident | 25.782
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 25.826
|  |  |  | Coincident | 25.826
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 22.451
|  |  |  | Coincident | 22.451
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 22.49
|  |  |  | Coincident | 22.49
| Mylor 11kV | Substation Rating | MVA | Non-Coincident | 4.94
|  |  |  | Coincident | 4.94
|  | Raw Adjusted MD | MW | Non-Coincident | 2.133
|  |  |  | Coincident | 2.133
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.148
|  |  |  | Coincident | 2.148
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.094
|  |  |  | Coincident | 0.094
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.709
|  |  |  | Coincident | 1.709
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.722
|  |  |  | Coincident | 1.722
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.594
|  |  |  | Coincident | 1.594
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.605
|  |  |  | Coincident | 1.605
| Nairne 11kV | Substation Rating | MVA | Non-Coincident | 9.192
|  |  |  | Coincident | 9.192
|  | Raw Adjusted MD | MW | Non-Coincident | 5.995
|  |  |  | Coincident | 5.995
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.009
|  |  |  | Coincident | 6.009
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.193
|  |  |  | Coincident | 0.193
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.778
|  |  |  | Coincident | 5.778
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.792
|  |  |  | Coincident | 5.792
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.123
|  |  |  | Coincident | 5.123
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.135
|  |  |  | Coincident | 5.135
| Piccadilly 11kV | Substation Rating | MVA | Non-Coincident | 3.895
|  |  |  | Coincident | 3.895
|  | Raw Adjusted MD | MW | Non-Coincident | 1.252
|  |  |  | Coincident | 1.151
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.258
|  |  |  | Coincident | 1.152
|  | Date MD occurred |  | Non-Coincident | 28/11/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 11:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 1.152
|  |  |  | Coincident | 0.042
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.327
|  |  |  | Coincident | 1.22
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.334
|  |  |  | Coincident | 1.221
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.234
|  |  |  | Coincident | 1.134
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.24
|  |  |  | Coincident | 1.135
| Stirling East 11kV | Substation Rating | MVA | Non-Coincident | 17.5
|  |  |  | Coincident | 17.5
|  | Raw Adjusted MD | MW | Non-Coincident | 5.776
|  |  |  | Coincident | 5.773
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.802
|  |  |  | Coincident | 5.796
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.357
|  |  |  | Coincident | 0.16
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.595
|  |  |  | Coincident | 6.593
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.625
|  |  |  | Coincident | 6.618
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.853
|  |  |  | Coincident | 5.85
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.88
|  |  |  | Coincident | 5.873
| Strathalbyn 11kV | Substation Rating | MVA | Non-Coincident | 16.9
|  |  |  | Coincident | 16.9
|  | Raw Adjusted MD | MW | Non-Coincident | 10.227
|  |  |  | Coincident | 10.126
|  | Raw Adjusted MD | MVA | Non-Coincident | 10.228
|  |  |  | Coincident | 10.128
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.005
|  |  |  | Coincident | 0.255
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.171
|  |  |  | Coincident | 10.071
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.172
|  |  |  | Coincident | 10.073
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 8.856
|  |  |  | Coincident | 8.769
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 8.857
|  |  |  | Coincident | 8.77
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Uraidla 11kV | Substation Rating | MVA | Non-Coincident | 17.33
|  |  |  | Coincident | 17.33
|  | Raw Adjusted MD | MW | Non-Coincident | 3.978
|  |  |  | Coincident | 3.696
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.119
|  |  |  | Coincident | 3.791
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.309
|  |  |  | Coincident | 0.138
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.415
|  |  |  | Coincident | 4.102
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.572
|  |  |  | Coincident | 4.208
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.979
|  |  |  | Coincident | 3.698
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.12
|  |  |  | Coincident | 3.793
| Uraidla 33kV | Substation Rating | MVA | Non-Coincident | 31
|  |  |  | Coincident | 31
|  | Raw Adjusted MD | MW | Non-Coincident | 12.88
|  |  |  | Coincident | 12.88
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.907
|  |  |  | Coincident | 12.9
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.789
|  |  |  | Coincident | 0.353
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 13.634
|  |  |  | Coincident | 13.634
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 13.663
|  |  |  | Coincident | 13.656
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.354
|  |  |  | Coincident | 12.354
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.38
|  |  |  | Coincident | 12.374
| Verdun 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.882
|  |  |  | Coincident | 0.789
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.899
|  |  |  | Coincident | 0.798
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.028
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.984
|  |  |  | Coincident | 0.88
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.003
|  |  |  | Coincident | 0.89
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.884
|  |  |  | Coincident | 0.79
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.901
|  |  |  | Coincident | 0.799
| Woodside 11kV | Substation Rating | MVA | Non-Coincident | 13.385
|  |  |  | Coincident | 13.385
|  | Raw Adjusted MD | MW | Non-Coincident | 7.354
|  |  |  | Coincident | 7.354
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.605
|  |  |  | Coincident | 7.605
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.218
|  |  |  | Coincident | 0.218
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 7.812
|  |  |  | Coincident | 7.812
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.079
|  |  |  | Coincident | 8.079
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.212
|  |  |  | Coincident | 7.212
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.458
|  |  |  | Coincident | 7.458
| Mount Gambier 11kV | Substation Rating | MVA | Non-Coincident | 25.444
|  |  |  | Coincident | 25.444
|  | Raw Adjusted MD | MW | Non-Coincident | 12.69
|  |  |  | Coincident | 12.365
|  | Raw Adjusted MD | MVA | Non-Coincident | 12.798
|  |  |  | Coincident | 12.482
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.576
|  |  |  | Coincident | 0.137
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 14.016
|  |  |  | Coincident | 13.657
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 14.135
|  |  |  | Coincident | 13.786
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 12.625
|  |  |  | Coincident | 12.302
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 12.733
|  |  |  | Coincident | 12.418
| Tarpeena South 11kV | Substation Rating | MVA | Non-Coincident | 10.86
|  |  |  | Coincident | 10.86
|  | Raw Adjusted MD | MW | Non-Coincident | 6.267
|  |  |  | Coincident | 3.719
|  | Raw Adjusted MD | MVA | Non-Coincident | 6.836
|  |  |  | Coincident | 3.989
|  | Date MD occurred |  | Non-Coincident | 29/11/2023
|  |  |  | Coincident | 21/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 9:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.16
|  |  |  | Coincident | 0.004
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.264
|  |  |  | Coincident | 3.718
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 6.834
|  |  |  | Coincident | 3.988
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.139
|  |  |  | Coincident | 3.643
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.696
|  |  |  | Coincident | 3.908
| Hawker 11kV | Substation Rating | MVA | Non-Coincident | 1.122
|  |  |  | Coincident | 1.122
|  | Raw Adjusted MD | MW | Non-Coincident | 0.827
|  |  |  | Coincident | 0.827
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.839
|  |  |  | Coincident | 0.839
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 13/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.025
|  |  |  | Coincident | 0.025
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.97
|  |  |  | Coincident | 0.97
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.984
|  |  |  | Coincident | 0.984
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.876
|  |  |  | Coincident | 0.876
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.888
|  |  |  | Coincident | 0.888
| Cadell 11kV | Substation Rating | MVA | Non-Coincident | 2.621
|  |  |  | Coincident | 2.621
|  | Raw Adjusted MD | MW | Non-Coincident | 1.105
|  |  |  | Coincident | 0.829
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.156
|  |  |  | Coincident | 0.861
|  | Date MD occurred |  | Non-Coincident | 04/12/2023
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.035
|  |  |  | Coincident | 0.776
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.082
|  |  |  | Coincident | 0.806
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.955
|  |  |  | Coincident | 0.716
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.999
|  |  |  | Coincident | 0.744
| Cordola 11kV | Substation Rating | MVA | Non-Coincident | 2.841
|  |  |  | Coincident | 2.841
|  | Raw Adjusted MD | MW | Non-Coincident | 1.117
|  |  |  | Coincident | 0.295
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.126
|  |  |  | Coincident | 0.302
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.098
|  |  |  | Coincident | 0.289
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.106
|  |  |  | Coincident | 0.297
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.005
|  |  |  | Coincident | 0.265
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.013
|  |  |  | Coincident | 0.272
| Morgan 11kV | Substation Rating | MVA | Non-Coincident | 1.425
|  |  |  | Coincident | 1.425
|  | Raw Adjusted MD | MW | Non-Coincident | 1.006
|  |  |  | Coincident | 0.42
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.016
|  |  |  | Coincident | 0.424
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.074
|  |  |  | Coincident | 0.448
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.084
|  |  |  | Coincident | 0.452
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.966
|  |  |  | Coincident | 0.404
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.976
|  |  |  | Coincident | 0.407
| Portee 11kV | Substation Rating | MVA | Non-Coincident | 0.7
|  |  |  | Coincident | 0.7
|  | Raw Adjusted MD | MW | Non-Coincident | 0.435
|  |  |  | Coincident | 0.281
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.458
|  |  |  | Coincident | 0.296
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.066
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.527
|  |  |  | Coincident | 0.34
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.554
|  |  |  | Coincident | 0.358
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.473
|  |  |  | Coincident | 0.305
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.498
|  |  |  | Coincident | 0.322
| Qualco 11kV | Substation Rating | MVA | Non-Coincident | 3.25
|  |  |  | Coincident | 3.25
|  | Raw Adjusted MD | MW | Non-Coincident | 2.567
|  |  |  | Coincident | 2.167
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.719
|  |  |  | Coincident | 2.296
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 2:30:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.633
|  |  |  | Coincident | 2.223
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.789
|  |  |  | Coincident | 2.355
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.493
|  |  |  | Coincident | 2.105
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.641
|  |  |  | Coincident | 2.23
| Ramco 11kV | Substation Rating | MVA | Non-Coincident | 9.387
|  |  |  | Coincident | 9.387
|  | Raw Adjusted MD | MW | Non-Coincident | 4.997
|  |  |  | Coincident | 3.977
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.273
|  |  |  | Coincident | 4.173
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 22:30:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.909
|  |  |  | Coincident | 3.907
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.181
|  |  |  | Coincident | 4.1
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.535
|  |  |  | Coincident | 3.61
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.787
|  |  |  | Coincident | 3.788
| Roonka 11kV | Substation Rating | MVA | Non-Coincident | 8
|  |  |  | Coincident | 8
|  | Raw Adjusted MD | MW | Non-Coincident | 2.715
|  |  |  | Coincident | 1.615
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.867
|  |  |  | Coincident | 1.711
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.487
|  |  |  | Coincident | 1.479
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.627
|  |  |  | Coincident | 1.567
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.301
|  |  |  | Coincident | 1.368
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.43
|  |  |  | Coincident | 1.45
| Swan Reach 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.083
|  |  |  | Coincident | 0.437
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.168
|  |  |  | Coincident | 0.448
|  | Date MD occurred |  | Non-Coincident | 11/11/2023
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 1:00:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.216
|  |  |  | Coincident | 0.491
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.311
|  |  |  | Coincident | 0.503
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.108
|  |  |  | Coincident | 0.447
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.195
|  |  |  | Coincident | 0.458
| Swan Reach 33kV | Substation Rating | MVA | Non-Coincident | 7.125
|  |  |  | Coincident | 7.125
|  | Raw Adjusted MD | MW | Non-Coincident | 1.668
|  |  |  | Coincident | 0.975
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.882
|  |  |  | Coincident | 1.055
|  | Date MD occurred |  | Non-Coincident | 10/11/2023
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 22:00:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.823
|  |  |  | Coincident | 1.065
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.057
|  |  |  | Coincident | 1.153
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.679
|  |  |  | Coincident | 0.981
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.895
|  |  |  | Coincident | 1.062
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Waikerie 11kV | Substation Rating | MVA | Non-Coincident | 12.229
|  |  |  | Coincident | 12.229
|  | Raw Adjusted MD | MW | Non-Coincident | 7.197
|  |  |  | Coincident | 4.812
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.284
|  |  |  | Coincident | 4.844
|  | Date MD occurred |  | Non-Coincident | 22/02/2024
|  |  |  | Coincident | 28/02/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 1:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.555
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 8.001
|  |  |  | Coincident | 5.349
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 8.097
|  |  |  | Coincident | 5.385
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 7.144
|  |  |  | Coincident | 4.777
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 7.23
|  |  |  | Coincident | 4.808
| Coonawarra 11kV | Substation Rating | MVA | Non-Coincident | 12.448
|  |  |  | Coincident | 12.448
|  | Raw Adjusted MD | MW | Non-Coincident | 3.751
|  |  |  | Coincident | 3.751
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.983
|  |  |  | Coincident | 3.983
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.024
|  |  |  | Coincident | 0.024
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.057
|  |  |  | Coincident | 4.057
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.308
|  |  |  | Coincident | 4.308
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.625
|  |  |  | Coincident | 3.625
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.85
|  |  |  | Coincident | 3.85
| Nangwarry 11kV | Substation Rating | MVA | Non-Coincident | 3.62
|  |  |  | Coincident | 3.62
|  | Raw Adjusted MD | MW | Non-Coincident | 0.473
|  |  |  | Coincident | 0.437
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.483
|  |  |  | Coincident | 0.446
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.012
|  |  |  | Coincident | 0.012
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.497
|  |  |  | Coincident | 0.459
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.508
|  |  |  | Coincident | 0.469
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.484
|  |  |  | Coincident | 0.447
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.494
|  |  |  | Coincident | 0.456
| Penola 11kV | Substation Rating | MVA | Non-Coincident | 4.264
|  |  |  | Coincident | 4.264
|  | Raw Adjusted MD | MW | Non-Coincident | 2.448
|  |  |  | Coincident | 2.282
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.491
|  |  |  | Coincident | 2.34
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.047
|  |  |  | Coincident | 0.047
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.761
|  |  |  | Coincident | 2.573
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.809
|  |  |  | Coincident | 2.639
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.444
|  |  |  | Coincident | 2.278
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.488
|  |  |  | Coincident | 2.337
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Coffin Bay 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.342
|  |  |  | Coincident | 1.257
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.351
|  |  |  | Coincident | 1.269
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.031
|  |  |  | Coincident | 0.031
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.708
|  |  |  | Coincident | 1.599
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.718
|  |  |  | Coincident | 1.615
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.559
|  |  |  | Coincident | 1.461
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.569
|  |  |  | Coincident | 1.475
| Cummins 11kV | Substation Rating | MVA | Non-Coincident | 4.595
|  |  |  | Coincident | 4.595
|  | Raw Adjusted MD | MW | Non-Coincident | 2.355
|  |  |  | Coincident | 2.345
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.374
|  |  |  | Coincident | 2.362
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.055
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.477
|  |  |  | Coincident | 2.466
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.498
|  |  |  | Coincident | 2.485
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.204
|  |  |  | Coincident | 2.194
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.222
|  |  |  | Coincident | 2.211
| Little Swamp 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.18
|  |  |  | Coincident | 0.161
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.181
|  |  |  | Coincident | 0.161
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.005
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.145
|  |  |  | Coincident | 0.13
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.146
|  |  |  | Coincident | 0.13
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.135
|  |  |  | Coincident | 0.121
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.136
|  |  |  | Coincident | 0.121
| Point Boston 11kV | Substation Rating | MVA | Non-Coincident | 2.185
|  |  |  | Coincident | 2.185
|  | Raw Adjusted MD | MW | Non-Coincident | 1.265
|  |  |  | Coincident | 1.245
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.351
|  |  |  | Coincident | 1.332
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 15:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.038
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.318
|  |  |  | Coincident | 1.297
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.407
|  |  |  | Coincident | 1.387
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.291
|  |  |  | Coincident | 1.271
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.378
|  |  |  | Coincident | 1.359
| Poonindie 11kV | Substation Rating | MVA | Non-Coincident | 1.235
|  |  |  | Coincident | 1.235
|  | Raw Adjusted MD | MW | Non-Coincident | 0.46
|  |  |  | Coincident | 0.43
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.484
|  |  |  | Coincident | 0.452
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.011
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.463
|  |  |  | Coincident | 0.433
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.487
|  |  |  | Coincident | 0.455
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.437
|  |  |  | Coincident | 0.409
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.46
|  |  |  | Coincident | 0.43
| Port Lincoln City 11kV | Substation Rating | MVA | Non-Coincident | 28.418
|  |  |  | Coincident | 28.418
|  | Raw Adjusted MD | MW | Non-Coincident | 8.328
|  |  |  | Coincident | 7.553
|  | Raw Adjusted MD | MVA | Non-Coincident | 8.341
|  |  |  | Coincident | 7.584
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.231
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 10.332
|  |  |  | Coincident | 9.371
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 10.348
|  |  |  | Coincident | 9.409
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 9.458
|  |  |  | Coincident | 8.578
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 9.473
|  |  |  | Coincident | 8.613
| Port Lincoln Docks 11kV | Substation Rating | MVA | Non-Coincident | 13.4
|  |  |  | Coincident | 13.4
|  | Raw Adjusted MD | MW | Non-Coincident | 5.093
|  |  |  | Coincident | 4.619
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.101
|  |  |  | Coincident | 4.638
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.058
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.92
|  |  |  | Coincident | 5.369
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.929
|  |  |  | Coincident | 5.391
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.511
|  |  |  | Coincident | 4.999
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.52
|  |  |  | Coincident | 5.019
| Port Lincoln Marina 11kV | Substation Rating | MVA | Non-Coincident | 17.8
|  |  |  | Coincident | 17.8
|  | Raw Adjusted MD | MW | Non-Coincident | 4.821
|  |  |  | Coincident | 4.372
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.828
|  |  |  | Coincident | 4.39
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.108
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.852
|  |  |  | Coincident | 5.307
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.861
|  |  |  | Coincident | 5.329
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 5.318
|  |  |  | Coincident | 4.823
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.326
|  |  |  | Coincident | 4.843
| Tumby Bay 11kV | Substation Rating | MVA | Non-Coincident | 5.165
|  |  |  | Coincident | 5.165
|  | Raw Adjusted MD | MW | Non-Coincident | 2.358
|  |  |  | Coincident | 2.074
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.359
|  |  |  | Coincident | 2.075
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.068
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.462
|  |  |  | Coincident | 2.166
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.463
|  |  |  | Coincident | 2.167
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.213
|  |  |  | Coincident | 1.947
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.214
|  |  |  | Coincident | 1.948
| Uley 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.233
|  |  |  | Coincident | 0.217
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.238
|  |  |  | Coincident | 0.222
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.006
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.289
|  |  |  | Coincident | 0.268
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.295
|  |  |  | Coincident | 0.275
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.268
|  |  |  | Coincident | 0.249
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.274
|  |  |  | Coincident | 0.255
| Uley South 11kV | Substation Rating | MVA | Non-Coincident | 1.235
|  |  |  | Coincident | 1.235
|  | Raw Adjusted MD | MW | Non-Coincident | 0.558
|  |  |  | Coincident | 0.383
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.575
|  |  |  | Coincident | 0.395
|  | Date MD occurred |  | Non-Coincident | 09/11/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
|  |  |  | Coincident | 19:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.603
|  |  |  | Coincident | 0.414
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.621
|  |  |  | Coincident | 0.427
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.568
|  |  |  | Coincident | 0.391
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.586
|  |  |  | Coincident | 0.403
| Booyoolie 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.02
|  |  |  | Coincident | 0.012
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.02
|  |  |  | Coincident | 0.012
|  | Date MD occurred |  | Non-Coincident | 12/02/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.022
|  |  |  | Coincident | 0.013
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.023
|  |  |  | Coincident | 0.013
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.021
|  |  |  | Coincident | 0.012
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.021
|  |  |  | Coincident | 0.012
| Caltowie 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.103
|  |  |  | Coincident | 0.016
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.111
|  |  |  | Coincident | 0.017
|  | Date MD occurred |  | Non-Coincident | 01/12/2023
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 13:30:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.094
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.1
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.108
|  |  |  | Coincident | 0.017
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.086
|  |  |  | Coincident | 0.013
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.092
|  |  |  | Coincident | 0.014
| Crystal Brook 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.006
|  |  |  | Coincident | 0.728
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.028
|  |  |  | Coincident | 0.728
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.032
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.214
|  |  |  | Coincident | 0.803
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.238
|  |  |  | Coincident | 0.803
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.962
|  |  |  | Coincident | 0.712
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.984
|  |  |  | Coincident | 0.712
| Gladstone 11kV | Substation Rating | MVA | Non-Coincident | 4.753
|  |  |  | Coincident | 4.753
|  | Raw Adjusted MD | MW | Non-Coincident | 2.252
|  |  |  | Coincident | 0.933
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.289
|  |  |  | Coincident | 0.934
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.039
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.435
|  |  |  | Coincident | 1.009
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.475
|  |  |  | Coincident | 1.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.194
|  |  |  | Coincident | 0.909
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.23
|  |  |  | Coincident | 0.91
| Jamestown 11kV | Substation Rating | MVA | Non-Coincident | 4.112
|  |  |  | Coincident | 4.112
|  | Raw Adjusted MD | MW | Non-Coincident | 2.417
|  |  |  | Coincident | 1.037
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.467
|  |  |  | Coincident | 1.04
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.051
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.538
|  |  |  | Coincident | 1.089
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.591
|  |  |  | Coincident | 1.092
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.259
|  |  |  | Coincident | 0.969
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.306
|  |  |  | Coincident | 0.972
| Peterborough 11kV | Substation Rating | MVA | Non-Coincident | 2.8
|  |  |  | Coincident | 2.8
|  | Raw Adjusted MD | MW | Non-Coincident | 1.686
|  |  |  | Coincident | 0.825
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.697
|  |  |  | Coincident | 0.826
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.022
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.907
|  |  |  | Coincident | 0.934
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.919
|  |  |  | Coincident | 0.935
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.711
|  |  |  | Coincident | 0.837
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.721
|  |  |  | Coincident | 0.838
| Port Broughton 11kV | Substation Rating | MVA | Non-Coincident | 5.283
|  |  |  | Coincident | 5.283
|  | Raw Adjusted MD | MW | Non-Coincident | 2.876
|  |  |  | Coincident | 0.779
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.126
|  |  |  | Coincident | 0.847
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.051
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.357
|  |  |  | Coincident | 0.909
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.649
|  |  |  | Coincident | 0.988
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.199
|  |  |  | Coincident | 0.867
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.477
|  |  |  | Coincident | 0.942
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Port Pirie South 11kV | Substation Rating | MVA | Non-Coincident | 40.51
|  |  |  | Coincident | 40.51
|  | Raw Adjusted MD | MW | Non-Coincident | 18.211
|  |  |  | Coincident | 3.468
|  | Raw Adjusted MD | MVA | Non-Coincident | 18.667
|  |  |  | Coincident | 3.673
|  | Date MD occurred |  | Non-Coincident | 12/03/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.347
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 21.512
|  |  |  | Coincident | 4.096
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 22.05
|  |  |  | Coincident | 4.339
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 19.123
|  |  |  | Coincident | 3.641
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 19.601
|  |  |  | Coincident | 3.857
| Yongala 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.045
|  |  |  | Coincident | 0.011
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.045
|  |  |  | Coincident | 0.011
|  | Date MD occurred |  | Non-Coincident | 28/02/2024
|  |  |  | Coincident | 07/11/2023
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 2:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.058
|  |  |  | Coincident | 0.014
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.058
|  |  |  | Coincident | 0.014
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.053
|  |  |  | Coincident | 0.013
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.053
|  |  |  | Coincident | 0.013
| Beachport 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.142
|  |  |  | Coincident | 1.083
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.145
|  |  |  | Coincident | 1.086
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.028
|  |  |  | Coincident | 0.062
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.901
|  |  |  | Coincident | 0.854
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.904
|  |  |  | Coincident | 0.857
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.817
|  |  |  | Coincident | 0.775
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.82
|  |  |  | Coincident | 0.777
| Hatherleigh 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.072
|  |  |  | Coincident | 0.072
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.072
|  |  |  | Coincident | 0.072
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.003
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.075
|  |  |  | Coincident | 0.075
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.076
|  |  |  | Coincident | 0.076
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.068
|  |  |  | Coincident | 0.068
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.069
|  |  |  | Coincident | 0.069
| Kalangadoo 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.534
|  |  |  | Coincident | 0.534
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.538
|  |  |  | Coincident | 0.538
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.551
|  |  |  | Coincident | 0.551
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.554
|  |  |  | Coincident | 0.554
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.488
|  |  |  | Coincident | 0.488
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.491
|  |  |  | Coincident | 0.491
| Kalangadoo West 11kV | Substation Rating | MVA | Non-Coincident | 1.293
|  |  |  | Coincident | 1.293
|  | Raw Adjusted MD | MW | Non-Coincident | 0.773
|  |  |  | Coincident | 0.634
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.806
|  |  |  | Coincident | 0.662
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.026
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.703
|  |  |  | Coincident | 0.577
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.734
|  |  |  | Coincident | 0.602
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.636
|  |  |  | Coincident | 0.522
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.664
|  |  |  | Coincident | 0.545
| Millicent 11kV | Substation Rating | MVA | Non-Coincident | 12.477
|  |  |  | Coincident | 12.477
|  | Raw Adjusted MD | MW | Non-Coincident | 5.11
|  |  |  | Coincident | 4.676
|  | Raw Adjusted MD | MVA | Non-Coincident | 5.266
|  |  |  | Coincident | 4.794
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.124
|  |  |  | Coincident | 0.278
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.356
|  |  |  | Coincident | 4.901
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.52
|  |  |  | Coincident | 5.025
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.933
|  |  |  | Coincident | 4.514
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 5.084
|  |  |  | Coincident | 4.628
| Mount Burr 11kV | Substation Rating | MVA | Non-Coincident | 0.362
|  |  |  | Coincident | 0.362
|  | Raw Adjusted MD | MW | Non-Coincident | 0.336
|  |  |  | Coincident | 0.336
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.338
|  |  |  | Coincident | 0.338
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.015
|  |  |  | Coincident | 0.015
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.407
|  |  |  | Coincident | 0.407
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.409
|  |  |  | Coincident | 0.409
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.349
|  |  |  | Coincident | 0.349
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.351
|  |  |  | Coincident | 0.351
| Robe 7.6kV | Substation Rating | MVA | Non-Coincident | 6.426
|  |  |  | Coincident | 6.426
|  | Raw Adjusted MD | MW | Non-Coincident | 2.277
|  |  |  | Coincident | 2.044
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.277
|  |  |  | Coincident | 2.045
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.121
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.559
|  |  |  | Coincident | 2.297
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.559
|  |  |  | Coincident | 2.298
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.297
|  |  |  | Coincident | 2.062
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.297
|  |  |  | Coincident | 2.063
| South End 11kV | Substation Rating | MVA | Non-Coincident | 0.78
|  |  |  | Coincident | 0.78
|  | Raw Adjusted MD | MW | Non-Coincident | 0.356
|  |  |  | Coincident | 0.261
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.373
|  |  |  | Coincident | 0.265
|  | Date MD occurred |  | Non-Coincident | 07/03/2024
|  |  |  | Coincident | 09/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 0:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.027
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.376
|  |  |  | Coincident | 0.276
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.394
|  |  |  | Coincident | 0.28
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.347
|  |  |  | Coincident | 0.255
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.364
|  |  |  | Coincident | 0.259
| Binnies 11kV | Substation Rating | MVA | Non-Coincident | 2.47
|  |  |  | Coincident | 2.47
|  | Raw Adjusted MD | MW | Non-Coincident | 0.834
|  |  |  | Coincident | 0.616
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.871
|  |  |  | Coincident | 0.631
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 14:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.016
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.922
|  |  |  | Coincident | 0.681
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.963
|  |  |  | Coincident | 0.698
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.87
|  |  |  | Coincident | 0.642
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.909
|  |  |  | Coincident | 0.659
| Campbell Park 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.451
|  |  |  | Coincident | 0.161
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.462
|  |  |  | Coincident | 0.165
|  | Date MD occurred |  | Non-Coincident | 25/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 5:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.489
|  |  |  | Coincident | 0.175
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.501
|  |  |  | Coincident | 0.179
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.455
|  |  |  | Coincident | 0.163
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.466
|  |  |  | Coincident | 0.167
| Coomandook 11kV | Substation Rating | MVA | Non-Coincident | 0.713
|  |  |  | Coincident | 0.713
|  | Raw Adjusted MD | MW | Non-Coincident | 0.374
|  |  |  | Coincident | 0.359
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.381
|  |  |  | Coincident | 0.368
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.407
|  |  |  | Coincident | 0.391
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.415
|  |  |  | Coincident | 0.401
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.369
|  |  |  | Coincident | 0.354
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.376
|  |  |  | Coincident | 0.363
| Coonalpyn 11kV | Substation Rating | MVA | Non-Coincident | 1.235
|  |  |  | Coincident | 1.235
|  | Raw Adjusted MD | MW | Non-Coincident | 0.408
|  |  |  | Coincident | 0.408
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.41
|  |  |  | Coincident | 0.41
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.451
|  |  |  | Coincident | 0.451
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.453
|  |  |  | Coincident | 0.453
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.407
|  |  |  | Coincident | 0.407
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.409
|  |  |  | Coincident | 0.409
| Geranium 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.069
|  |  |  | Coincident | 0.057
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.071
|  |  |  | Coincident | 0.06
|  | Date MD occurred |  | Non-Coincident | 19/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 5:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.093
|  |  |  | Coincident | 0.077
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.096
|  |  |  | Coincident | 0.081
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.084
|  |  |  | Coincident | 0.07
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.087
|  |  |  | Coincident | 0.073
| Jabuk 11kV | Substation Rating | MVA | Non-Coincident | 0.26
|  |  |  | Coincident | 0.26
|  | Raw Adjusted MD | MW | Non-Coincident | 0.076
|  |  |  | Coincident | 0.076
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.078
|  |  |  | Coincident | 0.078
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.08
|  |  |  | Coincident | 0.08
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.082
|  |  |  | Coincident | 0.082
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.075
|  |  |  | Coincident | 0.075
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.076
|  |  |  | Coincident | 0.076
| Jervois 11kV | Substation Rating | MVA | Non-Coincident | 4.94
|  |  |  | Coincident | 4.94
|  | Raw Adjusted MD | MW | Non-Coincident | 2.565
|  |  |  | Coincident | 2.114
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.776
|  |  |  | Coincident | 2.274
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.022
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.925
|  |  |  | Coincident | 2.411
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.165
|  |  |  | Coincident | 2.593
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.769
|  |  |  | Coincident | 2.282
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.996
|  |  |  | Coincident | 2.454
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| Karoonda 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 0.857
|  |  |  | Coincident | 0.816
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.864
|  |  |  | Coincident | 0.826
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.823
|  |  |  | Coincident | 0.783
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.83
|  |  |  | Coincident | 0.793
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.742
|  |  |  | Coincident | 0.706
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.748
|  |  |  | Coincident | 0.715
| Ki Ki 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.105
|  |  |  | Coincident | 0.105
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.108
|  |  |  | Coincident | 0.108
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.11
|  |  |  | Coincident | 0.11
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.112
|  |  |  | Coincident | 0.112
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.102
|  |  |  | Coincident | 0.102
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.105
|  |  |  | Coincident | 0.105
| Lameroo 11kV | Substation Rating | MVA | Non-Coincident | 2.581
|  |  |  | Coincident | 2.581
|  | Raw Adjusted MD | MW | Non-Coincident | 1.172
|  |  |  | Coincident | 1.014
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.184
|  |  |  | Coincident | 1.021
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 18:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.039
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.395
|  |  |  | Coincident | 1.207
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.409
|  |  |  | Coincident | 1.215
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.251
|  |  |  | Coincident | 1.083
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.264
|  |  |  | Coincident | 1.09
| Meningie 11kV | Substation Rating | MVA | Non-Coincident | 6.98
|  |  |  | Coincident | 6.98
|  | Raw Adjusted MD | MW | Non-Coincident | 2.06
|  |  |  | Coincident | 1.951
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.097
|  |  |  | Coincident | 1.979
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.038
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.064
|  |  |  | Coincident | 1.955
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.101
|  |  |  | Coincident | 1.984
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.906
|  |  |  | Coincident | 1.805
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.94
|  |  |  | Coincident | 1.832
| Narrung 11kV | Substation Rating | MVA | Non-Coincident | 3.8
|  |  |  | Coincident | 3.8
|  | Raw Adjusted MD | MW | Non-Coincident | 0.945
|  |  |  | Coincident | 0.604
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.018
|  |  |  | Coincident | 0.656
|  | Date MD occurred |  | Non-Coincident | 18/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.147
|  |  |  | Coincident | 0.733
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.236
|  |  |  | Coincident | 0.796
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.078
|  |  |  | Coincident | 0.689
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.161
|  |  |  | Coincident | 0.748
| Parilla 11kV | Substation Rating | MVA | Non-Coincident | 3.1
|  |  |  | Coincident | 3.1
|  | Raw Adjusted MD | MW | Non-Coincident | 1.799
|  |  |  | Coincident | 1.155
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.065
|  |  |  | Coincident | 1.243
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.245
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.747
|  |  |  | Coincident | 1.121
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.006
|  |  |  | Coincident | 1.207
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.69
|  |  |  | Coincident | 1.085
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.94
|  |  |  | Coincident | 1.167
| Peake 11kV | Substation Rating | MVA | Non-Coincident | 0.362
|  |  |  | Coincident | 0.362
|  | Raw Adjusted MD | MW | Non-Coincident | 0.125
|  |  |  | Coincident | 0.125
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.128
|  |  |  | Coincident | 0.128
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.144
|  |  |  | Coincident | 0.144
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.148
|  |  |  | Coincident | 0.148
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.132
|  |  |  | Coincident | 0.132
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.135
|  |  |  | Coincident | 0.135
| Pinnaroo 11kV | Substation Rating | MVA | Non-Coincident | 2.486
|  |  |  | Coincident | 2.486
|  | Raw Adjusted MD | MW | Non-Coincident | 1.503
|  |  |  | Coincident | 1.253
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.552
|  |  |  | Coincident | 1.294
|  | Date MD occurred |  | Non-Coincident | 12/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.009
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.672
|  |  |  | Coincident | 1.393
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.727
|  |  |  | Coincident | 1.439
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.536
|  |  |  | Coincident | 1.28
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.587
|  |  |  | Coincident | 1.322
| Pinnaroo South 11kV | Substation Rating | MVA | Non-Coincident | 0.39
|  |  |  | Coincident | 0.39
|  | Raw Adjusted MD | MW | Non-Coincident | 0.018
|  |  |  | Coincident | 0.008
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.019
|  |  |  | Coincident | 0.008
|  | Date MD occurred |  | Non-Coincident | 10/11/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.02
|  |  |  | Coincident | 0.009
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.022
|  |  |  | Coincident | 0.01
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.018
|  |  |  | Coincident | 0.008
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.02
|  |  |  | Coincident | 0.009
| Sherlock 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.017
|  |  |  | Coincident | 0.017
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.017
|  |  |  | Coincident | 0.017
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.023
|  |  |  | Coincident | 0.023
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.024
|  |  |  | Coincident | 0.024
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.021
|  |  |  | Coincident | 0.021
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.022
|  |  |  | Coincident | 0.022
| Tailem Bend Town 11kV | Substation Rating | MVA | Non-Coincident | 4.167
|  |  |  | Coincident | 4.167
|  | Raw Adjusted MD | MW | Non-Coincident | 2.686
|  |  |  | Coincident | 2.497
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.704
|  |  |  | Coincident | 2.517
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.994
|  |  |  | Coincident | 2.783
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.015
|  |  |  | Coincident | 2.806
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.691
|  |  |  | Coincident | 2.501
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.709
|  |  |  | Coincident | 2.521
| White Sands 11kV | Substation Rating | MVA | Non-Coincident | 8.5
|  |  |  | Coincident | 8.5
|  | Raw Adjusted MD | MW | Non-Coincident | 3.361
|  |  |  | Coincident | 1.885
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.699
|  |  |  | Coincident | 2.098
|  | Date MD occurred |  | Non-Coincident | 09/11/2023
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 13:00:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.672
|  |  |  | Coincident | 2.059
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.042
|  |  |  | Coincident | 2.293
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.54
|  |  |  | Coincident | 1.985
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.896
|  |  |  | Coincident | 2.21
| Woods Point 11kV | Substation Rating | MVA | Non-Coincident | 8.9
|  |  |  | Coincident | 8.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.476
|  |  |  | Coincident | 2.276
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.515
|  |  |  | Coincident | 2.3
|  | Date MD occurred |  | Non-Coincident | 10/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 20:00:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.263
|  |  |  | Coincident | 2.081
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.3
|  |  |  | Coincident | 2.103
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.142
|  |  |  | Coincident | 1.969
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.176
|  |  |  | Coincident | 1.989
| Alma 11kV | Substation Rating | MVA | Non-Coincident | 0.195
|  |  |  | Coincident | 0.195
|  | Raw Adjusted MD | MW | Non-Coincident | 0.1
|  |  |  | Coincident | 0.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.102
|  |  |  | Coincident | 0.102
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.115
|  |  |  | Coincident | 0.115
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.117
|  |  |  | Coincident | 0.117
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.103
|  |  |  | Coincident | 0.103
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.105
|  |  |  | Coincident | 0.105
| Freeling 11kV | Substation Rating | MVA | Non-Coincident | 3.889
|  |  |  | Coincident | 3.889
|  | Raw Adjusted MD | MW | Non-Coincident | 0.486
|  |  |  | Coincident | 0.441
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.486
|  |  |  | Coincident | 0.441
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.016
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.561
|  |  |  | Coincident | 0.51
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.561
|  |  |  | Coincident | 0.51
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.492
|  |  |  | Coincident | 0.447
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.492
|  |  |  | Coincident | 0.447
| Freeling North 11kV | Substation Rating | MVA | Non-Coincident | 4.4
|  |  |  | Coincident | 4.4
|  | Raw Adjusted MD | MW | Non-Coincident | 3.062
|  |  |  | Coincident | 2.685
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.098
|  |  |  | Coincident | 2.714
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.078
|  |  |  | Coincident | 0.119
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.294
|  |  |  | Coincident | 2.889
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.333
|  |  |  | Coincident | 2.92
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.95
|  |  |  | Coincident | 2.587
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.985
|  |  |  | Coincident | 2.615
| Gawler Belt TF1 11kV | Substation Rating | MVA | Non-Coincident | 14
|  |  |  | Coincident | 14
|  | Raw Adjusted MD | MW | Non-Coincident | 4.008
|  |  |  | Coincident | 3.77
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.104
|  |  |  | Coincident | 3.866
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 17:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.881
|  |  |  | Coincident | 0.168
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.525
|  |  |  | Coincident | 4.256
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.633
|  |  |  | Coincident | 4.365
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.101
|  |  |  | Coincident | 3.857
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.199
|  |  |  | Coincident | 3.956
| Gawler Belt TF2 11kV | Substation Rating | MVA | Non-Coincident | 15.9
|  |  |  | Coincident | 15.9
|  | Raw Adjusted MD | MW | Non-Coincident | 4.496
|  |  |  | Coincident | 4.363
|  | Raw Adjusted MD | MVA | Non-Coincident | 4.558
|  |  |  | Coincident | 4.431
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.079
|  |  |  | Coincident | 0.143
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 5.591
|  |  |  | Coincident | 5.427
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 5.669
|  |  |  | Coincident | 5.511
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.892
|  |  |  | Coincident | 4.748
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.96
|  |  |  | Coincident | 4.822
| Hamley Bridge 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.019
|  |  |  | Coincident | 1.934
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.032
|  |  |  | Coincident | 1.953
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.032
|  |  |  | Coincident | 0.049
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.504
|  |  |  | Coincident | 2.399
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.521
|  |  |  | Coincident | 2.422
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.275
|  |  |  | Coincident | 2.179
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.29
|  |  |  | Coincident | 2.2
| Kapunda TF1 11kV | Substation Rating | MVA | Non-Coincident | 17.1
|  |  |  | Coincident | 17.1
|  | Raw Adjusted MD | MW | Non-Coincident | 3.074
|  |  |  | Coincident | 2.109
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.187
|  |  |  | Coincident | 2.158
|  | Date MD occurred |  | Non-Coincident | 13/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 16:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.806
|  |  |  | Coincident | 0.07
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.951
|  |  |  | Coincident | 2.71
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.096
|  |  |  | Coincident | 2.773
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.602
|  |  |  | Coincident | 2.471
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.734
|  |  |  | Coincident | 2.528
| Kapunda TF2 11kV | Substation Rating | MVA | Non-Coincident | 17.3
|  |  |  | Coincident | 17.3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.507
|  |  |  | Coincident | 2.507
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.508
|  |  |  | Coincident | 2.508
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.086
|  |  |  | Coincident | 0.086
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.362
|  |  |  | Coincident | 3.362
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.364
|  |  |  | Coincident | 3.364
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.99
|  |  |  | Coincident | 2.99
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.991
|  |  |  | Coincident | 2.991
| Mallala 11kV | Substation Rating | MVA | Non-Coincident | 7.083
|  |  |  | Coincident | 7.083
|  | Raw Adjusted MD | MW | Non-Coincident | 3.756
|  |  |  | Coincident | 3.619
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.842
|  |  |  | Coincident | 3.706
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.067
|  |  |  | Coincident | 0.122
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 4.682
|  |  |  | Coincident | 4.511
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 4.789
|  |  |  | Coincident | 4.62
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 4.185
|  |  |  | Coincident | 4.033
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 4.281
|  |  |  | Coincident | 4.13
| Wasleys 11kV | Substation Rating | MVA | Non-Coincident | 2.7
|  |  |  | Coincident | 2.7
|  | Raw Adjusted MD | MW | Non-Coincident | 1.387
|  |  |  | Coincident | 1.274
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.387
|  |  |  | Coincident | 1.274
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.06
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.723
|  |  |  | Coincident | 1.583
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.724
|  |  |  | Coincident | 1.584
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.54
|  |  |  | Coincident | 1.414
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.54
|  |  |  | Coincident | 1.415
| Auburn 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 2.82
|  |  |  | Coincident | 2.452
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.925
|  |  |  | Coincident | 2.549
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.056
|  |  |  | Coincident | 0.125
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.051
|  |  |  | Coincident | 2.652
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.165
|  |  |  | Coincident | 2.758
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.833
|  |  |  | Coincident | 2.464
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.939
|  |  |  | Coincident | 2.562
| Eudunda 11kV | Substation Rating | MVA | Non-Coincident | 2.4
|  |  |  | Coincident | 2.4
|  | Raw Adjusted MD | MW | Non-Coincident | 1.361
|  |  |  | Coincident | 1.232
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.381
|  |  |  | Coincident | 1.257
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.076
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.568
|  |  |  | Coincident | 1.419
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.591
|  |  |  | Coincident | 1.448
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.423
|  |  |  | Coincident | 1.288
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.444
|  |  |  | Coincident | 1.314
| Marrabel 11kV | Substation Rating | MVA | Non-Coincident | 2.66
|  |  |  | Coincident | 2.66
|  | Raw Adjusted MD | MW | Non-Coincident | 0.756
|  |  |  | Coincident | 0.612
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.756
|  |  |  | Coincident | 0.612
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.049
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.856
|  |  |  | Coincident | 0.693
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.856
|  |  |  | Coincident | 0.693
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.766
|  |  |  | Coincident | 0.62
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.766
|  |  |  | Coincident | 0.62
| Riverton 11kV | Substation Rating | MVA | Non-Coincident | 3.9
|  |  |  | Coincident | 3.9
|  | Raw Adjusted MD | MW | Non-Coincident | 1.507
|  |  |  | Coincident | 1.366
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.544
|  |  |  | Coincident | 1.386
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.03
|  |  |  | Coincident | 0.078
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 1.918
|  |  |  | Coincident | 1.738
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 1.965
|  |  |  | Coincident | 1.764
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.732
|  |  |  | Coincident | 1.57
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.775
|  |  |  | Coincident | 1.593
| Robertstown 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.765
|  |  |  | Coincident | 0.665
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.765
|  |  |  | Coincident | 0.665
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.036
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.909
|  |  |  | Coincident | 0.79
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.909
|  |  |  | Coincident | 0.79
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.833
|  |  |  | Coincident | 0.724
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.833
|  |  |  | Coincident | 0.724
| Waterloo Town 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.187
|  |  |  | Coincident | 0.136
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.188
|  |  |  | Coincident | 0.138
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.008
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.254
|  |  |  | Coincident | 0.184
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.255
|  |  |  | Coincident | 0.187
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.227
|  |  |  | Coincident | 0.164
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.227
|  |  |  | Coincident | 0.167
| Whyalla City 11kV | Substation Rating | MVA | Non-Coincident | 25.129
|  |  |  | Coincident | 25.129
|  | Raw Adjusted MD | MW | Non-Coincident | 16.157
|  |  |  | Coincident | 14.327
|  | Raw Adjusted MD | MVA | Non-Coincident | 16.307
|  |  |  | Coincident | 14.519
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.423
|  |  |  | Coincident | 1.892
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 20.494
|  |  |  | Coincident | 18.172
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 20.684
|  |  |  | Coincident | 18.417
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 18.157
|  |  |  | Coincident | 16.1
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 18.326
|  |  |  | Coincident | 16.317
| Whyalla North 11kV | Substation Rating | MVA | Non-Coincident | 1.425
|  |  |  | Coincident | 1.425
|  | Raw Adjusted MD | MW | Non-Coincident | 0.461
|  |  |  | Coincident | 0.369
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.49
|  |  |  | Coincident | 0.398
|  | Date MD occurred |  | Non-Coincident | 10/11/2023
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.025
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.449
|  |  |  | Coincident | 0.36
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.478
|  |  |  | Coincident | 0.388
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.434
|  |  |  | Coincident | 0.348
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.462
|  |  |  | Coincident | 0.375
| Whyalla Stuart 11kV | Substation Rating | MVA | Non-Coincident | 29.313
|  |  |  | Coincident | 29.313
|  | Raw Adjusted MD | MW | Non-Coincident | 14.957
|  |  |  | Coincident | 13.37
|  | Raw Adjusted MD | MVA | Non-Coincident | 15.064
|  |  |  | Coincident | 13.511
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 23/01/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 18:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.337
|  |  |  | Coincident | 1.508
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 17.903
|  |  |  | Coincident | 16.004
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 18.031
|  |  |  | Coincident | 16.173
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 16.013
|  |  |  | Coincident | 14.315
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 16.128
|  |  |  | Coincident | 14.466
| Ceduna 11kV | Substation Rating | MVA | Non-Coincident | 12.79
|  |  |  | Coincident | 12.79
|  | Raw Adjusted MD | MW | Non-Coincident | 7.122
|  |  |  | Coincident | 6.868
|  | Raw Adjusted MD | MVA | Non-Coincident | 7.207
|  |  |  | Coincident | 6.944
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.093
|  |  |  | Coincident | 0.002
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 6.976
|  |  |  | Coincident | 6.727
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 7.059
|  |  |  | Coincident | 6.802
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 6.242
|  |  |  | Coincident | 6.019
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 6.316
|  |  |  | Coincident | 6.086
| Moorkitabie 11kV | Substation Rating | MVA | Non-Coincident | 1.4
|  |  |  | Coincident | 1.4
|  | Raw Adjusted MD | MW | Non-Coincident | 0.68
|  |  |  | Coincident | 0.63
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.685
|  |  |  | Coincident | 0.633
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.7
|  |  |  | Coincident | 0.648
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.705
|  |  |  | Coincident | 0.651
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.63
|  |  |  | Coincident | 0.583
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.634
|  |  |  | Coincident | 0.586
| Polda 11kV | Substation Rating | MVA | Non-Coincident | 1.3
|  |  |  | Coincident | 1.3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.728
|  |  |  | Coincident | 0.614
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.728
|  |  |  | Coincident | 0.614
|  | Date MD occurred |  | Non-Coincident | 27/02/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.646
|  |  |  | Coincident | 0.545
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.647
|  |  |  | Coincident | 0.545
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.603
|  |  |  | Coincident | 0.509
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.603
|  |  |  | Coincident | 0.509
| Streaky Bay 11kV | Substation Rating | MVA | Non-Coincident | 7.119
|  |  |  | Coincident | 7.119
|  | Raw Adjusted MD | MW | Non-Coincident | 3.302
|  |  |  | Coincident | 2.768
|  | Raw Adjusted MD | MVA | Non-Coincident | 3.305
|  |  |  | Coincident | 2.781
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.003
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 3.374
|  |  |  | Coincident | 2.828
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 3.377
|  |  |  | Coincident | 2.842
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 3.017
|  |  |  | Coincident | 2.529
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 3.02
|  |  |  | Coincident | 2.541
| Tarlton 11kV | Substation Rating | MVA | Non-Coincident | 1.1
|  |  |  | Coincident | 1.1
|  | Raw Adjusted MD | MW | Non-Coincident | 0.519
|  |  |  | Coincident | 0.479
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.57
|  |  |  | Coincident | 0.538
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.595
|  |  |  | Coincident | 0.549
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.654
|  |  |  | Coincident | 0.617
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.538
|  |  |  | Coincident | 0.496
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.591
|  |  |  | Coincident | 0.558
| Wudinna 11kV | Substation Rating | MVA | Non-Coincident | 5.456
|  |  |  | Coincident | 5.456
|  | Raw Adjusted MD | MW | Non-Coincident | 1.899
|  |  |  | Coincident | 1.62
|  | Raw Adjusted MD | MVA | Non-Coincident | 1.91
|  |  |  | Coincident | 1.635
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 21:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.144
|  |  |  | Coincident | 1.829
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.157
|  |  |  | Coincident | 1.846
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.916
|  |  |  | Coincident | 1.635
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.928
|  |  |  | Coincident | 1.65
| Arno Bay 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.772
|  |  |  | Coincident | 0.598
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.836
|  |  |  | Coincident | 0.648
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.59
|  |  |  | Coincident | 0.457
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.639
|  |  |  | Coincident | 0.495
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.557
|  |  |  | Coincident | 0.431
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.603
|  |  |  | Coincident | 0.467
| Boothby 33kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 0.804
|  |  |  | Coincident | 0.775
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.874
|  |  |  | Coincident | 0.842
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.892
|  |  |  | Coincident | 0.859
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.969
|  |  |  | Coincident | 0.934
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.825
|  |  |  | Coincident | 0.795
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.896
|  |  |  | Coincident | 0.864
| Caralue 11kV | Substation Rating | MVA | Non-Coincident | 3.2
|  |  |  | Coincident | 3.2
|  | Raw Adjusted MD | MW | Non-Coincident | 2.178
|  |  |  | Coincident | 2.178
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.234
|  |  |  | Coincident | 2.234
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.43
|  |  |  | Coincident | 2.43
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.492
|  |  |  | Coincident | 2.492
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.244
|  |  |  | Coincident | 2.244
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.302
|  |  |  | Coincident | 2.302
| Cleve 11kV | Substation Rating | MVA | Non-Coincident | 7.111
|  |  |  | Coincident | 7.111
|  | Raw Adjusted MD | MW | Non-Coincident | 2.221
|  |  |  | Coincident | 2.216
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.249
|  |  |  | Coincident | 2.241
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.442
|  |  |  | Coincident | 2.437
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.473
|  |  |  | Coincident | 2.464
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.214
|  |  |  | Coincident | 2.21
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.242
|  |  |  | Coincident | 2.234
| Cleve 33kV | Substation Rating | MVA | Non-Coincident | 17.7
|  |  |  | Coincident | 17.7
|  | Raw Adjusted MD | MW | Non-Coincident | 2.6
|  |  |  | Coincident | 2.1
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.608
|  |  |  | Coincident | 2.102
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.246
|  |  |  | Coincident | 1.814
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.253
|  |  |  | Coincident | 1.816
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 2.042
|  |  |  | Coincident | 1.649
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 2.048
|  |  |  | Coincident | 1.651
| Cowell 11kV | Substation Rating | MVA | Non-Coincident | 3
|  |  |  | Coincident | 3
|  | Raw Adjusted MD | MW | Non-Coincident | 2.15
|  |  |  | Coincident | 1.97
|  | Raw Adjusted MD | MVA | Non-Coincident | 2.155
|  |  |  | Coincident | 1.973
|  | Date MD occurred |  | Non-Coincident | 09/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.001
|  |  |  | Coincident | 0.001
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 2.195
|  |  |  | Coincident | 2.011
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 2.2
|  |  |  | Coincident | 2.015
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 1.961
|  |  |  | Coincident | 1.797
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 1.966
|  |  |  | Coincident | 1.8
| Darke Peak 11kV | Substation Rating | MVA | Non-Coincident | 1.425
|  |  |  | Coincident | 1.425
|  | Raw Adjusted MD | MW | Non-Coincident | 0.276
|  |  |  | Coincident | 0.258
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.311
|  |  |  | Coincident | 0.294
|  | Date MD occurred |  | Non-Coincident | 23/01/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 20:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.004
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.325
|  |  |  | Coincident | 0.304
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.366
|  |  |  | Coincident | 0.347
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.303
|  |  |  | Coincident | 0.283
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.341
|  |  |  | Coincident | 0.323
| Lock 11kV | Substation Rating | MVA | Non-Coincident | 1.2
|  |  |  | Coincident | 1.2
|  | Raw Adjusted MD | MW | Non-Coincident | 0.627
|  |  |  | Coincident | 0.627
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.667
|  |  |  | Coincident | 0.667
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:30:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.724
|  |  |  | Coincident | 0.724
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.771
|  |  |  | Coincident | 0.771
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.673
|  |  |  | Coincident | 0.673
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.717
|  |  |  | Coincident | 0.717
| Rudall 11kV | Substation Rating | MVA | Non-Coincident | 0.65
|  |  |  | Coincident | 0.65
|  | Raw Adjusted MD | MW | Non-Coincident | 0.25
|  |  |  | Coincident | 0.241
|  | Raw Adjusted MD | MVA | Non-Coincident | 0.261
|  |  |  | Coincident | 0.253
|  | Date MD occurred |  | Non-Coincident | 11/03/2024
|  |  |  | Coincident | 11/03/2024
|  | Half hour time period MD occurred |  | Non-Coincident | 19:00:00
|  |  |  | Coincident | 19:30:00
|  | Winter/Summer Peaking |  | Non-Coincident | Summer
|  |  |  | Coincident | Summer
|  | Adjustments - Embedded generation | MW | Non-Coincident | 0.002
|  |  |  | Coincident | 0
|  | Weather Corrected MD 10% POE | MW | Non-Coincident | 0.261
|  |  |  | Coincident | 0.252
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident | 0.273
|  |  |  | Coincident | 0.265
|  | Weather Corrected MD 50% POE | MW | Non-Coincident | 0.236
|  |  |  | Coincident | 0.227
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident | 0.246
|  |  |  | Coincident | 0.239
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
|  | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
| <Enter substation name> | Substation Rating | MVA | Non-Coincident
Coincident
|  | Raw Adjusted MD | MW | Non-Coincident
Coincident
|  | Raw Adjusted MD | MVA | Non-Coincident
Coincident
|  | Date MD occurred |  | Non-Coincident
Coincident
|  | Half hour time period MD occurred |  | Non-Coincident
Coincident
|  | Winter/Summer Peaking |  | Non-Coincident
Coincident
|  | Adjustments - Embedded generation | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 10% POE | MVA | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MW | Non-Coincident
Coincident
|  | Weather Corrected MD 50% POE | MVA | Non-Coincident
Coincident
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## 6.3 Sustained interruptions
REGULATORY REPORTING STATEMENT
SA Power Networks
CATEGORY ANALYSIS 2023-24
6.3 SUSTAINED INTERRUPTIONS TO SUPPLY
TEMPLATE DATE - MAY 2024
6.3.1 - SUSTAINED INTERRUPTIONS TO SUPPLY (for 2023-24)
There is ONE table on this worksheet. It has been grouped into five subgroups of 10000 rows each for navigation purposes. See the Instructions sheet on how to group and ungroup data.
Definitions:
Feeder classification definitions (column E) |  |  |  |  | Average duration of sustained customer interruption (column I) |  | Effect on unplanned SAIDI (column J) |  | Effect on unplanned SAIFI (column K)
CBD feeder: a feeder supplying predominantly commercial, high-rise buildings, supplied by a predominantly underground distribution network containing significant interconnection and redundancy when compared to urban areas. Urban feeder: a feeder, that is not a CBD feeder, with actual maximum demand over the reporting period per total feeder route length greater than 0.3 MVA/km. Short rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length less than 200 km. Long rural feeder: a feeder that is not a CBD or urban feeder with a total feeder route length greater than 200 km. |  |  |  |  | The average duration of an interruption experienced by an affected customer. |  | The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less). |  | The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
Date of event | Time of interruption | Asset ID | Feeder classification | Reason for interruption | Detailed reason for interruption | Number of customers affected by the interruption | Average duration of sustained customer interruption | Effect on unplanned SAIDI | Effect on unplanned SAIFI | MED
(DD/MM/YYYY) | (HH:MM) | (eg. feeder ID) | (drop down) | (select from options in drop-down box) | (select from options in column 'O' that correspond with reason in column 'F') |  | (minutes)
01/07/2023 | 01:56 | KA06 | LONG RURAL | Overloads |  | 1.00 | 83.0 | 0.000596 | 0.0000072 | No
01/07/2023 | 06:49 | SSD171 | SHORT RURAL | Unknown | Unknown | 1.00 | 18.0 | 0.000127 | 0.0000070 | No
01/07/2023 | 08:38 | M21 | LONG RURAL | Asset failure | LV | 1.00 | 343.0 | 0.002461 | 0.0000072 | No
01/07/2023 | 09:20 | SB21 | LONG RURAL | Asset failure | HV | 2.00 | 158.5 | 0.002275 | 0.0000144 | No
01/07/2023 | 09:20 | ME116C | URBAN | Asset failure | LV | 1.00 | 264.0 | 0.000407 | 0.0000015 | No
01/07/2023 | 09:33 | AP146B | URBAN | Unknown | Unknown | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
01/07/2023 | 10:54 | CV30 | LONG RURAL | Unknown | Unknown | 86.00 | 439.6 | 0.271287 | 0.0006172 | No
01/07/2023 | 11:19 | KA01 | SHORT RURAL | Asset failure | LV | 16.00 | 30.0 | 0.003377 | 0.0001126 | No
01/07/2023 | 12:23 | NL115B | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
01/07/2023 | 13:17 | KA04 | LONG RURAL | Asset failure | LV | 1.00 | 127.0 | 0.000911 | 0.0000072 | No
01/07/2023 | 13:22 | AP372D | URBAN | Asset failure | LV | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
01/07/2023 | 13:25 | NA01 | LONG RURAL | Asset failure | LV | 19.00 | 200.2 | 0.027299 | 0.0001364 | No
01/07/2023 | 14:25 | MT11 | LONG RURAL | Unknown | Unknown | 1.00 | 155.0 | 0.001112 | 0.0000072 | No
01/07/2023 | 14:28 | VH32 | SHORT RURAL | Asset failure | LV | 1.00 | 373.0 | 0.002624 | 0.0000070 | No
01/07/2023 | 16:06 | NL115D | URBAN | Asset failure | LV | 39.00 | 45.3 | 0.002721 | 0.0000601 | No
01/07/2023 | 17:37 | BT14 | LONG RURAL | Asset failure | LV | 2.00 | 1,077.0 | 0.015458 | 0.0000144 | No
01/07/2023 | 18:05 | AP149A | URBAN | Asset failure | LV | 81.00 | 186.0 | 0.023228 | 0.0001249 | No
02/07/2023 | 02:53 | MB81 | LONG RURAL | Third Party | Vehicle impact | 387.00 | 115.0 | 0.319383 | 0.0027772 | No
02/07/2023 | 04:57 | HH148A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 356.00 | 71.2 | 0.039060 | 0.0005489 | No
02/07/2023 | 07:58 | MV64 | SHORT RURAL | Asset failure | LV | 16.00 | 454.0 | 0.051106 | 0.0001126 | No
02/07/2023 | 08:20 | AP132C | URBAN | Planned |  | 24.00 | 360.8 | 0.013349 | 0.0000370 | No
02/07/2023 | 10:41 | AP355A | URBAN | Unknown | Unknown | 73.00 | 166.0 | 0.018683 | 0.0001125 | No
02/07/2023 | 10:52 | HH121D | URBAN | Asset failure | LV | 1.00 | 95.0 | 0.000146 | 0.0000015 | No
02/07/2023 | 11:07 | SM126C | URBAN | Animal | Animal nesting/burrowing, etc and other | 170.00 | 105.0 | 0.027520 | 0.0002621 | No
02/07/2023 | 11:18 | SM216B | URBAN | Unknown | Unknown | 1.00 | 313.0 | 0.000483 | 0.0000015 | No
02/07/2023 | 12:17 | EL01Z | URBAN | Overloads |  | 10.00 | 155.0 | 0.002390 | 0.0000154 | No
02/07/2023 | 12:24 | BM13 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 36.00 | 103.0 | 0.026088 | 0.0002533 | No
02/07/2023 | 12:33 | NL234B | URBAN | Asset failure | LV | 1.00 | 759.0 | 0.001170 | 0.0000015 | No
02/07/2023 | 12:59 | SM126A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 281.00 | 675.1 | 0.292494 | 0.0004332 | No
02/07/2023 | 13:23 | SA32 | URBAN | Asset failure | LV | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
02/07/2023 | 13:37 | BM13 | SHORT RURAL | Animal | Animal impact | 1.00 | 51.0 | 0.000359 | 0.0000070 | No
02/07/2023 | 14:00 | HH403B | URBAN | Unknown | Unknown | 1,847.00 | 16.3 | 0.046287 | 0.0028476 | No
02/07/2023 | 14:43 | BM13 | SHORT RURAL | Unknown | Unknown | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
02/07/2023 | 15:48 | CV15 | LONG RURAL | Asset failure | LV | 2.00 | 43.0 | 0.000617 | 0.0000144 | No
02/07/2023 | 16:30 | SM349E | URBAN | Asset failure | LV | 101.00 | 284.0 | 0.044224 | 0.0001557 | No
02/07/2023 | 16:55 | EL01Z | URBAN | Asset failure | LV | 10.00 | 369.0 | 0.005689 | 0.0000154 | No
02/07/2023 | 17:40 | HH177E | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
02/07/2023 | 17:46 | AP227B | URBAN | Third Party | Other | 59.00 | 152.0 | 0.013826 | 0.0000910 | No
02/07/2023 | 18:04 | MG32 | LONG RURAL | Asset failure | LV | 9.00 | 94.0 | 0.006071 | 0.0000646 | No
02/07/2023 | 18:32 | SM374C | URBAN | Asset failure | LV | 1.00 | 379.0 | 0.000584 | 0.0000015 | No
02/07/2023 | 19:18 | WHY06 | URBAN | Asset failure | LV | 16.67 | 128.0 | 0.003289 | 0.0000257 | No
02/07/2023 | 19:26 | NL210E | URBAN | Asset failure | LV | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
02/07/2023 | 20:06 | MTB11 | LONG RURAL | Asset failure | HV | 711.00 | 310.2 | 1.582940 | 0.0051024 | No
02/07/2023 | 20:06 | MTB11 | SHORT RURAL | Asset failure | HV | 100.00 | 617.8 | 0.434681 | 0.0007035 | No
02/07/2023 | 20:22 | SA744D | URBAN | Asset failure | LV | 1.00 | 1,330.0 | 0.002051 | 0.0000015 | No
02/07/2023 | 20:22 | EL13 | URBAN | Overloads |  | 1.00 | 449.0 | 0.000692 | 0.0000015 | No
02/07/2023 | 21:51 | AP125D | URBAN | Asset failure | LV | 1.00 | 56.0 | 0.000086 | 0.0000015 | No
02/07/2023 | 22:03 | CN41 | LONG RURAL | Unknown | Unknown | 33.00 | 261.0 | 0.061810 | 0.0002368 | No
03/07/2023 | 05:55 | HH148D | URBAN | Overloads |  | 17.67 | 277.0 | 0.007545 | 0.0000272 | No
03/07/2023 | 07:56 | M91 | LONG RURAL | Asset failure | LV | 6.00 | 256.0 | 0.011023 | 0.0000431 | No
03/07/2023 | 08:30 | NL210A | URBAN | Asset failure | HV | 35.00 | 810.0 | 0.043709 | 0.0000540 | No
03/07/2023 | 08:46 | AP149F | URBAN | Planned |  | 39.00 | 303.0 | 0.018219 | 0.0000601 | No
03/07/2023 | 08:49 | MG03 | SHORT RURAL | Unknown | Unknown | 12.67 | 281.0 | 0.025042 | 0.0000891 | No
03/07/2023 | 08:55 | AP424A | URBAN | Asset failure | LV | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
03/07/2023 | 09:17 | GA800A | SHORT RURAL | Planned |  | 99.00 | 137.8 | 0.095999 | 0.0006965 | No
03/07/2023 | 09:17 | MG17 | LONG RURAL | Asset failure | LV | 1.00 | 451.0 | 0.003237 | 0.0000072 | No
03/07/2023 | 09:32 | NL115C | URBAN | Asset failure | LV | 1.00 | 762.0 | 0.001175 | 0.0000015 | No
03/07/2023 | 09:33 | WHY09 | URBAN | Unknown | Unknown | 1.00 | 415.0 | 0.000640 | 0.0000015 | No
03/07/2023 | 09:38 | GU32 | LONG RURAL | Planned |  | 2.00 | 355.0 | 0.005095 | 0.0000144 | No
03/07/2023 | 09:41 | AP372D | URBAN | Overloads |  | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
03/07/2023 | 09:47 | MT27 | SHORT RURAL | Planned |  | 11.00 | 156.5 | 0.012108 | 0.0000774 | No
03/07/2023 | 09:52 | VH23 | SHORT RURAL | Planned |  | 120.00 | 290.7 | 0.245398 | 0.0008443 | No
03/07/2023 | 09:53 | WK42 | SHORT RURAL | Overloads |  | 3.33 | 278.0 | 0.006520 | 0.0000235 | No
03/07/2023 | 09:57 | ME427D | URBAN | Asset failure | LV | 57.00 | 179.0 | 0.015731 | 0.0000879 | No
03/07/2023 | 10:01 | BT18 | LONG RURAL | Planned |  | 2.00 | 168.0 | 0.002411 | 0.0000144 | No
03/07/2023 | 10:05 | MTB33 | SHORT RURAL | Asset failure | LV | 4.00 | 85.0 | 0.002392 | 0.0000281 | No
03/07/2023 | 10:10 | CL05 | LONG RURAL | Planned |  | 2.00 | 189.0 | 0.002713 | 0.0000144 | No
03/07/2023 | 10:11 | ST35 | LONG RURAL | Planned |  | 54.00 | 123.0 | 0.047665 | 0.0003875 | No
03/07/2023 | 10:24 | CD03 | SHORT RURAL | Planned |  | 15.00 | 67.6 | 0.007134 | 0.0001055 | No
03/07/2023 | 10:24 | MB44 | LONG RURAL | Planned |  | 61.00 | 152.0 | 0.066539 | 0.0004378 | No
03/07/2023 | 10:25 | HH409F | URBAN | Other |  | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
03/07/2023 | 10:50 | WK41 | SHORT RURAL | Asset failure | LV | 20.00 | 174.0 | 0.024484 | 0.0001407 | No
03/07/2023 | 10:55 | SA36 | URBAN | Overloads |  | 4.33 | 286.0 | 0.001911 | 0.0000067 | No
03/07/2023 | 11:13 | AP139D | URBAN | Overloads |  | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
03/07/2023 | 11:30 | KA01 | SHORT RURAL | Unknown | Unknown | 10.00 | 186.0 | 0.013086 | 0.0000704 | No
03/07/2023 | 11:41 | NL210A | URBAN | Planned |  | 226.00 | 19.0 | 0.006620 | 0.0003484 | No
03/07/2023 | 11:55 | YK01 | LONG RURAL | Asset failure | HV | 69.00 | 361.4 | 0.178978 | 0.0004952 | No
03/07/2023 | 12:04 | MG17 | LONG RURAL | Asset failure | LV | 1.00 | 273.0 | 0.001959 | 0.0000072 | No
03/07/2023 | 12:51 | WHY12 | URBAN | Unknown | Unknown | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
03/07/2023 | 13:07 | GU31 | LONG RURAL | Asset failure | LV | 2.00 | 360.0 | 0.005167 | 0.0000144 | No
03/07/2023 | 13:13 | ME116D | URBAN | Asset failure | LV | 33.67 | 36.3 | 0.001883 | 0.0000519 | No
03/07/2023 | 13:27 | KI13 | LONG RURAL | Planned |  | 10.00 | 66.0 | 0.004736 | 0.0000718 | No
03/07/2023 | 13:34 | EL01L | URBAN | Asset failure | LV | 1.00 | 74.0 | 0.000114 | 0.0000015 | No
03/07/2023 | 13:49 | HH409E | URBAN | Overloads |  | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
03/07/2023 | 13:55 | SG01 | SHORT RURAL | Asset failure | LV | 2.00 | 240.0 | 0.003377 | 0.0000141 | No
03/07/2023 | 14:48 | MV22 | SHORT RURAL | Animal | Animal impact | 9.00 | 153.0 | 0.009688 | 0.0000633 | No
03/07/2023 | 14:55 | AP829F | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
03/07/2023 | 15:05 | MV33 | SHORT RURAL | Asset failure | LV | 2.00 | 1,439.0 | 0.020248 | 0.0000141 | No
03/07/2023 | 16:05 | WHY06 | URBAN | Asset failure | LV | 13.00 | 102.0 | 0.002044 | 0.0000200 | No
03/07/2023 | 16:48 | CBD367V | CBD | Network business | Switching and protection error | 2.00 | 282.0 | 0.081485 | 0.0002890 | No
03/07/2023 | 17:14 | ME131A | URBAN | Asset failure | LV | 26.00 | 71.0 | 0.002846 | 0.0000401 | No
03/07/2023 | 17:17 | MV22 | SHORT RURAL | Animal | Animal impact | 1.00 | 201.0 | 0.001414 | 0.0000070 | No
03/07/2023 | 17:23 | SM137A | URBAN | Asset failure | LV | 30.00 | 116.0 | 0.005365 | 0.0000463 | No
03/07/2023 | 19:27 | MV15 | SHORT RURAL | Asset failure | HV | 4.00 | 43.0 | 0.001210 | 0.0000281 | No
03/07/2023 | 20:01 | HH177F | URBAN | Asset failure | LV | 1.00 | 421.0 | 0.000649 | 0.0000015 | No
03/07/2023 | 22:17 | HH409E | URBAN | Asset failure | LV | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
03/07/2023 | 22:35 | ME427E | URBAN | Asset failure | LV | 29.00 | 65.1 | 0.002909 | 0.0000447 | No
04/07/2023 | 00:13 | ME347A | URBAN | Overloads |  | 1.00 | 583.0 | 0.000899 | 0.0000015 | No
04/07/2023 | 01:15 | MI15 | LONG RURAL | Asset failure | HV | 1.00 | 732.0 | 0.005253 | 0.0000072 | No
04/07/2023 | 02:02 | HH177F | URBAN | Asset failure | HV | 5.00 | 50.0 | 0.000385 | 0.0000077 | No
04/07/2023 | 04:23 | PP09 | LONG RURAL | Asset failure | LV | 1.00 | 575.0 | 0.004126 | 0.0000072 | No
04/07/2023 | 07:02 | HH496C | URBAN | Asset failure | LV | 11.00 | 276.0 | 0.004681 | 0.0000170 | No
04/07/2023 | 07:49 | AP226D | URBAN | Asset failure | LV | 1.00 | 557.0 | 0.000859 | 0.0000015 | No
04/07/2023 | 08:11 | HH102D | URBAN | Asset failure | LV | 6.00 | 522.0 | 0.004829 | 0.0000093 | No
04/07/2023 | 08:26 | SM402A | URBAN | Asset failure | LV | 2.33 | 24.0 | 0.000086 | 0.0000036 | No
04/07/2023 | 08:41 | MV62 | SHORT RURAL | Planned |  | 290.00 | 372.9 | 0.760804 | 0.0020403 | No
04/07/2023 | 09:04 | CV32 | LONG RURAL | Planned |  | 8.00 | 279.0 | 0.016018 | 0.0000574 | No
04/07/2023 | 09:18 | M13 | LONG RURAL | Asset failure | LV | 1.00 | 162.0 | 0.001163 | 0.0000072 | No
04/07/2023 | 10:34 | M21 | LONG RURAL | Unknown | Unknown | 68.33 | 176.0 | 0.086307 | 0.0004904 | No
04/07/2023 | 11:04 | KA14 | LONG RURAL | Planned |  | 12.00 | 94.0 | 0.008095 | 0.0000861 | No
04/07/2023 | 11:18 | EL01Z | URBAN | Asset failure | LV | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
04/07/2023 | 11:18 | M61 | LONG RURAL | Planned |  | 21.00 | 162.0 | 0.024414 | 0.0001507 | No
04/07/2023 | 11:31 | MG06 | SHORT RURAL | Weather |  | 40.00 | 27.0 | 0.007598 | 0.0002814 | No
04/07/2023 | 14:02 | WHY07 | URBAN | Asset failure | LV | 61.00 | 77.0 | 0.007242 | 0.0000940 | No
04/07/2023 | 14:28 | BT20 | LONG RURAL | Asset failure | HV | 60.00 | 1,241.0 | 0.534350 | 0.0004306 | No
04/07/2023 | 14:36 | ME200A | URBAN | Asset failure | LV | 36.33 | 156.0 | 0.008739 | 0.0000560 | No
04/07/2023 | 16:48 | KA29 | LONG RURAL | Asset failure | HV | 109.00 | 24.0 | 0.018773 | 0.0007822 | No
04/07/2023 | 17:29 | ME347B | URBAN | Asset failure | HV | 58.00 | 247.0 | 0.022087 | 0.0000894 | No
04/07/2023 | 17:39 | VH72 | SHORT RURAL | Asset failure | HV | 91.67 | 257.2 | 0.165880 | 0.0006449 | No
04/07/2023 | 17:54 | HH496C | URBAN | Asset failure | LV | 1.00 | 253.0 | 0.000390 | 0.0000015 | No
04/07/2023 | 18:33 | SM126D | URBAN | Animal | Animal impact | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
04/07/2023 | 18:49 | SM350F | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
04/07/2023 | 21:21 | MG27 | LONG RURAL | Asset failure | HV | 19.00 | 48.0 | 0.006545 | 0.0001364 | No
04/07/2023 | 22:30 | HH403A | URBAN | Overloads |  | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
04/07/2023 | 22:49 | SA41 | URBAN | Overloads |  | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
05/07/2023 | 05:38 | EL09 | URBAN | Overloads |  | 4.33 | 186.0 | 0.001243 | 0.0000067 | No
05/07/2023 | 06:55 | HH130A | URBAN | Unknown | Unknown | 1,137.67 | 11.0 | 0.019298 | 0.0017540 | No
05/07/2023 | 07:10 | ST23 | SHORT RURAL | Animal | Animal impact | 191.00 | 19.9 | 0.026749 | 0.0013438 | No
05/07/2023 | 07:16 | SM350B | URBAN | Asset failure | LV | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
05/07/2023 | 07:51 | MG13 | SHORT RURAL | Animal | Animal impact | 1.00 | 237.0 | 0.001667 | 0.0000070 | No
05/07/2023 | 08:05 | MG13 | SHORT RURAL | Unknown | Unknown | 110.33 | 18.6 | 0.014411 | 0.0007762 | No
05/07/2023 | 08:16 | HH130C | URBAN | Planned |  | 1.00 | 348.0 | 0.000537 | 0.0000015 | No
05/07/2023 | 08:40 | GA26 | URBAN | Planned |  | 191.00 | 164.1 | 0.048328 | 0.0002945 | No
05/07/2023 | 08:57 | KA22 | LONG RURAL | Planned |  | 1.00 | 338.0 | 0.002426 | 0.0000072 | No
05/07/2023 | 09:03 | EL19 | URBAN | Asset failure | HV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
05/07/2023 | 09:03 | EL19 | URBAN | Planned |  | 7.00 | 187.0 | 0.002018 | 0.0000108 | No
05/07/2023 | 09:13 | CM05 | LONG RURAL | Asset failure | LV | 1.00 | 381.0 | 0.002734 | 0.0000072 | No
05/07/2023 | 09:55 | KI51 | LONG RURAL | Planned |  | 2.00 | 119.0 | 0.001708 | 0.0000144 | No
05/07/2023 | 10:02 | VH35 | SHORT RURAL | Unknown | Unknown | 1.00 | 569.0 | 0.004003 | 0.0000070 | No
05/07/2023 | 10:06 | VH45 | SHORT RURAL | Planned |  | 9.00 | 399.3 | 0.025286 | 0.0000633 | No
05/07/2023 | 10:07 | NL115D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 5.00 | 63.4 | 0.000489 | 0.0000077 | No
05/07/2023 | 10:40 | SG04 | SHORT RURAL | Asset failure | LV | 3.33 | 35.0 | 0.000821 | 0.0000235 | No
05/07/2023 | 10:40 | PA06 | LONG RURAL | Asset failure | LV | 1.00 | 317.0 | 0.002275 | 0.0000072 | No
05/07/2023 | 10:48 | NA04 | LONG RURAL | Asset failure | LV | 1.00 | 2,911.0 | 0.020890 | 0.0000072 | No
05/07/2023 | 11:09 | AP425A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,517.00 | 78.3 | 0.183245 | 0.0023388 | No
05/07/2023 | 11:19 | BM34 | SHORT RURAL | Unknown | Unknown | 121.00 | 247.0 | 0.210270 | 0.0008513 | No
05/07/2023 | 11:29 | HH409E | URBAN | Asset failure | LV | 8.00 | 221.0 | 0.002726 | 0.0000123 | No
05/07/2023 | 11:32 | CL27 | LONG RURAL | Planned |  | 1.00 | 136.0 | 0.000976 | 0.0000072 | No
05/07/2023 | 12:37 | KI51 | LONG RURAL | Planned |  | 1.00 | 57.0 | 0.000409 | 0.0000072 | No
05/07/2023 | 12:55 | NA61 | LONG RURAL | Asset failure | HV | 15.00 | 95.0 | 0.010226 | 0.0001076 | No
05/07/2023 | 13:02 | HH432F | URBAN | Asset failure | LV | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
05/07/2023 | 13:09 | CV30 | LONG RURAL | Asset failure | HV | 1.00 | 11.0 | 0.000079 | 0.0000072 | No
05/07/2023 | 13:09 | NL544B | URBAN | Unknown | Unknown | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
05/07/2023 | 13:11 | SG13 | SHORT RURAL | Asset failure | LV | 31.00 | 144.0 | 0.031406 | 0.0002181 | No
05/07/2023 | 13:21 | AP149H | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 45.00 | 62.0 | 0.004301 | 0.0000694 | No
05/07/2023 | 13:31 | CBD103F | URBAN | Weather |  | 12.00 | 91.0 | 0.001684 | 0.0000185 | No
05/07/2023 | 13:31 | SA18 | URBAN | Overloads |  | 1.00 | 895.0 | 0.001380 | 0.0000015 | No
05/07/2023 | 13:36 | SM137B | URBAN | Asset failure | LV | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
05/07/2023 | 15:00 | HH496C | URBAN | Unknown | Unknown | 1.00 | 276.0 | 0.000426 | 0.0000015 | No
05/07/2023 | 15:03 | AP146E | URBAN | Asset failure | LV | 1.00 | 335.0 | 0.000516 | 0.0000015 | No
05/07/2023 | 15:06 | SA20 | URBAN | Third Party | Vehicle impact | 282.00 | 630.5 | 0.274133 | 0.0004348 | No
05/07/2023 | 15:19 | SA38 | URBAN | Overloads |  | 4.67 | 182.0 | 0.001309 | 0.0000072 | No
05/07/2023 | 15:34 | BM51 | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
05/07/2023 | 16:04 | SM137B | URBAN | Network business | Switching and protection error | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
05/07/2023 | 19:37 | HH386D | URBAN | Overloads |  | 43.00 | 117.4 | 0.007781 | 0.0000663 | No
05/07/2023 | 21:25 | AP146E | URBAN | Asset failure | LV | 143.00 | 81.0 | 0.017858 | 0.0002205 | No
05/07/2023 | 21:55 | HH121G | URBAN | Overloads |  | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
05/07/2023 | 23:10 | MB27 | SHORT RURAL | Weather |  | 190.00 | 84.6 | 0.113131 | 0.0013367 | No
06/07/2023 | 01:36 | HH403B | URBAN | Weather |  | 1,327.00 | 219.7 | 0.449463 | 0.0020459 | No
06/07/2023 | 03:48 | HH403B | URBAN | Asset failure | LV | 1.00 | 73.0 | 0.000113 | 0.0000015 | No
06/07/2023 | 05:37 | PL07 | LONG RURAL | Weather |  | 1.00 | 14.0 | 0.000100 | 0.0000072 | No
06/07/2023 | 05:37 | PL07 | URBAN | Weather |  | 3,294.00 | 16.7 | 0.084604 | 0.0050785 | No
06/07/2023 | 06:37 | M04 | LONG RURAL | Unknown | Unknown | 107.00 | 772.1 | 0.592908 | 0.0007679 | No
06/07/2023 | 06:56 | PL22 | LONG RURAL | Weather |  | 42.00 | 205.0 | 0.061788 | 0.0003014 | No
06/07/2023 | 07:03 | PL07 | URBAN | Asset failure | LV | 1.00 | 233.0 | 0.000359 | 0.0000015 | No
06/07/2023 | 07:42 | AP365F | URBAN | Asset failure | LV | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
06/07/2023 | 07:42 | AP149H | URBAN | Asset failure | LV | 45.00 | 56.0 | 0.003885 | 0.0000694 | No
06/07/2023 | 08:10 | SM216B | URBAN | Third Party | Other | 8.67 | 90.5 | 0.001209 | 0.0000134 | No
06/07/2023 | 08:36 | EL15 | URBAN | Third Party | Vehicle impact | 10.00 | 228.0 | 0.003515 | 0.0000154 | No
06/07/2023 | 08:39 | EL260C | URBAN | Planned |  | 82.00 | 246.8 | 0.031197 | 0.0001264 | No
06/07/2023 | 08:39 | MG06 | SHORT RURAL | Planned |  | 1.00 | 100.0 | 0.000704 | 0.0000070 | No
06/07/2023 | 08:44 | SG14 | SHORT RURAL | Overloads |  | 1.00 | 191.0 | 0.001344 | 0.0000070 | No
06/07/2023 | 08:45 | PL07 | URBAN | Asset failure | HV | 145.00 | 130.0 | 0.029062 | 0.0002236 | No
06/07/2023 | 08:45 | PL07 | URBAN | Asset failure | LV | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
06/07/2023 | 08:46 | GU21 | LONG RURAL | Weather |  | 215.00 | 106.4 | 0.164101 | 0.0015429 | No
06/07/2023 | 08:52 | EL02 | URBAN | Planned |  | 17.00 | 89.1 | 0.002336 | 0.0000262 | No
06/07/2023 | 08:57 | VH12 | SHORT RURAL | Planned |  | 63.00 | 344.0 | 0.152473 | 0.0004432 | No
06/07/2023 | 09:06 | MG06 | SHORT RURAL | Planned |  | 63.00 | 112.0 | 0.049642 | 0.0004432 | No
06/07/2023 | 09:15 | AP355C | URBAN | Planned |  | 103.00 | 340.0 | 0.053992 | 0.0001588 | No
06/07/2023 | 09:22 | LX54 | SHORT RURAL | Planned |  | 46.00 | 186.9 | 0.060491 | 0.0003236 | No
06/07/2023 | 09:26 | VH23 | SHORT RURAL | Planned |  | 13.00 | 307.5 | 0.028121 | 0.0000915 | No
06/07/2023 | 09:42 | HH107B | URBAN | Planned |  | 179.00 | 476.0 | 0.131364 | 0.0002760 | No
06/07/2023 | 09:52 | SM172E | URBAN | Planned |  | 41.00 | 221.0 | 0.013970 | 0.0000632 | No
06/07/2023 | 09:54 | SB21 | LONG RURAL | Unknown | Unknown | 4.00 | 53.0 | 0.001521 | 0.0000287 | No
06/07/2023 | 09:55 | CL20 | LONG RURAL | Overloads |  | 1.00 | 281.0 | 0.002017 | 0.0000072 | No
06/07/2023 | 09:55 | MTB21 | SHORT RURAL | Overloads |  | 1.00 | 70.0 | 0.000492 | 0.0000070 | No
06/07/2023 | 10:16 | HH145C | URBAN | Planned |  | 96.00 | 278.0 | 0.041146 | 0.0001480 | No
06/07/2023 | 10:18 | MI07 | LONG RURAL | Asset failure | HV | 3.00 | 94.0 | 0.002024 | 0.0000215 | No
06/07/2023 | 10:45 | KI44 | LONG RURAL | Planned |  | 2.00 | 135.0 | 0.001938 | 0.0000144 | No
06/07/2023 | 11:06 | HH130B | URBAN | Asset failure | LV | 82.00 | 45.6 | 0.005771 | 0.0001264 | No
06/07/2023 | 11:10 | HH341D | URBAN | Asset failure | LV | 79.00 | 64.0 | 0.007795 | 0.0001218 | No
06/07/2023 | 11:27 | HH409B | URBAN | Asset failure | LV | 25.00 | 93.0 | 0.003585 | 0.0000385 | No
06/07/2023 | 11:33 | ME347C | URBAN | Asset failure | LV | 1.00 | 557.0 | 0.000859 | 0.0000015 | No
06/07/2023 | 11:44 | SM349C | URBAN | Asset failure | LV | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
06/07/2023 | 11:50 | MV62 | SHORT RURAL | Planned |  | 52.00 | 33.0 | 0.012073 | 0.0003658 | No
06/07/2023 | 12:08 | HH341H | URBAN | Asset failure | LV | 49.00 | 57.8 | 0.004368 | 0.0000755 | No
06/07/2023 | 12:26 | ME427E | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
06/07/2023 | 12:59 | NL111Q | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
06/07/2023 | 13:14 | ST11 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 65.33 | 77.0 | 0.035393 | 0.0004597 | No
06/07/2023 | 13:57 | AP365A | URBAN | Overloads |  | 1.00 | 335.0 | 0.000516 | 0.0000015 | No
06/07/2023 | 14:04 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 156.0 | 0.003293 | 0.0000211 | No
06/07/2023 | 14:23 | HH341C | URBAN | Vegetation | Grow-in - NSP responsibility | 3.67 | 301.0 | 0.001702 | 0.0000057 | No
06/07/2023 | 14:39 | EL15 | URBAN | Overloads |  | 1.00 | 158.0 | 0.000244 | 0.0000015 | No
06/07/2023 | 14:54 | HH386B | URBAN | Asset failure | LV | 15.33 | 82.0 | 0.001938 | 0.0000236 | No
06/07/2023 | 15:09 | WHY08 | URBAN | Asset failure | LV | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
06/07/2023 | 16:28 | NL451C | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
06/07/2023 | 17:05 | ME427E | URBAN | Asset failure | LV | 1.00 | 319.0 | 0.000492 | 0.0000015 | No
06/07/2023 | 19:00 | SG02 | SHORT RURAL | Overloads |  | 1.00 | 961.0 | 0.006761 | 0.0000070 | No
06/07/2023 | 19:22 | NL115C | URBAN | Asset failure | LV | 1.00 | 272.0 | 0.000419 | 0.0000015 | No
06/07/2023 | 19:25 | EL260C | URBAN | Unknown | Unknown | 3.67 | 282.0 | 0.001594 | 0.0000057 | No
06/07/2023 | 20:15 | MG25 | LONG RURAL | Unknown | Unknown | 26.00 | 121.0 | 0.022577 | 0.0001866 | No
06/07/2023 | 20:26 | HH386C | URBAN | Asset failure | LV | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
06/07/2023 | 20:43 | SM410A | URBAN | Asset failure | LV | 13.00 | 114.0 | 0.002285 | 0.0000200 | No
06/07/2023 | 21:29 | EL03 | URBAN | Overloads |  | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
06/07/2023 | 21:57 | PL04 | URBAN | Asset failure | LV | 1.00 | 706.0 | 0.001088 | 0.0000015 | No
06/07/2023 | 22:12 | SM411E | URBAN | Asset failure | LV | 64.00 | 71.0 | 0.007006 | 0.0000987 | No
07/07/2023 | 00:42 | HH145E | URBAN | Unknown | Unknown | 18.00 | 88.0 | 0.002442 | 0.0000278 | No
07/07/2023 | 01:00 | MG25 | LONG RURAL | Weather |  | 26.00 | 447.5 | 0.083489 | 0.0001866 | No
07/07/2023 | 04:38 | R05 | LONG RURAL | Asset failure | HV | 48.00 | 497.4 | 0.171328 | 0.0003445 | No
07/07/2023 | 06:47 | ST23 | SHORT RURAL | Animal | Animal impact | 8.00 | 167.0 | 0.009399 | 0.0000563 | No
07/07/2023 | 09:01 | VH19 | SHORT RURAL | Asset failure | LV | 1.00 | 191.0 | 0.001344 | 0.0000070 | No
07/07/2023 | 09:02 | KI31 | SHORT RURAL | Planned |  | 2.00 | 143.0 | 0.002012 | 0.0000141 | No
07/07/2023 | 09:07 | HH102C | URBAN | Overloads |  | 1.00 | 339.0 | 0.000523 | 0.0000015 | No
07/07/2023 | 09:23 | AP139B | URBAN | Overloads |  | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
07/07/2023 | 09:39 | HH496C | URBAN | Overloads |  | 3.67 | 477.0 | 0.002697 | 0.0000057 | No
07/07/2023 | 09:42 | MV61 | URBAN | Planned |  | 343.00 | 42.6 | 0.022553 | 0.0005288 | No
07/07/2023 | 10:03 | HH130B | URBAN | Asset failure | LV | 18.00 | 75.2 | 0.002086 | 0.0000278 | No
07/07/2023 | 10:09 | WK72 | SHORT RURAL | Planned |  | 96.00 | 123.0 | 0.083075 | 0.0006754 | No
07/07/2023 | 10:21 | NU03 | LONG RURAL | Other |  | 5.00 | 58.2 | 0.002088 | 0.0000359 | No
07/07/2023 | 10:32 | MB72 | LONG RURAL | Other |  | 1.00 | 36.0 | 0.000258 | 0.0000072 | No
07/07/2023 | 11:03 | EL10 | URBAN | Asset failure | LV | 10.00 | 101.8 | 0.001570 | 0.0000154 | No
07/07/2023 | 11:59 | MTB52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 156.0 | 0.002239 | 0.0000144 | No
07/07/2023 | 12:23 | HH177F | URBAN | Unknown | Unknown | 17.00 | 293.0 | 0.007679 | 0.0000262 | No
07/07/2023 | 13:05 | M04 | LONG RURAL | Weather |  | 107.00 | 39.0 | 0.029947 | 0.0007679 | No
07/07/2023 | 13:24 | SG09 | SHORT RURAL | Unknown | Unknown | 1.00 | 2,012.0 | 0.014155 | 0.0000070 | No
07/07/2023 | 14:14 | MV61 | URBAN | Asset failure | LV | 3.67 | 281.0 | 0.001589 | 0.0000057 | No
07/07/2023 | 14:56 | SM126D | URBAN | Overloads |  | 23.33 | 118.0 | 0.004245 | 0.0000360 | No
07/07/2023 | 16:07 | AP425C | URBAN | Asset failure | LV | 24.33 | 124.0 | 0.004652 | 0.0000375 | No
07/07/2023 | 16:13 | VH21 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 21.00 | 352.0 | 0.052006 | 0.0001477 | No
07/07/2023 | 16:40 | AP424C | URBAN | Overloads |  | 2.00 | 217.0 | 0.000669 | 0.0000031 | No
07/07/2023 | 17:19 | VH72 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 38.00 | 451.8 | 0.120785 | 0.0002673 | No
07/07/2023 | 18:10 | SG12 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 184.00 | 420.9 | 0.544864 | 0.0012945 | No
07/07/2023 | 19:01 | PL01 | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
07/07/2023 | 19:45 | HH522C | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
07/07/2023 | 19:50 | VH16 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 450.0 | 0.003166 | 0.0000070 | No
07/07/2023 | 19:53 | VH12 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 10.33 | 412.0 | 0.029952 | 0.0000727 | No
07/07/2023 | 20:14 | AP425A | URBAN | Overloads |  | 1.00 | 74.0 | 0.000114 | 0.0000015 | No
07/07/2023 | 20:18 | VH21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2,992.00 | 62.1 | 1.306723 | 0.0210502 | No
07/07/2023 | 20:38 | KA09 | LONG RURAL | Overloads |  | 1.00 | 88.0 | 0.000632 | 0.0000072 | No
07/07/2023 | 20:46 | KI55 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 74.00 | 1,644.0 | 0.873022 | 0.0005310 | No
07/07/2023 | 20:47 | PL23 | LONG RURAL | Asset failure | HV | 13.00 | 900.0 | 0.083963 | 0.0000933 | No
07/07/2023 | 21:33 | HH118D | URBAN | Vegetation | Grow-in - NSP responsibility | 54.67 | 105.0 | 0.008850 | 0.0000843 | No
07/07/2023 | 21:52 | HH496C | URBAN | Asset failure | LV | 1.00 | 307.0 | 0.000473 | 0.0000015 | No
07/07/2023 | 21:54 | KI53 | LONG RURAL | Asset failure | HV | 26.00 | 328.0 | 0.061200 | 0.0001866 | No
07/07/2023 | 21:54 | KI53 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 92.00 | 4,166.0 | 2.750486 | 0.0006602 | No
07/07/2023 | 22:18 | VH21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 38.00 | 164.0 | 0.043845 | 0.0002673 | No
07/07/2023 | 22:28 | GA26 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
07/07/2023 | 22:38 | VH71 | SHORT RURAL | Weather |  | 354.00 | 1,053.5 | 2.623774 | 0.0024906 | No
07/07/2023 | 22:48 | VH10 | SHORT RURAL | Third Party | Other | 86.00 | 263.0 | 0.159129 | 0.0006051 | No
07/07/2023 | 23:01 | MB22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 74.00 | 1,204.2 | 0.626918 | 0.0005206 | No
07/07/2023 | 23:14 | ME131D | URBAN | Overloads |  | 36.33 | 73.0 | 0.004089 | 0.0000560 | No
07/07/2023 | 23:21 | M21 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 262.00 | 161.0 | 0.302712 | 0.0018802 | No
08/07/2023 | 00:11 | HH118D | URBAN | Asset failure | LV | 19.00 | 186.0 | 0.005449 | 0.0000293 | No
08/07/2023 | 00:16 | MB31 | LONG RURAL | Weather |  | 229.00 | 181.0 | 0.297452 | 0.0016434 | No
08/07/2023 | 00:16 | MB31 | LONG RURAL | Weather |  | 2.67 | 1,287.0 | 0.024629 | 0.0000191 | No
08/07/2023 | 00:37 | ME200G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,811.00 | 36.9 | 0.103129 | 0.0027921 | No
08/07/2023 | 00:37 | HH121C | URBAN | Overloads |  | 16.67 | 220.0 | 0.005653 | 0.0000257 | No
08/07/2023 | 00:39 | HH496C | URBAN | Overloads |  | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
08/07/2023 | 01:01 | NU31 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 423.00 | 123.0 | 0.373377 | 0.0030356 | No
08/07/2023 | 01:30 | MTB54 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 487.00 | 44.9 | 0.156968 | 0.0034949 | No
08/07/2023 | 01:37 | GU43 | LONG RURAL | Unknown | Unknown | 94.00 | 152.0 | 0.102535 | 0.0006746 | No
08/07/2023 | 01:37 | GU43 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 141.00 | 254.7 | 0.257688 | 0.0010119 | No
08/07/2023 | 01:50 | HH121F | URBAN | Unknown | Unknown | 23.33 | 191.0 | 0.006871 | 0.0000360 | No
08/07/2023 | 01:51 | SM126B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 29.00 | 320.0 | 0.014307 | 0.0000447 | No
08/07/2023 | 02:40 | ST11 | SHORT RURAL | Weather |  | 300.00 | 266.1 | 0.561629 | 0.0021106 | No
08/07/2023 | 02:44 | HH121A | URBAN | Asset failure | LV | 25.00 | 443.0 | 0.017075 | 0.0000385 | No
08/07/2023 | 02:51 | MB71 | LONG RURAL | Other |  | 13.00 | 543.0 | 0.050658 | 0.0000933 | No
08/07/2023 | 03:37 | HH496G | URBAN | Unknown | Unknown | 9.33 | 152.0 | 0.002187 | 0.0000144 | No
08/07/2023 | 03:58 | HH102B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
08/07/2023 | 04:23 | AP139B | URBAN | Asset failure | LV | 18.33 | 209.0 | 0.005907 | 0.0000283 | No
08/07/2023 | 04:26 | HH121A | URBAN | Weather |  | 18.33 | 349.0 | 0.009865 | 0.0000283 | No
08/07/2023 | 04:43 | MI09 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 53.00 | 597.3 | 0.227195 | 0.0003803 | No
08/07/2023 | 04:44 | MTB71 | SHORT RURAL | Weather |  | 208.00 | 457.7 | 0.669807 | 0.0014634 | No
08/07/2023 | 05:11 | AP425A | URBAN | Asset failure | LV | 12.00 | 270.0 | 0.004995 | 0.0000185 | No
08/07/2023 | 05:43 | HH107A | URBAN | Weather |  | 1.00 | 1,251.0 | 0.001929 | 0.0000015 | No
08/07/2023 | 06:04 | MV42 | SHORT RURAL | Unknown | Unknown | 5.00 | 594.2 | 0.020902 | 0.0000352 | No
08/07/2023 | 06:22 | HH148A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 53.00 | 453.0 | 0.037016 | 0.0000817 | No
08/07/2023 | 06:43 | SD38100 | LONG RURAL | Unknown | Unknown | 2.67 | 851.0 | 0.016285 | 0.0000191 | No
08/07/2023 | 06:48 | MTB21 | SHORT RURAL | Unknown | Unknown | 37.00 | 166.0 | 0.043212 | 0.0002603 | No
08/07/2023 | 06:50 | MG21 | LONG RURAL | Unknown | Unknown | 67.00 | 1,760.0 | 0.846233 | 0.0004808 | No
08/07/2023 | 06:56 | AP214B | URBAN | Unknown | Unknown | 76.00 | 472.0 | 0.055306 | 0.0001172 | No
08/07/2023 | 06:57 | SM402B | URBAN | Asset failure | LV | 2.00 | 136.0 | 0.000419 | 0.0000031 | No
08/07/2023 | 07:20 | MV54 | SHORT RURAL | Unknown | Unknown | 2.00 | 1,052.0 | 0.014803 | 0.0000141 | No
08/07/2023 | 07:25 | HH118A | URBAN | Asset failure | LV | 9.00 | 237.0 | 0.003289 | 0.0000139 | No
08/07/2023 | 07:27 | HH522C | URBAN | Asset failure | LV | 1.00 | 962.0 | 0.001483 | 0.0000015 | No
08/07/2023 | 07:30 | BM55 | SHORT RURAL | Asset failure | HV | 52.00 | 224.0 | 0.081949 | 0.0003658 | No
08/07/2023 | 07:49 | CD04 | SHORT RURAL | Asset failure | LV | 1.00 | 345.0 | 0.002427 | 0.0000070 | No
08/07/2023 | 07:52 | PP09 | LONG RURAL | Asset failure | LV | 6.67 | 115.0 | 0.005502 | 0.0000478 | No
08/07/2023 | 07:55 | ME200E | URBAN | Vegetation | Grow-in - NSP responsibility | 21.00 | 185.0 | 0.005990 | 0.0000324 | No
08/07/2023 | 08:03 | MG02 | LONG RURAL | Asset failure | LV | 1.00 | 1,812.0 | 0.013004 | 0.0000072 | No
08/07/2023 | 08:23 | MI14 | LONG RURAL | Weather |  | 749.00 | 129.9 | 0.698386 | 0.0053751 | No
08/07/2023 | 08:31 | ST35 | LONG RURAL | Weather |  | 6.00 | 632.0 | 0.027213 | 0.0000431 | No
08/07/2023 | 08:31 | ST35 | LONG RURAL | Weather |  | 1.00 | 1,909.0 | 0.013700 | 0.0000072 | No
08/07/2023 | 08:35 | LC01 | LONG RURAL | Asset failure | HV | 125.00 | 8.0 | 0.007176 | 0.0008970 | No
08/07/2023 | 08:35 | LC01 | SHORT RURAL | Asset failure | HV | 246.00 | 8.0 | 0.013846 | 0.0017307 | No
08/07/2023 | 08:39 | SM172F | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 298.0 | 0.000459 | 0.0000015 | No
08/07/2023 | 09:09 | HH386F | URBAN | Asset failure | LV | 15.33 | 190.0 | 0.004492 | 0.0000236 | No
08/07/2023 | 09:16 | HH118D | URBAN | Asset failure | LV | 166.00 | 393.0 | 0.100590 | 0.0002559 | No
08/07/2023 | 09:34 | ME427C | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 1.00 | 47.0 | 0.000072 | 0.0000015 | No
08/07/2023 | 09:35 | HH341C | URBAN | Asset failure | LV | 103.00 | 195.0 | 0.030966 | 0.0001588 | No
08/07/2023 | 09:38 | ME131C | URBAN | Asset failure | LV | 2.00 | 645.0 | 0.001989 | 0.0000031 | No
08/07/2023 | 09:43 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 1,823.0 | 0.013082 | 0.0000072 | No
08/07/2023 | 09:53 | HH121H | URBAN | Asset failure | LV | 1.00 | 834.0 | 0.001286 | 0.0000015 | No
08/07/2023 | 09:53 | AP226C | URBAN | Asset failure | LV | 1.00 | 297.0 | 0.000458 | 0.0000015 | No
08/07/2023 | 10:21 | NU20 | LONG RURAL | Unknown | Unknown | 3.00 | 624.0 | 0.013434 | 0.0000215 | No
08/07/2023 | 10:43 | AP424D | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
08/07/2023 | 10:47 | AP149E | URBAN | Asset failure | LV | 5.00 | 64.0 | 0.000493 | 0.0000077 | No
08/07/2023 | 10:47 | HH177B | URBAN | Asset failure | LV | 2.00 | 994.0 | 0.003065 | 0.0000031 | No
08/07/2023 | 11:28 | MG28 | LONG RURAL | Unknown | Unknown | 149.00 | 4.0 | 0.004277 | 0.0010693 | No
08/07/2023 | 11:28 | MG29 | LONG RURAL | Unknown | Unknown | 56.00 | 1,690.5 | 0.679369 | 0.0004019 | No
08/07/2023 | 11:47 | M61 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 7.00 | 564.0 | 0.028332 | 0.0000502 | No
08/07/2023 | 13:03 | M01 | LONG RURAL | Third Party | Other | 3.00 | 671.0 | 0.014446 | 0.0000215 | No
08/07/2023 | 13:09 | MG52 | URBAN | Vegetation | Grow-in - NSP responsibility | 91.00 | 197.0 | 0.027639 | 0.0001403 | No
08/07/2023 | 13:16 | SA16 | URBAN | Asset failure | LV | 1.00 | 773.0 | 0.001192 | 0.0000015 | No
08/07/2023 | 13:27 | NU15 | LONG RURAL | Asset failure | HV | 519.00 | 150.6 | 0.560801 | 0.0037245 | No
08/07/2023 | 13:43 | EL20 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 40.67 | 208.0 | 0.013041 | 0.0000627 | No
08/07/2023 | 13:51 | MG11 | SHORT RURAL | Unknown | Unknown | 1,464.00 | 353.1 | 3.637025 | 0.0103000 | No
08/07/2023 | 13:51 | HH145A | URBAN | Asset failure | LV | 1.00 | 501.0 | 0.000772 | 0.0000015 | No
08/07/2023 | 13:56 | MG41 | URBAN | Other |  | 1.00 | 1,545.0 | 0.002382 | 0.0000015 | No
08/07/2023 | 14:07 | MG52 | URBAN | Weather |  | 90.00 | 394.0 | 0.054671 | 0.0001388 | No
08/07/2023 | 14:18 | EL10 | URBAN | Asset failure | LV | 12.00 | 574.0 | 0.010620 | 0.0000185 | No
08/07/2023 | 14:48 | SM350G | URBAN | Asset failure | LV | 12.00 | 275.0 | 0.005088 | 0.0000185 | No
08/07/2023 | 15:05 | NL210A | URBAN | Overloads |  | 1.00 | 262.0 | 0.000404 | 0.0000015 | No
08/07/2023 | 15:06 | AP226D | URBAN | Asset failure | LV | 22.00 | 660.0 | 0.022386 | 0.0000339 | No
08/07/2023 | 15:08 | SM350G | URBAN | Asset failure | LV | 13.00 | 196.0 | 0.003928 | 0.0000200 | No
08/07/2023 | 15:16 | SM350A | URBAN | Unknown | Unknown | 1.00 | 233.0 | 0.000359 | 0.0000015 | No
08/07/2023 | 15:24 | SD49100 | LONG RURAL | Asset failure | Subtransmission | 3,065.00 | 136.8 | 3.009279 | 0.0219955 | No
08/07/2023 | 16:47 | HH496C | URBAN | Asset failure | LV | 3.33 | 217.0 | 0.001115 | 0.0000051 | No
08/07/2023 | 17:38 | HH102D | URBAN | Asset failure | LV | 108.00 | 116.0 | 0.019315 | 0.0001665 | No
08/07/2023 | 18:15 | SM216B | URBAN | Asset failure | LV | 93.00 | 188.0 | 0.026956 | 0.0001434 | No
08/07/2023 | 20:01 | AP149F | URBAN | Unknown | Unknown | 36.00 | 186.0 | 0.010324 | 0.0000555 | No
08/07/2023 | 20:23 | EL12 | URBAN | Asset failure | HV | 6.00 | 295.5 | 0.002734 | 0.0000093 | No
08/07/2023 | 20:26 | SA16 | URBAN | Asset failure | LV | 1.00 | 291.0 | 0.000449 | 0.0000015 | No
08/07/2023 | 20:56 | MG52 | SHORT RURAL | Asset failure | HV | 1.00 | 1,124.0 | 0.007908 | 0.0000070 | No
08/07/2023 | 21:37 | HH496C | URBAN | Asset failure | LV | 1.00 | 1,442.0 | 0.002223 | 0.0000015 | No
08/07/2023 | 23:15 | MI20 | LONG RURAL | Asset failure | HV | 321.00 | 137.4 | 0.316483 | 0.0023036 | No
09/07/2023 | 00:03 | ST35 | LONG RURAL | Asset failure | LV | 6.00 | 102.7 | 0.004421 | 0.0000431 | No
09/07/2023 | 00:29 | SD40400 | LONG RURAL | Unknown | Unknown | 168.00 | 55.8 | 0.067278 | 0.0012056 | No
09/07/2023 | 01:10 | AP355H | URBAN | Asset failure | LV | 119.00 | 102.2 | 0.018755 | 0.0001835 | No
09/07/2023 | 06:14 | AP149B | URBAN | Asset failure | LV | 25.67 | 389.0 | 0.015393 | 0.0000396 | No
09/07/2023 | 07:15 | HH522A | URBAN | Asset failure | LV | 1.00 | 449.0 | 0.000692 | 0.0000015 | No
09/07/2023 | 07:59 | VH33 | SHORT RURAL | Asset failure | LV | 1.00 | 383.0 | 0.002695 | 0.0000070 | No
09/07/2023 | 08:22 | ME347C | URBAN | Asset failure | LV | 1.00 | 179.0 | 0.000276 | 0.0000015 | No
09/07/2023 | 08:56 | AP125D | URBAN | Planned |  | 46.00 | 404.8 | 0.028709 | 0.0000709 | No
09/07/2023 | 09:11 | MV13 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 15.00 | 801.1 | 0.084538 | 0.0001055 | No
09/07/2023 | 09:28 | R08 | LONG RURAL | Planned |  | 29.00 | 357.0 | 0.074297 | 0.0002081 | No
09/07/2023 | 09:52 | CBD103B | URBAN | Asset failure | LV | 1.00 | 316.0 | 0.000487 | 0.0000015 | No
09/07/2023 | 12:18 | KI12 | LONG RURAL | Asset failure | LV | 2.00 | 1,438.0 | 0.020639 | 0.0000144 | No
09/07/2023 | 12:23 | AP125D | URBAN | Overloads |  | 1.00 | 477.0 | 0.000735 | 0.0000015 | No
09/07/2023 | 14:12 | HH341C | URBAN | Asset failure | LV | 15.00 | 114.7 | 0.002652 | 0.0000231 | No
09/07/2023 | 15:50 | AP227A | URBAN | Overloads |  | 1.00 | 452.0 | 0.000697 | 0.0000015 | No
09/07/2023 | 16:31 | SA33 | URBAN | Third Party | Other | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
09/07/2023 | 17:02 | VH10 | SHORT RURAL | Asset failure | LV | 8.00 | 326.0 | 0.018349 | 0.0000563 | No
09/07/2023 | 17:21 | VH10 | SHORT RURAL | Asset failure | LV | 11.00 | 308.0 | 0.023836 | 0.0000774 | No
09/07/2023 | 17:24 | SA33 | URBAN | Planned |  | 2,578.00 | 3.0 | 0.011924 | 0.0039746 | No
09/07/2023 | 17:34 | HH428A | URBAN | Unknown | Unknown | 12.00 | 275.0 | 0.005088 | 0.0000185 | No
09/07/2023 | 18:22 | G17 | LONG RURAL | Overloads |  | 1.00 | 239.0 | 0.001715 | 0.0000072 | No
09/07/2023 | 18:56 | HH341E | URBAN | Asset failure | LV | 1.00 | 357.0 | 0.000550 | 0.0000015 | No
09/07/2023 | 19:12 | GU42 | LONG RURAL | Overloads |  | 1.00 | 245.0 | 0.001758 | 0.0000072 | No
09/07/2023 | 19:22 | AP424C | URBAN | Overloads |  | 1.00 | 403.0 | 0.000621 | 0.0000015 | No
09/07/2023 | 19:49 | MTB51 | LONG RURAL | Unknown | Unknown | 2.33 | 173.0 | 0.002897 | 0.0000167 | No
09/07/2023 | 20:49 | HH121C | URBAN | Asset failure | LV | 12.00 | 51.0 | 0.000944 | 0.0000185 | No
09/07/2023 | 21:28 | MG21 | LONG RURAL | Unknown | Unknown | 67.00 | 477.3 | 0.229513 | 0.0004808 | No
09/07/2023 | 21:48 | HH102B | URBAN | Other |  | 19.67 | 111.0 | 0.003366 | 0.0000303 | No
09/07/2023 | 21:49 | HH102B | URBAN | Other |  | 11.33 | 109.0 | 0.001905 | 0.0000175 | No
10/07/2023 | 04:22 | G32 | LONG RURAL | Unknown | Unknown | 101.00 | 344.8 | 0.249944 | 0.0007248 | No
10/07/2023 | 05:26 | EL260B | URBAN | Asset failure | HV | 621.00 | 60.5 | 0.057890 | 0.0009574 | No
10/07/2023 | 06:02 | SA14 | URBAN | Asset failure | HV | 1,055.67 | 86.3 | 0.140379 | 0.0016276 | No
10/07/2023 | 07:32 | CBD367U | CBD | Third Party | Unauthorised access | 9.00 | 320.0 | 0.416095 | 0.0013003 | No
10/07/2023 | 08:19 | MTB13 | SHORT RURAL | Asset failure | LV | 1.00 | 153.0 | 0.001076 | 0.0000070 | No
10/07/2023 | 08:35 | SA744D | URBAN | Asset failure | LV | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
10/07/2023 | 08:49 | SG14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 422.0 | 0.002969 | 0.0000070 | No
10/07/2023 | 08:54 | EL10 | URBAN | Unknown | Unknown | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
10/07/2023 | 09:00 | AP351C | URBAN | Asset failure | LV | 27.67 | 207.0 | 0.008830 | 0.0000427 | No
10/07/2023 | 09:09 | NU15 | LONG RURAL | Asset failure | HV | 18.33 | 56.0 | 0.007368 | 0.0001316 | No
10/07/2023 | 09:22 | CL28 | LONG RURAL | Planned |  | 11.00 | 100.0 | 0.007894 | 0.0000789 | No
10/07/2023 | 09:23 | HH409F | URBAN | Asset failure | LV | 1.00 | 460.0 | 0.000709 | 0.0000015 | No
10/07/2023 | 09:36 | NU20 | LONG RURAL | Asset failure | LV | 1.00 | 192.0 | 0.001378 | 0.0000072 | No
10/07/2023 | 09:56 | CM05 | LONG RURAL | Planned |  | 91.00 | 17.0 | 0.011102 | 0.0006530 | No
10/07/2023 | 10:28 | SA744D | URBAN | Asset failure | LV | 1.00 | 399.0 | 0.000615 | 0.0000015 | No
10/07/2023 | 10:33 | SD49200 | LONG RURAL | Weather |  | 2.00 | 32.0 | 0.000459 | 0.0000144 | No
10/07/2023 | 11:11 | EL07 | URBAN | Asset failure | LV | 1.00 | 923.0 | 0.001423 | 0.0000015 | No
10/07/2023 | 11:16 | SA34 | URBAN | Unknown | Unknown | 1.00 | 403.0 | 0.000621 | 0.0000015 | No
10/07/2023 | 11:27 | KI12 | LONG RURAL | Asset failure | HV | 1.00 | 15.0 | 0.000108 | 0.0000072 | No
10/07/2023 | 11:47 | EL02 | URBAN | Unknown | Unknown | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
10/07/2023 | 12:05 | GU42 | LONG RURAL | Overloads |  | 1.00 | 365.0 | 0.002619 | 0.0000072 | No
10/07/2023 | 12:15 | GA02 | SHORT RURAL | Asset failure | LV | 5.00 | 475.0 | 0.016709 | 0.0000352 | No
10/07/2023 | 12:26 | G40 | LONG RURAL | Asset failure | LV | 28.00 | 128.0 | 0.025720 | 0.0002009 | No
10/07/2023 | 12:29 | MG22 | LONG RURAL | Unknown | Unknown | 137.00 | 24.2 | 0.023754 | 0.0009832 | No
10/07/2023 | 13:15 | HH145A | URBAN | Asset failure | LV | 1.00 | 454.0 | 0.000700 | 0.0000015 | No
10/07/2023 | 13:23 | AP226D | URBAN | Third Party | Vehicle impact | 41.00 | 538.3 | 0.034030 | 0.0000632 | No
10/07/2023 | 13:45 | MG44 | URBAN | Overloads |  | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
10/07/2023 | 14:03 | GA02 | SHORT RURAL | Unknown | Unknown | 48.67 | 530.2 | 0.181525 | 0.0003424 | No
10/07/2023 | 14:24 | HH102D | URBAN | Asset failure | LV | 1.00 | 314.0 | 0.000484 | 0.0000015 | No
10/07/2023 | 15:04 | CV15 | LONG RURAL | Third Party | Vehicle impact | 61.00 | 178.2 | 0.078007 | 0.0004378 | No
10/07/2023 | 15:47 | WK31 | SHORT RURAL | Other |  | 1.00 | 30.0 | 0.000211 | 0.0000070 | No
10/07/2023 | 17:08 | SM374E | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 322.0 | 0.000496 | 0.0000015 | No
10/07/2023 | 17:09 | HH386C | URBAN | Asset failure | LV | 1.00 | 274.0 | 0.000422 | 0.0000015 | No
10/07/2023 | 17:12 | CL01 | LONG RURAL | Unknown | Unknown | 93.67 | 135.0 | 0.090745 | 0.0006722 | No
10/07/2023 | 17:45 | MG43 | URBAN | Asset failure | LV | 1.00 | 1,203.0 | 0.001855 | 0.0000015 | No
10/07/2023 | 18:10 | SA31 | URBAN | Asset failure | LV | 2.67 | 424.0 | 0.001743 | 0.0000041 | No
10/07/2023 | 18:28 | HH145B | URBAN | Asset failure | LV | 1.00 | 361.0 | 0.000557 | 0.0000015 | No
10/07/2023 | 18:50 | AP529E | URBAN | Overloads |  | 1.00 | 216.0 | 0.000333 | 0.0000015 | No
10/07/2023 | 18:51 | HH130B | URBAN | Asset failure | LV | 1.00 | 360.0 | 0.000555 | 0.0000015 | No
10/07/2023 | 18:52 | HH121F | URBAN | Asset failure | LV | 1.00 | 400.0 | 0.000617 | 0.0000015 | No
10/07/2023 | 19:47 | AP365A | URBAN | Overloads |  | 29.67 | 155.0 | 0.007089 | 0.0000457 | No
10/07/2023 | 19:49 | SM411C | URBAN | Asset failure | LV | 8.67 | 90.0 | 0.001203 | 0.0000134 | No
10/07/2023 | 20:45 | SM137D | URBAN | Asset failure | LV | 6.00 | 29.0 | 0.000268 | 0.0000093 | No
10/07/2023 | 21:23 | SM137D | URBAN | Asset failure | LV | 9.00 | 825.0 | 0.011448 | 0.0000139 | No
10/07/2023 | 22:37 | MG21 | LONG RURAL | Weather |  | 67.00 | 646.5 | 0.310850 | 0.0004808 | No
11/07/2023 | 06:17 | SM137B | URBAN | Asset failure | LV | 2.00 | 345.0 | 0.001064 | 0.0000031 | No
11/07/2023 | 06:49 | AP149F | URBAN | Unknown | Unknown | 8.00 | 123.0 | 0.001517 | 0.0000123 | No
11/07/2023 | 07:25 | CN25 | LONG RURAL | Asset failure | HV | 2.00 | 255.0 | 0.003660 | 0.0000144 | No
11/07/2023 | 08:22 | CL04 | LONG RURAL | Planned |  | 27.00 | 349.0 | 0.067623 | 0.0001938 | No
11/07/2023 | 08:29 | KA32 | LONG RURAL | Planned |  | 38.00 | 11.0 | 0.003000 | 0.0002727 | No
11/07/2023 | 08:48 | SM349H | URBAN | Planned |  | 1.00 | 14,778.0 | 0.022784 | 0.0000015 | No
11/07/2023 | 09:00 | NL115B | URBAN | Asset failure | LV | 76.00 | 253.0 | 0.029645 | 0.0001172 | No
11/07/2023 | 09:11 | SA38 | URBAN | Planned |  | 2.00 | 254.0 | 0.000783 | 0.0000031 | No
11/07/2023 | 09:15 | MT01 | LONG RURAL | Planned |  | 1.00 | 153.0 | 0.001098 | 0.0000072 | No
11/07/2023 | 09:31 | ST11 | SHORT RURAL | Planned |  | 136.00 | 1.0 | 0.000957 | 0.0009568 | No
11/07/2023 | 09:37 | GU32 | LONG RURAL | Planned |  | 1.00 | 303.0 | 0.002174 | 0.0000072 | No
11/07/2023 | 09:55 | MV34 | SHORT RURAL | Planned |  | 234.00 | 268.0 | 0.441210 | 0.0016463 | No
11/07/2023 | 10:10 | MG02 | LONG RURAL | Unknown | Unknown | 17.00 | 128.0 | 0.015616 | 0.0001220 | No
11/07/2023 | 10:13 | SD36101 | SHORT RURAL | Planned |  | 1.00 | 218.0 | 0.001534 | 0.0000070 | No
11/07/2023 | 10:22 | SA31 | URBAN | Planned |  | 1,404.00 | 62.6 | 0.135409 | 0.0021646 | No
11/07/2023 | 10:49 | SM350A | URBAN | Planned |  | 42.00 | 2,974.0 | 0.192577 | 0.0000648 | No
11/07/2023 | 10:59 | CN25 | LONG RURAL | Asset failure | HV | 94.00 | 4.0 | 0.002698 | 0.0006746 | No
11/07/2023 | 12:01 | HH121H | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
11/07/2023 | 14:09 | ST12 | SHORT RURAL | Planned |  | 136.00 | 7.0 | 0.006698 | 0.0009568 | No
11/07/2023 | 14:54 | M81 | LONG RURAL | Asset failure | LV | 1.00 | 1,152.0 | 0.008267 | 0.0000072 | No
11/07/2023 | 15:25 | MI05 | LONG RURAL | Asset failure | LV | 1.00 | 168.0 | 0.001206 | 0.0000072 | No
11/07/2023 | 17:05 | ME116C | URBAN | Asset failure | LV | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
11/07/2023 | 17:10 | SA42 | URBAN | Asset failure | LV | 12.00 | 253.0 | 0.004681 | 0.0000185 | No
11/07/2023 | 17:26 | NL234E | URBAN | Asset failure | LV | 2.00 | 203.0 | 0.000626 | 0.0000031 | No
11/07/2023 | 17:37 | AP139C | URBAN | Unknown | Unknown | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
11/07/2023 | 17:38 | WHY01 | SHORT RURAL | Asset failure | LV | 1.00 | 61.0 | 0.000429 | 0.0000070 | No
11/07/2023 | 18:26 | CN51 | LONG RURAL | Third Party | Vehicle impact | 207.00 | 182.0 | 0.270361 | 0.0014855 | No
11/07/2023 | 18:32 | VH21 | SHORT RURAL | Asset failure | LV | 56.00 | 77.0 | 0.030337 | 0.0003940 | No
11/07/2023 | 19:52 | NL234C | URBAN | Asset failure | LV | 1.00 | 89.0 | 0.000137 | 0.0000015 | No
11/07/2023 | 19:56 | NL115C | URBAN | Asset failure | LV | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
11/07/2023 | 20:46 | HH496A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 97.00 | 341.1 | 0.051004 | 0.0001496 | No
11/07/2023 | 21:08 | SM179A | URBAN | Planned |  | 320.00 | 420.3 | 0.207378 | 0.0004934 | No
11/07/2023 | 22:44 | SM349C | URBAN | Other |  | 270.00 | 135.1 | 0.056228 | 0.0004163 | No
11/07/2023 | 23:30 | SA13 | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
12/07/2023 | 06:17 | AP226D | URBAN | Asset failure | LV | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
12/07/2023 | 06:23 | SD52300 | LONG RURAL | Unknown | Unknown | 109.00 | 173.0 | 0.135324 | 0.0007822 | No
12/07/2023 | 06:23 | SD52300 | SHORT RURAL | Unknown | Unknown | 614.00 | 173.0 | 0.747324 | 0.0043198 | No
12/07/2023 | 06:23 | SD52300 | LONG RURAL | Network business | Switching and protection error | 2,477.00 | 6.0 | 0.106655 | 0.0177758 | No
12/07/2023 | 06:23 | SD52300 | SHORT RURAL | Network business | Switching and protection error | 1.00 | 6.0 | 0.000042 | 0.0000070 | No
12/07/2023 | 08:14 | EL260A | URBAN | Planned |  | 27.00 | 281.0 | 0.011697 | 0.0000416 | No
12/07/2023 | 08:16 | MB63 | LONG RURAL | Planned |  | 2.00 | 401.0 | 0.005755 | 0.0000144 | No
12/07/2023 | 08:21 | BS0189 | SHORT RURAL | Planned |  | 1.00 | 205.0 | 0.001442 | 0.0000070 | No
12/07/2023 | 08:27 | CL04 | LONG RURAL | Planned |  | 27.00 | 433.2 | 0.083934 | 0.0001938 | No
12/07/2023 | 08:31 | SM216E | URBAN | Asset failure | LV | 1.00 | 95.0 | 0.000146 | 0.0000015 | No
12/07/2023 | 09:11 | SD37200 | LONG RURAL | Planned |  | 1.00 | 298.0 | 0.002139 | 0.0000072 | No
12/07/2023 | 09:29 | YK07 | LONG RURAL | Planned |  | 74.00 | 377.0 | 0.200205 | 0.0005310 | No
12/07/2023 | 09:30 | SB23 | LONG RURAL | Planned |  | 8.00 | 351.0 | 0.020151 | 0.0000574 | No
12/07/2023 | 09:57 | NL234E | URBAN | Asset failure | LV | 1.00 | 687.0 | 0.001059 | 0.0000015 | No
12/07/2023 | 10:29 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 768.00 | 161.3 | 0.871500 | 0.0054033 | No
12/07/2023 | 11:37 | HH429A | URBAN | Asset failure | LV | 20.00 | 340.0 | 0.010484 | 0.0000308 | No
12/07/2023 | 11:49 | ST34 | LONG RURAL | Planned |  | 8.00 | 39.0 | 0.002239 | 0.0000574 | No
12/07/2023 | 11:57 | MG03 | SHORT RURAL | Asset failure | LV | 2.00 | 53.0 | 0.000746 | 0.0000141 | No
12/07/2023 | 12:26 | SD40101 | LONG RURAL | Asset failure | Subtransmission | 2,291.00 | 124.9 | 2.053392 | 0.0164410 | No
12/07/2023 | 12:47 | NL115F | URBAN | Asset failure | LV | 39.00 | 302.0 | 0.018159 | 0.0000601 | No
12/07/2023 | 12:55 | NA28 | LONG RURAL | Asset failure | HV | 1.00 | 411.0 | 0.002949 | 0.0000072 | No
12/07/2023 | 13:27 | MI21 | LONG RURAL | Asset failure | LV | 1.00 | 167.0 | 0.001198 | 0.0000072 | No
12/07/2023 | 13:57 | HH107C | URBAN | Planned |  | 164.00 | 33.0 | 0.008344 | 0.0002528 | No
12/07/2023 | 15:13 | PP03 | URBAN | Asset failure | LV | 49.00 | 87.0 | 0.006576 | 0.0000755 | No
12/07/2023 | 15:35 | SD59100 | LONG RURAL | Planned |  | 349.00 | 21.0 | 0.052595 | 0.0025045 | No
12/07/2023 | 15:42 | SM179D | URBAN | Asset failure | LV | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
12/07/2023 | 16:28 | SA711C | URBAN | Asset failure | LV | 54.00 | 57.1 | 0.004752 | 0.0000833 | No
12/07/2023 | 16:34 | HH177G | URBAN | Asset failure | LV | 15.00 | 530.0 | 0.012257 | 0.0000231 | No
12/07/2023 | 16:50 | HH409D | URBAN | Asset failure | LV | 1.00 | 516.0 | 0.000796 | 0.0000015 | No
12/07/2023 | 17:09 | YK07 | LONG RURAL | Asset failure | LV | 17.00 | 76.0 | 0.009272 | 0.0001220 | No
12/07/2023 | 17:10 | HH428B | URBAN | Asset failure | LV | 61.00 | 287.0 | 0.026991 | 0.0000940 | No
12/07/2023 | 17:12 | GA08 | LONG RURAL | Asset failure | LV | 1.00 | 102.0 | 0.000732 | 0.0000072 | No
12/07/2023 | 17:58 | HH428B | URBAN | Asset failure | LV | 75.00 | 239.0 | 0.027636 | 0.0001156 | No
12/07/2023 | 18:34 | HH177G | URBAN | Asset failure | HV | 2,321.00 | 168.3 | 0.602180 | 0.0035784 | No
12/07/2023 | 20:26 | MB71 | LONG RURAL | Asset failure | LV | 1.00 | 248.0 | 0.001780 | 0.0000072 | No
12/07/2023 | 22:28 | AP227C | URBAN | Planned |  | 1,192.00 | 316.7 | 0.582015 | 0.0018378 | No
12/07/2023 | 23:08 | MB71 | LONG RURAL | Asset failure | LV | 2.00 | 89.0 | 0.001277 | 0.0000144 | No
13/07/2023 | 02:44 | HH177G | URBAN | Asset failure | LV | 1.00 | 92.0 | 0.000142 | 0.0000015 | No
13/07/2023 | 04:50 | SA744D | URBAN | Asset failure | LV | 1.00 | 281.0 | 0.000433 | 0.0000015 | No
13/07/2023 | 07:51 | NL234E | URBAN | Unknown | Unknown | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
13/07/2023 | 08:27 | BM12 | SHORT RURAL | Planned |  | 93.00 | 264.6 | 0.173157 | 0.0006543 | No
13/07/2023 | 08:49 | KA01 | SHORT RURAL | Planned |  | 1.00 | 206.0 | 0.001449 | 0.0000070 | No
13/07/2023 | 08:54 | HH496D | URBAN | Planned |  | 159.00 | 221.1 | 0.054208 | 0.0002451 | No
13/07/2023 | 08:59 | SA32 | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
13/07/2023 | 09:01 | PL04 | URBAN | Planned |  | 6.00 | 263.0 | 0.002433 | 0.0000093 | No
13/07/2023 | 09:09 | MI18 | LONG RURAL | Planned |  | 1.00 | 90.0 | 0.000646 | 0.0000072 | No
13/07/2023 | 09:18 | AP424F | URBAN | Planned |  | 173.00 | 184.3 | 0.049148 | 0.0002667 | No
13/07/2023 | 09:22 | SD34102 | LONG RURAL | Planned |  | 247.00 | 299.4 | 0.530725 | 0.0017726 | No
13/07/2023 | 09:33 | MV42 | SHORT RURAL | Planned |  | 344.00 | 298.7 | 0.722967 | 0.0024202 | No
13/07/2023 | 09:39 | CL13 | LONG RURAL | Planned |  | 34.00 | 237.0 | 0.057827 | 0.0002440 | No
13/07/2023 | 09:41 | CV753A | LONG RURAL | Planned |  | 484.00 | 198.6 | 0.689825 | 0.0034733 | No
13/07/2023 | 09:47 | MV64 | SHORT RURAL | Planned |  | 132.00 | 315.0 | 0.292536 | 0.0009287 | No
13/07/2023 | 10:06 | SM216C | URBAN | Asset failure | LV | 33.00 | 96.9 | 0.004931 | 0.0000509 | No
13/07/2023 | 10:14 | MTB32 | LONG RURAL | Planned |  | 233.00 | 259.8 | 0.434484 | 0.0016721 | No
13/07/2023 | 10:20 | AP425D | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
13/07/2023 | 10:33 | PA02 | URBAN | Asset failure | LV | 1.00 | 271.0 | 0.000418 | 0.0000015 | No
13/07/2023 | 10:57 | HH118B | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
13/07/2023 | 11:09 | HH177F | URBAN | Asset failure | LV | 8.00 | 114.0 | 0.001406 | 0.0000123 | No
13/07/2023 | 11:21 | ME427E | URBAN | Asset failure | LV | 59.00 | 75.0 | 0.006822 | 0.0000910 | No
13/07/2023 | 11:40 | NU21 | LONG RURAL | Planned |  | 136.00 | 22.0 | 0.021472 | 0.0009760 | No
13/07/2023 | 11:47 | HH177B | URBAN | Overloads |  | 1.00 | 373.0 | 0.000575 | 0.0000015 | No
13/07/2023 | 12:03 | CV16 | LONG RURAL | Asset failure | HV | 55.00 | 572.4 | 0.225911 | 0.0003947 | No
13/07/2023 | 12:14 | NL111Q | URBAN | Overloads |  | 1.00 | 1,703.0 | 0.002626 | 0.0000015 | No
13/07/2023 | 12:45 | MB12 | SHORT RURAL | Asset failure | LV | 2.00 | 561.0 | 0.007894 | 0.0000141 | No
13/07/2023 | 12:55 | NU33 | LONG RURAL | Asset failure | HV | 9.33 | 68.0 | 0.004555 | 0.0000670 | No
13/07/2023 | 13:14 | MB01 | LONG RURAL | Planned |  | 2.00 | 1.0 | 0.000014 | 0.0000144 | No
13/07/2023 | 13:45 | MB71 | LONG RURAL | Asset failure | LV | 1.00 | 113.0 | 0.000811 | 0.0000072 | No
13/07/2023 | 14:27 | ME131C | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
13/07/2023 | 15:45 | MV32 | SHORT RURAL | Unknown | Unknown | 2.00 | 193.0 | 0.002716 | 0.0000141 | No
13/07/2023 | 16:01 | ST21 | SHORT RURAL | Unknown | Unknown | 1.00 | 334.0 | 0.002350 | 0.0000070 | No
13/07/2023 | 16:15 | EL01L | URBAN | Asset failure | LV | 1.00 | 291.0 | 0.000449 | 0.0000015 | No
13/07/2023 | 16:36 | HH177B | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
13/07/2023 | 16:39 | MB72 | LONG RURAL | Planned |  | 276.00 | 6.0 | 0.011884 | 0.0019807 | No
13/07/2023 | 16:39 | MB72 | LONG RURAL | Unknown | Unknown | 52.00 | 21.0 | 0.007837 | 0.0003732 | No
13/07/2023 | 17:43 | VH22 | SHORT RURAL | Overloads |  | 30.00 | 192.0 | 0.040524 | 0.0002111 | No
13/07/2023 | 18:09 | KA05 | LONG RURAL | Asset failure | LV | 1.00 | 160.0 | 0.001148 | 0.0000072 | No
13/07/2023 | 18:15 | HH121H | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
13/07/2023 | 18:55 | EL01R | URBAN | Network business | Switching and protection error | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
13/07/2023 | 19:43 | G10 | LONG RURAL | Asset failure | LV | 1.00 | 899.0 | 0.006452 | 0.0000072 | No
13/07/2023 | 19:55 | AP149F | URBAN | Asset failure | LV | 8.00 | 207.0 | 0.002553 | 0.0000123 | No
13/07/2023 | 21:01 | HH409C | URBAN | Asset failure | LV | 46.00 | 124.0 | 0.008794 | 0.0000709 | No
13/07/2023 | 21:05 | CBD27D | CBD | Overloads |  | 1.00 | 247.0 | 0.035686 | 0.0001445 | No
13/07/2023 | 21:14 | MV61 | URBAN | Asset failure | LV | 7.00 | 659.0 | 0.007112 | 0.0000108 | No
13/07/2023 | 21:40 | HH177F | URBAN | Asset failure | LV | 1.00 | 523.0 | 0.000806 | 0.0000015 | No
13/07/2023 | 23:38 | HH428F | URBAN | Asset failure | LV | 94.00 | 65.0 | 0.009420 | 0.0001449 | No
14/07/2023 | 02:27 | GA02 | SHORT RURAL | Asset failure | LV | 1.00 | 795.0 | 0.005593 | 0.0000070 | No
14/07/2023 | 03:03 | HH177F | URBAN | Asset failure | HV | 812.00 | 120.0 | 0.150228 | 0.0012519 | No
14/07/2023 | 07:03 | HH177F | URBAN | Asset failure | LV | 1.00 | 290.0 | 0.000447 | 0.0000015 | No
14/07/2023 | 07:09 | SM374A | URBAN | Asset failure | LV | 13.00 | 143.0 | 0.002866 | 0.0000200 | No
14/07/2023 | 08:11 | HH496G | URBAN | Asset failure | LV | 4.00 | 93.0 | 0.000574 | 0.0000062 | No
14/07/2023 | 08:16 | NU31 | LONG RURAL | Animal | Animal impact | 2.00 | 90.0 | 0.001292 | 0.0000144 | No
14/07/2023 | 08:25 | AP829G | URBAN | Asset failure | LV | 3.00 | 54.0 | 0.000250 | 0.0000046 | No
14/07/2023 | 08:46 | GA745A | SHORT RURAL | Planned |  | 203.00 | 688.6 | 0.983393 | 0.0014282 | No
14/07/2023 | 08:48 | HH148A | URBAN | Overloads |  | 18.67 | 116.0 | 0.003338 | 0.0000288 | No
14/07/2023 | 08:59 | WK72 | SHORT RURAL | Unknown | Unknown | 1.00 | 190.0 | 0.001337 | 0.0000070 | No
14/07/2023 | 09:13 | HH130F | URBAN | Planned |  | 83.00 | 348.0 | 0.044532 | 0.0001280 | No
14/07/2023 | 09:27 | MTB11 | SHORT RURAL | Planned |  | 116.00 | 272.0 | 0.221984 | 0.0008161 | No
14/07/2023 | 09:37 | SD34201 | SHORT RURAL | Planned |  | 48.00 | 281.0 | 0.094895 | 0.0003377 | No
14/07/2023 | 09:37 | GA53 | SHORT RURAL | Third Party | Vehicle impact | 10.00 | 173.0 | 0.012171 | 0.0000704 | No
14/07/2023 | 09:54 | BT06 | LONG RURAL | Planned |  | 22.00 | 461.5 | 0.072868 | 0.0001579 | No
14/07/2023 | 09:55 | WHY08 | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
14/07/2023 | 09:58 | HH496G | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
14/07/2023 | 10:11 | MV62 | SHORT RURAL | Asset failure | LV | 6.00 | 248.0 | 0.010469 | 0.0000422 | No
14/07/2023 | 10:13 | ST36 | LONG RURAL | Unknown | Unknown | 61.00 | 266.0 | 0.116443 | 0.0004378 | No
14/07/2023 | 11:42 | SG14 | SHORT RURAL | Planned |  | 3.00 | 250.0 | 0.005277 | 0.0000211 | No
14/07/2023 | 11:42 | SG14 | SHORT RURAL | Unknown | Unknown | 379.00 | 24.0 | 0.063939 | 0.0026665 | No
14/07/2023 | 11:45 | HH496C | URBAN | Asset failure | LV | 6.00 | 522.0 | 0.004829 | 0.0000093 | No
14/07/2023 | 11:48 | SA16 | URBAN | Overloads |  | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
14/07/2023 | 11:51 | SG14 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 1.00 | 37.0 | 0.000260 | 0.0000070 | No
14/07/2023 | 12:01 | SA17 | URBAN | Overloads |  | 1.00 | 91.0 | 0.000140 | 0.0000015 | No
14/07/2023 | 12:18 | HH102D | URBAN | Asset failure | LV | 29.00 | 134.0 | 0.005991 | 0.0000447 | No
14/07/2023 | 12:55 | MB12 | SHORT RURAL | Unknown | Unknown | 1.00 | 99.0 | 0.000697 | 0.0000070 | No
14/07/2023 | 13:03 | MV31 | SHORT RURAL | Planned |  | 2.00 | 104.0 | 0.001463 | 0.0000141 | No
14/07/2023 | 13:43 | HH432F | URBAN | Overloads |  | 1.00 | 401.0 | 0.000618 | 0.0000015 | No
14/07/2023 | 14:22 | LX61 | LONG RURAL | Asset failure | HV | 2.00 | 37.0 | 0.000531 | 0.0000144 | No
14/07/2023 | 15:08 | ST22 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 211.0 | 0.001484 | 0.0000070 | No
14/07/2023 | 15:08 | VH16 | SHORT RURAL | Overloads |  | 1.00 | 121.0 | 0.000851 | 0.0000070 | No
14/07/2023 | 15:56 | BM33 | SHORT RURAL | Asset failure | HV | 417.00 | 210.3 | 0.617041 | 0.0029338 | No
14/07/2023 | 16:12 | MB41 | LONG RURAL | Asset failure | LV | 15.00 | 567.6 | 0.061099 | 0.0001076 | No
14/07/2023 | 18:24 | NL234A | URBAN | Asset failure | LV | 1.00 | 162.0 | 0.000250 | 0.0000015 | No
14/07/2023 | 18:49 | SG13 | SHORT RURAL | Asset failure | LV | 2.00 | 143.0 | 0.002012 | 0.0000141 | No
14/07/2023 | 21:45 | EL14 | URBAN | Other |  | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
14/07/2023 | 22:24 | EL01Q | URBAN | Asset failure | LV | 1.00 | 168.0 | 0.000259 | 0.0000015 | No
14/07/2023 | 23:19 | ME116B | URBAN | Asset failure | LV | 17.67 | 113.0 | 0.003078 | 0.0000272 | No
15/07/2023 | 08:18 | SA43 | URBAN | Planned |  | 1.00 | 437.0 | 0.000674 | 0.0000015 | No
15/07/2023 | 08:49 | AP424E | URBAN | Asset failure | LV | 1.00 | 303.0 | 0.000467 | 0.0000015 | No
15/07/2023 | 09:15 | CL25 | LONG RURAL | Planned |  | 517.00 | 229.0 | 0.849627 | 0.0037102 | No
15/07/2023 | 09:28 | HH177E | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
15/07/2023 | 09:43 | WHY08 | URBAN | Asset failure | LV | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
15/07/2023 | 10:12 | R01 | LONG RURAL | Planned |  | 135.00 | 12.0 | 0.011626 | 0.0009688 | No
15/07/2023 | 10:12 | R01 | SHORT RURAL | Planned |  | 1.00 | 12.0 | 0.000084 | 0.0000070 | No
15/07/2023 | 10:34 | GU31 | LONG RURAL | Overloads |  | 1.00 | 150.0 | 0.001076 | 0.0000072 | No
15/07/2023 | 11:11 | AP227A | URBAN | Asset failure | LV | 1.00 | 203.0 | 0.000313 | 0.0000015 | No
15/07/2023 | 11:52 | AP365F | URBAN | Overloads |  | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
15/07/2023 | 15:44 | MG17 | LONG RURAL | Asset failure | LV | 1.00 | 173.0 | 0.001242 | 0.0000072 | No
15/07/2023 | 17:44 | R26 | LONG RURAL | Asset failure | LV | 2.00 | 270.0 | 0.003875 | 0.0000144 | No
15/07/2023 | 19:05 | SM411A | URBAN | Asset failure | LV | 1.00 | 191.0 | 0.000294 | 0.0000015 | No
16/07/2023 | 03:03 | EL01A | URBAN | Asset failure | LV | 1.00 | 29.0 | 0.000045 | 0.0000015 | No
16/07/2023 | 03:15 | LC01 | LONG RURAL | Planned |  | 125.00 | 497.0 | 0.445829 | 0.0008970 | No
16/07/2023 | 03:15 | LC01 | SHORT RURAL | Planned |  | 241.00 | 497.0 | 0.842690 | 0.0016956 | No
16/07/2023 | 05:48 | SD38100 | LONG RURAL | Asset failure | Subtransmission | 2.67 | 368.0 | 0.007042 | 0.0000191 | No
16/07/2023 | 07:59 | AP149A | URBAN | Planned |  | 123.00 | 309.2 | 0.058636 | 0.0001896 | No
16/07/2023 | 08:18 | SM216G | URBAN | Planned |  | 57.00 | 505.0 | 0.044379 | 0.0000879 | No
16/07/2023 | 08:23 | SD38100 | LONG RURAL | Overloads |  | 2.00 | 218.0 | 0.003129 | 0.0000144 | No
16/07/2023 | 08:25 | PA08 | LONG RURAL | Planned |  | 770.00 | 169.0 | 0.933856 | 0.0055258 | No
16/07/2023 | 08:39 | R15 | LONG RURAL | Weather |  | 58.00 | 144.0 | 0.059937 | 0.0004162 | No
16/07/2023 | 08:43 | SD33200 | LONG RURAL | Planned |  | 1,092.00 | 329.5 | 2.581756 | 0.0078366 | No
16/07/2023 | 08:59 | HH403A | URBAN | Planned |  | 76.00 | 284.2 | 0.033296 | 0.0001172 | No
16/07/2023 | 08:59 | HH130D | URBAN | Asset failure | LV | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
16/07/2023 | 10:12 | HH130G | URBAN | Overloads |  | 24.00 | 88.0 | 0.003256 | 0.0000370 | No
16/07/2023 | 11:10 | SG07 | SHORT RURAL | Unknown | Unknown | 83.00 | 160.0 | 0.093431 | 0.0005839 | No
16/07/2023 | 12:38 | HH432F | URBAN | Asset failure | LV | 13.67 | 77.0 | 0.001622 | 0.0000211 | No
16/07/2023 | 12:53 | HH341K | URBAN | Overloads |  | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
16/07/2023 | 14:15 | SM216E | URBAN | Asset failure | LV | 30.33 | 30.5 | 0.001427 | 0.0000468 | No
16/07/2023 | 16:56 | AP829E | URBAN | Asset failure | HV | 222.00 | 158.1 | 0.054103 | 0.0003423 | No
16/07/2023 | 17:19 | VH21 | SHORT RURAL | Unknown | Unknown | 1.00 | 111.0 | 0.000781 | 0.0000070 | No
16/07/2023 | 17:25 | G15 | LONG RURAL | Asset failure | LV | 2.00 | 1,129.0 | 0.016204 | 0.0000144 | No
16/07/2023 | 18:44 | MI01 | LONG RURAL | Asset failure | LV | 1.00 | 172.0 | 0.001234 | 0.0000072 | No
16/07/2023 | 19:16 | R12 | LONG RURAL | Asset failure | HV | 90.00 | 497.0 | 0.320997 | 0.0006459 | No
16/07/2023 | 20:04 | WHY07 | URBAN | Asset failure | LV | 1.00 | 179.0 | 0.000276 | 0.0000015 | No
16/07/2023 | 21:06 | SM126D | URBAN | Asset failure | LV | 58.00 | 103.0 | 0.009210 | 0.0000894 | No
16/07/2023 | 21:09 | AP227B | URBAN | Asset failure | LV | 9.33 | 15.0 | 0.000216 | 0.0000144 | No
16/07/2023 | 22:51 | NL511C | URBAN | Asset failure | HV | 682.00 | 139.5 | 0.146670 | 0.0010515 | No
16/07/2023 | 23:13 | MB27 | SHORT RURAL | Asset failure | HV | 3.00 | 90.0 | 0.001900 | 0.0000211 | No
17/07/2023 | 00:25 | SG13 | SHORT RURAL | Other |  | 1.00 | 216.0 | 0.001520 | 0.0000070 | No
17/07/2023 | 07:31 | MT02 | LONG RURAL | Asset failure | HV | 1.00 | 363.0 | 0.002605 | 0.0000072 | No
17/07/2023 | 08:13 | MG21 | LONG RURAL | Asset failure | LV | 1.00 | 190.0 | 0.001364 | 0.0000072 | No
17/07/2023 | 08:23 | NU20 | LONG RURAL | Planned |  | 915.00 | 458.8 | 3.012386 | 0.0065663 | No
17/07/2023 | 08:40 | ME347B | URBAN | Asset failure | LV | 9.00 | 460.8 | 0.006394 | 0.0000139 | No
17/07/2023 | 08:46 | KI22 | LONG RURAL | Planned |  | 16.00 | 190.0 | 0.021816 | 0.0001148 | No
17/07/2023 | 08:46 | MB72 | LONG RURAL | Asset failure | LV | 4.00 | 255.0 | 0.007320 | 0.0000287 | No
17/07/2023 | 09:00 | GU43 | LONG RURAL | Planned |  | 10.00 | 175.0 | 0.012559 | 0.0000718 | No
17/07/2023 | 09:03 | SD36201 | LONG RURAL | Planned |  | 77.00 | 127.9 | 0.070687 | 0.0005526 | No
17/07/2023 | 09:16 | NU19 | LONG RURAL | Planned |  | 1.00 | 199.0 | 0.001428 | 0.0000072 | No
17/07/2023 | 09:18 | ST21 | SHORT RURAL | Animal | Animal impact | 10.00 | 360.0 | 0.025328 | 0.0000704 | No
17/07/2023 | 09:26 | BM12 | SHORT RURAL | Other |  | 3.00 | 148.0 | 0.003124 | 0.0000211 | No
17/07/2023 | 09:27 | PP13 | LONG RURAL | Unknown | Unknown | 74.00 | 317.0 | 0.168342 | 0.0005310 | No
17/07/2023 | 09:34 | GA53 | SHORT RURAL | Asset failure | LV | 1.00 | 336.0 | 0.002364 | 0.0000070 | No
17/07/2023 | 09:36 | CM25 | LONG RURAL | Planned |  | 36.00 | 237.0 | 0.061228 | 0.0002583 | No
17/07/2023 | 09:50 | MB97 | LONG RURAL | Planned |  | 1.00 | 90.0 | 0.000646 | 0.0000072 | No
17/07/2023 | 09:51 | HH177C | URBAN | Unknown | Unknown | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
17/07/2023 | 10:15 | SD37102 | LONG RURAL | Planned |  | 88.00 | 173.1 | 0.109288 | 0.0006315 | No
17/07/2023 | 10:19 | WHY04 | URBAN | Asset failure | LV | 1.00 | 89.0 | 0.000137 | 0.0000015 | No
17/07/2023 | 10:27 | WK65 | SHORT RURAL | Asset failure | LV | 1.00 | 228.0 | 0.001604 | 0.0000070 | No
17/07/2023 | 10:58 | HH177F | URBAN | Planned |  | 16.00 | 303.0 | 0.007474 | 0.0000247 | No
17/07/2023 | 11:17 | NA62 | LONG RURAL | Planned |  | 24.00 | 111.0 | 0.019118 | 0.0001722 | No
17/07/2023 | 11:29 | BT26 | LONG RURAL | Asset failure | HV | 1.00 | 66.0 | 0.000474 | 0.0000072 | No
17/07/2023 | 11:44 | ME347C | URBAN | Asset failure | LV | 1.00 | 498.0 | 0.000768 | 0.0000015 | No
17/07/2023 | 11:52 | NL111Q | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 656.0 | 0.001011 | 0.0000015 | No
17/07/2023 | 12:00 | MV62 | SHORT RURAL | Asset failure | LV | 1.00 | 551.0 | 0.003877 | 0.0000070 | No
17/07/2023 | 13:26 | SM216C | URBAN | Asset failure | LV | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
17/07/2023 | 13:35 | SG03 | SHORT RURAL | Asset failure | LV | 1.00 | 1,242.0 | 0.008738 | 0.0000070 | No
17/07/2023 | 14:45 | HH409A | URBAN | Asset failure | LV | 42.00 | 180.0 | 0.011656 | 0.0000648 | No
17/07/2023 | 15:34 | AP149F | URBAN | Asset failure | LV | 2.00 | 228.0 | 0.000703 | 0.0000031 | No
17/07/2023 | 16:12 | HH409D | URBAN | Asset failure | LV | 1.00 | 361.0 | 0.000557 | 0.0000015 | No
17/07/2023 | 16:15 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 63.0 | 0.000443 | 0.0000070 | No
17/07/2023 | 17:35 | AP424E | URBAN | Asset failure | LV | 1.00 | 540.0 | 0.000833 | 0.0000015 | No
17/07/2023 | 17:43 | HH409A | URBAN | Overloads |  | 4.00 | 287.0 | 0.001770 | 0.0000062 | No
17/07/2023 | 18:35 | AP149B | URBAN | Unknown | Unknown | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
17/07/2023 | 18:48 | AP125A | URBAN | Planned |  | 30.00 | 58.0 | 0.002683 | 0.0000463 | No
17/07/2023 | 18:48 | AP125A | URBAN | Planned |  | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
17/07/2023 | 18:48 | AP125A | URBAN | Planned |  | 70.00 | 58.0 | 0.006260 | 0.0001079 | No
17/07/2023 | 18:48 | AP125A | URBAN | Planned |  | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
17/07/2023 | 18:48 | AP125A | URBAN | Planned |  | 208.00 | 58.0 | 0.018600 | 0.0003207 | No
17/07/2023 | 19:15 | SM411B | URBAN | Asset failure | LV | 1.00 | 198.0 | 0.000305 | 0.0000015 | No
17/07/2023 | 20:28 | ST12 | SHORT RURAL | Asset failure | LV | 6.00 | 216.0 | 0.009118 | 0.0000422 | No
17/07/2023 | 21:44 | PA12 | LONG RURAL | Overloads |  | 2.00 | 262.0 | 0.003760 | 0.0000144 | No
17/07/2023 | 22:32 | BM57 | SHORT RURAL | Asset failure | LV | 1.00 | 1,077.0 | 0.007577 | 0.0000070 | No
18/07/2023 | 07:43 | SM349A | URBAN | Asset failure | LV | 1.00 | 252.0 | 0.000389 | 0.0000015 | No
18/07/2023 | 08:12 | NL115E | URBAN | Unknown | Unknown | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
18/07/2023 | 08:17 | NU20 | LONG RURAL | Planned |  | 125.00 | 511.8 | 0.459142 | 0.0008970 | No
18/07/2023 | 08:25 | SD33200 | LONG RURAL | Planned |  | 32.00 | 198.0 | 0.045469 | 0.0002296 | No
18/07/2023 | 08:31 | BS0198 | URBAN | Planned |  | 1.00 | 3,401.0 | 0.005244 | 0.0000015 | No
18/07/2023 | 08:43 | SA11 | URBAN | Other |  | 27.00 | 98.0 | 0.004079 | 0.0000416 | No
18/07/2023 | 08:48 | VH17 | SHORT RURAL | Planned |  | 65.00 | 453.0 | 0.207160 | 0.0004573 | No
18/07/2023 | 09:03 | BM41 | SHORT RURAL | Planned |  | 2.00 | 313.0 | 0.004404 | 0.0000141 | No
18/07/2023 | 09:04 | HH428B | URBAN | Planned |  | 124.00 | 386.0 | 0.073795 | 0.0001912 | No
18/07/2023 | 09:33 | SA31 | URBAN | Planned |  | 1,089.00 | 392.9 | 0.659732 | 0.0016790 | No
18/07/2023 | 09:38 | NL234B | URBAN | Planned |  | 274.00 | 175.0 | 0.073927 | 0.0004224 | No
18/07/2023 | 10:22 | MG45 | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
18/07/2023 | 10:32 | SM179B | URBAN | Planned |  | 88.00 | 411.0 | 0.055762 | 0.0001357 | No
18/07/2023 | 10:46 | PL803C | URBAN | Asset failure | LV | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
18/07/2023 | 12:36 | YK02 | SHORT RURAL | Asset failure | LV | 1.00 | 292.0 | 0.002054 | 0.0000070 | No
18/07/2023 | 12:55 | EL260B | URBAN | Asset failure | HV | 2,595.00 | 37.8 | 0.151033 | 0.0040009 | No
18/07/2023 | 13:35 | HH341G | URBAN | Asset failure | LV | 1.00 | 1,015.0 | 0.001565 | 0.0000015 | No
18/07/2023 | 13:51 | VH31 | SHORT RURAL | Asset failure | LV | 39.00 | 60.0 | 0.016463 | 0.0002744 | No
18/07/2023 | 14:11 | YK19 | LONG RURAL | Planned |  | 29.00 | 38.0 | 0.007908 | 0.0002081 | No
18/07/2023 | 14:20 | KA03 | LONG RURAL | Asset failure | LV | 1.00 | 114.0 | 0.000818 | 0.0000072 | No
18/07/2023 | 15:02 | WK41 | SHORT RURAL | Asset failure | HV | 45.67 | 27.0 | 0.008675 | 0.0003213 | No
18/07/2023 | 16:26 | AP149A | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
18/07/2023 | 17:41 | SA744D | URBAN | Asset failure | LV | 8.00 | 748.3 | 0.009229 | 0.0000123 | No
18/07/2023 | 18:14 | LM11 | LONG RURAL | Overloads |  | 1.00 | 939.0 | 0.006739 | 0.0000072 | No
18/07/2023 | 18:31 | EL01N | URBAN | Asset failure | LV | 1.00 | 535.0 | 0.000825 | 0.0000015 | No
18/07/2023 | 19:23 | ST12 | SHORT RURAL | Asset failure | LV | 1.00 | 242.0 | 0.001703 | 0.0000070 | No
18/07/2023 | 20:06 | SA18 | URBAN | Asset failure | LV | 1.00 | 507.0 | 0.000782 | 0.0000015 | No
18/07/2023 | 21:27 | HH409F | URBAN | Asset failure | LV | 44.00 | 511.2 | 0.034679 | 0.0000678 | No
18/07/2023 | 22:48 | SM126D | URBAN | Planned |  | 48.00 | 348.4 | 0.025783 | 0.0000740 | No
18/07/2023 | 23:35 | AP226B | URBAN | Planned |  | 122.00 | 214.0 | 0.040252 | 0.0001881 | No
19/07/2023 | 03:33 | MTB14 | SHORT RURAL | Asset failure | HV | 17.00 | 737.0 | 0.088148 | 0.0001196 | No
19/07/2023 | 04:43 | HH177F | URBAN | Asset failure | LV | 5.67 | 284.0 | 0.002481 | 0.0000087 | No
19/07/2023 | 08:08 | NU20 | LONG RURAL | Planned |  | 25.00 | 333.2 | 0.059772 | 0.0001794 | No
19/07/2023 | 08:24 | KI32 | SHORT RURAL | Planned |  | 19.00 | 356.0 | 0.047588 | 0.0001337 | No
19/07/2023 | 08:25 | HH522B | URBAN | Planned |  | 1.00 | 394.0 | 0.000607 | 0.0000015 | No
19/07/2023 | 08:27 | ME116D | URBAN | Overloads |  | 3.00 | 87.0 | 0.000402 | 0.0000046 | No
19/07/2023 | 08:36 | WHY04 | URBAN | Planned |  | 75.00 | 326.1 | 0.037705 | 0.0001156 | No
19/07/2023 | 08:40 | GU32 | LONG RURAL | Planned |  | 617.00 | 434.1 | 1.921900 | 0.0044278 | No
19/07/2023 | 08:41 | R02 | LONG RURAL | Planned |  | 218.00 | 349.8 | 0.547202 | 0.0015644 | No
19/07/2023 | 08:48 | PL07 | URBAN | Asset failure | LV | 1.00 | 358.0 | 0.000552 | 0.0000015 | No
19/07/2023 | 08:53 | SD34201 | SHORT RURAL | Planned |  | 5.00 | 394.8 | 0.013888 | 0.0000352 | No
19/07/2023 | 09:02 | M92 | LONG RURAL | Planned |  | 772.00 | 428.0 | 2.371174 | 0.0055401 | No
19/07/2023 | 09:06 | EL10 | URBAN | Asset failure | LV | 15.00 | 270.0 | 0.006244 | 0.0000231 | No
19/07/2023 | 09:09 | HH522C | URBAN | Asset failure | LV | 35.00 | 104.0 | 0.005612 | 0.0000540 | No
19/07/2023 | 09:12 | CV23 | LONG RURAL | Planned |  | 14.00 | 381.0 | 0.038279 | 0.0001005 | No
19/07/2023 | 09:42 | BT02 | LONG RURAL | Planned |  | 15.00 | 137.0 | 0.014747 | 0.0001076 | No
19/07/2023 | 09:44 | SD32103 | URBAN | Planned |  | 2.00 | 281.0 | 0.000866 | 0.0000031 | No
19/07/2023 | 10:14 | MT08 | LONG RURAL | Planned |  | 57.00 | 12.0 | 0.004909 | 0.0004091 | No
19/07/2023 | 10:15 | MTB14 | LONG RURAL | Asset failure | HV | 4.00 | 7.0 | 0.000201 | 0.0000287 | No
19/07/2023 | 10:15 | MTB14 | SHORT RURAL | Asset failure | HV | 2,790.00 | 7.0 | 0.137403 | 0.0196290 | No
19/07/2023 | 10:34 | AP425D | URBAN | Asset failure | LV | 89.00 | 81.0 | 0.011115 | 0.0001372 | No
19/07/2023 | 10:38 | HH386G | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
19/07/2023 | 11:03 | EL18 | URBAN | Asset failure | LV | 1.00 | 334.0 | 0.000515 | 0.0000015 | No
19/07/2023 | 11:10 | HH386B | URBAN | Asset failure | LV | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
19/07/2023 | 11:16 | EL18 | URBAN | Asset failure | LV | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
19/07/2023 | 11:19 | HH102D | URBAN | Asset failure | LV | 1.00 | 156.0 | 0.000241 | 0.0000015 | No
19/07/2023 | 11:50 | KA24 | LONG RURAL | Weather |  | 3.00 | 46.0 | 0.000990 | 0.0000215 | No
19/07/2023 | 12:01 | SM350A | URBAN | Asset failure | LV | 1.00 | 347.0 | 0.000535 | 0.0000015 | No
19/07/2023 | 12:17 | SSD236 | SHORT RURAL | Unknown | Unknown | 473.00 | 87.8 | 0.292233 | 0.0033278 | No
19/07/2023 | 12:28 | HH386E | URBAN | Overloads |  | 4.67 | 113.0 | 0.000813 | 0.0000072 | No
19/07/2023 | 12:51 | NL111B | URBAN | Other |  | 63.00 | 134.0 | 0.013015 | 0.0000971 | No
19/07/2023 | 13:15 | HH409C | URBAN | Asset failure | LV | 6.00 | 220.0 | 0.002035 | 0.0000093 | No
19/07/2023 | 13:16 | BT15 | LONG RURAL | Planned |  | 113.00 | 1.0 | 0.000811 | 0.0008109 | No
19/07/2023 | 13:24 | SM402D | URBAN | Asset failure | LV | 1.00 | 460.0 | 0.000709 | 0.0000015 | No
19/07/2023 | 13:34 | ME131B | URBAN | Asset failure | LV | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
19/07/2023 | 13:51 | HH121G | URBAN | Asset failure | LV | 5.00 | 47.0 | 0.000362 | 0.0000077 | No
19/07/2023 | 15:02 | HH386B | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
19/07/2023 | 15:36 | NL511D | URBAN | Unknown | Unknown | 12.00 | 299.3 | 0.005536 | 0.0000185 | No
19/07/2023 | 15:38 | EL18 | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
19/07/2023 | 16:00 | NL760B | URBAN | Asset failure | LV | 1.00 | 514.0 | 0.000792 | 0.0000015 | No
19/07/2023 | 17:17 | NU19 | LONG RURAL | Asset failure | HV | 3.00 | 104.0 | 0.002239 | 0.0000215 | No
19/07/2023 | 18:20 | VH16 | SHORT RURAL | Asset failure | LV | 1.00 | 200.0 | 0.001407 | 0.0000070 | No
19/07/2023 | 18:52 | HH145A | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
19/07/2023 | 18:58 | MI03 | LONG RURAL | Asset failure | LV | 2.00 | 318.0 | 0.004564 | 0.0000144 | No
19/07/2023 | 19:21 | EL19 | URBAN | Asset failure | LV | 1.00 | 230.0 | 0.000355 | 0.0000015 | No
19/07/2023 | 20:00 | HH177D | URBAN | Third Party | Vehicle impact | 1.00 | 93.0 | 0.000143 | 0.0000015 | No
19/07/2023 | 20:20 | SM374B | URBAN | Asset failure | LV | 5.00 | 70.0 | 0.000540 | 0.0000077 | No
19/07/2023 | 20:21 | HH177D | URBAN | Third Party | Unauthorised access | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
19/07/2023 | 20:38 | EL07 | URBAN | Asset failure | LV | 1.00 | 266.0 | 0.000410 | 0.0000015 | No
19/07/2023 | 20:39 | MV62 | SHORT RURAL | Asset failure | HV | 104.00 | 50.0 | 0.036585 | 0.0007317 | No
19/07/2023 | 23:16 | HH428B | URBAN | Overloads |  | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
19/07/2023 | 23:44 | ME131C | URBAN | Asset failure | LV | 18.00 | 227.0 | 0.006300 | 0.0000278 | No
20/07/2023 | 05:24 | MV42 | SHORT RURAL | Asset failure | HV | 822.00 | 50.4 | 0.291509 | 0.0057832 | No
20/07/2023 | 06:16 | MV14 | SHORT RURAL | Weather |  | 23.33 | 441.7 | 0.072512 | 0.0001642 | No
20/07/2023 | 07:31 | MV42 | SHORT RURAL | Asset failure | HV | 154.00 | 243.6 | 0.263958 | 0.0010835 | No
20/07/2023 | 07:38 | HH130F | URBAN | Network business | Switching and protection error | 6.33 | 248.0 | 0.002422 | 0.0000098 | No
20/07/2023 | 08:01 | NL451A | URBAN | Asset failure | LV | 1.00 | 226.0 | 0.000348 | 0.0000015 | No
20/07/2023 | 08:13 | MB22 | SHORT RURAL | Asset failure | LV | 1.00 | 384.0 | 0.002702 | 0.0000070 | No
20/07/2023 | 08:22 | MV11 | SHORT RURAL | Asset failure | HV | 5.00 | 1,020.2 | 0.035888 | 0.0000352 | No
20/07/2023 | 08:29 | ME116D | URBAN | Overloads |  | 3.00 | 136.0 | 0.000629 | 0.0000046 | No
20/07/2023 | 08:48 | NU02 | LONG RURAL | Planned |  | 599.00 | 369.0 | 1.586069 | 0.0042986 | No
20/07/2023 | 08:48 | NU02 | SHORT RURAL | Planned |  | 1.00 | 371.0 | 0.002610 | 0.0000070 | No
20/07/2023 | 08:52 | BT10 | LONG RURAL | Planned |  | 34.00 | 338.0 | 0.082470 | 0.0002440 | No
20/07/2023 | 09:04 | AP139C | URBAN | Asset failure | LV | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
20/07/2023 | 09:11 | PL29 | LONG RURAL | Planned |  | 89.00 | 224.0 | 0.143067 | 0.0006387 | No
20/07/2023 | 09:13 | MI17 | LONG RURAL | Unknown | Unknown | 10.00 | 61.5 | 0.004413 | 0.0000718 | No
20/07/2023 | 09:15 | NU06 | LONG RURAL | Planned |  | 75.00 | 97.1 | 0.052251 | 0.0005382 | No
20/07/2023 | 09:29 | SM374B | URBAN | Asset failure | LV | 1.00 | 786.0 | 0.001212 | 0.0000015 | No
20/07/2023 | 09:32 | CD01 | SHORT RURAL | Planned |  | 44.00 | 305.0 | 0.094416 | 0.0003096 | No
20/07/2023 | 09:36 | WHY12 | URBAN | Unknown | Unknown | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
20/07/2023 | 09:43 | KI11 | LONG RURAL | Planned |  | 51.00 | 342.0 | 0.125170 | 0.0003660 | No
20/07/2023 | 09:44 | KI54 | LONG RURAL | Unknown | Unknown | 1.00 | 51.0 | 0.000366 | 0.0000072 | No
20/07/2023 | 10:12 | ME231C | URBAN | Vegetation | Grow-in - NSP responsibility | 4.00 | 782.0 | 0.004823 | 0.0000062 | No
20/07/2023 | 10:18 | GA07 | LONG RURAL | Asset failure | HV | 1.00 | 63.0 | 0.000452 | 0.0000072 | No
20/07/2023 | 10:18 | MTB52 | LONG RURAL | Planned |  | 47.00 | 149.0 | 0.050256 | 0.0003373 | No
20/07/2023 | 10:46 | W26 | LONG RURAL | Planned |  | 30.00 | 188.0 | 0.040474 | 0.0002153 | No
20/07/2023 | 10:49 | HH121D | URBAN | Asset failure | LV | 1.00 | 253.0 | 0.000390 | 0.0000015 | No
20/07/2023 | 11:33 | MTB32 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 62.00 | 62.0 | 0.027586 | 0.0004449 | No
20/07/2023 | 11:56 | NL115E | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
20/07/2023 | 12:07 | SA31 | URBAN | Asset failure | LV | 1.00 | 334.0 | 0.000515 | 0.0000015 | No
20/07/2023 | 12:09 | MTB41 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 270.00 | 16.1 | 0.030618 | 0.0018996 | No
20/07/2023 | 12:17 | R21 | LONG RURAL | Planned |  | 1.00 | 71.0 | 0.000510 | 0.0000072 | No
20/07/2023 | 12:39 | GA15 | SHORT RURAL | Weather |  | 655.00 | 110.1 | 0.507210 | 0.0046082 | No
20/07/2023 | 13:14 | BM44 | SHORT RURAL | Asset failure | LV | 1.00 | 182.0 | 0.001280 | 0.0000070 | No
20/07/2023 | 13:31 | HH130F | URBAN | Asset failure | LV | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
20/07/2023 | 13:44 | M22 | LONG RURAL | Asset failure | LV | 1.00 | 234.0 | 0.001679 | 0.0000072 | No
20/07/2023 | 13:48 | VH23 | SHORT RURAL | Unknown | Unknown | 1.00 | 103.0 | 0.000725 | 0.0000070 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 36.00 | 85.0 | 0.004718 | 0.0000555 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 35.00 | 85.0 | 0.004587 | 0.0000540 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 37.00 | 85.0 | 0.004849 | 0.0000570 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 78.00 | 85.0 | 0.010222 | 0.0001203 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 85.0 | 0.005373 | 0.0000632 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 85.0 | 0.005373 | 0.0000632 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 36.00 | 85.0 | 0.004718 | 0.0000555 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 14.00 | 85.0 | 0.001835 | 0.0000216 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 40.00 | 85.0 | 0.005242 | 0.0000617 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 33.00 | 85.0 | 0.004325 | 0.0000509 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 42.00 | 85.0 | 0.005504 | 0.0000648 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 48.00 | 85.0 | 0.006290 | 0.0000740 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 55.00 | 85.0 | 0.007208 | 0.0000848 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 85.0 | 0.000393 | 0.0000046 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 10.00 | 85.0 | 0.001310 | 0.0000154 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 64.00 | 85.0 | 0.008387 | 0.0000987 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 67.00 | 85.0 | 0.008780 | 0.0001033 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.00 | 85.0 | 0.003669 | 0.0000432 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 73.00 | 85.0 | 0.009567 | 0.0001125 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 48.00 | 85.0 | 0.006290 | 0.0000740 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 32.00 | 85.0 | 0.004194 | 0.0000493 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 12.00 | 85.0 | 0.001573 | 0.0000185 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 48.00 | 85.0 | 0.006290 | 0.0000740 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 19.00 | 85.0 | 0.002490 | 0.0000293 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 14.00 | 85.0 | 0.001835 | 0.0000216 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 36.00 | 85.0 | 0.004718 | 0.0000555 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 43.00 | 85.0 | 0.005635 | 0.0000663 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 55.00 | 85.0 | 0.007208 | 0.0000848 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 35.00 | 85.0 | 0.004587 | 0.0000540 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 59.00 | 85.0 | 0.007732 | 0.0000910 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 60.00 | 85.0 | 0.007863 | 0.0000925 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 67.00 | 85.0 | 0.008780 | 0.0001033 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 66.00 | 85.0 | 0.008649 | 0.0001018 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 44.00 | 85.0 | 0.005766 | 0.0000678 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 32.00 | 85.0 | 0.004194 | 0.0000493 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 45.00 | 85.0 | 0.005897 | 0.0000694 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 85.0 | 0.005373 | 0.0000632 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 79.00 | 85.0 | 0.010353 | 0.0001218 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 85.0 | 0.005373 | 0.0000632 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 48.00 | 85.0 | 0.006290 | 0.0000740 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 69.00 | 85.0 | 0.009042 | 0.0001064 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 48.00 | 85.0 | 0.006290 | 0.0000740 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 97.00 | 85.0 | 0.012712 | 0.0001496 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
20/07/2023 | 14:17 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 827.00 | 85.0 | 0.108378 | 0.0012750 | No
20/07/2023 | 14:59 | SM172E | URBAN | Planned |  | 54.00 | 1.0 | 0.000083 | 0.0000833 | No
20/07/2023 | 15:25 | SA14 | URBAN | Asset failure | LV | 1.00 | 1,557.0 | 0.002401 | 0.0000015 | No
20/07/2023 | 15:55 | SM216E | URBAN | Asset failure | LV | 12.67 | 333.0 | 0.006503 | 0.0000195 | No
20/07/2023 | 16:14 | NU14 | LONG RURAL | Asset failure | HV | 4.00 | 206.5 | 0.005928 | 0.0000287 | No
20/07/2023 | 17:14 | BS0198 | URBAN | Planned |  | 1.00 | 2,899.0 | 0.004470 | 0.0000015 | No
20/07/2023 | 18:03 | SM350A | URBAN | Asset failure | LV | 54.00 | 73.9 | 0.006150 | 0.0000833 | No
20/07/2023 | 18:04 | NL451C | URBAN | Unknown | Unknown | 1.00 | 405.0 | 0.000624 | 0.0000015 | No
20/07/2023 | 18:18 | EL01R | URBAN | Asset failure | LV | 1.00 | 434.0 | 0.000669 | 0.0000015 | No
20/07/2023 | 19:47 | HH130B | URBAN | Asset failure | LV | 9.33 | 148.0 | 0.002130 | 0.0000144 | No
20/07/2023 | 21:22 | PA03 | URBAN | Asset failure | LV | 2.00 | 153.0 | 0.000472 | 0.0000031 | No
20/07/2023 | 21:57 | GA25 | SHORT RURAL | Asset failure | LV | 20.67 | 102.0 | 0.014831 | 0.0001454 | No
21/07/2023 | 00:46 | HH130F | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
21/07/2023 | 05:22 | MV33 | SHORT RURAL | Asset failure | LV | 1.00 | 681.0 | 0.004791 | 0.0000070 | No
21/07/2023 | 07:18 | NL115E | URBAN | Asset failure | LV | 1.00 | 263.0 | 0.000405 | 0.0000015 | No
21/07/2023 | 08:51 | MTB11 | SHORT RURAL | Unknown | Unknown | 1.00 | 112.0 | 0.000788 | 0.0000070 | No
21/07/2023 | 08:53 | SD60101 | SHORT RURAL | Asset failure | Subtransmission | 33.00 | 262.0 | 0.060829 | 0.0002322 | No
21/07/2023 | 09:03 | MI23 | LONG RURAL | Planned |  | 2.00 | 125.0 | 0.001794 | 0.0000144 | No
21/07/2023 | 09:13 | HH409A | URBAN | Planned |  | 291.00 | 246.4 | 0.110531 | 0.0004487 | No
21/07/2023 | 09:15 | CD02 | LONG RURAL | Planned |  | 329.00 | 336.5 | 0.794398 | 0.0023610 | No
21/07/2023 | 09:15 | R28 | LONG RURAL | Planned |  | 86.00 | 27.0 | 0.016663 | 0.0006172 | No
21/07/2023 | 09:24 | NU24 | LONG RURAL | Planned |  | 17.00 | 163.8 | 0.019979 | 0.0001220 | No
21/07/2023 | 09:25 | PA04 | URBAN | Planned |  | 23.00 | 167.0 | 0.005922 | 0.0000355 | No
21/07/2023 | 09:45 | VH17 | SHORT RURAL | Planned |  | 32.00 | 312.0 | 0.070242 | 0.0002251 | No
21/07/2023 | 10:34 | KI44 | LONG RURAL | Planned |  | 2.00 | 94.0 | 0.001349 | 0.0000144 | No
21/07/2023 | 10:36 | SM179B | URBAN | Asset failure | LV | 24.00 | 114.0 | 0.004218 | 0.0000370 | No
21/07/2023 | 12:30 | VH32 | SHORT RURAL | Unknown | Unknown | 533.00 | 43.0 | 0.161246 | 0.0037499 | No
21/07/2023 | 13:21 | MV12 | URBAN | Overloads |  | 1.00 | 266.0 | 0.000410 | 0.0000015 | No
21/07/2023 | 13:34 | EL10 | URBAN | Asset failure | LV | 1.00 | 280.0 | 0.000432 | 0.0000015 | No
21/07/2023 | 13:53 | HH118D | URBAN | Asset failure | LV | 1.00 | 228.0 | 0.000352 | 0.0000015 | No
21/07/2023 | 14:43 | HH428C | URBAN | Third Party | Vehicle impact | 1,164.00 | 131.0 | 0.235093 | 0.0017946 | No
21/07/2023 | 15:17 | HH429A | URBAN | Asset failure | LV | 1.00 | 191.0 | 0.000294 | 0.0000015 | No
21/07/2023 | 16:34 | R01 | LONG RURAL | Unknown | Unknown | 8.67 | 174.0 | 0.010822 | 0.0000622 | No
21/07/2023 | 17:31 | R33 | LONG RURAL | Asset failure | LV | 2.00 | 257.0 | 0.003689 | 0.0000144 | No
21/07/2023 | 19:06 | SM216D | URBAN | Asset failure | LV | 37.67 | 157.0 | 0.009117 | 0.0000581 | No
21/07/2023 | 20:23 | ME200A | URBAN | Asset failure | LV | 6.00 | 225.0 | 0.002081 | 0.0000093 | No
21/07/2023 | 20:51 | SA16 | URBAN | Asset failure | LV | 45.00 | 68.0 | 0.004718 | 0.0000694 | No
21/07/2023 | 21:33 | HH496B | URBAN | Unknown | Unknown | 8.00 | 63.0 | 0.000777 | 0.0000123 | No
21/07/2023 | 23:16 | GA15 | SHORT RURAL | Asset failure | LV | 3.00 | 1,055.0 | 0.022267 | 0.0000211 | No
22/07/2023 | 06:43 | SD49200 | LONG RURAL | Animal | Animal impact | 48.67 | 236.0 | 0.082423 | 0.0003492 | No
22/07/2023 | 07:52 | HH145C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 850.00 | 48.5 | 0.063604 | 0.0013105 | No
22/07/2023 | 08:11 | EL04 | URBAN | Planned |  | 1.00 | 384.0 | 0.000592 | 0.0000015 | No
22/07/2023 | 08:14 | SD40800 | LONG RURAL | Planned |  | 3.00 | 1,717.0 | 0.036965 | 0.0000215 | No
22/07/2023 | 11:45 | ME131D | URBAN | Asset failure | LV | 1.00 | 433.0 | 0.000668 | 0.0000015 | No
22/07/2023 | 11:47 | PL07 | URBAN | Asset failure | LV | 1.00 | 168.0 | 0.000259 | 0.0000015 | No
22/07/2023 | 12:05 | AP227C | URBAN | Unknown | Unknown | 13.33 | 128.0 | 0.002631 | 0.0000206 | No
22/07/2023 | 15:18 | SM179C | URBAN | Weather |  | 1,354.00 | 95.0 | 0.198231 | 0.0020875 | No
22/07/2023 | 15:43 | AP214A | URBAN | Asset failure | LV | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
22/07/2023 | 16:51 | SM172A | URBAN | Asset failure | LV | 37.00 | 45.0 | 0.002567 | 0.0000570 | No
22/07/2023 | 17:45 | AP424D | URBAN | Asset failure | LV | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
22/07/2023 | 18:11 | SM350A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 278.00 | 54.0 | 0.023145 | 0.0004286 | No
22/07/2023 | 18:43 | G32 | LONG RURAL | Asset failure | HV | 101.00 | 112.0 | 0.081200 | 0.0007248 | No
22/07/2023 | 19:04 | AP149F | URBAN | Asset failure | LV | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
22/07/2023 | 19:04 | SG01 | SHORT RURAL | Asset failure | LV | 1.00 | 143.0 | 0.001006 | 0.0000070 | No
22/07/2023 | 19:55 | SA744C | URBAN | Asset failure | HV | 2.00 | 97.0 | 0.000299 | 0.0000031 | No
22/07/2023 | 20:24 | NL544B | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
22/07/2023 | 20:56 | SA33 | URBAN | Overloads |  | 86.00 | 150.0 | 0.019889 | 0.0001326 | No
22/07/2023 | 21:01 | NA51 | LONG RURAL | Unknown | Unknown | 12.33 | 138.0 | 0.012214 | 0.0000885 | No
22/07/2023 | 21:12 | NA51 | LONG RURAL | Asset failure | LV | 1.00 | 240.0 | 0.001722 | 0.0000072 | No
22/07/2023 | 23:50 | WHY07 | URBAN | Third Party | Vehicle impact | 37.00 | 340.1 | 0.019398 | 0.0000570 | No
23/07/2023 | 00:50 | SA18 | URBAN | Network business | Switching and protection error | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
23/07/2023 | 07:43 | NL760C | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
23/07/2023 | 08:16 | SM172F | URBAN | Planned |  | 58.00 | 307.0 | 0.027452 | 0.0000894 | No
23/07/2023 | 08:26 | AP355C | URBAN | Planned |  | 12.00 | 287.0 | 0.005310 | 0.0000185 | No
23/07/2023 | 10:19 | SA32 | URBAN | Asset failure | HV | 2,739.00 | 93.2 | 0.393454 | 0.0042229 | No
23/07/2023 | 10:32 | NA51 | LONG RURAL | Weather |  | 18.00 | 70.0 | 0.009042 | 0.0001292 | No
23/07/2023 | 10:39 | CBD27F | CBD | Unknown | Unknown | 1.00 | 193.0 | 0.027884 | 0.0001445 | No
23/07/2023 | 11:13 | CN25 | LONG RURAL | Planned |  | 2.00 | 78.0 | 0.001120 | 0.0000144 | No
23/07/2023 | 11:47 | AP149E | URBAN | Asset failure | LV | 25.67 | 103.0 | 0.004076 | 0.0000396 | No
23/07/2023 | 12:11 | KI41 | LONG RURAL | Unknown | Unknown | 2.00 | 11,621.0 | 0.166792 | 0.0000144 | No
23/07/2023 | 13:04 | R01 | LONG RURAL | Overloads |  | 4.33 | 230.0 | 0.007152 | 0.0000311 | No
23/07/2023 | 14:28 | G32 | LONG RURAL | Weather |  | 10.00 | 33.0 | 0.002368 | 0.0000718 | No
23/07/2023 | 16:29 | WK41 | SHORT RURAL | Asset failure | LV | 9.67 | 98.0 | 0.006665 | 0.0000680 | No
23/07/2023 | 17:29 | MI14 | LONG RURAL | Asset failure | LV | 1.00 | 148.0 | 0.001062 | 0.0000072 | No
23/07/2023 | 18:47 | NL544A | URBAN | Asset failure | LV | 78.00 | 346.0 | 0.041609 | 0.0001203 | No
23/07/2023 | 19:55 | HH177C | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
23/07/2023 | 20:13 | R01 | LONG RURAL | Overloads |  | 4.33 | 214.0 | 0.006655 | 0.0000311 | No
23/07/2023 | 21:29 | AP139A | URBAN | Third Party | Vehicle impact | 1,049.00 | 177.9 | 0.287716 | 0.0016173 | No
23/07/2023 | 21:46 | HH118E | URBAN | Planned |  | 26.00 | 353.1 | 0.014153 | 0.0000401 | No
23/07/2023 | 22:00 | NL115F | URBAN | Asset failure | LV | 17.67 | 66.2 | 0.001802 | 0.0000272 | No
23/07/2023 | 23:10 | SA32 | URBAN | Unknown | Unknown | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
23/07/2023 | 23:28 | EL18 | URBAN | Asset failure | LV | 1.00 | 81.0 | 0.000125 | 0.0000015 | No
23/07/2023 | 23:56 | EL18 | URBAN | Asset failure | LV | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
23/07/2023 | 23:57 | SA32 | URBAN | Unknown | Unknown | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
24/07/2023 | 00:35 | NU23 | LONG RURAL | Asset failure | LV | 3.00 | 725.0 | 0.015609 | 0.0000215 | No
24/07/2023 | 05:04 | EL01L | URBAN | Unknown | Unknown | 1.00 | 313.0 | 0.000483 | 0.0000015 | No
24/07/2023 | 05:41 | HH522B | URBAN | Asset failure | LV | 19.33 | 185.0 | 0.005514 | 0.0000298 | No
24/07/2023 | 05:57 | AP227C | URBAN | Unknown | Unknown | 6.67 | 157.0 | 0.001614 | 0.0000103 | No
24/07/2023 | 07:46 | GA53 | SHORT RURAL | Overloads |  | 1.00 | 152.0 | 0.001069 | 0.0000070 | No
24/07/2023 | 08:08 | BT02 | LONG RURAL | Unknown | Unknown | 1.00 | 5,939.0 | 0.042620 | 0.0000072 | No
24/07/2023 | 08:24 | MG42 | SHORT RURAL | Planned |  | 114.00 | 59.0 | 0.047321 | 0.0008020 | No
24/07/2023 | 08:36 | NL544A | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
24/07/2023 | 09:30 | NA24 | LONG RURAL | Planned |  | 4.00 | 286.0 | 0.008210 | 0.0000287 | No
24/07/2023 | 09:41 | PL29 | LONG RURAL | Animal | Animal impact | 89.00 | 148.3 | 0.094728 | 0.0006387 | No
24/07/2023 | 09:46 | SB01 | LONG RURAL | Planned |  | 25.00 | 180.0 | 0.032301 | 0.0001794 | No
24/07/2023 | 10:13 | SB03 | LONG RURAL | Asset failure | LV | 2.00 | 412.0 | 0.005913 | 0.0000144 | No
24/07/2023 | 10:41 | PA05 | LONG RURAL | Planned |  | 188.00 | 111.2 | 0.150043 | 0.0013491 | No
24/07/2023 | 11:29 | SA33 | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 7.67 | 167.0 | 0.001974 | 0.0000118 | No
24/07/2023 | 11:42 | NA13 | LONG RURAL | Asset failure | HV | 4.00 | 97.0 | 0.002784 | 0.0000287 | No
24/07/2023 | 11:48 | CD01 | SHORT RURAL | Asset failure | LV | 3.00 | 141.0 | 0.002976 | 0.0000211 | No
24/07/2023 | 13:08 | PA04 | URBAN | Asset failure | LV | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
24/07/2023 | 14:37 | CN71 | LONG RURAL | Asset failure | HV | 236.00 | 11.1 | 0.018766 | 0.0016936 | No
24/07/2023 | 15:11 | MI14 | LONG RURAL | Asset failure | HV | 2.00 | 32.0 | 0.000459 | 0.0000144 | No
24/07/2023 | 15:27 | EL10 | URBAN | Asset failure | LV | 1.00 | 577.0 | 0.000890 | 0.0000015 | No
24/07/2023 | 15:55 | MB13 | SHORT RURAL | Asset failure | LV | 15.00 | 395.0 | 0.041685 | 0.0001055 | No
24/07/2023 | 16:30 | YK17 | LONG RURAL | Unknown | Unknown | 1.00 | 263.0 | 0.001887 | 0.0000072 | No
24/07/2023 | 16:36 | LX62 | LONG RURAL | Asset failure | HV | 14.00 | 102.0 | 0.010248 | 0.0001005 | No
24/07/2023 | 18:01 | MV31 | SHORT RURAL | Weather |  | 110.00 | 298.0 | 0.230637 | 0.0007739 | No
24/07/2023 | 18:25 | VH11 | URBAN | Asset failure | LV | 1.00 | 447.0 | 0.000689 | 0.0000015 | No
24/07/2023 | 18:57 | SM216B | URBAN | Asset failure | LV | 12.00 | 129.0 | 0.002387 | 0.0000185 | No
24/07/2023 | 19:08 | PP03 | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
24/07/2023 | 20:20 | EL260C | URBAN | Asset failure | LV | 3.00 | 92.0 | 0.000426 | 0.0000046 | No
24/07/2023 | 21:10 | ME347A | URBAN | Other |  | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
25/07/2023 | 00:27 | SM216C | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
25/07/2023 | 05:25 | MV22 | SHORT RURAL | Unknown | Unknown | 28.67 | 441.0 | 0.088943 | 0.0002017 | No
25/07/2023 | 07:07 | CN43 | LONG RURAL | Animal | Animal impact | 2.00 | 364.0 | 0.005224 | 0.0000144 | No
25/07/2023 | 08:07 | NU04 | SHORT RURAL | Unknown | Unknown | 1.00 | 233.0 | 0.001639 | 0.0000070 | No
25/07/2023 | 08:23 | BT15 | LONG RURAL | Asset failure | LV | 3.00 | 4,493.0 | 0.096730 | 0.0000215 | No
25/07/2023 | 08:28 | AP355H | URBAN | Planned |  | 273.00 | 76.5 | 0.032200 | 0.0004209 | No
25/07/2023 | 08:35 | PL11 | LONG RURAL | Planned |  | 14.00 | 162.0 | 0.016276 | 0.0001005 | No
25/07/2023 | 08:54 | ME200E | URBAN | Unknown | Unknown | 1.67 | 138.0 | 0.000355 | 0.0000026 | No
25/07/2023 | 08:55 | NA52 | LONG RURAL | Planned |  | 3.00 | 179.7 | 0.003868 | 0.0000215 | No
25/07/2023 | 09:02 | SD54300 | LONG RURAL | Planned |  | 1.00 | 42.0 | 0.000301 | 0.0000072 | No
25/07/2023 | 09:04 | PA03 | URBAN | Asset failure | LV | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
25/07/2023 | 09:26 | VH43 | SHORT RURAL | Unknown | Unknown | 3.00 | 467.0 | 0.009857 | 0.0000211 | No
25/07/2023 | 09:26 | HH148D | URBAN | Planned |  | 45.00 | 306.5 | 0.021267 | 0.0000694 | No
25/07/2023 | 09:29 | MB63 | LONG RURAL | Planned |  | 295.00 | 334.5 | 0.708210 | 0.0021170 | No
25/07/2023 | 09:34 | HH121F | URBAN | Planned |  | 121.00 | 169.6 | 0.031634 | 0.0001866 | No
25/07/2023 | 09:40 | EL15 | URBAN | Planned |  | 4.00 | 179.0 | 0.001104 | 0.0000062 | No
25/07/2023 | 09:54 | MI24 | LONG RURAL | Planned |  | 46.00 | 167.0 | 0.055129 | 0.0003301 | No
25/07/2023 | 10:33 | PP09 | LONG RURAL | Planned |  | 42.00 | 11.0 | 0.003315 | 0.0003014 | No
25/07/2023 | 10:53 | W02 | LONG RURAL | Planned |  | 356.00 | 30.0 | 0.076643 | 0.0025548 | No
25/07/2023 | 11:55 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 458.0 | 0.003222 | 0.0000070 | No
25/07/2023 | 12:12 | LX61 | LONG RURAL | Planned |  | 2.00 | 48.0 | 0.000689 | 0.0000144 | No
25/07/2023 | 12:40 | NA60 | LONG RURAL | Planned |  | 56.00 | 142.0 | 0.057066 | 0.0004019 | No
25/07/2023 | 13:07 | SM350G | URBAN | Asset failure | LV | 58.00 | 333.0 | 0.029777 | 0.0000894 | No
25/07/2023 | 14:45 | MG10 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 2.00 | 106.0 | 0.001521 | 0.0000144 | No
25/07/2023 | 14:52 | BM13 | SHORT RURAL | Planned |  | 5.00 | 101.0 | 0.003553 | 0.0000352 | No
25/07/2023 | 15:00 | NL234C | URBAN | Third Party | Other | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
25/07/2023 | 15:35 | MG45 | URBAN | Asset failure | LV | 2.00 | 409.0 | 0.001261 | 0.0000031 | No
25/07/2023 | 18:09 | HH496C | URBAN | Asset failure | LV | 26.00 | 190.0 | 0.007616 | 0.0000401 | No
25/07/2023 | 18:21 | LX21 | SHORT RURAL | Asset failure | HV | 1.00 | 1,307.0 | 0.009195 | 0.0000070 | No
25/07/2023 | 19:27 | MTB13 | SHORT RURAL | Overloads |  | 2.00 | 232.0 | 0.003264 | 0.0000141 | No
25/07/2023 | 19:51 | SM349B | URBAN | Overloads |  | 1.00 | 234.0 | 0.000361 | 0.0000015 | No
25/07/2023 | 20:15 | SD40700 | LONG RURAL | Asset failure | Subtransmission | 2.00 | 58.0 | 0.000832 | 0.0000144 | No
25/07/2023 | 21:00 | ME347C | URBAN | Asset failure | LV | 134.00 | 368.0 | 0.076027 | 0.0002066 | No
25/07/2023 | 22:09 | ME200B | URBAN | Planned |  | 2.00 | 457.0 | 0.001409 | 0.0000031 | No
26/07/2023 | 02:04 | SA20 | URBAN | Asset failure | LV | 15.00 | 771.3 | 0.017837 | 0.0000231 | No
26/07/2023 | 07:54 | WHY12 | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
26/07/2023 | 07:56 | AP139C | URBAN | Asset failure | LV | 3.00 | 173.3 | 0.000802 | 0.0000046 | No
26/07/2023 | 08:04 | HH121D | URBAN | Overloads |  | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
26/07/2023 | 08:09 | VH71 | SHORT RURAL | Planned |  | 141.00 | 464.1 | 0.460395 | 0.0009920 | No
26/07/2023 | 08:23 | AP355H | URBAN | Planned |  | 296.00 | 216.9 | 0.098968 | 0.0004564 | No
26/07/2023 | 08:25 | NL451C | URBAN | Planned |  | 1.00 | 420.0 | 0.000648 | 0.0000015 | No
26/07/2023 | 08:51 | EL260B | URBAN | Asset failure | LV | 1.00 | 840.0 | 0.001295 | 0.0000015 | No
26/07/2023 | 08:54 | MG31 | LONG RURAL | Planned |  | 1.00 | 25.0 | 0.000179 | 0.0000072 | No
26/07/2023 | 09:09 | SD32302 | LONG RURAL | Planned |  | 1.00 | 576.0 | 0.004134 | 0.0000072 | No
26/07/2023 | 09:25 | NL511A | URBAN | Overloads |  | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
26/07/2023 | 09:26 | HH121F | URBAN | Planned |  | 135.00 | 187.5 | 0.039034 | 0.0002081 | No
26/07/2023 | 09:52 | SA41 | URBAN | Overloads |  | 1.00 | 516.0 | 0.000796 | 0.0000015 | No
26/07/2023 | 09:55 | MTB11 | SHORT RURAL | Planned |  | 8.00 | 283.0 | 0.015928 | 0.0000563 | No
26/07/2023 | 09:59 | EL260B | URBAN | Third Party | Unauthorised access | 1.00 | 4,179.0 | 0.006443 | 0.0000015 | No
26/07/2023 | 10:13 | AP425B | URBAN | Asset failure | LV | 21.00 | 61.0 | 0.001975 | 0.0000324 | No
26/07/2023 | 10:20 | CM17 | LONG RURAL | Weather |  | 36.00 | 161.0 | 0.041594 | 0.0002583 | No
26/07/2023 | 11:26 | SM126E | URBAN | Overloads |  | 17.67 | 500.8 | 0.013639 | 0.0000272 | No
26/07/2023 | 11:34 | CM20 | LONG RURAL | Asset failure | LV | 1.00 | 287.0 | 0.002060 | 0.0000072 | No
26/07/2023 | 12:21 | BT26 | LONG RURAL | Planned |  | 1.00 | 109.0 | 0.000782 | 0.0000072 | No
26/07/2023 | 12:23 | NL210A | URBAN | Asset failure | LV | 6.00 | 1,119.0 | 0.010351 | 0.0000093 | No
26/07/2023 | 13:22 | SM172A | URBAN | Overloads |  | 1.00 | 228.0 | 0.000352 | 0.0000015 | No
26/07/2023 | 14:11 | AP355H | URBAN | Asset failure | LV | 66.00 | 299.0 | 0.030425 | 0.0001018 | No
26/07/2023 | 15:03 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 75.0 | 0.000528 | 0.0000070 | No
26/07/2023 | 15:25 | ST35 | LONG RURAL | Asset failure | LV | 1.00 | 159.0 | 0.001141 | 0.0000072 | No
26/07/2023 | 15:47 | AP355H | URBAN | Asset failure | LV | 1.00 | 329.0 | 0.000507 | 0.0000015 | No
26/07/2023 | 16:09 | NA57 | LONG RURAL | Asset failure | HV | 1.00 | 9.0 | 0.000065 | 0.0000072 | No
26/07/2023 | 16:17 | SM126C | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
26/07/2023 | 16:30 | EL01A | URBAN | Asset failure | LV | 1.00 | 332.0 | 0.000512 | 0.0000015 | No
26/07/2023 | 16:47 | AP355H | URBAN | Asset failure | LV | 18.00 | 144.0 | 0.003996 | 0.0000278 | No
26/07/2023 | 17:49 | VH22 | SHORT RURAL | Asset failure | LV | 101.00 | 15.0 | 0.010659 | 0.0007106 | No
26/07/2023 | 18:41 | HH107D | URBAN | Asset failure | LV | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
26/07/2023 | 19:53 | HH341E | URBAN | Asset failure | LV | 26.00 | 160.0 | 0.006414 | 0.0000401 | No
26/07/2023 | 20:40 | ME200G | URBAN | Asset failure | LV | 146.00 | 87.0 | 0.019583 | 0.0002251 | No
26/07/2023 | 21:39 | SM126C | URBAN | Unknown | Unknown | 1.00 | 277.0 | 0.000427 | 0.0000015 | No
27/07/2023 | 06:29 | ME131E | URBAN | Asset failure | LV | 1.00 | 191.0 | 0.000294 | 0.0000015 | No
27/07/2023 | 07:13 | GA745B | SHORT RURAL | Asset failure | LV | 1.67 | 292.0 | 0.003424 | 0.0000117 | No
27/07/2023 | 07:52 | MV15 | SHORT RURAL | Asset failure | LV | 1.00 | 220.0 | 0.001548 | 0.0000070 | No
27/07/2023 | 08:09 | HH409A | URBAN | Asset failure | LV | 1.67 | 89.0 | 0.000229 | 0.0000026 | No
27/07/2023 | 08:19 | BS0396 | SHORT RURAL | Planned |  | 1.00 | 375.0 | 0.002638 | 0.0000070 | No
27/07/2023 | 08:48 | KI31 | SHORT RURAL | Planned |  | 16.00 | 256.4 | 0.028860 | 0.0001126 | No
27/07/2023 | 08:49 | EL02 | URBAN | Planned |  | 108.00 | 377.0 | 0.062774 | 0.0001665 | No
27/07/2023 | 08:57 | SG09 | SHORT RURAL | Planned |  | 50.00 | 317.0 | 0.111513 | 0.0003518 | No
27/07/2023 | 09:03 | SA33 | URBAN | Planned |  | 57.00 | 363.0 | 0.031900 | 0.0000879 | No
27/07/2023 | 09:07 | BT27 | LONG RURAL | Planned |  | 2.00 | 143.0 | 0.002052 | 0.0000144 | No
27/07/2023 | 09:12 | MG12 | LONG RURAL | Planned |  | 17.00 | 174.0 | 0.021228 | 0.0001220 | No
27/07/2023 | 09:16 | EL25 | URBAN | Asset failure | LV | 2.00 | 136.0 | 0.000419 | 0.0000031 | No
27/07/2023 | 09:45 | PP04 | SHORT RURAL | Planned |  | 101.00 | 217.0 | 0.154197 | 0.0007106 | No
27/07/2023 | 09:59 | BM12 | SHORT RURAL | Asset failure | LV | 1.33 | 330.0 | 0.003096 | 0.0000094 | No
27/07/2023 | 10:09 | WK31 | SHORT RURAL | Planned |  | 5.00 | 158.0 | 0.005558 | 0.0000352 | No
27/07/2023 | 10:27 | ST42 | LONG RURAL | Planned |  | 3.00 | 252.0 | 0.005425 | 0.0000215 | No
27/07/2023 | 10:43 | EL07 | URBAN | Overloads |  | 1.00 | 230.0 | 0.000355 | 0.0000015 | No
27/07/2023 | 12:44 | HH409B | URBAN | Asset failure | LV | 1.00 | 499.0 | 0.000769 | 0.0000015 | No
27/07/2023 | 14:26 | HH118A | URBAN | Asset failure | HV | 151.00 | 54.0 | 0.012571 | 0.0002328 | No
27/07/2023 | 14:26 | HH145D | URBAN | Asset failure | LV | 11.67 | 186.0 | 0.003346 | 0.0000180 | No
27/07/2023 | 14:29 | ME131B | URBAN | Asset failure | LV | 36.00 | 201.1 | 0.011161 | 0.0000555 | No
27/07/2023 | 15:21 | M91 | LONG RURAL | Asset failure | HV | 294.00 | 488.1 | 1.029854 | 0.0021098 | No
27/07/2023 | 16:52 | VH16 | SHORT RURAL | Asset failure | LV | 116.00 | 169.0 | 0.137924 | 0.0008161 | No
27/07/2023 | 18:29 | SA33 | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
27/07/2023 | 18:41 | BM44 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 137.0 | 0.000964 | 0.0000070 | No
27/07/2023 | 18:42 | MV53 | SHORT RURAL | Unknown | Unknown | 2.00 | 367.0 | 0.005164 | 0.0000141 | No
27/07/2023 | 21:34 | AP351C | URBAN | Third Party | Vehicle impact | 36.00 | 813.0 | 0.045124 | 0.0000555 | No
27/07/2023 | 21:59 | SM374B | URBAN | Asset failure | LV | 34.67 | 152.0 | 0.008124 | 0.0000534 | No
27/07/2023 | 23:19 | HH496C | URBAN | Planned |  | 769.00 | 39.9 | 0.047262 | 0.0011856 | No
27/07/2023 | 23:34 | BT06 | LONG RURAL | Unknown | Unknown | 53.00 | 176.0 | 0.066941 | 0.0003803 | No
28/07/2023 | 00:12 | EL01L | URBAN | Overloads |  | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
28/07/2023 | 00:31 | NL210C | URBAN | Unknown | Unknown | 72.00 | 117.0 | 0.012988 | 0.0001110 | No
28/07/2023 | 02:01 | MV52 | SHORT RURAL | Unknown | Unknown | 36.00 | 425.0 | 0.107643 | 0.0002533 | No
28/07/2023 | 07:32 | KA06 | LONG RURAL | Asset failure | LV | 1.00 | 437.0 | 0.003136 | 0.0000072 | No
28/07/2023 | 08:01 | NU34 | LONG RURAL | Unknown | Unknown | 1.00 | 139.0 | 0.000998 | 0.0000072 | No
28/07/2023 | 09:02 | LX24 | SHORT RURAL | Unknown | Unknown | 4.00 | 203.8 | 0.005734 | 0.0000281 | No
28/07/2023 | 09:05 | BT33 | LONG RURAL | Planned |  | 2.00 | 108.0 | 0.001550 | 0.0000144 | No
28/07/2023 | 09:08 | CL09 | LONG RURAL | Asset failure | HV | 2.00 | 506.0 | 0.007262 | 0.0000144 | No
28/07/2023 | 09:09 | EL01L | URBAN | Planned |  | 149.00 | 152.0 | 0.034918 | 0.0002297 | No
28/07/2023 | 09:25 | MTB51 | LONG RURAL | Planned |  | 5.00 | 63.0 | 0.002261 | 0.0000359 | No
28/07/2023 | 09:27 | NL451C | URBAN | Planned |  | 211.00 | 112.6 | 0.036629 | 0.0003253 | No
28/07/2023 | 09:28 | W29 | LONG RURAL | Planned |  | 2.00 | 201.0 | 0.002885 | 0.0000144 | No
28/07/2023 | 09:29 | MG25 | LONG RURAL | Planned |  | 26.00 | 237.0 | 0.044221 | 0.0001866 | No
28/07/2023 | 10:09 | MG45 | URBAN | Third Party | Unauthorised access | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
28/07/2023 | 10:11 | NL210D | URBAN | Network business | Switching and protection error | 3,002.00 | 22.2 | 0.102719 | 0.0046283 | No
28/07/2023 | 11:00 | MT22 | LONG RURAL | Planned |  | 2.00 | 53.0 | 0.000761 | 0.0000144 | No
28/07/2023 | 11:00 | SM411A | URBAN | Asset failure | LV | 4.00 | 330.0 | 0.002035 | 0.0000062 | No
28/07/2023 | 11:37 | HH130A | URBAN | Asset failure | LV | 1.00 | 1,011.0 | 0.001559 | 0.0000015 | No
28/07/2023 | 12:04 | SM349C | URBAN | Animal | Animal impact | 872.00 | 94.8 | 0.127389 | 0.0013444 | No
28/07/2023 | 12:39 | SA16 | URBAN | Overloads |  | 1.00 | 344.0 | 0.000530 | 0.0000015 | No
28/07/2023 | 12:54 | BS0465 | SHORT RURAL | Unknown | Unknown | 1.00 | 36.0 | 0.000253 | 0.0000070 | No
28/07/2023 | 13:12 | HH409E | URBAN | Unknown | Unknown | 19.67 | 72.0 | 0.002183 | 0.0000303 | No
28/07/2023 | 13:14 | HH102D | URBAN | Asset failure | LV | 58.00 | 106.0 | 0.009479 | 0.0000894 | No
28/07/2023 | 13:28 | LX24 | SHORT RURAL | Animal | Animal impact | 1.00 | 4,350.0 | 0.030604 | 0.0000070 | No
28/07/2023 | 14:19 | HH107A | URBAN | Animal | Animal impact | 26.00 | 194.0 | 0.007777 | 0.0000401 | No
28/07/2023 | 15:22 | MG22 | LONG RURAL | Asset failure | LV | 1.00 | 222.0 | 0.001593 | 0.0000072 | No
28/07/2023 | 16:02 | HH145E | URBAN | Unknown | Unknown | 96.00 | 141.0 | 0.020869 | 0.0001480 | No
28/07/2023 | 16:43 | EL14 | URBAN | Third Party | Unauthorised access | 1.00 | 226.0 | 0.000348 | 0.0000015 | No
28/07/2023 | 17:04 | YK19 | LONG RURAL | Weather |  | 10.00 | 59.0 | 0.004234 | 0.0000718 | No
28/07/2023 | 17:39 | SM126D | URBAN | Asset failure | LV | 8.67 | 184.0 | 0.002459 | 0.0000134 | No
28/07/2023 | 17:40 | SM126C | URBAN | Asset failure | LV | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
28/07/2023 | 17:52 | NL210A | URBAN | Asset failure | LV | 8.67 | 441.0 | 0.005893 | 0.0000134 | No
28/07/2023 | 18:20 | NL115D | URBAN | Asset failure | LV | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
28/07/2023 | 19:21 | HH102D | URBAN | Asset failure | LV | 12.00 | 639.0 | 0.011822 | 0.0000185 | No
28/07/2023 | 19:34 | M42 | LONG RURAL | Asset failure | HV | 1.00 | 53.0 | 0.000380 | 0.0000072 | No
28/07/2023 | 19:43 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 166.0 | 0.001168 | 0.0000070 | No
28/07/2023 | 20:13 | HH341E | URBAN | Asset failure | LV | 2.00 | 102.0 | 0.000315 | 0.0000031 | No
28/07/2023 | 20:26 | MV12 | URBAN | Asset failure | HV | 2.00 | 38.0 | 0.000117 | 0.0000031 | No
28/07/2023 | 20:30 | EL09 | URBAN | Asset failure | LV | 1.00 | 292.0 | 0.000450 | 0.0000015 | No
28/07/2023 | 21:19 | AP214C | URBAN | Asset failure | LV | 109.00 | 288.0 | 0.048399 | 0.0001681 | No
28/07/2023 | 23:53 | R12 | LONG RURAL | Unknown | Unknown | 1.00 | 206.0 | 0.001478 | 0.0000072 | No
29/07/2023 | 07:08 | HH177B | URBAN | Overloads |  | 27.33 | 210.0 | 0.008850 | 0.0000421 | No
29/07/2023 | 07:10 | AP214A | URBAN | Asset failure | LV | 18.00 | 212.0 | 0.005883 | 0.0000278 | No
29/07/2023 | 07:43 | MV53 | SHORT RURAL | Unknown | Unknown | 159.00 | 11.8 | 0.013185 | 0.0011186 | No
29/07/2023 | 07:46 | AP424F | URBAN | Asset failure | LV | 21.00 | 165.0 | 0.005342 | 0.0000324 | No
29/07/2023 | 09:44 | NU25 | LONG RURAL | Asset failure | LV | 10.00 | 47.0 | 0.003373 | 0.0000718 | No
29/07/2023 | 10:06 | R18 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 658.00 | 179.0 | 0.845242 | 0.0047220 | No
29/07/2023 | 10:39 | HH428D | URBAN | Asset failure | LV | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
29/07/2023 | 10:56 | HH177B | URBAN | Asset failure | LV | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
29/07/2023 | 11:11 | YK27 | LONG RURAL | Asset failure | LV | 1.00 | 333.0 | 0.002390 | 0.0000072 | No
29/07/2023 | 11:17 | HH177B | URBAN | Asset failure | LV | 22.00 | 62.0 | 0.002103 | 0.0000339 | No
29/07/2023 | 11:57 | AP355A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
29/07/2023 | 12:01 | SSD250 | LONG RURAL | Planned |  | 802.00 | 6.0 | 0.034532 | 0.0057554 | No
29/07/2023 | 12:01 | SSD250 | SHORT RURAL | Planned |  | 1,450.00 | 6.2 | 0.063355 | 0.0102015 | No
29/07/2023 | 12:03 | MG11 | SHORT RURAL | Asset failure | LV | 1.00 | 162.0 | 0.001140 | 0.0000070 | No
29/07/2023 | 12:38 | ST41 | LONG RURAL | Unknown | Unknown | 15.33 | 149.0 | 0.016396 | 0.0001100 | No
29/07/2023 | 12:55 | SA744C | URBAN | Asset failure | LV | 3.00 | 201.0 | 0.000930 | 0.0000046 | No
29/07/2023 | 13:03 | NL760B | URBAN | Asset failure | LV | 8.00 | 392.0 | 0.004835 | 0.0000123 | No
29/07/2023 | 13:05 | ST23 | SHORT RURAL | Unknown | Unknown | 8.00 | 421.0 | 0.023696 | 0.0000563 | No
29/07/2023 | 13:29 | EL01A | URBAN | Asset failure | LV | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
29/07/2023 | 14:11 | ME231A | URBAN | Asset failure | LV | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
29/07/2023 | 14:30 | KI21 | LONG RURAL | Asset failure | LV | 2.00 | 200.0 | 0.002871 | 0.0000144 | No
29/07/2023 | 14:39 | AP149F | URBAN | Asset failure | LV | 1.00 | 397.0 | 0.000612 | 0.0000015 | No
29/07/2023 | 16:42 | AP227C | URBAN | Overloads |  | 6.67 | 217.0 | 0.002230 | 0.0000103 | No
29/07/2023 | 16:52 | NL210E | URBAN | Unknown | Unknown | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
29/07/2023 | 17:55 | WHY09 | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
29/07/2023 | 20:21 | EL01R | URBAN | Asset failure | LV | 9.00 | 547.0 | 0.007590 | 0.0000139 | No
29/07/2023 | 22:26 | HH432G | URBAN | Planned |  | 1.00 | 339.0 | 0.000523 | 0.0000015 | No
30/07/2023 | 01:55 | HH432F | URBAN | Asset failure | LV | 7.00 | 104.0 | 0.001122 | 0.0000108 | No
30/07/2023 | 06:17 | MI08 | LONG RURAL | Overloads |  | 1.00 | 629.0 | 0.004514 | 0.0000072 | No
30/07/2023 | 08:00 | SSD318 | LONG RURAL | Planned |  | 887.00 | 433.0 | 2.756220 | 0.0063654 | No
30/07/2023 | 08:00 | SSD318 | SHORT RURAL | Planned |  | 1,419.00 | 434.1 | 4.333320 | 0.0099834 | No
30/07/2023 | 08:16 | HH341J | URBAN | Asset failure | LV | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
30/07/2023 | 08:19 | NL760C | URBAN | Planned |  | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
30/07/2023 | 08:31 | SA13 | URBAN | Planned |  | 121.00 | 226.6 | 0.042269 | 0.0001866 | No
30/07/2023 | 08:34 | SD54300 | LONG RURAL | Planned |  | 880.00 | 274.0 | 1.730357 | 0.0063152 | No
30/07/2023 | 08:34 | GA02 | SHORT RURAL | Planned |  | 111.00 | 215.1 | 0.168008 | 0.0007809 | No
30/07/2023 | 08:36 | SA14 | URBAN | Planned |  | 2.00 | 24.0 | 0.000074 | 0.0000031 | No
30/07/2023 | 08:44 | AP344F | URBAN | Asset failure | LV | 11.67 | 128.0 | 0.002302 | 0.0000180 | No
30/07/2023 | 08:52 | MB28 | SHORT RURAL | Animal | Animal impact | 4.00 | 250.0 | 0.007035 | 0.0000281 | No
30/07/2023 | 08:55 | CV25 | LONG RURAL | Planned |  | 2.00 | 275.0 | 0.003947 | 0.0000144 | No
30/07/2023 | 09:04 | AP355F | URBAN | Planned |  | 29.00 | 209.3 | 0.009358 | 0.0000447 | No
30/07/2023 | 09:06 | BS0198 | URBAN | Unknown | Unknown | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
30/07/2023 | 09:59 | AP149E | URBAN | Asset failure | LV | 4.00 | 252.0 | 0.001554 | 0.0000062 | No
30/07/2023 | 10:21 | HH522B | URBAN | Asset failure | LV | 1.00 | 359.0 | 0.000553 | 0.0000015 | No
30/07/2023 | 11:15 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 402.0 | 0.002828 | 0.0000070 | No
30/07/2023 | 11:15 | SD44300 | LONG RURAL | Weather |  | 1,060.00 | 148.7 | 1.131126 | 0.0076069 | No
30/07/2023 | 14:26 | NL210A | URBAN | Asset failure | LV | 1.00 | 469.0 | 0.000723 | 0.0000015 | No
30/07/2023 | 15:18 | HH121F | URBAN | Overloads |  | 14.67 | 110.0 | 0.002487 | 0.0000226 | No
30/07/2023 | 17:13 | ME347C | URBAN | Asset failure | LV | 25.00 | 34.0 | 0.001310 | 0.0000385 | No
30/07/2023 | 18:11 | HH121D | URBAN | Asset failure | LV | 27.33 | 98.0 | 0.004130 | 0.0000421 | No
30/07/2023 | 18:14 | HH121D | URBAN | Asset failure | LV | 1.00 | 97.0 | 0.000150 | 0.0000015 | No
30/07/2023 | 18:49 | HH177D | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
30/07/2023 | 19:29 | SD53100 | LONG RURAL | Asset failure | Subtransmission | 47.00 | 352.0 | 0.118725 | 0.0003373 | No
30/07/2023 | 19:50 | R02 | LONG RURAL | Asset failure | LV | 1.00 | 191.0 | 0.001371 | 0.0000072 | No
30/07/2023 | 20:16 | PL27 | LONG RURAL | Asset failure | LV | 13.00 | 14.0 | 0.001306 | 0.0000933 | No
30/07/2023 | 20:55 | MG26 | LONG RURAL | Unknown | Unknown | 12.00 | 128.0 | 0.011023 | 0.0000861 | No
30/07/2023 | 21:29 | EL01M | URBAN | Asset failure | LV | 6.00 | 4.0 | 0.000037 | 0.0000093 | No
30/07/2023 | 21:52 | SA520E | URBAN | Asset failure | LV | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
30/07/2023 | 22:09 | MB41 | LONG RURAL | Asset failure | LV | 29.00 | 214.0 | 0.044536 | 0.0002081 | No
30/07/2023 | 23:00 | AP425D | URBAN | Overloads |  | 1.00 | 268.0 | 0.000413 | 0.0000015 | No
31/07/2023 | 00:59 | MG37 | LONG RURAL | Asset failure | LV | 5.67 | 496.0 | 0.020170 | 0.0000407 | No
31/07/2023 | 06:33 | WHY12 | URBAN | Unknown | Unknown | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
31/07/2023 | 07:19 | SA744D | URBAN | Asset failure | LV | 8.00 | 205.5 | 0.002535 | 0.0000123 | No
31/07/2023 | 07:42 | HH177C | URBAN | Overloads |  | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
31/07/2023 | 08:47 | ME347B | URBAN | Asset failure | LV | 66.00 | 179.0 | 0.018219 | 0.0001018 | No
31/07/2023 | 08:53 | HH386G | URBAN | Planned |  | 99.00 | 306.0 | 0.046706 | 0.0001526 | No
31/07/2023 | 08:53 | GU13 | LONG RURAL | Planned |  | 18.00 | 365.6 | 0.047220 | 0.0001292 | No
31/07/2023 | 09:03 | CL14 | LONG RURAL | Planned |  | 5.00 | 80.0 | 0.002871 | 0.0000359 | No
31/07/2023 | 09:05 | MV61 | SHORT RURAL | Planned |  | 162.00 | 79.0 | 0.090012 | 0.0011397 | No
31/07/2023 | 09:05 | MV61 | URBAN | Planned |  | 31.00 | 52.0 | 0.002485 | 0.0000478 | No
31/07/2023 | 09:18 | PL04 | URBAN | Planned |  | 83.00 | 330.2 | 0.042250 | 0.0001280 | No
31/07/2023 | 09:22 | SA31 | URBAN | Asset failure | HV | 302.00 | 289.6 | 0.134826 | 0.0004656 | No
31/07/2023 | 09:45 | BT22 | LONG RURAL | Planned |  | 3.00 | 247.0 | 0.005318 | 0.0000215 | No
31/07/2023 | 10:13 | HH107A | URBAN | Asset failure | LV | 20.00 | 81.0 | 0.002498 | 0.0000308 | No
31/07/2023 | 10:32 | MB12 | SHORT RURAL | Planned |  | 13.00 | 110.0 | 0.010061 | 0.0000915 | No
31/07/2023 | 11:25 | SM179A | URBAN | Overloads |  | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
31/07/2023 | 11:46 | NA13 | LONG RURAL | Weather |  | 14.00 | 82.0 | 0.008238 | 0.0001005 | No
31/07/2023 | 12:01 | G18 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 4.0 | 0.000029 | 0.0000072 | No
31/07/2023 | 12:21 | CM03 | LONG RURAL | Unknown | Unknown | 14.00 | 316.0 | 0.031748 | 0.0001005 | No
31/07/2023 | 12:35 | ME231A | URBAN | Asset failure | LV | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
31/07/2023 | 12:55 | VH15 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 87.0 | 0.000612 | 0.0000070 | No
31/07/2023 | 13:15 | MI03 | LONG RURAL | Weather |  | 10.00 | 414.0 | 0.029710 | 0.0000718 | No
31/07/2023 | 14:09 | CV17 | LONG RURAL | Asset failure | HV | 47.00 | 25.0 | 0.008432 | 0.0003373 | No
31/07/2023 | 14:10 | AP149B | URBAN | Asset failure | LV | 1.00 | 202.0 | 0.000311 | 0.0000015 | No
31/07/2023 | 14:33 | PL29 | LONG RURAL | Unknown | Unknown | 1.00 | 365.0 | 0.002619 | 0.0000072 | No
31/07/2023 | 14:51 | NL451E | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
31/07/2023 | 15:46 | MTB14 | SHORT RURAL | Weather |  | 4.00 | 82.0 | 0.002308 | 0.0000281 | No
31/07/2023 | 16:10 | WK31 | SHORT RURAL | Asset failure | LV | 2.00 | 1,290.0 | 0.018152 | 0.0000141 | No
31/07/2023 | 16:20 | CV25 | LONG RURAL | Asset failure | LV | 1.00 | 116.0 | 0.000832 | 0.0000072 | No
31/07/2023 | 16:25 | CL05 | LONG RURAL | Asset failure | HV | 1.00 | 70.0 | 0.000502 | 0.0000072 | No
31/07/2023 | 16:41 | HH409F | URBAN | Asset failure | LV | 44.00 | 141.0 | 0.009565 | 0.0000678 | No
31/07/2023 | 17:24 | WK32 | SHORT RURAL | Unknown | Unknown | 119.00 | 5.3 | 0.004397 | 0.0008372 | No
31/07/2023 | 17:57 | SM349C | URBAN | Unknown | Unknown | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
31/07/2023 | 17:57 | NL111C | URBAN | Asset failure | LV | 7.00 | 194.0 | 0.002094 | 0.0000108 | No
31/07/2023 | 18:36 | BM51 | URBAN | Asset failure | LV | 39.00 | 185.0 | 0.011124 | 0.0000601 | No
31/07/2023 | 18:52 | HH428B | URBAN | Asset failure | LV | 1.00 | 501.0 | 0.000772 | 0.0000015 | No
31/07/2023 | 19:33 | NL234A | URBAN | Asset failure | LV | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
31/07/2023 | 19:38 | AP529D | URBAN | Asset failure | LV | 1.00 | 330.0 | 0.000509 | 0.0000015 | No
31/07/2023 | 20:39 | HH341D | URBAN | Third Party | Vehicle impact | 1.00 | 68.0 | 0.000105 | 0.0000015 | No
31/07/2023 | 21:39 | HH409F | URBAN | Asset failure | HV | 29.33 | 977.0 | 0.044185 | 0.0000452 | No
31/07/2023 | 23:38 | SA14 | URBAN | Overloads |  | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
01/08/2023 | 01:14 | SG14 | SHORT RURAL | Asset failure | LV | 1.00 | 633.0 | 0.004453 | 0.0000070 | No
01/08/2023 | 07:23 | CV753A | LONG RURAL | Asset failure | LV | 23.00 | 159.2 | 0.026273 | 0.0001651 | No
01/08/2023 | 07:37 | BT15 | LONG RURAL | Asset failure | LV | 7.00 | 554.0 | 0.027830 | 0.0000502 | No
01/08/2023 | 08:09 | HH432B | URBAN | Asset failure | LV | 1.00 | 217.0 | 0.000335 | 0.0000015 | No
01/08/2023 | 08:22 | AP355H | URBAN | Planned |  | 51.00 | 274.6 | 0.021595 | 0.0000786 | No
01/08/2023 | 08:25 | CL25 | LONG RURAL | Planned |  | 105.00 | 382.2 | 0.288029 | 0.0007535 | No
01/08/2023 | 08:47 | GA26 | URBAN | Planned |  | 35.00 | 324.4 | 0.017505 | 0.0000540 | No
01/08/2023 | 09:01 | PL803A | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
01/08/2023 | 09:13 | CD15 | LONG RURAL | Planned |  | 25.00 | 262.0 | 0.047005 | 0.0001794 | No
01/08/2023 | 09:17 | VH22 | SHORT RURAL | Planned |  | 26.00 | 344.2 | 0.062968 | 0.0001829 | No
01/08/2023 | 09:25 | YK03 | LONG RURAL | Planned |  | 281.00 | 224.0 | 0.451707 | 0.0020165 | No
01/08/2023 | 09:37 | SB17 | LONG RURAL | Planned |  | 161.00 | 115.0 | 0.132870 | 0.0011554 | No
01/08/2023 | 09:44 | W18 | LONG RURAL | Planned |  | 59.00 | 321.0 | 0.135913 | 0.0004234 | No
01/08/2023 | 10:24 | WK32 | SHORT RURAL | Asset failure | HV | 97.67 | 83.5 | 0.057389 | 0.0006871 | No
01/08/2023 | 10:57 | CV01 | SHORT RURAL | Asset failure | LV | 1.00 | 551.0 | 0.003877 | 0.0000070 | No
01/08/2023 | 11:35 | PL29 | LONG RURAL | Animal | Animal impact | 89.00 | 146.4 | 0.093486 | 0.0006387 | No
01/08/2023 | 11:56 | AP125C | URBAN | Asset failure | LV | 3.00 | 468.0 | 0.002165 | 0.0000046 | No
01/08/2023 | 11:59 | SD31100 | LONG RURAL | Network business | Switching and protection error | 1,249.00 | 22.0 | 0.197191 | 0.0089632 | No
01/08/2023 | 12:19 | PP03 | URBAN | Asset failure | LV | 1.00 | 153.0 | 0.000236 | 0.0000015 | No
01/08/2023 | 12:51 | SA16 | URBAN | Asset failure | LV | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
01/08/2023 | 13:00 | SA744H | URBAN | Planned |  | 1.00 | 29.0 | 0.000045 | 0.0000015 | No
01/08/2023 | 14:07 | SD31100 | LONG RURAL | Animal | Animal impact | 1,250.00 | 5.2 | 0.046603 | 0.0089704 | No
01/08/2023 | 14:50 | HH118A | URBAN | Asset failure | LV | 1.00 | 395.0 | 0.000609 | 0.0000015 | No
01/08/2023 | 15:08 | BT03 | LONG RURAL | Unknown | Unknown | 368.00 | 87.0 | 0.229664 | 0.0026409 | No
01/08/2023 | 15:27 | GA26 | URBAN | Asset failure | LV | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
01/08/2023 | 16:31 | SA14 | URBAN | Asset failure | LV | 1.00 | 308.0 | 0.000475 | 0.0000015 | No
01/08/2023 | 17:01 | MB13 | SHORT RURAL | Asset failure | HV | 121.00 | 104.9 | 0.089266 | 0.0008513 | No
01/08/2023 | 17:21 | AP425D | URBAN | Asset failure | LV | 88.00 | 17.0 | 0.002306 | 0.0001357 | No
01/08/2023 | 17:45 | EL10 | URBAN | Overloads |  | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
01/08/2023 | 17:59 | HH409C | URBAN | Asset failure | LV | 60.00 | 267.0 | 0.024699 | 0.0000925 | No
01/08/2023 | 18:04 | SA711C | URBAN | Asset failure | LV | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
01/08/2023 | 19:40 | SA17 | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
02/08/2023 | 08:35 | PL11 | LONG RURAL | Planned |  | 12.00 | 247.0 | 0.021271 | 0.0000861 | No
02/08/2023 | 08:35 | VH71 | SHORT RURAL | Planned |  | 374.00 | 315.4 | 0.829857 | 0.0026313 | No
02/08/2023 | 08:40 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 270.0 | 0.001900 | 0.0000070 | No
02/08/2023 | 08:48 | GA26 | URBAN | Planned |  | 143.00 | 189.4 | 0.041757 | 0.0002205 | No
02/08/2023 | 09:06 | SD40200 | LONG RURAL | Planned |  | 1.00 | 44.0 | 0.000316 | 0.0000072 | No
02/08/2023 | 09:10 | BM31 | SHORT RURAL | Planned |  | 56.00 | 297.8 | 0.117345 | 0.0003940 | No
02/08/2023 | 09:30 | KI21 | LONG RURAL | Planned |  | 196.00 | 301.0 | 0.423375 | 0.0014066 | No
02/08/2023 | 09:42 | MV42 | SHORT RURAL | Planned |  | 135.00 | 290.3 | 0.275742 | 0.0009498 | No
02/08/2023 | 09:59 | ST11 | SHORT RURAL | Planned |  | 2.00 | 122.0 | 0.001717 | 0.0000141 | No
02/08/2023 | 10:15 | GU13 | LONG RURAL | Planned |  | 2.00 | 99.0 | 0.001421 | 0.0000144 | No
02/08/2023 | 10:36 | HH121D | URBAN | Asset failure | LV | 1.00 | 1,927.0 | 0.002971 | 0.0000015 | No
02/08/2023 | 11:12 | AP139C | URBAN | Asset failure | HV | 933.00 | 6.0 | 0.008631 | 0.0014385 | No
02/08/2023 | 11:33 | CBD27F | CBD | Asset failure | LV | 1.00 | 34.0 | 0.004912 | 0.0001445 | No
02/08/2023 | 11:38 | R09 | LONG RURAL | Unknown | Unknown | 9.00 | 1,816.0 | 0.117290 | 0.0000646 | No
02/08/2023 | 11:42 | SD33200 | LONG RURAL | Planned |  | 2.00 | 211.0 | 0.003028 | 0.0000144 | No
02/08/2023 | 12:20 | AP355H | URBAN | Asset failure | LV | 4.00 | 57.0 | 0.000352 | 0.0000062 | No
02/08/2023 | 13:22 | MT06 | LONG RURAL | Overloads |  | 1.00 | 141.0 | 0.001012 | 0.0000072 | No
02/08/2023 | 14:03 | AP125D | URBAN | Asset failure | LV | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
02/08/2023 | 14:29 | SA18 | URBAN | Asset failure | LV | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
02/08/2023 | 14:49 | KA16 | LONG RURAL | Weather |  | 30.00 | 33.9 | 0.007291 | 0.0002153 | No
02/08/2023 | 16:53 | SA31 | URBAN | Asset failure | LV | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
02/08/2023 | 17:56 | ST23 | SHORT RURAL | Unknown | Unknown | 8.00 | 216.0 | 0.012157 | 0.0000563 | No
02/08/2023 | 18:11 | VH15 | SHORT RURAL | Asset failure | LV | 60.00 | 95.0 | 0.040102 | 0.0004221 | No
02/08/2023 | 18:26 | HH522C | URBAN | Asset failure | LV | 1.00 | 159.0 | 0.000245 | 0.0000015 | No
02/08/2023 | 18:54 | MTB11 | SHORT RURAL | Asset failure | LV | 13.33 | 27.0 | 0.002533 | 0.0000938 | No
02/08/2023 | 21:42 | SM349A | URBAN | Planned |  | 204.00 | 496.0 | 0.156001 | 0.0003145 | No
02/08/2023 | 23:08 | MV12 | SHORT RURAL | Planned |  | 1.00 | 264.0 | 0.001857 | 0.0000070 | No
02/08/2023 | 23:08 | MV12 | URBAN | Planned |  | 78.00 | 264.0 | 0.031748 | 0.0001203 | No
03/08/2023 | 04:46 | PL27 | LONG RURAL | Asset failure | HV | 148.00 | 436.0 | 0.463074 | 0.0010621 | No
03/08/2023 | 06:09 | HH403A | URBAN | Third Party | Vehicle impact | 84.00 | 1,132.8 | 0.146701 | 0.0001295 | No
03/08/2023 | 07:27 | HH496C | URBAN | Asset failure | LV | 1.00 | 447.0 | 0.000689 | 0.0000015 | No
03/08/2023 | 07:41 | ST12 | SHORT RURAL | Asset failure | LV | 2.33 | 105.0 | 0.001724 | 0.0000164 | No
03/08/2023 | 07:45 | PL28 | LONG RURAL | Asset failure | HV | 94.00 | 308.0 | 0.207769 | 0.0006746 | No
03/08/2023 | 07:46 | BT03 | LONG RURAL | Unknown | Unknown | 18.00 | 229.0 | 0.029581 | 0.0001292 | No
03/08/2023 | 08:05 | AP355H | URBAN | Planned |  | 102.00 | 172.0 | 0.027049 | 0.0001573 | No
03/08/2023 | 08:51 | GA26 | URBAN | Planned |  | 51.00 | 157.0 | 0.012345 | 0.0000786 | No
03/08/2023 | 09:00 | EL260A | URBAN | Planned |  | 85.00 | 253.0 | 0.033155 | 0.0001310 | No
03/08/2023 | 09:09 | G31 | LONG RURAL | Planned |  | 60.00 | 238.0 | 0.102478 | 0.0004306 | No
03/08/2023 | 11:13 | WK81 | SHORT RURAL | Asset failure | HV | 3.33 | 54.0 | 0.001266 | 0.0000235 | No
03/08/2023 | 11:31 | W31 | SHORT RURAL | Planned |  | 1.00 | 140.0 | 0.000985 | 0.0000070 | No
03/08/2023 | 13:52 | MI02 | SHORT RURAL | Asset failure | HV | 227.00 | 207.0 | 0.330591 | 0.0015971 | No
03/08/2023 | 13:52 | MI02 | SHORT RURAL | Asset failure | HV | 20.00 | 272.4 | 0.038329 | 0.0001407 | No
03/08/2023 | 14:16 | SM402D | URBAN | Unknown | Unknown | 4.00 | 166.0 | 0.001024 | 0.0000062 | No
03/08/2023 | 14:20 | R29 | LONG RURAL | Asset failure | HV | 2.00 | 26.0 | 0.000373 | 0.0000144 | No
03/08/2023 | 14:56 | BT03 | LONG RURAL | Asset failure | HV | 1.00 | 4,213.0 | 0.030234 | 0.0000072 | No
03/08/2023 | 14:57 | HH148A | URBAN | Asset failure | LV | 1.00 | 557.0 | 0.000859 | 0.0000015 | No
03/08/2023 | 16:51 | NL210E | URBAN | Overloads |  | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
03/08/2023 | 17:21 | AP355A | URBAN | Unknown | Unknown | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
03/08/2023 | 17:28 | HH148A | URBAN | Asset failure | LV | 3.33 | 45.0 | 0.000231 | 0.0000051 | No
03/08/2023 | 17:41 | R09 | LONG RURAL | Asset failure | HV | 1.00 | 5.0 | 0.000036 | 0.0000072 | No
03/08/2023 | 17:49 | HH409E | URBAN | Asset failure | LV | 1.00 | 20.0 | 0.000031 | 0.0000015 | No
03/08/2023 | 18:55 | NL111C | URBAN | Planned |  | 2.00 | 15.0 | 0.000046 | 0.0000031 | No
03/08/2023 | 21:44 | SG07 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 13.00 | 450.0 | 0.041158 | 0.0000915 | No
04/08/2023 | 00:14 | MV53 | SHORT RURAL | Unknown | Unknown | 2.00 | 191.0 | 0.002688 | 0.0000141 | No
04/08/2023 | 02:29 | AP227A | URBAN | Asset failure | LV | 6.00 | 140.0 | 0.001295 | 0.0000093 | No
04/08/2023 | 07:31 | GA15 | SHORT RURAL | Weather |  | 655.00 | 163.1 | 0.751820 | 0.0046082 | No
04/08/2023 | 07:51 | HH341C | URBAN | Unknown | Unknown | 4.00 | 60.0 | 0.000370 | 0.0000062 | No
04/08/2023 | 08:32 | VH15 | SHORT RURAL | Planned |  | 30.00 | 299.6 | 0.063235 | 0.0002111 | No
04/08/2023 | 08:36 | PL14 | URBAN | Planned |  | 17.00 | 215.3 | 0.005643 | 0.0000262 | No
04/08/2023 | 09:25 | SB19 | LONG RURAL | Planned |  | 57.00 | 186.7 | 0.076356 | 0.0004091 | No
04/08/2023 | 09:28 | CV25 | LONG RURAL | Planned |  | 3.00 | 151.0 | 0.003251 | 0.0000215 | No
04/08/2023 | 09:30 | EL23 | URBAN | Planned |  | 63.00 | 176.0 | 0.017095 | 0.0000971 | No
04/08/2023 | 10:01 | VH15 | SHORT RURAL | Unknown | Unknown | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
04/08/2023 | 10:13 | SA17 | URBAN | Planned |  | 58.00 | 43.0 | 0.003845 | 0.0000894 | No
04/08/2023 | 10:59 | AP351C | URBAN | Planned |  | 64.00 | 197.0 | 0.019438 | 0.0000987 | No
04/08/2023 | 11:00 | CN81 | LONG RURAL | Other |  | 282.00 | 17.5 | 0.035351 | 0.0020237 | No
04/08/2023 | 11:03 | MG05 | LONG RURAL | Asset failure | LV | 1.00 | 213.0 | 0.001529 | 0.0000072 | No
04/08/2023 | 11:39 | LX75 | LONG RURAL | Planned |  | 1.00 | 49.0 | 0.000352 | 0.0000072 | No
04/08/2023 | 11:50 | KI55 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 74.00 | 251.0 | 0.133293 | 0.0005310 | No
04/08/2023 | 11:52 | HH341C | URBAN | Asset failure | LV | 4.00 | 111.0 | 0.000685 | 0.0000062 | No
04/08/2023 | 12:08 | KA19 | LONG RURAL | Asset failure | LV | 2.00 | 153.0 | 0.002196 | 0.0000144 | No
04/08/2023 | 12:34 | MTB61 | SHORT RURAL | Asset failure | LV | 1.00 | 77.0 | 0.000542 | 0.0000070 | No
04/08/2023 | 12:46 | MB62 | LONG RURAL | Unknown | Unknown | 1.00 | 4,219.0 | 0.030277 | 0.0000072 | No
04/08/2023 | 12:49 | HH121A | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
04/08/2023 | 12:54 | ME347G | URBAN | Unknown | Unknown | 62.00 | 549.0 | 0.052478 | 0.0000956 | No
04/08/2023 | 13:07 | VH72 | SHORT RURAL | Asset failure | LV | 1.00 | 210.0 | 0.001477 | 0.0000070 | No
04/08/2023 | 13:07 | SM349E | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
04/08/2023 | 13:46 | SG09 | SHORT RURAL | Overloads |  | 1.00 | 365.0 | 0.002568 | 0.0000070 | No
04/08/2023 | 13:48 | NL511B | URBAN | Asset failure | LV | 28.00 | 58.3 | 0.002516 | 0.0000432 | No
04/08/2023 | 14:03 | SM410A | URBAN | Asset failure | LV | 5.00 | 439.0 | 0.003384 | 0.0000077 | No
04/08/2023 | 14:44 | CV753A | LONG RURAL | Overloads |  | 1.00 | 172.0 | 0.001234 | 0.0000072 | No
04/08/2023 | 15:07 | AP226D | URBAN | Unknown | Unknown | 1.00 | 282.0 | 0.000435 | 0.0000015 | No
04/08/2023 | 15:37 | GA01 | URBAN | Third Party | Vehicle impact | 157.00 | 632.8 | 0.153162 | 0.0002421 | No
04/08/2023 | 15:46 | WHY12 | URBAN | Overloads |  | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
04/08/2023 | 16:22 | SM137A | URBAN | Asset failure | LV | 1.00 | 375.0 | 0.000578 | 0.0000015 | No
04/08/2023 | 16:42 | SD39300 | LONG RURAL | Asset failure | Subtransmission | 3.00 | 3,966.0 | 0.085384 | 0.0000215 | No
04/08/2023 | 17:36 | NL760B | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
04/08/2023 | 17:36 | SM349F | URBAN | Asset failure | LV | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
04/08/2023 | 17:50 | AP355B | URBAN | Unknown | Unknown | 1.00 | 162.0 | 0.000250 | 0.0000015 | No
04/08/2023 | 18:15 | AP355B | URBAN | Unknown | Unknown | 2.00 | 146.0 | 0.000450 | 0.0000031 | No
04/08/2023 | 18:16 | M21 | LONG RURAL | Other |  | 1.00 | 3,865.0 | 0.027737 | 0.0000072 | No
04/08/2023 | 18:26 | HH145B | URBAN | Asset failure | LV | 1.00 | 369.0 | 0.000569 | 0.0000015 | No
04/08/2023 | 20:17 | AP226D | URBAN | Unknown | Unknown | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
04/08/2023 | 22:41 | NL210D | URBAN | Asset failure | LV | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
05/08/2023 | 00:41 | NL760C | URBAN | Asset failure | HV | 671.00 | 205.0 | 0.212076 | 0.0010345 | No
05/08/2023 | 03:40 | EL01N | URBAN | Asset failure | LV | 1.00 | 660.0 | 0.001018 | 0.0000015 | No
05/08/2023 | 07:13 | PL01 | URBAN | Overloads |  | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
05/08/2023 | 09:02 | ME347G | URBAN | Asset failure | LV | 20.67 | 257.0 | 0.008189 | 0.0000319 | No
05/08/2023 | 09:10 | HH496F | URBAN | Unknown | Unknown | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
05/08/2023 | 09:41 | EL260A | URBAN | Unknown | Unknown | 10.67 | 211.0 | 0.003470 | 0.0000164 | No
05/08/2023 | 11:28 | SM411E | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
05/08/2023 | 12:22 | VH12 | SHORT RURAL | Asset failure | LV | 1.00 | 191.0 | 0.001344 | 0.0000070 | No
05/08/2023 | 12:50 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 105.0 | 0.000739 | 0.0000070 | No
05/08/2023 | 13:14 | HH386D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
05/08/2023 | 14:33 | NL115D | URBAN | Asset failure | LV | 1.00 | 64.0 | 0.000099 | 0.0000015 | No
05/08/2023 | 15:22 | SG02 | SHORT RURAL | Asset failure | LV | 1.00 | 253.0 | 0.001780 | 0.0000070 | No
05/08/2023 | 16:27 | AP132B | URBAN | Overloads |  | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
05/08/2023 | 18:32 | MI09 | LONG RURAL | Asset failure | HV | 3.00 | 935.0 | 0.020130 | 0.0000215 | No
05/08/2023 | 18:48 | PP08 | LONG RURAL | Asset failure | LV | 12.33 | 111.0 | 0.009824 | 0.0000885 | No
05/08/2023 | 19:08 | HH386D | URBAN | Asset failure | LV | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
05/08/2023 | 19:49 | SA744D | URBAN | Asset failure | LV | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
05/08/2023 | 21:15 | EL10 | URBAN | Unknown | Unknown | 5.00 | 47.0 | 0.000362 | 0.0000077 | No
05/08/2023 | 21:30 | MI12 | LONG RURAL | Weather |  | 79.00 | 31.0 | 0.017575 | 0.0005669 | No
05/08/2023 | 22:18 | EL10 | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
06/08/2023 | 04:15 | EL18 | URBAN | Overloads |  | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
06/08/2023 | 04:49 | EL18 | URBAN | Overloads |  | 1.00 | 114.0 | 0.000176 | 0.0000015 | No
06/08/2023 | 04:49 | EL18 | URBAN | Overloads |  | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
06/08/2023 | 04:57 | EL18 | URBAN | Overloads |  | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
06/08/2023 | 08:28 | ME116A | URBAN | Planned |  | 123.00 | 234.0 | 0.044375 | 0.0001896 | No
06/08/2023 | 09:01 | EL04 | URBAN | Planned |  | 10.00 | 284.6 | 0.004388 | 0.0000154 | No
06/08/2023 | 09:04 | HH121F | URBAN | Planned |  | 233.00 | 162.0 | 0.058206 | 0.0003592 | No
06/08/2023 | 09:17 | BT03 | LONG RURAL | Planned |  | 17.00 | 223.0 | 0.027205 | 0.0001220 | No
06/08/2023 | 09:21 | CV08 | LONG RURAL | Planned |  | 664.00 | 355.6 | 1.694446 | 0.0047651 | No
06/08/2023 | 10:11 | WK31 | SHORT RURAL | Asset failure | LV | 10.00 | 49.0 | 0.003447 | 0.0000704 | No
06/08/2023 | 11:05 | NL511A | URBAN | Third Party | Other | 27.00 | 93.0 | 0.003871 | 0.0000416 | No
06/08/2023 | 11:37 | SM137A | URBAN | Third Party | Unauthorised access | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
06/08/2023 | 11:55 | SD54300 | LONG RURAL | Asset failure | Subtransmission | 2.00 | 102.0 | 0.001464 | 0.0000144 | No
06/08/2023 | 13:14 | MG18 | LONG RURAL | Overloads |  | 1.00 | 212.0 | 0.001521 | 0.0000072 | No
06/08/2023 | 13:16 | HH496D | URBAN | Asset failure | LV | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
06/08/2023 | 13:21 | LX43 | SHORT RURAL | Unknown | Unknown | 17.00 | 70.0 | 0.008372 | 0.0001196 | No
06/08/2023 | 13:54 | HH130F | URBAN | Asset failure | LV | 9.33 | 384.4 | 0.005532 | 0.0000144 | No
06/08/2023 | 14:47 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 194.0 | 0.001365 | 0.0000070 | No
06/08/2023 | 17:28 | BT04 | LONG RURAL | Unknown | Unknown | 9.33 | 269.0 | 0.018017 | 0.0000670 | No
06/08/2023 | 17:30 | HH409D | URBAN | Asset failure | LV | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
06/08/2023 | 18:17 | HH341C | URBAN | Unknown | Unknown | 75.00 | 106.0 | 0.012257 | 0.0001156 | No
06/08/2023 | 18:40 | EL01L | URBAN | Asset failure | LV | 1.00 | 866.0 | 0.001335 | 0.0000015 | No
06/08/2023 | 19:06 | AP149E | URBAN | Overloads |  | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
06/08/2023 | 19:31 | HH429C | URBAN | Asset failure | LV | 85.00 | 61.0 | 0.007994 | 0.0001310 | No
06/08/2023 | 21:22 | HH130G | URBAN | Planned |  | 2.00 | 409.0 | 0.001261 | 0.0000031 | No
06/08/2023 | 23:39 | MTB81 | SHORT RURAL | Unknown | Unknown | 95.67 | 210.0 | 0.141343 | 0.0006731 | No
07/08/2023 | 07:45 | VH51 | SHORT RURAL | Other |  | 1.00 | 396.0 | 0.002786 | 0.0000070 | No
07/08/2023 | 08:50 | KI31 | SHORT RURAL | Planned |  | 1.00 | 324.0 | 0.002279 | 0.0000070 | No
07/08/2023 | 09:03 | HH522B | URBAN | Planned |  | 1.00 | 4,638.0 | 0.007151 | 0.0000015 | No
07/08/2023 | 09:03 | MTB52 | LONG RURAL | Planned |  | 67.00 | 377.1 | 0.181317 | 0.0004808 | No
07/08/2023 | 09:05 | MT19 | LONG RURAL | Planned |  | 64.00 | 325.0 | 0.149268 | 0.0004593 | No
07/08/2023 | 09:32 | BT26 | LONG RURAL | Planned |  | 70.00 | 263.0 | 0.132116 | 0.0005023 | No
07/08/2023 | 09:41 | MG06 | SHORT RURAL | Planned |  | 2.00 | 310.0 | 0.004362 | 0.0000141 | No
07/08/2023 | 09:51 | ME427F | URBAN | Planned |  | 104.00 | 239.0 | 0.038322 | 0.0001603 | No
07/08/2023 | 09:52 | YK12 | LONG RURAL | Planned |  | 5.00 | 181.6 | 0.006516 | 0.0000359 | No
07/08/2023 | 10:03 | CBD27L | CBD | Asset failure | LV | 2.00 | 170.0 | 0.049122 | 0.0002890 | No
07/08/2023 | 10:15 | CL05 | LONG RURAL | Unknown | Unknown | 1.00 | 386.0 | 0.002770 | 0.0000072 | No
07/08/2023 | 10:34 | SG12 | SHORT RURAL | Asset failure | LV | 2.00 | 133.0 | 0.001871 | 0.0000141 | No
07/08/2023 | 10:35 | SA711C | URBAN | Planned |  | 143.00 | 109.0 | 0.024031 | 0.0002205 | No
07/08/2023 | 10:43 | SD44200 | SHORT RURAL | Asset failure | Subtransmission | 697.00 | 11.0 | 0.053843 | 0.0049037 | No
07/08/2023 | 10:49 | ME131E | URBAN | Planned |  | 77.00 | 2.0 | 0.000237 | 0.0001187 | No
07/08/2023 | 10:58 | R29 | LONG RURAL | Planned |  | 3.00 | 137.0 | 0.002949 | 0.0000215 | No
07/08/2023 | 11:08 | VH23 | SHORT RURAL | Asset failure | LV | 26.67 | 100.0 | 0.018761 | 0.0001876 | No
07/08/2023 | 12:08 | SD35500 | LONG RURAL | Unknown | Unknown | 91.00 | 312.0 | 0.203750 | 0.0006530 | No
07/08/2023 | 12:13 | SG14 | SHORT RURAL | Overloads |  | 1.00 | 130.0 | 0.000915 | 0.0000070 | No
07/08/2023 | 12:46 | AP214A | URBAN | Overloads |  | 44.00 | 129.0 | 0.008751 | 0.0000678 | No
07/08/2023 | 12:51 | PP02 | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
07/08/2023 | 12:59 | HH121D | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
07/08/2023 | 13:21 | HH403D | URBAN | Asset failure | LV | 101.00 | 52.0 | 0.008097 | 0.0001557 | No
07/08/2023 | 13:39 | MB13 | SHORT RURAL | Planned |  | 102.00 | 46.2 | 0.033137 | 0.0007176 | No
07/08/2023 | 14:05 | NU29 | LONG RURAL | Asset failure | LV | 1.00 | 223.0 | 0.001600 | 0.0000072 | No
07/08/2023 | 17:06 | GA745C | SHORT RURAL | Asset failure | LV | 1.00 | 475.0 | 0.003342 | 0.0000070 | No
07/08/2023 | 18:17 | LX53 | SHORT RURAL | Unknown | Unknown | 15.00 | 75.0 | 0.007915 | 0.0001055 | No
07/08/2023 | 21:46 | SA744D | URBAN | Asset failure | LV | 41.00 | 142.0 | 0.008976 | 0.0000632 | No
07/08/2023 | 21:57 | AP355F | URBAN | Third Party | Vehicle impact | 2.00 | 210.0 | 0.000648 | 0.0000031 | No
08/08/2023 | 07:01 | ME231F | URBAN | Asset failure | LV | 2.00 | 188.0 | 0.000580 | 0.0000031 | No
08/08/2023 | 07:44 | HH107C | URBAN | Overloads |  | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
08/08/2023 | 08:23 | PL14 | URBAN | Planned |  | 106.00 | 339.2 | 0.055435 | 0.0001634 | No
08/08/2023 | 08:26 | SA38 | URBAN | Planned |  | 2.00 | 322.0 | 0.000993 | 0.0000031 | No
08/08/2023 | 08:38 | SD49200 | LONG RURAL | Asset failure | Subtransmission | 2.00 | 187.0 | 0.002684 | 0.0000144 | No
08/08/2023 | 08:54 | HH148B | URBAN | Asset failure | LV | 79.00 | 307.9 | 0.037500 | 0.0001218 | No
08/08/2023 | 08:59 | SM411D | URBAN | Asset failure | LV | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
08/08/2023 | 09:22 | VH43 | SHORT RURAL | Planned |  | 10.00 | 342.3 | 0.024082 | 0.0000704 | No
08/08/2023 | 09:26 | HH177A | URBAN | Overloads |  | 23.00 | 93.0 | 0.003298 | 0.0000355 | No
08/08/2023 | 09:29 | SM349H | URBAN | Planned |  | 60.00 | 88.0 | 0.008140 | 0.0000925 | No
08/08/2023 | 09:30 | SM349H | URBAN | Planned |  | 63.00 | 87.0 | 0.008450 | 0.0000971 | No
08/08/2023 | 09:31 | W20 | LONG RURAL | Planned |  | 53.00 | 140.0 | 0.053248 | 0.0003803 | No
08/08/2023 | 09:31 | SA36 | URBAN | Planned |  | 24.00 | 312.0 | 0.011545 | 0.0000370 | No
08/08/2023 | 09:34 | KI32 | SHORT RURAL | Planned |  | 7.00 | 247.0 | 0.012164 | 0.0000492 | No
08/08/2023 | 09:34 | SA17 | URBAN | Planned |  | 62.00 | 15.0 | 0.001434 | 0.0000956 | No
08/08/2023 | 09:36 | KA05 | LONG RURAL | Planned |  | 145.00 | 134.6 | 0.140053 | 0.0010406 | No
08/08/2023 | 09:58 | EL10 | URBAN | Unknown | Unknown | 5.00 | 225.0 | 0.001734 | 0.0000077 | No
08/08/2023 | 10:00 | MT13 | LONG RURAL | Planned |  | 217.00 | 126.0 | 0.196215 | 0.0015573 | No
08/08/2023 | 10:10 | HH177A | URBAN | Unknown | Unknown | 2.00 | 53.0 | 0.000163 | 0.0000031 | No
08/08/2023 | 10:16 | W01 | LONG RURAL | Planned |  | 2.00 | 149.0 | 0.002139 | 0.0000144 | No
08/08/2023 | 11:14 | HH428F | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
08/08/2023 | 11:40 | G31 | LONG RURAL | Planned |  | 2.00 | 69.0 | 0.000990 | 0.0000144 | No
08/08/2023 | 11:58 | VH21 | SHORT RURAL | Asset failure | HV | 526.00 | 231.7 | 0.857296 | 0.0037007 | No
08/08/2023 | 13:12 | M11 | LONG RURAL | Asset failure | LV | 6.00 | 78.0 | 0.003359 | 0.0000431 | No
08/08/2023 | 13:45 | AP372D | URBAN | Asset failure | LV | 36.00 | 95.0 | 0.005273 | 0.0000555 | No
08/08/2023 | 13:51 | HH409D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.67 | 144.0 | 0.006364 | 0.0000442 | No
08/08/2023 | 14:30 | AP226D | URBAN | Asset failure | LV | 1.00 | 1,181.0 | 0.001821 | 0.0000015 | No
08/08/2023 | 14:43 | BT02 | LONG RURAL | Weather |  | 3.00 | 41.0 | 0.000883 | 0.0000215 | No
08/08/2023 | 14:48 | MTB22 | SHORT RURAL | Third Party | Vehicle impact | 27.00 | 135.0 | 0.025644 | 0.0001900 | No
08/08/2023 | 15:04 | AP829N | URBAN | Overloads |  | 1.00 | 562.0 | 0.000866 | 0.0000015 | No
08/08/2023 | 16:03 | ME347A | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
08/08/2023 | 16:50 | NL111C | URBAN | Asset failure | LV | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
08/08/2023 | 17:24 | EL01L | URBAN | Asset failure | LV | 25.00 | 358.0 | 0.013799 | 0.0000385 | No
08/08/2023 | 17:45 | EL03 | URBAN | Asset failure | LV | 21.00 | 69.6 | 0.002254 | 0.0000324 | No
08/08/2023 | 18:17 | NL115C | URBAN | Asset failure | LV | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
08/08/2023 | 18:23 | AP424F | URBAN | Asset failure | LV | 9.00 | 170.0 | 0.002359 | 0.0000139 | No
08/08/2023 | 20:24 | SD32200 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 109.00 | 140.0 | 0.109511 | 0.0007822 | No
08/08/2023 | 20:56 | NL760B | URBAN | Asset failure | LV | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
08/08/2023 | 22:35 | SM137B | URBAN | Asset failure | LV | 27.00 | 954.0 | 0.039712 | 0.0000416 | No
09/08/2023 | 01:25 | KA01 | SHORT RURAL | Asset failure | LV | 1.00 | 621.0 | 0.004369 | 0.0000070 | No
09/08/2023 | 05:36 | HH177B | URBAN | Asset failure | LV | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
09/08/2023 | 08:01 | SM179A | URBAN | Unknown | Unknown | 4.00 | 168.0 | 0.001036 | 0.0000062 | No
09/08/2023 | 08:04 | EL10 | URBAN | Asset failure | LV | 27.00 | 333.0 | 0.013862 | 0.0000416 | No
09/08/2023 | 08:12 | SA14 | URBAN | Asset failure | LV | 121.00 | 148.6 | 0.027728 | 0.0001866 | No
09/08/2023 | 08:16 | BM11 | SHORT RURAL | Planned |  | 49.00 | 227.2 | 0.078333 | 0.0003447 | No
09/08/2023 | 08:19 | EL19 | URBAN | Animal | Animal impact | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
09/08/2023 | 08:26 | KA02 | SHORT RURAL | Planned |  | 25.00 | 694.2 | 0.122101 | 0.0001759 | No
09/08/2023 | 08:51 | SA38 | URBAN | Planned |  | 2.00 | 321.0 | 0.000990 | 0.0000031 | No
09/08/2023 | 08:57 | EL23 | URBAN | Planned |  | 156.00 | 563.8 | 0.135590 | 0.0002405 | No
09/08/2023 | 09:20 | AP424F | URBAN | Asset failure | LV | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
09/08/2023 | 09:21 | R12 | LONG RURAL | Planned |  | 3.00 | 329.0 | 0.007083 | 0.0000215 | No
09/08/2023 | 10:03 | SG12 | SHORT RURAL | Unknown | Unknown | 257.00 | 140.0 | 0.253137 | 0.0018081 | No
09/08/2023 | 10:08 | ME427E | URBAN | Unknown | Unknown | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
09/08/2023 | 10:33 | MV53 | SHORT RURAL | Planned |  | 1.00 | 97.0 | 0.000682 | 0.0000070 | No
09/08/2023 | 10:33 | PL07 | URBAN | Weather |  | 10.33 | 215.0 | 0.003425 | 0.0000159 | No
09/08/2023 | 10:34 | SM126D | URBAN | Planned |  | 82.00 | 56.0 | 0.007080 | 0.0001264 | No
09/08/2023 | 10:35 | LM54 | LONG RURAL | Planned |  | 82.00 | 78.0 | 0.045900 | 0.0005885 | No
09/08/2023 | 11:53 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 309.0 | 0.002174 | 0.0000070 | No
09/08/2023 | 11:55 | EL03 | URBAN | Asset failure | LV | 73.00 | 69.0 | 0.007766 | 0.0001125 | No
09/08/2023 | 11:57 | KI32 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 772.00 | 80.6 | 0.437755 | 0.0054314 | No
09/08/2023 | 13:06 | CL12 | LONG RURAL | Third Party | Vehicle impact | 13.00 | 297.0 | 0.027708 | 0.0000933 | No
09/08/2023 | 13:46 | SM126D | URBAN | Asset failure | LV | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
09/08/2023 | 13:59 | EL23 | URBAN | Planned |  | 3.00 | 102.0 | 0.000472 | 0.0000046 | No
09/08/2023 | 15:09 | KA13 | LONG RURAL | Asset failure | HV | 64.00 | 276.3 | 0.126906 | 0.0004593 | No
09/08/2023 | 15:15 | VH23 | SHORT RURAL | Asset failure | HV | 579.33 | 107.3 | 0.437275 | 0.0040759 | No
09/08/2023 | 15:41 | NL115A | URBAN | Asset failure | LV | 14.00 | 140.0 | 0.003022 | 0.0000216 | No
09/08/2023 | 16:51 | GU41 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 199.0 | 0.002856 | 0.0000144 | No
09/08/2023 | 17:00 | CN42 | LONG RURAL | Asset failure | HV | 31.00 | 12.5 | 0.002770 | 0.0002225 | No
09/08/2023 | 17:45 | MTB51 | LONG RURAL | Asset failure | LV | 14.33 | 146.0 | 0.015018 | 0.0001029 | No
09/08/2023 | 17:57 | MTB51 | LONG RURAL | Asset failure | LV | 62.00 | 134.0 | 0.059621 | 0.0004449 | No
09/08/2023 | 18:21 | YK15 | LONG RURAL | Asset failure | HV | 3.00 | 86.0 | 0.001851 | 0.0000215 | No
09/08/2023 | 18:27 | HH130C | URBAN | Unknown | Unknown | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
09/08/2023 | 18:53 | EL260C | URBAN | Third Party | Other | 12.00 | 217.0 | 0.004015 | 0.0000185 | No
09/08/2023 | 19:55 | VH23 | SHORT RURAL | Unknown | Unknown | 1.00 | 152.0 | 0.001069 | 0.0000070 | No
09/08/2023 | 20:07 | EL23 | URBAN | Planned |  | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
09/08/2023 | 20:22 | MTB21 | SHORT RURAL | Overloads |  | 1.00 | 316.0 | 0.002223 | 0.0000070 | No
09/08/2023 | 20:31 | MG28 | LONG RURAL | Unknown | Unknown | 56.00 | 118.0 | 0.047421 | 0.0004019 | No
09/08/2023 | 21:50 | AP149F | URBAN | Asset failure | LV | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
09/08/2023 | 23:29 | EL01L | URBAN | Asset failure | LV | 13.00 | 64.0 | 0.001283 | 0.0000200 | No
10/08/2023 | 01:10 | HH428B | URBAN | Asset failure | LV | 33.00 | 95.0 | 0.004833 | 0.0000509 | No
10/08/2023 | 08:10 | HH409F | URBAN | Overloads |  | 3.33 | 205.0 | 0.001054 | 0.0000051 | No
10/08/2023 | 08:26 | KA04 | LONG RURAL | Planned |  | 72.00 | 239.9 | 0.123942 | 0.0005167 | No
10/08/2023 | 08:39 | WHY04 | URBAN | Planned |  | 85.00 | 372.0 | 0.048750 | 0.0001310 | No
10/08/2023 | 08:52 | ME131C | URBAN | Planned |  | 205.00 | 360.0 | 0.113781 | 0.0003161 | No
10/08/2023 | 09:03 | SM402B | URBAN | Asset failure | LV | 1.00 | 541.0 | 0.000834 | 0.0000015 | No
10/08/2023 | 09:14 | AP355A | URBAN | Planned |  | 146.00 | 404.0 | 0.090939 | 0.0002251 | No
10/08/2023 | 09:27 | PL13 | LONG RURAL | Planned |  | 5.00 | 237.0 | 0.008504 | 0.0000359 | No
10/08/2023 | 09:30 | KI51 | LONG RURAL | Planned |  | 2.00 | 181.0 | 0.002598 | 0.0000144 | No
10/08/2023 | 09:39 | SD34300 | SHORT RURAL | Planned |  | 360.00 | 198.0 | 0.501490 | 0.0025328 | No
10/08/2023 | 09:44 | NL451A | URBAN | Third Party | Dig-in | 17.00 | 541.0 | 0.014180 | 0.0000262 | No
10/08/2023 | 09:55 | HH121C | URBAN | Planned |  | 57.00 | 316.8 | 0.027839 | 0.0000879 | No
10/08/2023 | 10:03 | MG46 | SHORT RURAL | Planned |  | 119.00 | 153.0 | 0.128095 | 0.0008372 | No
10/08/2023 | 10:12 | GA03 | LONG RURAL | Planned |  | 3.00 | 290.0 | 0.006243 | 0.0000215 | No
10/08/2023 | 10:27 | ST35 | LONG RURAL | Unknown | Unknown | 2.00 | 216.0 | 0.003100 | 0.0000144 | No
10/08/2023 | 10:37 | EL19 | URBAN | Asset failure | HV | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
10/08/2023 | 10:37 | EL19 | URBAN | Asset failure | HV | 1.00 | 16.0 | 0.000025 | 0.0000015 | No
10/08/2023 | 10:42 | MG05 | LONG RURAL | Asset failure | LV | 1.00 | 295.0 | 0.002117 | 0.0000072 | No
10/08/2023 | 10:47 | NL760C | URBAN | Asset failure | LV | 1.00 | 240.0 | 0.000370 | 0.0000015 | No
10/08/2023 | 12:33 | MI03 | LONG RURAL | Asset failure | HV | 4.00 | 14.0 | 0.000402 | 0.0000287 | No
10/08/2023 | 13:27 | SM216G | URBAN | Asset failure | LV | 1.00 | 500.0 | 0.000771 | 0.0000015 | No
10/08/2023 | 15:08 | HH432C | URBAN | Third Party | Vehicle impact | 64.00 | 665.0 | 0.065617 | 0.0000987 | No
10/08/2023 | 16:05 | CBD412S | URBAN | Unknown | Unknown | 29.00 | 62.0 | 0.002772 | 0.0000447 | No
10/08/2023 | 16:35 | MI19 | LONG RURAL | Asset failure | HV | 2.00 | 99.0 | 0.001421 | 0.0000144 | No
10/08/2023 | 18:21 | PL24 | LONG RURAL | Unknown | Unknown | 31.00 | 325.0 | 0.072302 | 0.0002225 | No
10/08/2023 | 18:37 | SG01 | SHORT RURAL | Animal | Animal impact | 5.00 | 124.0 | 0.004362 | 0.0000352 | No
10/08/2023 | 18:52 | MG10 | LONG RURAL | Asset failure | HV | 4.00 | 194.8 | 0.005590 | 0.0000287 | No
10/08/2023 | 19:31 | MB61 | LONG RURAL | Asset failure | LV | 1.00 | 905.0 | 0.006495 | 0.0000072 | No
10/08/2023 | 19:44 | GA02 | SHORT RURAL | Animal | Animal impact | 35.33 | 288.0 | 0.071593 | 0.0002486 | No
10/08/2023 | 20:31 | SG13 | SHORT RURAL | Asset failure | LV | 1.00 | 480.0 | 0.003377 | 0.0000070 | No
10/08/2023 | 20:34 | HH107B | URBAN | Overloads |  | 28.33 | 92.0 | 0.004019 | 0.0000437 | No
10/08/2023 | 21:54 | HH432C | URBAN | Unknown | Unknown | 1.00 | 331.0 | 0.000510 | 0.0000015 | No
10/08/2023 | 22:22 | HH177A | URBAN | Asset failure | LV | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
10/08/2023 | 23:21 | AP355D | URBAN | Planned |  | 14.00 | 210.0 | 0.004533 | 0.0000216 | No
11/08/2023 | 01:33 | MG02 | LONG RURAL | Unknown | Unknown | 140.00 | 170.0 | 0.170797 | 0.0010047 | No
11/08/2023 | 08:37 | SA38 | URBAN | Planned |  | 2.00 | 377.0 | 0.001162 | 0.0000031 | No
11/08/2023 | 08:44 | SD54300 | LONG RURAL | Planned |  | 1.00 | 159.0 | 0.001141 | 0.0000072 | No
11/08/2023 | 09:16 | CV757A | LONG RURAL | Planned |  | 69.00 | 46.0 | 0.022778 | 0.0004952 | No
11/08/2023 | 09:22 | SM126A | URBAN | Planned |  | 31.00 | 300.0 | 0.014338 | 0.0000478 | No
11/08/2023 | 09:26 | GA04 | LONG RURAL | Planned |  | 15.00 | 141.0 | 0.015178 | 0.0001076 | No
11/08/2023 | 09:29 | SD34201 | SHORT RURAL | Planned |  | 67.00 | 287.0 | 0.135285 | 0.0004714 | No
11/08/2023 | 09:52 | YK13 | SHORT RURAL | Planned |  | 1.00 | 178.0 | 0.001252 | 0.0000070 | No
11/08/2023 | 09:53 | HH428B | URBAN | Asset failure | LV | 1.00 | 423.0 | 0.000652 | 0.0000015 | No
11/08/2023 | 09:57 | W19 | LONG RURAL | Planned |  | 15.00 | 138.0 | 0.014855 | 0.0001076 | No
11/08/2023 | 10:09 | CN02 | LONG RURAL | Planned |  | 63.00 | 176.0 | 0.079571 | 0.0004521 | No
11/08/2023 | 10:14 | NL511A | URBAN | Asset failure | LV | 1.00 | 406.0 | 0.000626 | 0.0000015 | No
11/08/2023 | 10:36 | BT14 | LONG RURAL | Asset failure | HV | 5.00 | 84.0 | 0.003014 | 0.0000359 | No
11/08/2023 | 10:41 | CD16 | SHORT RURAL | Planned |  | 1.00 | 81.0 | 0.000570 | 0.0000070 | No
11/08/2023 | 10:41 | HH130B | URBAN | Planned |  | 443.00 | 64.7 | 0.044207 | 0.0006830 | No
11/08/2023 | 11:18 | HH496C | URBAN | Unknown | Unknown | 1.00 | 191.0 | 0.000294 | 0.0000015 | No
11/08/2023 | 11:36 | NL234C | URBAN | Asset failure | LV | 33.00 | 96.0 | 0.004884 | 0.0000509 | No
11/08/2023 | 11:56 | MG10 | LONG RURAL | Asset failure | HV | 4.00 | 104.0 | 0.002985 | 0.0000287 | No
11/08/2023 | 12:12 | CD16 | SHORT RURAL | Planned |  | 1.00 | 20.0 | 0.000141 | 0.0000070 | No
11/08/2023 | 12:31 | BT03 | LONG RURAL | Unknown | Unknown | 368.00 | 137.4 | 0.362778 | 0.0026409 | No
11/08/2023 | 12:42 | HH145B | URBAN | Asset failure | LV | 6.67 | 180.0 | 0.001850 | 0.0000103 | No
11/08/2023 | 12:42 | ST22 | SHORT RURAL | Overloads |  | 3.00 | 122.0 | 0.002575 | 0.0000211 | No
11/08/2023 | 14:43 | SA520D | URBAN | Overloads |  | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
11/08/2023 | 16:36 | MB24 | SHORT RURAL | Asset failure | HV | 328.00 | 7.6 | 0.017471 | 0.0023076 | No
11/08/2023 | 16:39 | SA40 | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
11/08/2023 | 18:10 | AP344E | URBAN | Unknown | Unknown | 32.00 | 180.0 | 0.008881 | 0.0000493 | No
11/08/2023 | 18:13 | NL111C | URBAN | Asset failure | LV | 1.00 | 323.0 | 0.000498 | 0.0000015 | No
11/08/2023 | 18:49 | EL10 | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
11/08/2023 | 21:29 | MT14 | SHORT RURAL | Other |  | 2.00 | 113.0 | 0.001590 | 0.0000141 | No
11/08/2023 | 21:37 | AP344E | URBAN | Asset failure | LV | 16.00 | 975.0 | 0.024051 | 0.0000247 | No
12/08/2023 | 00:17 | SM411D | URBAN | Asset failure | LV | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
12/08/2023 | 01:00 | GU32 | LONG RURAL | Weather |  | 618.00 | 788.7 | 3.497829 | 0.0044350 | No
12/08/2023 | 06:15 | CBD367M | CBD | Planned |  | 1.00 | 595.0 | 0.085964 | 0.0001445 | No
12/08/2023 | 08:57 | HH177D | URBAN | Asset failure | LV | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
12/08/2023 | 09:30 | SD34300 | SHORT RURAL | Planned |  | 231.00 | 313.7 | 0.509827 | 0.0016252 | No
12/08/2023 | 09:44 | SA40 | URBAN | Planned |  | 346.00 | 68.2 | 0.036404 | 0.0005334 | No
12/08/2023 | 10:04 | AP214D | URBAN | Asset failure | LV | 31.33 | 289.0 | 0.013961 | 0.0000483 | No
12/08/2023 | 10:31 | CM03 | LONG RURAL | Unknown | Unknown | 7.00 | 179.0 | 0.008992 | 0.0000502 | No
12/08/2023 | 10:47 | EL10 | URBAN | Asset failure | LV | 1.00 | 274.0 | 0.000422 | 0.0000015 | No
12/08/2023 | 11:34 | BT03 | LONG RURAL | Third Party | Other | 368.00 | 147.6 | 0.389703 | 0.0026409 | No
12/08/2023 | 11:44 | AP424A | URBAN | Asset failure | LV | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
12/08/2023 | 14:44 | NL544A | URBAN | Asset failure | LV | 15.00 | 586.5 | 0.013563 | 0.0000231 | No
12/08/2023 | 15:46 | MV53 | SHORT RURAL | Asset failure | HV | 3.00 | 294.0 | 0.006205 | 0.0000211 | No
12/08/2023 | 15:46 | MV53 | SHORT RURAL | Asset failure | HV | 6.00 | 1,099.0 | 0.046392 | 0.0000422 | No
12/08/2023 | 16:13 | SA744B | URBAN | Planned |  | 1.00 | 786.0 | 0.001212 | 0.0000015 | No
12/08/2023 | 16:47 | HH121C | URBAN | Third Party | Vehicle impact | 57.00 | 648.0 | 0.056946 | 0.0000879 | No
12/08/2023 | 17:48 | HH341E | URBAN | Asset failure | LV | 79.00 | 108.0 | 0.013154 | 0.0001218 | No
12/08/2023 | 19:32 | HH522C | URBAN | Unknown | Unknown | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
12/08/2023 | 20:53 | HH428F | URBAN | Asset failure | LV | 58.00 | 139.0 | 0.012430 | 0.0000894 | No
12/08/2023 | 21:12 | GA53 | SHORT RURAL | Asset failure | LV | 1.00 | 79.0 | 0.000556 | 0.0000070 | No
12/08/2023 | 21:25 | AP226D | URBAN | Unknown | Unknown | 1.00 | 289.0 | 0.000446 | 0.0000015 | No
12/08/2023 | 21:25 | HH341D | URBAN | Unknown | Unknown | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
13/08/2023 | 00:14 | MB24 | SHORT RURAL | Asset failure | HV | 23.67 | 92.1 | 0.015342 | 0.0001665 | No
13/08/2023 | 06:19 | PA02 | URBAN | Asset failure | LV | 45.00 | 44.0 | 0.003053 | 0.0000694 | No
13/08/2023 | 07:32 | NL451E | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
13/08/2023 | 08:01 | SSD318 | LONG RURAL | Planned |  | 886.00 | 402.0 | 2.556008 | 0.0063582 | No
13/08/2023 | 08:01 | SSD318 | SHORT RURAL | Planned |  | 1,417.00 | 402.0 | 4.007655 | 0.0099693 | No
13/08/2023 | 08:19 | NL111C | URBAN | Planned |  | 375.00 | 354.0 | 0.204645 | 0.0005782 | No
13/08/2023 | 08:23 | MV15 | SHORT RURAL | Animal | Animal impact | 1,174.00 | 176.0 | 1.453349 | 0.0082597 | No
13/08/2023 | 08:25 | AP829C | URBAN | Planned |  | 1.00 | 343.0 | 0.000529 | 0.0000015 | No
13/08/2023 | 08:56 | HH107C | URBAN | Planned |  | 8.00 | 249.0 | 0.003071 | 0.0000123 | No
13/08/2023 | 09:00 | SA42 | URBAN | Planned |  | 74.00 | 467.7 | 0.053363 | 0.0001141 | No
13/08/2023 | 09:06 | MG42 | SHORT RURAL | Planned |  | 3.00 | 453.0 | 0.009561 | 0.0000211 | No
13/08/2023 | 09:44 | NL210C | URBAN | Planned |  | 289.00 | 28.0 | 0.012476 | 0.0004456 | No
13/08/2023 | 10:08 | HH341B | URBAN | Planned |  | 3.00 | 315.0 | 0.001457 | 0.0000046 | No
13/08/2023 | 10:15 | MTB32 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 11.33 | 95.0 | 0.007727 | 0.0000813 | No
13/08/2023 | 10:41 | YK03 | LONG RURAL | Planned |  | 638.00 | 198.0 | 0.906543 | 0.0045785 | No
13/08/2023 | 12:53 | CN01 | LONG RURAL | Asset failure | LV | 2.00 | 466.0 | 0.006688 | 0.0000144 | No
13/08/2023 | 13:29 | SM349F | URBAN | Asset failure | LV | 1.00 | 363.0 | 0.000560 | 0.0000015 | No
13/08/2023 | 14:45 | MTB54 | LONG RURAL | Unknown | Unknown | 10.00 | 18.0 | 0.001292 | 0.0000718 | No
13/08/2023 | 15:19 | MTB54 | LONG RURAL | Other |  | 15.00 | 10.6 | 0.001141 | 0.0001076 | No
13/08/2023 | 17:30 | CBD353M | CBD | Asset failure | HV | 53.00 | 178.4 | 1.365745 | 0.0076573 | No
13/08/2023 | 17:47 | GU41 | LONG RURAL | Other |  | 2.00 | 68.0 | 0.000976 | 0.0000144 | No
13/08/2023 | 18:32 | SB01 | LONG RURAL | Unknown | Unknown | 1.00 | 76.0 | 0.000545 | 0.0000072 | No
13/08/2023 | 18:32 | PL14 | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
13/08/2023 | 18:36 | SD40400 | LONG RURAL | Unknown | Unknown | 168.00 | 61.7 | 0.074426 | 0.0012056 | No
14/08/2023 | 07:36 | HH428F | URBAN | Asset failure | LV | 42.67 | 95.0 | 0.006249 | 0.0000658 | No
14/08/2023 | 08:48 | WHY07 | URBAN | Planned |  | 21.00 | 297.0 | 0.009616 | 0.0000324 | No
14/08/2023 | 09:08 | PL04 | URBAN | Planned |  | 1.00 | 19.0 | 0.000029 | 0.0000015 | No
14/08/2023 | 09:08 | VH16 | SHORT RURAL | Planned |  | 10.00 | 341.6 | 0.024033 | 0.0000704 | No
14/08/2023 | 09:16 | SM411E | URBAN | Planned |  | 74.00 | 319.0 | 0.036395 | 0.0001141 | No
14/08/2023 | 09:19 | VH18 | SHORT RURAL | Unknown | Unknown | 34.00 | 474.0 | 0.113384 | 0.0002392 | No
14/08/2023 | 09:19 | CN76 | LONG RURAL | Planned |  | 12.00 | 117.0 | 0.010076 | 0.0000861 | No
14/08/2023 | 09:41 | YK25 | LONG RURAL | Planned |  | 114.00 | 175.0 | 0.143168 | 0.0008181 | No
14/08/2023 | 09:58 | G06 | LONG RURAL | Planned |  | 69.00 | 154.0 | 0.076256 | 0.0004952 | No
14/08/2023 | 11:07 | KA17 | LONG RURAL | Planned |  | 25.00 | 99.0 | 0.017761 | 0.0001794 | No
14/08/2023 | 12:05 | CL08 | LONG RURAL | Planned |  | 66.00 | 1.0 | 0.000474 | 0.0004736 | No
14/08/2023 | 13:18 | LM64 | LONG RURAL | Asset failure | LV | 2.00 | 430.0 | 0.006172 | 0.0000144 | No
14/08/2023 | 13:38 | NL511B | URBAN | Third Party | Other | 56.00 | 26.0 | 0.002245 | 0.0000863 | No
14/08/2023 | 13:38 | VH11 | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
14/08/2023 | 14:04 | HH341G | URBAN | Overloads |  | 24.67 | 26.0 | 0.000989 | 0.0000380 | No
14/08/2023 | 14:07 | MB81 | LONG RURAL | Asset failure | LV | 1.00 | 705.0 | 0.005059 | 0.0000072 | No
14/08/2023 | 14:43 | HH409D | URBAN | Overloads |  | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
14/08/2023 | 16:26 | SM172E | URBAN | Unknown | Unknown | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
14/08/2023 | 18:13 | HH130E | URBAN | Overloads |  | 8.67 | 52.0 | 0.000695 | 0.0000134 | No
14/08/2023 | 18:31 | MV22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 469.00 | 5.6 | 0.018334 | 0.0032996 | No
14/08/2023 | 18:58 | NL451C | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
14/08/2023 | 19:26 | HH130E | URBAN | Asset failure | LV | 26.00 | 645.0 | 0.025855 | 0.0000401 | No
14/08/2023 | 20:45 | MG21 | LONG RURAL | Asset failure | HV | 71.00 | 302.2 | 0.153954 | 0.0005095 | No
14/08/2023 | 22:39 | SG10 | SHORT RURAL | Asset failure | LV | 1.00 | 180.0 | 0.001266 | 0.0000070 | No
14/08/2023 | 22:40 | AP829C | URBAN | Planned |  | 16.00 | 338.4 | 0.008347 | 0.0000247 | No
15/08/2023 | 02:53 | HH130A | URBAN | Overloads |  | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
15/08/2023 | 06:45 | NL115E | URBAN | Overloads |  | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
15/08/2023 | 08:11 | KA02 | SHORT RURAL | Planned |  | 1.00 | 149.0 | 0.001048 | 0.0000070 | No
15/08/2023 | 08:38 | CD03 | SHORT RURAL | Planned |  | 8.00 | 63.0 | 0.003546 | 0.0000563 | No
15/08/2023 | 08:41 | KI31 | SHORT RURAL | Planned |  | 1.00 | 351.0 | 0.002469 | 0.0000070 | No
15/08/2023 | 09:12 | MT01 | LONG RURAL | Planned |  | 39.00 | 119.2 | 0.033370 | 0.0002799 | No
15/08/2023 | 09:28 | AP149A | URBAN | Planned |  | 103.00 | 2,731.0 | 0.433685 | 0.0001588 | No
15/08/2023 | 09:32 | NL544B | URBAN | Planned |  | 95.00 | 13.0 | 0.001904 | 0.0001465 | No
15/08/2023 | 09:54 | HH409E | URBAN | Planned |  | 131.00 | 290.0 | 0.058571 | 0.0002020 | No
15/08/2023 | 10:37 | HH177F | URBAN | Planned |  | 25.00 | 77.0 | 0.002968 | 0.0000385 | No
15/08/2023 | 10:50 | NU12 | LONG RURAL | Planned |  | 2.00 | 51.0 | 0.000732 | 0.0000144 | No
15/08/2023 | 10:53 | MB12 | SHORT RURAL | Asset failure | LV | 1.00 | 447.0 | 0.003145 | 0.0000070 | No
15/08/2023 | 11:03 | WHY04 | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
15/08/2023 | 11:58 | CD18 | LONG RURAL | Planned |  | 1.00 | 13.0 | 0.000093 | 0.0000072 | No
15/08/2023 | 12:01 | NL760B | URBAN | Asset failure | LV | 80.00 | 160.0 | 0.019734 | 0.0001233 | No
15/08/2023 | 12:17 | AP829C | URBAN | Asset failure | LV | 19.00 | 339.0 | 0.009930 | 0.0000293 | No
15/08/2023 | 12:41 | LX43 | SHORT RURAL | Overloads |  | 9.00 | 40.0 | 0.002533 | 0.0000633 | No
15/08/2023 | 12:51 | CL17 | LONG RURAL | Asset failure | LV | 2.00 | 118.0 | 0.001694 | 0.0000144 | No
15/08/2023 | 13:22 | AP344E | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
15/08/2023 | 13:35 | ME116A | URBAN | Third Party | Vehicle impact | 2.00 | 111.0 | 0.000342 | 0.0000031 | No
15/08/2023 | 13:57 | CBD412M | URBAN | Overloads |  | 1.00 | 354.0 | 0.000546 | 0.0000015 | No
15/08/2023 | 14:07 | HH121D | URBAN | Planned |  | 306.00 | 5.0 | 0.002359 | 0.0004718 | No
15/08/2023 | 14:44 | HH121E | URBAN | Asset failure | LV | 5.00 | 303.0 | 0.002336 | 0.0000077 | No
15/08/2023 | 15:01 | AP344D | URBAN | Asset failure | LV | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
15/08/2023 | 16:16 | NL760B | URBAN | Asset failure | LV | 85.00 | 98.0 | 0.012843 | 0.0001310 | No
15/08/2023 | 16:35 | NL760B | URBAN | Unknown | Unknown | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
15/08/2023 | 17:07 | SA520D | URBAN | Asset failure | LV | 1.00 | 184.0 | 0.000284 | 0.0000015 | No
15/08/2023 | 17:26 | HH177C | URBAN | Third Party | Other | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
15/08/2023 | 17:57 | NL210A | URBAN | Asset failure | LV | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
15/08/2023 | 18:05 | SA744F | URBAN | Planned |  | 1.00 | 707.0 | 0.001090 | 0.0000015 | No
15/08/2023 | 18:29 | PL07 | URBAN | Asset failure | LV | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
15/08/2023 | 19:09 | PP10 | URBAN | Overloads |  | 1,664.00 | 6.1 | 0.015559 | 0.0025655 | No
15/08/2023 | 20:01 | EL260C | URBAN | Asset failure | LV | 73.00 | 75.0 | 0.008441 | 0.0001125 | No
15/08/2023 | 23:19 | MB15 | SHORT RURAL | Unknown | Unknown | 1.00 | 113.0 | 0.000795 | 0.0000070 | No
16/08/2023 | 05:23 | EL01M | URBAN | Overloads |  | 23.00 | 232.0 | 0.008227 | 0.0000355 | No
16/08/2023 | 06:10 | HH496F | URBAN | Asset failure | LV | 13.00 | 460.0 | 0.009220 | 0.0000200 | No
16/08/2023 | 06:11 | HH496H | URBAN | Asset failure | LV | 1.00 | 617.0 | 0.000951 | 0.0000015 | No
16/08/2023 | 08:26 | HH496G | URBAN | Overloads |  | 4.00 | 157.0 | 0.000968 | 0.0000062 | No
16/08/2023 | 08:32 | NU04 | SHORT RURAL | Third Party | Vehicle impact | 591.00 | 74.4 | 0.309526 | 0.0041580 | No
16/08/2023 | 08:38 | SM411F | URBAN | Unknown | Unknown | 1.00 | 1,614.0 | 0.002488 | 0.0000015 | No
16/08/2023 | 08:50 | CL06 | LONG RURAL | Planned |  | 9.00 | 373.0 | 0.024091 | 0.0000646 | No
16/08/2023 | 08:51 | SM216G | URBAN | Planned |  | 75.00 | 370.0 | 0.042784 | 0.0001156 | No
16/08/2023 | 09:11 | VH45 | SHORT RURAL | Planned |  | 68.00 | 176.0 | 0.084201 | 0.0004784 | No
16/08/2023 | 09:19 | NL451A | URBAN | Planned |  | 2.00 | 354.0 | 0.001092 | 0.0000031 | No
16/08/2023 | 09:23 | CV23 | LONG RURAL | Planned |  | 7.00 | 360.0 | 0.018084 | 0.0000502 | No
16/08/2023 | 10:12 | PL08 | URBAN | Planned |  | 1.00 | 60.0 | 0.000093 | 0.0000015 | No
16/08/2023 | 10:15 | CM16 | LONG RURAL | Planned |  | 8.00 | 107.0 | 0.006143 | 0.0000574 | No
16/08/2023 | 10:35 | CL19 | LONG RURAL | Planned |  | 29.00 | 70.0 | 0.014568 | 0.0002081 | No
16/08/2023 | 10:53 | YK23 | LONG RURAL | Planned |  | 11.00 | 315.0 | 0.024866 | 0.0000789 | No
16/08/2023 | 11:33 | PP10 | URBAN | Planned |  | 1,664.00 | 3.0 | 0.007696 | 0.0025655 | No
16/08/2023 | 11:40 | M21 | LONG RURAL | Unknown | Unknown | 1.00 | 532.0 | 0.003818 | 0.0000072 | No
16/08/2023 | 12:26 | MB20 | SHORT RURAL | Asset failure | HV | 2.00 | 335.0 | 0.004714 | 0.0000141 | No
16/08/2023 | 13:36 | NU04 | SHORT RURAL | Third Party | Vehicle impact | 13.00 | 347.0 | 0.031737 | 0.0000915 | No
16/08/2023 | 15:14 | PP10 | URBAN | Unknown | Unknown | 3.00 | 34.0 | 0.000157 | 0.0000046 | No
16/08/2023 | 15:15 | BT02 | LONG RURAL | Planned |  | 4.00 | 1.0 | 0.000029 | 0.0000287 | No
16/08/2023 | 15:44 | BS0186 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 2.00 | 38.0 | 0.000535 | 0.0000141 | No
16/08/2023 | 15:56 | SM216A | URBAN | Asset failure | LV | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
16/08/2023 | 15:57 | SM349B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 77.0 | 0.000119 | 0.0000015 | No
16/08/2023 | 16:01 | YK01 | LONG RURAL | Overloads |  | 2.00 | 136.0 | 0.001952 | 0.0000144 | No
16/08/2023 | 16:02 | NL451E | URBAN | Asset failure | LV | 1.00 | 216.0 | 0.000333 | 0.0000015 | No
16/08/2023 | 16:36 | CM02 | LONG RURAL | Asset failure | LV | 14.00 | 115.0 | 0.011554 | 0.0001005 | No
16/08/2023 | 18:13 | SA18 | URBAN | Asset failure | LV | 16.00 | 194.0 | 0.004786 | 0.0000247 | No
16/08/2023 | 18:16 | NL111B | URBAN | Asset failure | LV | 1.00 | 290.0 | 0.000447 | 0.0000015 | No
16/08/2023 | 18:40 | HH107A | URBAN | Asset failure | LV | 1.00 | 421.0 | 0.000649 | 0.0000015 | No
16/08/2023 | 18:44 | ME347G | URBAN | Asset failure | LV | 47.00 | 108.0 | 0.007826 | 0.0000725 | No
16/08/2023 | 19:14 | HH121B | URBAN | Asset failure | LV | 1.00 | 343.0 | 0.000529 | 0.0000015 | No
16/08/2023 | 19:28 | HH107D | URBAN | Asset failure | LV | 1.00 | 321.0 | 0.000495 | 0.0000015 | No
16/08/2023 | 21:01 | AP214C | URBAN | Asset failure | LV | 36.33 | 46.0 | 0.002577 | 0.0000560 | No
16/08/2023 | 21:02 | NL21 | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
16/08/2023 | 22:36 | SA520A | URBAN | Third Party | Unauthorised access | 1.00 | 87.0 | 0.000134 | 0.0000015 | No
16/08/2023 | 22:54 | CL26 | LONG RURAL | Unknown | Unknown | 40.00 | 321.6 | 0.092323 | 0.0002871 | No
16/08/2023 | 23:11 | HH403A | URBAN | Planned |  | 1.00 | 350.0 | 0.000540 | 0.0000015 | No
17/08/2023 | 06:13 | SM349E | URBAN | Unknown | Unknown | 29.00 | 182.0 | 0.008137 | 0.0000447 | No
17/08/2023 | 06:33 | CL26 | LONG RURAL | Weather |  | 40.00 | 137.2 | 0.039377 | 0.0002871 | No
17/08/2023 | 08:36 | LX21 | SHORT RURAL | Planned |  | 18.00 | 228.7 | 0.028958 | 0.0001266 | No
17/08/2023 | 08:43 | KA02 | SHORT RURAL | Planned |  | 28.00 | 296.6 | 0.058437 | 0.0001970 | No
17/08/2023 | 08:50 | CV19 | LONG RURAL | Planned |  | 58.00 | 316.1 | 0.131571 | 0.0004162 | No
17/08/2023 | 09:44 | AP529E | URBAN | Asset failure | LV | 1.00 | 546.0 | 0.000842 | 0.0000015 | No
17/08/2023 | 09:54 | LM61 | LONG RURAL | Planned |  | 17.00 | 213.0 | 0.025985 | 0.0001220 | No
17/08/2023 | 10:31 | SA20 | URBAN | Asset failure | LV | 1.00 | 283.0 | 0.000436 | 0.0000015 | No
17/08/2023 | 10:38 | AP344F | URBAN | Planned |  | 61.00 | 9.0 | 0.000846 | 0.0000940 | No
17/08/2023 | 10:50 | NA23 | LONG RURAL | Planned |  | 1.00 | 67.0 | 0.000481 | 0.0000072 | No
17/08/2023 | 11:25 | CL04 | LONG RURAL | Other |  | 5.00 | 65.0 | 0.002332 | 0.0000359 | No
17/08/2023 | 12:05 | MT18 | LONG RURAL | Weather |  | 24.00 | 32.0 | 0.005511 | 0.0001722 | No
17/08/2023 | 12:09 | HH121D | URBAN | Third Party | Dig-in | 18.00 | 290.0 | 0.008048 | 0.0000278 | No
17/08/2023 | 12:31 | R18 | LONG RURAL | Asset failure | LV | 1.00 | 208.0 | 0.001493 | 0.0000072 | No
17/08/2023 | 12:36 | GA31 | LONG RURAL | Overloads |  | 1.00 | 152.0 | 0.001091 | 0.0000072 | No
17/08/2023 | 13:07 | R18 | LONG RURAL | Asset failure | LV | 34.00 | 168.0 | 0.040991 | 0.0002440 | No
17/08/2023 | 14:13 | PL26 | URBAN | Planned |  | 2.00 | 68.0 | 0.000210 | 0.0000031 | No
17/08/2023 | 14:14 | W33 | LONG RURAL | Planned |  | 12.00 | 1.0 | 0.000086 | 0.0000861 | No
17/08/2023 | 14:33 | SM411E | URBAN | Asset failure | LV | 17.00 | 105.0 | 0.002752 | 0.0000262 | No
17/08/2023 | 15:05 | HH118C | URBAN | Overloads |  | 76.00 | 124.7 | 0.014610 | 0.0001172 | No
17/08/2023 | 15:21 | HH496G | URBAN | Weather |  | 10.00 | 565.5 | 0.008719 | 0.0000154 | No
17/08/2023 | 15:28 | SD46201 | LONG RURAL | Network business | Switching and protection error | 3,017.00 | 18.0 | 0.389718 | 0.0216510 | No
17/08/2023 | 16:03 | SM349B | URBAN | Asset failure | LV | 87.00 | 112.6 | 0.015101 | 0.0001341 | No
17/08/2023 | 16:10 | MTB32 | LONG RURAL | Unknown | Unknown | 16.00 | 192.0 | 0.022046 | 0.0001148 | No
17/08/2023 | 16:14 | PP08 | LONG RURAL | Asset failure | LV | 1.00 | 95.0 | 0.000682 | 0.0000072 | No
17/08/2023 | 17:05 | EL03 | URBAN | Asset failure | LV | 53.00 | 207.0 | 0.016915 | 0.0000817 | No
17/08/2023 | 17:20 | EL10 | URBAN | Overloads |  | 1.00 | 33.0 | 0.000051 | 0.0000015 | No
17/08/2023 | 17:22 | HH341E | URBAN | Asset failure | LV | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
17/08/2023 | 17:28 | HH341A | URBAN | Asset failure | LV | 65.00 | 358.0 | 0.035877 | 0.0001002 | No
17/08/2023 | 17:55 | BM32 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1,060.00 | 77.2 | 0.575749 | 0.0074576 | No
17/08/2023 | 18:14 | VH21 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 109.00 | 178.8 | 0.137115 | 0.0007669 | No
17/08/2023 | 18:42 | AP149H | URBAN | Asset failure | LV | 1.00 | 353.0 | 0.000544 | 0.0000015 | No
17/08/2023 | 20:08 | W04 | LONG RURAL | Unknown | Unknown | 473.00 | 248.0 | 0.841812 | 0.0033944 | No
17/08/2023 | 20:22 | HH522C | URBAN | Overloads |  | 265.00 | 188.1 | 0.076855 | 0.0004086 | No
17/08/2023 | 22:40 | SM179D | URBAN | Unknown | Unknown | 741.00 | 60.3 | 0.068923 | 0.0011424 | No
18/08/2023 | 02:16 | NL115A | URBAN | Asset failure | LV | 14.00 | 507.0 | 0.010943 | 0.0000216 | No
18/08/2023 | 03:13 | GU17 | LONG RURAL | Asset failure | LV | 5.00 | 627.0 | 0.022498 | 0.0000359 | No
18/08/2023 | 06:41 | GA50 | URBAN | Third Party | Other | 529.00 | 136.0 | 0.110920 | 0.0008156 | No
18/08/2023 | 06:51 | NL115B | URBAN | Asset failure | LV | 1.00 | 349.0 | 0.000538 | 0.0000015 | No
18/08/2023 | 07:51 | R12 | LONG RURAL | Overloads |  | 1.00 | 5,983.0 | 0.042936 | 0.0000072 | No
18/08/2023 | 08:24 | MG17 | LONG RURAL | Animal | Animal impact | 1.00 | 307.0 | 0.002203 | 0.0000072 | No
18/08/2023 | 08:35 | SD51300 | LONG RURAL | Planned |  | 1.00 | 372.0 | 0.002670 | 0.0000072 | No
18/08/2023 | 08:35 | SD51300 | SHORT RURAL | Planned |  | 1.00 | 300.0 | 0.002111 | 0.0000070 | No
18/08/2023 | 08:38 | KA01 | SHORT RURAL | Planned |  | 326.00 | 178.2 | 0.408748 | 0.0022936 | No
18/08/2023 | 09:06 | PA19 | LONG RURAL | Planned |  | 29.00 | 224.0 | 0.046617 | 0.0002081 | No
18/08/2023 | 09:11 | LX61 | LONG RURAL | Planned |  | 2.00 | 190.0 | 0.002727 | 0.0000144 | No
18/08/2023 | 09:23 | BU05 | LONG RURAL | Asset failure | HV | 26.00 | 96.8 | 0.018056 | 0.0001866 | No
18/08/2023 | 09:23 | MV13 | SHORT RURAL | Planned |  | 61.00 | 119.7 | 0.051387 | 0.0004292 | No
18/08/2023 | 09:39 | CV08 | LONG RURAL | Planned |  | 67.00 | 246.0 | 0.118280 | 0.0004808 | No
18/08/2023 | 09:51 | MI32 | LONG RURAL | Asset failure | LV | 36.00 | 65.8 | 0.016994 | 0.0002583 | No
18/08/2023 | 09:59 | BU05 | LONG RURAL | Asset failure | LV | 1.00 | 76.0 | 0.000545 | 0.0000072 | No
18/08/2023 | 10:45 | CN21 | LONG RURAL | Asset failure | LV | 3.00 | 490.0 | 0.010549 | 0.0000215 | No
18/08/2023 | 10:51 | SG09 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 26.00 | 246.5 | 0.045097 | 0.0001829 | No
18/08/2023 | 11:13 | HH341J | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
18/08/2023 | 11:23 | AP214A | URBAN | Planned |  | 103.00 | 10.0 | 0.001588 | 0.0001588 | No
18/08/2023 | 11:30 | NL210A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 63.33 | 59.0 | 0.005761 | 0.0000976 | No
18/08/2023 | 12:23 | EL10 | URBAN | Asset failure | LV | 5.00 | 150.0 | 0.001156 | 0.0000077 | No
18/08/2023 | 13:42 | HH177G | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
18/08/2023 | 13:44 | MG17 | LONG RURAL | Animal | Animal impact | 1.00 | 9.0 | 0.000065 | 0.0000072 | No
18/08/2023 | 13:59 | GU43 | LONG RURAL | Overloads |  | 3.00 | 355.0 | 0.007643 | 0.0000215 | No
18/08/2023 | 14:10 | HH148B | URBAN | Overloads |  | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
18/08/2023 | 14:18 | VH21 | SHORT RURAL | Asset failure | HV | 273.00 | 156.0 | 0.299627 | 0.0019207 | No
18/08/2023 | 14:23 | NL760B | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
18/08/2023 | 14:32 | CL19 | LONG RURAL | Planned |  | 2.00 | 51.0 | 0.000732 | 0.0000144 | No
18/08/2023 | 14:37 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 324.0 | 0.002279 | 0.0000070 | No
18/08/2023 | 17:25 | MTB11 | SHORT RURAL | Asset failure | LV | 1.00 | 1,084.0 | 0.007626 | 0.0000070 | No
18/08/2023 | 17:26 | YK25 | LONG RURAL | Unknown | Unknown | 1.00 | 121.0 | 0.000868 | 0.0000072 | No
18/08/2023 | 18:15 | AP149H | URBAN | Asset failure | LV | 1.00 | 262.0 | 0.000404 | 0.0000015 | No
18/08/2023 | 19:51 | EL11 | URBAN | Overloads |  | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
18/08/2023 | 23:45 | HH429C | URBAN | Asset failure | LV | 1.00 | 335.0 | 0.000516 | 0.0000015 | No
19/08/2023 | 04:54 | NL234E | URBAN | Asset failure | LV | 11.33 | 222.0 | 0.003879 | 0.0000175 | No
19/08/2023 | 06:51 | HH403A | URBAN | Unknown | Unknown | 1,519.00 | 87.0 | 0.203747 | 0.0023419 | No
19/08/2023 | 07:29 | SA520J | URBAN | Planned |  | 1.00 | 581.0 | 0.000896 | 0.0000015 | No
19/08/2023 | 08:03 | EL260A | URBAN | Third Party | Unauthorised access | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
19/08/2023 | 08:39 | AP146C | URBAN | Asset failure | LV | 2.00 | 271.0 | 0.000836 | 0.0000031 | No
19/08/2023 | 08:55 | SA18 | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
19/08/2023 | 09:58 | NL210B | URBAN | Overloads |  | 1.00 | 377.0 | 0.000581 | 0.0000015 | No
19/08/2023 | 10:12 | NU04 | SHORT RURAL | Overloads |  | 1.00 | 216.0 | 0.001520 | 0.0000070 | No
19/08/2023 | 10:49 | AP344D | URBAN | Overloads |  | 1.00 | 343.0 | 0.000529 | 0.0000015 | No
19/08/2023 | 11:30 | AP226C | URBAN | Overloads |  | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
19/08/2023 | 12:47 | SM179D | URBAN | Asset failure | LV | 36.00 | 94.0 | 0.005217 | 0.0000555 | No
19/08/2023 | 14:22 | NL111C | URBAN | Asset failure | LV | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
19/08/2023 | 16:09 | NL210C | URBAN | Overloads |  | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
19/08/2023 | 16:29 | SA17 | URBAN | Asset failure | LV | 1.00 | 96.0 | 0.000148 | 0.0000015 | No
19/08/2023 | 17:02 | NL210D | URBAN | Unknown | Unknown | 1.00 | 68.0 | 0.000105 | 0.0000015 | No
19/08/2023 | 18:28 | NL111B | URBAN | Asset failure | LV | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
19/08/2023 | 18:46 | NL451C | URBAN | Asset failure | LV | 1.00 | 316.0 | 0.000487 | 0.0000015 | No
19/08/2023 | 19:05 | SM350B | URBAN | Overloads |  | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
19/08/2023 | 19:19 | SM350B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
19/08/2023 | 20:10 | NL115B | URBAN | Asset failure | LV | 15.00 | 271.0 | 0.006267 | 0.0000231 | No
19/08/2023 | 20:45 | AP214C | URBAN | Overloads |  | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
20/08/2023 | 02:48 | SA34 | URBAN | Overloads |  | 1.00 | 308.0 | 0.000475 | 0.0000015 | No
20/08/2023 | 02:51 | NL210A | URBAN | Overloads |  | 7.67 | 183.0 | 0.002163 | 0.0000118 | No
20/08/2023 | 02:54 | EL17 | URBAN | Unknown | Unknown | 2.00 | 360.0 | 0.001110 | 0.0000031 | No
20/08/2023 | 05:30 | KI32 | SHORT RURAL | Planned |  | 10.00 | 201.0 | 0.014141 | 0.0000704 | No
20/08/2023 | 06:00 | NL451E | URBAN | Unknown | Unknown | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
20/08/2023 | 08:08 | PL04 | URBAN | Planned |  | 134.00 | 456.0 | 0.094207 | 0.0002066 | No
20/08/2023 | 08:09 | SD46201 | LONG RURAL | Unknown | Unknown | 3,017.00 | 190.0 | 4.113687 | 0.0216510 | No
20/08/2023 | 09:13 | NU21 | LONG RURAL | Planned |  | 90.00 | 146.0 | 0.094297 | 0.0006459 | No
20/08/2023 | 09:40 | PP09 | LONG RURAL | Asset failure | LV | 1.00 | 216.0 | 0.001550 | 0.0000072 | No
20/08/2023 | 10:19 | AP372F | URBAN | Asset failure | LV | 3.00 | 301.0 | 0.001392 | 0.0000046 | No
20/08/2023 | 10:31 | EL01X | URBAN | Overloads |  | 2.00 | 41.0 | 0.000126 | 0.0000031 | No
20/08/2023 | 11:27 | NA24 | LONG RURAL | Unknown | Unknown | 38.00 | 197.2 | 0.053779 | 0.0002727 | No
20/08/2023 | 13:49 | NL115B | URBAN | Unknown | Unknown | 1.00 | 298.0 | 0.000459 | 0.0000015 | No
20/08/2023 | 14:28 | HH428B | URBAN | Asset failure | LV | 19.00 | 197.9 | 0.005797 | 0.0000293 | No
20/08/2023 | 14:54 | SM137D | URBAN | Asset failure | LV | 1.00 | 668.0 | 0.001030 | 0.0000015 | No
20/08/2023 | 14:58 | AP226D | URBAN | Asset failure | LV | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
20/08/2023 | 15:30 | R23 | LONG RURAL | Asset failure | LV | 1.00 | 219.0 | 0.001572 | 0.0000072 | No
20/08/2023 | 15:42 | HH177E | URBAN | Asset failure | LV | 61.00 | 138.0 | 0.012978 | 0.0000940 | No
20/08/2023 | 16:34 | SM374C | URBAN | Asset failure | LV | 109.00 | 434.0 | 0.072934 | 0.0001681 | No
20/08/2023 | 16:48 | HH177D | URBAN | Asset failure | LV | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
20/08/2023 | 18:27 | SA711C | URBAN | Asset failure | HV | 635.33 | 235.0 | 0.230201 | 0.0009795 | No
20/08/2023 | 18:53 | SM349A | URBAN | Unknown | Unknown | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
20/08/2023 | 19:21 | MI03 | LONG RURAL | Weather |  | 8.00 | 112.0 | 0.006430 | 0.0000574 | No
20/08/2023 | 19:21 | MI17 | LONG RURAL | Asset failure | HV | 5.00 | 961.0 | 0.034482 | 0.0000359 | No
20/08/2023 | 20:00 | SM350E | URBAN | Unknown | Unknown | 1.00 | 763.0 | 0.001176 | 0.0000015 | No
20/08/2023 | 20:27 | SA711C | URBAN | Unknown | Unknown | 1.00 | 2,549.0 | 0.003930 | 0.0000015 | No
20/08/2023 | 20:27 | SA711C | URBAN | Unknown | Unknown | 1.00 | 576.0 | 0.000888 | 0.0000015 | No
20/08/2023 | 20:41 | HH177C | URBAN | Asset failure | LV | 1.00 | 247.0 | 0.000381 | 0.0000015 | No
20/08/2023 | 21:08 | G29 | LONG RURAL | Asset failure | LV | 2.00 | 970.0 | 0.013922 | 0.0000144 | No
20/08/2023 | 22:48 | GA25 | SHORT RURAL | Asset failure | LV | 1.00 | 28.0 | 0.000197 | 0.0000070 | No
20/08/2023 | 22:52 | HH177G | URBAN | Overloads |  | 1.00 | 16.0 | 0.000025 | 0.0000015 | No
20/08/2023 | 23:51 | SM350F | URBAN | Asset failure | LV | 32.00 | 108.0 | 0.005328 | 0.0000493 | No
21/08/2023 | 00:02 | ME427F | URBAN | Asset failure | LV | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
21/08/2023 | 03:39 | HH428A | URBAN | Unknown | Unknown | 2.00 | 267.0 | 0.000823 | 0.0000031 | No
21/08/2023 | 07:03 | SD35403 | SHORT RURAL | Animal | Animal impact | 2.00 | 522.0 | 0.007345 | 0.0000141 | No
21/08/2023 | 07:08 | HH341E | URBAN | Overloads |  | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
21/08/2023 | 08:51 | HH130B | URBAN | Asset failure | LV | 9.00 | 76.0 | 0.001055 | 0.0000139 | No
21/08/2023 | 08:53 | NL111Q | URBAN | Planned |  | 111.00 | 392.0 | 0.067085 | 0.0001711 | No
21/08/2023 | 09:18 | MTB54 | LONG RURAL | Planned |  | 2.00 | 190.0 | 0.002727 | 0.0000144 | No
21/08/2023 | 09:21 | NL234C | URBAN | Asset failure | LV | 24.67 | 161.0 | 0.006123 | 0.0000380 | No
21/08/2023 | 09:32 | CM12 | LONG RURAL | Planned |  | 71.00 | 282.0 | 0.143684 | 0.0005095 | No
21/08/2023 | 09:36 | SG02 | URBAN | Planned |  | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
21/08/2023 | 09:36 | BU13 | LONG RURAL | Planned |  | 6.00 | 185.0 | 0.007966 | 0.0000431 | No
21/08/2023 | 10:06 | BU11 | SHORT RURAL | Planned |  | 7.00 | 235.0 | 0.011573 | 0.0000492 | No
21/08/2023 | 10:08 | HH130A | URBAN | Asset failure | LV | 1.00 | 393.0 | 0.000606 | 0.0000015 | No
21/08/2023 | 10:17 | CV03 | SHORT RURAL | Asset failure | HV | 89.00 | 381.1 | 0.238644 | 0.0006262 | No
21/08/2023 | 10:19 | MI11 | LONG RURAL | Planned |  | 43.00 | 199.0 | 0.061408 | 0.0003086 | No
21/08/2023 | 10:21 | SB22 | LONG RURAL | Planned |  | 47.00 | 199.0 | 0.067120 | 0.0003373 | No
21/08/2023 | 11:22 | BM34 | SHORT RURAL | Asset failure | LV | 2.00 | 284.0 | 0.003996 | 0.0000141 | No
21/08/2023 | 12:43 | AP529C | URBAN | Asset failure | LV | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
21/08/2023 | 13:51 | HH403D | URBAN | Unknown | Unknown | 1.00 | 411.0 | 0.000634 | 0.0000015 | No
21/08/2023 | 14:54 | MG30 | LONG RURAL | Asset failure | LV | 2.00 | 136.0 | 0.001952 | 0.0000144 | No
21/08/2023 | 15:02 | W30 | LONG RURAL | Unknown | Unknown | 2.00 | 122.0 | 0.001751 | 0.0000144 | No
21/08/2023 | 15:49 | HH428F | URBAN | Asset failure | LV | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
21/08/2023 | 15:57 | HH177B | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
21/08/2023 | 17:15 | SA11 | URBAN | Asset failure | LV | 45.00 | 84.0 | 0.005828 | 0.0000694 | No
21/08/2023 | 17:28 | AP132E | URBAN | Unknown | Unknown | 1.00 | 55.0 | 0.000085 | 0.0000015 | No
21/08/2023 | 17:37 | NL451E | URBAN | Asset failure | LV | 1.00 | 492.0 | 0.000759 | 0.0000015 | No
21/08/2023 | 17:53 | WK72 | SHORT RURAL | Asset failure | HV | 1.00 | 55.0 | 0.000387 | 0.0000070 | No
21/08/2023 | 18:03 | EL09 | URBAN | Asset failure | LV | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
21/08/2023 | 18:06 | SM126A | URBAN | Asset failure | LV | 31.00 | 136.9 | 0.006542 | 0.0000478 | No
21/08/2023 | 18:36 | AP529C | URBAN | Asset failure | LV | 22.00 | 89.0 | 0.003019 | 0.0000339 | No
21/08/2023 | 19:26 | AP149E | URBAN | Asset failure | LV | 1.00 | 1,833.0 | 0.002826 | 0.0000015 | No
21/08/2023 | 19:41 | HH148A | URBAN | Asset failure | LV | 1.00 | 158.0 | 0.000244 | 0.0000015 | No
21/08/2023 | 19:47 | CM02 | LONG RURAL | Unknown | Unknown | 70.00 | 153.0 | 0.076858 | 0.0005023 | No
21/08/2023 | 20:59 | ME347F | URBAN | Weather |  | 19.33 | 84.0 | 0.002504 | 0.0000298 | No
21/08/2023 | 23:02 | HH145E | URBAN | Asset failure | LV | 1.00 | 36.0 | 0.000056 | 0.0000015 | No
21/08/2023 | 23:20 | MV22 | SHORT RURAL | Weather |  | 60.00 | 174.0 | 0.073451 | 0.0004221 | No
21/08/2023 | 23:25 | SA17 | URBAN | Asset failure | LV | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
22/08/2023 | 00:17 | SD34102 | LONG RURAL | Weather |  | 3.00 | 830.0 | 0.017869 | 0.0000215 | No
22/08/2023 | 02:02 | SM179D | URBAN | Asset failure | LV | 25.33 | 280.0 | 0.010936 | 0.0000391 | No
22/08/2023 | 03:12 | AP149A | URBAN | Weather |  | 36.67 | 99.0 | 0.005597 | 0.0000565 | No
22/08/2023 | 03:20 | SG12 | SHORT RURAL | Overloads |  | 11.00 | 951.0 | 0.073598 | 0.0000774 | No
22/08/2023 | 03:42 | AP227D | URBAN | Asset failure | LV | 1.00 | 336.0 | 0.000518 | 0.0000015 | No
22/08/2023 | 05:18 | SM349F | URBAN | Asset failure | LV | 50.00 | 535.0 | 0.041242 | 0.0000771 | No
22/08/2023 | 07:01 | LX31 | SHORT RURAL | Unknown | Unknown | 6.00 | 64.0 | 0.002702 | 0.0000422 | No
22/08/2023 | 07:24 | MTB12 | SHORT RURAL | Overloads |  | 1.00 | 1,034.0 | 0.007275 | 0.0000070 | No
22/08/2023 | 07:28 | HH145A | URBAN | Asset failure | LV | 1.00 | 570.0 | 0.000879 | 0.0000015 | No
22/08/2023 | 07:34 | HH341D | URBAN | Asset failure | LV | 46.00 | 384.0 | 0.027234 | 0.0000709 | No
22/08/2023 | 07:43 | HH341C | URBAN | Asset failure | LV | 1.00 | 73.0 | 0.000113 | 0.0000015 | No
22/08/2023 | 07:46 | WHY02 | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
22/08/2023 | 08:19 | MI08 | LONG RURAL | Asset failure | LV | 50.00 | 98.0 | 0.035164 | 0.0003588 | No
22/08/2023 | 08:31 | HH145A | URBAN | Asset failure | LV | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
22/08/2023 | 08:40 | NL234E | URBAN | Asset failure | LV | 11.33 | 96.0 | 0.001677 | 0.0000175 | No
22/08/2023 | 09:24 | HH102B | URBAN | Planned |  | 46.00 | 320.0 | 0.022695 | 0.0000709 | No
22/08/2023 | 09:26 | HH102B | URBAN | Planned |  | 12.00 | 319.0 | 0.005902 | 0.0000185 | No
22/08/2023 | 09:26 | HH102B | URBAN | Planned |  | 52.00 | 318.0 | 0.025494 | 0.0000802 | No
22/08/2023 | 09:28 | SB18 | LONG RURAL | Planned |  | 26.00 | 159.0 | 0.029667 | 0.0001866 | No
22/08/2023 | 09:28 | KI31 | SHORT RURAL | Planned |  | 1.00 | 142.0 | 0.000999 | 0.0000070 | No
22/08/2023 | 09:48 | HK03 | LONG RURAL | Planned |  | 4.00 | 204.0 | 0.005856 | 0.0000287 | No
22/08/2023 | 10:16 | W26 | LONG RURAL | Planned |  | 27.00 | 263.0 | 0.050959 | 0.0001938 | No
22/08/2023 | 10:29 | NL234E | URBAN | Asset failure | LV | 17.00 | 282.0 | 0.007391 | 0.0000262 | No
22/08/2023 | 10:38 | EL260C | URBAN | Asset failure | LV | 73.00 | 34.0 | 0.003827 | 0.0001125 | No
22/08/2023 | 11:11 | YK21 | LONG RURAL | Planned |  | 10.00 | 104.0 | 0.007463 | 0.0000718 | No
22/08/2023 | 11:45 | SM350F | URBAN | Asset failure | LV | 1.00 | 809.0 | 0.001247 | 0.0000015 | No
22/08/2023 | 12:04 | MV62 | SHORT RURAL | Planned |  | 2.00 | 35.0 | 0.000492 | 0.0000141 | No
22/08/2023 | 12:55 | VH12 | SHORT RURAL | Asset failure | LV | 14.00 | 108.0 | 0.010638 | 0.0000985 | No
22/08/2023 | 13:19 | HH145E | URBAN | Weather |  | 15.00 | 65.0 | 0.001503 | 0.0000231 | No
22/08/2023 | 13:23 | SG05 | SHORT RURAL | Other |  | 23.67 | 109.7 | 0.018271 | 0.0001665 | No
22/08/2023 | 14:28 | SM179D | URBAN | Overloads |  | 1.00 | 304.0 | 0.000469 | 0.0000015 | No
22/08/2023 | 16:06 | SD34102 | LONG RURAL | Unknown | Unknown | 3.00 | 125.0 | 0.002691 | 0.0000215 | No
22/08/2023 | 16:40 | NL111C | URBAN | Asset failure | LV | 1.00 | 335.0 | 0.000516 | 0.0000015 | No
22/08/2023 | 18:08 | VH22 | SHORT RURAL | Asset failure | LV | 2.00 | 185.0 | 0.002603 | 0.0000141 | No
22/08/2023 | 18:25 | HH145A | URBAN | Asset failure | LV | 2.00 | 371.5 | 0.001146 | 0.0000031 | No
22/08/2023 | 18:25 | HH177G | URBAN | Asset failure | LV | 18.00 | 292.0 | 0.008103 | 0.0000278 | No
22/08/2023 | 19:06 | NL760B | URBAN | Asset failure | LV | 1.00 | 232.0 | 0.000358 | 0.0000015 | No
22/08/2023 | 20:46 | MB12 | SHORT RURAL | Planned |  | 69.00 | 374.1 | 0.181600 | 0.0004854 | No
22/08/2023 | 20:57 | SM216A | URBAN | Planned |  | 140.00 | 450.0 | 0.097130 | 0.0002158 | No
22/08/2023 | 22:43 | HH107C | URBAN | Asset failure | LV | 1.00 | 278.0 | 0.000429 | 0.0000015 | No
23/08/2023 | 08:56 | HH107B | URBAN | Asset failure | LV | 22.00 | 92.0 | 0.003121 | 0.0000339 | No
23/08/2023 | 09:05 | BS0396 | SHORT RURAL | Planned |  | 1.00 | 3,060.0 | 0.021529 | 0.0000070 | No
23/08/2023 | 09:07 | PA15 | LONG RURAL | Planned |  | 11.00 | 55.0 | 0.004342 | 0.0000789 | No
23/08/2023 | 09:09 | MV61 | SHORT RURAL | Planned |  | 130.00 | 121.1 | 0.110732 | 0.0009146 | No
23/08/2023 | 09:09 | MV61 | URBAN | Planned |  | 753.00 | 103.6 | 0.120328 | 0.0011609 | No
23/08/2023 | 09:15 | EL17 | URBAN | Planned |  | 20.00 | 96.0 | 0.002960 | 0.0000308 | No
23/08/2023 | 09:20 | GA53 | SHORT RURAL | Planned |  | 8.00 | 296.0 | 0.016660 | 0.0000563 | No
23/08/2023 | 09:21 | SA18 | URBAN | Asset failure | LV | 56.00 | 519.7 | 0.044868 | 0.0000863 | No
23/08/2023 | 09:24 | PL33 | LONG RURAL | Planned |  | 1.00 | 301.0 | 0.002160 | 0.0000072 | No
23/08/2023 | 10:02 | W27 | LONG RURAL | Planned |  | 77.00 | 292.0 | 0.161353 | 0.0005526 | No
23/08/2023 | 10:03 | GA21 | LONG RURAL | Planned |  | 29.00 | 227.0 | 0.047242 | 0.0002081 | No
23/08/2023 | 10:15 | HH107A | URBAN | Overloads |  | 2.00 | 204.0 | 0.000629 | 0.0000031 | No
23/08/2023 | 10:16 | MTB11 | SHORT RURAL | Asset failure | LV | 1.00 | 250.0 | 0.001759 | 0.0000070 | No
23/08/2023 | 10:17 | YK03 | LONG RURAL | Planned |  | 51.00 | 266.0 | 0.097354 | 0.0003660 | No
23/08/2023 | 11:13 | HH428A | URBAN | Asset failure | LV | 12.00 | 62.0 | 0.001147 | 0.0000185 | No
23/08/2023 | 11:20 | MG41 | URBAN | Unknown | Unknown | 28.67 | 127.0 | 0.005613 | 0.0000442 | No
23/08/2023 | 11:31 | MG41 | URBAN | Unknown | Unknown | 1.00 | 122.0 | 0.000188 | 0.0000015 | No
23/08/2023 | 11:57 | NL210E | URBAN | Asset failure | LV | 78.00 | 198.0 | 0.023811 | 0.0001203 | No
23/08/2023 | 12:23 | BT02 | LONG RURAL | Asset failure | HV | 97.00 | 307.6 | 0.214156 | 0.0006961 | No
23/08/2023 | 16:20 | SM179C | URBAN | Overloads |  | 1.00 | 371.0 | 0.000572 | 0.0000015 | No
23/08/2023 | 16:51 | HH386D | URBAN | Asset failure | LV | 1.00 | 565.0 | 0.000871 | 0.0000015 | No
23/08/2023 | 17:02 | M22 | LONG RURAL | Planned |  | 9.00 | 14.0 | 0.000904 | 0.0000646 | No
23/08/2023 | 17:20 | ME347F | URBAN | Asset failure | LV | 41.00 | 73.0 | 0.004614 | 0.0000632 | No
23/08/2023 | 19:29 | HH177B | URBAN | Asset failure | LV | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
23/08/2023 | 20:16 | HH177A | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
23/08/2023 | 20:16 | G10 | LONG RURAL | Overloads |  | 1.00 | 291.0 | 0.002088 | 0.0000072 | No
24/08/2023 | 01:45 | MT03 | LONG RURAL | Asset failure | LV | 28.00 | 183.0 | 0.036772 | 0.0002009 | No
24/08/2023 | 06:42 | BU02 | LONG RURAL | Unknown | Unknown | 97.00 | 240.2 | 0.167230 | 0.0006961 | No
24/08/2023 | 08:29 | SM411D | URBAN | Asset failure | LV | 11.00 | 248.0 | 0.004206 | 0.0000170 | No
24/08/2023 | 08:39 | CD02 | LONG RURAL | Planned |  | 58.00 | 84.3 | 0.035099 | 0.0004162 | No
24/08/2023 | 08:46 | ME347F | URBAN | Planned |  | 27.00 | 318.0 | 0.013237 | 0.0000416 | No
24/08/2023 | 08:52 | NL760B | URBAN | Planned |  | 72.00 | 294.0 | 0.032636 | 0.0001110 | No
24/08/2023 | 08:54 | SA18 | URBAN | Planned |  | 135.00 | 286.2 | 0.059569 | 0.0002081 | No
24/08/2023 | 09:04 | AP355A | URBAN | Planned |  | 146.00 | 366.0 | 0.082385 | 0.0002251 | No
24/08/2023 | 09:07 | SM172E | URBAN | Planned |  | 54.00 | 319.0 | 0.026558 | 0.0000833 | No
24/08/2023 | 09:18 | HH107A | URBAN | Asset failure | LV | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
24/08/2023 | 09:34 | YK01 | LONG RURAL | Planned |  | 69.00 | 345.0 | 0.170833 | 0.0004952 | No
24/08/2023 | 09:38 | KA14 | LONG RURAL | Planned |  | 2.00 | 143.0 | 0.002052 | 0.0000144 | No
24/08/2023 | 09:53 | BT06 | LONG RURAL | Planned |  | 1.00 | 307.0 | 0.002203 | 0.0000072 | No
24/08/2023 | 10:01 | EL15 | URBAN | Planned |  | 4.00 | 182.0 | 0.001122 | 0.0000062 | No
24/08/2023 | 10:26 | G31 | LONG RURAL | Planned |  | 2.00 | 140.0 | 0.002009 | 0.0000144 | No
24/08/2023 | 10:36 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 90.0 | 0.000633 | 0.0000070 | No
24/08/2023 | 11:00 | HH118C | URBAN | Asset failure | LV | 24.00 | 119.0 | 0.004403 | 0.0000370 | No
24/08/2023 | 11:03 | PP14 | LONG RURAL | Asset failure | LV | 2.00 | 146.0 | 0.002095 | 0.0000144 | No
24/08/2023 | 11:22 | KA11 | LONG RURAL | Overloads |  | 2.00 | 217.0 | 0.003115 | 0.0000144 | No
24/08/2023 | 11:33 | NU13 | LONG RURAL | Unknown | Unknown | 1.00 | 61.0 | 0.000438 | 0.0000072 | No
24/08/2023 | 11:44 | W26 | LONG RURAL | Third Party | Vehicle impact | 101.00 | 216.7 | 0.157032 | 0.0007248 | No
24/08/2023 | 11:59 | MV52 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 21.00 | 109.0 | 0.016104 | 0.0001477 | No
24/08/2023 | 13:33 | ME347F | URBAN | Asset failure | LV | 3.00 | 85.0 | 0.000393 | 0.0000046 | No
24/08/2023 | 13:46 | MG02 | LONG RURAL | Unknown | Unknown | 1.00 | 73.0 | 0.000524 | 0.0000072 | No
24/08/2023 | 13:57 | SM411D | URBAN | Asset failure | LV | 33.00 | 507.0 | 0.025795 | 0.0000509 | No
24/08/2023 | 16:01 | EL14 | URBAN | Asset failure | LV | 14.67 | 125.0 | 0.002827 | 0.0000226 | No
24/08/2023 | 18:09 | EL20 | URBAN | Overloads |  | 3.00 | 254.0 | 0.001175 | 0.0000046 | No
24/08/2023 | 18:15 | HH386G | URBAN | Asset failure | LV | 20.33 | 225.0 | 0.007054 | 0.0000313 | No
24/08/2023 | 19:56 | EL01Q | URBAN | Overloads |  | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
24/08/2023 | 20:05 | AP132A | URBAN | Asset failure | LV | 2.33 | 189.0 | 0.000680 | 0.0000036 | No
24/08/2023 | 21:49 | AP132C | URBAN | Vegetation | Grow-in - NSP responsibility | 16.00 | 109.0 | 0.002689 | 0.0000247 | No
24/08/2023 | 22:12 | HH386G | URBAN | Asset failure | LV | 20.33 | 142.0 | 0.004452 | 0.0000313 | No
25/08/2023 | 07:19 | HH121B | URBAN | Asset failure | LV | 13.33 | 123.0 | 0.002528 | 0.0000206 | No
25/08/2023 | 08:03 | AP227D | URBAN | Overloads |  | 1.00 | 346.0 | 0.000533 | 0.0000015 | No
25/08/2023 | 08:07 | YK26 | SHORT RURAL | Planned |  | 1.00 | 387.0 | 0.002723 | 0.0000070 | No
25/08/2023 | 08:09 | NL451A | URBAN | Asset failure | LV | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
25/08/2023 | 08:24 | SA18 | URBAN | Planned |  | 101.00 | 339.2 | 0.052814 | 0.0001557 | No
25/08/2023 | 08:32 | SM411D | URBAN | Asset failure | LV | 8.00 | 589.8 | 0.007274 | 0.0000123 | No
25/08/2023 | 08:50 | AP214A | URBAN | Asset failure | LV | 80.00 | 64.0 | 0.007894 | 0.0001233 | No
25/08/2023 | 09:08 | SA14 | URBAN | Overloads |  | 1.00 | 436.0 | 0.000672 | 0.0000015 | No
25/08/2023 | 09:12 | MV62 | SHORT RURAL | Planned |  | 135.00 | 307.7 | 0.292219 | 0.0009498 | No
25/08/2023 | 09:13 | BU04 | LONG RURAL | Planned |  | 3.00 | 136.0 | 0.002928 | 0.0000215 | No
25/08/2023 | 09:20 | SA31 | URBAN | Asset failure | LV | 9.00 | 357.0 | 0.004954 | 0.0000139 | No
25/08/2023 | 09:25 | SG09 | SHORT RURAL | Planned |  | 35.00 | 298.0 | 0.073380 | 0.0002462 | No
25/08/2023 | 09:29 | HH121E | URBAN | Planned |  | 31.00 | 42.0 | 0.002007 | 0.0000478 | No
25/08/2023 | 10:02 | CM03 | LONG RURAL | Planned |  | 1.00 | 58.0 | 0.000416 | 0.0000072 | No
25/08/2023 | 10:02 | SG09 | SHORT RURAL | Planned |  | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
25/08/2023 | 10:04 | CV753A | LONG RURAL | Planned |  | 6.00 | 273.0 | 0.011755 | 0.0000431 | No
25/08/2023 | 10:08 | MI04 | LONG RURAL | Third Party | Vehicle impact | 49.00 | 280.4 | 0.098610 | 0.0003516 | No
25/08/2023 | 10:09 | AP146C | URBAN | Other |  | 1.00 | 271.0 | 0.000418 | 0.0000015 | No
25/08/2023 | 10:29 | R06 | LONG RURAL | Planned |  | 1.00 | 70.0 | 0.000502 | 0.0000072 | No
25/08/2023 | 11:14 | NL115E | URBAN | Asset failure | LV | 25.67 | 25.0 | 0.000989 | 0.0000396 | No
25/08/2023 | 12:11 | MG06 | SHORT RURAL | Asset failure | LV | 2.00 | 412.0 | 0.005797 | 0.0000141 | No
25/08/2023 | 13:09 | SG09 | SHORT RURAL | Planned |  | 1.00 | 112.0 | 0.000788 | 0.0000070 | No
25/08/2023 | 13:39 | LX51 | SHORT RURAL | Asset failure | LV | 1.00 | 231.0 | 0.001625 | 0.0000070 | No
25/08/2023 | 14:31 | HH121E | URBAN | Asset failure | LV | 37.00 | 281.0 | 0.016030 | 0.0000570 | No
25/08/2023 | 15:24 | SG08 | SHORT RURAL | Asset failure | HV | 78.00 | 166.4 | 0.091293 | 0.0005488 | No
25/08/2023 | 15:36 | MTB21 | SHORT RURAL | Unknown | Unknown | 38.00 | 290.0 | 0.077531 | 0.0002673 | No
25/08/2023 | 17:30 | HH121B | URBAN | Overloads |  | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
25/08/2023 | 18:13 | NL451A | URBAN | Asset failure | LV | 12.00 | 1,391.0 | 0.025735 | 0.0000185 | No
25/08/2023 | 18:19 | W06 | LONG RURAL | Unknown | Unknown | 1.00 | 333.0 | 0.002390 | 0.0000072 | No
25/08/2023 | 18:25 | M13 | LONG RURAL | Asset failure | HV | 1,017.00 | 141.2 | 1.030270 | 0.0072983 | No
25/08/2023 | 20:14 | SD49100 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 42.0 | 0.000301 | 0.0000072 | No
25/08/2023 | 21:04 | ME427D | URBAN | Unknown | Unknown | 11.00 | 114.0 | 0.001933 | 0.0000170 | No
26/08/2023 | 00:54 | HH496D | URBAN | Asset failure | LV | 10.00 | 196.0 | 0.003022 | 0.0000154 | No
26/08/2023 | 04:41 | SM216G | URBAN | Third Party | Vehicle impact | 71.00 | 394.2 | 0.043148 | 0.0001095 | No
26/08/2023 | 08:25 | HH496D | URBAN | Asset failure | LV | 1.00 | 364.0 | 0.000561 | 0.0000015 | No
26/08/2023 | 08:52 | SA18 | URBAN | Other |  | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
26/08/2023 | 08:55 | CV25 | LONG RURAL | Planned |  | 13.00 | 453.0 | 0.042261 | 0.0000933 | No
26/08/2023 | 09:24 | SM349H | URBAN | Asset failure | LV | 1.00 | 357.0 | 0.000550 | 0.0000015 | No
26/08/2023 | 09:28 | CV25 | LONG RURAL | Planned |  | 6.00 | 322.0 | 0.013865 | 0.0000431 | No
26/08/2023 | 11:14 | NL760B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
26/08/2023 | 11:22 | NA21 | LONG RURAL | Asset failure | HV | 60.00 | 250.0 | 0.107645 | 0.0004306 | No
26/08/2023 | 12:59 | HH121D | URBAN | Asset failure | LV | 16.00 | 811.0 | 0.020006 | 0.0000247 | No
26/08/2023 | 13:09 | HH148A | URBAN | Asset failure | LV | 1.00 | 461.0 | 0.000711 | 0.0000015 | No
26/08/2023 | 13:09 | NL115D | URBAN | Asset failure | LV | 1.00 | 114.0 | 0.000176 | 0.0000015 | No
26/08/2023 | 13:15 | CL09 | LONG RURAL | Unknown | Unknown | 89.00 | 159.0 | 0.101552 | 0.0006387 | No
26/08/2023 | 13:23 | CL09 | LONG RURAL | Unknown | Unknown | 1.00 | 235.0 | 0.001686 | 0.0000072 | No
26/08/2023 | 15:04 | NA21 | LONG RURAL | Asset failure | HV | 1.00 | 8.0 | 0.000057 | 0.0000072 | No
26/08/2023 | 15:07 | MB13 | SHORT RURAL | Asset failure | LV | 28.00 | 66.0 | 0.013002 | 0.0001970 | No
26/08/2023 | 16:08 | CL09 | LONG RURAL | Unknown | Unknown | 1.00 | 71.0 | 0.000510 | 0.0000072 | No
26/08/2023 | 17:12 | AP425C | URBAN | Asset failure | LV | 1.00 | 628.0 | 0.000968 | 0.0000015 | No
26/08/2023 | 18:13 | EL260C | URBAN | Overloads |  | 9.00 | 156.0 | 0.002165 | 0.0000139 | No
26/08/2023 | 18:24 | HH403D | URBAN | Asset failure | LV | 1.00 | 2,481.0 | 0.003825 | 0.0000015 | No
26/08/2023 | 19:33 | EL260C | URBAN | Overloads |  | 2.00 | 1,065.0 | 0.003284 | 0.0000031 | No
26/08/2023 | 20:14 | SA18 | URBAN | Asset failure | LV | 1.00 | 296.0 | 0.000456 | 0.0000015 | No
26/08/2023 | 22:27 | AP424F | URBAN | Asset failure | LV | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
27/08/2023 | 08:40 | CV33 | LONG RURAL | Planned |  | 37.00 | 299.0 | 0.079392 | 0.0002655 | No
27/08/2023 | 09:12 | NL511A | URBAN | Planned |  | 16.00 | 237.0 | 0.005846 | 0.0000247 | No
27/08/2023 | 11:22 | SA32 | URBAN | Asset failure | LV | 1.00 | 337.0 | 0.000520 | 0.0000015 | No
27/08/2023 | 11:44 | SM402D | URBAN | Asset failure | LV | 29.00 | 41.0 | 0.001832 | 0.0000447 | No
27/08/2023 | 12:59 | HH130C | URBAN | Asset failure | LV | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
27/08/2023 | 13:13 | CL09 | LONG RURAL | Asset failure | HV | 10.00 | 159.0 | 0.011410 | 0.0000718 | No
27/08/2023 | 15:01 | NL451C | URBAN | Asset failure | LV | 21.00 | 121.0 | 0.003916 | 0.0000324 | No
27/08/2023 | 18:56 | AP149C | URBAN | Asset failure | LV | 22.00 | 164.0 | 0.005563 | 0.0000339 | No
27/08/2023 | 19:46 | HH145D | URBAN | Asset failure | LV | 31.33 | 100.0 | 0.004831 | 0.0000483 | No
27/08/2023 | 21:28 | NL451E | URBAN | Asset failure | HV | 387.00 | 130.0 | 0.077566 | 0.0005967 | No
27/08/2023 | 21:46 | SD38200 | LONG RURAL | Overloads |  | 1.00 | 303.0 | 0.002174 | 0.0000072 | No
27/08/2023 | 23:18 | HH118C | URBAN | Planned |  | 80.00 | 368.0 | 0.045389 | 0.0001233 | No
28/08/2023 | 08:43 | HH121E | URBAN | Asset failure | LV | 1.00 | 177.0 | 0.000273 | 0.0000015 | No
28/08/2023 | 08:51 | BU09 | LONG RURAL | Planned |  | 23.00 | 45.0 | 0.007428 | 0.0001651 | No
28/08/2023 | 09:08 | AP214D | URBAN | Planned |  | 94.00 | 292.0 | 0.042318 | 0.0001449 | No
28/08/2023 | 09:08 | WK41 | SHORT RURAL | Planned |  | 1.00 | 368.0 | 0.002589 | 0.0000070 | No
28/08/2023 | 09:12 | CL04 | LONG RURAL | Unknown | Unknown | 1.00 | 357.0 | 0.002562 | 0.0000072 | No
28/08/2023 | 09:31 | BT02 | LONG RURAL | Planned |  | 7.00 | 309.0 | 0.015522 | 0.0000502 | No
28/08/2023 | 09:46 | MI08 | LONG RURAL | Planned |  | 48.00 | 279.5 | 0.096278 | 0.0003445 | No
28/08/2023 | 10:23 | G17 | LONG RURAL | Planned |  | 13.00 | 186.8 | 0.017424 | 0.0000933 | No
28/08/2023 | 10:31 | HH177F | URBAN | Asset failure | LV | 26.00 | 921.0 | 0.036919 | 0.0000401 | No
28/08/2023 | 11:01 | EL14 | URBAN | Asset failure | LV | 1.00 | 358.0 | 0.000552 | 0.0000015 | No
28/08/2023 | 11:12 | BU10 | LONG RURAL | Planned |  | 5.00 | 50.0 | 0.001794 | 0.0000359 | No
28/08/2023 | 11:17 | SD46400 | SHORT RURAL | Planned |  | 21.33 | 3.0 | 0.000450 | 0.0001501 | No
28/08/2023 | 11:22 | EL260A | URBAN | Third Party | Vehicle impact | 1.00 | 33.0 | 0.000051 | 0.0000015 | No
28/08/2023 | 11:51 | BM53 | SHORT RURAL | Asset failure | LV | 1.00 | 210.0 | 0.001477 | 0.0000070 | No
28/08/2023 | 12:07 | HH341B | URBAN | Asset failure | LV | 24.00 | 56.0 | 0.002072 | 0.0000370 | No
28/08/2023 | 12:22 | M81 | LONG RURAL | Asset failure | LV | 1.00 | 294.0 | 0.002110 | 0.0000072 | No
28/08/2023 | 13:41 | MI21 | LONG RURAL | Planned |  | 4.00 | 51.0 | 0.001464 | 0.0000287 | No
28/08/2023 | 14:20 | BT26 | LONG RURAL | Asset failure | LV | 2.00 | 234.0 | 0.003359 | 0.0000144 | No
28/08/2023 | 18:03 | G15 | LONG RURAL | Other |  | 1.00 | 344.0 | 0.002469 | 0.0000072 | No
28/08/2023 | 18:21 | AP226D | URBAN | Asset failure | LV | 1.00 | 289.0 | 0.000446 | 0.0000015 | No
28/08/2023 | 18:47 | SG07 | SHORT RURAL | Asset failure | LV | 1.00 | 928.0 | 0.006529 | 0.0000070 | No
28/08/2023 | 19:23 | SM411B | URBAN | Asset failure | LV | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
28/08/2023 | 19:30 | NL544A | URBAN | Vegetation | Grow-in - NSP responsibility | 20.33 | 142.0 | 0.004452 | 0.0000313 | No
28/08/2023 | 22:13 | CBD367S | CBD | Planned |  | 1.00 | 388.0 | 0.056057 | 0.0001445 | No
29/08/2023 | 04:22 | SA17 | URBAN | Asset failure | LV | 1.00 | 558.0 | 0.000860 | 0.0000015 | No
29/08/2023 | 06:10 | HH409F | URBAN | Asset failure | HV | 448.00 | 145.6 | 0.100535 | 0.0006907 | No
29/08/2023 | 07:28 | CBD367A | CBD | Other |  | 1.00 | 208.0 | 0.030051 | 0.0001445 | No
29/08/2023 | 07:48 | NU20 | LONG RURAL | Planned |  | 356.00 | 528.8 | 1.350980 | 0.0025548 | No
29/08/2023 | 08:20 | VH11 | URBAN | Planned |  | 42.00 | 527.0 | 0.034125 | 0.0000648 | No
29/08/2023 | 09:12 | PL12 | LONG RURAL | Planned |  | 1.00 | 273.0 | 0.001959 | 0.0000072 | No
29/08/2023 | 09:26 | BT02 | LONG RURAL | Planned |  | 1.00 | 194.0 | 0.001392 | 0.0000072 | No
29/08/2023 | 09:34 | YK07 | LONG RURAL | Planned |  | 74.00 | 364.0 | 0.193302 | 0.0005310 | No
29/08/2023 | 09:43 | CN42 | LONG RURAL | Planned |  | 71.00 | 167.0 | 0.085090 | 0.0005095 | No
29/08/2023 | 09:46 | G25 | LONG RURAL | Planned |  | 32.00 | 262.0 | 0.060166 | 0.0002296 | No
29/08/2023 | 09:47 | SA20 | URBAN | Planned |  | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
29/08/2023 | 09:49 | ME347C | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
29/08/2023 | 09:49 | SD34102 | LONG RURAL | Planned |  | 3.00 | 295.0 | 0.006351 | 0.0000215 | No
29/08/2023 | 09:58 | CD17 | LONG RURAL | Planned |  | 83.00 | 42.0 | 0.025017 | 0.0005956 | No
29/08/2023 | 10:10 | SM179D | URBAN | Asset failure | LV | 31.00 | 115.0 | 0.005496 | 0.0000478 | No
29/08/2023 | 10:10 | AP149F | URBAN | Network business | Switching and protection error | 1.00 | 468.0 | 0.000722 | 0.0000015 | No
29/08/2023 | 10:15 | NL115D | URBAN | Asset failure | HV | 2,582.00 | 101.5 | 0.404143 | 0.0039808 | No
29/08/2023 | 10:15 | NL115D | URBAN | Asset failure | HV | 42.00 | 1,169.0 | 0.075697 | 0.0000648 | No
29/08/2023 | 10:50 | SA20 | URBAN | Planned |  | 12.00 | 186.0 | 0.003441 | 0.0000185 | No
29/08/2023 | 10:51 | PL01 | URBAN | Asset failure | LV | 2.00 | 116.0 | 0.000358 | 0.0000031 | No
29/08/2023 | 10:55 | MB44 | LONG RURAL | Planned |  | 61.00 | 189.0 | 0.082736 | 0.0004378 | No
29/08/2023 | 11:21 | AP132A | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
29/08/2023 | 11:28 | KA06 | LONG RURAL | Asset failure | LV | 21.00 | 252.0 | 0.037977 | 0.0001507 | No
29/08/2023 | 11:52 | AP829A | URBAN | Asset failure | LV | 13.00 | 45.0 | 0.000902 | 0.0000200 | No
29/08/2023 | 12:08 | KA29 | LONG RURAL | Third Party | Vehicle impact | 43.00 | 215.0 | 0.066345 | 0.0003086 | No
29/08/2023 | 12:59 | SM374B | URBAN | Asset failure | LV | 128.00 | 263.6 | 0.052022 | 0.0001973 | No
29/08/2023 | 13:01 | SA711C | URBAN | Asset failure | LV | 1.00 | 469.0 | 0.000723 | 0.0000015 | No
29/08/2023 | 13:06 | ME200B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.00 | 53.0 | 0.002288 | 0.0000432 | No
29/08/2023 | 13:35 | VH45 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 20.00 | 82.0 | 0.011538 | 0.0001407 | No
29/08/2023 | 13:43 | SA16 | URBAN | Asset failure | LV | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
29/08/2023 | 14:23 | HH386B | URBAN | Asset failure | LV | 48.00 | 224.6 | 0.016619 | 0.0000740 | No
29/08/2023 | 14:39 | GA22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1,253.00 | 36.7 | 0.323365 | 0.0088155 | No
29/08/2023 | 14:46 | CN21 | LONG RURAL | Asset failure | HV | 1.00 | 1,281.0 | 0.009193 | 0.0000072 | No
29/08/2023 | 15:35 | SM411B | URBAN | Asset failure | LV | 1.00 | 372.0 | 0.000574 | 0.0000015 | No
29/08/2023 | 15:37 | LX42 | SHORT RURAL | Asset failure | HV | 120.00 | 419.0 | 0.353744 | 0.0008443 | No
29/08/2023 | 15:45 | LX43 | SHORT RURAL | Asset failure | LV | 2.00 | 1,494.0 | 0.021022 | 0.0000141 | No
29/08/2023 | 16:08 | CBD27P | CBD | Unknown | Unknown | 1.00 | 292.0 | 0.042187 | 0.0001445 | No
29/08/2023 | 16:50 | EL260D | URBAN | Asset failure | LV | 17.00 | 440.0 | 0.011532 | 0.0000262 | No
29/08/2023 | 17:09 | CN24 | LONG RURAL | Asset failure | LV | 66.00 | 47.0 | 0.022261 | 0.0004736 | No
29/08/2023 | 17:19 | HH386C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 64.00 | 73.0 | 0.007203 | 0.0000987 | No
29/08/2023 | 18:07 | SM172F | URBAN | Asset failure | LV | 4.00 | 345.0 | 0.002128 | 0.0000062 | No
29/08/2023 | 18:21 | HH386B | URBAN | Asset failure | LV | 15.67 | 21.0 | 0.000507 | 0.0000242 | No
29/08/2023 | 18:24 | PP06 | LONG RURAL | Other |  | 2.00 | 170.0 | 0.002440 | 0.0000144 | No
29/08/2023 | 18:34 | HH386B | URBAN | Unknown | Unknown | 1.00 | 19.0 | 0.000029 | 0.0000015 | No
29/08/2023 | 19:27 | HH121E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,879.00 | 122.1 | 0.353708 | 0.0028970 | No
29/08/2023 | 19:56 | NU05 | LONG RURAL | Asset failure | HV | 2.00 | 227.0 | 0.003258 | 0.0000144 | No
29/08/2023 | 19:56 | NU05 | SHORT RURAL | Asset failure | HV | 550.00 | 237.5 | 0.918863 | 0.0038695 | No
29/08/2023 | 20:03 | CN24 | LONG RURAL | Asset failure | LV | 45.00 | 79.0 | 0.025512 | 0.0003229 | No
29/08/2023 | 22:22 | BM52 | URBAN | Vegetation | Grow-in - NSP responsibility | 1,272.00 | 280.0 | 0.549111 | 0.0019611 | No
29/08/2023 | 23:04 | EL01A | URBAN | Planned |  | 457.00 | 195.3 | 0.137581 | 0.0007046 | No
30/08/2023 | 03:44 | SM410B | URBAN | Asset failure | LV | 3.00 | 13,633.0 | 0.063056 | 0.0000046 | No
30/08/2023 | 03:46 | SB21 | LONG RURAL | Unknown | Unknown | 79.00 | 378.0 | 0.214314 | 0.0005669 | No
30/08/2023 | 06:21 | LX42 | SHORT RURAL | Asset failure | LV | 2.00 | 609.0 | 0.008569 | 0.0000141 | No
30/08/2023 | 06:32 | AP425C | URBAN | Asset failure | LV | 1.00 | 264.0 | 0.000407 | 0.0000015 | No
30/08/2023 | 07:53 | G04 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 68.67 | 120.6 | 0.059444 | 0.0004928 | No
30/08/2023 | 07:56 | PA01 | URBAN | Asset failure | LV | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
30/08/2023 | 08:13 | NU20 | LONG RURAL | Planned |  | 409.00 | 489.3 | 1.436034 | 0.0029351 | No
30/08/2023 | 08:37 | SM216C | URBAN | Planned |  | 70.00 | 139.0 | 0.015001 | 0.0001079 | No
30/08/2023 | 08:41 | PL04 | URBAN | Planned |  | 8.00 | 167.0 | 0.002060 | 0.0000123 | No
30/08/2023 | 08:53 | AP139D | URBAN | Asset failure | LV | 17.00 | 186.0 | 0.004875 | 0.0000262 | No
30/08/2023 | 09:13 | AP132A | URBAN | Third Party | Vehicle impact | 3.00 | 89.0 | 0.000412 | 0.0000046 | No
30/08/2023 | 09:15 | CV24 | LONG RURAL | Planned |  | 7.00 | 247.0 | 0.012408 | 0.0000502 | No
30/08/2023 | 09:20 | PL24 | LONG RURAL | Planned |  | 1.00 | 18.0 | 0.000129 | 0.0000072 | No
30/08/2023 | 09:28 | HH428F | URBAN | Asset failure | LV | 2.00 | 761.0 | 0.002347 | 0.0000031 | No
30/08/2023 | 09:40 | SD37301 | SHORT RURAL | Planned |  | 2.00 | 16.0 | 0.000225 | 0.0000141 | No
30/08/2023 | 09:41 | BS0356 | LONG RURAL | Planned |  | 1.00 | 268.0 | 0.001923 | 0.0000072 | No
30/08/2023 | 09:45 | PP09 | LONG RURAL | Planned |  | 45.00 | 140.4 | 0.045354 | 0.0003229 | No
30/08/2023 | 09:45 | M72 | LONG RURAL | Planned |  | 61.00 | 163.0 | 0.071354 | 0.0004378 | No
30/08/2023 | 09:47 | VH43 | SHORT RURAL | Asset failure | LV | 2.00 | 107.0 | 0.001506 | 0.0000141 | No
30/08/2023 | 09:55 | MB27 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 258.0 | 0.001851 | 0.0000072 | No
30/08/2023 | 09:55 | MB27 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 189.00 | 258.8 | 0.344120 | 0.0013297 | No
30/08/2023 | 11:07 | YK11 | LONG RURAL | Planned |  | 1.00 | 9.0 | 0.000065 | 0.0000072 | No
30/08/2023 | 11:27 | HH409F | URBAN | Asset failure | LV | 95.00 | 145.0 | 0.021238 | 0.0001465 | No
30/08/2023 | 11:42 | HH341B | URBAN | Asset failure | LV | 19.00 | 35.0 | 0.001025 | 0.0000293 | No
30/08/2023 | 11:55 | SM350H | URBAN | Unknown | Unknown | 1.00 | 87.0 | 0.000134 | 0.0000015 | No
30/08/2023 | 13:09 | NU04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 590.00 | 93.4 | 0.387796 | 0.0041509 | No
30/08/2023 | 13:41 | SD31200 | LONG RURAL | Planned |  | 3.00 | 104.0 | 0.002239 | 0.0000215 | No
30/08/2023 | 13:45 | VH13 | SHORT RURAL | Asset failure | LV | 1.00 | 4,336.0 | 0.030506 | 0.0000070 | No
30/08/2023 | 14:03 | G01 | LONG RURAL | Planned |  | 639.00 | 34.6 | 0.158862 | 0.0045857 | No
30/08/2023 | 14:55 | CL12 | LONG RURAL | Asset failure | HV | 10.00 | 91.0 | 0.006530 | 0.0000718 | No
30/08/2023 | 15:40 | NU15 | LONG RURAL | Animal | Animal impact | 2.00 | 246.0 | 0.003531 | 0.0000144 | No
30/08/2023 | 16:39 | SB21 | LONG RURAL | Weather |  | 79.00 | 102.8 | 0.058265 | 0.0005669 | No
30/08/2023 | 16:52 | SM172F | URBAN | Asset failure | LV | 1.00 | 332.0 | 0.000512 | 0.0000015 | No
30/08/2023 | 18:18 | AP355H | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
30/08/2023 | 18:19 | BT03 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 3.00 | 49.0 | 0.001055 | 0.0000215 | No
30/08/2023 | 20:57 | HH341E | URBAN | Asset failure | LV | 86.00 | 60.0 | 0.007955 | 0.0001326 | No
30/08/2023 | 21:17 | AP425A | URBAN | Asset failure | LV | 4.00 | 194.0 | 0.001196 | 0.0000062 | No
30/08/2023 | 21:29 | NA05 | LONG RURAL | Unknown | Unknown | 27.00 | 141.0 | 0.027320 | 0.0001938 | No
31/08/2023 | 01:52 | SM411D | URBAN | Overloads |  | 21.00 | 442.0 | 0.014311 | 0.0000324 | No
31/08/2023 | 05:25 | MB72 | LONG RURAL | Asset failure | HV | 184.00 | 439.0 | 0.579675 | 0.0013204 | No
31/08/2023 | 06:14 | MI10 | LONG RURAL | Asset failure | HV | 53.00 | 236.4 | 0.089919 | 0.0003803 | No
31/08/2023 | 08:02 | NU20 | LONG RURAL | Planned |  | 75.00 | 707.6 | 0.380833 | 0.0005382 | No
31/08/2023 | 08:18 | SD31200 | LONG RURAL | Planned |  | 81.00 | 337.0 | 0.195892 | 0.0005813 | No
31/08/2023 | 08:23 | AP529D | URBAN | Overloads |  | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
31/08/2023 | 08:34 | NL111C | URBAN | Planned |  | 62.00 | 425.0 | 0.040625 | 0.0000956 | No
31/08/2023 | 08:49 | MTB14 | SHORT RURAL | Planned |  | 24.00 | 396.2 | 0.066900 | 0.0001689 | No
31/08/2023 | 08:52 | G01 | LONG RURAL | Planned |  | 35.00 | 260.7 | 0.065491 | 0.0002512 | No
31/08/2023 | 09:08 | EL08D | URBAN | Planned |  | 59.00 | 2.0 | 0.000182 | 0.0000910 | No
31/08/2023 | 09:21 | HH121G | URBAN | Planned |  | 91.00 | 340.0 | 0.047702 | 0.0001403 | No
31/08/2023 | 09:21 | EL08D | URBAN | Planned |  | 173.00 | 267.0 | 0.071215 | 0.0002667 | No
31/08/2023 | 09:28 | KI32 | SHORT RURAL | Asset failure | LV | 1.00 | 132.0 | 0.000929 | 0.0000070 | No
31/08/2023 | 09:46 | CD23 | LONG RURAL | Planned |  | 3.00 | 146.7 | 0.003158 | 0.0000215 | No
31/08/2023 | 09:48 | AP227B | URBAN | Asset failure | LV | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
31/08/2023 | 10:10 | G05 | LONG RURAL | Planned |  | 103.00 | 149.0 | 0.110135 | 0.0007392 | No
31/08/2023 | 11:17 | MG36 | LONG RURAL | Planned |  | 3.00 | 161.0 | 0.003466 | 0.0000215 | No
31/08/2023 | 11:19 | KA29 | LONG RURAL | Asset failure | LV | 1.00 | 5,956.0 | 0.042742 | 0.0000072 | No
31/08/2023 | 11:26 | KI41 | LONG RURAL | Planned |  | 3.00 | 119.0 | 0.002562 | 0.0000215 | No
31/08/2023 | 11:52 | GA34 | SHORT RURAL | Planned |  | 8.00 | 113.0 | 0.006360 | 0.0000563 | No
31/08/2023 | 12:47 | AP425A | URBAN | Asset failure | LV | 12.00 | 259.0 | 0.004792 | 0.0000185 | No
31/08/2023 | 13:00 | HH121G | URBAN | Planned |  | 1.00 | 49.0 | 0.000076 | 0.0000015 | No
31/08/2023 | 15:29 | BM12 | SHORT RURAL | Asset failure | LV | 7.00 | 39.0 | 0.001921 | 0.0000492 | No
31/08/2023 | 16:54 | CL23 | LONG RURAL | Asset failure | LV | 1.00 | 146.0 | 0.001048 | 0.0000072 | No
31/08/2023 | 20:45 | SM374B | URBAN | Unknown | Unknown | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
31/08/2023 | 20:53 | NL451E | URBAN | Asset failure | LV | 6.33 | 118.0 | 0.001152 | 0.0000098 | No
31/08/2023 | 22:33 | HH341K | URBAN | Vegetation | Grow-in - NSP responsibility | 45.00 | 151.0 | 0.010476 | 0.0000694 | No
01/09/2023 | 01:28 | PL803C | URBAN | Asset failure | LV | 12.00 | 363.0 | 0.006716 | 0.0000185 | No
01/09/2023 | 08:02 | NU06 | LONG RURAL | Planned |  | 50.00 | 559.5 | 0.200743 | 0.0003588 | No
01/09/2023 | 08:46 | CL09 | LONG RURAL | Planned |  | 2.00 | 29.0 | 0.000416 | 0.0000144 | No
01/09/2023 | 09:02 | NA13 | LONG RURAL | Planned |  | 4.00 | 298.0 | 0.008554 | 0.0000287 | No
01/09/2023 | 09:03 | VH23 | SHORT RURAL | Planned |  | 419.00 | 296.9 | 0.875095 | 0.0029479 | No
01/09/2023 | 09:21 | CL16 | LONG RURAL | Planned |  | 1.00 | 200.0 | 0.001435 | 0.0000072 | No
01/09/2023 | 09:32 | GA09 | LONG RURAL | Planned |  | 55.00 | 298.9 | 0.117972 | 0.0003947 | No
01/09/2023 | 09:33 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 242.0 | 0.001703 | 0.0000070 | No
01/09/2023 | 09:39 | CV21 | LONG RURAL | Planned |  | 32.00 | 130.0 | 0.029854 | 0.0002296 | No
01/09/2023 | 09:43 | MB01 | LONG RURAL | Planned |  | 120.00 | 175.0 | 0.150703 | 0.0008612 | No
01/09/2023 | 10:14 | SM350G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 170.00 | 115.9 | 0.030382 | 0.0002621 | No
01/09/2023 | 10:50 | R07 | SHORT RURAL | Planned |  | 26.00 | 129.0 | 0.023597 | 0.0001829 | No
01/09/2023 | 11:19 | PA01 | URBAN | Asset failure | LV | 2.00 | 3,008.0 | 0.009275 | 0.0000031 | No
01/09/2023 | 12:11 | HH341G | URBAN | Asset failure | LV | 73.00 | 49.0 | 0.005515 | 0.0001125 | No
01/09/2023 | 12:13 | KA06 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 167.0 | 0.001198 | 0.0000072 | No
01/09/2023 | 12:22 | HH177C | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
01/09/2023 | 13:44 | HH409F | URBAN | Asset failure | LV | 1.00 | 253.0 | 0.000390 | 0.0000015 | No
01/09/2023 | 14:59 | SA40 | URBAN | Unknown | Unknown | 20.00 | 129.0 | 0.003978 | 0.0000308 | No
01/09/2023 | 16:50 | HH432E | URBAN | Asset failure | LV | 1.00 | 368.0 | 0.000567 | 0.0000015 | No
01/09/2023 | 17:52 | G13 | LONG RURAL | Asset failure | LV | 2.00 | 287.0 | 0.004119 | 0.0000144 | No
01/09/2023 | 18:04 | HH177C | URBAN | Third Party | Unauthorised access | 127.00 | 36.0 | 0.007049 | 0.0001958 | No
01/09/2023 | 18:46 | CBD103C | URBAN | Asset failure | LV | 12.00 | 131.0 | 0.002424 | 0.0000185 | No
01/09/2023 | 20:05 | AP132A | URBAN | Asset failure | LV | 19.00 | 474.0 | 0.013885 | 0.0000293 | No
01/09/2023 | 21:42 | CBD103C | URBAN | Asset failure | LV | 1.00 | 256.0 | 0.000395 | 0.0000015 | No
02/09/2023 | 03:00 | ME116B | URBAN | Asset failure | LV | 1.00 | 439.0 | 0.000677 | 0.0000015 | No
02/09/2023 | 06:14 | NA58 | LONG RURAL | Unknown | Unknown | 20.00 | 327.0 | 0.046933 | 0.0001435 | No
02/09/2023 | 08:26 | BS0273 | URBAN | Planned |  | 2.00 | 3,114.0 | 0.009602 | 0.0000031 | No
02/09/2023 | 08:27 | NL760C | URBAN | Asset failure | LV | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
02/09/2023 | 08:39 | G34 | LONG RURAL | Planned |  | 37.00 | 245.8 | 0.065269 | 0.0002655 | No
02/09/2023 | 08:47 | CD20 | LONG RURAL | Planned |  | 64.00 | 252.0 | 0.115740 | 0.0004593 | No
02/09/2023 | 09:11 | PA03 | URBAN | Planned |  | 34.00 | 130.3 | 0.006832 | 0.0000524 | No
02/09/2023 | 10:20 | WHY08 | URBAN | Asset failure | LV | 13.00 | 306.0 | 0.006133 | 0.0000200 | No
02/09/2023 | 10:23 | PA07 | LONG RURAL | Planned |  | 3.00 | 105.0 | 0.002261 | 0.0000215 | No
02/09/2023 | 12:27 | EL10 | URBAN | Asset failure | LV | 1.00 | 366.0 | 0.000564 | 0.0000015 | No
02/09/2023 | 12:42 | CN33 | LONG RURAL | Planned |  | 4.00 | 78.0 | 0.002239 | 0.0000287 | No
02/09/2023 | 15:22 | SA40 | URBAN | Asset failure | LV | 13.33 | 779.0 | 0.016014 | 0.0000206 | No
02/09/2023 | 17:05 | AP344D | URBAN | Asset failure | LV | 67.00 | 33.7 | 0.003486 | 0.0001033 | No
02/09/2023 | 19:06 | MG44 | URBAN | Asset failure | LV | 1.00 | 122.0 | 0.000188 | 0.0000015 | No
02/09/2023 | 20:42 | ST34 | LONG RURAL | Animal | Animal impact | 8.00 | 174.9 | 0.010040 | 0.0000574 | No
02/09/2023 | 21:50 | HH496F | URBAN | Overloads |  | 22.00 | 343.5 | 0.011649 | 0.0000339 | No
02/09/2023 | 22:08 | GA28 | LONG RURAL | Third Party | Vehicle impact | 362.00 | 542.0 | 1.408082 | 0.0025978 | No
03/09/2023 | 06:44 | SM137A | URBAN | Asset failure | LV | 1.00 | 257.0 | 0.000396 | 0.0000015 | No
03/09/2023 | 07:59 | MTB13 | SHORT RURAL | Asset failure | LV | 1.00 | 270.0 | 0.001900 | 0.0000070 | No
03/09/2023 | 08:03 | ME347B | URBAN | Planned |  | 4.00 | 359.0 | 0.002214 | 0.0000062 | No
03/09/2023 | 08:11 | PP18 | LONG RURAL | Planned |  | 222.00 | 243.0 | 0.387134 | 0.0015931 | No
03/09/2023 | 08:24 | HH341B | URBAN | Planned |  | 24.00 | 383.0 | 0.014172 | 0.0000370 | No
03/09/2023 | 09:05 | BT18 | LONG RURAL | Planned |  | 59.00 | 447.0 | 0.189261 | 0.0004234 | No
03/09/2023 | 09:51 | SM350D | URBAN | Unknown | Unknown | 1.00 | 304.0 | 0.000469 | 0.0000015 | No
03/09/2023 | 10:02 | SSD174 | SHORT RURAL | Unknown | Unknown | 88.00 | 157.0 | 0.097202 | 0.0006191 | No
03/09/2023 | 13:13 | SA36 | URBAN | Asset failure | LV | 4.00 | 1,224.0 | 0.007548 | 0.0000062 | No
03/09/2023 | 13:39 | HH177E | URBAN | Asset failure | LV | 21.00 | 84.0 | 0.002720 | 0.0000324 | No
03/09/2023 | 15:23 | GA08 | LONG RURAL | Asset failure | HV | 208.00 | 291.6 | 0.435259 | 0.0014927 | No
03/09/2023 | 17:32 | HH102B | URBAN | Vegetation | Grow-in - NSP responsibility | 26.33 | 58.0 | 0.002355 | 0.0000406 | No
03/09/2023 | 21:00 | MTB54 | LONG RURAL | Asset failure | LV | 1.00 | 233.0 | 0.001672 | 0.0000072 | No
03/09/2023 | 22:36 | ME347D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 205.00 | 72.0 | 0.022756 | 0.0003161 | No
04/09/2023 | 05:17 | HH428F | URBAN | Asset failure | LV | 6.00 | 313.0 | 0.002895 | 0.0000093 | No
04/09/2023 | 06:15 | AP344D | URBAN | Animal | Animal impact | 1.00 | 615.0 | 0.000948 | 0.0000015 | No
04/09/2023 | 07:01 | AP829B | URBAN | Asset failure | LV | 2.00 | 539.0 | 0.001662 | 0.0000031 | No
04/09/2023 | 08:40 | YK07 | LONG RURAL | Overloads |  | 2.00 | 1,402.0 | 0.020122 | 0.0000144 | No
04/09/2023 | 08:56 | SD32400 | LONG RURAL | Planned |  | 452.00 | 230.3 | 0.746970 | 0.0032437 | No
04/09/2023 | 09:18 | SB15 | LONG RURAL | Planned |  | 1.00 | 125.0 | 0.000897 | 0.0000072 | No
04/09/2023 | 09:37 | GA43 | SHORT RURAL | Planned |  | 11.00 | 247.0 | 0.019115 | 0.0000774 | No
04/09/2023 | 09:50 | MG04 | SHORT RURAL | Planned |  | 2.00 | 322.0 | 0.004531 | 0.0000141 | No
04/09/2023 | 09:57 | EL09 | URBAN | Asset failure | LV | 1.00 | 715.0 | 0.001102 | 0.0000015 | No
04/09/2023 | 10:08 | SD54300 | LONG RURAL | Planned |  | 3.00 | 60.0 | 0.001292 | 0.0000215 | No
04/09/2023 | 10:13 | MG06 | SHORT RURAL | Asset failure | HV | 374.00 | 177.6 | 0.467424 | 0.0026313 | No
04/09/2023 | 10:49 | G12 | LONG RURAL | Planned |  | 4.00 | 119.0 | 0.003416 | 0.0000287 | No
04/09/2023 | 10:54 | NL760A | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
04/09/2023 | 11:58 | NL544A | URBAN | Network business | Switching and protection error | 2.00 | 5.0 | 0.000015 | 0.0000031 | No
04/09/2023 | 16:29 | HH429C | URBAN | Asset failure | LV | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
04/09/2023 | 17:01 | MG07 | SHORT RURAL | Asset failure | LV | 2.00 | 225.0 | 0.003166 | 0.0000141 | No
04/09/2023 | 18:34 | NL234C | URBAN | Unknown | Unknown | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
04/09/2023 | 20:08 | SA18 | URBAN | Network business | Switching and protection error | 21.00 | 157.0 | 0.005083 | 0.0000324 | No
04/09/2023 | 20:16 | M44 | LONG RURAL | Asset failure | HV | 57.00 | 477.0 | 0.195117 | 0.0004091 | No
04/09/2023 | 21:03 | ME116D | URBAN | Asset failure | LV | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
04/09/2023 | 21:11 | HH429A | URBAN | Asset failure | LV | 49.00 | 80.0 | 0.006044 | 0.0000755 | No
04/09/2023 | 22:03 | AP344D | URBAN | Asset failure | LV | 100.00 | 125.0 | 0.019272 | 0.0001542 | No
04/09/2023 | 22:08 | HH148B | URBAN | Overloads |  | 27.67 | 42.0 | 0.001792 | 0.0000427 | No
04/09/2023 | 22:15 | HH130E | URBAN | Overloads |  | 13.00 | 81.0 | 0.001623 | 0.0000200 | No
04/09/2023 | 23:39 | SD37102 | LONG RURAL | Asset failure | Subtransmission | 34.00 | 93.0 | 0.022692 | 0.0002440 | No
05/09/2023 | 05:34 | EL09 | URBAN | Asset failure | LV | 7.00 | 180.0 | 0.001943 | 0.0000108 | No
05/09/2023 | 05:59 | MI11 | LONG RURAL | Unknown | Unknown | 43.00 | 295.0 | 0.091032 | 0.0003086 | No
05/09/2023 | 06:29 | HH130E | URBAN | Asset failure | LV | 1.00 | 259.0 | 0.000399 | 0.0000015 | No
05/09/2023 | 06:37 | LC01 | SHORT RURAL | Unknown | Unknown | 1.00 | 388.0 | 0.002730 | 0.0000070 | No
05/09/2023 | 06:48 | HH341C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
05/09/2023 | 08:22 | SD31400 | LONG RURAL | Planned |  | 387.00 | 352.3 | 0.978528 | 0.0027772 | No
05/09/2023 | 08:22 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 149.0 | 0.001048 | 0.0000070 | No
05/09/2023 | 08:27 | PP01 | URBAN | Planned |  | 2.00 | 827.0 | 0.002550 | 0.0000031 | No
05/09/2023 | 08:37 | SA744C | URBAN | Asset failure | LV | 2.00 | 349.0 | 0.001076 | 0.0000031 | No
05/09/2023 | 08:52 | MTB14 | SHORT RURAL | Planned |  | 5.00 | 299.0 | 0.010518 | 0.0000352 | No
05/09/2023 | 08:53 | NL115F | URBAN | Unknown | Unknown | 1.00 | 255.0 | 0.000393 | 0.0000015 | No
05/09/2023 | 08:59 | SD32200 | LONG RURAL | Planned |  | 138.00 | 84.0 | 0.083188 | 0.0009903 | No
05/09/2023 | 09:11 | KA02 | SHORT RURAL | Planned |  | 26.00 | 11.0 | 0.002012 | 0.0001829 | No
05/09/2023 | 09:14 | SB17 | LONG RURAL | Planned |  | 27.00 | 165.0 | 0.031971 | 0.0001938 | No
05/09/2023 | 09:21 | AP424C | URBAN | Planned |  | 84.00 | 298.5 | 0.038658 | 0.0001295 | No
05/09/2023 | 09:21 | SA31 | URBAN | Planned |  | 1,288.00 | 272.0 | 0.540144 | 0.0019858 | No
05/09/2023 | 09:22 | HH177E | URBAN | Planned |  | 121.00 | 158.0 | 0.029475 | 0.0001866 | No
05/09/2023 | 09:29 | PL06 | URBAN | Asset failure | LV | 2.00 | 169.0 | 0.000521 | 0.0000031 | No
05/09/2023 | 09:41 | R30 | LONG RURAL | Planned |  | 23.00 | 128.0 | 0.021127 | 0.0001651 | No
05/09/2023 | 09:45 | R09 | LONG RURAL | Planned |  | 14.00 | 124.0 | 0.012458 | 0.0001005 | No
05/09/2023 | 09:52 | NL111C | URBAN | Asset failure | LV | 41.00 | 311.4 | 0.019682 | 0.0000632 | No
05/09/2023 | 10:04 | EL09 | URBAN | Asset failure | LV | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
05/09/2023 | 10:36 | AP146B | URBAN | Asset failure | LV | 90.00 | 38.0 | 0.005273 | 0.0001388 | No
05/09/2023 | 10:36 | HH107D | URBAN | Asset failure | LV | 50.00 | 79.0 | 0.006090 | 0.0000771 | No
05/09/2023 | 15:21 | VH45 | SHORT RURAL | Asset failure | LV | 2.00 | 881.0 | 0.012397 | 0.0000141 | No
05/09/2023 | 15:24 | HH409D | URBAN | Asset failure | LV | 11.00 | 132.0 | 0.002239 | 0.0000170 | No
05/09/2023 | 15:31 | KA03 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 92.0 | 0.000660 | 0.0000072 | No
05/09/2023 | 16:28 | WK71 | SHORT RURAL | Animal | Animal impact | 1.00 | 34.0 | 0.000239 | 0.0000070 | No
05/09/2023 | 17:33 | CV20 | LONG RURAL | Weather |  | 14.00 | 75.0 | 0.007535 | 0.0001005 | No
05/09/2023 | 19:21 | SA20 | URBAN | Asset failure | LV | 17.00 | 166.0 | 0.004351 | 0.0000262 | No
05/09/2023 | 19:50 | GU41 | LONG RURAL | Other |  | 1.00 | 339.0 | 0.002433 | 0.0000072 | No
06/09/2023 | 01:10 | MTB81 | LONG RURAL | Animal | Animal impact | 1.00 | 216.0 | 0.001550 | 0.0000072 | No
06/09/2023 | 01:10 | MTB81 | SHORT RURAL | Animal | Animal impact | 657.00 | 216.3 | 0.999940 | 0.0046223 | No
06/09/2023 | 08:18 | AP139C | URBAN | Asset failure | LV | 1.00 | 158.0 | 0.000244 | 0.0000015 | No
06/09/2023 | 08:34 | BT08 | LONG RURAL | Planned |  | 65.00 | 350.0 | 0.163261 | 0.0004665 | No
06/09/2023 | 08:36 | HH118C | URBAN | Asset failure | LV | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
06/09/2023 | 08:51 | MV64 | SHORT RURAL | Planned |  | 127.00 | 375.6 | 0.335579 | 0.0008935 | No
06/09/2023 | 09:04 | G22 | LONG RURAL | Planned |  | 98.00 | 167.0 | 0.117448 | 0.0007033 | No
06/09/2023 | 09:43 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 156.0 | 0.001098 | 0.0000070 | No
06/09/2023 | 09:53 | NL210B | URBAN | Asset failure | LV | 2.00 | 1,103.0 | 0.003401 | 0.0000031 | No
06/09/2023 | 09:56 | NL451C | URBAN | Planned |  | 1.00 | 3,153.0 | 0.004861 | 0.0000015 | No
06/09/2023 | 10:01 | SD54102 | LONG RURAL | Planned |  | 1.00 | 58.0 | 0.000416 | 0.0000072 | No
06/09/2023 | 10:11 | MI26 | LONG RURAL | Planned |  | 13.00 | 211.0 | 0.019685 | 0.0000933 | No
06/09/2023 | 10:30 | SA20 | URBAN | Planned |  | 1.00 | 42.0 | 0.000065 | 0.0000015 | No
06/09/2023 | 10:34 | SM374B | URBAN | Unknown | Unknown | 1.00 | 446.0 | 0.000688 | 0.0000015 | No
06/09/2023 | 10:38 | SD32302 | LONG RURAL | Planned |  | 75.00 | 277.0 | 0.149088 | 0.0005382 | No
06/09/2023 | 12:31 | SA17 | URBAN | Asset failure | LV | 1.00 | 506.0 | 0.000780 | 0.0000015 | No
06/09/2023 | 13:14 | SA14 | URBAN | Overloads |  | 6.33 | 349.0 | 0.003408 | 0.0000098 | No
06/09/2023 | 13:27 | PA07 | LONG RURAL | Overloads |  | 1.00 | 92.0 | 0.000660 | 0.0000072 | No
06/09/2023 | 13:38 | BM15 | SHORT RURAL | Weather |  | 2.00 | 246.0 | 0.003461 | 0.0000141 | No
06/09/2023 | 14:57 | SA16 | URBAN | Asset failure | LV | 66.00 | 147.6 | 0.015015 | 0.0001018 | No
06/09/2023 | 15:48 | BM31 | SHORT RURAL | Asset failure | LV | 7.00 | 29.9 | 0.001470 | 0.0000492 | No
06/09/2023 | 16:33 | MB26 | LONG RURAL | Planned |  | 1.00 | 24.0 | 0.000172 | 0.0000072 | No
06/09/2023 | 17:34 | MTB51 | LONG RURAL | Asset failure | LV | 1.00 | 254.0 | 0.001823 | 0.0000072 | No
06/09/2023 | 17:37 | HH121C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 58.67 | 74.0 | 0.006693 | 0.0000904 | No
06/09/2023 | 17:38 | NL21 | URBAN | Asset failure | HV | 44.00 | 93.8 | 0.006361 | 0.0000678 | No
06/09/2023 | 17:58 | SA16 | URBAN | Other |  | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
06/09/2023 | 17:58 | MV62 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 325.0 | 0.002287 | 0.0000070 | No
06/09/2023 | 18:28 | KI14 | LONG RURAL | Asset failure | LV | 1.00 | 144.0 | 0.001033 | 0.0000072 | No
06/09/2023 | 19:33 | MG09 | SHORT RURAL | Asset failure | LV | 1.00 | 77.0 | 0.000542 | 0.0000070 | No
06/09/2023 | 19:51 | SM374B | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
06/09/2023 | 22:50 | MTB13 | SHORT RURAL | Animal | Animal impact | 1.00 | 106.0 | 0.000746 | 0.0000070 | No
06/09/2023 | 23:12 | SM216B | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
07/09/2023 | 04:26 | NL210B | URBAN | Asset failure | LV | 2.00 | 369.5 | 0.001139 | 0.0000031 | No
07/09/2023 | 05:56 | SSD094 | LONG RURAL | Third Party | Other | 64.00 | 693.0 | 0.318285 | 0.0004593 | No
07/09/2023 | 08:11 | NL115D | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
07/09/2023 | 08:32 | SD31100 | LONG RURAL | Planned |  | 110.00 | 195.0 | 0.153932 | 0.0007894 | No
07/09/2023 | 08:34 | SA18 | URBAN | Unknown | Unknown | 1.00 | 348.0 | 0.000537 | 0.0000015 | No
07/09/2023 | 08:51 | BM32 | SHORT RURAL | Planned |  | 53.00 | 198.0 | 0.073830 | 0.0003729 | No
07/09/2023 | 09:20 | NA06 | LONG RURAL | Planned |  | 30.00 | 84.0 | 0.018084 | 0.0002153 | No
07/09/2023 | 09:41 | HH386F | URBAN | Unknown | Unknown | 39.00 | 180.0 | 0.010823 | 0.0000601 | No
07/09/2023 | 09:59 | SD49100 | LONG RURAL | Unknown | Unknown | 2.67 | 94.0 | 0.001799 | 0.0000191 | No
07/09/2023 | 10:05 | ME427E | URBAN | Planned |  | 1.00 | 19,607.0 | 0.030229 | 0.0000015 | No
07/09/2023 | 10:19 | WHY10 | URBAN | Asset failure | LV | 21.67 | 98.0 | 0.003274 | 0.0000334 | No
07/09/2023 | 10:20 | GA40 | SHORT RURAL | Asset failure | LV | 1.00 | 1,423.0 | 0.010012 | 0.0000070 | No
07/09/2023 | 10:22 | SM126B | URBAN | Planned |  | 43.00 | 224.4 | 0.014879 | 0.0000663 | No
07/09/2023 | 10:36 | HH121F | URBAN | Vegetation | Grow-in - NSP responsibility | 611.00 | 41.1 | 0.038676 | 0.0009420 | No
07/09/2023 | 10:41 | GA36 | LONG RURAL | Planned |  | 2.00 | 36.0 | 0.000517 | 0.0000144 | No
07/09/2023 | 11:23 | CV16 | LONG RURAL | Planned |  | 13.00 | 177.0 | 0.016513 | 0.0000933 | No
07/09/2023 | 12:20 | SM374B | URBAN | Vegetation | Grow-in - NSP responsibility | 92.00 | 129.0 | 0.018298 | 0.0001418 | No
07/09/2023 | 12:32 | SM349B | URBAN | Third Party | Other | 21.00 | 155.0 | 0.005018 | 0.0000324 | No
07/09/2023 | 12:33 | LX43 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 126.0 | 0.000886 | 0.0000070 | No
07/09/2023 | 12:36 | YK17 | LONG RURAL | Asset failure | LV | 1.00 | 155.0 | 0.001112 | 0.0000072 | No
07/09/2023 | 13:49 | HH341D | URBAN | Asset failure | LV | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
07/09/2023 | 13:57 | SM402D | URBAN | Unknown | Unknown | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
07/09/2023 | 13:58 | W01 | LONG RURAL | Overloads |  | 1.00 | 174.0 | 0.001249 | 0.0000072 | No
07/09/2023 | 14:00 | EL17 | URBAN | Asset failure | HV | 1,608.00 | 52.0 | 0.128983 | 0.0024791 | No
07/09/2023 | 14:00 | HH409E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 925.00 | 80.0 | 0.114090 | 0.0014261 | No
07/09/2023 | 14:09 | HH121A | URBAN | Asset failure | LV | 21.67 | 200.0 | 0.006681 | 0.0000334 | No
07/09/2023 | 14:23 | VH31 | SHORT RURAL | Asset failure | HV | 152.00 | 107.4 | 0.114875 | 0.0010694 | No
07/09/2023 | 14:30 | HH107C | URBAN | Vegetation | Grow-in - NSP responsibility | 24.33 | 231.0 | 0.008666 | 0.0000375 | No
07/09/2023 | 14:34 | PL01 | URBAN | Asset failure | LV | 14.33 | 110.0 | 0.002431 | 0.0000221 | No
07/09/2023 | 14:51 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 43.33 | 210.0 | 0.014030 | 0.0000668 | No
07/09/2023 | 15:06 | SM179D | URBAN | Asset failure | LV | 148.00 | 262.0 | 0.059783 | 0.0002282 | No
07/09/2023 | 15:14 | HH428D | URBAN | Overloads |  | 67.00 | 102.0 | 0.010536 | 0.0001033 | No
07/09/2023 | 15:15 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 214.00 | 188.1 | 0.283136 | 0.0015056 | No
07/09/2023 | 16:41 | SM349A | URBAN | Overloads |  | 1.00 | 408.0 | 0.000629 | 0.0000015 | No
07/09/2023 | 16:42 | MV14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 661.00 | 83.0 | 0.385988 | 0.0046505 | No
07/09/2023 | 17:07 | ME116C | URBAN | Asset failure | LV | 1.00 | 522.0 | 0.000805 | 0.0000015 | No
07/09/2023 | 17:10 | SM402B | URBAN | Asset failure | LV | 56.00 | 345.0 | 0.029787 | 0.0000863 | No
07/09/2023 | 17:14 | SM349E | URBAN | Asset failure | LV | 41.67 | 94.1 | 0.006045 | 0.0000642 | No
07/09/2023 | 17:16 | HH428D | URBAN | Other |  | 22.33 | 224.0 | 0.007713 | 0.0000344 | No
07/09/2023 | 17:27 | HH121F | URBAN | Unknown | Unknown | 23.33 | 97.0 | 0.003489 | 0.0000360 | No
07/09/2023 | 17:39 | HH118A | URBAN | Asset failure | LV | 1.00 | 390.0 | 0.000601 | 0.0000015 | No
07/09/2023 | 17:46 | NL111P | URBAN | Asset failure | LV | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
07/09/2023 | 18:07 | NL21 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 217.0 | 0.000335 | 0.0000015 | No
07/09/2023 | 18:37 | GU32 | LONG RURAL | Asset failure | HV | 8.00 | 320.8 | 0.018414 | 0.0000574 | No
07/09/2023 | 18:41 | GA22 | SHORT RURAL | Asset failure | LV | 1.00 | 831.0 | 0.005846 | 0.0000070 | No
07/09/2023 | 18:42 | HH148A | URBAN | Asset failure | LV | 6.67 | 658.0 | 0.006763 | 0.0000103 | No
07/09/2023 | 18:51 | SG12 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 14.00 | 25.0 | 0.002462 | 0.0000985 | No
07/09/2023 | 19:06 | SM349F | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 374.0 | 0.000577 | 0.0000015 | No
07/09/2023 | 19:07 | ME231A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 496.67 | 51.4 | 0.039344 | 0.0007657 | No
07/09/2023 | 19:29 | HH130C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 4,473.0 | 0.006896 | 0.0000015 | No
07/09/2023 | 19:37 | MV14 | SHORT RURAL | Unknown | Unknown | 6.67 | 143.0 | 0.006707 | 0.0000469 | No
07/09/2023 | 19:37 | AP149E | URBAN | Asset failure | LV | 26.33 | 106.0 | 0.004304 | 0.0000406 | No
07/09/2023 | 20:21 | CN32 | LONG RURAL | Asset failure | HV | 57.67 | 184.9 | 0.076533 | 0.0004138 | No
07/09/2023 | 20:33 | WK43 | SHORT RURAL | Asset failure | LV | 1.00 | 850.0 | 0.005980 | 0.0000070 | No
07/09/2023 | 20:36 | NL451C | URBAN | Asset failure | LV | 11.33 | 128.0 | 0.002237 | 0.0000175 | No
07/09/2023 | 21:04 | HH177D | URBAN | Weather |  | 1,109.00 | 43.1 | 0.073736 | 0.0017098 | No
07/09/2023 | 21:21 | KA05 | LONG RURAL | Asset failure | LV | 1.00 | 69.0 | 0.000495 | 0.0000072 | No
07/09/2023 | 21:55 | HH130B | URBAN | Vegetation | Grow-in - NSP responsibility | 10.00 | 63.0 | 0.000971 | 0.0000154 | No
07/09/2023 | 22:34 | NA52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 487.00 | 105.5 | 0.368576 | 0.0034949 | No
07/09/2023 | 22:35 | NA52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 485.00 | 371.0 | 1.291273 | 0.0034805 | No
07/09/2023 | 22:39 | HH409E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,134.0 | 0.001748 | 0.0000015 | No
07/09/2023 | 22:47 | KI52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 40.00 | 476.1 | 0.136652 | 0.0002871 | No
07/09/2023 | 22:52 | MI08 | LONG RURAL | Weather |  | 1,245.00 | 340.3 | 3.040180 | 0.0089345 | No
07/09/2023 | 23:12 | SM216C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 561.00 | 89.0 | 0.076978 | 0.0008649 | No
07/09/2023 | 23:49 | SM350F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,004.00 | 99.2 | 0.153522 | 0.0015479 | No
08/09/2023 | 00:14 | HH145B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 786.00 | 111.0 | 0.134512 | 0.0012118 | No
08/09/2023 | 00:45 | HH130C | URBAN | Unknown | Unknown | 24.67 | 247.0 | 0.009393 | 0.0000380 | No
08/09/2023 | 00:49 | CN02 | LONG RURAL | Asset failure | HV | 82.00 | 940.5 | 0.553431 | 0.0005885 | No
08/09/2023 | 01:24 | AP227B | URBAN | Asset failure | LV | 5.33 | 99.6 | 0.000819 | 0.0000082 | No
08/09/2023 | 01:32 | MI20 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 5.33 | 749.0 | 0.028667 | 0.0000383 | No
08/09/2023 | 02:14 | MG17 | LONG RURAL | Weather |  | 1.00 | 571.0 | 0.004098 | 0.0000072 | No
08/09/2023 | 02:16 | SM172E | URBAN | Unknown | Unknown | 24.00 | 591.0 | 0.021868 | 0.0000370 | No
08/09/2023 | 02:30 | HH118A | URBAN | Other |  | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
08/09/2023 | 02:36 | AP132D | URBAN | Asset failure | LV | 2.00 | 122.0 | 0.000376 | 0.0000031 | No
08/09/2023 | 02:38 | NA52 | LONG RURAL | Third Party | Other | 81.00 | 42.0 | 0.024414 | 0.0005813 | No
08/09/2023 | 02:41 | MG43 | URBAN | Vegetation | Grow-in - NSP responsibility | 52.00 | 230.0 | 0.018442 | 0.0000802 | No
08/09/2023 | 03:00 | MG06 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 374.00 | 408.0 | 1.073560 | 0.0026313 | No
08/09/2023 | 03:11 | HH428D | URBAN | Third Party | Vehicle impact | 142.00 | 424.0 | 0.092821 | 0.0002189 | No
08/09/2023 | 03:11 | R35 | LONG RURAL | Unknown | Unknown | 73.00 | 443.3 | 0.232219 | 0.0005239 | No
08/09/2023 | 03:13 | MG19 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 288.00 | 464.0 | 0.958987 | 0.0020668 | No
08/09/2023 | 03:19 | SM172D | URBAN | Vegetation | Grow-in - NSP responsibility | 74.33 | 121.1 | 0.013877 | 0.0001146 | No
08/09/2023 | 03:25 | MG16 | LONG RURAL | Weather |  | 480.00 | 281.8 | 0.970685 | 0.0034446 | No
08/09/2023 | 04:10 | BT06 | LONG RURAL | Weather |  | 25.00 | 248.0 | 0.044493 | 0.0001794 | No
08/09/2023 | 04:13 | MG41 | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 26.67 | 290.0 | 0.011923 | 0.0000411 | No
08/09/2023 | 04:39 | SG14 | SHORT RURAL | Unknown | Unknown | 38.00 | 412.0 | 0.110148 | 0.0002673 | No
08/09/2023 | 04:49 | HH341E | URBAN | Vegetation | Grow-in - NSP responsibility | 33.67 | 417.0 | 0.021645 | 0.0000519 | No
08/09/2023 | 05:24 | HH121B | URBAN | Asset failure | LV | 19.67 | 560.0 | 0.016980 | 0.0000303 | No
08/09/2023 | 05:31 | AP149A | URBAN | Asset failure | LV | 4.00 | 195.0 | 0.001203 | 0.0000062 | No
08/09/2023 | 05:37 | HH130F | URBAN | Unknown | Unknown | 59.00 | 307.0 | 0.027926 | 0.0000910 | No
08/09/2023 | 06:07 | AP132D | URBAN | Asset failure | LV | 2.00 | 656.0 | 0.002023 | 0.0000031 | No
08/09/2023 | 06:12 | HH428D | URBAN | Third Party | Vehicle impact | 200.00 | 72.6 | 0.022386 | 0.0003084 | No
08/09/2023 | 06:22 | BT18 | LONG RURAL | Unknown | Unknown | 2.00 | 346.0 | 0.004966 | 0.0000144 | No
08/09/2023 | 06:56 | CBD103C | URBAN | Asset failure | LV | 20.67 | 131.0 | 0.004174 | 0.0000319 | No
08/09/2023 | 07:01 | MG29 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 7.00 | 2,280.0 | 0.114534 | 0.0000502 | No
08/09/2023 | 07:01 | MG43 | URBAN | Vegetation | Grow-in - NSP responsibility | 119.00 | 37.0 | 0.006788 | 0.0001835 | No
08/09/2023 | 07:18 | SM172B | URBAN | Asset failure | LV | 1.00 | 5,212.0 | 0.008036 | 0.0000015 | No
08/09/2023 | 07:30 | AP226D | URBAN | Unknown | Unknown | 200.00 | 92.4 | 0.028501 | 0.0003084 | No
08/09/2023 | 07:35 | BM54 | SHORT RURAL | Asset failure | LV | 1.00 | 321.0 | 0.002258 | 0.0000070 | No
08/09/2023 | 08:00 | CV22 | LONG RURAL | Asset failure | LV | 1.00 | 329.0 | 0.002361 | 0.0000072 | No
08/09/2023 | 08:08 | ME131C | URBAN | Vegetation | Grow-in - NSP responsibility | 2.00 | 175.0 | 0.000540 | 0.0000031 | No
08/09/2023 | 08:09 | SM349D | URBAN | Asset failure | LV | 11.00 | 529.0 | 0.008971 | 0.0000170 | No
08/09/2023 | 08:11 | CN27 | LONG RURAL | Weather |  | 68.00 | 281.0 | 0.137125 | 0.0004880 | No
08/09/2023 | 08:14 | AP529A | URBAN | Asset failure | LV | 1.00 | 452.0 | 0.000697 | 0.0000015 | No
08/09/2023 | 08:17 | MI32 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 43.00 | 266.1 | 0.082104 | 0.0003086 | No
08/09/2023 | 08:19 | AP424F | URBAN | Planned |  | 102.00 | 453.2 | 0.071264 | 0.0001573 | No
08/09/2023 | 08:23 | PL14 | URBAN | Planned |  | 80.00 | 302.3 | 0.037280 | 0.0001233 | No
08/09/2023 | 08:40 | NA52 | LONG RURAL | Weather |  | 1.00 | 475.0 | 0.003409 | 0.0000072 | No
08/09/2023 | 08:50 | SM216A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 491.0 | 0.000757 | 0.0000015 | No
08/09/2023 | 09:03 | ME200F | URBAN | Asset failure | LV | 13.00 | 76.0 | 0.001523 | 0.0000200 | No
08/09/2023 | 09:05 | AP149H | URBAN | Asset failure | LV | 86.00 | 140.0 | 0.018563 | 0.0001326 | No
08/09/2023 | 09:06 | CD03 | SHORT RURAL | Planned |  | 3.00 | 135.0 | 0.002849 | 0.0000211 | No
08/09/2023 | 09:14 | YK07 | LONG RURAL | Asset failure | LV | 1.00 | 119.0 | 0.000854 | 0.0000072 | No
08/09/2023 | 09:14 | HH522A | URBAN | Asset failure | LV | 14.00 | 416.0 | 0.008979 | 0.0000216 | No
08/09/2023 | 09:26 | GA800A | SHORT RURAL | Asset failure | LV | 1.00 | 288.0 | 0.002026 | 0.0000070 | No
08/09/2023 | 09:48 | ME116A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 431.0 | 0.000664 | 0.0000015 | No
08/09/2023 | 10:00 | CV21 | LONG RURAL | Planned |  | 61.00 | 280.0 | 0.122572 | 0.0004378 | No
08/09/2023 | 10:04 | HH148B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 40.00 | 17.0 | 0.001048 | 0.0000617 | No
08/09/2023 | 10:04 | NL111Q | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 29.00 | 208.0 | 0.009300 | 0.0000447 | No
08/09/2023 | 10:12 | MG17 | LONG RURAL | Other |  | 68.00 | 66.2 | 0.032322 | 0.0004880 | No
08/09/2023 | 10:18 | HH341F | URBAN | Asset failure | LV | 114.00 | 111.7 | 0.019630 | 0.0001758 | No
08/09/2023 | 10:26 | SD34201 | SHORT RURAL | Planned |  | 12.00 | 249.0 | 0.021022 | 0.0000844 | No
08/09/2023 | 10:29 | MG32 | LONG RURAL | Asset failure | LV | 1.00 | 1,953.0 | 0.014015 | 0.0000072 | No
08/09/2023 | 10:48 | R09 | LONG RURAL | Asset failure | HV | 1.00 | 24.0 | 0.000172 | 0.0000072 | No
08/09/2023 | 11:12 | GA800C | SHORT RURAL | Asset failure | LV | 4.00 | 193.0 | 0.005431 | 0.0000281 | No
08/09/2023 | 12:10 | ME116B | URBAN | Asset failure | LV | 1.00 | 447.0 | 0.000689 | 0.0000015 | No
08/09/2023 | 12:54 | G17 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 290.0 | 0.002081 | 0.0000072 | No
08/09/2023 | 14:16 | MI32 | LONG RURAL | Weather |  | 1.00 | 149.0 | 0.001069 | 0.0000072 | No
08/09/2023 | 14:24 | KI43 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 181.0 | 0.002598 | 0.0000144 | No
08/09/2023 | 14:41 | MI21 | LONG RURAL | Overloads |  | 1.00 | 1,340.0 | 0.009616 | 0.0000072 | No
08/09/2023 | 14:59 | NU31 | LONG RURAL | Unknown | Unknown | 1.00 | 95.0 | 0.000682 | 0.0000072 | No
08/09/2023 | 16:28 | VH16 | SHORT RURAL | Asset failure | LV | 31.00 | 116.0 | 0.025300 | 0.0002181 | No
08/09/2023 | 16:53 | YK10 | LONG RURAL | Asset failure | LV | 1.00 | 193.0 | 0.001385 | 0.0000072 | No
08/09/2023 | 17:14 | MG17 | LONG RURAL | Asset failure | LV | 1.00 | 999.0 | 0.007169 | 0.0000072 | No
08/09/2023 | 17:17 | CL03 | LONG RURAL | Asset failure | HV | 7.00 | 128.0 | 0.006430 | 0.0000502 | No
08/09/2023 | 17:18 | ME427A | URBAN | Vegetation | Grow-in - NSP responsibility | 22.00 | 91.0 | 0.003087 | 0.0000339 | No
08/09/2023 | 17:25 | MT08 | LONG RURAL | Overloads |  | 56.00 | 94.0 | 0.037776 | 0.0004019 | No
08/09/2023 | 17:28 | HH522A | URBAN | Asset failure | LV | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
08/09/2023 | 17:45 | VH21 | SHORT RURAL | Overloads |  | 1.00 | 88.0 | 0.000619 | 0.0000070 | No
08/09/2023 | 18:12 | SM411A | URBAN | Overloads |  | 2.00 | 1,095.0 | 0.003376 | 0.0000031 | No
08/09/2023 | 18:15 | NL760C | URBAN | Overloads |  | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
08/09/2023 | 18:43 | GA15 | SHORT RURAL | Third Party | Vehicle impact | 6.00 | 503.2 | 0.021240 | 0.0000422 | No
08/09/2023 | 20:19 | GA15 | SHORT RURAL | Third Party | Vehicle impact | 651.00 | 58.0 | 0.265470 | 0.0045801 | No
08/09/2023 | 20:31 | MG19 | LONG RURAL | Asset failure | LV | 1.00 | 912.0 | 0.006545 | 0.0000072 | No
08/09/2023 | 20:38 | VH51 | SHORT RURAL | Asset failure | LV | 2.00 | 795.0 | 0.011186 | 0.0000141 | No
08/09/2023 | 21:58 | MG17 | LONG RURAL | Planned |  | 1.00 | 19.0 | 0.000136 | 0.0000072 | No
09/09/2023 | 00:03 | SM216B | URBAN | Asset failure | LV | 125.00 | 217.0 | 0.041828 | 0.0001927 | No
09/09/2023 | 00:10 | EL09 | URBAN | Asset failure | LV | 8.00 | 831.0 | 0.010250 | 0.0000123 | No
09/09/2023 | 03:25 | NU31 | LONG RURAL | Asset failure | HV | 405.00 | 160.5 | 0.466469 | 0.0029064 | No
09/09/2023 | 07:07 | NA52 | LONG RURAL | Asset failure | LV | 1.00 | 717.0 | 0.005145 | 0.0000072 | No
09/09/2023 | 07:34 | SM350G | URBAN | Asset failure | LV | 58.00 | 582.5 | 0.052085 | 0.0000894 | No
09/09/2023 | 08:07 | MI02 | SHORT RURAL | Asset failure | LV | 1.00 | 187.0 | 0.001316 | 0.0000070 | No
09/09/2023 | 09:17 | AP424D | URBAN | Asset failure | LV | 1.00 | 276.0 | 0.000426 | 0.0000015 | No
09/09/2023 | 09:41 | ST11 | SHORT RURAL | Asset failure | LV | 1.00 | 146.0 | 0.001027 | 0.0000070 | No
09/09/2023 | 09:46 | AP149E | URBAN | Asset failure | LV | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
09/09/2023 | 10:53 | MG43 | URBAN | Vegetation | Grow-in - NSP responsibility | 30.00 | 288.8 | 0.013358 | 0.0000463 | No
09/09/2023 | 11:05 | SM349E | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
09/09/2023 | 11:16 | CD03 | SHORT RURAL | Overloads |  | 2.00 | 230.0 | 0.003236 | 0.0000141 | No
09/09/2023 | 11:46 | SM349E | URBAN | Overloads |  | 1.00 | 644.0 | 0.000993 | 0.0000015 | No
09/09/2023 | 11:51 | SA520D | URBAN | Unknown | Unknown | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
09/09/2023 | 11:52 | MG11 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 8.00 | 224.0 | 0.012608 | 0.0000563 | No
09/09/2023 | 12:08 | MG03 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 300.67 | 88.0 | 0.186241 | 0.0021153 | No
09/09/2023 | 12:43 | MG02 | LONG RURAL | Unknown | Unknown | 138.00 | 127.0 | 0.125772 | 0.0009903 | No
09/09/2023 | 12:44 | HH341G | URBAN | Overloads |  | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
09/09/2023 | 13:10 | SM410C | URBAN | Third Party | Vehicle impact | 9.00 | 253.0 | 0.003511 | 0.0000139 | No
09/09/2023 | 13:28 | CN02 | LONG RURAL | Asset failure | HV | 1.00 | 112.0 | 0.000804 | 0.0000072 | No
09/09/2023 | 13:59 | SM349E | URBAN | Overloads |  | 1.00 | 442.0 | 0.000681 | 0.0000015 | No
09/09/2023 | 15:45 | SM179A | URBAN | Asset failure | LV | 22.00 | 486.0 | 0.016484 | 0.0000339 | No
09/09/2023 | 15:59 | MI14 | LONG RURAL | Asset failure | LV | 1.00 | 295.0 | 0.002117 | 0.0000072 | No
09/09/2023 | 16:11 | ME347A | URBAN | Asset failure | LV | 1.00 | 57.0 | 0.000088 | 0.0000015 | No
09/09/2023 | 19:28 | AP425A | URBAN | Asset failure | LV | 1.00 | 239.0 | 0.000368 | 0.0000015 | No
09/09/2023 | 19:46 | SM126C | URBAN | Asset failure | LV | 12.00 | 77.2 | 0.001428 | 0.0000185 | No
09/09/2023 | 20:27 | NL210B | URBAN | Asset failure | LV | 1.00 | 336.0 | 0.000518 | 0.0000015 | No
09/09/2023 | 22:37 | SA17 | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | No
10/09/2023 | 07:09 | HH130E | URBAN | Unknown | Unknown | 13.00 | 154.0 | 0.003087 | 0.0000200 | No
10/09/2023 | 08:13 | PA13 | LONG RURAL | Planned |  | 35.00 | 212.0 | 0.053248 | 0.0002512 | No
10/09/2023 | 08:43 | HH121F | URBAN | Planned |  | 80.00 | 230.0 | 0.028368 | 0.0001233 | No
10/09/2023 | 08:56 | MB22 | SHORT RURAL | Planned |  | 2.00 | 209.0 | 0.002941 | 0.0000141 | No
10/09/2023 | 09:18 | BT26 | LONG RURAL | Planned |  | 2.00 | 141.0 | 0.002024 | 0.0000144 | No
10/09/2023 | 09:25 | ST34 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 68.00 | 217.4 | 0.106095 | 0.0004880 | No
10/09/2023 | 09:56 | MG34 | LONG RURAL | Asset failure | HV | 213.00 | 223.2 | 0.341148 | 0.0015286 | No
10/09/2023 | 10:05 | HH130E | URBAN | Asset failure | LV | 39.00 | 91.0 | 0.005472 | 0.0000601 | No
10/09/2023 | 11:25 | SA17 | URBAN | Asset failure | LV | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
10/09/2023 | 13:39 | BT34 | LONG RURAL | Planned |  | 20.00 | 75.0 | 0.010764 | 0.0001435 | No
10/09/2023 | 17:34 | NL210D | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
10/09/2023 | 19:05 | SA18 | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
10/09/2023 | 19:06 | HH386D | URBAN | Third Party | Vehicle impact | 60.00 | 308.0 | 0.028492 | 0.0000925 | No
11/09/2023 | 00:38 | SM126C | URBAN | Animal | Animal impact | 34.67 | 150.0 | 0.008017 | 0.0000534 | No
11/09/2023 | 02:03 | LX43 | SHORT RURAL | Unknown | Unknown | 1.00 | 544.0 | 0.003827 | 0.0000070 | No
11/09/2023 | 06:05 | HH130E | URBAN | Asset failure | LV | 39.00 | 245.0 | 0.014731 | 0.0000601 | No
11/09/2023 | 07:57 | VH23 | SHORT RURAL | Weather |  | 870.00 | 92.0 | 0.563121 | 0.0061209 | No
11/09/2023 | 08:05 | HH148A | URBAN | Unknown | Unknown | 1.00 | 73.0 | 0.000113 | 0.0000015 | No
11/09/2023 | 08:20 | AP355H | URBAN | Planned |  | 24.00 | 227.0 | 0.008399 | 0.0000370 | No
11/09/2023 | 08:20 | NU22 | LONG RURAL | Overloads |  | 1.00 | 116.0 | 0.000832 | 0.0000072 | No
11/09/2023 | 08:32 | HH118C | URBAN | Asset failure | LV | 2.00 | 265.0 | 0.000817 | 0.0000031 | No
11/09/2023 | 08:56 | NA60 | LONG RURAL | Asset failure | HV | 2.00 | 307.0 | 0.004406 | 0.0000144 | No
11/09/2023 | 08:57 | HH118C | URBAN | Asset failure | HV | 690.00 | 27.8 | 0.029598 | 0.0010638 | No
11/09/2023 | 09:32 | CV16 | LONG RURAL | Planned |  | 2.00 | 115.0 | 0.001651 | 0.0000144 | No
11/09/2023 | 09:34 | MTB51 | LONG RURAL | Planned |  | 40.00 | 181.0 | 0.051957 | 0.0002871 | No
11/09/2023 | 09:51 | R06 | LONG RURAL | Planned |  | 60.00 | 231.0 | 0.099464 | 0.0004306 | No
11/09/2023 | 09:57 | MB25 | LONG RURAL | Planned |  | 55.00 | 70.0 | 0.027629 | 0.0003947 | No
11/09/2023 | 09:58 | AP529A | URBAN | Asset failure | LV | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
11/09/2023 | 10:55 | M91 | LONG RURAL | Planned |  | 356.00 | 245.0 | 0.625919 | 0.0025548 | No
11/09/2023 | 10:55 | SA34 | URBAN | Asset failure | LV | 1.00 | 458.0 | 0.000706 | 0.0000015 | No
11/09/2023 | 10:59 | MI26 | LONG RURAL | Planned |  | 25.00 | 60.0 | 0.010764 | 0.0001794 | No
11/09/2023 | 11:09 | HH118C | URBAN | Asset failure | HV | 956.00 | 7.0 | 0.010317 | 0.0014739 | No
11/09/2023 | 11:16 | HH118D | URBAN | Asset failure | LV | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
11/09/2023 | 11:24 | SG04 | SHORT RURAL | Weather |  | 1.00 | 106.0 | 0.000746 | 0.0000070 | No
11/09/2023 | 11:26 | SG04 | SHORT RURAL | Weather |  | 42.00 | 55.0 | 0.016252 | 0.0002955 | No
11/09/2023 | 12:00 | NL111B | URBAN | Asset failure | LV | 1.00 | 297.0 | 0.000458 | 0.0000015 | No
11/09/2023 | 12:07 | MG21 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 294.0 | 0.006330 | 0.0000215 | No
11/09/2023 | 13:25 | GA50 | URBAN | Asset failure | LV | 83.00 | 52.0 | 0.006654 | 0.0001280 | No
11/09/2023 | 14:19 | NL511A | URBAN | Asset failure | LV | 73.00 | 283.0 | 0.031851 | 0.0001125 | No
11/09/2023 | 14:39 | SA14 | URBAN | Overloads |  | 1.00 | 397.0 | 0.000612 | 0.0000015 | No
11/09/2023 | 14:52 | MI12 | LONG RURAL | Asset failure | LV | 1.00 | 261.0 | 0.001873 | 0.0000072 | No
11/09/2023 | 16:03 | SA744D | URBAN | Asset failure | LV | 1.00 | 352.0 | 0.000543 | 0.0000015 | No
11/09/2023 | 16:07 | SA34 | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
11/09/2023 | 16:11 | NL760B | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
11/09/2023 | 16:46 | AP139A | URBAN | Asset failure | LV | 79.00 | 98.0 | 0.011936 | 0.0001218 | No
11/09/2023 | 17:21 | HH145A | URBAN | Asset failure | LV | 1.00 | 354.0 | 0.000546 | 0.0000015 | No
11/09/2023 | 17:34 | AP344E | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
11/09/2023 | 18:19 | SA18 | URBAN | Unknown | Unknown | 13.00 | 116.0 | 0.002325 | 0.0000200 | No
11/09/2023 | 19:36 | MT12 | SHORT RURAL | Asset failure | HV | 78.00 | 83.0 | 0.045548 | 0.0005488 | No
11/09/2023 | 19:57 | SM374E | URBAN | Asset failure | LV | 19.00 | 86.0 | 0.002519 | 0.0000293 | No
11/09/2023 | 22:54 | ME347C | URBAN | Overloads |  | 1.00 | 699.0 | 0.001078 | 0.0000015 | No
11/09/2023 | 23:00 | NL115D | URBAN | Unknown | Unknown | 1,575.00 | 94.7 | 0.230033 | 0.0024283 | No
11/09/2023 | 23:42 | CBD353Q | CBD | Planned |  | 1.00 | 308.0 | 0.044499 | 0.0001445 | No
12/09/2023 | 03:34 | NL115D | URBAN | Asset failure | HV | 400.00 | 103.5 | 0.063856 | 0.0006167 | No
12/09/2023 | 06:26 | SG14 | SHORT RURAL | Asset failure | LV | 1.00 | 222.0 | 0.001562 | 0.0000070 | No
12/09/2023 | 07:04 | HH107C | URBAN | Asset failure | LV | 1.00 | 571.0 | 0.000880 | 0.0000015 | No
12/09/2023 | 07:55 | HH496G | URBAN | Overloads |  | 4.00 | 59.0 | 0.000364 | 0.0000062 | No
12/09/2023 | 08:26 | SD49500 | LONG RURAL | Animal | Animal impact | 5.00 | 80.0 | 0.002871 | 0.0000359 | No
12/09/2023 | 09:01 | NU22 | LONG RURAL | Planned |  | 49.00 | 359.4 | 0.126375 | 0.0003516 | No
12/09/2023 | 09:14 | KI13 | LONG RURAL | Planned |  | 71.00 | 10.0 | 0.005095 | 0.0005095 | No
12/09/2023 | 09:34 | CV16 | LONG RURAL | Planned |  | 24.00 | 243.0 | 0.041852 | 0.0001722 | No
12/09/2023 | 09:34 | CV19 | LONG RURAL | Planned |  | 14.00 | 89.0 | 0.008942 | 0.0001005 | No
12/09/2023 | 09:39 | KI13 | LONG RURAL | Planned |  | 1.00 | 248.0 | 0.001780 | 0.0000072 | No
12/09/2023 | 09:39 | HH341G | URBAN | Planned |  | 288.00 | 416.0 | 0.184714 | 0.0004440 | No
12/09/2023 | 09:43 | M71 | LONG RURAL | Planned |  | 5.00 | 78.0 | 0.002799 | 0.0000359 | No
12/09/2023 | 10:21 | GA43 | SHORT RURAL | Planned |  | 22.00 | 26.0 | 0.004024 | 0.0001548 | No
12/09/2023 | 10:32 | AP529A | URBAN | Asset failure | LV | 112.00 | 10.5 | 0.001812 | 0.0001727 | No
12/09/2023 | 10:46 | G09 | LONG RURAL | Planned |  | 1.00 | 73.0 | 0.000524 | 0.0000072 | No
12/09/2023 | 10:53 | MB03 | LONG RURAL | Planned |  | 100.00 | 244.0 | 0.175102 | 0.0007176 | No
12/09/2023 | 11:03 | MI01 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 466.00 | 80.0 | 0.267534 | 0.0033442 | No
12/09/2023 | 11:08 | CV16 | LONG RURAL | Planned |  | 2.00 | 53.0 | 0.000761 | 0.0000144 | No
12/09/2023 | 11:36 | MT14 | SHORT RURAL | Asset failure | HV | 39.00 | 26.0 | 0.007134 | 0.0002744 | No
12/09/2023 | 11:38 | MT14 | SHORT RURAL | Asset failure | LV | 1.00 | 49.0 | 0.000345 | 0.0000070 | No
12/09/2023 | 11:47 | LX34 | SHORT RURAL | Planned |  | 4.00 | 36.0 | 0.001013 | 0.0000281 | No
12/09/2023 | 12:08 | HH145B | URBAN | Asset failure | LV | 24.00 | 44.0 | 0.001628 | 0.0000370 | No
12/09/2023 | 12:40 | VH17 | SHORT RURAL | Unknown | Unknown | 1.00 | 156.0 | 0.001098 | 0.0000070 | No
12/09/2023 | 12:59 | G09 | LONG RURAL | Planned |  | 1.00 | 84.0 | 0.000603 | 0.0000072 | No
12/09/2023 | 13:11 | AP351C | URBAN | Asset failure | LV | 29.00 | 215.0 | 0.009613 | 0.0000447 | No
12/09/2023 | 13:13 | ME427E | URBAN | Asset failure | LV | 43.00 | 52.0 | 0.003447 | 0.0000663 | No
12/09/2023 | 13:42 | SM411A | URBAN | Asset failure | LV | 84.00 | 42.4 | 0.005492 | 0.0001295 | No
12/09/2023 | 13:54 | HH429C | URBAN | Asset failure | LV | 96.00 | 56.0 | 0.008288 | 0.0001480 | No
12/09/2023 | 14:09 | KI16 | LONG RURAL | Planned |  | 71.00 | 9.0 | 0.004586 | 0.0005095 | No
12/09/2023 | 14:42 | CL16 | LONG RURAL | Asset failure | LV | 13.00 | 182.7 | 0.017044 | 0.0000933 | No
12/09/2023 | 15:23 | MI12 | LONG RURAL | Asset failure | LV | 1.00 | 192.0 | 0.001378 | 0.0000072 | No
12/09/2023 | 15:48 | BM52 | URBAN | Asset failure | LV | 40.00 | 40.0 | 0.002467 | 0.0000617 | No
12/09/2023 | 16:36 | NL760C | URBAN | Other |  | 1.00 | 40.0 | 0.000062 | 0.0000015 | No
12/09/2023 | 17:07 | MTB12 | SHORT RURAL | Weather |  | 292.00 | 104.0 | 0.213654 | 0.0020544 | No
12/09/2023 | 17:26 | WK43 | SHORT RURAL | Asset failure | LV | 2.00 | 264.0 | 0.003715 | 0.0000141 | No
12/09/2023 | 17:28 | NL234A | URBAN | Asset failure | LV | 39.33 | 26.0 | 0.001577 | 0.0000606 | No
12/09/2023 | 17:57 | SM126D | URBAN | Overloads |  | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
12/09/2023 | 18:12 | HH102C | URBAN | Asset failure | LV | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
12/09/2023 | 18:13 | MV14 | SHORT RURAL | Weather |  | 6.00 | 39.0 | 0.001646 | 0.0000422 | No
12/09/2023 | 19:18 | CN52 | LONG RURAL | Asset failure | HV | 12.00 | 90.3 | 0.007779 | 0.0000861 | No
12/09/2023 | 19:40 | HH341J | URBAN | Asset failure | LV | 39.00 | 66.0 | 0.003968 | 0.0000601 | No
12/09/2023 | 20:23 | WK43 | SHORT RURAL | Asset failure | HV | 2.67 | 78.0 | 0.001463 | 0.0000188 | No
12/09/2023 | 21:04 | EL01C | URBAN | Overloads |  | 4.00 | 94.0 | 0.000580 | 0.0000062 | No
12/09/2023 | 21:13 | NL511A | URBAN | Asset failure | LV | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
12/09/2023 | 21:22 | ME200G | URBAN | Third Party | Vehicle impact | 20.00 | 188.0 | 0.005797 | 0.0000308 | No
13/09/2023 | 02:39 | NL210A | URBAN | Asset failure | LV | 6.33 | 1,211.0 | 0.011825 | 0.0000098 | No
13/09/2023 | 06:31 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 484.0 | 0.003405 | 0.0000070 | No
13/09/2023 | 08:54 | SG01 | SHORT RURAL | Planned |  | 97.00 | 258.6 | 0.176506 | 0.0006824 | No
13/09/2023 | 09:00 | HH409C | URBAN | Planned |  | 235.00 | 364.5 | 0.132059 | 0.0003623 | No
13/09/2023 | 09:09 | KA30 | SHORT RURAL | Planned |  | 67.00 | 206.0 | 0.097104 | 0.0004714 | No
13/09/2023 | 09:15 | CV18 | SHORT RURAL | Planned |  | 3.00 | 239.0 | 0.005044 | 0.0000211 | No
13/09/2023 | 09:15 | YK16 | LONG RURAL | Planned |  | 2.00 | 32.0 | 0.000459 | 0.0000144 | No
13/09/2023 | 09:21 | VH71 | SHORT RURAL | Planned |  | 346.00 | 289.0 | 0.703507 | 0.0024343 | No
13/09/2023 | 09:26 | SG03 | SHORT RURAL | Planned |  | 40.00 | 128.0 | 0.036022 | 0.0002814 | No
13/09/2023 | 09:27 | EL09 | URBAN | Overloads |  | 1.00 | 2,023.0 | 0.003119 | 0.0000015 | No
13/09/2023 | 09:38 | EL16 | URBAN | Planned |  | 42.00 | 311.0 | 0.020138 | 0.0000648 | No
13/09/2023 | 09:41 | HH496G | URBAN | Asset failure | LV | 12.00 | 89.0 | 0.001647 | 0.0000185 | No
13/09/2023 | 09:52 | G09 | LONG RURAL | Planned |  | 2.00 | 118.0 | 0.001694 | 0.0000144 | No
13/09/2023 | 10:02 | MB42 | LONG RURAL | Planned |  | 25.00 | 147.0 | 0.026373 | 0.0001794 | No
13/09/2023 | 10:06 | ME347C | URBAN | Asset failure | LV | 44.00 | 88.0 | 0.005970 | 0.0000678 | No
13/09/2023 | 10:11 | PP13 | LONG RURAL | Asset failure | LV | 1.00 | 324.0 | 0.002325 | 0.0000072 | No
13/09/2023 | 10:21 | R29 | LONG RURAL | Planned |  | 16.00 | 113.0 | 0.012975 | 0.0001148 | No
13/09/2023 | 11:52 | PA25 | SHORT RURAL | Weather |  | 9.00 | 51.0 | 0.003229 | 0.0000633 | No
13/09/2023 | 11:59 | G40 | LONG RURAL | Overloads |  | 1.00 | 465.0 | 0.003337 | 0.0000072 | No
13/09/2023 | 12:44 | G09 | LONG RURAL | Planned |  | 4.00 | 41.0 | 0.001177 | 0.0000287 | No
13/09/2023 | 12:50 | HH107B | URBAN | Asset failure | LV | 1.00 | 1,551.0 | 0.002391 | 0.0000015 | No
13/09/2023 | 13:53 | SA711C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 259.0 | 0.000399 | 0.0000015 | No
13/09/2023 | 14:14 | HH341E | URBAN | Third Party | Other | 20.00 | 51.0 | 0.001573 | 0.0000308 | No
13/09/2023 | 15:33 | MG19 | LONG RURAL | Asset failure | HV | 287.00 | 97.0 | 0.199782 | 0.0020596 | No
13/09/2023 | 16:38 | HH121C | URBAN | Asset failure | LV | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
13/09/2023 | 16:46 | LX43 | SHORT RURAL | Asset failure | LV | 1.00 | 226.0 | 0.001590 | 0.0000070 | No
13/09/2023 | 18:02 | SD37301 | SHORT RURAL | Other |  | 2.00 | 20.0 | 0.000281 | 0.0000141 | No
13/09/2023 | 18:05 | SD40300 | LONG RURAL | Asset failure | Subtransmission | 1,286.00 | 116.3 | 1.073091 | 0.0092288 | No
13/09/2023 | 19:31 | HH409A | URBAN | Animal | Animal impact | 63.33 | 101.0 | 0.009862 | 0.0000976 | No
13/09/2023 | 19:43 | MV53 | SHORT RURAL | Unknown | Unknown | 69.00 | 178.0 | 0.086410 | 0.0004854 | No
13/09/2023 | 20:05 | HH118C | URBAN | Asset failure | LV | 6.33 | 154.0 | 0.001504 | 0.0000098 | No
13/09/2023 | 23:17 | ME231E | URBAN | Planned |  | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
14/09/2023 | 02:38 | SA18 | URBAN | Asset failure | HV | 1.00 | 81.0 | 0.000125 | 0.0000015 | No
14/09/2023 | 06:28 | NA62 | LONG RURAL | Asset failure | HV | 42.00 | 494.1 | 0.148938 | 0.0003014 | No
14/09/2023 | 07:24 | HH496G | URBAN | Asset failure | HV | 138.00 | 263.0 | 0.055963 | 0.0002128 | No
14/09/2023 | 07:39 | HH496F | URBAN | Unknown | Unknown | 13.00 | 493.0 | 0.009881 | 0.0000200 | No
14/09/2023 | 08:34 | VH45 | SHORT RURAL | Asset failure | LV | 62.00 | 147.0 | 0.064121 | 0.0004362 | No
14/09/2023 | 09:04 | MG14 | LONG RURAL | Planned |  | 41.00 | 201.0 | 0.059140 | 0.0002942 | No
14/09/2023 | 09:21 | SM126B | URBAN | Overloads |  | 1.00 | 184.0 | 0.000284 | 0.0000015 | No
14/09/2023 | 09:28 | MTB22 | SHORT RURAL | Planned |  | 37.00 | 254.0 | 0.066120 | 0.0002603 | No
14/09/2023 | 09:29 | HH522A | URBAN | Planned |  | 41.00 | 8.0 | 0.000506 | 0.0000632 | No
14/09/2023 | 09:30 | SA36 | URBAN | Asset failure | LV | 17.00 | 108.2 | 0.002837 | 0.0000262 | No
14/09/2023 | 09:35 | EL20 | URBAN | Planned |  | 15.00 | 290.0 | 0.006707 | 0.0000231 | No
14/09/2023 | 09:46 | M13 | LONG RURAL | Planned |  | 3.00 | 143.0 | 0.003079 | 0.0000215 | No
14/09/2023 | 10:04 | BM13 | SHORT RURAL | Unknown | Unknown | 1.00 | 269.0 | 0.001893 | 0.0000070 | No
14/09/2023 | 10:10 | CV31 | LONG RURAL | Planned |  | 1.00 | 52.0 | 0.000373 | 0.0000072 | No
14/09/2023 | 10:11 | SD49200 | LONG RURAL | Unknown | Unknown | 1.00 | 1,561.0 | 0.011202 | 0.0000072 | No
14/09/2023 | 10:14 | HH341K | URBAN | Vegetation | Grow-in - NSP responsibility | 9.33 | 122.0 | 0.001756 | 0.0000144 | No
14/09/2023 | 10:29 | BT06 | LONG RURAL | Planned |  | 2.00 | 52.0 | 0.000746 | 0.0000144 | No
14/09/2023 | 10:49 | SD34102 | LONG RURAL | Planned |  | 3.00 | 255.0 | 0.005490 | 0.0000215 | No
14/09/2023 | 10:50 | SB03 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 1,680.00 | 78.5 | 0.946637 | 0.0120562 | No
14/09/2023 | 10:50 | SB03 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 744.00 | 135.6 | 0.709536 | 0.0052344 | No
14/09/2023 | 10:53 | SM216D | URBAN | Asset failure | LV | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
14/09/2023 | 10:53 | CN12 | LONG RURAL | Planned |  | 12.00 | 92.0 | 0.007923 | 0.0000861 | No
14/09/2023 | 10:58 | ME427F | URBAN | Asset failure | LV | 58.00 | 175.0 | 0.015649 | 0.0000894 | No
14/09/2023 | 11:04 | NA04 | LONG RURAL | Asset failure | HV | 118.33 | 6.0 | 0.005095 | 0.0008492 | No
14/09/2023 | 11:34 | AP214D | URBAN | Asset failure | LV | 2.00 | 366.0 | 0.001129 | 0.0000031 | No
14/09/2023 | 11:42 | HH341K | URBAN | Vegetation | Grow-in - NSP responsibility | 19.00 | 118.0 | 0.003457 | 0.0000293 | No
14/09/2023 | 11:51 | EL11 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 67.00 | 137.0 | 0.014152 | 0.0001033 | No
14/09/2023 | 12:30 | SA14 | URBAN | Asset failure | LV | 19.00 | 367.7 | 0.010772 | 0.0000293 | No
14/09/2023 | 12:36 | HH386B | URBAN | Asset failure | LV | 3.00 | 636.0 | 0.002942 | 0.0000046 | No
14/09/2023 | 12:36 | GA03 | LONG RURAL | Planned |  | 35.00 | 9.0 | 0.002261 | 0.0002512 | No
14/09/2023 | 12:45 | WHY03 | URBAN | Asset failure | LV | 14.00 | 484.4 | 0.010456 | 0.0000216 | No
14/09/2023 | 12:53 | MB28 | SHORT RURAL | Asset failure | HV | 328.00 | 142.5 | 0.328895 | 0.0023076 | No
14/09/2023 | 12:59 | MB61 | LONG RURAL | Asset failure | LV | 1.00 | 495.0 | 0.003552 | 0.0000072 | No
14/09/2023 | 13:06 | SA40 | URBAN | Third Party | Other | 2,785.00 | 42.8 | 0.183666 | 0.0042938 | No
14/09/2023 | 13:12 | W01 | LONG RURAL | Asset failure | HV | 19.00 | 208.0 | 0.028361 | 0.0001364 | No
14/09/2023 | 13:25 | EL03 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 510.0 | 0.000786 | 0.0000015 | No
14/09/2023 | 13:34 | NA56 | LONG RURAL | Asset failure | LV | 1.00 | 418.0 | 0.003000 | 0.0000072 | No
14/09/2023 | 13:38 | SM349F | URBAN | Unknown | Unknown | 16.67 | 282.0 | 0.007246 | 0.0000257 | No
14/09/2023 | 13:39 | HH145B | URBAN | Third Party | Other | 30.00 | 46.0 | 0.002128 | 0.0000463 | No
14/09/2023 | 13:44 | HH118A | URBAN | Asset failure | LV | 19.33 | 40.0 | 0.001192 | 0.0000298 | No
14/09/2023 | 13:45 | SA520G | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 60.00 | 83.0 | 0.007678 | 0.0000925 | No
14/09/2023 | 14:05 | HH121F | URBAN | Unknown | Unknown | 1.00 | 277.0 | 0.000427 | 0.0000015 | No
14/09/2023 | 14:16 | HH177G | URBAN | Asset failure | LV | 1.00 | 591.0 | 0.000911 | 0.0000015 | No
14/09/2023 | 14:38 | CM20 | LONG RURAL | Asset failure | HV | 241.00 | 121.5 | 0.210094 | 0.0017295 | No
14/09/2023 | 14:42 | W24 | LONG RURAL | Asset failure | HV | 69.00 | 312.6 | 0.154808 | 0.0004952 | No
14/09/2023 | 15:02 | SM126E | URBAN | Other |  | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
14/09/2023 | 15:06 | KI12 | LONG RURAL | Asset failure | HV | 2.00 | 45.0 | 0.000646 | 0.0000144 | No
14/09/2023 | 15:37 | NU10 | LONG RURAL | Asset failure | LV | 1.33 | 151.0 | 0.001445 | 0.0000096 | No
14/09/2023 | 15:37 | HH522A | URBAN | Asset failure | LV | 1.00 | 300.0 | 0.000463 | 0.0000015 | No
14/09/2023 | 15:46 | NA04 | LONG RURAL | Asset failure | HV | 140.00 | 7.0 | 0.007033 | 0.0010047 | No
14/09/2023 | 15:50 | W01 | LONG RURAL | Asset failure | HV | 92.67 | 47.0 | 0.031255 | 0.0006650 | No
14/09/2023 | 16:28 | SM216C | URBAN | Asset failure | LV | 1.00 | 430.0 | 0.000663 | 0.0000015 | No
14/09/2023 | 17:07 | VH44 | SHORT RURAL | Asset failure | LV | 2.00 | 227.0 | 0.003194 | 0.0000141 | No
14/09/2023 | 17:33 | EL02 | URBAN | Asset failure | LV | 68.00 | 414.0 | 0.043403 | 0.0001048 | No
14/09/2023 | 18:55 | HH341D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 107.33 | 321.0 | 0.053120 | 0.0001655 | No
14/09/2023 | 21:34 | SM137B | URBAN | Asset failure | LV | 66.67 | 73.0 | 0.007503 | 0.0001028 | No
14/09/2023 | 22:10 | SD41200 | SHORT RURAL | Planned |  | 1,617.00 | 541.1 | 6.156202 | 0.0113764 | No
14/09/2023 | 22:52 | SG10 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 180.0 | 0.001266 | 0.0000070 | No
15/09/2023 | 00:46 | HH177A | URBAN | Asset failure | LV | 30.00 | 69.0 | 0.003191 | 0.0000463 | No
15/09/2023 | 01:51 | HH341E | URBAN | Asset failure | LV | 19.00 | 62.0 | 0.001816 | 0.0000293 | No
15/09/2023 | 06:27 | HH496C | URBAN | Asset failure | LV | 1.00 | 281.0 | 0.000433 | 0.0000015 | No
15/09/2023 | 07:29 | BM21 | SHORT RURAL | Asset failure | LV | 1.00 | 97.0 | 0.000682 | 0.0000070 | No
15/09/2023 | 08:38 | KA11 | LONG RURAL | Planned |  | 127.00 | 129.6 | 0.118094 | 0.0009114 | No
15/09/2023 | 09:08 | CL12 | LONG RURAL | Planned |  | 18.00 | 268.0 | 0.034619 | 0.0001292 | No
15/09/2023 | 09:16 | SA12 | URBAN | Third Party | Vehicle impact | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
15/09/2023 | 09:30 | G13 | LONG RURAL | Planned |  | 20.00 | 119.0 | 0.017080 | 0.0001435 | No
15/09/2023 | 09:31 | CD23 | LONG RURAL | Planned |  | 50.00 | 261.0 | 0.093651 | 0.0003588 | No
15/09/2023 | 09:47 | M73 | LONG RURAL | Planned |  | 24.00 | 138.0 | 0.023768 | 0.0001722 | No
15/09/2023 | 09:56 | MB22 | SHORT RURAL | Asset failure | LV | 1.00 | 27,533.0 | 0.193708 | 0.0000070 | No
15/09/2023 | 11:01 | W06 | LONG RURAL | Planned |  | 21.00 | 319.0 | 0.048074 | 0.0001507 | No
15/09/2023 | 12:03 | G13 | LONG RURAL | Planned |  | 6.00 | 61.0 | 0.002627 | 0.0000431 | No
15/09/2023 | 12:28 | HH341D | URBAN | Vegetation | Grow-in - NSP responsibility | 2.00 | 611.0 | 0.001884 | 0.0000031 | No
15/09/2023 | 13:07 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 864.0 | 0.006079 | 0.0000070 | No
15/09/2023 | 13:31 | VH11 | URBAN | Asset failure | LV | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
15/09/2023 | 15:00 | ME347C | URBAN | Asset failure | LV | 51.00 | 110.0 | 0.008649 | 0.0000786 | No
15/09/2023 | 15:11 | NL234C | URBAN | Asset failure | LV | 1.00 | 630.0 | 0.000971 | 0.0000015 | No
15/09/2023 | 15:32 | AP139C | URBAN | Overloads |  | 10.00 | 143.0 | 0.002205 | 0.0000154 | No
15/09/2023 | 16:15 | ME347C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 11.33 | 86.0 | 0.001503 | 0.0000175 | No
15/09/2023 | 18:04 | MG10 | LONG RURAL | Unknown | Unknown | 130.00 | 34.0 | 0.031719 | 0.0009329 | No
15/09/2023 | 18:07 | PP10 | URBAN | Asset failure | LV | 1.00 | 406.0 | 0.000626 | 0.0000015 | No
15/09/2023 | 18:37 | ME116B | URBAN | Animal | Animal impact | 32.00 | 463.0 | 0.022843 | 0.0000493 | No
15/09/2023 | 18:40 | ME116B | URBAN | Animal | Animal impact | 1.00 | 448.0 | 0.000691 | 0.0000015 | No
15/09/2023 | 19:32 | MG11 | SHORT RURAL | Asset failure | LV | 1.00 | 944.0 | 0.006642 | 0.0000070 | No
15/09/2023 | 20:32 | NL210D | URBAN | Asset failure | LV | 1.00 | 340.0 | 0.000524 | 0.0000015 | No
15/09/2023 | 21:46 | R35 | LONG RURAL | Asset failure | HV | 2.00 | 22.0 | 0.000316 | 0.0000144 | No
15/09/2023 | 23:17 | ME116B | URBAN | Animal | Animal impact | 58.33 | 72.6 | 0.006525 | 0.0000899 | No
15/09/2023 | 23:33 | GA745A | SHORT RURAL | Unknown | Unknown | 7.00 | 265.0 | 0.013051 | 0.0000492 | No
16/09/2023 | 00:03 | R08 | LONG RURAL | Animal | Animal impact | 121.00 | 811.0 | 0.704220 | 0.0008683 | No
16/09/2023 | 06:28 | MV62 | SHORT RURAL | Asset failure | LV | 1.00 | 336.0 | 0.002364 | 0.0000070 | No
16/09/2023 | 07:50 | NU15 | LONG RURAL | Unknown | Unknown | 91.33 | 212.0 | 0.138953 | 0.0006554 | No
16/09/2023 | 08:00 | CBD366U | CBD | Planned |  | 2.00 | 441.0 | 0.127429 | 0.0002890 | No
16/09/2023 | 08:06 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 215.0 | 0.001513 | 0.0000070 | No
16/09/2023 | 08:58 | CL23 | LONG RURAL | Planned |  | 4.00 | 72.0 | 0.002067 | 0.0000287 | No
16/09/2023 | 10:14 | HH107B | URBAN | Overloads |  | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
16/09/2023 | 10:14 | WHY03 | URBAN | Asset failure | LV | 14.00 | 217.6 | 0.004696 | 0.0000216 | No
16/09/2023 | 10:36 | HH145D | URBAN | Overloads |  | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
16/09/2023 | 11:13 | VH11 | URBAN | Asset failure | LV | 4.00 | 139.5 | 0.000860 | 0.0000062 | No
16/09/2023 | 11:21 | HH496A | URBAN | Asset failure | LV | 49.00 | 28.0 | 0.002115 | 0.0000755 | No
16/09/2023 | 12:27 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 256.0 | 0.001801 | 0.0000070 | No
16/09/2023 | 15:31 | SD54102 | LONG RURAL | Asset failure | Subtransmission | 10.00 | 211.0 | 0.015142 | 0.0000718 | No
16/09/2023 | 15:42 | PA05 | LONG RURAL | Asset failure | LV | 1.00 | 197.0 | 0.001414 | 0.0000072 | No
16/09/2023 | 15:48 | PA05 | LONG RURAL | Asset failure | LV | 1.00 | 190.0 | 0.001364 | 0.0000072 | No
16/09/2023 | 16:28 | HH148C | URBAN | Asset failure | LV | 25.00 | 32.0 | 0.001233 | 0.0000385 | No
16/09/2023 | 17:41 | SD54102 | LONG RURAL | Asset failure | Subtransmission | 97.00 | 22.0 | 0.015329 | 0.0006961 | No
16/09/2023 | 18:21 | LX21 | SHORT RURAL | Unknown | Unknown | 18.00 | 234.0 | 0.029633 | 0.0001266 | No
16/09/2023 | 20:17 | EL15 | URBAN | Third Party | Other | 8.00 | 465.5 | 0.005741 | 0.0000123 | No
16/09/2023 | 20:34 | LX21 | SHORT RURAL | Unknown | Unknown | 1.00 | 116.0 | 0.000816 | 0.0000070 | No
16/09/2023 | 21:34 | MTB11 | SHORT RURAL | Unknown | Unknown | 1.00 | 154.0 | 0.001083 | 0.0000070 | No
17/09/2023 | 01:47 | HH496A | URBAN | Asset failure | LV | 16.33 | 89.0 | 0.002241 | 0.0000252 | No
17/09/2023 | 06:36 | SD40102 | LONG RURAL | Unknown | Unknown | 1.00 | 155.0 | 0.001112 | 0.0000072 | No
17/09/2023 | 07:31 | KI41 | LONG RURAL | Unknown | Unknown | 3.00 | 133.0 | 0.002863 | 0.0000215 | No
17/09/2023 | 07:51 | M04 | LONG RURAL | Unknown | Unknown | 107.00 | 356.9 | 0.274071 | 0.0007679 | No
17/09/2023 | 07:57 | HH130B | URBAN | Planned |  | 337.00 | 315.6 | 0.163995 | 0.0005196 | No
17/09/2023 | 08:53 | SM350E | URBAN | Planned |  | 40.00 | 493.7 | 0.030447 | 0.0000617 | No
17/09/2023 | 08:56 | AP139C | URBAN | Planned |  | 29.00 | 1,821.0 | 0.081418 | 0.0000447 | No
17/09/2023 | 09:14 | NL111B | URBAN | Planned |  | 89.00 | 326.7 | 0.044823 | 0.0001372 | No
17/09/2023 | 09:37 | SA520E | URBAN | Planned |  | 2.00 | 354.0 | 0.001092 | 0.0000031 | No
17/09/2023 | 09:37 | SA19 | URBAN | Planned |  | 267.00 | 108.0 | 0.044458 | 0.0004116 | No
17/09/2023 | 10:55 | NL115E | URBAN | Asset failure | LV | 15.33 | 196.0 | 0.004633 | 0.0000236 | No
17/09/2023 | 11:04 | SG07 | SHORT RURAL | Third Party | Vehicle impact | 8.00 | 140.0 | 0.007880 | 0.0000563 | No
17/09/2023 | 11:30 | NL115B | URBAN | Vegetation | Grow-in - NSP responsibility | 2.00 | 156.0 | 0.000481 | 0.0000031 | No
17/09/2023 | 11:48 | SG14 | SHORT RURAL | Overloads |  | 1.00 | 247.0 | 0.001738 | 0.0000070 | No
17/09/2023 | 14:34 | SA32 | URBAN | Asset failure | LV | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
17/09/2023 | 14:34 | AP226B | URBAN | Overloads |  | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
17/09/2023 | 16:17 | NL451C | URBAN | Asset failure | LV | 1.00 | 279.0 | 0.000430 | 0.0000015 | No
17/09/2023 | 16:37 | ME427A | URBAN | Asset failure | LV | 16.00 | 84.0 | 0.002072 | 0.0000247 | No
17/09/2023 | 18:01 | MI01 | LONG RURAL | Asset failure | LV | 1.00 | 217.0 | 0.001557 | 0.0000072 | No
17/09/2023 | 18:17 | MG26 | LONG RURAL | Unknown | Unknown | 12.00 | 290.0 | 0.024974 | 0.0000861 | No
17/09/2023 | 18:29 | NU02 | LONG RURAL | Overloads |  | 1.00 | 386.0 | 0.002770 | 0.0000072 | No
17/09/2023 | 21:27 | LX21 | SHORT RURAL | Unknown | Unknown | 15.33 | 209.0 | 0.022546 | 0.0001079 | No
17/09/2023 | 21:48 | NL511A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
17/09/2023 | 21:57 | MG32 | LONG RURAL | Asset failure | LV | 1.00 | 236.0 | 0.001694 | 0.0000072 | No
17/09/2023 | 22:10 | NU25 | LONG RURAL | Planned |  | 135.00 | 443.0 | 0.429180 | 0.0009688 | No
18/09/2023 | 07:06 | AP355A | URBAN | Asset failure | LV | 43.00 | 181.0 | 0.011999 | 0.0000663 | No
18/09/2023 | 07:44 | MG32 | LONG RURAL | Asset failure | HV | 2.00 | 190.0 | 0.002727 | 0.0000144 | No
18/09/2023 | 08:37 | MG02 | LONG RURAL | Planned |  | 19.00 | 248.0 | 0.033815 | 0.0001364 | No
18/09/2023 | 08:43 | NL234C | URBAN | Planned |  | 52.00 | 285.0 | 0.022849 | 0.0000802 | No
18/09/2023 | 09:00 | MG39 | SHORT RURAL | Asset failure | LV | 1.00 | 342.0 | 0.002406 | 0.0000070 | No
18/09/2023 | 09:03 | R24 | LONG RURAL | Planned |  | 31.00 | 286.3 | 0.063697 | 0.0002225 | No
18/09/2023 | 09:34 | MV52 | SHORT RURAL | Asset failure | LV | 7.00 | 243.0 | 0.011967 | 0.0000492 | No
18/09/2023 | 09:39 | MB63 | LONG RURAL | Planned |  | 6.00 | 67.0 | 0.002885 | 0.0000431 | No
18/09/2023 | 09:47 | CM21 | LONG RURAL | Planned |  | 6.00 | 183.0 | 0.007880 | 0.0000431 | No
18/09/2023 | 09:55 | GA11 | SHORT RURAL | Planned |  | 17.00 | 131.0 | 0.015668 | 0.0001196 | No
18/09/2023 | 10:47 | BM41 | SHORT RURAL | Asset failure | LV | 1.00 | 1,831.0 | 0.012882 | 0.0000070 | No
18/09/2023 | 11:03 | HH341E | URBAN | Asset failure | LV | 21.00 | 55.0 | 0.001781 | 0.0000324 | No
18/09/2023 | 11:04 | MI18 | LONG RURAL | Unknown | Unknown | 2.00 | 301.0 | 0.004320 | 0.0000144 | No
18/09/2023 | 11:07 | NL451D | URBAN | Third Party | Unauthorised access | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
18/09/2023 | 11:39 | NL234C | URBAN | Unknown | Unknown | 5.00 | 303.0 | 0.002336 | 0.0000077 | No
18/09/2023 | 11:45 | SM126E | URBAN | Planned |  | 1.00 | 3,667.0 | 0.005654 | 0.0000015 | No
18/09/2023 | 12:54 | GU32 | LONG RURAL | Planned |  | 29.00 | 9.0 | 0.001873 | 0.0002081 | No
18/09/2023 | 13:11 | AP139C | URBAN | Asset failure | LV | 21.00 | 11.0 | 0.000356 | 0.0000324 | No
18/09/2023 | 13:50 | CL10 | LONG RURAL | Unknown | Unknown | 85.00 | 176.7 | 0.107774 | 0.0006100 | No
18/09/2023 | 14:21 | BM33 | SHORT RURAL | Asset failure | LV | 1.00 | 183.0 | 0.001287 | 0.0000070 | No
18/09/2023 | 14:55 | SM126C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
18/09/2023 | 15:05 | AP365A | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
18/09/2023 | 16:19 | SM216A | URBAN | Asset failure | LV | 7.00 | 335.0 | 0.003615 | 0.0000108 | No
18/09/2023 | 16:20 | MT15 | LONG RURAL | Asset failure | LV | 2.00 | 143.0 | 0.002052 | 0.0000144 | No
18/09/2023 | 17:00 | HH130E | URBAN | Asset failure | LV | 39.00 | 154.0 | 0.009260 | 0.0000601 | No
18/09/2023 | 19:40 | HH409E | URBAN | Third Party | Other | 47.00 | 332.3 | 0.024081 | 0.0000725 | No
18/09/2023 | 20:27 | AP139C | URBAN | Third Party | Vehicle impact | 61.00 | 280.7 | 0.026395 | 0.0000940 | No
18/09/2023 | 22:10 | CBD366M | CBD | Planned |  | 3.00 | 272.0 | 0.117894 | 0.0004334 | No
19/09/2023 | 05:22 | NL234D | URBAN | Third Party | Unauthorised access | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
19/09/2023 | 07:03 | NU22 | LONG RURAL | Unknown | Unknown | 2.00 | 170.0 | 0.002440 | 0.0000144 | No
19/09/2023 | 07:32 | SM349H | URBAN | Asset failure | LV | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
19/09/2023 | 08:04 | MG39 | SHORT RURAL | Planned |  | 218.00 | 426.0 | 0.653344 | 0.0015337 | No
19/09/2023 | 08:26 | SA744D | URBAN | Overloads |  | 1.00 | 55.0 | 0.000085 | 0.0000015 | No
19/09/2023 | 09:07 | KI53 | LONG RURAL | Planned |  | 18.00 | 184.0 | 0.023768 | 0.0001292 | No
19/09/2023 | 09:13 | HH102B | URBAN | Planned |  | 113.00 | 303.4 | 0.052857 | 0.0001742 | No
19/09/2023 | 09:17 | CD24 | LONG RURAL | Planned |  | 8.00 | 257.0 | 0.014755 | 0.0000574 | No
19/09/2023 | 09:30 | MI28 | LONG RURAL | Planned |  | 18.00 | 145.0 | 0.018730 | 0.0001292 | No
19/09/2023 | 09:31 | NA61 | LONG RURAL | Planned |  | 34.00 | 155.0 | 0.037819 | 0.0002440 | No
19/09/2023 | 09:37 | R25 | LONG RURAL | Planned |  | 17.00 | 118.0 | 0.014396 | 0.0001220 | No
19/09/2023 | 09:43 | CM22 | LONG RURAL | Planned |  | 39.00 | 185.0 | 0.051777 | 0.0002799 | No
19/09/2023 | 09:50 | SD34405 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 86.0 | 0.000617 | 0.0000072 | No
19/09/2023 | 09:54 | SSD215 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 524.00 | 4.0 | 0.015042 | 0.0037604 | No
19/09/2023 | 09:54 | SSD215 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 20,326.00 | 4.0 | 0.572042 | 0.1430034 | No
19/09/2023 | 09:54 | SSD215 | URBAN | 5 - STPIS Exclusion (3.3)(a) |  | 2,156.00 | 4.0 | 0.013296 | 0.0033240 | No
19/09/2023 | 10:04 | ST12 | SHORT RURAL | Asset failure | LV | 10.00 | 950.0 | 0.066837 | 0.0000704 | No
19/09/2023 | 10:43 | AP146D | URBAN | Overloads |  | 1.00 | 378.0 | 0.000583 | 0.0000015 | No
19/09/2023 | 11:01 | SD34201 | LONG RURAL | Planned |  | 1.00 | 250.0 | 0.001794 | 0.0000072 | No
19/09/2023 | 12:44 | HH428A | URBAN | Unknown | Unknown | 3.33 | 259.0 | 0.001331 | 0.0000051 | No
19/09/2023 | 14:02 | NL234C | URBAN | Asset failure | LV | 23.00 | 21.0 | 0.000745 | 0.0000355 | No
19/09/2023 | 16:28 | HH522C | URBAN | Asset failure | LV | 11.33 | 95.0 | 0.001660 | 0.0000175 | No
19/09/2023 | 16:37 | NL111Q | URBAN | Asset failure | LV | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
19/09/2023 | 18:22 | EL260C | URBAN | Asset failure | LV | 73.00 | 41.0 | 0.004614 | 0.0001125 | No
19/09/2023 | 18:40 | HH341D | URBAN | Asset failure | LV | 1.00 | 243.0 | 0.000375 | 0.0000015 | No
19/09/2023 | 19:26 | SA20 | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
19/09/2023 | 20:38 | CL05 | LONG RURAL | Unknown | Unknown | 1.00 | 5.0 | 0.000036 | 0.0000072 | No
19/09/2023 | 21:24 | SSD239 | SHORT RURAL | Asset failure | Zone substation | 1,450.00 | 401.3 | 4.094219 | 0.0102015 | No
19/09/2023 | 21:33 | AP829F | URBAN | Planned |  | 5.00 | 310.0 | 0.002390 | 0.0000077 | No
19/09/2023 | 21:55 | HH177F | URBAN | Asset failure | HV | 71.00 | 506.7 | 0.055471 | 0.0001095 | No
19/09/2023 | 22:34 | SG12 | SHORT RURAL | Animal | Animal impact | 258.00 | 163.0 | 0.295871 | 0.0018152 | No
20/09/2023 | 00:59 | ST35 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 159.00 | 112.0 | 0.127796 | 0.0011410 | No
20/09/2023 | 00:59 | ST35 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 112.0 | 0.000788 | 0.0000070 | No
20/09/2023 | 04:02 | GA28 | LONG RURAL | Weather |  | 344.00 | 347.3 | 0.857370 | 0.0024687 | No
20/09/2023 | 06:11 | SA711C | URBAN | Asset failure | LV | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
20/09/2023 | 06:27 | EL16 | URBAN | Weather |  | 326.00 | 277.5 | 0.139496 | 0.0005026 | No
20/09/2023 | 07:07 | SG07 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 9.33 | 121.0 | 0.007945 | 0.0000657 | No
20/09/2023 | 07:10 | EL01P | URBAN | Asset failure | HV | 1,474.00 | 134.3 | 0.305289 | 0.0022725 | No
20/09/2023 | 07:25 | SA20 | URBAN | Asset failure | LV | 1.00 | 590.0 | 0.000910 | 0.0000015 | No
20/09/2023 | 07:47 | HH177A | URBAN | Unknown | Unknown | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
20/09/2023 | 08:02 | ME200A | URBAN | Asset failure | LV | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
20/09/2023 | 08:02 | MV64 | SHORT RURAL | Planned |  | 79.00 | 444.0 | 0.246777 | 0.0005558 | No
20/09/2023 | 08:35 | MG13 | SHORT RURAL | Planned |  | 7.00 | 368.0 | 0.018123 | 0.0000492 | No
20/09/2023 | 08:48 | MG17 | LONG RURAL | Planned |  | 203.00 | 317.8 | 0.463017 | 0.0014568 | No
20/09/2023 | 09:38 | VH23 | SHORT RURAL | Planned |  | 911.00 | 347.1 | 2.224770 | 0.0064093 | No
20/09/2023 | 09:38 | MB123 | LONG RURAL | Planned |  | 79.00 | 127.0 | 0.072000 | 0.0005669 | No
20/09/2023 | 09:51 | G28 | LONG RURAL | Planned |  | 40.00 | 285.0 | 0.081810 | 0.0002871 | No
20/09/2023 | 10:22 | NL234A | URBAN | Asset failure | LV | 1.00 | 214.0 | 0.000330 | 0.0000015 | No
20/09/2023 | 11:30 | SD49100 | LONG RURAL | Other |  | 1.00 | 301.0 | 0.002160 | 0.0000072 | No
20/09/2023 | 11:45 | WHY14 | URBAN | Overloads |  | 1.00 | 153.0 | 0.000236 | 0.0000015 | No
20/09/2023 | 13:03 | MG42 | SHORT RURAL | Asset failure | LV | 1.00 | 243.0 | 0.001710 | 0.0000070 | No
20/09/2023 | 13:27 | VH21 | SHORT RURAL | Unknown | Unknown | 1.00 | 99.0 | 0.000697 | 0.0000070 | No
20/09/2023 | 13:28 | EL01L | URBAN | Overloads |  | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
20/09/2023 | 13:38 | HH121B | URBAN | Unknown | Unknown | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
20/09/2023 | 14:00 | WHY01 | SHORT RURAL | Overloads |  | 1.00 | 69.0 | 0.000485 | 0.0000070 | No
20/09/2023 | 14:27 | SM172C | URBAN | Asset failure | LV | 33.33 | 178.0 | 0.009148 | 0.0000514 | No
20/09/2023 | 14:33 | M92 | LONG RURAL | Weather |  | 1.00 | 1,377.0 | 0.009882 | 0.0000072 | No
20/09/2023 | 14:39 | EL03 | URBAN | Vegetation | Grow-in - NSP responsibility | 3.00 | 353.0 | 0.001633 | 0.0000046 | No
20/09/2023 | 14:40 | BM52 | URBAN | Asset failure | LV | 1.00 | 282.0 | 0.000435 | 0.0000015 | No
20/09/2023 | 15:06 | NU22 | LONG RURAL | Unknown | Unknown | 4.00 | 149.0 | 0.004277 | 0.0000287 | No
20/09/2023 | 15:26 | ME131A | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
20/09/2023 | 15:28 | EL03 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 311.0 | 0.000479 | 0.0000015 | No
20/09/2023 | 17:28 | AP344B | URBAN | Weather |  | 37.00 | 78.0 | 0.004450 | 0.0000570 | No
20/09/2023 | 17:54 | HH177F | URBAN | Asset failure | LV | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
20/09/2023 | 18:47 | M11 | LONG RURAL | Unknown | Unknown | 74.00 | 282.0 | 0.149756 | 0.0005310 | No
20/09/2023 | 19:49 | HH177F | URBAN | Asset failure | LV | 1.00 | 20.0 | 0.000031 | 0.0000015 | No
20/09/2023 | 20:05 | AP529D | URBAN | Overloads |  | 1.00 | 198.0 | 0.000305 | 0.0000015 | No
20/09/2023 | 20:59 | AP214D | URBAN | Asset failure | LV | 65.00 | 89.0 | 0.008919 | 0.0001002 | No
20/09/2023 | 22:00 | SD36300 | LONG RURAL | Planned |  | 1,347.00 | 416.2 | 4.023409 | 0.0096665 | No
20/09/2023 | 22:24 | HH145B | URBAN | Unknown | Unknown | 43.00 | 97.0 | 0.006431 | 0.0000663 | No
20/09/2023 | 23:07 | SG06 | SHORT RURAL | Unknown | Unknown | 13.33 | 82.0 | 0.007692 | 0.0000938 | No
21/09/2023 | 02:00 | GA28 | LONG RURAL | Asset failure | HV | 361.00 | 463.4 | 1.200521 | 0.0025907 | No
21/09/2023 | 03:54 | MB81 | LONG RURAL | Unknown | Unknown | 390.00 | 170.3 | 0.476709 | 0.0027988 | No
21/09/2023 | 05:32 | CL11 | SHORT RURAL | Asset failure | LV | 2.00 | 695.0 | 0.009779 | 0.0000141 | No
21/09/2023 | 05:47 | R02 | LONG RURAL | Unknown | Unknown | 1.00 | 747.0 | 0.005361 | 0.0000072 | No
21/09/2023 | 05:55 | HH496G | URBAN | Asset failure | LV | 6.67 | 327.0 | 0.003361 | 0.0000103 | No
21/09/2023 | 06:55 | SG07 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 238.00 | 221.4 | 0.370742 | 0.0016744 | No
21/09/2023 | 07:55 | SA31 | URBAN | Asset failure | HV | 35.00 | 147.0 | 0.007932 | 0.0000540 | No
21/09/2023 | 08:08 | HH403D | URBAN | Asset failure | LV | 1.00 | 590.0 | 0.000910 | 0.0000015 | No
21/09/2023 | 08:10 | HH102B | URBAN | Asset failure | LV | 1.00 | 285.0 | 0.000439 | 0.0000015 | No
21/09/2023 | 08:12 | SD38100 | LONG RURAL | Unknown | Unknown | 9.67 | 358.0 | 0.024835 | 0.0000694 | No
21/09/2023 | 08:41 | CBD27F | CBD | Overloads |  | 1.00 | 140.0 | 0.020227 | 0.0001445 | No
21/09/2023 | 09:02 | NU02 | LONG RURAL | Planned |  | 78.00 | 432.0 | 0.241814 | 0.0005598 | No
21/09/2023 | 09:05 | CBD27L | CBD | Overloads |  | 2.00 | 120.0 | 0.034675 | 0.0002890 | No
21/09/2023 | 09:11 | HH130D | URBAN | Planned |  | 44.00 | 325.0 | 0.022047 | 0.0000678 | No
21/09/2023 | 09:13 | NA07 | LONG RURAL | Planned |  | 4.00 | 133.0 | 0.003818 | 0.0000287 | No
21/09/2023 | 09:20 | HH428D | URBAN | Planned |  | 291.00 | 292.0 | 0.131018 | 0.0004487 | No
21/09/2023 | 09:39 | ST13 | SHORT RURAL | Planned |  | 150.00 | 352.0 | 0.371474 | 0.0010553 | No
21/09/2023 | 09:46 | HH428F | URBAN | Planned |  | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
21/09/2023 | 09:51 | WK11 | SHORT RURAL | Planned |  | 3.00 | 157.0 | 0.003314 | 0.0000211 | No
21/09/2023 | 09:53 | ST11 | SHORT RURAL | Planned |  | 2.00 | 285.0 | 0.004010 | 0.0000141 | No
21/09/2023 | 09:56 | CL23 | LONG RURAL | Animal | Animal impact | 1.00 | 225.0 | 0.001615 | 0.0000072 | No
21/09/2023 | 09:56 | ME427E | URBAN | Planned |  | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
21/09/2023 | 10:08 | HH341G | URBAN | Asset failure | LV | 35.33 | 293.0 | 0.015961 | 0.0000545 | No
21/09/2023 | 10:11 | MI23 | LONG RURAL | Unknown | Unknown | 1.00 | 309.0 | 0.002217 | 0.0000072 | No
21/09/2023 | 10:12 | SA19 | URBAN | Planned |  | 88.00 | 271.4 | 0.036820 | 0.0001357 | No
21/09/2023 | 10:30 | ME427E | URBAN | Planned |  | 1.00 | 51.0 | 0.000079 | 0.0000015 | No
21/09/2023 | 11:18 | BM41 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 633.0 | 0.004453 | 0.0000070 | No
21/09/2023 | 11:30 | MG44 | URBAN | Asset failure | LV | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
21/09/2023 | 11:49 | BM41 | SHORT RURAL | Third Party | Dig-in | 3.00 | 811.3 | 0.017124 | 0.0000211 | No
21/09/2023 | 12:01 | CBD27L | CBD | Asset failure | LV | 2.00 | 938.0 | 0.271040 | 0.0002890 | No
21/09/2023 | 12:05 | HH496G | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
21/09/2023 | 12:30 | BT15 | LONG RURAL | Network business | Switching and protection error | 113.00 | 217.9 | 0.176681 | 0.0008109 | No
21/09/2023 | 13:08 | WK11 | SHORT RURAL | Planned |  | 3.00 | 8.0 | 0.000169 | 0.0000211 | No
21/09/2023 | 14:07 | HH341K | URBAN | Asset failure | LV | 15.67 | 384.0 | 0.009275 | 0.0000242 | No
21/09/2023 | 14:48 | HH386B | URBAN | Unknown | Unknown | 1.00 | 650.0 | 0.001002 | 0.0000015 | No
21/09/2023 | 15:25 | MV63 | SHORT RURAL | Asset failure | LV | 1.00 | 218.0 | 0.001534 | 0.0000070 | No
21/09/2023 | 15:31 | MT21 | LONG RURAL | Asset failure | LV | 17.00 | 162.0 | 0.019764 | 0.0001220 | No
21/09/2023 | 16:42 | BS0270 | URBAN | Planned |  | 1.00 | 5,551.0 | 0.008558 | 0.0000015 | No
21/09/2023 | 16:55 | HH428E | URBAN | Asset failure | LV | 1.00 | 344.0 | 0.000530 | 0.0000015 | No
21/09/2023 | 17:08 | NL451C | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | No
21/09/2023 | 17:27 | LC01 | SHORT RURAL | Asset failure | LV | 1.00 | 230.0 | 0.001618 | 0.0000070 | No
21/09/2023 | 18:58 | SA744D | URBAN | Overloads |  | 1.00 | 331.0 | 0.000510 | 0.0000015 | No
21/09/2023 | 21:53 | AP227A | URBAN | Asset failure | LV | 79.00 | 254.0 | 0.030937 | 0.0001218 | No
21/09/2023 | 23:15 | HH341K | URBAN | Asset failure | LV | 21.00 | 92.0 | 0.002979 | 0.0000324 | No
22/09/2023 | 00:18 | HH121G | URBAN | Weather |  | 157.00 | 36.0 | 0.008723 | 0.0002421 | No
22/09/2023 | 07:28 | NL210E | URBAN | Asset failure | LV | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
22/09/2023 | 08:24 | KA04 | LONG RURAL | Planned |  | 1.00 | 13.0 | 0.000093 | 0.0000072 | No
22/09/2023 | 08:25 | NL511A | URBAN | Planned |  | 69.00 | 299.0 | 0.031808 | 0.0001064 | No
22/09/2023 | 08:31 | CV22 | LONG RURAL | Planned |  | 15.00 | 398.0 | 0.042843 | 0.0001076 | No
22/09/2023 | 08:41 | CBD366V | CBD | Asset failure | LV | 1.00 | 683.0 | 0.098678 | 0.0001445 | No
22/09/2023 | 08:45 | MG18 | LONG RURAL | Planned |  | 10.00 | 83.0 | 0.005956 | 0.0000718 | No
22/09/2023 | 08:54 | NL451C | URBAN | Planned |  | 107.00 | 222.0 | 0.036623 | 0.0001650 | No
22/09/2023 | 08:57 | NU20 | LONG RURAL | Planned |  | 159.00 | 195.6 | 0.223198 | 0.0011410 | No
22/09/2023 | 09:04 | MTB14 | SHORT RURAL | Planned |  | 16.00 | 240.0 | 0.027016 | 0.0001126 | No
22/09/2023 | 09:05 | NA12 | LONG RURAL | Planned |  | 9.00 | 136.0 | 0.008784 | 0.0000646 | No
22/09/2023 | 09:18 | KI32 | SHORT RURAL | Planned |  | 66.00 | 189.0 | 0.087761 | 0.0004643 | No
22/09/2023 | 09:20 | CN42 | LONG RURAL | Planned |  | 31.00 | 148.0 | 0.032925 | 0.0002225 | No
22/09/2023 | 09:24 | NU19 | LONG RURAL | Planned |  | 25.00 | 156.3 | 0.028045 | 0.0001794 | No
22/09/2023 | 09:39 | YK05 | LONG RURAL | Planned |  | 40.00 | 143.0 | 0.041049 | 0.0002871 | No
22/09/2023 | 09:54 | NA27 | LONG RURAL | Planned |  | 46.00 | 254.0 | 0.083848 | 0.0003301 | No
22/09/2023 | 10:12 | HH121A | URBAN | Planned |  | 298.00 | 238.3 | 0.109471 | 0.0004594 | No
22/09/2023 | 10:16 | CBD27L | CBD | Asset failure | LV | 22.00 | 589.0 | 1.872138 | 0.0031785 | No
22/09/2023 | 10:16 | HH341E | URBAN | Asset failure | LV | 34.00 | 59.0 | 0.003093 | 0.0000524 | No
22/09/2023 | 10:25 | MV33 | SHORT RURAL | Planned |  | 1.00 | 230.0 | 0.001618 | 0.0000070 | No
22/09/2023 | 10:25 | HH409C | URBAN | Planned |  | 1.00 | 64.0 | 0.000099 | 0.0000015 | No
22/09/2023 | 10:33 | CV16 | LONG RURAL | Planned |  | 36.00 | 228.0 | 0.058903 | 0.0002583 | No
22/09/2023 | 10:37 | SM126E | URBAN | Asset failure | LV | 12.67 | 101.0 | 0.001972 | 0.0000195 | No
22/09/2023 | 11:04 | BU09 | LONG RURAL | Planned |  | 1.00 | 24.0 | 0.000172 | 0.0000072 | No
22/09/2023 | 11:14 | MV63 | SHORT RURAL | Asset failure | LV | 1.00 | 116.0 | 0.000816 | 0.0000070 | No
22/09/2023 | 11:52 | BU09 | LONG RURAL | Planned |  | 1.00 | 47.0 | 0.000337 | 0.0000072 | No
22/09/2023 | 12:03 | NL511A | URBAN | Unknown | Unknown | 1.00 | 74.0 | 0.000114 | 0.0000015 | No
22/09/2023 | 12:56 | MV62 | SHORT RURAL | Asset failure | LV | 1.00 | 484.0 | 0.003405 | 0.0000070 | No
22/09/2023 | 13:16 | SD32200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 294.0 | 0.002110 | 0.0000072 | No
22/09/2023 | 14:29 | EL15 | URBAN | Asset failure | LV | 2.00 | 239.0 | 0.000737 | 0.0000031 | No
22/09/2023 | 15:35 | MG17 | LONG RURAL | Asset failure | LV | 1.00 | 181.0 | 0.001299 | 0.0000072 | No
22/09/2023 | 16:09 | SM411D | URBAN | Third Party | Vehicle impact | 39.00 | 693.0 | 0.041669 | 0.0000601 | No
22/09/2023 | 16:12 | W08 | SHORT RURAL | Asset failure | HV | 5.00 | 55.0 | 0.001935 | 0.0000352 | No
22/09/2023 | 17:16 | NL451A | URBAN | Asset failure | LV | 1.00 | 1,681.0 | 0.002592 | 0.0000015 | No
22/09/2023 | 17:35 | SM411F | URBAN | Asset failure | LV | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
22/09/2023 | 18:54 | CN72 | LONG RURAL | Asset failure | HV | 3.00 | 88.7 | 0.001909 | 0.0000215 | No
22/09/2023 | 19:42 | ME200F | URBAN | Asset failure | LV | 18.00 | 45.0 | 0.001249 | 0.0000278 | No
22/09/2023 | 23:08 | HH130A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 69.00 | 319.7 | 0.034013 | 0.0001064 | No
22/09/2023 | 23:29 | CN43 | LONG RURAL | Animal | Animal impact | 2.00 | 797.0 | 0.011439 | 0.0000144 | No
23/09/2023 | 08:11 | R08 | LONG RURAL | Unknown | Unknown | 121.00 | 343.3 | 0.298076 | 0.0008683 | No
23/09/2023 | 08:20 | SM349H | URBAN | Asset failure | LV | 1.00 | 390.0 | 0.000601 | 0.0000015 | No
23/09/2023 | 08:31 | WK42 | SHORT RURAL | Planned |  | 36.00 | 151.0 | 0.038245 | 0.0002533 | No
23/09/2023 | 08:40 | SD33100 | LONG RURAL | Planned |  | 594.00 | 314.9 | 1.342368 | 0.0042627 | No
23/09/2023 | 09:28 | CL09 | LONG RURAL | Animal | Animal impact | 1.00 | 487.0 | 0.003495 | 0.0000072 | No
23/09/2023 | 09:38 | BT02 | LONG RURAL | Planned |  | 3.00 | 157.0 | 0.003380 | 0.0000215 | No
23/09/2023 | 10:19 | BT03 | LONG RURAL | Planned |  | 5.00 | 114.0 | 0.004091 | 0.0000359 | No
23/09/2023 | 10:44 | W24 | LONG RURAL | Unknown | Unknown | 69.00 | 338.3 | 0.167531 | 0.0004952 | No
23/09/2023 | 10:46 | HH177C | URBAN | Asset failure | LV | 26.00 | 175.0 | 0.007015 | 0.0000401 | No
23/09/2023 | 11:19 | M91 | LONG RURAL | Unknown | Unknown | 356.00 | 179.0 | 0.457304 | 0.0025548 | No
23/09/2023 | 11:38 | KI31 | SHORT RURAL | Asset failure | LV | 19.00 | 129.0 | 0.017244 | 0.0001337 | No
23/09/2023 | 12:12 | BM51 | URBAN | Asset failure | LV | 30.00 | 15.0 | 0.000694 | 0.0000463 | No
23/09/2023 | 12:16 | HH130B | URBAN | Unknown | Unknown | 154.67 | 52.0 | 0.012400 | 0.0002385 | No
23/09/2023 | 13:10 | BT03 | LONG RURAL | Planned |  | 3.00 | 147.0 | 0.003165 | 0.0000215 | No
23/09/2023 | 13:11 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 400.0 | 0.002814 | 0.0000070 | No
23/09/2023 | 13:30 | HH130B | URBAN | Asset failure | HV | 232.00 | 301.5 | 0.107855 | 0.0003577 | No
23/09/2023 | 13:39 | MG11 | SHORT RURAL | Unknown | Unknown | 1.00 | 250.0 | 0.001759 | 0.0000070 | No
23/09/2023 | 16:26 | SD39100 | LONG RURAL | Animal | Animal impact | 786.00 | 136.2 | 0.768276 | 0.0056406 | No
24/09/2023 | 08:18 | PL803C | URBAN | Planned |  | 79.00 | 373.8 | 0.045526 | 0.0001218 | No
24/09/2023 | 08:26 | MG02 | LONG RURAL | Asset failure | HV | 6.00 | 236.2 | 0.010169 | 0.0000431 | No
24/09/2023 | 08:26 | HH341E | URBAN | Planned |  | 298.00 | 288.1 | 0.132344 | 0.0004594 | No
24/09/2023 | 08:38 | SD34201 | SHORT RURAL | Planned |  | 4.00 | 318.0 | 0.008949 | 0.0000281 | No
24/09/2023 | 09:07 | EL23 | URBAN | Planned |  | 89.00 | 401.5 | 0.055087 | 0.0001372 | No
24/09/2023 | 09:11 | HH177E | URBAN | Asset failure | LV | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
24/09/2023 | 09:32 | W01 | LONG RURAL | Planned |  | 34.00 | 415.0 | 0.101258 | 0.0002440 | No
24/09/2023 | 09:37 | NL234A | URBAN | Asset failure | LV | 1.00 | 257.0 | 0.000396 | 0.0000015 | No
24/09/2023 | 11:43 | HH341K | URBAN | Planned |  | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
24/09/2023 | 13:23 | SA744C | URBAN | Other |  | 141.00 | 9.0 | 0.001956 | 0.0002174 | No
24/09/2023 | 13:32 | ME427A | URBAN | Asset failure | LV | 1.00 | 458.0 | 0.000706 | 0.0000015 | No
24/09/2023 | 14:19 | AP146C | URBAN | Asset failure | LV | 1.00 | 258.0 | 0.000398 | 0.0000015 | No
24/09/2023 | 18:32 | NL115F | URBAN | Asset failure | LV | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
24/09/2023 | 18:54 | HH522B | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
25/09/2023 | 00:25 | NU21 | LONG RURAL | Asset failure | LV | 16.00 | 56.0 | 0.006430 | 0.0001148 | No
25/09/2023 | 02:16 | HH121D | URBAN | Unknown | Unknown | 16.00 | 417.0 | 0.010287 | 0.0000247 | No
25/09/2023 | 06:17 | CD26 | LONG RURAL | Unknown | Unknown | 18.00 | 274.0 | 0.035394 | 0.0001292 | No
25/09/2023 | 09:04 | AP355C | URBAN | Planned |  | 102.00 | 328.0 | 0.051581 | 0.0001573 | No
25/09/2023 | 09:06 | VH12 | SHORT RURAL | Planned |  | 63.00 | 423.0 | 0.187489 | 0.0004432 | No
25/09/2023 | 09:12 | CM27 | LONG RURAL | Planned |  | 29.00 | 330.4 | 0.068756 | 0.0002081 | No
25/09/2023 | 09:16 | MB14 | SHORT RURAL | Planned |  | 110.00 | 313.0 | 0.242232 | 0.0007739 | No
25/09/2023 | 09:17 | BM15 | SHORT RURAL | Planned |  | 1.00 | 115.0 | 0.000809 | 0.0000070 | No
25/09/2023 | 09:18 | HH145D | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
25/09/2023 | 09:46 | BT10 | LONG RURAL | Planned |  | 9.00 | 53.0 | 0.003423 | 0.0000646 | No
25/09/2023 | 09:54 | BS0396 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 15.0 | 0.000106 | 0.0000070 | No
25/09/2023 | 09:55 | EL19 | SHORT RURAL | Third Party | Vehicle impact | 2.00 | 55.0 | 0.000774 | 0.0000141 | No
25/09/2023 | 09:55 | EL19 | URBAN | Third Party | Vehicle impact | 422.00 | 74.8 | 0.048676 | 0.0006506 | No
25/09/2023 | 10:00 | MI31 | LONG RURAL | Planned |  | 46.00 | 279.0 | 0.092101 | 0.0003301 | No
25/09/2023 | 10:26 | EL10 | URBAN | Asset failure | LV | 11.00 | 590.0 | 0.010006 | 0.0000170 | No
25/09/2023 | 10:36 | CN25 | LONG RURAL | Asset failure | HV | 1.00 | 8.0 | 0.000057 | 0.0000072 | No
25/09/2023 | 10:50 | MV13 | SHORT RURAL | Planned |  | 10.00 | 247.0 | 0.017378 | 0.0000704 | No
25/09/2023 | 10:59 | SM126A | URBAN | Asset failure | LV | 1.00 | 156.0 | 0.000241 | 0.0000015 | No
25/09/2023 | 11:15 | HH121F | URBAN | Planned |  | 84.00 | 129.0 | 0.016706 | 0.0001295 | No
25/09/2023 | 11:35 | SD34102 | SHORT RURAL | Planned |  | 17.00 | 140.0 | 0.016744 | 0.0001196 | No
25/09/2023 | 13:43 | HH429C | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
25/09/2023 | 14:07 | HH341D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
25/09/2023 | 14:14 | MI17 | LONG RURAL | Asset failure | HV | 6.00 | 33.0 | 0.001421 | 0.0000431 | No
25/09/2023 | 14:41 | G16 | LONG RURAL | Asset failure | HV | 46.00 | 105.2 | 0.034719 | 0.0003301 | No
25/09/2023 | 14:46 | NL234E | URBAN | Other |  | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
25/09/2023 | 15:27 | HH145B | URBAN | Other |  | 2.00 | 125.0 | 0.000385 | 0.0000031 | No
25/09/2023 | 16:02 | MTB22 | SHORT RURAL | Asset failure | LV | 1.00 | 344.0 | 0.002420 | 0.0000070 | No
25/09/2023 | 17:14 | MV52 | SHORT RURAL | Asset failure | LV | 2.00 | 557.0 | 0.007838 | 0.0000141 | No
25/09/2023 | 17:30 | BT15 | LONG RURAL | Unknown | Unknown | 331.00 | 123.0 | 0.292098 | 0.0023754 | No
25/09/2023 | 17:48 | SD49100 | LONG RURAL | Asset failure | Subtransmission | 2.00 | 202.0 | 0.002899 | 0.0000144 | No
25/09/2023 | 18:46 | BM34 | SHORT RURAL | Unknown | Unknown | 14.00 | 97.0 | 0.009554 | 0.0000985 | No
25/09/2023 | 21:10 | CBD103C | URBAN | Network business | Switching and protection error | 65.00 | 63.1 | 0.006326 | 0.0001002 | No
25/09/2023 | 22:05 | HH386D | URBAN | Unknown | Unknown | 98.00 | 77.0 | 0.011634 | 0.0001511 | No
25/09/2023 | 22:10 | HH386D | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
26/09/2023 | 02:28 | HH107C | URBAN | Unknown | Unknown | 659.00 | 102.0 | 0.103634 | 0.0010160 | No
26/09/2023 | 06:18 | SD35200 | LONG RURAL | Asset failure | Subtransmission | 3,214.00 | 149.8 | 3.454735 | 0.0230647 | No
26/09/2023 | 06:18 | SD35200 | URBAN | Asset failure | Subtransmission | 5.00 | 173.0 | 0.001334 | 0.0000077 | No
26/09/2023 | 06:54 | BM54 | SHORT RURAL | Animal | Animal impact | 23.33 | 217.0 | 0.035623 | 0.0001642 | No
26/09/2023 | 07:20 | R08 | LONG RURAL | Unknown | Unknown | 41.00 | 276.6 | 0.081394 | 0.0002942 | No
26/09/2023 | 08:14 | LX44 | URBAN | Planned |  | 1.00 | 334.0 | 0.000515 | 0.0000015 | No
26/09/2023 | 08:26 | AP529C | URBAN | Asset failure | LV | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
26/09/2023 | 08:48 | MG51 | LONG RURAL | Planned |  | 16.00 | 182.0 | 0.020897 | 0.0001148 | No
26/09/2023 | 09:15 | WK61 | SHORT RURAL | Planned |  | 91.00 | 305.1 | 0.195319 | 0.0006402 | No
26/09/2023 | 09:24 | EL23 | URBAN | Planned |  | 16.00 | 331.5 | 0.008177 | 0.0000247 | No
26/09/2023 | 09:31 | MTB81 | SHORT RURAL | Planned |  | 656.00 | 267.0 | 1.232280 | 0.0046153 | No
26/09/2023 | 09:40 | SM411C | URBAN | Animal | Animal impact | 6.00 | 115.0 | 0.001064 | 0.0000093 | No
26/09/2023 | 09:40 | SG02 | URBAN | Planned |  | 176.00 | 293.0 | 0.079499 | 0.0002713 | No
26/09/2023 | 09:44 | GA11 | SHORT RURAL | Planned |  | 17.00 | 179.0 | 0.021409 | 0.0001196 | No
26/09/2023 | 09:45 | SM216C | URBAN | Vegetation | Grow-in - NSP responsibility | 13.33 | 77.6 | 0.001596 | 0.0000206 | No
26/09/2023 | 11:27 | G18 | LONG RURAL | Planned |  | 26.00 | 62.0 | 0.011568 | 0.0001866 | No
26/09/2023 | 12:05 | SA711C | URBAN | Asset failure | LV | 1.00 | 263.0 | 0.000405 | 0.0000015 | No
26/09/2023 | 12:12 | HH386D | URBAN | Network business | Switching and protection error | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
26/09/2023 | 14:14 | VH71 | SHORT RURAL | Overloads |  | 1.00 | 139.0 | 0.000978 | 0.0000070 | No
26/09/2023 | 15:19 | EL14 | URBAN | Overloads |  | 1.00 | 56.0 | 0.000086 | 0.0000015 | No
26/09/2023 | 15:30 | G15 | LONG RURAL | Planned |  | 12.00 | 65.0 | 0.005598 | 0.0000861 | No
26/09/2023 | 16:41 | HH429C | URBAN | Asset failure | LV | 84.00 | 34.0 | 0.004403 | 0.0001295 | No
26/09/2023 | 17:30 | GU41 | LONG RURAL | Asset failure | HV | 1.00 | 160.0 | 0.001148 | 0.0000072 | No
26/09/2023 | 17:38 | G18 | LONG RURAL | Asset failure | LV | 1.00 | 106.0 | 0.000761 | 0.0000072 | No
26/09/2023 | 18:00 | EL10 | URBAN | Asset failure | LV | 1.00 | 479.0 | 0.000739 | 0.0000015 | No
26/09/2023 | 18:16 | HH145B | URBAN | Asset failure | HV | 2,999.00 | 33.5 | 0.154673 | 0.0046237 | No
26/09/2023 | 18:46 | NL21 | URBAN | Asset failure | HV | 263.00 | 267.0 | 0.108263 | 0.0004055 | No
26/09/2023 | 19:46 | LX21 | SHORT RURAL | Unknown | Unknown | 5.00 | 175.2 | 0.006163 | 0.0000352 | No
27/09/2023 | 01:02 | SD49200 | LONG RURAL | Planned |  | 2,002.00 | 103.6 | 1.488873 | 0.0143670 | No
27/09/2023 | 06:50 | HH429B | URBAN | Asset failure | LV | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
27/09/2023 | 07:18 | VH51 | SHORT RURAL | Unknown | Unknown | 102.00 | 237.0 | 0.170076 | 0.0007176 | No
27/09/2023 | 07:32 | SD39300 | LONG RURAL | Asset failure | Subtransmission | 762.00 | 107.3 | 0.586844 | 0.0054684 | No
27/09/2023 | 08:06 | HH428A | URBAN | Unknown | Unknown | 25.33 | 187.0 | 0.007304 | 0.0000391 | No
27/09/2023 | 08:09 | PL04 | URBAN | Planned |  | 68.00 | 412.0 | 0.043194 | 0.0001048 | No
27/09/2023 | 08:31 | LX31 | SHORT RURAL | Planned |  | 3.00 | 503.7 | 0.010631 | 0.0000211 | No
27/09/2023 | 08:45 | G31 | LONG RURAL | Unknown | Unknown | 59.00 | 364.3 | 0.154255 | 0.0004234 | No
27/09/2023 | 08:46 | BM41 | SHORT RURAL | Planned |  | 2.00 | 396.0 | 0.005572 | 0.0000141 | No
27/09/2023 | 08:54 | HH496A | URBAN | Unknown | Unknown | 593.00 | 198.6 | 0.181532 | 0.0009143 | No
27/09/2023 | 09:10 | VH71 | SHORT RURAL | Planned |  | 347.00 | 379.0 | 0.925280 | 0.0024413 | No
27/09/2023 | 09:10 | SB23 | LONG RURAL | Planned |  | 54.00 | 153.2 | 0.059384 | 0.0003875 | No
27/09/2023 | 09:22 | SD40800 | LONG RURAL | Planned |  | 978.00 | 16.0 | 0.112295 | 0.0070185 | No
27/09/2023 | 09:58 | BM15 | SHORT RURAL | Asset failure | LV | 8.00 | 170.0 | 0.009568 | 0.0000563 | No
27/09/2023 | 10:19 | ST11 | SHORT RURAL | Planned |  | 17.00 | 301.0 | 0.036001 | 0.0001196 | No
27/09/2023 | 10:24 | GA28 | LONG RURAL | Planned |  | 2.00 | 234.0 | 0.003359 | 0.0000144 | No
27/09/2023 | 10:49 | NA51 | LONG RURAL | Planned |  | 1.00 | 338.0 | 0.002426 | 0.0000072 | No
27/09/2023 | 10:57 | CV28 | LONG RURAL | Planned |  | 80.00 | 195.0 | 0.111951 | 0.0005741 | No
27/09/2023 | 11:04 | AP132A | URBAN | Asset failure | LV | 1.00 | 412.0 | 0.000635 | 0.0000015 | No
27/09/2023 | 11:41 | YK14 | LONG RURAL | Planned |  | 14.00 | 183.0 | 0.018386 | 0.0001005 | No
27/09/2023 | 12:39 | MV53 | SHORT RURAL | Asset failure | LV | 2.33 | 40.0 | 0.000657 | 0.0000164 | No
27/09/2023 | 13:37 | NL210A | URBAN | Asset failure | LV | 1.00 | 268.0 | 0.000413 | 0.0000015 | No
27/09/2023 | 14:27 | HH145B | URBAN | Asset failure | HV | 593.00 | 130.4 | 0.119239 | 0.0009143 | No
27/09/2023 | 15:39 | NA04 | LONG RURAL | Planned |  | 118.00 | 5.0 | 0.004234 | 0.0008468 | No
27/09/2023 | 16:35 | LM13 | LONG RURAL | Weather |  | 23.00 | 56.0 | 0.009243 | 0.0001651 | No
27/09/2023 | 16:43 | NA04 | LONG RURAL | Asset failure | HV | 118.33 | 24.0 | 0.020381 | 0.0008492 | No
27/09/2023 | 16:46 | LX42 | SHORT RURAL | Asset failure | LV | 3.00 | 161.0 | 0.003398 | 0.0000211 | No
27/09/2023 | 17:06 | KI16 | LONG RURAL | Asset failure | LV | 1.00 | 1,039.0 | 0.007456 | 0.0000072 | No
27/09/2023 | 17:34 | AP529C | URBAN | Asset failure | LV | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
27/09/2023 | 18:40 | NL115B | URBAN | Asset failure | LV | 1.00 | 268.0 | 0.000413 | 0.0000015 | No
27/09/2023 | 18:47 | PL803A | URBAN | Asset failure | LV | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
27/09/2023 | 19:31 | EL01N | URBAN | Asset failure | LV | 1.00 | 34.0 | 0.000052 | 0.0000015 | No
27/09/2023 | 21:46 | AP829F | URBAN | Planned |  | 43.00 | 422.2 | 0.027992 | 0.0000663 | No
27/09/2023 | 22:33 | HH496A | URBAN | Unknown | Unknown | 1.00 | 1,012.0 | 0.001560 | 0.0000015 | No
27/09/2023 | 23:00 | PA10 | LONG RURAL | Unknown | Unknown | 1.00 | 200.0 | 0.001435 | 0.0000072 | No
28/09/2023 | 02:46 | KA01 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 313.00 | 126.0 | 0.277466 | 0.0022021 | No
28/09/2023 | 08:11 | KI32 | SHORT RURAL | Planned |  | 26.00 | 360.0 | 0.065852 | 0.0001829 | No
28/09/2023 | 08:26 | KA10 | LONG RURAL | Planned |  | 10.00 | 63.0 | 0.004521 | 0.0000718 | No
28/09/2023 | 08:53 | HH341E | URBAN | Asset failure | LV | 46.00 | 63.0 | 0.004468 | 0.0000709 | No
28/09/2023 | 09:02 | WK31 | SHORT RURAL | Planned |  | 11.00 | 339.1 | 0.026242 | 0.0000774 | No
28/09/2023 | 09:06 | VH45 | SHORT RURAL | Planned |  | 1,338.00 | 334.5 | 3.148790 | 0.0094135 | No
28/09/2023 | 09:14 | SD49100 | LONG RURAL | Planned |  | 1.00 | 194.0 | 0.001392 | 0.0000072 | No
28/09/2023 | 09:17 | R28 | LONG RURAL | Planned |  | 2.00 | 43.0 | 0.000617 | 0.0000144 | No
28/09/2023 | 09:42 | CV25 | LONG RURAL | Planned |  | 1.00 | 193.0 | 0.001385 | 0.0000072 | No
28/09/2023 | 09:43 | PL34 | LONG RURAL | Planned |  | 60.00 | 241.6 | 0.104028 | 0.0004306 | No
28/09/2023 | 09:43 | VH12 | SHORT RURAL | Other |  | 65.00 | 324.0 | 0.148167 | 0.0004573 | No
28/09/2023 | 09:46 | WK81 | SHORT RURAL | Planned |  | 4.00 | 187.0 | 0.005263 | 0.0000281 | No
28/09/2023 | 09:55 | EL01N | URBAN | Asset failure | LV | 15.00 | 251.0 | 0.005805 | 0.0000231 | No
28/09/2023 | 10:12 | EL01N | URBAN | Planned |  | 85.00 | 125.0 | 0.016381 | 0.0001310 | No
28/09/2023 | 10:27 | SM126B | URBAN | Planned |  | 44.00 | 145.4 | 0.009864 | 0.0000678 | No
28/09/2023 | 10:37 | EL01R | URBAN | Network business | Switching and protection error | 1.00 | 199.0 | 0.000307 | 0.0000015 | No
28/09/2023 | 10:53 | W24 | LONG RURAL | Planned |  | 20.00 | 66.0 | 0.009473 | 0.0001435 | No
28/09/2023 | 11:37 | CD26 | LONG RURAL | Animal | Animal impact | 18.00 | 182.0 | 0.023510 | 0.0001292 | No
28/09/2023 | 12:37 | SD39400 | SHORT RURAL | Unknown | Unknown | 6.00 | 292.0 | 0.012326 | 0.0000422 | No
28/09/2023 | 13:35 | NL451C | URBAN | Asset failure | LV | 55.00 | 83.0 | 0.007038 | 0.0000848 | No
28/09/2023 | 14:07 | HH522B | URBAN | Overloads |  | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
28/09/2023 | 15:05 | NL111Q | URBAN | Asset failure | LV | 1.00 | 377.0 | 0.000581 | 0.0000015 | No
28/09/2023 | 15:19 | VH12 | SHORT RURAL | Asset failure | LV | 65.00 | 7.0 | 0.003201 | 0.0004573 | No
28/09/2023 | 16:12 | HH177B | URBAN | Asset failure | LV | 14.00 | 269.0 | 0.005806 | 0.0000216 | No
28/09/2023 | 16:34 | HH107C | URBAN | Overloads |  | 1.00 | 87.0 | 0.000134 | 0.0000015 | No
28/09/2023 | 17:01 | AP425C | URBAN | Asset failure | LV | 75.00 | 78.0 | 0.009019 | 0.0001156 | No
28/09/2023 | 18:00 | NA04 | LONG RURAL | Asset failure | HV | 16.00 | 500.3 | 0.057439 | 0.0001148 | No
28/09/2023 | 18:20 | NL111B | URBAN | Third Party | Dig-in | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
28/09/2023 | 18:59 | WK21 | SHORT RURAL | Unknown | Unknown | 13.00 | 153.0 | 0.013994 | 0.0000915 | No
28/09/2023 | 21:17 | HH177B | URBAN | Asset failure | LV | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
28/09/2023 | 21:43 | SA520D | URBAN | Asset failure | LV | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
29/09/2023 | 01:40 | HH341E | URBAN | Asset failure | LV | 47.00 | 45.0 | 0.003261 | 0.0000725 | No
29/09/2023 | 06:34 | CD26 | LONG RURAL | Unknown | Unknown | 18.00 | 182.0 | 0.023510 | 0.0001292 | No
29/09/2023 | 06:54 | MI26 | LONG RURAL | Unknown | Unknown | 76.00 | 853.6 | 0.465543 | 0.0005454 | No
29/09/2023 | 07:11 | SM137B | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
29/09/2023 | 07:12 | VH14 | SHORT RURAL | Asset failure | LV | 1.00 | 169.0 | 0.001189 | 0.0000070 | No
29/09/2023 | 07:12 | BM33 | SHORT RURAL | Asset failure | LV | 1.33 | 636.0 | 0.005966 | 0.0000094 | No
29/09/2023 | 08:20 | BT26 | LONG RURAL | Asset failure | LV | 1.00 | 300.0 | 0.002153 | 0.0000072 | No
29/09/2023 | 08:30 | EL10 | URBAN | Asset failure | LV | 1.00 | 343.0 | 0.000529 | 0.0000015 | No
29/09/2023 | 08:30 | CBD103C | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
29/09/2023 | 08:42 | KA07 | LONG RURAL | Planned |  | 1.00 | 142.0 | 0.001019 | 0.0000072 | No
29/09/2023 | 08:49 | MTB32 | LONG RURAL | Planned |  | 15.00 | 322.0 | 0.034662 | 0.0001076 | No
29/09/2023 | 08:50 | CL26 | LONG RURAL | Planned |  | 40.00 | 261.0 | 0.074921 | 0.0002871 | No
29/09/2023 | 08:51 | MTB14 | SHORT RURAL | Planned |  | 447.00 | 307.9 | 0.968266 | 0.0031449 | No
29/09/2023 | 09:07 | GA15 | SHORT RURAL | Planned |  | 594.00 | 209.7 | 0.876411 | 0.0041791 | No
29/09/2023 | 09:08 | NL760B | URBAN | Overloads |  | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
29/09/2023 | 09:24 | MB13 | SHORT RURAL | Planned |  | 120.00 | 84.0 | 0.070918 | 0.0008443 | No
29/09/2023 | 09:25 | WK65 | SHORT RURAL | Planned |  | 81.00 | 79.0 | 0.045020 | 0.0005699 | No
29/09/2023 | 09:45 | PA26 | LONG RURAL | Planned |  | 3.00 | 30.0 | 0.000646 | 0.0000215 | No
29/09/2023 | 10:19 | CV32 | LONG RURAL | Planned |  | 8.00 | 127.0 | 0.007291 | 0.0000574 | No
29/09/2023 | 10:44 | G41 | LONG RURAL | Planned |  | 4.00 | 91.0 | 0.002612 | 0.0000287 | No
29/09/2023 | 10:57 | PL15 | LONG RURAL | Animal | Animal impact | 7.00 | 166.0 | 0.008339 | 0.0000502 | No
29/09/2023 | 11:22 | MV15 | SHORT RURAL | Planned |  | 2.00 | 137.0 | 0.001928 | 0.0000141 | No
29/09/2023 | 11:49 | BM55 | SHORT RURAL | Unknown | Unknown | 50.67 | 85.0 | 0.030300 | 0.0003565 | No
29/09/2023 | 14:05 | MT08 | LONG RURAL | Asset failure | LV | 1.00 | 209.0 | 0.001500 | 0.0000072 | No
29/09/2023 | 15:14 | VH72 | SHORT RURAL | Asset failure | LV | 2.00 | 134.0 | 0.001886 | 0.0000141 | No
29/09/2023 | 15:42 | BM11 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 7.00 | 192.0 | 0.009456 | 0.0000492 | No
29/09/2023 | 17:31 | BU02 | LONG RURAL | Asset failure | LV | 1.00 | 1,136.0 | 0.008152 | 0.0000072 | No
29/09/2023 | 19:02 | SM216A | URBAN | Overloads |  | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
29/09/2023 | 19:39 | NL210F | URBAN | Animal | Animal impact | 44.00 | 19.0 | 0.001289 | 0.0000678 | No
29/09/2023 | 22:38 | SM374A | URBAN | Asset failure | LV | 69.00 | 137.0 | 0.014574 | 0.0001064 | No
29/09/2023 | 22:51 | SA11 | URBAN | Overloads |  | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
29/09/2023 | 23:03 | SM349B | URBAN | Third Party | Vehicle impact | 2.00 | 476.0 | 0.001468 | 0.0000031 | No
29/09/2023 | 23:09 | WK52 | SHORT RURAL | Asset failure | HV | 34.33 | 288.9 | 0.069787 | 0.0002416 | No
30/09/2023 | 03:12 | AP365A | URBAN | Third Party | Vehicle impact | 59.00 | 748.9 | 0.068122 | 0.0000910 | No
30/09/2023 | 04:01 | MTB52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 994.00 | 138.9 | 0.990750 | 0.0071333 | No
30/09/2023 | 06:00 | NL511A | URBAN | Asset failure | LV | 1.00 | 334.0 | 0.000515 | 0.0000015 | No
30/09/2023 | 06:20 | HH177F | URBAN | Asset failure | LV | 77.00 | 880.0 | 0.104469 | 0.0001187 | No
30/09/2023 | 06:38 | SD40600 | LONG RURAL | Unknown | Unknown | 2.00 | 449.0 | 0.006444 | 0.0000144 | No
30/09/2023 | 06:43 | CN41 | LONG RURAL | Unknown | Unknown | 32.00 | 258.0 | 0.059248 | 0.0002296 | No
30/09/2023 | 07:13 | CN24 | LONG RURAL | Asset failure | LV | 22.00 | 509.0 | 0.080360 | 0.0001579 | No
30/09/2023 | 10:28 | AP424A | URBAN | Unknown | Unknown | 1.00 | 39.0 | 0.000060 | 0.0000015 | No
30/09/2023 | 12:06 | HH428B | URBAN | Overloads |  | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
30/09/2023 | 13:09 | MTB10 | URBAN | Asset failure | LV | 5.00 | 56.0 | 0.000432 | 0.0000077 | No
30/09/2023 | 13:18 | SM349H | URBAN | Asset failure | LV | 1.00 | 277.0 | 0.000427 | 0.0000015 | No
30/09/2023 | 14:02 | HH432F | URBAN | Third Party | Vehicle impact | 99.00 | 354.0 | 0.054032 | 0.0001526 | No
30/09/2023 | 14:23 | AP372F | URBAN | Overloads |  | 6.00 | 85.0 | 0.000786 | 0.0000093 | No
30/09/2023 | 15:23 | VH17 | SHORT RURAL | Unknown | Unknown | 27.00 | 152.0 | 0.028874 | 0.0001900 | No
30/09/2023 | 17:07 | SA18 | URBAN | Overloads |  | 1.00 | 32.0 | 0.000049 | 0.0000015 | No
30/09/2023 | 17:45 | MTB52 | LONG RURAL | Overloads |  | 9.00 | 97.0 | 0.006265 | 0.0000646 | No
30/09/2023 | 18:22 | SM179D | URBAN | Unknown | Unknown | 1.00 | 464.0 | 0.000715 | 0.0000015 | No
30/09/2023 | 18:40 | SM216G | URBAN | Asset failure | LV | 13.67 | 282.0 | 0.005942 | 0.0000211 | No
30/09/2023 | 22:29 | CV29 | LONG RURAL | Asset failure | HV | 95.00 | 157.0 | 0.107035 | 0.0006818 | No
01/10/2023 | 00:43 | AP139A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,050.00 | 85.0 | 0.137602 | 0.0016188 | No
01/10/2023 | 00:49 | AP365A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
01/10/2023 | 03:22 | EL01R | URBAN | Animal | Animal impact | 492.00 | 123.0 | 0.093282 | 0.0007585 | No
01/10/2023 | 08:39 | WHY05 | URBAN | Asset failure | LV | 1.00 | 297.0 | 0.000458 | 0.0000015 | No
01/10/2023 | 10:06 | VH71 | SHORT RURAL | Overloads |  | 1.00 | 324.0 | 0.002279 | 0.0000070 | No
01/10/2023 | 10:38 | HH177C | URBAN | Asset failure | HV | 45.00 | 1,584.4 | 0.109921 | 0.0000694 | No
01/10/2023 | 10:50 | LM13 | LONG RURAL | Planned |  | 35.00 | 60.0 | 0.015070 | 0.0002512 | No
01/10/2023 | 11:26 | SG06 | SHORT RURAL | Unknown | Unknown | 1.00 | 139.0 | 0.000978 | 0.0000070 | No
01/10/2023 | 11:36 | AP139A | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
01/10/2023 | 12:07 | SG01 | SHORT RURAL | Asset failure | LV | 1.00 | 233.0 | 0.001639 | 0.0000070 | No
01/10/2023 | 12:28 | HH341C | URBAN | Unknown | Unknown | 24.33 | 144.0 | 0.005402 | 0.0000375 | No
01/10/2023 | 13:53 | SM172B | URBAN | Asset failure | LV | 114.00 | 168.6 | 0.029631 | 0.0001758 | No
01/10/2023 | 14:46 | SD54300 | LONG RURAL | Animal | Animal impact | 93.00 | 17.0 | 0.011346 | 0.0006674 | No
01/10/2023 | 16:21 | HH121F | URBAN | Asset failure | HV | 488.00 | 35.3 | 0.026527 | 0.0007524 | No
01/10/2023 | 17:03 | EL01N | URBAN | Overloads |  | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
01/10/2023 | 17:53 | AP344F | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
01/10/2023 | 18:27 | GA08 | LONG RURAL | Animal | Animal impact | 1.00 | 1,000.0 | 0.007176 | 0.0000072 | No
01/10/2023 | 20:02 | AP425C | URBAN | Asset failure | LV | 1.00 | 327.0 | 0.000504 | 0.0000015 | No
01/10/2023 | 20:26 | MI26 | LONG RURAL | Weather |  | 25.00 | 408.0 | 0.073199 | 0.0001794 | No
02/10/2023 | 02:12 | MTB22 | SHORT RURAL | Asset failure | HV | 432.00 | 114.0 | 0.346582 | 0.0030393 | Yes
02/10/2023 | 08:31 | HH496C | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | Yes
02/10/2023 | 11:04 | SM216G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,619.00 | 77.0 | 0.192200 | 0.0024961 | Yes
02/10/2023 | 11:26 | SA31 | URBAN | Asset failure | HV | 395.33 | 7.0 | 0.004267 | 0.0006095 | Yes
02/10/2023 | 12:11 | SM179B | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | Yes
02/10/2023 | 12:19 | SD39400 | SHORT RURAL | Unknown | Unknown | 2.00 | 610.0 | 0.008583 | 0.0000141 | Yes
02/10/2023 | 12:21 | M92 | LONG RURAL | Unknown | Unknown | 1.00 | 2,971.0 | 0.021321 | 0.0000072 | Yes
02/10/2023 | 13:19 | HH496C | URBAN | Overloads |  | 12.33 | 172.0 | 0.003271 | 0.0000190 | Yes
02/10/2023 | 13:30 | BT04 | LONG RURAL | Asset failure | LV | 1.00 | 212.0 | 0.001521 | 0.0000072 | Yes
02/10/2023 | 13:40 | G02 | LONG RURAL | Planned |  | 12.33 | 13.0 | 0.001151 | 0.0000885 | Yes
02/10/2023 | 17:16 | NL210A | URBAN | Asset failure | LV | 1.00 | 233.0 | 0.000359 | 0.0000015 | Yes
02/10/2023 | 17:26 | PA02 | URBAN | Weather |  | 1,034.00 | 20.7 | 0.032974 | 0.0015942 | Yes
02/10/2023 | 17:32 | NL210A | URBAN | Third Party | Other | 146.00 | 824.9 | 0.185690 | 0.0002251 | Yes
02/10/2023 | 17:44 | PA13 | LONG RURAL | Weather |  | 23.00 | 363.0 | 0.059915 | 0.0001651 | Yes
02/10/2023 | 19:09 | CV02 | LONG RURAL | Weather |  | 54.67 | 229.0 | 0.089838 | 0.0003923 | Yes
02/10/2023 | 19:25 | PA04 | URBAN | Weather |  | 1.00 | 63.0 | 0.000097 | 0.0000015 | Yes
02/10/2023 | 19:43 | PA07 | LONG RURAL | Unknown | Unknown | 48.00 | 177.0 | 0.060970 | 0.0003445 | Yes
02/10/2023 | 20:52 | MT03 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 554.00 | 97.0 | 0.385642 | 0.0039757 | Yes
02/10/2023 | 21:00 | WHY08 | URBAN | Asset failure | LV | 12.00 | 81.0 | 0.001499 | 0.0000185 | Yes
02/10/2023 | 21:06 | ME427E | URBAN | Asset failure | LV | 117.00 | 1,329.0 | 0.239732 | 0.0001804 | Yes
02/10/2023 | 21:20 | LX25 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 338.00 | 135.0 | 0.321029 | 0.0023780 | Yes
02/10/2023 | 21:28 | AP125B | URBAN | Weather |  | 491.00 | 229.0 | 0.173353 | 0.0007570 | Yes
02/10/2023 | 21:28 | AP125B | URBAN | Weather |  | 6.00 | 3,136.7 | 0.029016 | 0.0000093 | Yes
02/10/2023 | 21:30 | NU20 | LONG RURAL | Weather |  | 7.33 | 270.0 | 0.014209 | 0.0000526 | Yes
02/10/2023 | 21:30 | AP344D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,297.00 | 566.0 | 1.131805 | 0.0019997 | Yes
02/10/2023 | 21:31 | AP132C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 288.00 | 794.4 | 0.352735 | 0.0004440 | Yes
02/10/2023 | 21:31 | AP344E | URBAN | Unknown | Unknown | 817.00 | 465.0 | 0.585720 | 0.0012596 | Yes
02/10/2023 | 21:32 | AP149D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 897.00 | 795.2 | 1.099784 | 0.0013830 | Yes
02/10/2023 | 21:32 | AP139B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,093.00 | 1,054.4 | 3.402558 | 0.0032269 | Yes
02/10/2023 | 21:33 | NL511A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,624.00 | 868.8 | 2.175202 | 0.0025038 | Yes
02/10/2023 | 21:33 | AP139D | URBAN | Third Party | Other | 2,037.00 | 903.0 | 2.835919 | 0.0031406 | Yes
02/10/2023 | 21:34 | NU04 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 89.0 | 0.000639 | 0.0000072 | Yes
02/10/2023 | 21:34 | NU04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 587.00 | 109.2 | 0.451010 | 0.0041298 | Yes
02/10/2023 | 21:34 | HH121A | URBAN | Asset failure | LV | 16.00 | 682.0 | 0.016824 | 0.0000247 | Yes
02/10/2023 | 21:35 | NL111C | URBAN | Asset failure | LV | 19.00 | 1,989.3 | 0.058272 | 0.0000293 | Yes
02/10/2023 | 21:35 | NL115B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 839.00 | 1,602.4 | 2.072762 | 0.0012935 | Yes
02/10/2023 | 21:35 | NL760B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,833.00 | 1,278.4 | 5.583981 | 0.0043678 | Yes
02/10/2023 | 21:35 | SM126D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,138.00 | 1,110.8 | 3.661610 | 0.0032963 | Yes
02/10/2023 | 21:36 | SSD212 | SHORT RURAL | Unknown | Unknown | 4.00 | 175.0 | 0.004925 | 0.0000281 | Yes
02/10/2023 | 21:36 | AP125D | URBAN | Weather |  | 101.00 | 453.0 | 0.070540 | 0.0001557 | Yes
02/10/2023 | 21:37 | AP424D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,490.0 | 0.002297 | 0.0000015 | Yes
02/10/2023 | 21:37 | NL234A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 224.00 | 1,410.0 | 0.486948 | 0.0003454 | Yes
02/10/2023 | 21:38 | NL115B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 933.00 | 1,335.2 | 1.920663 | 0.0014385 | Yes
02/10/2023 | 21:38 | NL210A | URBAN | Weather |  | 669.00 | 423.0 | 0.436296 | 0.0010314 | Yes
02/10/2023 | 21:38 | AP214D | URBAN | Weather |  | 75.00 | 325.0 | 0.037580 | 0.0001156 | Yes
02/10/2023 | 21:38 | AP227A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 24.00 | 1,548.0 | 0.057279 | 0.0000370 | Yes
02/10/2023 | 21:39 | AP139A | URBAN | Weather |  | 44.00 | 1,331.0 | 0.090291 | 0.0000678 | Yes
02/10/2023 | 21:39 | AP227A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 49.00 | 1,086.0 | 0.082043 | 0.0000755 | Yes
02/10/2023 | 21:39 | AP344A | URBAN | Unknown | Unknown | 74.00 | 1,839.0 | 0.209811 | 0.0001141 | Yes
02/10/2023 | 21:39 | SM411E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 696.00 | 849.7 | 0.911810 | 0.0010731 | Yes
02/10/2023 | 21:39 | SM411E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,069.0 | 0.001648 | 0.0000015 | Yes
02/10/2023 | 21:40 | MV15 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1,173.00 | 1,287.0 | 10.620777 | 0.0082526 | Yes
02/10/2023 | 21:40 | AP529E | URBAN | Asset failure | LV | 21.33 | 1,203.0 | 0.039568 | 0.0000329 | Yes
02/10/2023 | 21:40 | SM172F | URBAN | Unknown | Unknown | 22.00 | 1,213.0 | 0.041143 | 0.0000339 | Yes
02/10/2023 | 21:41 | AP355H | URBAN | Third Party | Other | 92.00 | 1,347.0 | 0.191060 | 0.0001418 | Yes
02/10/2023 | 21:41 | HH386C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,440.00 | 150.6 | 0.334246 | 0.0022201 | Yes
02/10/2023 | 21:42 | SG01 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 443.00 | 321.0 | 1.000489 | 0.0031167 | Yes
02/10/2023 | 21:42 | SG01 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 2,713.0 | 0.019087 | 0.0000070 | Yes
02/10/2023 | 21:44 | NL210F | URBAN | Asset failure | HV | 109.00 | 1,180.0 | 0.198300 | 0.0001681 | Yes
02/10/2023 | 21:45 | AP214B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 25.00 | 1,034.0 | 0.039854 | 0.0000385 | Yes
02/10/2023 | 21:45 | MTB32 | LONG RURAL | Asset failure | HV | 83.67 | 147.3 | 0.088415 | 0.0006004 | Yes
02/10/2023 | 21:45 | SM402D | URBAN | Weather |  | 106.00 | 946.0 | 0.154601 | 0.0001634 | Yes
02/10/2023 | 21:45 | NL111C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 47.00 | 332.0 | 0.024058 | 0.0000725 | Yes
02/10/2023 | 21:46 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 45.00 | 1,034.0 | 0.071738 | 0.0000694 | Yes
02/10/2023 | 21:46 | SM410C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 52.67 | 1,065.0 | 0.086477 | 0.0000812 | Yes
02/10/2023 | 21:47 | ME131D | URBAN | Asset failure | LV | 37.00 | 1,475.0 | 0.084141 | 0.0000570 | Yes
02/10/2023 | 21:50 | SM410C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 13.33 | 1,061.0 | 0.021811 | 0.0000206 | Yes
02/10/2023 | 21:51 | ME347F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 60.00 | 1,164.0 | 0.107676 | 0.0000925 | Yes
02/10/2023 | 21:51 | AP227A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 31.00 | 362.0 | 0.017302 | 0.0000478 | Yes
02/10/2023 | 21:51 | AP226C | URBAN | Weather |  | 1.00 | 201.0 | 0.000310 | 0.0000015 | Yes
02/10/2023 | 21:52 | SM349F | URBAN | Unknown | Unknown | 16.67 | 1,139.0 | 0.029268 | 0.0000257 | Yes
02/10/2023 | 21:52 | HH118B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 3.00 | 93.0 | 0.000430 | 0.0000046 | Yes
02/10/2023 | 21:52 | NL21 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.33 | 2,489.0 | 0.005117 | 0.0000021 | Yes
02/10/2023 | 21:53 | ME231E | URBAN | Asset failure | LV | 111.00 | 1,218.0 | 0.208442 | 0.0001711 | Yes
02/10/2023 | 21:54 | AP424D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 2.00 | 324.0 | 0.000999 | 0.0000031 | Yes
02/10/2023 | 21:58 | NL234D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 633.0 | 0.000976 | 0.0000015 | Yes
02/10/2023 | 21:59 | HH386B | URBAN | Unknown | Unknown | 64.00 | 843.0 | 0.083181 | 0.0000987 | Yes
02/10/2023 | 21:59 | NL760B | URBAN | Third Party | Other | 8.33 | 1,954.0 | 0.025105 | 0.0000128 | Yes
02/10/2023 | 21:59 | NL111P | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 65.00 | 189.0 | 0.018940 | 0.0001002 | Yes
02/10/2023 | 22:01 | NL234A | URBAN | Third Party | Other | 118.00 | 359.0 | 0.065312 | 0.0001819 | Yes
02/10/2023 | 22:08 | NL234A | URBAN | Weather |  | 45.00 | 1,783.0 | 0.123703 | 0.0000694 | Yes
02/10/2023 | 22:08 | CN42 | LONG RURAL | Asset failure | HV | 21.33 | 711.0 | 0.108851 | 0.0001531 | Yes
02/10/2023 | 22:08 | CN42 | LONG RURAL | Asset failure | HV | 7.00 | 2,365.0 | 0.118804 | 0.0000502 | Yes
02/10/2023 | 22:10 | AP125A | URBAN | Asset failure | LV | 2.00 | 216.0 | 0.000666 | 0.0000031 | Yes
02/10/2023 | 22:15 | SM349D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,277.0 | 0.001969 | 0.0000015 | Yes
02/10/2023 | 22:19 | NL115C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 268.0 | 0.000413 | 0.0000015 | Yes
02/10/2023 | 22:20 | AP146A | URBAN | Asset failure | LV | 1.00 | 611.0 | 0.000942 | 0.0000015 | Yes
02/10/2023 | 22:21 | MV32 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 13.00 | 665.0 | 0.060822 | 0.0000915 | Yes
02/10/2023 | 22:24 | M51 | SHORT RURAL | Third Party | Vehicle impact | 5.00 | 228.0 | 0.008020 | 0.0000352 | Yes
02/10/2023 | 22:26 | AP351C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 148.0 | 0.000456 | 0.0000031 | Yes
02/10/2023 | 22:33 | SM374A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 11.00 | 758.5 | 0.012864 | 0.0000170 | Yes
02/10/2023 | 22:43 | NL111P | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 154.0 | 0.000237 | 0.0000015 | Yes
02/10/2023 | 22:44 | WK72 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 456.00 | 286.0 | 0.917541 | 0.0032082 | Yes
02/10/2023 | 22:47 | HH148C | URBAN | Unknown | Unknown | 9.00 | 659.0 | 0.009144 | 0.0000139 | Yes
02/10/2023 | 22:48 | SM179D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,238.00 | 836.8 | 2.887184 | 0.0034504 | Yes
02/10/2023 | 22:52 | SM374C | URBAN | Unknown | Unknown | 105.00 | 988.0 | 0.159942 | 0.0001619 | Yes
02/10/2023 | 23:00 | WHY08 | URBAN | Unknown | Unknown | 1.00 | 22.0 | 0.000034 | 0.0000015 | Yes
02/10/2023 | 23:05 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 609.00 | 898.0 | 0.843157 | 0.0009389 | Yes
02/10/2023 | 23:12 | SM402D | URBAN | Unknown | Unknown | 1.00 | 631.0 | 0.000973 | 0.0000015 | Yes
02/10/2023 | 23:13 | SM402B | URBAN | Unknown | Unknown | 16.00 | 1,225.0 | 0.030218 | 0.0000247 | Yes
02/10/2023 | 23:15 | SM402D | URBAN | Unknown | Unknown | 1.00 | 656.0 | 0.001011 | 0.0000015 | Yes
02/10/2023 | 23:18 | SM402D | URBAN | Unknown | Unknown | 1.00 | 697.0 | 0.001075 | 0.0000015 | Yes
02/10/2023 | 23:22 | ME131D | URBAN | Asset failure | LV | 1.00 | 1,681.0 | 0.002592 | 0.0000015 | Yes
02/10/2023 | 23:22 | EL260C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 24.33 | 615.0 | 0.023072 | 0.0000375 | Yes
02/10/2023 | 23:23 | BT15 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 331.00 | 528.1 | 1.254473 | 0.0023754 | Yes
02/10/2023 | 23:24 | SM402D | URBAN | Unknown | Unknown | 1.00 | 820.0 | 0.001264 | 0.0000015 | Yes
02/10/2023 | 23:28 | NL210C | URBAN | Weather |  | 593.00 | 918.0 | 0.839291 | 0.0009143 | Yes
02/10/2023 | 23:30 | SM402D | URBAN | Unknown | Unknown | 1.00 | 736.0 | 0.001135 | 0.0000015 | Yes
02/10/2023 | 23:47 | VH43 | SHORT RURAL | Unknown | Unknown | 4.00 | 222.0 | 0.006248 | 0.0000281 | Yes
02/10/2023 | 23:49 | SA744C | URBAN | Unknown | Unknown | 24.00 | 576.0 | 0.021313 | 0.0000370 | Yes
03/10/2023 | 00:18 | MG13 | SHORT RURAL | Weather |  | 19.00 | 812.0 | 0.108544 | 0.0001337 | No
03/10/2023 | 00:36 | SM374C | URBAN | Unknown | Unknown | 51.00 | 885.0 | 0.069587 | 0.0000786 | No
03/10/2023 | 00:36 | BS0216 | CBD | Planned |  | 1.00 | 11,458.0 | 1.655422 | 0.0001445 | No
03/10/2023 | 00:55 | NL111C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 34.00 | 139.0 | 0.007286 | 0.0000524 | No
03/10/2023 | 01:46 | NL111P | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 580.0 | 0.000894 | 0.0000015 | No
03/10/2023 | 01:58 | KA14 | LONG RURAL | Asset failure | HV | 85.00 | 520.0 | 0.317194 | 0.0006100 | No
03/10/2023 | 02:02 | GA28 | LONG RURAL | Unknown | Unknown | 343.00 | 461.6 | 1.136164 | 0.0024615 | No
03/10/2023 | 02:17 | KA09 | LONG RURAL | Weather |  | 46.00 | 823.0 | 0.271681 | 0.0003301 | No
03/10/2023 | 02:21 | SM179D | URBAN | Unknown | Unknown | 1.00 | 954.0 | 0.001471 | 0.0000015 | No
03/10/2023 | 02:29 | HH121E | URBAN | Unknown | Unknown | 49.00 | 520.0 | 0.039284 | 0.0000755 | No
03/10/2023 | 02:33 | SD34400 | LONG RURAL | Unknown | Unknown | 710.00 | 559.3 | 2.849842 | 0.0050952 | No
03/10/2023 | 02:49 | CL07 | LONG RURAL | Weather |  | 53.00 | 452.0 | 0.171916 | 0.0003803 | No
03/10/2023 | 02:56 | R35 | LONG RURAL | Weather |  | 73.00 | 481.5 | 0.252241 | 0.0005239 | No
03/10/2023 | 03:05 | HH130F | URBAN | Vegetation | Grow-in - NSP responsibility | 17.33 | 397.0 | 0.010609 | 0.0000267 | No
03/10/2023 | 03:06 | CL04 | LONG RURAL | Weather |  | 3.00 | 817.0 | 0.017589 | 0.0000215 | No
03/10/2023 | 03:10 | EL11 | URBAN | Weather |  | 67.00 | 617.0 | 0.063738 | 0.0001033 | No
03/10/2023 | 03:25 | SD38100 | LONG RURAL | Unknown | Unknown | 1.00 | 678.0 | 0.004866 | 0.0000072 | No
03/10/2023 | 03:29 | WHY07 | LONG RURAL | Weather |  | 2.00 | 657.0 | 0.009430 | 0.0000144 | No
03/10/2023 | 03:29 | WHY07 | URBAN | Weather |  | 163.00 | 483.3 | 0.121444 | 0.0002513 | No
03/10/2023 | 05:11 | AP139A | URBAN | Vegetation | Grow-in - NSP responsibility | 89.00 | 890.0 | 0.122122 | 0.0001372 | No
03/10/2023 | 05:12 | SM374A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
03/10/2023 | 05:26 | AP125D | URBAN | Weather |  | 101.00 | 1,303.0 | 0.202899 | 0.0001557 | No
03/10/2023 | 05:41 | CN73 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 794.0 | 0.017094 | 0.0000215 | No
03/10/2023 | 05:48 | PP04 | SHORT RURAL | Weather |  | 35.67 | 165.0 | 0.041404 | 0.0002509 | No
03/10/2023 | 06:21 | BU06 | LONG RURAL | Unknown | Unknown | 1.00 | 534.0 | 0.003832 | 0.0000072 | No
03/10/2023 | 06:25 | MG29 | LONG RURAL | Asset failure | HV | 7.00 | 528.0 | 0.026524 | 0.0000502 | No
03/10/2023 | 06:32 | GU31 | LONG RURAL | Weather |  | 1.00 | 566.0 | 0.004062 | 0.0000072 | No
03/10/2023 | 06:35 | CL04 | LONG RURAL | Unknown | Unknown | 51.00 | 213.0 | 0.077971 | 0.0003660 | No
03/10/2023 | 06:39 | HK05 | LONG RURAL | Weather |  | 21.00 | 300.9 | 0.045340 | 0.0001507 | No
03/10/2023 | 06:48 | MV14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 45.00 | 1,159.0 | 0.366936 | 0.0003166 | No
03/10/2023 | 06:49 | NA12 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 7.00 | 144.0 | 0.007234 | 0.0000502 | No
03/10/2023 | 06:53 | MG22 | LONG RURAL | Weather |  | 17.00 | 534.8 | 0.065247 | 0.0001220 | No
03/10/2023 | 06:53 | MTB32 | LONG RURAL | Asset failure | HV | 27.00 | 240.1 | 0.046524 | 0.0001938 | No
03/10/2023 | 07:09 | MT12 | LONG RURAL | Weather |  | 4.00 | 304.5 | 0.008741 | 0.0000287 | No
03/10/2023 | 07:13 | MTB22 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 2.00 | 422.0 | 0.005938 | 0.0000141 | No
03/10/2023 | 07:15 | CL11 | SHORT RURAL | Asset failure | LV | 1.00 | 529.0 | 0.003722 | 0.0000070 | No
03/10/2023 | 07:26 | AP139A | URBAN | Vegetation | Grow-in - NSP responsibility | 31.00 | 518.9 | 0.024802 | 0.0000478 | No
03/10/2023 | 07:26 | HH121A | URBAN | Asset failure | LV | 6.00 | 96.0 | 0.000888 | 0.0000093 | No
03/10/2023 | 07:27 | SG14 | SHORT RURAL | Weather |  | 27.00 | 795.0 | 0.151017 | 0.0001900 | No
03/10/2023 | 07:34 | KA22 | LONG RURAL | Weather |  | 1.00 | 529.0 | 0.003796 | 0.0000072 | No
03/10/2023 | 07:37 | MT14 | SHORT RURAL | Weather |  | 78.00 | 507.2 | 0.278331 | 0.0005488 | No
03/10/2023 | 07:38 | NU21 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 564.0 | 0.008095 | 0.0000144 | No
03/10/2023 | 07:40 | NL210E | URBAN | Asset failure | LV | 8.00 | 899.0 | 0.011088 | 0.0000123 | No
03/10/2023 | 07:45 | BM34 | SHORT RURAL | Unknown | Unknown | 120.00 | 380.0 | 0.320818 | 0.0008443 | No
03/10/2023 | 07:47 | BM34 | SHORT RURAL | Unknown | Unknown | 247.00 | 324.0 | 0.563036 | 0.0017378 | No
03/10/2023 | 07:54 | LX41 | SHORT RURAL | Weather |  | 1.00 | 874.0 | 0.006149 | 0.0000070 | No
03/10/2023 | 08:10 | PP08 | LONG RURAL | Weather |  | 1.00 | 274.0 | 0.001966 | 0.0000072 | No
03/10/2023 | 08:24 | M21 | LONG RURAL | Animal | Animal impact | 15.67 | 550.0 | 0.061836 | 0.0001124 | No
03/10/2023 | 08:24 | CBD367J | CBD | Planned |  | 2.00 | 400.0 | 0.115582 | 0.0002890 | No
03/10/2023 | 08:30 | NL115C | URBAN | Unknown | Unknown | 8.33 | 1,614.0 | 0.020737 | 0.0000128 | No
03/10/2023 | 08:40 | BS0157 | URBAN | Weather |  | 1.00 | 72.0 | 0.000111 | 0.0000015 | No
03/10/2023 | 08:42 | HH522C | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
03/10/2023 | 08:47 | AP149C | URBAN | Unknown | Unknown | 77.00 | 643.0 | 0.076334 | 0.0001187 | No
03/10/2023 | 08:57 | HH107B | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
03/10/2023 | 09:10 | WK72 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 21.00 | 666.0 | 0.098398 | 0.0001477 | No
03/10/2023 | 09:14 | NL210D | URBAN | Unknown | Unknown | 40.00 | 421.0 | 0.025963 | 0.0000617 | No
03/10/2023 | 09:29 | CN02 | LONG RURAL | Asset failure | LV | 2.00 | 401.0 | 0.005755 | 0.0000144 | No
03/10/2023 | 09:44 | VH12 | SHORT RURAL | Asset failure | LV | 1.00 | 147.0 | 0.001034 | 0.0000070 | No
03/10/2023 | 09:46 | HH121A | URBAN | Overloads |  | 1.00 | 153.0 | 0.000236 | 0.0000015 | No
03/10/2023 | 09:59 | SM126C | URBAN | Asset failure | LV | 1.00 | 1,702.0 | 0.002624 | 0.0000015 | No
03/10/2023 | 10:01 | CV25 | LONG RURAL | Weather |  | 49.00 | 146.2 | 0.051418 | 0.0003516 | No
03/10/2023 | 10:07 | NL111Q | URBAN | Unknown | Unknown | 63.00 | 151.0 | 0.014667 | 0.0000971 | No
03/10/2023 | 10:16 | HH341A | URBAN | Overloads |  | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
03/10/2023 | 10:19 | HH130F | URBAN | Vegetation | Grow-in - NSP responsibility | 17.33 | 45.0 | 0.001203 | 0.0000267 | No
03/10/2023 | 10:47 | LX41 | SHORT RURAL | Unknown | Unknown | 1.00 | 586.0 | 0.004123 | 0.0000070 | No
03/10/2023 | 11:10 | MB71 | LONG RURAL | Weather |  | 1.00 | 625.0 | 0.004485 | 0.0000072 | No
03/10/2023 | 11:11 | BM15 | SHORT RURAL | Weather |  | 1.00 | 487.0 | 0.003426 | 0.0000070 | No
03/10/2023 | 11:13 | AP227A | URBAN | Third Party | Other | 25.00 | 50.0 | 0.001927 | 0.0000385 | No
03/10/2023 | 11:21 | MV22 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 9.00 | 1,643.0 | 0.104034 | 0.0000633 | No
03/10/2023 | 11:51 | KA14 | LONG RURAL | Unknown | Unknown | 12.00 | 124.0 | 0.010678 | 0.0000861 | No
03/10/2023 | 12:31 | W02 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 4.00 | 345.8 | 0.009925 | 0.0000287 | No
03/10/2023 | 12:32 | SM374A | URBAN | Asset failure | LV | 36.00 | 254.0 | 0.014098 | 0.0000555 | No
03/10/2023 | 12:41 | SM374A | URBAN | Weather |  | 1.00 | 575.0 | 0.000887 | 0.0000015 | No
03/10/2023 | 12:47 | MT12 | LONG RURAL | Weather |  | 2.00 | 346.0 | 0.004966 | 0.0000144 | No
03/10/2023 | 12:54 | AP829A | URBAN | Weather |  | 4.00 | 267.0 | 0.001647 | 0.0000062 | No
03/10/2023 | 13:25 | NL111B | URBAN | Unknown | Unknown | 2.00 | 584.0 | 0.001801 | 0.0000031 | No
03/10/2023 | 13:30 | HH102B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,501.00 | 61.0 | 0.141165 | 0.0023142 | No
03/10/2023 | 13:39 | EL260C | URBAN | Third Party | Other | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
03/10/2023 | 13:45 | HH102A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 391.0 | 0.000603 | 0.0000015 | No
03/10/2023 | 13:56 | SM216G | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 28.00 | 326.0 | 0.014073 | 0.0000432 | No
03/10/2023 | 14:03 | CD02 | LONG RURAL | Weather |  | 55.00 | 497.0 | 0.196165 | 0.0003947 | No
03/10/2023 | 14:13 | SM374A | URBAN | Weather |  | 1.00 | 453.0 | 0.000698 | 0.0000015 | No
03/10/2023 | 14:27 | AP149D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 463.0 | 0.000714 | 0.0000015 | No
03/10/2023 | 14:31 | NL210E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 2,887.00 | 78.0 | 0.347181 | 0.0044510 | No
03/10/2023 | 14:50 | SA744C | URBAN | Third Party | Vehicle impact | 1,529.00 | 285.2 | 0.672405 | 0.0023573 | No
03/10/2023 | 15:01 | AP214B | URBAN | Unknown | Unknown | 2.00 | 329.0 | 0.001014 | 0.0000031 | No
03/10/2023 | 15:15 | SA744D | URBAN | Third Party | Vehicle impact | 37.00 | 559.0 | 0.031888 | 0.0000570 | No
03/10/2023 | 15:16 | R09 | LONG RURAL | Asset failure | LV | 1.00 | 185.0 | 0.001328 | 0.0000072 | No
03/10/2023 | 15:29 | SD57100 | LONG RURAL | Unknown | Unknown | 1.00 | 194.0 | 0.001392 | 0.0000072 | No
03/10/2023 | 15:31 | BT03 | LONG RURAL | Weather |  | 151.67 | 154.0 | 0.167615 | 0.0010884 | No
03/10/2023 | 15:33 | AP214B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 25.00 | 4.0 | 0.000154 | 0.0000385 | No
03/10/2023 | 15:54 | SM411E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 14.33 | 77.0 | 0.001702 | 0.0000221 | No
03/10/2023 | 16:36 | PA02 | URBAN | Asset failure | LV | 14.33 | 111.0 | 0.002453 | 0.0000221 | No
03/10/2023 | 16:45 | KA22 | LONG RURAL | Third Party | Other | 188.00 | 18.0 | 0.024285 | 0.0013491 | No
03/10/2023 | 16:52 | M81 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 178.33 | 179.0 | 0.229080 | 0.0012798 | No
03/10/2023 | 17:25 | CN76 | LONG RURAL | Asset failure | LV | 1.00 | 287.0 | 0.002060 | 0.0000072 | No
03/10/2023 | 17:27 | AP529D | URBAN | Weather |  | 1.00 | 338.0 | 0.000521 | 0.0000015 | No
03/10/2023 | 17:31 | SM411E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 7.00 | 532.0 | 0.005741 | 0.0000108 | No
03/10/2023 | 17:41 | CN01 | LONG RURAL | Asset failure | HV | 45.00 | 518.0 | 0.167280 | 0.0003229 | No
03/10/2023 | 17:42 | SB18 | LONG RURAL | Weather |  | 42.00 | 450.7 | 0.135848 | 0.0003014 | No
03/10/2023 | 18:25 | AP149E | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
03/10/2023 | 18:29 | MV22 | SHORT RURAL | Unknown | Unknown | 2.00 | 1,255.0 | 0.017659 | 0.0000141 | No
03/10/2023 | 19:10 | NL210A | URBAN | Asset failure | LV | 25.33 | 699.0 | 0.027301 | 0.0000391 | No
03/10/2023 | 19:17 | NL210A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 38.00 | 135.0 | 0.007909 | 0.0000586 | No
03/10/2023 | 19:24 | NL210F | URBAN | Unknown | Unknown | 54.00 | 70.0 | 0.005828 | 0.0000833 | No
03/10/2023 | 19:28 | SM126D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 75.00 | 580.0 | 0.067066 | 0.0001156 | No
03/10/2023 | 19:43 | SM349C | URBAN | Asset failure | LV | 1.00 | 401.0 | 0.000618 | 0.0000015 | No
03/10/2023 | 19:49 | MTB14 | SHORT RURAL | Animal | Animal impact | 2,856.00 | 170.3 | 3.421064 | 0.0200934 | No
03/10/2023 | 19:57 | MTB14 | SHORT RURAL | Asset failure | LV | 1.00 | 259.0 | 0.001822 | 0.0000070 | No
03/10/2023 | 20:02 | AP355D | URBAN | Asset failure | LV | 3.00 | 93.0 | 0.000430 | 0.0000046 | No
03/10/2023 | 20:16 | KA27 | LONG RURAL | Unknown | Unknown | 2.00 | 187.0 | 0.002684 | 0.0000144 | No
03/10/2023 | 20:17 | NL210E | URBAN | Unknown | Unknown | 1.00 | 2,214.0 | 0.003413 | 0.0000015 | No
03/10/2023 | 20:35 | NL210C | URBAN | Asset failure | HV | 3,450.00 | 98.8 | 0.525575 | 0.0053191 | No
03/10/2023 | 20:35 | NL210E | URBAN | Asset failure | HV | 30.00 | 1,046.4 | 0.048400 | 0.0000463 | No
03/10/2023 | 20:44 | M21 | LONG RURAL | Weather |  | 4.00 | 1,037.0 | 0.029767 | 0.0000287 | No
03/10/2023 | 21:01 | W29 | LONG RURAL | Unknown | Unknown | 39.00 | 917.9 | 0.256891 | 0.0002799 | No
03/10/2023 | 21:43 | ME347C | URBAN | Unknown | Unknown | 1.00 | 164.0 | 0.000253 | 0.0000015 | No
03/10/2023 | 21:48 | HH102C | URBAN | Asset failure | LV | 6.00 | 203.0 | 0.001878 | 0.0000093 | No
03/10/2023 | 22:26 | AP355D | URBAN | Overloads |  | 1.00 | 381.0 | 0.000587 | 0.0000015 | No
03/10/2023 | 23:14 | ME200G | URBAN | Asset failure | LV | 157.00 | 64.0 | 0.015492 | 0.0002421 | No
03/10/2023 | 23:39 | KA09 | LONG RURAL | Asset failure | HV | 46.00 | 559.7 | 0.184747 | 0.0003301 | No
04/10/2023 | 01:25 | PL803C | URBAN | Weather |  | 1,090.00 | 139.6 | 0.234609 | 0.0016805 | No
04/10/2023 | 02:15 | VH18 | SHORT RURAL | Weather |  | 253.00 | 193.7 | 0.344802 | 0.0017800 | No
04/10/2023 | 07:42 | LX43 | SHORT RURAL | Asset failure | HV | 143.33 | 262.0 | 0.264206 | 0.0010084 | No
04/10/2023 | 07:56 | NL115B | URBAN | Weather |  | 1.00 | 299.0 | 0.000461 | 0.0000015 | No
04/10/2023 | 08:50 | EL23 | URBAN | Planned |  | 164.00 | 175.6 | 0.044399 | 0.0002528 | No
04/10/2023 | 09:13 | PL07 | URBAN | Planned |  | 49.00 | 140.4 | 0.010609 | 0.0000755 | No
04/10/2023 | 09:34 | VH44 | SHORT RURAL | Unknown | Unknown | 2.00 | 411.0 | 0.005783 | 0.0000141 | No
04/10/2023 | 09:36 | NA34 | LONG RURAL | Asset failure | LV | 1.00 | 111.0 | 0.000797 | 0.0000072 | No
04/10/2023 | 09:39 | NL210A | URBAN | Weather |  | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
04/10/2023 | 10:01 | NL210E | URBAN | Third Party | Other | 7.00 | 547.0 | 0.005903 | 0.0000108 | No
04/10/2023 | 10:02 | HH145E | URBAN | Third Party | Dig-in | 15.00 | 89.0 | 0.002058 | 0.0000231 | No
04/10/2023 | 10:24 | HH145B | URBAN | Planned |  | 89.00 | 248.0 | 0.034030 | 0.0001372 | No
04/10/2023 | 10:35 | HH121D | URBAN | Asset failure | LV | 1.00 | 252.0 | 0.000389 | 0.0000015 | No
04/10/2023 | 10:38 | NL115F | URBAN | Planned |  | 95.00 | 143.0 | 0.020945 | 0.0001465 | No
04/10/2023 | 10:39 | NL210A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 95.00 | 81.0 | 0.011864 | 0.0001465 | No
04/10/2023 | 11:32 | BM33 | SHORT RURAL | Unknown | Unknown | 240.00 | 178.0 | 0.300556 | 0.0016885 | No
04/10/2023 | 11:49 | PP02 | URBAN | Unknown | Unknown | 1.00 | 72.0 | 0.000111 | 0.0000015 | No
04/10/2023 | 11:57 | HH145B | URBAN | Asset failure | LV | 9.00 | 100.0 | 0.001388 | 0.0000139 | No
04/10/2023 | 12:05 | MTB22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 31.00 | 54.0 | 0.011777 | 0.0002181 | No
04/10/2023 | 12:05 | KA19 | LONG RURAL | Planned |  | 5.00 | 61.6 | 0.002210 | 0.0000359 | No
04/10/2023 | 13:16 | EL23 | URBAN | Network business | Switching and protection error | 2.00 | 69.0 | 0.000213 | 0.0000031 | No
04/10/2023 | 13:20 | SM216E | URBAN | Unknown | Unknown | 90.00 | 216.0 | 0.029972 | 0.0001388 | No
04/10/2023 | 13:29 | HH177B | URBAN | Overloads |  | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
04/10/2023 | 13:40 | HH177G | URBAN | Asset failure | LV | 57.00 | 73.0 | 0.006415 | 0.0000879 | No
04/10/2023 | 13:41 | BM21 | SHORT RURAL | Animal | Animal impact | 1.00 | 78.0 | 0.000549 | 0.0000070 | No
04/10/2023 | 14:01 | AP226D | URBAN | Asset failure | LV | 29.00 | 67.0 | 0.002996 | 0.0000447 | No
04/10/2023 | 14:03 | GU43 | LONG RURAL | Asset failure | LV | 1.00 | 7,270.0 | 0.052172 | 0.0000072 | No
04/10/2023 | 14:07 | EL23 | URBAN | Network business | Switching and protection error | 74.00 | 9.0 | 0.001027 | 0.0001141 | No
04/10/2023 | 14:20 | SA744D | URBAN | Asset failure | LV | 21.00 | 359.0 | 0.011623 | 0.0000324 | No
04/10/2023 | 14:51 | HH130F | URBAN | Asset failure | LV | 1.00 | 232.0 | 0.000358 | 0.0000015 | No
04/10/2023 | 16:00 | NL115C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
04/10/2023 | 16:06 | SM126D | URBAN | Unknown | Unknown | 1.00 | 403.0 | 0.000621 | 0.0000015 | No
04/10/2023 | 16:11 | AP149D | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
04/10/2023 | 16:24 | MV61 | URBAN | Unknown | Unknown | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
04/10/2023 | 17:22 | SM411E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 380.0 | 0.000586 | 0.0000015 | No
04/10/2023 | 17:33 | SA33 | URBAN | Overloads |  | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
04/10/2023 | 17:57 | EL16 | URBAN | Weather |  | 325.00 | 119.2 | 0.059706 | 0.0005011 | No
04/10/2023 | 18:10 | NU13 | LONG RURAL | Overloads |  | 1.00 | 206.0 | 0.001478 | 0.0000072 | No
04/10/2023 | 18:23 | HH386B | URBAN | Overloads |  | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
04/10/2023 | 18:33 | GA53 | SHORT RURAL | Asset failure | LV | 9.67 | 197.0 | 0.013398 | 0.0000680 | No
04/10/2023 | 18:44 | NL234A | URBAN | Asset failure | LV | 2.00 | 203.0 | 0.000626 | 0.0000031 | No
04/10/2023 | 18:44 | NL111C | URBAN | Other |  | 26.00 | 66.0 | 0.002646 | 0.0000401 | No
04/10/2023 | 19:15 | LM54 | LONG RURAL | Asset failure | HV | 19.00 | 48.0 | 0.006545 | 0.0001364 | No
04/10/2023 | 21:27 | MTB12 | SHORT RURAL | Unknown | Unknown | 1.00 | 147.0 | 0.001034 | 0.0000070 | No
04/10/2023 | 22:13 | HH145E | URBAN | Overloads |  | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
04/10/2023 | 23:01 | HH121E | URBAN | Unknown | Unknown | 10.67 | 159.0 | 0.002615 | 0.0000164 | No
04/10/2023 | 23:24 | NL115C | URBAN | Weather |  | 10.67 | 79.6 | 0.001308 | 0.0000164 | No
05/10/2023 | 00:26 | NL760C | URBAN | Weather |  | 18.67 | 112.0 | 0.003223 | 0.0000288 | No
05/10/2023 | 07:19 | NU20 | LONG RURAL | Asset failure | LV | 1.00 | 315.0 | 0.002261 | 0.0000072 | No
05/10/2023 | 07:57 | WHY04 | URBAN | Planned |  | 86.00 | 541.0 | 0.071732 | 0.0001326 | No
05/10/2023 | 08:37 | YK03 | LONG RURAL | Planned |  | 632.00 | 336.5 | 1.526233 | 0.0045354 | No
05/10/2023 | 08:53 | AP425D | URBAN | Planned |  | 13.00 | 357.0 | 0.007155 | 0.0000200 | No
05/10/2023 | 09:03 | KA01 | SHORT RURAL | Planned |  | 1.00 | 20.0 | 0.000141 | 0.0000070 | No
05/10/2023 | 09:05 | EL260A | URBAN | Planned |  | 165.00 | 382.2 | 0.097215 | 0.0002544 | No
05/10/2023 | 09:07 | CD04 | SHORT RURAL | Planned |  | 194.00 | 194.0 | 0.264788 | 0.0013649 | No
05/10/2023 | 09:09 | SG09 | SHORT RURAL | Planned |  | 6.00 | 9,152.8 | 0.386368 | 0.0000422 | No
05/10/2023 | 09:10 | KI51 | LONG RURAL | Planned |  | 20.00 | 205.0 | 0.029423 | 0.0001435 | No
05/10/2023 | 09:11 | SA17 | URBAN | Planned |  | 1.00 | 348.0 | 0.000537 | 0.0000015 | No
05/10/2023 | 10:49 | EL12 | URBAN | Unknown | Unknown | 199.00 | 252.6 | 0.077490 | 0.0003068 | No
05/10/2023 | 10:49 | MTB32 | LONG RURAL | Planned |  | 20.00 | 143.0 | 0.020524 | 0.0001435 | No
05/10/2023 | 11:06 | SD32200 | LONG RURAL | Planned |  | 71.00 | 87.0 | 0.044314 | 0.0005095 | No
05/10/2023 | 11:44 | GU14 | LONG RURAL | Overloads |  | 24.00 | 26.3 | 0.004528 | 0.0001722 | No
05/10/2023 | 12:15 | AP355D | URBAN | Asset failure | LV | 12.00 | 1,043.0 | 0.019297 | 0.0000185 | No
05/10/2023 | 12:20 | AP425A | URBAN | Asset failure | LV | 1.00 | 1,320.0 | 0.002035 | 0.0000015 | No
05/10/2023 | 13:47 | W29 | LONG RURAL | Weather |  | 39.00 | 215.0 | 0.060174 | 0.0002799 | No
05/10/2023 | 14:16 | R21 | LONG RURAL | Unknown | Unknown | 4.00 | 83.0 | 0.002383 | 0.0000287 | No
05/10/2023 | 15:29 | MV14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 573.00 | 51.6 | 0.208025 | 0.0040313 | No
05/10/2023 | 16:31 | CN32 | LONG RURAL | Animal | Animal impact | 2.00 | 144.0 | 0.002067 | 0.0000144 | No
05/10/2023 | 16:50 | AP829A | URBAN | Asset failure | HV | 4.00 | 383.0 | 0.002362 | 0.0000062 | No
05/10/2023 | 17:08 | GA15 | SHORT RURAL | Asset failure | LV | 2.33 | 522.4 | 0.008576 | 0.0000164 | No
05/10/2023 | 17:09 | AP149B | URBAN | Asset failure | LV | 1.00 | 933.0 | 0.001438 | 0.0000015 | No
05/10/2023 | 18:58 | WK11 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 166.7 | 0.003518 | 0.0000211 | No
05/10/2023 | 21:13 | SM411D | URBAN | Asset failure | LV | 1.00 | 263.0 | 0.000405 | 0.0000015 | No
05/10/2023 | 21:17 | GA26 | URBAN | Planned |  | 111.00 | 386.7 | 0.066184 | 0.0001711 | No
05/10/2023 | 22:08 | ME347F | URBAN | Asset failure | HV | 955.00 | 404.8 | 0.595985 | 0.0014724 | No
05/10/2023 | 22:31 | AP529A | URBAN | Asset failure | LV | 26.00 | 629.0 | 0.025214 | 0.0000401 | No
05/10/2023 | 23:22 | HH496C | URBAN | Asset failure | LV | 37.00 | 211.0 | 0.012036 | 0.0000570 | No
06/10/2023 | 04:21 | ME347E | URBAN | Asset failure | LV | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
06/10/2023 | 04:21 | ME347E | URBAN | Asset failure | HV | 243.00 | 83.0 | 0.031096 | 0.0003746 | No
06/10/2023 | 04:25 | AP355D | URBAN | Asset failure | LV | 1.33 | 65.0 | 0.000134 | 0.0000021 | No
06/10/2023 | 07:37 | YK27 | LONG RURAL | Asset failure | LV | 1.00 | 198.0 | 0.001421 | 0.0000072 | No
06/10/2023 | 08:06 | PL07 | URBAN | Planned |  | 8.00 | 43.0 | 0.000530 | 0.0000123 | No
06/10/2023 | 08:46 | KA14 | LONG RURAL | Planned |  | 85.00 | 233.0 | 0.142113 | 0.0006100 | No
06/10/2023 | 08:51 | HH341G | URBAN | Asset failure | LV | 136.00 | 32.0 | 0.006710 | 0.0002097 | No
06/10/2023 | 09:00 | MTB32 | LONG RURAL | Planned |  | 67.00 | 292.4 | 0.140584 | 0.0004808 | No
06/10/2023 | 09:00 | MTB32 | SHORT RURAL | Planned |  | 1.00 | 267.0 | 0.001878 | 0.0000070 | No
06/10/2023 | 09:01 | SG14 | SHORT RURAL | Planned |  | 172.00 | 300.3 | 0.363425 | 0.0012101 | No
06/10/2023 | 09:05 | HH121B | URBAN | Planned |  | 96.00 | 834.5 | 0.123518 | 0.0001480 | No
06/10/2023 | 09:05 | HH121B | URBAN | Planned |  | 18.00 | 839.0 | 0.023284 | 0.0000278 | No
06/10/2023 | 09:13 | NA24 | LONG RURAL | Asset failure | LV | 1.00 | 173.0 | 0.001242 | 0.0000072 | No
06/10/2023 | 09:14 | SD55100 | LONG RURAL | Planned |  | 269.00 | 90.0 | 0.173739 | 0.0019304 | No
06/10/2023 | 09:24 | EL10 | URBAN | Planned |  | 668.00 | 54.6 | 0.056249 | 0.0010299 | No
06/10/2023 | 09:30 | CM03 | LONG RURAL | Planned |  | 114.00 | 278.0 | 0.227432 | 0.0008181 | No
06/10/2023 | 09:48 | CD16 | SHORT RURAL | Planned |  | 2.00 | 198.0 | 0.002786 | 0.0000141 | No
06/10/2023 | 09:52 | MV63 | SHORT RURAL | Planned |  | 194.00 | 94.0 | 0.128299 | 0.0013649 | No
06/10/2023 | 10:01 | AP529A | URBAN | Asset failure | LV | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
06/10/2023 | 10:08 | CN43 | LONG RURAL | Planned |  | 4.00 | 68.0 | 0.001952 | 0.0000287 | No
06/10/2023 | 10:44 | HH496F | URBAN | Asset failure | LV | 1.00 | 364.0 | 0.000561 | 0.0000015 | No
06/10/2023 | 10:47 | MTB53 | LONG RURAL | Third Party | Vehicle impact | 19.00 | 412.0 | 0.056176 | 0.0001364 | No
06/10/2023 | 11:07 | MB25 | LONG RURAL | Planned |  | 55.00 | 116.0 | 0.045785 | 0.0003947 | No
06/10/2023 | 11:08 | BT20 | LONG RURAL | Planned |  | 33.00 | 226.0 | 0.053521 | 0.0002368 | No
06/10/2023 | 11:12 | NA24 | LONG RURAL | Asset failure | HV | 3.00 | 43.0 | 0.000926 | 0.0000215 | No
06/10/2023 | 11:45 | MG11 | SHORT RURAL | Unknown | Unknown | 3.00 | 125.0 | 0.002638 | 0.0000211 | No
06/10/2023 | 13:16 | CN42 | LONG RURAL | Planned |  | 8.00 | 37.0 | 0.002124 | 0.0000574 | No
06/10/2023 | 13:33 | YK28 | LONG RURAL | Planned |  | 15.00 | 54.0 | 0.005813 | 0.0001076 | No
06/10/2023 | 13:35 | CV24 | LONG RURAL | Weather |  | 74.00 | 70.5 | 0.037446 | 0.0005310 | No
06/10/2023 | 13:52 | PL803A | URBAN | Asset failure | LV | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
06/10/2023 | 13:55 | GA28 | LONG RURAL | Asset failure | HV | 33.00 | 56.0 | 0.013262 | 0.0002368 | No
06/10/2023 | 14:23 | AP226E | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
06/10/2023 | 15:32 | AP829B | URBAN | Overloads |  | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
06/10/2023 | 19:01 | NL115C | URBAN | Overloads |  | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
07/10/2023 | 06:47 | MV22 | SHORT RURAL | Asset failure | LV | 1.00 | 395.0 | 0.002779 | 0.0000070 | No
07/10/2023 | 07:28 | KI54 | LONG RURAL | Asset failure | LV | 1.00 | 405.0 | 0.002906 | 0.0000072 | No
07/10/2023 | 08:34 | NL210E | URBAN | Planned |  | 287.00 | 13.0 | 0.005752 | 0.0004425 | No
07/10/2023 | 08:34 | NL210E | URBAN | Unknown | Unknown | 98.00 | 262.8 | 0.039711 | 0.0001511 | No
07/10/2023 | 08:47 | M21 | LONG RURAL | Unknown | Unknown | 12.00 | 247.0 | 0.021271 | 0.0000861 | No
07/10/2023 | 08:55 | SSD398 | SHORT RURAL | Unknown | Unknown | 212.00 | 93.0 | 0.138712 | 0.0014915 | No
07/10/2023 | 08:55 | SSD398 | SHORT RURAL | Unknown | Unknown | 3,276.00 | 224.7 | 5.178958 | 0.0230483 | No
07/10/2023 | 08:55 | SSD398 | URBAN | Unknown | Unknown | 10.00 | 242.0 | 0.003731 | 0.0000154 | No
07/10/2023 | 09:35 | NL210E | URBAN | Asset failure | HV | 1,741.00 | 8.0 | 0.021474 | 0.0026842 | No
07/10/2023 | 09:41 | WHY05 | URBAN | Third Party | Vehicle impact | 35.00 | 201.2 | 0.010857 | 0.0000540 | No
07/10/2023 | 09:43 | HH145C | URBAN | Third Party | Unauthorised access | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
07/10/2023 | 12:13 | AP372B | URBAN | Other |  | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
07/10/2023 | 13:19 | VH15 | SHORT RURAL | Asset failure | LV | 69.00 | 137.2 | 0.066584 | 0.0004854 | No
07/10/2023 | 13:24 | AP529D | URBAN | Asset failure | LV | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
07/10/2023 | 13:30 | KI54 | LONG RURAL | Asset failure | HV | 3.00 | 29.0 | 0.000624 | 0.0000215 | No
07/10/2023 | 14:08 | MV61 | URBAN | Animal | Animal nesting/burrowing, etc and other | 1.00 | 420.0 | 0.000648 | 0.0000015 | No
07/10/2023 | 15:51 | EL25 | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
07/10/2023 | 17:23 | HH409E | URBAN | Animal | Animal impact | 1,544.00 | 10.8 | 0.025786 | 0.0023805 | No
07/10/2023 | 19:17 | NA52 | LONG RURAL | Unknown | Unknown | 1.00 | 300.0 | 0.002153 | 0.0000072 | No
08/10/2023 | 00:20 | WHY09 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 3.33 | 179.0 | 0.000920 | 0.0000051 | No
08/10/2023 | 01:46 | PA04 | URBAN | Asset failure | LV | 1.00 | 3,885.0 | 0.005990 | 0.0000015 | No
08/10/2023 | 04:27 | HH341C | URBAN | Planned |  | 15.00 | 336.0 | 0.007770 | 0.0000231 | No
08/10/2023 | 08:06 | MG05 | LONG RURAL | Planned |  | 21.00 | 120.0 | 0.018084 | 0.0001507 | No
08/10/2023 | 08:11 | SD49900 | URBAN | Unknown | Unknown | 2.00 | 127.0 | 0.000392 | 0.0000031 | No
08/10/2023 | 08:17 | SM216B | URBAN | Planned |  | 87.00 | 319.0 | 0.042788 | 0.0001341 | No
08/10/2023 | 08:30 | MI06 | LONG RURAL | Planned |  | 17.00 | 115.0 | 0.014030 | 0.0001220 | No
08/10/2023 | 08:40 | GA41 | LONG RURAL | Planned |  | 29.00 | 123.0 | 0.025598 | 0.0002081 | No
08/10/2023 | 08:59 | EL01L | URBAN | Planned |  | 253.00 | 241.5 | 0.094187 | 0.0003901 | No
08/10/2023 | 09:18 | MI15 | LONG RURAL | Planned |  | 27.00 | 212.0 | 0.041077 | 0.0001938 | No
08/10/2023 | 10:14 | CV16 | LONG RURAL | Unknown | Unknown | 41.00 | 202.0 | 0.059434 | 0.0002942 | No
08/10/2023 | 10:44 | LM53 | LONG RURAL | Planned |  | 64.00 | 313.0 | 0.143756 | 0.0004593 | No
08/10/2023 | 10:58 | SM374A | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
08/10/2023 | 11:27 | GA36 | LONG RURAL | Planned |  | 79.00 | 191.0 | 0.108284 | 0.0005669 | No
08/10/2023 | 12:13 | HH177B | URBAN | Asset failure | LV | 30.00 | 57.0 | 0.002636 | 0.0000463 | No
08/10/2023 | 12:15 | EL02 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
08/10/2023 | 12:50 | HH177A | URBAN | Asset failure | LV | 11.00 | 112.0 | 0.001899 | 0.0000170 | No
08/10/2023 | 12:57 | HH121D | URBAN | Overloads |  | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
08/10/2023 | 13:31 | GA22 | SHORT RURAL | Asset failure | LV | 1.00 | 118.0 | 0.000830 | 0.0000070 | No
08/10/2023 | 14:06 | WHY17 | SHORT RURAL | Asset failure | LV | 15.00 | 71.0 | 0.007493 | 0.0001055 | No
08/10/2023 | 14:08 | SA744D | URBAN | Asset failure | LV | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
08/10/2023 | 15:15 | HH341A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,302.00 | 51.0 | 0.102376 | 0.0020074 | No
08/10/2023 | 15:20 | HH148A | URBAN | Asset failure | LV | 41.00 | 512.0 | 0.032364 | 0.0000632 | No
08/10/2023 | 15:25 | HH130F | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
08/10/2023 | 15:40 | HH386B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 91.00 | 38.0 | 0.005331 | 0.0001403 | No
08/10/2023 | 16:39 | MI01 | LONG RURAL | Asset failure | LV | 1.00 | 1,313.0 | 0.009423 | 0.0000072 | No
08/10/2023 | 17:47 | EL01N | URBAN | Asset failure | LV | 1.00 | 272.0 | 0.000419 | 0.0000015 | No
08/10/2023 | 18:24 | PP14 | LONG RURAL | Third Party | Vehicle impact | 22.00 | 74.0 | 0.011683 | 0.0001579 | No
08/10/2023 | 18:24 | PP14 | LONG RURAL | Third Party | Vehicle impact | 30.00 | 1,100.9 | 0.237020 | 0.0002153 | No
08/10/2023 | 21:51 | EL18 | URBAN | Overloads |  | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
08/10/2023 | 23:33 | EL18 | URBAN | Asset failure | LV | 1.00 | 311.0 | 0.000479 | 0.0000015 | No
09/10/2023 | 08:09 | BM21 | SHORT RURAL | Asset failure | LV | 1.00 | 58.0 | 0.000408 | 0.0000070 | No
09/10/2023 | 08:30 | MG04 | SHORT RURAL | Planned |  | 1.00 | 249.0 | 0.001752 | 0.0000070 | No
09/10/2023 | 08:47 | CL12 | LONG RURAL | Planned |  | 10.00 | 144.0 | 0.010334 | 0.0000718 | No
09/10/2023 | 09:29 | GU11 | LONG RURAL | Planned |  | 10.00 | 174.0 | 0.012487 | 0.0000718 | No
09/10/2023 | 09:32 | NL451C | URBAN | Planned |  | 147.00 | 219.3 | 0.049691 | 0.0002266 | No
09/10/2023 | 09:35 | SM411C | URBAN | Planned |  | 48.00 | 268.5 | 0.019869 | 0.0000740 | No
09/10/2023 | 09:51 | GU21 | LONG RURAL | Planned |  | 2.00 | 25.0 | 0.000359 | 0.0000144 | No
09/10/2023 | 10:07 | HH428A | URBAN | Asset failure | LV | 9.00 | 188.0 | 0.002609 | 0.0000139 | No
09/10/2023 | 10:39 | MB123 | LONG RURAL | Planned |  | 79.00 | 247.0 | 0.140032 | 0.0005669 | No
09/10/2023 | 11:06 | HH121F | URBAN | Overloads |  | 1.00 | 583.0 | 0.000899 | 0.0000015 | No
09/10/2023 | 12:27 | HH341E | URBAN | Unknown | Unknown | 86.00 | 281.0 | 0.037258 | 0.0001326 | No
09/10/2023 | 12:33 | PA07 | LONG RURAL | Overloads |  | 16.00 | 176.0 | 0.020209 | 0.0001148 | No
09/10/2023 | 13:03 | EL17 | URBAN | Third Party | Unauthorised access | 4.00 | 359.0 | 0.002214 | 0.0000062 | No
09/10/2023 | 15:58 | ST21 | SHORT RURAL | Weather |  | 10.00 | 76.0 | 0.005347 | 0.0000704 | No
09/10/2023 | 16:01 | SM374B | URBAN | Asset failure | LV | 1.00 | 120.0 | 0.000185 | 0.0000015 | No
09/10/2023 | 16:54 | NL451A | URBAN | Asset failure | LV | 1.00 | 136.0 | 0.000210 | 0.0000015 | No
09/10/2023 | 17:06 | LM43 | LONG RURAL | Asset failure | HV | 13.00 | 95.2 | 0.008884 | 0.0000933 | No
09/10/2023 | 17:07 | HH428A | URBAN | Network business | Switching and protection error | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
09/10/2023 | 17:41 | SM179A | URBAN | Overloads |  | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
09/10/2023 | 17:54 | BS0402 | URBAN | Unknown | Unknown | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
09/10/2023 | 18:33 | LM31 | LONG RURAL | Asset failure | HV | 28.00 | 71.0 | 0.014267 | 0.0002009 | No
09/10/2023 | 20:49 | NL115D | URBAN | Asset failure | LV | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
09/10/2023 | 21:15 | NL111Q | URBAN | Other |  | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
09/10/2023 | 21:46 | NU02 | LONG RURAL | Overloads |  | 1.00 | 178.0 | 0.001277 | 0.0000072 | No
10/10/2023 | 01:23 | KA14 | LONG RURAL | Asset failure | HV | 85.00 | 282.0 | 0.172017 | 0.0006100 | No
10/10/2023 | 04:38 | EL01P | URBAN | Asset failure | HV | 566.00 | 191.2 | 0.166835 | 0.0008726 | No
10/10/2023 | 07:32 | ST23 | SHORT RURAL | Animal | Animal impact | 7.00 | 129.0 | 0.006353 | 0.0000492 | No
10/10/2023 | 08:31 | KI31 | SHORT RURAL | Planned |  | 144.00 | 170.0 | 0.172201 | 0.0010131 | No
10/10/2023 | 08:47 | MT09 | LONG RURAL | Asset failure | LV | 4.00 | 327.5 | 0.009401 | 0.0000287 | No
10/10/2023 | 08:49 | ME200A | URBAN | Planned |  | 130.00 | 386.0 | 0.077365 | 0.0002004 | No
10/10/2023 | 08:51 | MTB14 | SHORT RURAL | Planned |  | 31.00 | 287.0 | 0.062588 | 0.0002181 | No
10/10/2023 | 08:53 | CL06 | LONG RURAL | Planned |  | 6.00 | 201.0 | 0.008655 | 0.0000431 | No
10/10/2023 | 08:55 | SM126A | URBAN | Planned |  | 23.00 | 300.0 | 0.010638 | 0.0000355 | No
10/10/2023 | 09:11 | MTB12 | SHORT RURAL | Other |  | 1.00 | 250.0 | 0.001759 | 0.0000070 | No
10/10/2023 | 09:59 | CV32 | LONG RURAL | Planned |  | 3.00 | 159.0 | 0.003423 | 0.0000215 | No
10/10/2023 | 10:16 | MG19 | LONG RURAL | Planned |  | 8.00 | 94.0 | 0.005397 | 0.0000574 | No
10/10/2023 | 10:38 | G17 | LONG RURAL | Planned |  | 83.00 | 98.2 | 0.058494 | 0.0005956 | No
10/10/2023 | 10:39 | GA16 | LONG RURAL | Planned |  | 1.00 | 92.0 | 0.000660 | 0.0000072 | No
10/10/2023 | 10:50 | MI12 | LONG RURAL | Planned |  | 1.00 | 61.0 | 0.000438 | 0.0000072 | No
10/10/2023 | 10:57 | CD18 | LONG RURAL | Planned |  | 15.00 | 153.0 | 0.016470 | 0.0001076 | No
10/10/2023 | 10:58 | YK23 | LONG RURAL | Planned |  | 19.00 | 175.0 | 0.023861 | 0.0001364 | No
10/10/2023 | 11:25 | EL16 | URBAN | Overloads |  | 3.00 | 429.0 | 0.001984 | 0.0000046 | No
10/10/2023 | 11:53 | BT27 | LONG RURAL | Planned |  | 2.00 | 31.0 | 0.000445 | 0.0000144 | No
10/10/2023 | 12:26 | LM33 | LONG RURAL | Asset failure | HV | 1.00 | 15.0 | 0.000108 | 0.0000072 | No
10/10/2023 | 12:27 | AP132C | URBAN | Unknown | Unknown | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
10/10/2023 | 12:38 | MTB32 | LONG RURAL | Asset failure | LV | 2.00 | 163.0 | 0.002339 | 0.0000144 | No
10/10/2023 | 12:44 | PL07 | URBAN | Asset failure | LV | 1.00 | 1,091.0 | 0.001682 | 0.0000015 | No
10/10/2023 | 13:40 | SD40600 | LONG RURAL | Network business | Switching and protection error | 1,783.00 | 16.0 | 0.204669 | 0.0127954 | No
10/10/2023 | 14:02 | EL01P | URBAN | Asset failure | LV | 1.00 | 1,220.0 | 0.001881 | 0.0000015 | No
10/10/2023 | 14:51 | AP132C | URBAN | Asset failure | LV | 3.00 | 394.0 | 0.001822 | 0.0000046 | No
10/10/2023 | 16:59 | HH177F | URBAN | Asset failure | LV | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
10/10/2023 | 17:21 | NA04 | LONG RURAL | Asset failure | HV | 140.00 | 457.6 | 0.459716 | 0.0010047 | No
10/10/2023 | 18:51 | SM137D | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
10/10/2023 | 22:20 | MTB21 | SHORT RURAL | Planned |  | 34.00 | 365.0 | 0.087310 | 0.0002392 | No
11/10/2023 | 08:19 | PL04 | URBAN | Planned |  | 115.00 | 312.0 | 0.055318 | 0.0001773 | No
11/10/2023 | 08:43 | BM56 | SHORT RURAL | Planned |  | 32.00 | 225.0 | 0.050656 | 0.0002251 | No
11/10/2023 | 09:04 | NU13 | LONG RURAL | Asset failure | LV | 2.00 | 377.0 | 0.005411 | 0.0000144 | No
11/10/2023 | 09:13 | SM349B | URBAN | Planned |  | 99.00 | 352.0 | 0.053727 | 0.0001526 | No
11/10/2023 | 09:29 | SA14 | URBAN | Planned |  | 450.00 | 163.8 | 0.113666 | 0.0006938 | No
11/10/2023 | 09:30 | R26 | LONG RURAL | Third Party | Vehicle impact | 88.00 | 191.2 | 0.120735 | 0.0006315 | No
11/10/2023 | 09:33 | SM126A | URBAN | Planned |  | 143.00 | 348.0 | 0.076724 | 0.0002205 | No
11/10/2023 | 09:33 | CV31 | LONG RURAL | Planned |  | 28.00 | 108.0 | 0.021701 | 0.0002009 | No
11/10/2023 | 09:38 | GA25 | SHORT RURAL | Planned |  | 61.00 | 212.2 | 0.091060 | 0.0004292 | No
11/10/2023 | 09:39 | MTB14 | SHORT RURAL | Planned |  | 16.00 | 171.0 | 0.019249 | 0.0001126 | No
11/10/2023 | 09:53 | SM126C | URBAN | Planned |  | 49.00 | 312.0 | 0.023570 | 0.0000755 | No
11/10/2023 | 10:05 | BT04 | LONG RURAL | Planned |  | 69.00 | 193.0 | 0.095567 | 0.0004952 | No
11/10/2023 | 10:14 | CN01 | LONG RURAL | Planned |  | 65.00 | 179.0 | 0.083497 | 0.0004665 | No
11/10/2023 | 10:27 | LM63 | LONG RURAL | Planned |  | 2.00 | 76.0 | 0.001091 | 0.0000144 | No
11/10/2023 | 11:34 | MTB61 | SHORT RURAL | Third Party | Other | 6.67 | 55.7 | 0.002613 | 0.0000469 | No
11/10/2023 | 12:03 | ME200A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 451.00 | 26.0 | 0.018079 | 0.0006953 | No
11/10/2023 | 12:33 | NL760B | URBAN | Vegetation | Grow-in - NSP responsibility | 24.00 | 64.0 | 0.002368 | 0.0000370 | No
11/10/2023 | 12:38 | HH386C | URBAN | Asset failure | LV | 19.00 | 57.0 | 0.001670 | 0.0000293 | No
11/10/2023 | 12:44 | AP355H | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
11/10/2023 | 12:48 | AP355H | URBAN | Vegetation | Grow-in - NSP responsibility | 101.00 | 95.0 | 0.014793 | 0.0001557 | No
11/10/2023 | 13:21 | BM55 | SHORT RURAL | Unknown | Unknown | 4.00 | 118.0 | 0.003321 | 0.0000281 | No
11/10/2023 | 13:34 | SM172A | URBAN | Unknown | Unknown | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
11/10/2023 | 13:53 | AP355A | URBAN | Other |  | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
11/10/2023 | 14:08 | EL01P | URBAN | Asset failure | LV | 1.00 | 2,918.0 | 0.004499 | 0.0000015 | No
11/10/2023 | 14:17 | PA03 | URBAN | Asset failure | LV | 28.00 | 52.0 | 0.002245 | 0.0000432 | No
11/10/2023 | 14:38 | EL02 | URBAN | Unknown | Unknown | 1.00 | 322.0 | 0.000496 | 0.0000015 | No
11/10/2023 | 14:43 | SM350F | URBAN | Asset failure | LV | 1.00 | 273.0 | 0.000421 | 0.0000015 | No
11/10/2023 | 15:38 | VH15 | SHORT RURAL | Asset failure | LV | 2.00 | 81.0 | 0.001140 | 0.0000141 | No
11/10/2023 | 16:04 | HH121F | URBAN | Overloads |  | 23.33 | 78.0 | 0.002806 | 0.0000360 | No
11/10/2023 | 16:10 | SA520H | URBAN | Overloads |  | 10.33 | 858.0 | 0.013669 | 0.0000159 | No
11/10/2023 | 16:54 | HH121E | URBAN | Third Party | Vehicle impact | 2.00 | 206.0 | 0.000635 | 0.0000031 | No
11/10/2023 | 18:03 | SA711C | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
11/10/2023 | 19:11 | VH17 | SHORT RURAL | Asset failure | LV | 1.00 | 152.0 | 0.001069 | 0.0000070 | No
11/10/2023 | 19:20 | VH17 | SHORT RURAL | Asset failure | HV | 5.00 | 81.0 | 0.002849 | 0.0000352 | No
11/10/2023 | 19:25 | EL260C | URBAN | Unknown | Unknown | 48.67 | 256.0 | 0.019208 | 0.0000750 | No
11/10/2023 | 20:44 | WHY10 | URBAN | Third Party | Vehicle impact | 1.00 | 72.0 | 0.000111 | 0.0000015 | No
11/10/2023 | 22:26 | EL11 | URBAN | Weather |  | 97.00 | 247.0 | 0.036939 | 0.0001496 | No
11/10/2023 | 22:32 | MTB21 | SHORT RURAL | Planned |  | 34.00 | 370.0 | 0.088506 | 0.0002392 | No
11/10/2023 | 23:07 | CBD412A | URBAN | Planned |  | 68.00 | 302.4 | 0.031705 | 0.0001048 | No
12/10/2023 | 01:23 | MV42 | SHORT RURAL | Third Party | Vehicle impact | 155.00 | 625.9 | 0.682520 | 0.0010905 | No
12/10/2023 | 06:52 | NL234A | URBAN | Asset failure | LV | 26.33 | 408.0 | 0.016565 | 0.0000406 | No
12/10/2023 | 07:59 | AP214D | URBAN | Other |  | 75.00 | 254.0 | 0.029370 | 0.0001156 | No
12/10/2023 | 08:10 | MG22 | LONG RURAL | Other |  | 1.00 | 112.0 | 0.000804 | 0.0000072 | No
12/10/2023 | 08:30 | PL04 | URBAN | Planned |  | 134.00 | 330.0 | 0.068176 | 0.0002066 | No
12/10/2023 | 08:32 | AP355H | URBAN | Planned |  | 453.00 | 299.2 | 0.208959 | 0.0006984 | No
12/10/2023 | 08:37 | AP149H | URBAN | Asset failure | LV | 1.00 | 488.0 | 0.000752 | 0.0000015 | No
12/10/2023 | 08:40 | AP132B | URBAN | Planned |  | 9.00 | 297.0 | 0.004121 | 0.0000139 | No
12/10/2023 | 08:41 | AP355A | URBAN | Other |  | 11.67 | 252.0 | 0.004533 | 0.0000180 | No
12/10/2023 | 08:42 | SM374B | URBAN | Asset failure | HV | 1,115.00 | 279.8 | 0.480908 | 0.0017191 | No
12/10/2023 | 08:50 | KA19 | LONG RURAL | Planned |  | 4.00 | 48.0 | 0.001378 | 0.0000287 | No
12/10/2023 | 08:52 | CL09 | LONG RURAL | Planned |  | 23.00 | 365.1 | 0.060267 | 0.0001651 | No
12/10/2023 | 08:52 | AP132B | URBAN | Vegetation | Grow-in - NSP responsibility | 3.33 | 468.0 | 0.002405 | 0.0000051 | No
12/10/2023 | 09:07 | GU41 | LONG RURAL | Planned |  | 52.00 | 334.4 | 0.124782 | 0.0003732 | No
12/10/2023 | 09:11 | NL511A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 15.00 | 268.0 | 0.006198 | 0.0000231 | No
12/10/2023 | 09:14 | WK33 | SHORT RURAL | Planned |  | 31.00 | 247.3 | 0.053941 | 0.0002181 | No
12/10/2023 | 09:29 | NL115B | URBAN | Planned |  | 1.00 | 478.0 | 0.000737 | 0.0000015 | No
12/10/2023 | 09:38 | GA05 | SHORT RURAL | Planned |  | 2.00 | 113.0 | 0.001590 | 0.0000141 | No
12/10/2023 | 09:44 | M22 | LONG RURAL | Planned |  | 1.00 | 12.0 | 0.000086 | 0.0000072 | No
12/10/2023 | 09:51 | CN03 | LONG RURAL | Planned |  | 48.00 | 101.0 | 0.034791 | 0.0003445 | No
12/10/2023 | 09:51 | MV34 | SHORT RURAL | Asset failure | LV | 19.33 | 568.0 | 0.077259 | 0.0001360 | No
12/10/2023 | 09:58 | ST41 | LONG RURAL | Other |  | 7.00 | 126.0 | 0.006330 | 0.0000502 | No
12/10/2023 | 10:00 | NU26 | LONG RURAL | Planned |  | 19.00 | 100.0 | 0.013635 | 0.0001364 | No
12/10/2023 | 10:05 | CD02 | LONG RURAL | Planned |  | 24.00 | 300.8 | 0.051799 | 0.0001722 | No
12/10/2023 | 10:22 | MV34 | SHORT RURAL | Third Party | Unauthorised access | 1.00 | 632.0 | 0.004446 | 0.0000070 | No
12/10/2023 | 10:37 | HH432B | URBAN | Asset failure | LV | 124.00 | 68.0 | 0.013000 | 0.0001912 | No
12/10/2023 | 10:37 | CV21 | LONG RURAL | Planned |  | 4.00 | 133.0 | 0.003818 | 0.0000287 | No
12/10/2023 | 10:40 | SM374C | URBAN | Asset failure | LV | 7.00 | 670.0 | 0.007231 | 0.0000108 | No
12/10/2023 | 10:41 | MI10 | LONG RURAL | Other |  | 1.00 | 4.0 | 0.000029 | 0.0000072 | No
12/10/2023 | 10:53 | HH148D | URBAN | Planned |  | 17.00 | 102.0 | 0.002673 | 0.0000262 | No
12/10/2023 | 10:56 | SA42 | URBAN | Overloads |  | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
12/10/2023 | 11:44 | SA14 | URBAN | Planned |  | 375.00 | 13.4 | 0.007766 | 0.0005782 | No
12/10/2023 | 11:54 | HH145B | URBAN | Asset failure | LV | 21.67 | 87.0 | 0.002906 | 0.0000334 | No
12/10/2023 | 11:59 | HH130D | URBAN | Asset failure | LV | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
12/10/2023 | 12:29 | EL10 | URBAN | Planned |  | 843.00 | 11.4 | 0.014812 | 0.0012997 | No
12/10/2023 | 13:31 | GU31 | LONG RURAL | Unknown | Unknown | 26.00 | 196.0 | 0.036571 | 0.0001866 | No
12/10/2023 | 14:12 | MB11 | SHORT RURAL | Asset failure | LV | 1.00 | 307.0 | 0.002160 | 0.0000070 | No
12/10/2023 | 14:26 | SM349A | URBAN | Asset failure | LV | 76.00 | 110.9 | 0.012995 | 0.0001172 | No
12/10/2023 | 15:03 | MB62 | LONG RURAL | Asset failure | LV | 36.00 | 32.0 | 0.008267 | 0.0002583 | No
12/10/2023 | 16:03 | SM216C | URBAN | Asset failure | LV | 1.00 | 399.0 | 0.000615 | 0.0000015 | No
12/10/2023 | 16:33 | HH130C | URBAN | Overloads |  | 1.00 | 478.0 | 0.000737 | 0.0000015 | No
12/10/2023 | 18:31 | HH496D | URBAN | Asset failure | LV | 17.00 | 190.0 | 0.004980 | 0.0000262 | No
12/10/2023 | 19:28 | HH341K | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 94.0 | 0.000145 | 0.0000015 | No
12/10/2023 | 19:33 | VH45 | SHORT RURAL | Asset failure | LV | 1.00 | 132.0 | 0.000929 | 0.0000070 | No
12/10/2023 | 20:36 | NL451C | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
12/10/2023 | 20:50 | NL115E | URBAN | Unknown | Unknown | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
12/10/2023 | 23:00 | SM350C | URBAN | Unknown | Unknown | 4.00 | 49.0 | 0.000302 | 0.0000062 | No
13/10/2023 | 03:58 | EL260D | URBAN | Asset failure | HV | 1,610.00 | 178.2 | 0.442289 | 0.0024822 | No
13/10/2023 | 05:43 | EL260C | URBAN | Unknown | Unknown | 20.00 | 183.0 | 0.005643 | 0.0000308 | No
13/10/2023 | 08:35 | SM172F | URBAN | Asset failure | LV | 48.00 | 130.4 | 0.009647 | 0.0000740 | No
13/10/2023 | 08:42 | KI51 | LONG RURAL | Planned |  | 14.00 | 216.8 | 0.021780 | 0.0001005 | No
13/10/2023 | 08:42 | SB15 | LONG RURAL | Planned |  | 36.00 | 172.9 | 0.044665 | 0.0002583 | No
13/10/2023 | 09:05 | HH428D | URBAN | Planned |  | 124.00 | 348.0 | 0.066530 | 0.0001912 | No
13/10/2023 | 09:11 | ST23 | SHORT RURAL | Planned |  | 32.00 | 162.0 | 0.036472 | 0.0002251 | No
13/10/2023 | 09:25 | MV14 | SHORT RURAL | Asset failure | LV | 5.00 | 35.0 | 0.001231 | 0.0000352 | No
13/10/2023 | 09:40 | CN73 | LONG RURAL | Planned |  | 62.00 | 153.0 | 0.068075 | 0.0004449 | No
13/10/2023 | 09:41 | MB65 | LONG RURAL | Planned |  | 25.00 | 179.0 | 0.032114 | 0.0001794 | No
13/10/2023 | 09:42 | YK12 | LONG RURAL | Planned |  | 17.00 | 217.0 | 0.026473 | 0.0001220 | No
13/10/2023 | 09:54 | GU51 | URBAN | Planned |  | 42.00 | 273.0 | 0.017678 | 0.0000648 | No
13/10/2023 | 10:04 | CN77 | LONG RURAL | Planned |  | 81.00 | 131.0 | 0.076148 | 0.0005813 | No
13/10/2023 | 10:13 | CV08 | LONG RURAL | Planned |  | 11.00 | 103.0 | 0.008131 | 0.0000789 | No
13/10/2023 | 10:17 | NA58 | LONG RURAL | Planned |  | 20.00 | 92.0 | 0.013204 | 0.0001435 | No
13/10/2023 | 11:51 | HH386A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 64.00 | 201.0 | 0.019833 | 0.0000987 | No
13/10/2023 | 12:25 | MG44 | URBAN | Unknown | Unknown | 7.00 | 55.0 | 0.000594 | 0.0000108 | No
13/10/2023 | 12:47 | CN75 | LONG RURAL | Asset failure | HV | 1.00 | 8,603.0 | 0.061738 | 0.0000072 | No
13/10/2023 | 14:51 | EL01Z | URBAN | Unknown | Unknown | 19.00 | 77.0 | 0.002256 | 0.0000293 | No
13/10/2023 | 16:47 | SA31 | URBAN | Asset failure | LV | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
13/10/2023 | 17:56 | NL234C | URBAN | Asset failure | LV | 24.33 | 219.0 | 0.008216 | 0.0000375 | No
13/10/2023 | 18:05 | AP424F | URBAN | Asset failure | LV | 105.00 | 60.0 | 0.009713 | 0.0001619 | No
14/10/2023 | 02:06 | NL21 | URBAN | Asset failure | HV | 617.00 | 227.4 | 0.216314 | 0.0009513 | No
14/10/2023 | 03:05 | MG37 | LONG RURAL | Asset failure | HV | 16.00 | 469.0 | 0.053851 | 0.0001148 | No
14/10/2023 | 08:44 | SM350F | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 47.0 | 0.000072 | 0.0000015 | No
14/10/2023 | 11:38 | EL01Q | URBAN | Third Party | Unauthorised access | 2.00 | 333.0 | 0.001027 | 0.0000031 | No
14/10/2023 | 12:00 | G11 | LONG RURAL | Planned |  | 12.00 | 62.0 | 0.005339 | 0.0000861 | No
14/10/2023 | 12:16 | SA14 | URBAN | Asset failure | LV | 1.00 | 369.0 | 0.000569 | 0.0000015 | No
14/10/2023 | 13:13 | AP355F | URBAN | Asset failure | LV | 1.00 | 274.0 | 0.000422 | 0.0000015 | No
14/10/2023 | 18:04 | GA01 | URBAN | Asset failure | LV | 1.00 | 396.0 | 0.000611 | 0.0000015 | No
14/10/2023 | 20:06 | SA42 | URBAN | Third Party | Vehicle impact | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
14/10/2023 | 21:32 | SM137B | URBAN | Asset failure | LV | 1.00 | 295.0 | 0.000455 | 0.0000015 | No
15/10/2023 | 02:32 | AP125B | URBAN | Weather |  | 333.67 | 76.2 | 0.039211 | 0.0005144 | No
15/10/2023 | 02:48 | SM126C | URBAN | Third Party | Vehicle impact | 145.00 | 708.4 | 0.158361 | 0.0002236 | No
15/10/2023 | 05:53 | CV33 | LONG RURAL | Asset failure | HV | 37.00 | 312.0 | 0.082844 | 0.0002655 | No
15/10/2023 | 07:03 | HH522C | URBAN | Asset failure | LV | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
15/10/2023 | 08:01 | ME231B | URBAN | Planned |  | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
15/10/2023 | 08:39 | HH341B | URBAN | Planned |  | 4.00 | 101.0 | 0.000623 | 0.0000062 | No
15/10/2023 | 08:54 | MI30 | LONG RURAL | Planned |  | 41.00 | 254.0 | 0.074734 | 0.0002942 | No
15/10/2023 | 09:02 | SM349H | URBAN | Planned |  | 31.00 | 512.2 | 0.024482 | 0.0000478 | No
15/10/2023 | 09:40 | GA47 | LONG RURAL | Planned |  | 50.00 | 226.0 | 0.081093 | 0.0003588 | No
15/10/2023 | 10:01 | LX21 | SHORT RURAL | Unknown | Unknown | 18.00 | 187.0 | 0.023681 | 0.0001266 | No
15/10/2023 | 10:06 | LX21 | SHORT RURAL | Unknown | Unknown | 1.00 | 184.0 | 0.001295 | 0.0000070 | No
15/10/2023 | 10:39 | G06 | LONG RURAL | Planned |  | 57.00 | 110.0 | 0.044996 | 0.0004091 | No
15/10/2023 | 11:28 | CV28 | LONG RURAL | Third Party | Vehicle impact | 68.00 | 180.0 | 0.087838 | 0.0004880 | No
15/10/2023 | 11:28 | CV28 | LONG RURAL | Third Party | Vehicle impact | 12.00 | 1,757.0 | 0.151306 | 0.0000861 | No
15/10/2023 | 16:09 | SG13 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 37.00 | 212.2 | 0.055243 | 0.0002603 | No
15/10/2023 | 16:12 | YK16 | LONG RURAL | Asset failure | LV | 1.00 | 306.0 | 0.002196 | 0.0000072 | No
15/10/2023 | 16:21 | MG17 | LONG RURAL | Overloads |  | 1.00 | 118.0 | 0.000847 | 0.0000072 | No
15/10/2023 | 18:14 | SA31 | URBAN | Overloads |  | 1.00 | 157.0 | 0.000242 | 0.0000015 | No
15/10/2023 | 22:28 | GA26 | URBAN | Planned |  | 15.00 | 145.0 | 0.003353 | 0.0000231 | No
15/10/2023 | 23:40 | MTB33 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 108.00 | 163.0 | 0.123853 | 0.0007598 | No
16/10/2023 | 00:34 | GA53 | SHORT RURAL | Asset failure | LV | 2.00 | 359.0 | 0.005051 | 0.0000141 | No
16/10/2023 | 01:45 | HH118C | URBAN | Asset failure | HV | 1,037.00 | 21.0 | 0.033512 | 0.0015988 | No
16/10/2023 | 01:50 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,887.00 | 121.0 | 0.352024 | 0.0029093 | No
16/10/2023 | 03:13 | NL451C | URBAN | Asset failure | LV | 1.00 | 499.0 | 0.000769 | 0.0000015 | No
16/10/2023 | 05:53 | VH34 | SHORT RURAL | Asset failure | LV | 3.00 | 249.0 | 0.005256 | 0.0000211 | No
16/10/2023 | 06:59 | HH145A | URBAN | Asset failure | LV | 1.00 | 226.0 | 0.000348 | 0.0000015 | No
16/10/2023 | 08:26 | NL234C | URBAN | Asset failure | LV | 1.00 | 199.0 | 0.000307 | 0.0000015 | No
16/10/2023 | 08:41 | NU03 | LONG RURAL | Planned |  | 6.00 | 90.0 | 0.003875 | 0.0000431 | No
16/10/2023 | 09:50 | MV54 | SHORT RURAL | Third Party | Vehicle impact | 2.00 | 199.0 | 0.002800 | 0.0000141 | No
16/10/2023 | 09:53 | ST12 | SHORT RURAL | Asset failure | LV | 2.00 | 185.0 | 0.002603 | 0.0000141 | No
16/10/2023 | 10:36 | CN33 | LONG RURAL | Planned |  | 33.00 | 346.0 | 0.081939 | 0.0002368 | No
16/10/2023 | 10:50 | GA05 | SHORT RURAL | Asset failure | LV | 1.00 | 338.0 | 0.002378 | 0.0000070 | No
16/10/2023 | 12:20 | MV52 | SHORT RURAL | Asset failure | HV | 17.33 | 101.9 | 0.012429 | 0.0001219 | No
16/10/2023 | 12:22 | HH432E | URBAN | Asset failure | LV | 2.00 | 618.0 | 0.001906 | 0.0000031 | No
16/10/2023 | 12:23 | SM350E | URBAN | Third Party | Dig-in | 1.00 | 153.0 | 0.000236 | 0.0000015 | No
16/10/2023 | 14:02 | MI16 | LONG RURAL | Unknown | Unknown | 32.00 | 214.0 | 0.049144 | 0.0002296 | No
16/10/2023 | 14:33 | MI32 | LONG RURAL | Overloads |  | 1.00 | 181.0 | 0.001299 | 0.0000072 | No
16/10/2023 | 14:54 | HH386B | URBAN | Asset failure | LV | 30.33 | 214.0 | 0.010008 | 0.0000468 | No
16/10/2023 | 15:09 | SG14 | SHORT RURAL | Asset failure | HV | 31.00 | 60.3 | 0.013156 | 0.0002181 | No
16/10/2023 | 15:50 | AP139D | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
16/10/2023 | 17:11 | HH428F | URBAN | Overloads |  | 4.00 | 1,200.0 | 0.007400 | 0.0000062 | No
16/10/2023 | 17:11 | EL15 | URBAN | Overloads |  | 1.00 | 695.0 | 0.001072 | 0.0000015 | No
16/10/2023 | 17:22 | BU11 | SHORT RURAL | Planned |  | 26.00 | 39.0 | 0.007134 | 0.0001829 | No
16/10/2023 | 18:20 | CN83 | LONG RURAL | Asset failure | HV | 1.00 | 257.0 | 0.001844 | 0.0000072 | No
16/10/2023 | 18:37 | GU21 | LONG RURAL | Overloads |  | 3.00 | 384.0 | 0.008267 | 0.0000215 | No
16/10/2023 | 22:07 | SM126A | URBAN | Planned |  | 1.00 | 309.0 | 0.000476 | 0.0000015 | No
16/10/2023 | 23:15 | SD35300 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 146.0 | 0.001048 | 0.0000072 | No
17/10/2023 | 06:02 | NU25 | LONG RURAL | Asset failure | HV | 23.00 | 334.0 | 0.055129 | 0.0001651 | No
17/10/2023 | 07:34 | MB72 | LONG RURAL | Asset failure | LV | 1.00 | 606.0 | 0.004349 | 0.0000072 | No
17/10/2023 | 07:51 | LX43 | SHORT RURAL | Asset failure | LV | 1.00 | 218.0 | 0.001534 | 0.0000070 | No
17/10/2023 | 08:16 | NL451E | URBAN | Asset failure | LV | 1.00 | 92.0 | 0.000142 | 0.0000015 | No
17/10/2023 | 08:57 | R05 | LONG RURAL | Planned |  | 48.00 | 194.0 | 0.066826 | 0.0003445 | No
17/10/2023 | 08:58 | KI31 | SHORT RURAL | Planned |  | 6.00 | 220.0 | 0.009287 | 0.0000422 | No
17/10/2023 | 09:03 | SD49500 | LONG RURAL | Planned |  | 6.00 | 67.0 | 0.002885 | 0.0000431 | No
17/10/2023 | 09:03 | MG05 | LONG RURAL | Planned |  | 35.00 | 315.0 | 0.079119 | 0.0002512 | No
17/10/2023 | 09:10 | MG04 | SHORT RURAL | Planned |  | 5.00 | 108.0 | 0.003799 | 0.0000352 | No
17/10/2023 | 09:31 | MV31 | SHORT RURAL | Planned |  | 3.00 | 77.0 | 0.001625 | 0.0000211 | No
17/10/2023 | 09:34 | CL19 | LONG RURAL | Asset failure | LV | 1.00 | 171.0 | 0.001227 | 0.0000072 | No
17/10/2023 | 09:42 | EL12 | URBAN | Planned |  | 23.00 | 175.0 | 0.006206 | 0.0000355 | No
17/10/2023 | 10:10 | SD40700 | LONG RURAL | Planned |  | 82.00 | 130.5 | 0.076765 | 0.0005885 | No
17/10/2023 | 10:20 | HH409A | URBAN | Planned |  | 330.00 | 259.9 | 0.132238 | 0.0005088 | No
17/10/2023 | 10:36 | SG13 | SHORT RURAL | Asset failure | LV | 2.00 | 119.0 | 0.001674 | 0.0000141 | No
17/10/2023 | 10:40 | MB33 | LONG RURAL | Planned |  | 54.00 | 284.0 | 0.110056 | 0.0003875 | No
17/10/2023 | 10:53 | GU41 | LONG RURAL | Planned |  | 60.00 | 189.0 | 0.081380 | 0.0004306 | No
17/10/2023 | 11:06 | M04 | LONG RURAL | Planned |  | 67.00 | 204.0 | 0.098086 | 0.0004808 | No
17/10/2023 | 11:09 | CV08 | LONG RURAL | Planned |  | 51.00 | 328.0 | 0.120046 | 0.0003660 | No
17/10/2023 | 11:49 | SM126A | URBAN | Third Party | Vehicle impact | 417.00 | 124.8 | 0.080231 | 0.0006429 | No
17/10/2023 | 12:03 | MG52 | URBAN | Overloads |  | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
17/10/2023 | 13:22 | MB63 | LONG RURAL | Planned |  | 2.00 | 86.0 | 0.001234 | 0.0000144 | No
17/10/2023 | 13:41 | HH118C | URBAN | Asset failure | HV | 80.00 | 199.0 | 0.024545 | 0.0001233 | No
17/10/2023 | 14:34 | NL451A | URBAN | Asset failure | LV | 1.00 | 616.0 | 0.000950 | 0.0000015 | No
17/10/2023 | 14:52 | VH21 | SHORT RURAL | Asset failure | LV | 31.67 | 64.0 | 0.014259 | 0.0002228 | No
17/10/2023 | 15:04 | MI17 | LONG RURAL | Asset failure | HV | 1.00 | 14.0 | 0.000100 | 0.0000072 | No
17/10/2023 | 15:22 | EL23 | URBAN | Asset failure | LV | 1.00 | 400.0 | 0.000617 | 0.0000015 | No
17/10/2023 | 15:46 | SM179D | URBAN | Unknown | Unknown | 34.00 | 142.0 | 0.007444 | 0.0000524 | No
17/10/2023 | 15:59 | KI31 | SHORT RURAL | Asset failure | HV | 173.00 | 177.0 | 0.215434 | 0.0012171 | No
17/10/2023 | 17:48 | MT01 | LONG RURAL | Asset failure | LV | 2.00 | 309.0 | 0.004435 | 0.0000144 | No
17/10/2023 | 18:23 | CN21 | LONG RURAL | Asset failure | HV | 151.00 | 60.0 | 0.065018 | 0.0010836 | No
17/10/2023 | 18:31 | NL210D | URBAN | Asset failure | LV | 5.33 | 230.0 | 0.001891 | 0.0000082 | No
17/10/2023 | 19:02 | HK05 | LONG RURAL | Asset failure | HV | 21.00 | 32.9 | 0.004959 | 0.0001507 | No
17/10/2023 | 19:34 | AP424E | URBAN | Asset failure | LV | 1.00 | 281.0 | 0.000433 | 0.0000015 | No
17/10/2023 | 19:37 | GA53 | SHORT RURAL | Weather |  | 12.00 | 231.8 | 0.019566 | 0.0000844 | No
17/10/2023 | 21:59 | HH148D | URBAN | Planned |  | 5.00 | 436.8 | 0.003367 | 0.0000077 | No
17/10/2023 | 22:05 | SM411D | URBAN | Planned |  | 14.00 | 331.0 | 0.007144 | 0.0000216 | No
18/10/2023 | 01:45 | AP355A | URBAN | Unknown | Unknown | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
18/10/2023 | 02:09 | AP146D | URBAN | Unknown | Unknown | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
18/10/2023 | 05:08 | GA09 | LONG RURAL | Unknown | Unknown | 118.33 | 245.0 | 0.208054 | 0.0008492 | No
18/10/2023 | 08:17 | G07 | LONG RURAL | Unknown | Unknown | 28.00 | 195.0 | 0.039183 | 0.0002009 | No
18/10/2023 | 08:30 | HH341E | URBAN | Asset failure | LV | 48.00 | 160.0 | 0.011841 | 0.0000740 | No
18/10/2023 | 08:38 | ME131B | URBAN | Planned |  | 82.00 | 296.0 | 0.037421 | 0.0001264 | No
18/10/2023 | 08:54 | LX51 | SHORT RURAL | Planned |  | 57.00 | 314.4 | 0.126090 | 0.0004010 | No
18/10/2023 | 08:59 | NU15 | LONG RURAL | Planned |  | 176.00 | 361.0 | 0.455955 | 0.0012630 | No
18/10/2023 | 09:17 | R24 | LONG RURAL | Planned |  | 31.00 | 306.0 | 0.068075 | 0.0002225 | No
18/10/2023 | 09:23 | BT02 | LONG RURAL | Planned |  | 11.00 | 157.0 | 0.012394 | 0.0000789 | No
18/10/2023 | 09:24 | SB17 | LONG RURAL | Planned |  | 2.00 | 141.0 | 0.002024 | 0.0000144 | No
18/10/2023 | 09:27 | SM410C | URBAN | Asset failure | LV | 2.00 | 103.0 | 0.000318 | 0.0000031 | No
18/10/2023 | 09:38 | MI07 | LONG RURAL | Planned |  | 77.00 | 275.0 | 0.151959 | 0.0005526 | No
18/10/2023 | 09:42 | LM43 | LONG RURAL | Planned |  | 48.00 | 84.4 | 0.029078 | 0.0003445 | No
18/10/2023 | 09:49 | PL12 | LONG RURAL | Planned |  | 279.00 | 176.9 | 0.354152 | 0.0020022 | No
18/10/2023 | 09:55 | MTB61 | SHORT RURAL | Planned |  | 27.00 | 81.0 | 0.015387 | 0.0001900 | No
18/10/2023 | 10:12 | MT02 | LONG RURAL | Planned |  | 127.00 | 281.0 | 0.256102 | 0.0009114 | No
18/10/2023 | 10:14 | HH429C | URBAN | Overloads |  | 1.00 | 202.0 | 0.000311 | 0.0000015 | No
18/10/2023 | 10:33 | ST15 | SHORT RURAL | Asset failure | HV | 30.00 | 160.0 | 0.033770 | 0.0002111 | No
18/10/2023 | 10:38 | YK27 | LONG RURAL | Planned |  | 100.00 | 83.0 | 0.059564 | 0.0007176 | No
18/10/2023 | 10:42 | MI12 | LONG RURAL | Planned |  | 13.00 | 111.0 | 0.010355 | 0.0000933 | No
18/10/2023 | 10:47 | PA14 | LONG RURAL | Planned |  | 7.00 | 43.0 | 0.002160 | 0.0000502 | No
18/10/2023 | 10:49 | MG19 | LONG RURAL | Asset failure | HV | 433.00 | 105.0 | 0.326157 | 0.0031074 | No
18/10/2023 | 10:55 | G11 | LONG RURAL | Planned |  | 21.00 | 148.0 | 0.022304 | 0.0001507 | No
18/10/2023 | 11:09 | AP424A | URBAN | Asset failure | HV | 1,984.00 | 229.7 | 0.702680 | 0.0030588 | No
18/10/2023 | 13:22 | MT25 | LONG RURAL | Planned |  | 20.00 | 119.0 | 0.017080 | 0.0001435 | No
18/10/2023 | 13:46 | AP139B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 105.00 | 64.0 | 0.010361 | 0.0001619 | No
18/10/2023 | 14:53 | HH148C | URBAN | Asset failure | LV | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
18/10/2023 | 14:54 | GA22 | SHORT RURAL | Asset failure | LV | 1.00 | 437.0 | 0.003075 | 0.0000070 | No
18/10/2023 | 16:01 | SA520D | URBAN | Asset failure | LV | 1.00 | 325.0 | 0.000501 | 0.0000015 | No
18/10/2023 | 16:07 | WK65 | SHORT RURAL | Animal | Animal impact | 43.67 | 155.0 | 0.047619 | 0.0003072 | No
18/10/2023 | 16:11 | HH177D | URBAN | Asset failure | LV | 1.00 | 318.0 | 0.000490 | 0.0000015 | No
18/10/2023 | 17:01 | AP227B | URBAN | Overloads |  | 1.00 | 283.0 | 0.000436 | 0.0000015 | No
18/10/2023 | 17:10 | HH121H | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | No
18/10/2023 | 17:27 | SD35200 | LONG RURAL | Asset failure | Subtransmission | 5.00 | 201.0 | 0.007212 | 0.0000359 | No
18/10/2023 | 17:51 | HH177C | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
18/10/2023 | 19:01 | WHY01 | SHORT RURAL | Overloads |  | 1.00 | 107.0 | 0.000753 | 0.0000070 | No
18/10/2023 | 20:19 | EL09 | URBAN | Asset failure | LV | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
18/10/2023 | 22:41 | CBD412H | URBAN | Planned |  | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
19/10/2023 | 03:42 | SM126C | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
19/10/2023 | 03:54 | SM126C | URBAN | Animal | Animal impact | 34.67 | 155.0 | 0.008284 | 0.0000534 | No
19/10/2023 | 07:39 | SA711C | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
19/10/2023 | 08:22 | KA04 | LONG RURAL | Planned |  | 70.00 | 2,436.3 | 1.223858 | 0.0005023 | No
19/10/2023 | 08:32 | HH386F | URBAN | Asset failure | LV | 9.00 | 47.0 | 0.000652 | 0.0000139 | No
19/10/2023 | 08:40 | EL19 | URBAN | Animal | Animal impact | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
19/10/2023 | 08:53 | LX42 | SHORT RURAL | Planned |  | 33.00 | 205.9 | 0.047799 | 0.0002322 | No
19/10/2023 | 08:53 | GA01 | URBAN | Planned |  | 34.00 | 129.2 | 0.006771 | 0.0000524 | No
19/10/2023 | 09:06 | SM126D | URBAN | Planned |  | 99.00 | 150.0 | 0.022895 | 0.0001526 | No
19/10/2023 | 09:08 | CL09 | LONG RURAL | Planned |  | 79.00 | 419.1 | 0.237580 | 0.0005669 | No
19/10/2023 | 09:10 | MB21 | URBAN | Asset failure | LV | 1.00 | 417.0 | 0.000643 | 0.0000015 | No
19/10/2023 | 09:21 | LM51 | LONG RURAL | Planned |  | 13.00 | 97.0 | 0.009049 | 0.0000933 | No
19/10/2023 | 09:26 | MV22 | SHORT RURAL | Planned |  | 8.00 | 149.0 | 0.008386 | 0.0000563 | No
19/10/2023 | 09:27 | MV64 | SHORT RURAL | Planned |  | 281.00 | 329.4 | 0.651184 | 0.0019770 | No
19/10/2023 | 09:33 | M83 | LONG RURAL | Planned |  | 91.00 | 160.0 | 0.104487 | 0.0006530 | No
19/10/2023 | 09:39 | GA27 | LONG RURAL | Planned |  | 14.00 | 66.9 | 0.006717 | 0.0001005 | No
19/10/2023 | 09:43 | MI10 | LONG RURAL | Planned |  | 53.00 | 214.0 | 0.081394 | 0.0003803 | No
19/10/2023 | 09:52 | CN01 | LONG RURAL | Planned |  | 12.00 | 196.0 | 0.016879 | 0.0000861 | No
19/10/2023 | 09:56 | WK72 | SHORT RURAL | Unknown | Unknown | 2.00 | 341.0 | 0.004798 | 0.0000141 | No
19/10/2023 | 10:00 | GA53 | SHORT RURAL | Planned |  | 7.00 | 138.0 | 0.006796 | 0.0000492 | No
19/10/2023 | 10:06 | VH13 | SHORT RURAL | Planned |  | 4.00 | 108.0 | 0.003039 | 0.0000281 | No
19/10/2023 | 10:06 | KI55 | LONG RURAL | Planned |  | 2.00 | 169.0 | 0.002426 | 0.0000144 | No
19/10/2023 | 10:23 | NA04 | LONG RURAL | Planned |  | 1.00 | 33.0 | 0.000237 | 0.0000072 | No
19/10/2023 | 10:23 | R36 | SHORT RURAL | Planned |  | 1.00 | 57.0 | 0.000401 | 0.0000070 | No
19/10/2023 | 10:48 | LM64 | LONG RURAL | Asset failure | LV | 2.00 | 272.0 | 0.003904 | 0.0000144 | No
19/10/2023 | 10:53 | ST44 | LONG RURAL | Asset failure | LV | 1.00 | 248.0 | 0.001780 | 0.0000072 | No
19/10/2023 | 11:02 | MT25 | LONG RURAL | Planned |  | 16.00 | 158.0 | 0.018142 | 0.0001148 | No
19/10/2023 | 11:32 | HH496A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 155.0 | 0.000239 | 0.0000015 | No
19/10/2023 | 11:41 | GA25 | SHORT RURAL | Asset failure | LV | 19.00 | 49.0 | 0.006550 | 0.0001337 | No
19/10/2023 | 11:57 | SM126D | URBAN | Planned |  | 68.00 | 58.0 | 0.006081 | 0.0001048 | No
19/10/2023 | 12:04 | SM411A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 112.00 | 89.0 | 0.015368 | 0.0001727 | No
19/10/2023 | 12:32 | HH107C | URBAN | Asset failure | LV | 35.00 | 102.0 | 0.005504 | 0.0000540 | No
19/10/2023 | 12:42 | AP139C | URBAN | Third Party | Vehicle impact | 13.00 | 387.0 | 0.007757 | 0.0000200 | No
19/10/2023 | 13:10 | ST44 | LONG RURAL | Planned |  | 7.00 | 98.0 | 0.004923 | 0.0000502 | No
19/10/2023 | 13:15 | BM43 | SHORT RURAL | Asset failure | LV | 1.00 | 131.0 | 0.000922 | 0.0000070 | No
19/10/2023 | 13:17 | G20 | LONG RURAL | Asset failure | LV | 1.00 | 451.0 | 0.003237 | 0.0000072 | No
19/10/2023 | 13:37 | HH432C | URBAN | Unknown | Unknown | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
19/10/2023 | 13:41 | MG23 | SHORT RURAL | Unknown | Unknown | 1.00 | 5.0 | 0.000035 | 0.0000070 | No
19/10/2023 | 14:00 | CL04 | LONG RURAL | Unknown | Unknown | 181.00 | 132.0 | 0.171414 | 0.0012989 | No
19/10/2023 | 14:12 | BM42 | SHORT RURAL | Overloads |  | 2.00 | 26.0 | 0.000366 | 0.0000141 | No
19/10/2023 | 14:22 | MT15 | LONG RURAL | Planned |  | 5.00 | 97.0 | 0.003481 | 0.0000359 | No
19/10/2023 | 16:25 | KI51 | LONG RURAL | Asset failure | HV | 14.00 | 96.0 | 0.009645 | 0.0001005 | No
19/10/2023 | 17:58 | KA01 | SHORT RURAL | Asset failure | LV | 18.00 | 153.0 | 0.019376 | 0.0001266 | No
19/10/2023 | 18:28 | HH341G | URBAN | Asset failure | LV | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
19/10/2023 | 18:36 | HH145B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,745.00 | 57.0 | 0.153351 | 0.0026904 | No
19/10/2023 | 22:32 | SA711C | URBAN | Planned |  | 4.00 | 194.8 | 0.001201 | 0.0000062 | No
20/10/2023 | 04:25 | R04 | LONG RURAL | Unknown | Unknown | 48.00 | 441.8 | 0.152167 | 0.0003445 | No
20/10/2023 | 05:35 | HH341E | URBAN | Animal | Animal impact | 1,056.67 | 9.7 | 0.015736 | 0.0016291 | No
20/10/2023 | 07:36 | VH15 | SHORT RURAL | Asset failure | LV | 25.33 | 154.0 | 0.027448 | 0.0001782 | No
20/10/2023 | 08:06 | HH522A | URBAN | Planned |  | 49.00 | 372.0 | 0.028103 | 0.0000755 | No
20/10/2023 | 08:31 | AP372B | URBAN | Asset failure | LV | 19.33 | 121.0 | 0.003607 | 0.0000298 | No
20/10/2023 | 08:39 | SA36 | URBAN | Planned |  | 51.00 | 266.0 | 0.020915 | 0.0000786 | No
20/10/2023 | 08:39 | MG05 | LONG RURAL | Third Party | Vehicle impact | 10.00 | 54.8 | 0.003933 | 0.0000718 | No
20/10/2023 | 08:41 | LM51 | LONG RURAL | Planned |  | 16.00 | 140.0 | 0.016075 | 0.0001148 | No
20/10/2023 | 08:57 | WK43 | SHORT RURAL | Planned |  | 11.00 | 117.5 | 0.009090 | 0.0000774 | No
20/10/2023 | 09:15 | PA15 | LONG RURAL | Planned |  | 1.00 | 27.0 | 0.000194 | 0.0000072 | No
20/10/2023 | 09:31 | G09 | LONG RURAL | Planned |  | 18.00 | 371.0 | 0.047924 | 0.0001292 | No
20/10/2023 | 09:38 | MV14 | SHORT RURAL | Planned |  | 26.00 | 133.0 | 0.024329 | 0.0001829 | No
20/10/2023 | 09:41 | MTB32 | LONG RURAL | Planned |  | 10.00 | 266.0 | 0.019089 | 0.0000718 | No
20/10/2023 | 09:54 | ST41 | LONG RURAL | Planned |  | 100.00 | 120.0 | 0.086116 | 0.0007176 | No
20/10/2023 | 10:05 | MV62 | SHORT RURAL | Planned |  | 19.00 | 101.0 | 0.013501 | 0.0001337 | No
20/10/2023 | 10:09 | YK07 | LONG RURAL | Planned |  | 1.00 | 130.0 | 0.000933 | 0.0000072 | No
20/10/2023 | 10:13 | W01 | LONG RURAL | Unknown | Unknown | 1.00 | 5,605.0 | 0.040223 | 0.0000072 | No
20/10/2023 | 10:27 | CN43 | LONG RURAL | Planned |  | 26.00 | 177.0 | 0.033025 | 0.0001866 | No
20/10/2023 | 10:33 | HH130E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 3,303.00 | 143.7 | 0.731960 | 0.0050924 | No
20/10/2023 | 10:38 | CV757A | LONG RURAL | Asset failure | LV | 68.00 | 203.0 | 0.099062 | 0.0004880 | No
20/10/2023 | 10:40 | HH130E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 297.0 | 0.000458 | 0.0000015 | No
20/10/2023 | 12:52 | AP227B | URBAN | Overloads |  | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
20/10/2023 | 12:58 | HH107D | URBAN | Third Party | Vehicle impact | 3.00 | 115.0 | 0.000532 | 0.0000046 | No
20/10/2023 | 13:53 | GA30 | LONG RURAL | Overloads |  | 12.00 | 22.0 | 0.001895 | 0.0000861 | No
20/10/2023 | 13:58 | HH341G | URBAN | Asset failure | LV | 108.00 | 191.0 | 0.031803 | 0.0001665 | No
20/10/2023 | 16:02 | HH130E | URBAN | Overloads |  | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
20/10/2023 | 16:25 | MV14 | SHORT RURAL | Other |  | 1.00 | 9.0 | 0.000063 | 0.0000070 | No
20/10/2023 | 17:17 | HH145A | URBAN | Overloads |  | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
20/10/2023 | 17:45 | PL29 | LONG RURAL | Weather |  | 36.00 | 75.6 | 0.019520 | 0.0002583 | No
20/10/2023 | 17:46 | SA19 | URBAN | Asset failure | LV | 42.00 | 118.0 | 0.007641 | 0.0000648 | No
20/10/2023 | 19:21 | HH130F | URBAN | Asset failure | LV | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
20/10/2023 | 20:00 | BT06 | LONG RURAL | Asset failure | LV | 21.00 | 174.0 | 0.026222 | 0.0001507 | No
20/10/2023 | 21:28 | AP146B | URBAN | Asset failure | LV | 1.00 | 214.0 | 0.000330 | 0.0000015 | No
20/10/2023 | 22:00 | SM172F | URBAN | Asset failure | LV | 2.00 | 243.0 | 0.000749 | 0.0000031 | No
21/10/2023 | 00:23 | WHY04 | URBAN | Third Party | Vehicle impact | 1,109.00 | 160.7 | 0.274808 | 0.0017098 | No
21/10/2023 | 07:50 | SM411C | URBAN | Unknown | Unknown | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
21/10/2023 | 08:22 | NU06 | LONG RURAL | Weather |  | 803.00 | 133.9 | 0.771685 | 0.0057626 | No
21/10/2023 | 08:33 | MTB51 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 547.0 | 0.003925 | 0.0000072 | No
21/10/2023 | 08:55 | MV53 | SHORT RURAL | Planned |  | 26.00 | 144.7 | 0.026460 | 0.0001829 | No
21/10/2023 | 09:07 | NL111C | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
21/10/2023 | 09:53 | MG34 | LONG RURAL | Asset failure | LV | 2.00 | 124.0 | 0.001780 | 0.0000144 | No
21/10/2023 | 10:37 | HH341J | URBAN | Asset failure | LV | 80.00 | 49.0 | 0.006044 | 0.0001233 | No
21/10/2023 | 11:17 | AP425D | URBAN | Asset failure | LV | 1.00 | 371.0 | 0.000572 | 0.0000015 | No
21/10/2023 | 12:10 | SM137A | URBAN | Asset failure | LV | 19.67 | 202.0 | 0.006125 | 0.0000303 | No
21/10/2023 | 12:15 | AP149H | URBAN | Asset failure | LV | 61.00 | 202.0 | 0.018997 | 0.0000940 | No
21/10/2023 | 12:18 | SM137A | URBAN | Third Party | Other | 71.33 | 120.0 | 0.013197 | 0.0001100 | No
21/10/2023 | 12:33 | CV25 | LONG RURAL | Asset failure | HV | 57.00 | 9.0 | 0.003681 | 0.0004091 | No
21/10/2023 | 12:50 | HH118D | URBAN | Unknown | Unknown | 6.33 | 188.0 | 0.001836 | 0.0000098 | No
21/10/2023 | 13:00 | NU04 | LONG RURAL | Unknown | Unknown | 3.00 | 87.7 | 0.001887 | 0.0000215 | No
21/10/2023 | 13:00 | NU04 | SHORT RURAL | Unknown | Unknown | 598.00 | 68.7 | 0.289004 | 0.0042072 | No
21/10/2023 | 13:13 | SM172A | URBAN | Overloads |  | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
21/10/2023 | 13:34 | HH130B | URBAN | Overloads |  | 1.00 | 404.0 | 0.000623 | 0.0000015 | No
21/10/2023 | 13:34 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 9,209.0 | 0.014198 | 0.0000015 | No
21/10/2023 | 13:39 | HH145E | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
21/10/2023 | 14:47 | HH341K | URBAN | Unknown | Unknown | 77.00 | 108.0 | 0.012821 | 0.0001187 | No
21/10/2023 | 14:51 | HH118B | URBAN | Unknown | Unknown | 2.00 | 129.0 | 0.000398 | 0.0000031 | No
21/10/2023 | 14:58 | BM55 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 66.00 | 71.0 | 0.032968 | 0.0004643 | No
21/10/2023 | 15:01 | HH341K | URBAN | Unknown | Unknown | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
21/10/2023 | 15:06 | MTB51 | LONG RURAL | Third Party | Other | 14.00 | 153.0 | 0.015372 | 0.0001005 | No
21/10/2023 | 15:14 | AP226C | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
21/10/2023 | 15:21 | SG07 | SHORT RURAL | Asset failure | LV | 2.00 | 237.0 | 0.003335 | 0.0000141 | No
21/10/2023 | 16:15 | W04 | LONG RURAL | Asset failure | LV | 1.00 | 313.0 | 0.002246 | 0.0000072 | No
21/10/2023 | 16:53 | HH432B | URBAN | Asset failure | LV | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
21/10/2023 | 17:03 | SM179C | URBAN | Third Party | Other | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
21/10/2023 | 18:09 | SD39300 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 136.0 | 0.000976 | 0.0000072 | No
21/10/2023 | 18:42 | M13 | LONG RURAL | Asset failure | LV | 13.33 | 220.0 | 0.021051 | 0.0000957 | No
21/10/2023 | 19:05 | WHY04 | URBAN | Asset failure | LV | 43.00 | 38.0 | 0.002519 | 0.0000663 | No
21/10/2023 | 20:16 | SM350C | URBAN | Third Party | Vehicle impact | 33.00 | 137.0 | 0.006970 | 0.0000509 | No
21/10/2023 | 21:38 | HH102D | URBAN | Asset failure | LV | 56.00 | 82.0 | 0.007080 | 0.0000863 | No
21/10/2023 | 22:07 | EL10 | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
21/10/2023 | 22:40 | SM350H | URBAN | Third Party | Vehicle impact | 1.00 | 60.0 | 0.000093 | 0.0000015 | No
22/10/2023 | 02:28 | CV24 | LONG RURAL | Asset failure | HV | 84.00 | 572.2 | 0.344909 | 0.0006028 | No
22/10/2023 | 03:12 | HH121A | URBAN | Animal | Animal impact | 1,143.00 | 63.0 | 0.111020 | 0.0017622 | No
22/10/2023 | 05:11 | VH15 | SHORT RURAL | Asset failure | LV | 1.00 | 300.0 | 0.002111 | 0.0000070 | No
22/10/2023 | 05:24 | MG19 | LONG RURAL | Weather |  | 287.00 | 264.0 | 0.543736 | 0.0020596 | No
22/10/2023 | 06:38 | NL451C | URBAN | Planned |  | 137.00 | 131.4 | 0.027745 | 0.0002112 | No
22/10/2023 | 06:40 | GA745B | SHORT RURAL | Third Party | Unauthorised access | 1.00 | 73.0 | 0.000514 | 0.0000070 | No
22/10/2023 | 08:03 | KA11 | LONG RURAL | Planned |  | 31.00 | 244.0 | 0.054282 | 0.0002225 | No
22/10/2023 | 08:05 | AP139C | URBAN | Planned |  | 49.00 | 89.0 | 0.006724 | 0.0000755 | No
22/10/2023 | 08:34 | MI23 | LONG RURAL | Planned |  | 90.00 | 276.0 | 0.178260 | 0.0006459 | No
22/10/2023 | 08:42 | CM05 | LONG RURAL | Planned |  | 1,143.00 | 347.1 | 2.847316 | 0.0082025 | No
22/10/2023 | 09:08 | ME131E | URBAN | Planned |  | 7.00 | 281.3 | 0.003036 | 0.0000108 | No
22/10/2023 | 09:18 | GU34 | LONG RURAL | Planned |  | 93.00 | 153.0 | 0.102112 | 0.0006674 | No
22/10/2023 | 10:30 | MB66 | LONG RURAL | Planned |  | 44.00 | 147.0 | 0.046416 | 0.0003158 | No
22/10/2023 | 12:32 | AP829B | URBAN | Third Party | Unauthorised access | 2.00 | 27.0 | 0.000083 | 0.0000031 | No
22/10/2023 | 13:07 | SA33 | URBAN | Asset failure | LV | 1.00 | 299.0 | 0.000461 | 0.0000015 | No
22/10/2023 | 15:03 | BM56 | SHORT RURAL | Asset failure | HV | 246.33 | 27.8 | 0.048144 | 0.0017331 | No
22/10/2023 | 15:09 | HH177D | URBAN | Asset failure | HV | 672.00 | 72.9 | 0.075480 | 0.0010361 | No
22/10/2023 | 15:11 | SA33 | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
22/10/2023 | 16:49 | VH32 | SHORT RURAL | Weather |  | 7.00 | 38.0 | 0.001871 | 0.0000492 | No
22/10/2023 | 16:59 | AP529D | URBAN | Weather |  | 1,482.00 | 113.6 | 0.259613 | 0.0022849 | No
22/10/2023 | 17:25 | NL760B | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
22/10/2023 | 17:59 | HH177C | URBAN | Asset failure | LV | 1.00 | 156.0 | 0.000241 | 0.0000015 | No
22/10/2023 | 18:13 | MG37 | LONG RURAL | Asset failure | LV | 1.00 | 286.0 | 0.002052 | 0.0000072 | No
22/10/2023 | 21:33 | AP351D | URBAN | Asset failure | LV | 2.00 | 269.0 | 0.000829 | 0.0000031 | No
22/10/2023 | 22:09 | NL760A | URBAN | Planned |  | 405.00 | 333.0 | 0.207952 | 0.0006244 | No
23/10/2023 | 00:19 | ME347A | URBAN | Asset failure | LV | 21.00 | 57.0 | 0.001845 | 0.0000324 | No
23/10/2023 | 04:35 | NU15 | LONG RURAL | Animal | Animal impact | 1.00 | 313.0 | 0.002246 | 0.0000072 | No
23/10/2023 | 06:39 | HH121D | URBAN | Overloads |  | 5.33 | 137.0 | 0.001127 | 0.0000082 | No
23/10/2023 | 06:42 | SM126C | URBAN | Unknown | Unknown | 7.00 | 189.0 | 0.002040 | 0.0000108 | No
23/10/2023 | 07:30 | BU06 | LONG RURAL | Animal | Animal impact | 528.00 | 209.7 | 0.794535 | 0.0037891 | No
23/10/2023 | 07:30 | BU06 | SHORT RURAL | Animal | Animal impact | 1.00 | 230.0 | 0.001618 | 0.0000070 | No
23/10/2023 | 07:49 | SG01 | SHORT RURAL | Animal | Animal impact | 2.00 | 135.0 | 0.001900 | 0.0000141 | No
23/10/2023 | 08:50 | KA20 | LONG RURAL | Planned |  | 4.00 | 137.0 | 0.003933 | 0.0000287 | No
23/10/2023 | 09:05 | AP529C | URBAN | Asset failure | LV | 56.00 | 216.6 | 0.018697 | 0.0000863 | No
23/10/2023 | 09:06 | WK21 | SHORT RURAL | Planned |  | 83.00 | 94.0 | 0.054891 | 0.0005839 | No
23/10/2023 | 09:14 | KI21 | LONG RURAL | Planned |  | 15.00 | 229.7 | 0.024722 | 0.0001076 | No
23/10/2023 | 09:17 | CL03 | LONG RURAL | Planned |  | 1.00 | 338.0 | 0.002426 | 0.0000072 | No
23/10/2023 | 09:20 | NU07 | LONG RURAL | Planned |  | 30.00 | 161.0 | 0.034662 | 0.0002153 | No
23/10/2023 | 09:22 | PL803A | URBAN | Planned |  | 60.00 | 313.0 | 0.028954 | 0.0000925 | No
23/10/2023 | 09:24 | NU35 | LONG RURAL | Other |  | 32.00 | 197.0 | 0.045240 | 0.0002296 | No
23/10/2023 | 09:28 | EL15 | URBAN | Planned |  | 1.00 | 11,020.0 | 0.016990 | 0.0000015 | No
23/10/2023 | 09:46 | HH409A | URBAN | Planned |  | 47.00 | 291.0 | 0.021087 | 0.0000725 | No
23/10/2023 | 09:48 | HH428D | URBAN | Planned |  | 57.00 | 235.0 | 0.020652 | 0.0000879 | No
23/10/2023 | 10:36 | LM14 | LONG RURAL | Planned |  | 53.00 | 87.0 | 0.033090 | 0.0003803 | No
23/10/2023 | 10:50 | CBD103C | URBAN | Planned |  | 170.00 | 1,485.2 | 0.389277 | 0.0002621 | No
23/10/2023 | 10:56 | R31 | LONG RURAL | Planned |  | 16.00 | 185.0 | 0.021242 | 0.0001148 | No
23/10/2023 | 11:02 | CN41 | LONG RURAL | Planned |  | 16.00 | 95.0 | 0.010908 | 0.0001148 | No
23/10/2023 | 11:21 | MG10 | LONG RURAL | Planned |  | 1.00 | 56.0 | 0.000402 | 0.0000072 | No
23/10/2023 | 11:22 | HH432C | URBAN | Unknown | Unknown | 1.00 | 49.0 | 0.000076 | 0.0000015 | No
23/10/2023 | 11:30 | SSD184 | SHORT RURAL | Network business | Switching and protection error | 172.00 | 4.0 | 0.004840 | 0.0012101 | No
23/10/2023 | 11:30 | SSD184 | URBAN | Network business | Switching and protection error | 1,643.00 | 4.0 | 0.010132 | 0.0025331 | No
23/10/2023 | 12:09 | SA33 | URBAN | Overloads |  | 1.00 | 122.0 | 0.000188 | 0.0000015 | No
23/10/2023 | 12:48 | HH177A | URBAN | Asset failure | LV | 2.00 | 145.0 | 0.000447 | 0.0000031 | No
23/10/2023 | 14:42 | GU31 | LONG RURAL | Asset failure | HV | 1.00 | 92.0 | 0.000660 | 0.0000072 | No
23/10/2023 | 15:17 | EL19 | URBAN | Unknown | Unknown | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
23/10/2023 | 15:32 | AP355A | URBAN | Overloads |  | 47.67 | 152.0 | 0.011171 | 0.0000735 | No
23/10/2023 | 18:04 | MG02 | LONG RURAL | Overloads |  | 3.00 | 187.0 | 0.004026 | 0.0000215 | No
23/10/2023 | 19:25 | M83 | LONG RURAL | Planned |  | 8.00 | 25.0 | 0.001435 | 0.0000574 | No
23/10/2023 | 20:29 | SD39300 | LONG RURAL | Overloads |  | 10.67 | 113.0 | 0.008650 | 0.0000765 | No
23/10/2023 | 21:53 | AP149E | URBAN | Overloads |  | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
23/10/2023 | 22:04 | HH107E | URBAN | Third Party | Other | 1.00 | 66.0 | 0.000102 | 0.0000015 | No
23/10/2023 | 22:27 | VH71 | SHORT RURAL | Planned |  | 355.00 | 289.0 | 0.721806 | 0.0024976 | No
24/10/2023 | 00:13 | HH386B | URBAN | Overloads |  | 7.00 | 177.0 | 0.001910 | 0.0000108 | No
24/10/2023 | 01:58 | HH148D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 443.00 | 214.9 | 0.146784 | 0.0006830 | No
24/10/2023 | 03:32 | HH130A | URBAN | Asset failure | LV | 14.67 | 131.0 | 0.002962 | 0.0000226 | No
24/10/2023 | 04:20 | MTB32 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 63.00 | 182.0 | 0.082284 | 0.0004521 | No
24/10/2023 | 04:20 | MTB32 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 182.0 | 0.001280 | 0.0000070 | No
24/10/2023 | 05:06 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 214.00 | 250.3 | 0.376919 | 0.0015056 | No
24/10/2023 | 06:20 | SA31 | URBAN | Asset failure | LV | 3.67 | 232.0 | 0.001312 | 0.0000057 | No
24/10/2023 | 07:04 | MV22 | SHORT RURAL | Unknown | Unknown | 83.00 | 409.0 | 0.238834 | 0.0005839 | No
24/10/2023 | 07:05 | HH145E | URBAN | Animal | Animal nesting/burrowing, etc and other | 709.00 | 52.2 | 0.057074 | 0.0010931 | No
24/10/2023 | 07:32 | MG05 | LONG RURAL | Weather |  | 116.00 | 94.3 | 0.078459 | 0.0008325 | No
24/10/2023 | 07:54 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 337.0 | 0.002371 | 0.0000070 | No
24/10/2023 | 08:23 | MTB53 | LONG RURAL | Planned |  | 95.00 | 357.0 | 0.243385 | 0.0006818 | No
24/10/2023 | 08:50 | WHY12 | URBAN | Animal | Animal impact | 50.67 | 64.0 | 0.004999 | 0.0000781 | No
24/10/2023 | 09:04 | SG08 | SHORT RURAL | Planned |  | 9.00 | 34.0 | 0.002153 | 0.0000633 | No
24/10/2023 | 09:05 | MV31 | SHORT RURAL | Planned |  | 111.00 | 216.0 | 0.168683 | 0.0007809 | No
24/10/2023 | 09:08 | MTB32 | LONG RURAL | Planned |  | 60.00 | 147.0 | 0.063295 | 0.0004306 | No
24/10/2023 | 09:08 | MI14 | LONG RURAL | Asset failure | LV | 57.00 | 132.0 | 0.053980 | 0.0004091 | No
24/10/2023 | 09:13 | MV15 | SHORT RURAL | Planned |  | 65.00 | 290.0 | 0.132619 | 0.0004573 | No
24/10/2023 | 09:14 | WHY12 | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
24/10/2023 | 09:23 | MV53 | SHORT RURAL | Planned |  | 12.00 | 125.0 | 0.010553 | 0.0000844 | No
24/10/2023 | 09:32 | LM64 | LONG RURAL | Planned |  | 21.00 | 208.0 | 0.031346 | 0.0001507 | No
24/10/2023 | 09:33 | HH130B | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | No
24/10/2023 | 10:09 | NL451E | URBAN | Planned |  | 133.00 | 274.2 | 0.056219 | 0.0002051 | No
24/10/2023 | 10:21 | YK12 | LONG RURAL | Planned |  | 4.00 | 73.0 | 0.002095 | 0.0000287 | No
24/10/2023 | 10:44 | HK04 | LONG RURAL | Planned |  | 31.00 | 187.0 | 0.041601 | 0.0002225 | No
24/10/2023 | 11:06 | HH496C | URBAN | Asset failure | LV | 1.00 | 394.0 | 0.000607 | 0.0000015 | No
24/10/2023 | 11:23 | EL19 | URBAN | Animal | Animal impact | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
24/10/2023 | 11:58 | HH118D | URBAN | Unknown | Unknown | 6.33 | 159.0 | 0.001553 | 0.0000098 | No
24/10/2023 | 12:01 | YK12 | LONG RURAL | Planned |  | 8.00 | 72.0 | 0.004134 | 0.0000574 | No
24/10/2023 | 12:11 | ST16 | SHORT RURAL | Planned |  | 20.00 | 59.0 | 0.008302 | 0.0001407 | No
24/10/2023 | 13:24 | EL10 | URBAN | Unknown | Unknown | 52.00 | 42.0 | 0.003367 | 0.0000802 | No
24/10/2023 | 13:59 | NA52 | LONG RURAL | Weather |  | 6.00 | 34.0 | 0.001464 | 0.0000431 | No
24/10/2023 | 14:01 | MV31 | SHORT RURAL | Planned |  | 214.00 | 56.0 | 0.084313 | 0.0015056 | No
24/10/2023 | 14:07 | SSD152 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 712.00 | 199.6 | 0.999743 | 0.0050093 | No
24/10/2023 | 14:15 | NL210A | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
24/10/2023 | 14:24 | EL10 | URBAN | Asset failure | LV | 52.00 | 101.0 | 0.008097 | 0.0000802 | No
24/10/2023 | 14:55 | SA520E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 579.00 | 58.0 | 0.051775 | 0.0008927 | No
24/10/2023 | 15:10 | SM179A | URBAN | Asset failure | LV | 1.00 | 74.0 | 0.000114 | 0.0000015 | No
24/10/2023 | 16:01 | NL115C | URBAN | Asset failure | LV | 29.00 | 39.0 | 0.001744 | 0.0000447 | No
24/10/2023 | 16:10 | SA33 | URBAN | Overloads |  | 1.00 | 370.0 | 0.000570 | 0.0000015 | No
24/10/2023 | 16:16 | ME347C | URBAN | Vegetation | Grow-in - NSP responsibility | 31.67 | 175.0 | 0.008544 | 0.0000488 | No
24/10/2023 | 16:33 | NU04 | LONG RURAL | Asset failure | HV | 2.00 | 52.0 | 0.000746 | 0.0000144 | No
24/10/2023 | 16:33 | NU04 | SHORT RURAL | Asset failure | HV | 52.33 | 52.0 | 0.019146 | 0.0003682 | No
24/10/2023 | 16:45 | HH428F | URBAN | Asset failure | LV | 116.00 | 160.5 | 0.028711 | 0.0001788 | No
24/10/2023 | 16:46 | MB11 | SHORT RURAL | Third Party | Other | 1.00 | 206.0 | 0.001449 | 0.0000070 | No
24/10/2023 | 16:47 | SM349C | URBAN | Asset failure | LV | 1.00 | 370.0 | 0.000570 | 0.0000015 | No
24/10/2023 | 16:51 | HH121E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 37.00 | 115.0 | 0.006560 | 0.0000570 | No
24/10/2023 | 17:10 | NL451A | URBAN | Unknown | Unknown | 1.00 | 471.0 | 0.000726 | 0.0000015 | No
24/10/2023 | 17:22 | HH177B | URBAN | Asset failure | LV | 16.00 | 469.9 | 0.011591 | 0.0000247 | No
24/10/2023 | 17:27 | HH341D | URBAN | Asset failure | LV | 26.33 | 106.0 | 0.004304 | 0.0000406 | No
24/10/2023 | 17:58 | HH102D | URBAN | Asset failure | LV | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
24/10/2023 | 17:59 | SM350D | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
24/10/2023 | 18:15 | NL451E | URBAN | Unknown | Unknown | 1.00 | 348.0 | 0.000537 | 0.0000015 | No
24/10/2023 | 19:00 | SM374B | URBAN | Asset failure | LV | 106.00 | 121.0 | 0.019775 | 0.0001634 | No
24/10/2023 | 21:33 | SM349C | URBAN | Asset failure | LV | 83.00 | 244.5 | 0.031287 | 0.0001280 | No
24/10/2023 | 21:36 | AP146C | URBAN | Overloads |  | 1.00 | 330.0 | 0.000509 | 0.0000015 | No
24/10/2023 | 23:53 | AP344D | URBAN | Asset failure | LV | 26.67 | 132.8 | 0.005459 | 0.0000411 | No
25/10/2023 | 01:40 | VH22 | SHORT RURAL | Unknown | Unknown | 32.00 | 298.0 | 0.067090 | 0.0002251 | No
25/10/2023 | 01:46 | ST22 | SHORT RURAL | Unknown | Unknown | 14.00 | 495.0 | 0.048756 | 0.0000985 | No
25/10/2023 | 03:05 | AP424E | URBAN | Asset failure | HV | 615.00 | 93.9 | 0.089012 | 0.0009482 | No
25/10/2023 | 07:06 | HH121B | URBAN | Asset failure | LV | 29.00 | 144.0 | 0.006438 | 0.0000447 | No
25/10/2023 | 08:24 | SD56301 | URBAN | Planned |  | 115.00 | 416.2 | 0.073787 | 0.0001773 | No
25/10/2023 | 08:29 | HH121E | URBAN | Overloads |  | 2.00 | 209.0 | 0.000644 | 0.0000031 | No
25/10/2023 | 08:43 | EL11 | URBAN | Asset failure | LV | 1.67 | 204.0 | 0.000524 | 0.0000026 | No
25/10/2023 | 09:06 | SM374B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 177.0 | 0.000273 | 0.0000015 | No
25/10/2023 | 09:19 | HH409D | URBAN | Asset failure | LV | 32.00 | 141.9 | 0.007001 | 0.0000493 | No
25/10/2023 | 09:25 | CM16 | LONG RURAL | Planned |  | 76.00 | 271.0 | 0.147804 | 0.0005454 | No
25/10/2023 | 09:29 | M01 | LONG RURAL | Asset failure | LV | 1.00 | 57.0 | 0.000409 | 0.0000072 | No
25/10/2023 | 09:49 | LM63 | LONG RURAL | Planned |  | 16.00 | 129.0 | 0.014812 | 0.0001148 | No
25/10/2023 | 09:57 | LM64 | LONG RURAL | Third Party | Unauthorised access | 2.00 | 532.0 | 0.007636 | 0.0000144 | No
25/10/2023 | 10:05 | SG12 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 22.00 | 57.0 | 0.008823 | 0.0001548 | No
25/10/2023 | 10:12 | CN43 | LONG RURAL | Planned |  | 26.00 | 76.0 | 0.014180 | 0.0001866 | No
25/10/2023 | 10:22 | WK33 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 4.00 | 74.0 | 0.002083 | 0.0000281 | No
25/10/2023 | 10:24 | SD34201 | SHORT RURAL | Planned |  | 69.00 | 485.0 | 0.235443 | 0.0004854 | No
25/10/2023 | 10:29 | MTB72 | LONG RURAL | Planned |  | 16.00 | 125.0 | 0.014353 | 0.0001148 | No
25/10/2023 | 10:41 | CN32 | LONG RURAL | Planned |  | 44.00 | 179.7 | 0.056743 | 0.0003158 | No
25/10/2023 | 10:51 | VH23 | SHORT RURAL | Planned |  | 1.00 | 178.0 | 0.001252 | 0.0000070 | No
25/10/2023 | 10:52 | YK17 | LONG RURAL | Planned |  | 4.00 | 41.0 | 0.001177 | 0.0000287 | No
25/10/2023 | 11:11 | AP424D | URBAN | Planned |  | 96.00 | 170.0 | 0.025161 | 0.0001480 | No
25/10/2023 | 11:40 | HH148A | URBAN | Animal | Animal impact | 14.67 | 157.0 | 0.003550 | 0.0000226 | No
25/10/2023 | 11:49 | MG17 | LONG RURAL | Asset failure | LV | 3.00 | 161.0 | 0.003466 | 0.0000215 | No
25/10/2023 | 12:19 | SM374C | URBAN | Asset failure | LV | 40.00 | 212.0 | 0.013074 | 0.0000617 | No
25/10/2023 | 12:27 | SM374C | URBAN | Asset failure | LV | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
25/10/2023 | 12:28 | MG03 | SHORT RURAL | Unknown | Unknown | 178.00 | 107.0 | 0.133998 | 0.0012523 | No
25/10/2023 | 12:30 | SM374C | URBAN | Asset failure | HV | 54.33 | 142.0 | 0.011895 | 0.0000838 | No
25/10/2023 | 12:46 | SA711C | URBAN | Asset failure | LV | 48.00 | 71.0 | 0.005254 | 0.0000740 | No
25/10/2023 | 12:46 | HH409E | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
25/10/2023 | 12:48 | SM374C | URBAN | Asset failure | LV | 105.00 | 185.0 | 0.029949 | 0.0001619 | No
25/10/2023 | 12:52 | SM374C | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
25/10/2023 | 13:15 | W02 | LONG RURAL | Overloads |  | 1.00 | 175.0 | 0.001256 | 0.0000072 | No
25/10/2023 | 13:34 | LC01 | SHORT RURAL | Asset failure | LV | 14.00 | 91.6 | 0.009027 | 0.0000985 | No
25/10/2023 | 13:39 | KA05 | LONG RURAL | Asset failure | LV | 1.00 | 88.0 | 0.000632 | 0.0000072 | No
25/10/2023 | 13:49 | EL09 | URBAN | Asset failure | LV | 8.00 | 488.0 | 0.006019 | 0.0000123 | No
25/10/2023 | 14:23 | BM15 | SHORT RURAL | Planned |  | 18.00 | 21.9 | 0.002779 | 0.0001266 | No
25/10/2023 | 14:26 | HH121F | URBAN | Asset failure | LV | 19.33 | 133.0 | 0.003964 | 0.0000298 | No
25/10/2023 | 14:50 | HH177F | URBAN | Overloads |  | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
25/10/2023 | 15:12 | PA01 | URBAN | Asset failure | LV | 68.00 | 126.2 | 0.013230 | 0.0001048 | No
25/10/2023 | 16:07 | SM179A | URBAN | Asset failure | LV | 16.33 | 78.0 | 0.001964 | 0.0000252 | No
25/10/2023 | 16:12 | GU43 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 387.0 | 0.002777 | 0.0000072 | No
25/10/2023 | 16:21 | HH429C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 365.0 | 0.000563 | 0.0000015 | No
25/10/2023 | 16:56 | HH102A | URBAN | Vegetation | Grow-in - NSP responsibility | 33.00 | 56.1 | 0.002854 | 0.0000509 | No
25/10/2023 | 17:03 | MTB14 | SHORT RURAL | Third Party | Dig-in | 6.00 | 83.0 | 0.003504 | 0.0000422 | No
25/10/2023 | 17:16 | SM349F | URBAN | Asset failure | LV | 1.00 | 364.0 | 0.000561 | 0.0000015 | No
25/10/2023 | 17:57 | HH432C | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
25/10/2023 | 18:07 | HH409A | URBAN | Asset failure | LV | 15.00 | 258.0 | 0.005967 | 0.0000231 | No
25/10/2023 | 18:48 | SA31 | URBAN | Animal | Animal nesting/burrowing, etc and other | 11.00 | 35.0 | 0.000594 | 0.0000170 | No
25/10/2023 | 20:51 | MG11 | SHORT RURAL | Asset failure | LV | 3.00 | 84.0 | 0.001773 | 0.0000211 | No
25/10/2023 | 20:51 | SM216B | URBAN | Asset failure | LV | 61.00 | 20.0 | 0.001881 | 0.0000940 | No
25/10/2023 | 21:28 | CBD103G | URBAN | Asset failure | LV | 7.00 | 194.0 | 0.002094 | 0.0000108 | No
25/10/2023 | 22:01 | SM216B | URBAN | Planned |  | 27.00 | 76.0 | 0.003164 | 0.0000416 | No
25/10/2023 | 22:35 | HH121E | URBAN | Asset failure | LV | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
25/10/2023 | 23:59 | ST22 | SHORT RURAL | Unknown | Unknown | 17.00 | 379.0 | 0.045330 | 0.0001196 | No
26/10/2023 | 02:39 | SG10 | SHORT RURAL | Animal | Animal impact | 1,475.00 | 105.0 | 1.089622 | 0.0103773 | No
26/10/2023 | 05:55 | NL451C | URBAN | Asset failure | LV | 1.00 | 323.0 | 0.000498 | 0.0000015 | No
26/10/2023 | 06:46 | ST15 | SHORT RURAL | Animal | Animal impact | 95.00 | 199.5 | 0.133351 | 0.0006684 | No
26/10/2023 | 07:02 | HH386E | URBAN | Overloads |  | 2.00 | 258.0 | 0.000796 | 0.0000031 | No
26/10/2023 | 07:30 | HH130F | URBAN | Asset failure | LV | 1.00 | 806.0 | 0.001243 | 0.0000015 | No
26/10/2023 | 08:14 | WHY09 | URBAN | Planned |  | 513.00 | 205.5 | 0.162572 | 0.0007909 | No
26/10/2023 | 08:18 | EL260A | URBAN | Planned |  | 165.00 | 387.7 | 0.098626 | 0.0002544 | No
26/10/2023 | 08:37 | CN25 | LONG RURAL | Planned |  | 3.00 | 65.3 | 0.001407 | 0.0000215 | No
26/10/2023 | 08:39 | MG46 | SHORT RURAL | Planned |  | 8.00 | 53.0 | 0.002983 | 0.0000563 | No
26/10/2023 | 08:44 | HH145A | URBAN | Planned |  | 14.00 | 323.4 | 0.006981 | 0.0000216 | No
26/10/2023 | 09:01 | MT17 | SHORT RURAL | Planned |  | 79.00 | 311.8 | 0.173326 | 0.0005558 | No
26/10/2023 | 09:04 | MTB14 | SHORT RURAL | Planned |  | 26.00 | 199.0 | 0.036402 | 0.0001829 | No
26/10/2023 | 09:04 | NU04 | SHORT RURAL | Planned |  | 1.00 | 261.0 | 0.001836 | 0.0000070 | No
26/10/2023 | 09:18 | R03 | LONG RURAL | Planned |  | 29.00 | 120.0 | 0.024974 | 0.0002081 | No
26/10/2023 | 09:28 | PL11 | LONG RURAL | Planned |  | 5.00 | 55.0 | 0.001973 | 0.0000359 | No
26/10/2023 | 09:32 | ME231D | URBAN | Planned |  | 917.00 | 8.0 | 0.011310 | 0.0014138 | No
26/10/2023 | 09:45 | LM54 | LONG RURAL | Planned |  | 52.00 | 141.0 | 0.052617 | 0.0003732 | No
26/10/2023 | 09:46 | MTB32 | LONG RURAL | Planned |  | 40.00 | 164.8 | 0.047306 | 0.0002871 | No
26/10/2023 | 09:46 | MTB32 | SHORT RURAL | Planned |  | 1.00 | 162.0 | 0.001140 | 0.0000070 | No
26/10/2023 | 09:51 | EL17 | URBAN | Asset failure | LV | 9.00 | 519.1 | 0.007203 | 0.0000139 | No
26/10/2023 | 09:53 | CN27 | LONG RURAL | Planned |  | 68.00 | 215.0 | 0.104918 | 0.0004880 | No
26/10/2023 | 09:54 | GA01 | URBAN | Asset failure | LV | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
26/10/2023 | 10:04 | LC01 | SHORT RURAL | Asset failure | LV | 3.00 | 158.0 | 0.003335 | 0.0000211 | No
26/10/2023 | 10:06 | HH496E | URBAN | Planned |  | 30.00 | 241.0 | 0.011147 | 0.0000463 | No
26/10/2023 | 10:13 | KA02 | SHORT RURAL | Third Party | Other | 875.00 | 58.0 | 0.357051 | 0.0061561 | No
26/10/2023 | 10:24 | SM179B | URBAN | Asset failure | LV | 1.00 | 381.0 | 0.000587 | 0.0000015 | No
26/10/2023 | 10:28 | MI11 | LONG RURAL | Planned |  | 31.00 | 130.0 | 0.028921 | 0.0002225 | No
26/10/2023 | 10:40 | CN25 | LONG RURAL | Planned |  | 1.00 | 34.0 | 0.000244 | 0.0000072 | No
26/10/2023 | 11:06 | AP829A | URBAN | Asset failure | LV | 1.00 | 433.0 | 0.000668 | 0.0000015 | No
26/10/2023 | 11:52 | NL210A | URBAN | Asset failure | LV | 1.00 | 756.0 | 0.001166 | 0.0000015 | No
26/10/2023 | 12:09 | R06 | LONG RURAL | Asset failure | LV | 2.00 | 348.0 | 0.004995 | 0.0000144 | No
26/10/2023 | 12:10 | MI17 | LONG RURAL | Planned |  | 11.00 | 167.0 | 0.013183 | 0.0000789 | No
26/10/2023 | 12:37 | CN25 | LONG RURAL | Planned |  | 61.00 | 73.0 | 0.031956 | 0.0004378 | No
26/10/2023 | 13:21 | AP139D | URBAN | Asset failure | LV | 33.00 | 143.0 | 0.007276 | 0.0000509 | No
26/10/2023 | 13:44 | SG12 | SHORT RURAL | Planned |  | 30.00 | 60.0 | 0.012664 | 0.0002111 | No
26/10/2023 | 14:59 | HH121D | URBAN | Asset failure | LV | 1.00 | 523.0 | 0.000806 | 0.0000015 | No
26/10/2023 | 15:44 | AP425A | URBAN | Third Party | Vehicle impact | 8.00 | 113.0 | 0.001394 | 0.0000123 | No
26/10/2023 | 15:51 | HH386E | URBAN | Network business | Switching and protection error | 2.00 | 157.0 | 0.000484 | 0.0000031 | No
26/10/2023 | 16:10 | LX41 | SHORT RURAL | Other |  | 1.00 | 311.0 | 0.002188 | 0.0000070 | No
26/10/2023 | 17:44 | EL10 | URBAN | Overloads |  | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
26/10/2023 | 19:13 | MTB11 | LONG RURAL | Planned |  | 2.00 | 91.0 | 0.001306 | 0.0000144 | No
26/10/2023 | 19:13 | MTB11 | SHORT RURAL | Planned |  | 56.00 | 89.9 | 0.035431 | 0.0003940 | No
26/10/2023 | 19:45 | ME347G | URBAN | Asset failure | LV | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
26/10/2023 | 20:49 | HH386D | URBAN | Asset failure | LV | 29.33 | 63.0 | 0.002849 | 0.0000452 | No
26/10/2023 | 22:28 | CD22 | LONG RURAL | Asset failure | HV | 2.00 | 474.0 | 0.006803 | 0.0000144 | No
27/10/2023 | 01:22 | HH522C | URBAN | Overloads |  | 58.00 | 140.0 | 0.012519 | 0.0000894 | No
27/10/2023 | 08:05 | SM216E | URBAN | Third Party | Other | 26.00 | 94.0 | 0.003768 | 0.0000401 | No
27/10/2023 | 08:07 | SM411A | URBAN | Planned |  | 20.00 | 3.0 | 0.000093 | 0.0000308 | No
27/10/2023 | 08:40 | CL04 | LONG RURAL | Planned |  | 1.00 | 44.0 | 0.000316 | 0.0000072 | No
27/10/2023 | 08:47 | MG13 | SHORT RURAL | Planned |  | 1.00 | 93.0 | 0.000654 | 0.0000070 | No
27/10/2023 | 08:56 | BT04 | LONG RURAL | Planned |  | 2.00 | 30.0 | 0.000431 | 0.0000144 | No
27/10/2023 | 09:04 | PA07 | LONG RURAL | Planned |  | 2.00 | 48.0 | 0.000689 | 0.0000144 | No
27/10/2023 | 09:12 | PA07 | LONG RURAL | Unknown | Unknown | 1.00 | 72.0 | 0.000517 | 0.0000072 | No
27/10/2023 | 09:16 | VH18 | SHORT RURAL | Planned |  | 3.00 | 362.0 | 0.007641 | 0.0000211 | No
27/10/2023 | 09:20 | PL15 | LONG RURAL | Planned |  | 2.00 | 194.0 | 0.002784 | 0.0000144 | No
27/10/2023 | 09:21 | GA39 | LONG RURAL | Planned |  | 35.00 | 131.0 | 0.032903 | 0.0002512 | No
27/10/2023 | 09:30 | MI21 | LONG RURAL | Planned |  | 64.00 | 287.0 | 0.131815 | 0.0004593 | No
27/10/2023 | 09:40 | SB23 | LONG RURAL | Planned |  | 6.00 | 190.8 | 0.008217 | 0.0000431 | No
27/10/2023 | 09:40 | MV51 | SHORT RURAL | Planned |  | 38.00 | 305.7 | 0.081724 | 0.0002673 | No
27/10/2023 | 09:43 | NL511A | URBAN | Asset failure | LV | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
27/10/2023 | 09:51 | MB22 | SHORT RURAL | Asset failure | LV | 7.00 | 115.0 | 0.005664 | 0.0000492 | No
27/10/2023 | 09:52 | CN43 | LONG RURAL | Planned |  | 26.00 | 211.0 | 0.039369 | 0.0001866 | No
27/10/2023 | 09:58 | SD49100 | LONG RURAL | Animal | Animal impact | 4.67 | 180.0 | 0.006028 | 0.0000335 | No
27/10/2023 | 09:58 | HH121G | URBAN | Planned |  | 22.00 | 231.0 | 0.007835 | 0.0000339 | No
27/10/2023 | 10:02 | GU31 | LONG RURAL | Unknown | Unknown | 149.00 | 94.0 | 0.100512 | 0.0010693 | No
27/10/2023 | 10:12 | CN24 | LONG RURAL | Planned |  | 114.00 | 156.0 | 0.127624 | 0.0008181 | No
27/10/2023 | 10:47 | SM172E | URBAN | Overloads |  | 11.00 | 684.0 | 0.011600 | 0.0000170 | No
27/10/2023 | 11:09 | MG02 | LONG RURAL | Planned |  | 18.00 | 68.0 | 0.008784 | 0.0001292 | No
27/10/2023 | 11:24 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 239.0 | 0.001715 | 0.0000072 | No
27/10/2023 | 11:34 | MV22 | SHORT RURAL | Planned |  | 28.00 | 85.0 | 0.016744 | 0.0001970 | No
27/10/2023 | 11:47 | SM216B | URBAN | Overloads |  | 1.00 | 626.0 | 0.000965 | 0.0000015 | No
27/10/2023 | 12:05 | MV53 | SHORT RURAL | Planned |  | 7.00 | 46.6 | 0.002294 | 0.0000492 | No
27/10/2023 | 12:08 | MV15 | SHORT RURAL | Unknown | Unknown | 1,174.00 | 147.0 | 1.214171 | 0.0082597 | No
27/10/2023 | 13:14 | MV22 | SHORT RURAL | Planned |  | 41.00 | 36.0 | 0.010384 | 0.0002885 | No
27/10/2023 | 15:44 | SM349D | URBAN | Asset failure | LV | 1.00 | 385.0 | 0.000594 | 0.0000015 | No
27/10/2023 | 16:12 | NL451E | URBAN | Asset failure | LV | 1.00 | 416.0 | 0.000641 | 0.0000015 | No
27/10/2023 | 16:32 | SM411E | URBAN | Planned |  | 1.00 | 273.0 | 0.000421 | 0.0000015 | No
27/10/2023 | 16:33 | SM411E | URBAN | Planned |  | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
27/10/2023 | 16:34 | SM411E | URBAN | Vegetation | Grow-in - NSP responsibility | 215.00 | 180.0 | 0.059666 | 0.0003315 | No
27/10/2023 | 17:44 | VH21 | SHORT RURAL | Asset failure | LV | 50.00 | 131.0 | 0.046082 | 0.0003518 | No
27/10/2023 | 20:09 | NL234C | URBAN | Asset failure | LV | 161.00 | 48.0 | 0.011915 | 0.0002482 | No
27/10/2023 | 20:17 | EL10 | URBAN | Asset failure | LV | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
27/10/2023 | 22:50 | SM137B | URBAN | Planned |  | 5.00 | 792.0 | 0.006105 | 0.0000077 | No
28/10/2023 | 07:04 | GU18 | LONG RURAL | Unknown | Unknown | 2.00 | 324.5 | 0.004657 | 0.0000144 | No
28/10/2023 | 08:14 | HH428D | URBAN | Asset failure | LV | 19.67 | 116.0 | 0.003517 | 0.0000303 | No
28/10/2023 | 08:39 | W26 | LONG RURAL | Other |  | 6.00 | 83.0 | 0.003574 | 0.0000431 | No
28/10/2023 | 08:43 | SG04 | SHORT RURAL | Overloads |  | 1.00 | 429.0 | 0.003018 | 0.0000070 | No
28/10/2023 | 09:11 | MG11 | SHORT RURAL | Asset failure | LV | 2.00 | 1,627.0 | 0.022893 | 0.0000141 | No
28/10/2023 | 09:27 | MB26 | LONG RURAL | Planned |  | 63.00 | 143.0 | 0.064652 | 0.0004521 | No
28/10/2023 | 09:48 | SD59100 | LONG RURAL | Planned |  | 349.00 | 413.0 | 1.034375 | 0.0025045 | No
28/10/2023 | 10:09 | MV15 | SHORT RURAL | Planned |  | 6.00 | 100.0 | 0.004221 | 0.0000422 | No
28/10/2023 | 12:29 | HH341A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,316.00 | 65.8 | 0.133531 | 0.0020289 | No
28/10/2023 | 12:50 | HH386B | URBAN | Asset failure | LV | 101.00 | 23.5 | 0.003665 | 0.0001557 | No
28/10/2023 | 12:54 | SM402B | URBAN | Asset failure | HV | 241.33 | 147.3 | 0.054823 | 0.0003721 | No
28/10/2023 | 13:06 | MG06 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,518.0 | 0.010680 | 0.0000070 | No
28/10/2023 | 13:17 | MG05 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 269.67 | 104.5 | 0.202172 | 0.0019352 | No
28/10/2023 | 13:30 | SA520A | URBAN | Asset failure | HV | 928.00 | 187.0 | 0.267550 | 0.0014307 | No
28/10/2023 | 13:43 | GU31 | LONG RURAL | Other |  | 27.00 | 63.0 | 0.012207 | 0.0001938 | No
28/10/2023 | 13:47 | HH341A | URBAN | Vegetation | Grow-in - NSP responsibility | 46.33 | 212.1 | 0.015154 | 0.0000714 | No
28/10/2023 | 13:53 | HH118D | URBAN | Vegetation | Grow-in - NSP responsibility | 6.33 | 123.0 | 0.001201 | 0.0000098 | No
28/10/2023 | 14:41 | HH118D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
28/10/2023 | 15:07 | MI09 | LONG RURAL | Asset failure | HV | 3.00 | 277.0 | 0.005964 | 0.0000215 | No
28/10/2023 | 15:31 | SA711C | URBAN | Unknown | Unknown | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
28/10/2023 | 15:51 | MG34 | LONG RURAL | Asset failure | HV | 4.67 | 111.0 | 0.003717 | 0.0000335 | No
28/10/2023 | 15:51 | WK33 | SHORT RURAL | Unknown | Unknown | 2.00 | 250.0 | 0.003518 | 0.0000141 | No
28/10/2023 | 15:52 | BU08 | LONG RURAL | Asset failure | LV | 2.00 | 250.0 | 0.003588 | 0.0000144 | No
28/10/2023 | 16:02 | MG38 | SHORT RURAL | Asset failure | LV | 1.00 | 406.0 | 0.002856 | 0.0000070 | No
28/10/2023 | 17:55 | MB24 | SHORT RURAL | Unknown | Unknown | 1.00 | 153.0 | 0.001076 | 0.0000070 | No
28/10/2023 | 19:30 | SD31400 | LONG RURAL | Asset failure | Subtransmission | 3.00 | 219.0 | 0.004715 | 0.0000215 | No
29/10/2023 | 06:47 | ME347G | URBAN | Asset failure | LV | 15.67 | 168.0 | 0.004058 | 0.0000242 | No
29/10/2023 | 07:16 | MV15 | SHORT RURAL | Planned |  | 41.00 | 74.0 | 0.021346 | 0.0002885 | No
29/10/2023 | 08:14 | AP365D2 | URBAN | Planned |  | 9.00 | 215.9 | 0.002996 | 0.0000139 | No
29/10/2023 | 08:25 | GA02 | SHORT RURAL | Planned |  | 33.00 | 476.3 | 0.110591 | 0.0002322 | No
29/10/2023 | 08:27 | NU21 | LONG RURAL | Planned |  | 90.00 | 262.0 | 0.169218 | 0.0006459 | No
29/10/2023 | 09:01 | NL115B | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
29/10/2023 | 09:15 | W04 | LONG RURAL | Planned |  | 33.00 | 86.0 | 0.020366 | 0.0002368 | No
29/10/2023 | 09:16 | SD54300 | LONG RURAL | Planned |  | 881.00 | 237.0 | 1.498396 | 0.0063223 | No
29/10/2023 | 11:03 | AP227A | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
29/10/2023 | 11:16 | CN74 | LONG RURAL | Planned |  | 25.00 | 207.0 | 0.037138 | 0.0001794 | No
29/10/2023 | 14:23 | CL25 | LONG RURAL | Weather |  | 31.33 | 51.1 | 0.011501 | 0.0002249 | No
29/10/2023 | 17:39 | WK33 | SHORT RURAL | Animal | Animal impact | 4.00 | 195.0 | 0.005488 | 0.0000281 | No
29/10/2023 | 19:46 | NL115E | URBAN | Asset failure | LV | 8.00 | 166.0 | 0.002047 | 0.0000123 | No
29/10/2023 | 20:55 | MG37 | LONG RURAL | Unknown | Unknown | 4.67 | 141.0 | 0.004722 | 0.0000335 | No
29/10/2023 | 20:58 | HH121E | URBAN | Planned |  | 37.00 | 143.0 | 0.008157 | 0.0000570 | No
29/10/2023 | 22:31 | BM57 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,084.0 | 0.007626 | 0.0000070 | No
30/10/2023 | 01:59 | HH496C | URBAN | Overloads |  | 25.33 | 114.0 | 0.004453 | 0.0000391 | No
30/10/2023 | 06:21 | AP139C | URBAN | Asset failure | LV | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
30/10/2023 | 07:23 | MG05 | LONG RURAL | Third Party | Vehicle impact | 138.00 | 118.8 | 0.117656 | 0.0009903 | No
30/10/2023 | 07:25 | EL01L | URBAN | Asset failure | LV | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
30/10/2023 | 07:55 | MTB13 | SHORT RURAL | Asset failure | LV | 2.00 | 64.0 | 0.000901 | 0.0000141 | No
30/10/2023 | 08:15 | WHY05 | URBAN | Planned |  | 78.00 | 248.1 | 0.029833 | 0.0001203 | No
30/10/2023 | 08:45 | NU14 | LONG RURAL | Planned |  | 5.00 | 38.0 | 0.001364 | 0.0000359 | No
30/10/2023 | 08:46 | MTB14 | SHORT RURAL | Overloads |  | 2.00 | 170.0 | 0.002392 | 0.0000141 | No
30/10/2023 | 08:54 | CL02 | LONG RURAL | Planned |  | 32.00 | 219.0 | 0.050292 | 0.0002296 | No
30/10/2023 | 08:58 | KA22 | LONG RURAL | Unknown | Unknown | 460.00 | 317.1 | 1.046754 | 0.0033011 | No
30/10/2023 | 09:17 | MI12 | LONG RURAL | Planned |  | 15.00 | 325.0 | 0.034985 | 0.0001076 | No
30/10/2023 | 09:51 | SD54101 | LONG RURAL | Planned |  | 1.00 | 231.0 | 0.001658 | 0.0000072 | No
30/10/2023 | 10:05 | CN73 | LONG RURAL | Planned |  | 108.00 | 149.0 | 0.115481 | 0.0007750 | No
30/10/2023 | 10:29 | SA18 | URBAN | Overloads |  | 1.00 | 41.0 | 0.000063 | 0.0000015 | No
30/10/2023 | 10:35 | CN53 | LONG RURAL | Planned |  | 111.00 | 242.0 | 0.192771 | 0.0007966 | No
30/10/2023 | 10:58 | SM349D | URBAN | Third Party | Vehicle impact | 50.00 | 175.0 | 0.013490 | 0.0000771 | No
30/10/2023 | 11:04 | BT01 | LONG RURAL | Asset failure | LV | 1.00 | 323.0 | 0.002318 | 0.0000072 | No
30/10/2023 | 11:14 | G40 | LONG RURAL | Planned |  | 42.00 | 338.0 | 0.101875 | 0.0003014 | No
30/10/2023 | 11:58 | MG10 | LONG RURAL | Unknown | Unknown | 2.00 | 184.0 | 0.002641 | 0.0000144 | No
30/10/2023 | 12:20 | CBD27F | CBD | Unknown | Unknown | 2.00 | 478.0 | 0.138120 | 0.0002890 | No
30/10/2023 | 12:27 | NL115A | URBAN | Asset failure | LV | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
30/10/2023 | 12:49 | NL111P | URBAN | Vegetation | Grow-in - NSP responsibility | 54.00 | 92.0 | 0.007659 | 0.0000833 | No
30/10/2023 | 13:53 | MG06 | SHORT RURAL | Unknown | Unknown | 1.33 | 259.0 | 0.002430 | 0.0000094 | No
30/10/2023 | 14:29 | GA02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 481.00 | 77.0 | 0.260573 | 0.0033841 | No
30/10/2023 | 14:40 | MG12 | LONG RURAL | Asset failure | HV | 316.00 | 144.9 | 0.328482 | 0.0022677 | No
30/10/2023 | 14:55 | SM349D | URBAN | Asset failure | LV | 16.67 | 171.0 | 0.004394 | 0.0000257 | No
30/10/2023 | 15:46 | HH403B | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
30/10/2023 | 16:04 | MTB41 | SHORT RURAL | Unknown | Unknown | 26.00 | 74.0 | 0.013536 | 0.0001829 | No
30/10/2023 | 16:41 | NU01 | SHORT RURAL | Asset failure | HV | 111.00 | 86.4 | 0.067456 | 0.0007809 | No
30/10/2023 | 16:47 | MTB21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 36.00 | 220.0 | 0.055721 | 0.0002533 | No
30/10/2023 | 16:48 | NL115A | URBAN | Asset failure | HV | 34.00 | 305.0 | 0.015988 | 0.0000524 | No
30/10/2023 | 16:52 | BM34 | SHORT RURAL | Weather |  | 10.00 | 1,250.0 | 0.087944 | 0.0000704 | No
30/10/2023 | 17:38 | AP425D | URBAN | Asset failure | LV | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
30/10/2023 | 18:46 | NL760C | URBAN | Asset failure | LV | 34.67 | 91.0 | 0.004864 | 0.0000534 | No
30/10/2023 | 19:12 | AP227D | URBAN | Overloads |  | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
30/10/2023 | 19:36 | NU13 | LONG RURAL | Unknown | Unknown | 2.00 | 134.0 | 0.001923 | 0.0000144 | No
30/10/2023 | 19:47 | SD40102 | LONG RURAL | Other |  | 524.00 | 113.0 | 0.425068 | 0.0037604 | No
30/10/2023 | 23:00 | SM374B | URBAN | Weather |  | 900.00 | 117.6 | 0.163118 | 0.0013876 | No
31/10/2023 | 00:28 | CL23 | LONG RURAL | Planned |  | 14.00 | 230.0 | 0.023108 | 0.0001005 | No
31/10/2023 | 00:44 | NL451E | URBAN | Asset failure | HV | 1,809.00 | 166.9 | 0.465389 | 0.0027890 | No
31/10/2023 | 03:10 | KA01 | SHORT RURAL | Animal | Animal impact | 38.00 | 88.0 | 0.023527 | 0.0002673 | No
31/10/2023 | 05:56 | MG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 330.0 | 0.004643 | 0.0000141 | No
31/10/2023 | 05:58 | AP424C | URBAN | Asset failure | LV | 19.00 | 160.0 | 0.004687 | 0.0000293 | No
31/10/2023 | 06:37 | SM126C | URBAN | Asset failure | LV | 1.00 | 411.0 | 0.000634 | 0.0000015 | No
31/10/2023 | 07:02 | NL760A | URBAN | Unknown | Unknown | 182.67 | 131.6 | 0.037062 | 0.0002816 | No
31/10/2023 | 07:34 | EL01L | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
31/10/2023 | 08:10 | WHY09 | URBAN | Planned |  | 341.00 | 254.9 | 0.133988 | 0.0005257 | No
31/10/2023 | 08:14 | AP365A | URBAN | Asset failure | LV | 65.00 | 181.0 | 0.018139 | 0.0001002 | No
31/10/2023 | 08:24 | HH386G | URBAN | Planned |  | 67.00 | 486.8 | 0.050286 | 0.0001033 | No
31/10/2023 | 08:52 | SG10 | SHORT RURAL | Asset failure | LV | 1.00 | 92.0 | 0.000647 | 0.0000070 | No
31/10/2023 | 09:00 | NU31 | LONG RURAL | Planned |  | 5.00 | 343.0 | 0.012307 | 0.0000359 | No
31/10/2023 | 09:05 | MV33 | SHORT RURAL | Planned |  | 42.00 | 255.0 | 0.075350 | 0.0002955 | No
31/10/2023 | 09:07 | AP365D2 | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
31/10/2023 | 09:17 | PL28 | LONG RURAL | Planned |  | 94.00 | 313.0 | 0.211142 | 0.0006746 | No
31/10/2023 | 09:19 | CL07 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 53.00 | 177.8 | 0.067608 | 0.0003803 | No
31/10/2023 | 09:21 | EL23 | URBAN | Planned |  | 16.00 | 286.0 | 0.007055 | 0.0000247 | No
31/10/2023 | 09:23 | WHY04 | URBAN | Planned |  | 1.00 | 1,388.0 | 0.002140 | 0.0000015 | No
31/10/2023 | 09:27 | NA12 | LONG RURAL | Planned |  | 10.00 | 311.6 | 0.022361 | 0.0000718 | No
31/10/2023 | 09:30 | VH45 | SHORT RURAL | Planned |  | 166.00 | 320.0 | 0.373725 | 0.0011679 | No
31/10/2023 | 09:33 | SD50000 | URBAN | Planned |  | 2.00 | 57.0 | 0.000176 | 0.0000031 | No
31/10/2023 | 09:34 | MV15 | SHORT RURAL | Planned |  | 1.00 | 95.0 | 0.000668 | 0.0000070 | No
31/10/2023 | 09:39 | GU31 | LONG RURAL | Network business | Switching and protection error | 1.00 | 2,772.0 | 0.019893 | 0.0000072 | No
31/10/2023 | 09:40 | EL19 | URBAN | Unknown | Unknown | 2.00 | 43.0 | 0.000133 | 0.0000031 | No
31/10/2023 | 09:42 | CM11 | LONG RURAL | Planned |  | 2.00 | 14.0 | 0.000201 | 0.0000144 | No
31/10/2023 | 09:43 | MV64 | SHORT RURAL | Planned |  | 79.00 | 294.0 | 0.163406 | 0.0005558 | No
31/10/2023 | 09:55 | CM16 | LONG RURAL | Planned |  | 15.00 | 76.0 | 0.008181 | 0.0001076 | No
31/10/2023 | 09:59 | SB22 | LONG RURAL | Planned |  | 8.00 | 143.0 | 0.008210 | 0.0000574 | No
31/10/2023 | 10:04 | MG10 | LONG RURAL | Overloads |  | 3.00 | 180.0 | 0.003875 | 0.0000215 | No
31/10/2023 | 10:12 | VH32 | SHORT RURAL | Animal | Animal impact | 31.00 | 122.9 | 0.026798 | 0.0002181 | No
31/10/2023 | 10:14 | CN02 | LONG RURAL | Planned |  | 81.00 | 345.0 | 0.200543 | 0.0005813 | No
31/10/2023 | 10:24 | CN03 | LONG RURAL | Planned |  | 48.00 | 150.0 | 0.051670 | 0.0003445 | No
31/10/2023 | 10:25 | ST41 | LONG RURAL | Planned |  | 169.00 | 189.0 | 0.229219 | 0.0012128 | No
31/10/2023 | 10:47 | MI16 | LONG RURAL | Asset failure | LV | 1.00 | 115.0 | 0.000825 | 0.0000072 | No
31/10/2023 | 10:47 | MG17 | LONG RURAL | Animal | Animal impact | 1.00 | 195.0 | 0.001399 | 0.0000072 | No
31/10/2023 | 10:50 | CM11 | LONG RURAL | Planned |  | 5.00 | 66.0 | 0.002368 | 0.0000359 | No
31/10/2023 | 10:51 | MV31 | SHORT RURAL | Planned |  | 1.00 | 329.0 | 0.002315 | 0.0000070 | No
31/10/2023 | 10:51 | MV31 | SHORT RURAL | Planned |  | 1.00 | 339.0 | 0.002385 | 0.0000070 | No
31/10/2023 | 10:59 | NL210D | URBAN | Asset failure | LV | 1.00 | 240.0 | 0.000370 | 0.0000015 | No
31/10/2023 | 11:08 | KI31 | SHORT RURAL | Planned |  | 2.00 | 87.0 | 0.001224 | 0.0000141 | No
31/10/2023 | 11:10 | MV31 | SHORT RURAL | Planned |  | 107.00 | 247.0 | 0.185941 | 0.0007528 | No
31/10/2023 | 11:14 | MI20 | LONG RURAL | Asset failure | LV | 1.00 | 301.0 | 0.002160 | 0.0000072 | No
31/10/2023 | 11:35 | BT31 | LONG RURAL | Planned |  | 10.00 | 152.0 | 0.010908 | 0.0000718 | No
31/10/2023 | 11:41 | SD33100 | LONG RURAL | Planned |  | 14.00 | 155.0 | 0.015573 | 0.0001005 | No
31/10/2023 | 11:55 | MV13 | SHORT RURAL | Planned |  | 10.00 | 117.0 | 0.008232 | 0.0000704 | No
31/10/2023 | 12:36 | ME200A | URBAN | Asset failure | LV | 18.00 | 126.0 | 0.003497 | 0.0000278 | No
31/10/2023 | 13:53 | SM349H | URBAN | Asset failure | LV | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
31/10/2023 | 18:49 | SM126A | URBAN | Asset failure | LV | 1.00 | 364.0 | 0.000561 | 0.0000015 | No
31/10/2023 | 19:03 | BM21 | SHORT RURAL | Third Party | Other | 28.00 | 106.0 | 0.020881 | 0.0001970 | No
31/10/2023 | 19:58 | AP529E | URBAN | Asset failure | LV | 97.00 | 166.0 | 0.024821 | 0.0001496 | No
31/10/2023 | 21:11 | WHY09 | URBAN | Planned |  | 5.00 | 339.0 | 0.002613 | 0.0000077 | No
31/10/2023 | 21:43 | CBD367U | CBD | Planned |  | 4.00 | 236.0 | 0.136387 | 0.0005779 | No
01/11/2023 | 03:54 | KI54 | LONG RURAL | Unknown | Unknown | 11.00 | 579.0 | 0.045706 | 0.0000789 | No
01/11/2023 | 06:51 | NL115B | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
01/11/2023 | 08:22 | G31 | LONG RURAL | Unknown | Unknown | 59.00 | 242.1 | 0.102507 | 0.0004234 | No
01/11/2023 | 08:28 | HH429C | URBAN | Asset failure | LV | 28.00 | 158.0 | 0.006819 | 0.0000432 | No
01/11/2023 | 08:33 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 3,255.0 | 0.023359 | 0.0000072 | No
01/11/2023 | 08:37 | EL01M | URBAN | Planned |  | 728.00 | 14.0 | 0.015714 | 0.0011224 | No
01/11/2023 | 08:41 | NL234A | URBAN | Planned |  | 112.00 | 488.0 | 0.084266 | 0.0001727 | No
01/11/2023 | 08:45 | LC03 | LONG RURAL | Overloads |  | 2.00 | 612.0 | 0.008784 | 0.0000144 | No
01/11/2023 | 08:55 | AP355H | URBAN | Asset failure | LV | 3.00 | 17.0 | 0.000079 | 0.0000046 | No
01/11/2023 | 09:03 | SM374B | URBAN | Planned |  | 143.00 | 337.0 | 0.074299 | 0.0002205 | No
01/11/2023 | 09:07 | SD39300 | LONG RURAL | Planned |  | 2.00 | 40.0 | 0.000574 | 0.0000144 | No
01/11/2023 | 09:20 | SD55100 | LONG RURAL | Planned |  | 331.00 | 180.5 | 0.428836 | 0.0023754 | No
01/11/2023 | 09:25 | MG30 | LONG RURAL | Planned |  | 19.00 | 151.0 | 0.020589 | 0.0001364 | No
01/11/2023 | 09:50 | NL451C | URBAN | Asset failure | LV | 1.00 | 198.0 | 0.000305 | 0.0000015 | No
01/11/2023 | 10:10 | MG11 | SHORT RURAL | Overloads |  | 1.00 | 277.0 | 0.001949 | 0.0000070 | No
01/11/2023 | 10:17 | BU04 | LONG RURAL | Planned |  | 2.00 | 160.0 | 0.002296 | 0.0000144 | No
01/11/2023 | 10:32 | SA17 | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
01/11/2023 | 11:08 | NL451E | URBAN | Unknown | Unknown | 1.00 | 1,977.0 | 0.003048 | 0.0000015 | No
01/11/2023 | 12:17 | MV33 | SHORT RURAL | Planned |  | 37.00 | 145.0 | 0.037745 | 0.0002603 | No
01/11/2023 | 13:30 | AP424B | URBAN | Asset failure | LV | 1.00 | 548.0 | 0.000845 | 0.0000015 | No
01/11/2023 | 14:06 | VH21 | SHORT RURAL | Overloads |  | 18.67 | 325.0 | 0.042682 | 0.0001313 | No
01/11/2023 | 14:12 | AP351B | URBAN | Network business | Switching and protection error | 16.00 | 321.0 | 0.007918 | 0.0000247 | No
01/11/2023 | 15:03 | SM179B | URBAN | Overloads |  | 1.00 | 441.0 | 0.000680 | 0.0000015 | No
01/11/2023 | 15:22 | AP372B | URBAN | Unknown | Unknown | 2.00 | 284.0 | 0.000876 | 0.0000031 | No
01/11/2023 | 15:25 | CL03 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 71.00 | 186.0 | 0.094771 | 0.0005095 | No
01/11/2023 | 16:22 | EL10 | URBAN | Overloads |  | 1.00 | 311.0 | 0.000479 | 0.0000015 | No
01/11/2023 | 16:55 | BT28 | LONG RURAL | Weather |  | 14.00 | 356.0 | 0.035767 | 0.0001005 | No
01/11/2023 | 17:46 | EL14 | URBAN | Asset failure | LV | 23.00 | 253.0 | 0.008971 | 0.0000355 | No
01/11/2023 | 19:15 | NL234C | URBAN | Asset failure | LV | 1.00 | 279.0 | 0.000430 | 0.0000015 | No
01/11/2023 | 19:15 | HH130A | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
01/11/2023 | 20:10 | SM349B | URBAN | Asset failure | LV | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
01/11/2023 | 21:15 | CBD367U | CBD | Planned |  | 4.00 | 369.0 | 0.213249 | 0.0005779 | No
02/11/2023 | 01:20 | KI31 | SHORT RURAL | Asset failure | LV | 31.33 | 177.0 | 0.039019 | 0.0002204 | No
02/11/2023 | 06:45 | HH177G | URBAN | Asset failure | LV | 1.00 | 492.0 | 0.000759 | 0.0000015 | No
02/11/2023 | 08:39 | HH432B | URBAN | Planned |  | 112.00 | 363.0 | 0.062682 | 0.0001727 | No
02/11/2023 | 08:39 | MT06 | LONG RURAL | Planned |  | 21.00 | 336.0 | 0.050636 | 0.0001507 | No
02/11/2023 | 08:39 | HH130D | URBAN | Other |  | 27.00 | 166.0 | 0.006910 | 0.0000416 | No
02/11/2023 | 08:41 | HH121C | URBAN | Asset failure | LV | 21.67 | 97.6 | 0.003261 | 0.0000334 | No
02/11/2023 | 08:46 | MTB53 | LONG RURAL | Planned |  | 116.00 | 361.0 | 0.300516 | 0.0008325 | No
02/11/2023 | 08:49 | CV08 | LONG RURAL | Planned |  | 218.00 | 321.2 | 0.502573 | 0.0015644 | No
02/11/2023 | 08:51 | NA51 | LONG RURAL | Planned |  | 22.00 | 35.0 | 0.005526 | 0.0001579 | No
02/11/2023 | 08:52 | EL08D | URBAN | Planned |  | 23.00 | 1.0 | 0.000035 | 0.0000355 | No
02/11/2023 | 09:00 | LX21 | SHORT RURAL | Planned |  | 91.00 | 330.0 | 0.211276 | 0.0006402 | No
02/11/2023 | 09:06 | KI51 | LONG RURAL | Planned |  | 14.00 | 130.0 | 0.013061 | 0.0001005 | No
02/11/2023 | 09:13 | SM410C | URBAN | Planned |  | 161.00 | 328.0 | 0.081417 | 0.0002482 | No
02/11/2023 | 09:16 | SA38 | URBAN | Planned |  | 6.00 | 319.0 | 0.002951 | 0.0000093 | No
02/11/2023 | 09:20 | ST24 | SHORT RURAL | Planned |  | 65.00 | 322.0 | 0.147253 | 0.0004573 | No
02/11/2023 | 09:22 | NL111B | URBAN | Planned |  | 2.00 | 333.0 | 0.001027 | 0.0000031 | No
02/11/2023 | 09:26 | HH496G | URBAN | Planned |  | 71.00 | 304.9 | 0.033371 | 0.0001095 | No
02/11/2023 | 09:26 | SD37402 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 2,012.00 | 127.0 | 1.833732 | 0.0144388 | No
02/11/2023 | 09:26 | SD37402 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 2.00 | 127.0 | 0.001787 | 0.0000141 | No
02/11/2023 | 09:58 | NL234C | URBAN | Third Party | Vehicle impact | 2.00 | 81.0 | 0.000250 | 0.0000031 | No
02/11/2023 | 09:59 | VH34 | SHORT RURAL | Planned |  | 69.00 | 404.7 | 0.196466 | 0.0004854 | No
02/11/2023 | 10:09 | HH177B | URBAN | Asset failure | LV | 24.00 | 84.0 | 0.003108 | 0.0000370 | No
02/11/2023 | 10:42 | MI31 | LONG RURAL | Planned |  | 46.00 | 39.0 | 0.012874 | 0.0003301 | No
02/11/2023 | 10:53 | ME200A | URBAN | Asset failure | LV | 2.00 | 40.0 | 0.000123 | 0.0000031 | No
02/11/2023 | 12:38 | MV62 | SHORT RURAL | Unknown | Unknown | 1.00 | 162.0 | 0.001140 | 0.0000070 | No
02/11/2023 | 12:48 | BT18 | LONG RURAL | Unknown | Unknown | 1.00 | 164.0 | 0.001177 | 0.0000072 | No
02/11/2023 | 13:21 | AP372A | URBAN | Asset failure | LV | 28.00 | 110.7 | 0.004778 | 0.0000432 | No
02/11/2023 | 14:23 | LX53 | SHORT RURAL | Asset failure | LV | 5.00 | 125.0 | 0.004397 | 0.0000352 | No
02/11/2023 | 14:31 | HH145A | URBAN | Asset failure | LV | 2.00 | 308.0 | 0.000950 | 0.0000031 | No
02/11/2023 | 14:32 | EL08G | URBAN | Planned |  | 23.00 | 1.0 | 0.000035 | 0.0000355 | No
02/11/2023 | 15:26 | ME131D | URBAN | Asset failure | LV | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
02/11/2023 | 15:30 | HH130B | URBAN | Overloads |  | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
02/11/2023 | 15:35 | HH130B | URBAN | Unknown | Unknown | 38.67 | 83.0 | 0.004948 | 0.0000596 | No
02/11/2023 | 16:22 | ST35 | LONG RURAL | Unknown | Unknown | 1.00 | 374.0 | 0.002684 | 0.0000072 | No
02/11/2023 | 16:22 | SG12 | SHORT RURAL | Asset failure | LV | 2.00 | 156.0 | 0.002195 | 0.0000141 | No
02/11/2023 | 17:17 | NL111C | URBAN | Asset failure | LV | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
02/11/2023 | 17:43 | SD33100 | LONG RURAL | Unknown | Unknown | 6.00 | 234.0 | 0.010076 | 0.0000431 | No
02/11/2023 | 20:53 | EL01R | URBAN | Animal | Animal impact | 64.67 | 199.0 | 0.019840 | 0.0000997 | No
02/11/2023 | 21:01 | HH386A | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
02/11/2023 | 21:57 | LC04 | LONG RURAL | Unknown | Unknown | 2.00 | 631.0 | 0.009057 | 0.0000144 | No
02/11/2023 | 22:41 | AP149F | URBAN | Planned |  | 31.00 | 8.0 | 0.000382 | 0.0000478 | No
02/11/2023 | 22:51 | CBD367M | CBD | Planned |  | 1.00 | 277.0 | 0.040020 | 0.0001445 | No
02/11/2023 | 23:41 | ME427F | URBAN | Third Party | Vehicle impact | 1,679.00 | 79.4 | 0.205531 | 0.0025886 | No
03/11/2023 | 00:24 | GA09 | LONG RURAL | Unknown | Unknown | 1,016.00 | 191.0 | 1.392610 | 0.0072912 | No
03/11/2023 | 00:42 | HH429C | URBAN | Asset failure | LV | 53.00 | 205.8 | 0.016814 | 0.0000817 | No
03/11/2023 | 00:51 | NL210A | URBAN | Animal | Animal impact | 10.00 | 129.0 | 0.001989 | 0.0000154 | No
03/11/2023 | 03:21 | KA31 | LONG RURAL | Asset failure | LV | 1.00 | 436.0 | 0.003129 | 0.0000072 | No
03/11/2023 | 08:11 | MB03 | LONG RURAL | Overloads |  | 1.00 | 812.0 | 0.005827 | 0.0000072 | No
03/11/2023 | 08:33 | MG43 | URBAN | Asset failure | LV | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
03/11/2023 | 08:39 | WHY363A | SHORT RURAL | Planned |  | 55.00 | 116.0 | 0.044886 | 0.0003870 | No
03/11/2023 | 08:56 | CD17 | LONG RURAL | Planned |  | 7.00 | 166.0 | 0.008339 | 0.0000502 | No
03/11/2023 | 09:52 | SD35200 | LONG RURAL | Planned |  | 5.00 | 211.0 | 0.007571 | 0.0000359 | No
03/11/2023 | 10:13 | WK44 | SHORT RURAL | Asset failure | HV | 2.00 | 9.0 | 0.000127 | 0.0000141 | No
03/11/2023 | 10:31 | CN43 | LONG RURAL | Animal | Animal impact | 4.00 | 433.0 | 0.012429 | 0.0000287 | No
03/11/2023 | 10:55 | VH17 | SHORT RURAL | Asset failure | HV | 298.00 | 126.0 | 0.264162 | 0.0020966 | No
03/11/2023 | 11:20 | MI12 | LONG RURAL | Planned |  | 79.00 | 89.0 | 0.050457 | 0.0005669 | No
03/11/2023 | 11:22 | CN02 | LONG RURAL | Planned |  | 81.00 | 177.0 | 0.102887 | 0.0005813 | No
03/11/2023 | 11:35 | AP227A | URBAN | Asset failure | LV | 21.67 | 292.0 | 0.009754 | 0.0000334 | No
03/11/2023 | 12:05 | CL13 | LONG RURAL | Planned |  | 2.00 | 79.0 | 0.001134 | 0.0000144 | No
03/11/2023 | 12:14 | SD33100 | LONG RURAL | Planned |  | 14.00 | 74.0 | 0.007435 | 0.0001005 | No
03/11/2023 | 13:14 | AP529D | URBAN | Asset failure | HV | 1,486.00 | 234.9 | 0.538155 | 0.0022910 | No
03/11/2023 | 13:49 | MV32 | SHORT RURAL | Unknown | Unknown | 116.00 | 178.0 | 0.145269 | 0.0008161 | No
03/11/2023 | 14:57 | AP344F | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
03/11/2023 | 15:56 | BM33 | SHORT RURAL | Asset failure | HV | 8.00 | 61.0 | 0.003433 | 0.0000563 | No
03/11/2023 | 16:42 | AP149A | URBAN | Asset failure | LV | 1.00 | 233.0 | 0.000359 | 0.0000015 | No
03/11/2023 | 17:01 | SM402C | URBAN | Third Party | Vehicle impact | 3.00 | 286.0 | 0.001323 | 0.0000046 | No
03/11/2023 | 17:44 | AP424C | URBAN | Asset failure | LV | 2.00 | 188.0 | 0.000580 | 0.0000031 | No
03/11/2023 | 18:15 | WHY10 | URBAN | Vegetation | Grow-in - NSP responsibility | 38.00 | 216.0 | 0.012655 | 0.0000586 | No
03/11/2023 | 18:49 | LM62 | LONG RURAL | Asset failure | LV | 5.00 | 103.0 | 0.003696 | 0.0000359 | No
03/11/2023 | 19:14 | NL234B | URBAN | Asset failure | LV | 14.67 | 106.0 | 0.002397 | 0.0000226 | No
03/11/2023 | 19:52 | ME131A | URBAN | Asset failure | LV | 75.00 | 102.2 | 0.011814 | 0.0001156 | No
03/11/2023 | 21:01 | WHY14 | URBAN | Asset failure | LV | 1.00 | 917.0 | 0.001414 | 0.0000015 | No
03/11/2023 | 21:37 | MTB53 | LONG RURAL | Asset failure | LV | 1.00 | 1,126.0 | 0.008081 | 0.0000072 | No
03/11/2023 | 22:24 | SM126C | URBAN | Third Party | Other | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
03/11/2023 | 22:25 | MV53 | SHORT RURAL | Unknown | Unknown | 1.00 | 217.0 | 0.001527 | 0.0000070 | No
03/11/2023 | 22:26 | MV53 | SHORT RURAL | Unknown | Unknown | 1.00 | 219.0 | 0.001541 | 0.0000070 | No
03/11/2023 | 23:34 | SM126C | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
03/11/2023 | 23:37 | SM126C | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
04/11/2023 | 08:31 | NA52 | LONG RURAL | Asset failure | LV | 1.00 | 279.0 | 0.002002 | 0.0000072 | No
04/11/2023 | 08:45 | MB63 | LONG RURAL | Other |  | 6.33 | 232.0 | 0.010544 | 0.0000455 | No
04/11/2023 | 08:56 | HH121G | URBAN | Weather |  | 2.00 | 434.0 | 0.001338 | 0.0000031 | No
04/11/2023 | 09:44 | VH45 | SHORT RURAL | Animal | Animal impact | 51.00 | 2,302.7 | 0.826248 | 0.0003588 | No
04/11/2023 | 09:46 | BU01 | LONG RURAL | Weather |  | 1.00 | 166.0 | 0.001191 | 0.0000072 | No
04/11/2023 | 10:41 | VH17 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 298.00 | 59.9 | 0.125668 | 0.0020966 | No
04/11/2023 | 10:46 | HH121G | URBAN | Weather |  | 225.00 | 147.3 | 0.051103 | 0.0003469 | No
04/11/2023 | 11:17 | LX41 | SHORT RURAL | Unknown | Unknown | 4.00 | 107.0 | 0.003011 | 0.0000281 | No
04/11/2023 | 12:46 | KI31 | SHORT RURAL | Asset failure | LV | 1.00 | 2,202.0 | 0.015492 | 0.0000070 | No
04/11/2023 | 15:17 | HH177B | URBAN | Asset failure | LV | 1.00 | 564.0 | 0.000870 | 0.0000015 | No
04/11/2023 | 15:24 | HH130B | URBAN | Asset failure | LV | 1.00 | 484.0 | 0.000746 | 0.0000015 | No
04/11/2023 | 16:52 | AP355A | URBAN | Asset failure | LV | 18.00 | 75.0 | 0.002081 | 0.0000278 | No
04/11/2023 | 18:04 | AP149C | URBAN | Vegetation | Grow-in - NSP responsibility | 13.33 | 83.0 | 0.001706 | 0.0000206 | No
04/11/2023 | 18:13 | MV32 | SHORT RURAL | Asset failure | LV | 2.00 | 113.0 | 0.001590 | 0.0000141 | No
04/11/2023 | 18:36 | EL11 | URBAN | Overloads |  | 9.00 | 227.0 | 0.003150 | 0.0000139 | No
04/11/2023 | 22:30 | HH107D | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
05/11/2023 | 06:36 | YK22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 59.33 | 138.3 | 0.057733 | 0.0004174 | No
05/11/2023 | 09:02 | PL04 | URBAN | Planned |  | 134.00 | 352.0 | 0.072721 | 0.0002066 | No
05/11/2023 | 09:12 | GA02 | SHORT RURAL | Planned |  | 33.00 | 208.0 | 0.048292 | 0.0002322 | No
05/11/2023 | 09:23 | AP529D | URBAN | Asset failure | HV | 137.00 | 104.4 | 0.022058 | 0.0002112 | No
05/11/2023 | 09:29 | EL11 | URBAN | Asset failure | LV | 1.00 | 165.0 | 0.000254 | 0.0000015 | No
05/11/2023 | 09:46 | G08 | LONG RURAL | Planned |  | 2.00 | 180.0 | 0.002583 | 0.0000144 | No
05/11/2023 | 09:46 | VH22 | SHORT RURAL | Third Party | Vehicle impact | 71.00 | 541.3 | 0.270381 | 0.0004995 | No
05/11/2023 | 10:38 | AP365D1 | URBAN | Planned |  | 6.00 | 6.2 | 0.000057 | 0.0000093 | No
05/11/2023 | 11:06 | WK32 | SHORT RURAL | Asset failure | LV | 1.00 | 281.0 | 0.001977 | 0.0000070 | No
05/11/2023 | 13:13 | SA19 | URBAN | Third Party | Unauthorised access | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
05/11/2023 | 15:35 | WHY05 | URBAN | Asset failure | LV | 1.00 | 239.0 | 0.000368 | 0.0000015 | No
05/11/2023 | 16:46 | SM350H | URBAN | Asset failure | LV | 1.00 | 315.0 | 0.000486 | 0.0000015 | No
05/11/2023 | 20:01 | SA20 | URBAN | Asset failure | LV | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
05/11/2023 | 21:42 | AP365D2 | URBAN | Network business | Switching and protection error | 1.00 | 216.0 | 0.000333 | 0.0000015 | No
05/11/2023 | 22:02 | HH386D | URBAN | Weather |  | 92.00 | 181.5 | 0.025750 | 0.0001418 | No
06/11/2023 | 00:36 | GA02 | SHORT RURAL | Unknown | Unknown | 208.00 | 35.6 | 0.052063 | 0.0014634 | No
06/11/2023 | 01:01 | MI08 | LONG RURAL | Planned |  | 1,236.00 | 113.4 | 1.005547 | 0.0088699 | No
06/11/2023 | 01:47 | SB17 | LONG RURAL | Unknown | Unknown | 91.00 | 363.3 | 0.237221 | 0.0006530 | No
06/11/2023 | 02:18 | NU34 | LONG RURAL | Animal | Animal impact | 74.33 | 111.0 | 0.059212 | 0.0005334 | No
06/11/2023 | 06:16 | CD23 | LONG RURAL | Unknown | Unknown | 50.00 | 243.0 | 0.087192 | 0.0003588 | No
06/11/2023 | 07:39 | MB01 | LONG RURAL | Animal | Animal impact | 51.00 | 279.0 | 0.102112 | 0.0003660 | No
06/11/2023 | 08:08 | AP214C | URBAN | Planned |  | 6.00 | 369.0 | 0.003413 | 0.0000093 | No
06/11/2023 | 08:10 | GA02 | SHORT RURAL | Animal | Animal impact | 3.00 | 166.0 | 0.003504 | 0.0000211 | No
06/11/2023 | 08:28 | SA36 | URBAN | Planned |  | 18.00 | 208.1 | 0.005774 | 0.0000278 | No
06/11/2023 | 08:45 | NA04 | LONG RURAL | Planned |  | 2.00 | 163.0 | 0.002339 | 0.0000144 | No
06/11/2023 | 08:47 | VH43 | SHORT RURAL | Unknown | Unknown | 13.00 | 205.0 | 0.018750 | 0.0000915 | No
06/11/2023 | 08:50 | MTB14 | SHORT RURAL | Planned |  | 2.00 | 16.0 | 0.000225 | 0.0000141 | No
06/11/2023 | 08:56 | BT04 | LONG RURAL | Planned |  | 15.00 | 159.0 | 0.017116 | 0.0001076 | No
06/11/2023 | 09:20 | CM25 | LONG RURAL | Planned |  | 16.00 | 186.6 | 0.021421 | 0.0001148 | No
06/11/2023 | 09:27 | CL05 | LONG RURAL | Planned |  | 68.00 | 351.0 | 0.171285 | 0.0004880 | No
06/11/2023 | 09:30 | HH432F | URBAN | Asset failure | LV | 1.00 | 92.0 | 0.000142 | 0.0000015 | No
06/11/2023 | 09:54 | VH22 | SHORT RURAL | Planned |  | 3.00 | 159.0 | 0.003356 | 0.0000211 | No
06/11/2023 | 09:54 | SA17 | URBAN | Overloads |  | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
06/11/2023 | 10:02 | W26 | LONG RURAL | Planned |  | 3.00 | 133.0 | 0.002863 | 0.0000215 | No
06/11/2023 | 10:14 | SD50000 | URBAN | Planned |  | 2.00 | 132.0 | 0.000407 | 0.0000031 | No
06/11/2023 | 10:29 | GU31 | LONG RURAL | Planned |  | 39.00 | 141.0 | 0.039463 | 0.0002799 | No
06/11/2023 | 10:30 | GA09 | LONG RURAL | Unknown | Unknown | 1.00 | 106.0 | 0.000761 | 0.0000072 | No
06/11/2023 | 10:33 | NA21 | LONG RURAL | Planned |  | 1.00 | 116.0 | 0.000832 | 0.0000072 | No
06/11/2023 | 11:27 | HH121D | URBAN | Asset failure | LV | 1.00 | 202.0 | 0.000311 | 0.0000015 | No
06/11/2023 | 12:06 | ME131C | URBAN | Asset failure | LV | 24.00 | 52.0 | 0.001924 | 0.0000370 | No
06/11/2023 | 12:33 | MB01 | LONG RURAL | Unknown | Unknown | 51.00 | 288.6 | 0.105628 | 0.0003660 | No
06/11/2023 | 13:01 | NL111C | URBAN | Asset failure | LV | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
06/11/2023 | 13:17 | SD40400 | LONG RURAL | Unknown | Unknown | 135.67 | 99.2 | 0.096569 | 0.0009736 | No
06/11/2023 | 13:45 | HH145A | URBAN | Asset failure | LV | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
06/11/2023 | 14:18 | SM126C | URBAN | Asset failure | LV | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
06/11/2023 | 14:50 | GU36 | LONG RURAL | Planned |  | 2.00 | 5.0 | 0.000072 | 0.0000144 | No
06/11/2023 | 15:23 | GA800C | SHORT RURAL | Asset failure | LV | 1.00 | 291.0 | 0.002047 | 0.0000070 | No
06/11/2023 | 16:09 | BM15 | SHORT RURAL | Animal | Animal impact | 4.00 | 15.0 | 0.000422 | 0.0000281 | No
06/11/2023 | 16:21 | AP372D | URBAN | Asset failure | LV | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
06/11/2023 | 16:22 | LX42 | SHORT RURAL | Animal | Animal impact | 214.67 | 52.0 | 0.078582 | 0.0015103 | No
06/11/2023 | 16:47 | SA16 | URBAN | Asset failure | LV | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
06/11/2023 | 17:16 | NL451A | URBAN | Asset failure | LV | 1.00 | 417.0 | 0.000643 | 0.0000015 | No
06/11/2023 | 17:37 | SM374E | URBAN | Asset failure | LV | 1.00 | 1,310.0 | 0.002020 | 0.0000015 | No
06/11/2023 | 18:39 | SM350F | URBAN | Asset failure | LV | 33.00 | 224.0 | 0.011397 | 0.0000509 | No
06/11/2023 | 18:59 | M81 | LONG RURAL | Unknown | Unknown | 1.00 | 269.0 | 0.001930 | 0.0000072 | No
06/11/2023 | 20:25 | NU06 | LONG RURAL | Weather |  | 2.00 | 498.0 | 0.007148 | 0.0000144 | No
06/11/2023 | 21:10 | HH522C | URBAN | Other |  | 10.00 | 94.0 | 0.001449 | 0.0000154 | No
06/11/2023 | 21:10 | WK33 | SHORT RURAL | Animal | Animal impact | 2.67 | 164.0 | 0.003077 | 0.0000188 | No
06/11/2023 | 21:29 | AP365D2 | URBAN | Planned |  | 3.00 | 334.0 | 0.001545 | 0.0000046 | No
06/11/2023 | 23:10 | PL07 | URBAN | Asset failure | LV | 10.33 | 151.0 | 0.002406 | 0.0000159 | No
07/11/2023 | 00:39 | SA32 | URBAN | Animal | Animal impact | 58.00 | 83.0 | 0.007422 | 0.0000894 | No
07/11/2023 | 05:58 | NU02 | LONG RURAL | Animal | Animal impact | 47.00 | 203.0 | 0.068469 | 0.0003373 | No
07/11/2023 | 06:03 | WK33 | SHORT RURAL | Animal | Animal impact | 2.67 | 399.0 | 0.007486 | 0.0000188 | No
07/11/2023 | 08:10 | MTB14 | SHORT RURAL | Planned |  | 450.00 | 243.5 | 0.770766 | 0.0031660 | No
07/11/2023 | 08:37 | VH31 | SHORT RURAL | Asset failure | LV | 1.00 | 171.0 | 0.001203 | 0.0000070 | No
07/11/2023 | 08:41 | NL115C | URBAN | Asset failure | LV | 65.00 | 51.0 | 0.005111 | 0.0001002 | No
07/11/2023 | 08:57 | CN42 | LONG RURAL | Overloads |  | 2.33 | 357.0 | 0.005978 | 0.0000167 | No
07/11/2023 | 09:06 | PP09 | LONG RURAL | Planned |  | 116.00 | 139.2 | 0.115883 | 0.0008325 | No
07/11/2023 | 09:21 | NL451C | URBAN | Planned |  | 1.00 | 49.0 | 0.000076 | 0.0000015 | No
07/11/2023 | 09:30 | GA15 | SHORT RURAL | Planned |  | 15.00 | 335.0 | 0.035353 | 0.0001055 | No
07/11/2023 | 10:03 | SD38200 | LONG RURAL | Planned |  | 5.00 | 217.0 | 0.007786 | 0.0000359 | No
07/11/2023 | 10:07 | MI26 | LONG RURAL | Planned |  | 25.00 | 292.0 | 0.052387 | 0.0001794 | No
07/11/2023 | 10:54 | CN32 | LONG RURAL | Planned |  | 22.00 | 145.0 | 0.022892 | 0.0001579 | No
07/11/2023 | 11:03 | M04 | LONG RURAL | Planned |  | 108.00 | 190.8 | 0.147840 | 0.0007750 | No
07/11/2023 | 11:47 | MTB13 | SHORT RURAL | Asset failure | LV | 1.00 | 132.0 | 0.000929 | 0.0000070 | No
07/11/2023 | 12:02 | WHY04 | URBAN | Unknown | Unknown | 1.00 | 150.0 | 0.000231 | 0.0000015 | No
07/11/2023 | 12:23 | SD49100 | LONG RURAL | Asset failure | Subtransmission | 311.00 | 52.0 | 0.116056 | 0.0022318 | No
07/11/2023 | 13:14 | GA50 | URBAN | Asset failure | LV | 1.00 | 332.0 | 0.000512 | 0.0000015 | No
07/11/2023 | 13:46 | G09 | LONG RURAL | Weather |  | 50.00 | 16.1 | 0.005777 | 0.0003588 | No
07/11/2023 | 14:22 | SA16 | URBAN | Asset failure | LV | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
07/11/2023 | 16:14 | CV753A | LONG RURAL | Third Party | Vehicle impact | 1.00 | 186.0 | 0.001335 | 0.0000072 | No
07/11/2023 | 17:43 | VH15 | SHORT RURAL | Asset failure | LV | 1.00 | 299.0 | 0.002104 | 0.0000070 | No
07/11/2023 | 17:56 | SD52300 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 343.0 | 0.002461 | 0.0000072 | No
07/11/2023 | 19:54 | SA744D | URBAN | Asset failure | LV | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
07/11/2023 | 20:57 | YK21 | LONG RURAL | Asset failure | HV | 3.00 | 22.0 | 0.000474 | 0.0000215 | No
08/11/2023 | 00:06 | SD52300 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3,036.00 | 122.2 | 2.663308 | 0.0217873 | No
08/11/2023 | 00:06 | SD52300 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 613.00 | 122.0 | 0.526156 | 0.0043128 | No
08/11/2023 | 00:13 | CBD366J | CBD | Planned |  | 13.00 | 73.0 | 0.137109 | 0.0018782 | No
08/11/2023 | 00:13 | CBD366J | URBAN | Planned |  | 44.00 | 73.0 | 0.004952 | 0.0000678 | No
08/11/2023 | 06:20 | VH15 | SHORT RURAL | Planned |  | 105.00 | 123.2 | 0.090983 | 0.0007387 | No
08/11/2023 | 07:23 | SB17 | LONG RURAL | Weather |  | 91.00 | 440.2 | 0.287441 | 0.0006530 | No
08/11/2023 | 07:32 | CBD412B | URBAN | Third Party | Unauthorised access | 47.00 | 108.0 | 0.007826 | 0.0000725 | No
08/11/2023 | 08:19 | PL07 | URBAN | Planned |  | 52.00 | 216.0 | 0.017317 | 0.0000802 | No
08/11/2023 | 08:32 | BM51 | URBAN | Planned |  | 11.00 | 245.0 | 0.004155 | 0.0000170 | No
08/11/2023 | 09:03 | ME116C | URBAN | Asset failure | LV | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
08/11/2023 | 09:29 | SD54300 | LONG RURAL | Planned |  | 2.00 | 96.0 | 0.001378 | 0.0000144 | No
08/11/2023 | 09:34 | MTB51 | LONG RURAL | Asset failure | LV | 1.33 | 41.0 | 0.000392 | 0.0000096 | No
08/11/2023 | 09:39 | MV61 | SHORT RURAL | Planned |  | 18.00 | 269.0 | 0.034066 | 0.0001266 | No
08/11/2023 | 09:39 | MV61 | URBAN | Planned |  | 352.00 | 71.4 | 0.038735 | 0.0005427 | No
08/11/2023 | 10:02 | GA28 | LONG RURAL | Planned |  | 3.00 | 259.7 | 0.005590 | 0.0000215 | No
08/11/2023 | 10:04 | NA58 | LONG RURAL | Unknown | Unknown | 20.00 | 383.0 | 0.054971 | 0.0001435 | No
08/11/2023 | 10:42 | MTB52 | LONG RURAL | Planned |  | 1.00 | 94.0 | 0.000675 | 0.0000072 | No
08/11/2023 | 10:56 | VH23 | SHORT RURAL | Other |  | 24.00 | 62.4 | 0.010539 | 0.0001689 | No
08/11/2023 | 12:07 | CV18 | SHORT RURAL | Other |  | 2.00 | 24.0 | 0.000338 | 0.0000141 | No
08/11/2023 | 14:23 | CL07 | LONG RURAL | Planned |  | 2.00 | 157.0 | 0.002253 | 0.0000144 | No
08/11/2023 | 14:39 | SM350C | URBAN | Asset failure | LV | 1.00 | 157.0 | 0.000242 | 0.0000015 | No
08/11/2023 | 14:41 | ME200F | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
08/11/2023 | 15:59 | BM11 | SHORT RURAL | Other |  | 1.00 | 6.0 | 0.000042 | 0.0000070 | No
08/11/2023 | 16:09 | SG07 | SHORT RURAL | Unknown | Unknown | 2.33 | 149.0 | 0.002446 | 0.0000164 | No
08/11/2023 | 16:45 | GU43 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 5.33 | 181.0 | 0.006928 | 0.0000383 | No
08/11/2023 | 16:46 | HH177G | URBAN | Overloads |  | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
08/11/2023 | 18:07 | MV52 | SHORT RURAL | Asset failure | LV | 14.00 | 40.0 | 0.003940 | 0.0000985 | No
08/11/2023 | 18:24 | HH102D | URBAN | Asset failure | LV | 34.00 | 97.0 | 0.005085 | 0.0000524 | No
08/11/2023 | 18:50 | SG07 | SHORT RURAL | Unknown | Unknown | 2.33 | 185.0 | 0.003037 | 0.0000164 | No
08/11/2023 | 19:21 | CL22 | LONG RURAL | Asset failure | LV | 1.00 | 332.0 | 0.002383 | 0.0000072 | No
08/11/2023 | 19:34 | SM350E | URBAN | Asset failure | LV | 43.00 | 131.0 | 0.008685 | 0.0000663 | No
08/11/2023 | 19:57 | EL16 | URBAN | Overloads |  | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
08/11/2023 | 20:07 | SM411C | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
08/11/2023 | 21:09 | SM402D | URBAN | Planned |  | 69.00 | 169.5 | 0.018029 | 0.0001064 | No
08/11/2023 | 22:37 | NL234A | URBAN | Asset failure | LV | 7.33 | 42.0 | 0.000475 | 0.0000113 | No
09/11/2023 | 01:07 | SM137F | URBAN | Planned |  | 157.00 | 147.1 | 0.035596 | 0.0002421 | No
09/11/2023 | 04:10 | SG07 | SHORT RURAL | Asset failure | LV | 2.33 | 601.0 | 0.009866 | 0.0000164 | No
09/11/2023 | 05:36 | NL210B | URBAN | Asset failure | LV | 1.00 | 403.0 | 0.000621 | 0.0000015 | No
09/11/2023 | 08:26 | HK04 | LONG RURAL | Planned |  | 30.00 | 179.0 | 0.038537 | 0.0002153 | No
09/11/2023 | 08:39 | CD19 | LONG RURAL | Planned |  | 76.00 | 308.6 | 0.168299 | 0.0005454 | No
09/11/2023 | 08:40 | GA01 | URBAN | Planned |  | 65.00 | 135.0 | 0.013529 | 0.0001002 | No
09/11/2023 | 08:45 | NL451C | URBAN | Unknown | Unknown | 1.00 | 362.0 | 0.000558 | 0.0000015 | No
09/11/2023 | 08:45 | SM216C | URBAN | Planned |  | 70.00 | 275.0 | 0.029679 | 0.0001079 | No
09/11/2023 | 08:48 | MV64 | SHORT RURAL | Planned |  | 221.00 | 258.9 | 0.402522 | 0.0015548 | No
09/11/2023 | 08:48 | MV64 | URBAN | Planned |  | 32.00 | 270.0 | 0.013321 | 0.0000493 | No
09/11/2023 | 08:52 | MG10 | LONG RURAL | Planned |  | 6.00 | 340.5 | 0.014661 | 0.0000431 | No
09/11/2023 | 08:55 | VH15 | SHORT RURAL | Planned |  | 66.00 | 424.6 | 0.197149 | 0.0004643 | No
09/11/2023 | 08:56 | VH15 | SHORT RURAL | Planned |  | 97.00 | 435.0 | 0.296863 | 0.0006824 | No
09/11/2023 | 08:57 | SD38100 | LONG RURAL | Planned |  | 5.00 | 389.0 | 0.013958 | 0.0000359 | No
09/11/2023 | 09:23 | WK33 | SHORT RURAL | Animal | Animal impact | 2.67 | 215.0 | 0.004034 | 0.0000188 | No
09/11/2023 | 09:34 | NU35 | LONG RURAL | Planned |  | 75.00 | 199.0 | 0.107107 | 0.0005382 | No
09/11/2023 | 09:49 | VH43 | SHORT RURAL | Planned |  | 67.00 | 227.0 | 0.107003 | 0.0004714 | No
09/11/2023 | 10:05 | YK23 | LONG RURAL | Planned |  | 56.00 | 272.0 | 0.109310 | 0.0004019 | No
09/11/2023 | 10:23 | CN42 | LONG RURAL | Planned |  | 2.00 | 155.0 | 0.002225 | 0.0000144 | No
09/11/2023 | 10:35 | CN52 | LONG RURAL | Unknown | Unknown | 2.00 | 12.0 | 0.000172 | 0.0000144 | No
09/11/2023 | 11:14 | NL451E | URBAN | Unknown | Unknown | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
09/11/2023 | 11:27 | MI17 | LONG RURAL | Planned |  | 1.00 | 69.0 | 0.000495 | 0.0000072 | No
09/11/2023 | 11:53 | NL544B | URBAN | Third Party | Dig-in | 1.00 | 504.0 | 0.000777 | 0.0000015 | No
09/11/2023 | 12:57 | NL451E | URBAN | Unknown | Unknown | 108.00 | 94.6 | 0.015753 | 0.0001665 | No
09/11/2023 | 12:58 | MG19 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 4,515.0 | 0.032401 | 0.0000072 | No
09/11/2023 | 13:08 | HH177C | URBAN | Overloads |  | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
09/11/2023 | 13:21 | SA711C | URBAN | Planned |  | 107.00 | 85.2 | 0.014056 | 0.0001650 | No
09/11/2023 | 13:22 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 97.0 | 0.000682 | 0.0000070 | No
09/11/2023 | 13:28 | KA31 | LONG RURAL | Asset failure | LV | 2.00 | 63.0 | 0.000904 | 0.0000144 | No
09/11/2023 | 13:44 | SA711C | URBAN | Unknown | Unknown | 1.00 | 36.0 | 0.000056 | 0.0000015 | No
09/11/2023 | 14:15 | ME427F | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
09/11/2023 | 15:33 | GA24 | LONG RURAL | Overloads |  | 2.00 | 515.0 | 0.007392 | 0.0000144 | No
09/11/2023 | 16:12 | SM349D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
09/11/2023 | 16:59 | NL115C | URBAN | Asset failure | LV | 1.00 | 299.0 | 0.000461 | 0.0000015 | No
09/11/2023 | 18:34 | GU42 | LONG RURAL | Unknown | Unknown | 2.67 | 200.0 | 0.003827 | 0.0000191 | No
09/11/2023 | 19:57 | HH177G | URBAN | Asset failure | LV | 67.00 | 50.0 | 0.005165 | 0.0001033 | No
09/11/2023 | 20:13 | MI11 | LONG RURAL | Unknown | Unknown | 43.00 | 301.0 | 0.092883 | 0.0003086 | No
09/11/2023 | 20:43 | HH522C | URBAN | Overloads |  | 1.00 | 34.0 | 0.000052 | 0.0000015 | No
09/11/2023 | 21:26 | VH23 | SHORT RURAL | Asset failure | HV | 1,034.00 | 106.6 | 0.775600 | 0.0072747 | No
09/11/2023 | 21:26 | VH23 | SHORT RURAL | Asset failure | HV | 366.00 | 906.7 | 2.334735 | 0.0025750 | No
09/11/2023 | 23:27 | ME347C | URBAN | Asset failure | LV | 127.00 | 178.5 | 0.034953 | 0.0001958 | No
10/11/2023 | 00:29 | NL115F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 129.33 | 192.0 | 0.038285 | 0.0001994 | No
10/11/2023 | 00:39 | HH145B | URBAN | Asset failure | LV | 26.00 | 95.0 | 0.003808 | 0.0000401 | No
10/11/2023 | 03:45 | HH145A | URBAN | Unknown | Unknown | 44.00 | 282.0 | 0.019130 | 0.0000678 | No
10/11/2023 | 04:30 | EL23 | URBAN | Asset failure | LV | 1.67 | 315.0 | 0.000809 | 0.0000026 | No
10/11/2023 | 05:50 | VH23 | SHORT RURAL | Unknown | Unknown | 322.00 | 3.0 | 0.006796 | 0.0022654 | No
10/11/2023 | 06:12 | SG13 | SHORT RURAL | Animal | Animal impact | 8.00 | 224.0 | 0.012608 | 0.0000563 | No
10/11/2023 | 07:30 | BT02 | LONG RURAL | Animal | Animal impact | 198.67 | 3.2 | 0.004504 | 0.0014257 | No
10/11/2023 | 08:49 | PL23 | LONG RURAL | Planned |  | 12.00 | 278.0 | 0.023940 | 0.0000861 | No
10/11/2023 | 08:58 | SG13 | SHORT RURAL | Animal | Animal impact | 18.00 | 6.0 | 0.000760 | 0.0001266 | No
10/11/2023 | 09:08 | KA13 | LONG RURAL | Planned |  | 1.00 | 31.0 | 0.000222 | 0.0000072 | No
10/11/2023 | 09:10 | ME131D | URBAN | Planned |  | 1.00 | 331.0 | 0.000510 | 0.0000015 | No
10/11/2023 | 09:30 | MTB22 | SHORT RURAL | Planned |  | 2.00 | 180.0 | 0.002533 | 0.0000141 | No
10/11/2023 | 09:37 | HH496A | URBAN | Asset failure | LV | 13.00 | 85.0 | 0.001704 | 0.0000200 | No
10/11/2023 | 09:38 | MB63 | LONG RURAL | Planned |  | 1.00 | 242.0 | 0.001737 | 0.0000072 | No
10/11/2023 | 09:43 | SA14 | URBAN | Planned |  | 375.00 | 24.3 | 0.014027 | 0.0005782 | No
10/11/2023 | 10:07 | MG41 | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
10/11/2023 | 10:09 | CBD367Q | CBD | Asset failure | LV | 2.00 | 302.0 | 0.087264 | 0.0002890 | No
10/11/2023 | 10:27 | CV24 | LONG RURAL | Asset failure | HV | 82.00 | 883.0 | 0.519595 | 0.0005885 | No
10/11/2023 | 10:44 | AP226D | URBAN | Asset failure | LV | 1.00 | 429.0 | 0.000661 | 0.0000015 | No
10/11/2023 | 10:57 | CL10 | LONG RURAL | Planned |  | 1.00 | 82.0 | 0.000588 | 0.0000072 | No
10/11/2023 | 10:58 | SD38200 | LONG RURAL | Unknown | Unknown | 1.00 | 9.0 | 0.000065 | 0.0000072 | No
10/11/2023 | 11:44 | HH341B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 824.00 | 55.0 | 0.069872 | 0.0012704 | No
10/11/2023 | 11:53 | YK01 | LONG RURAL | Asset failure | LV | 1.00 | 228.0 | 0.001636 | 0.0000072 | No
10/11/2023 | 12:20 | BT01 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 56.00 | 190.0 | 0.076356 | 0.0004019 | No
10/11/2023 | 12:55 | ST36 | LONG RURAL | Asset failure | HV | 43.33 | 41.0 | 0.012750 | 0.0003110 | No
10/11/2023 | 14:05 | KA22 | LONG RURAL | Asset failure | LV | 1.00 | 283.0 | 0.002031 | 0.0000072 | No
10/11/2023 | 14:17 | HH130C | URBAN | Asset failure | LV | 20.00 | 57.6 | 0.001775 | 0.0000308 | No
10/11/2023 | 14:30 | HH403C | URBAN | Overloads |  | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
10/11/2023 | 14:32 | EL01Z | URBAN | Asset failure | HV | 663.00 | 190.0 | 0.194215 | 0.0010222 | No
10/11/2023 | 15:02 | HH121E | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
10/11/2023 | 15:04 | SM172C | URBAN | Third Party | Vehicle impact | 13.00 | 686.6 | 0.013762 | 0.0000200 | No
10/11/2023 | 15:11 | WK31 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 541.00 | 317.3 | 1.207839 | 0.0038062 | No
10/11/2023 | 15:16 | SD39100 | LONG RURAL | Third Party | Vehicle impact | 2,530.00 | 138.0 | 2.505544 | 0.0181561 | No
10/11/2023 | 15:59 | ST22 | SHORT RURAL | Unknown | Unknown | 3.00 | 499.0 | 0.010532 | 0.0000211 | No
10/11/2023 | 16:16 | MI15 | LONG RURAL | Unknown | Unknown | 134.00 | 241.6 | 0.232298 | 0.0009616 | No
10/11/2023 | 16:25 | HH118C | URBAN | Overloads |  | 26.67 | 200.0 | 0.008223 | 0.0000411 | No
10/11/2023 | 16:29 | CV08 | LONG RURAL | Asset failure | HV | 1,009.00 | 334.4 | 2.421408 | 0.0072409 | No
10/11/2023 | 16:29 | CV08 | SHORT RURAL | Asset failure | HV | 32.00 | 324.0 | 0.072944 | 0.0002251 | No
10/11/2023 | 18:19 | BT03 | LONG RURAL | Asset failure | LV | 11.33 | 133.0 | 0.010817 | 0.0000813 | No
10/11/2023 | 18:28 | EL25 | URBAN | Asset failure | LV | 10.00 | 232.9 | 0.003591 | 0.0000154 | No
10/11/2023 | 18:54 | AP227B | URBAN | Asset failure | LV | 8.00 | 1,312.0 | 0.016182 | 0.0000123 | No
10/11/2023 | 18:55 | EL20 | URBAN | Overloads |  | 4.00 | 47.0 | 0.000290 | 0.0000062 | No
10/11/2023 | 19:21 | MG05 | LONG RURAL | Asset failure | HV | 138.00 | 213.1 | 0.211056 | 0.0009903 | No
10/11/2023 | 19:26 | MB72 | LONG RURAL | Unknown | Unknown | 261.00 | 156.0 | 0.292191 | 0.0018730 | No
10/11/2023 | 19:30 | MG24 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,098.0 | 0.007725 | 0.0000070 | No
10/11/2023 | 19:36 | HH386F | URBAN | Vegetation | Grow-in - NSP responsibility | 13.67 | 190.0 | 0.004003 | 0.0000211 | No
10/11/2023 | 20:10 | AP365E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,359.00 | 146.2 | 0.306271 | 0.0020952 | No
10/11/2023 | 20:15 | AP365F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 21.00 | 252.0 | 0.008159 | 0.0000324 | No
10/11/2023 | 20:21 | AP372D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 67.00 | 288.0 | 0.029750 | 0.0001033 | No
10/11/2023 | 20:28 | AP227D | URBAN | Asset failure | LV | 1.00 | 873.0 | 0.001346 | 0.0000015 | No
10/11/2023 | 20:29 | HK06 | LONG RURAL | Overloads |  | 1.00 | 1,042.0 | 0.007478 | 0.0000072 | No
10/11/2023 | 20:57 | BM51 | URBAN | Asset failure | LV | 1.00 | 1,035.0 | 0.001596 | 0.0000015 | No
10/11/2023 | 21:04 | GA25 | SHORT RURAL | Asset failure | LV | 1.00 | 154.0 | 0.001083 | 0.0000070 | No
10/11/2023 | 21:38 | KA02 | SHORT RURAL | Weather |  | 70.67 | 43.0 | 0.021379 | 0.0004972 | No
10/11/2023 | 22:00 | SA38 | URBAN | Third Party | Vehicle impact | 39.00 | 53.0 | 0.003187 | 0.0000601 | No
10/11/2023 | 22:14 | MB72 | LONG RURAL | Unknown | Unknown | 95.00 | 211.3 | 0.144086 | 0.0006818 | No
10/11/2023 | 22:14 | MB72 | LONG RURAL | Asset failure | HV | 260.00 | 614.1 | 1.145766 | 0.0018658 | No
10/11/2023 | 22:14 | MB72 | LONG RURAL | Asset failure | HV | 1.00 | 2,271.0 | 0.016297 | 0.0000072 | No
11/11/2023 | 01:22 | EL10 | URBAN | Asset failure | LV | 43.00 | 286.5 | 0.018991 | 0.0000663 | No
11/11/2023 | 07:41 | HH121H | URBAN | Asset failure | LV | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
11/11/2023 | 08:09 | GA43 | SHORT RURAL | Overloads |  | 1.00 | 627.0 | 0.004411 | 0.0000070 | No
11/11/2023 | 08:14 | HH341K | URBAN | Planned |  | 189.00 | 258.8 | 0.075413 | 0.0002914 | No
11/11/2023 | 08:26 | AP365D2 | URBAN | Planned |  | 10.00 | 189.5 | 0.002922 | 0.0000154 | No
11/11/2023 | 08:50 | MI06 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 198.0 | 0.001421 | 0.0000072 | No
11/11/2023 | 08:54 | AP227D | URBAN | Planned |  | 1.00 | 1,942.0 | 0.002994 | 0.0000015 | No
11/11/2023 | 09:24 | MG46 | SHORT RURAL | Asset failure | LV | 1.00 | 384.0 | 0.002702 | 0.0000070 | No
11/11/2023 | 09:45 | SD59100 | LONG RURAL | Planned |  | 1.00 | 58.0 | 0.000416 | 0.0000072 | No
11/11/2023 | 10:33 | HH107A | URBAN | Asset failure | LV | 4.00 | 670.0 | 0.004132 | 0.0000062 | No
11/11/2023 | 10:38 | BM54 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 273.00 | 133.0 | 0.255452 | 0.0019207 | No
11/11/2023 | 12:27 | HH121H | URBAN | Asset failure | LV | 1.00 | 199.0 | 0.000307 | 0.0000015 | No
11/11/2023 | 14:45 | EL260C | URBAN | Asset failure | LV | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
11/11/2023 | 14:52 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 140.0 | 0.001005 | 0.0000072 | No
11/11/2023 | 17:51 | ST24 | SHORT RURAL | Asset failure | LV | 1.00 | 194.0 | 0.001365 | 0.0000070 | No
11/11/2023 | 18:28 | ME347C | URBAN | Unknown | Unknown | 1.00 | 296.0 | 0.000456 | 0.0000015 | No
11/11/2023 | 18:53 | SD32200 | LONG RURAL | Asset failure | Subtransmission | 496.00 | 328.8 | 1.170517 | 0.0035595 | No
11/11/2023 | 19:32 | CV26 | LONG RURAL | Asset failure | HV | 4.00 | 123.0 | 0.003531 | 0.0000287 | No
11/11/2023 | 19:57 | HH341H | URBAN | Asset failure | LV | 80.00 | 54.0 | 0.006660 | 0.0001233 | No
11/11/2023 | 20:20 | ST34 | LONG RURAL | Asset failure | HV | 66.00 | 386.7 | 0.183169 | 0.0004736 | No
11/11/2023 | 20:28 | NA36 | LONG RURAL | Unknown | Unknown | 1.00 | 239.0 | 0.001715 | 0.0000072 | No
12/11/2023 | 01:34 | EL16 | URBAN | Third Party | Vehicle impact | 57.00 | 344.0 | 0.030231 | 0.0000879 | No
12/11/2023 | 07:24 | NU04 | SHORT RURAL | Animal | Animal impact | 26.00 | 97.0 | 0.017744 | 0.0001829 | No
12/11/2023 | 09:29 | ME347C | URBAN | Overloads |  | 20.00 | 100.0 | 0.003084 | 0.0000308 | No
12/11/2023 | 09:46 | EL21 | URBAN | Planned |  | 1.00 | 7,342.0 | 0.011320 | 0.0000015 | No
12/11/2023 | 10:01 | SG14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 599.0 | 0.012643 | 0.0000211 | No
12/11/2023 | 14:47 | NL115C | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
12/11/2023 | 15:09 | NL210E | URBAN | Asset failure | LV | 30.00 | 70.0 | 0.003238 | 0.0000463 | No
12/11/2023 | 16:03 | AP146C | URBAN | Asset failure | LV | 25.33 | 201.0 | 0.007851 | 0.0000391 | No
12/11/2023 | 17:56 | PA19 | LONG RURAL | Weather |  | 28.00 | 220.5 | 0.044307 | 0.0002009 | No
12/11/2023 | 18:31 | SA17 | URBAN | Overloads |  | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
12/11/2023 | 19:27 | AP146C | URBAN | Asset failure | LV | 18.00 | 84.0 | 0.002331 | 0.0000278 | No
12/11/2023 | 19:32 | SM126E | URBAN | Third Party | Unauthorised access | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
12/11/2023 | 22:43 | AP425A | URBAN | Unknown | Unknown | 1.00 | 57.0 | 0.000088 | 0.0000015 | No
12/11/2023 | 23:44 | SM172F | URBAN | Asset failure | LV | 35.33 | 165.0 | 0.008988 | 0.0000545 | No
13/11/2023 | 06:04 | PP04 | SHORT RURAL | Unknown | Unknown | 74.00 | 139.0 | 0.072367 | 0.0005206 | No
13/11/2023 | 07:26 | EL18 | URBAN | Overloads |  | 4.00 | 84.0 | 0.000518 | 0.0000062 | No
13/11/2023 | 07:45 | SA744C | URBAN | Overloads |  | 1.00 | 384.0 | 0.000592 | 0.0000015 | No
13/11/2023 | 08:27 | GA22 | SHORT RURAL | Unknown | Unknown | 1.00 | 118.0 | 0.000830 | 0.0000070 | No
13/11/2023 | 08:32 | VH15 | SHORT RURAL | Unknown | Unknown | 1.00 | 90.0 | 0.000633 | 0.0000070 | No
13/11/2023 | 08:55 | ST44 | LONG RURAL | Animal | Animal impact | 4.67 | 330.0 | 0.011052 | 0.0000335 | No
13/11/2023 | 09:07 | AP227C | URBAN | Planned |  | 1,023.00 | 95.4 | 0.150435 | 0.0015772 | No
13/11/2023 | 09:21 | NA09 | LONG RURAL | Planned |  | 62.00 | 317.0 | 0.141044 | 0.0004449 | No
13/11/2023 | 09:21 | W31 | SHORT RURAL | Planned |  | 30.00 | 49.0 | 0.010342 | 0.0002111 | No
13/11/2023 | 09:27 | PL15 | LONG RURAL | Planned |  | 1.00 | 321.0 | 0.002304 | 0.0000072 | No
13/11/2023 | 09:35 | ST42 | LONG RURAL | Planned |  | 71.00 | 307.0 | 0.156422 | 0.0005095 | No
13/11/2023 | 09:41 | ST36 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 3.00 | 76.0 | 0.001636 | 0.0000215 | No
13/11/2023 | 09:56 | EL03 | URBAN | Overloads |  | 3.00 | 28.0 | 0.000130 | 0.0000046 | No
13/11/2023 | 10:01 | KI54 | LONG RURAL | Planned |  | 9.00 | 350.0 | 0.022605 | 0.0000646 | No
13/11/2023 | 10:26 | CV25 | LONG RURAL | Planned |  | 1.00 | 129.0 | 0.000926 | 0.0000072 | No
13/11/2023 | 11:13 | MV13 | SHORT RURAL | Unknown | Unknown | 1.00 | 7.0 | 0.000049 | 0.0000070 | No
13/11/2023 | 11:31 | EL01N | URBAN | Asset failure | LV | 2.00 | 187.0 | 0.000577 | 0.0000031 | No
13/11/2023 | 11:38 | M04 | LONG RURAL | Planned |  | 1.00 | 12.0 | 0.000086 | 0.0000072 | No
13/11/2023 | 11:54 | MV15 | SHORT RURAL | Unknown | Unknown | 2.00 | 80.0 | 0.001126 | 0.0000141 | No
13/11/2023 | 12:00 | PA02 | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
13/11/2023 | 12:08 | HH409A | URBAN | Asset failure | LV | 1.00 | 155.0 | 0.000239 | 0.0000015 | No
13/11/2023 | 12:54 | GU41 | LONG RURAL | Overloads |  | 4.00 | 235.0 | 0.006746 | 0.0000287 | No
13/11/2023 | 13:52 | MV64 | SHORT RURAL | Asset failure | LV | 24.33 | 90.0 | 0.015408 | 0.0001712 | No
13/11/2023 | 14:26 | W27 | LONG RURAL | Weather |  | 62.00 | 195.5 | 0.086963 | 0.0004449 | No
13/11/2023 | 14:51 | SA36 | URBAN | Overloads |  | 3.00 | 150.0 | 0.000694 | 0.0000046 | No
13/11/2023 | 14:55 | W25 | LONG RURAL | Unknown | Unknown | 9.00 | 247.0 | 0.015953 | 0.0000646 | No
13/11/2023 | 14:56 | LX41 | SHORT RURAL | Asset failure | LV | 1.00 | 143.0 | 0.001006 | 0.0000070 | No
13/11/2023 | 15:05 | CD23 | LONG RURAL | Weather |  | 50.00 | 994.9 | 0.357001 | 0.0003588 | No
13/11/2023 | 17:03 | BT15 | LONG RURAL | Planned |  | 1.00 | 73.0 | 0.000524 | 0.0000072 | No
13/11/2023 | 17:38 | HH341A | URBAN | Other |  | 4.00 | 12.0 | 0.000074 | 0.0000062 | No
13/11/2023 | 17:57 | HH107A | URBAN | Asset failure | HV | 535.00 | 97.9 | 0.080740 | 0.0008248 | No
13/11/2023 | 18:17 | PL30 | LONG RURAL | Unknown | Unknown | 19.00 | 1,146.8 | 0.156365 | 0.0001364 | No
13/11/2023 | 18:27 | YK14 | LONG RURAL | Weather |  | 41.00 | 643.2 | 0.189240 | 0.0002942 | No
13/11/2023 | 18:43 | SD35400 | SHORT RURAL | Weather |  | 851.00 | 242.5 | 1.452027 | 0.0059872 | No
13/11/2023 | 19:50 | HH145A | URBAN | Unknown | Unknown | 14.67 | 74.0 | 0.001673 | 0.0000226 | No
13/11/2023 | 20:11 | YK28 | LONG RURAL | Unknown | Unknown | 58.00 | 891.1 | 0.370909 | 0.0004162 | No
13/11/2023 | 21:37 | AP829F | URBAN | Planned |  | 57.00 | 333.0 | 0.029264 | 0.0000879 | No
13/11/2023 | 21:40 | PL13 | LONG RURAL | Weather |  | 17.00 | 818.0 | 0.099794 | 0.0001220 | No
13/11/2023 | 21:54 | CN24 | LONG RURAL | Unknown | Unknown | 109.00 | 278.1 | 0.217507 | 0.0007822 | No
13/11/2023 | 22:32 | KI14 | LONG RURAL | Weather |  | 141.00 | 454.2 | 0.459608 | 0.0010119 | No
13/11/2023 | 22:40 | SD35300 | LONG RURAL | Weather |  | 1,259.00 | 148.0 | 1.337180 | 0.0090350 | No
13/11/2023 | 23:01 | MT21 | LONG RURAL | Weather |  | 217.00 | 187.1 | 0.291345 | 0.0015573 | No
13/11/2023 | 23:11 | HH432A | URBAN | Planned |  | 3.00 | 61.0 | 0.000282 | 0.0000046 | No
13/11/2023 | 23:13 | HH107A | URBAN | Overloads |  | 1.00 | 28.0 | 0.000043 | 0.0000015 | No
13/11/2023 | 23:21 | VH22 | SHORT RURAL | Weather |  | 60.00 | 256.0 | 0.108065 | 0.0004221 | No
13/11/2023 | 23:57 | AP424D | URBAN | Weather |  | 1,087.00 | 92.5 | 0.154989 | 0.0016759 | No
14/11/2023 | 00:38 | MV64 | SHORT RURAL | Asset failure | HV | 621.00 | 168.4 | 0.735947 | 0.0043690 | No
14/11/2023 | 01:22 | PL33 | LONG RURAL | Unknown | Unknown | 1.00 | 896.0 | 0.006430 | 0.0000072 | No
14/11/2023 | 01:46 | MG46 | SHORT RURAL | Weather |  | 1,363.00 | 67.2 | 0.644240 | 0.0095894 | No
14/11/2023 | 01:56 | NA56 | LONG RURAL | Weather |  | 1.00 | 9,208.0 | 0.066080 | 0.0000072 | No
14/11/2023 | 03:18 | MI01 | LONG RURAL | Unknown | Unknown | 12.00 | 120.0 | 0.010334 | 0.0000861 | No
14/11/2023 | 04:09 | SD46400 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 21.33 | 126.0 | 0.018911 | 0.0001501 | No
14/11/2023 | 04:44 | VH22 | SHORT RURAL | Unknown | Unknown | 5.67 | 227.0 | 0.009050 | 0.0000399 | No
14/11/2023 | 06:07 | PL20 | LONG RURAL | Weather |  | 39.00 | 604.0 | 0.169046 | 0.0002799 | No
14/11/2023 | 06:19 | YK19 | LONG RURAL | Weather |  | 12.00 | 700.5 | 0.060324 | 0.0000861 | No
14/11/2023 | 06:27 | HH121G | URBAN | Overloads |  | 3.67 | 157.0 | 0.000888 | 0.0000057 | No
14/11/2023 | 07:11 | BM44 | SHORT RURAL | Asset failure | LV | 20.00 | 633.0 | 0.089069 | 0.0001407 | No
14/11/2023 | 07:32 | AP125D | URBAN | Third Party | Vehicle impact | 78.00 | 266.0 | 0.031988 | 0.0001203 | No
14/11/2023 | 07:38 | HH429B | URBAN | Asset failure | LV | 1.00 | 136.0 | 0.000210 | 0.0000015 | No
14/11/2023 | 07:49 | MV64 | SHORT RURAL | Overloads |  | 14.67 | 320.0 | 0.033020 | 0.0001032 | No
14/11/2023 | 07:54 | ME131A | URBAN | Asset failure | LV | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
14/11/2023 | 08:18 | SA744D | URBAN | Planned |  | 208.00 | 476.4 | 0.152789 | 0.0003207 | No
14/11/2023 | 08:31 | W25 | LONG RURAL | Weather |  | 24.00 | 109.4 | 0.018838 | 0.0001722 | No
14/11/2023 | 08:44 | NL115C | URBAN | Planned |  | 142.00 | 361.0 | 0.079033 | 0.0002189 | No
14/11/2023 | 09:06 | MV34 | SHORT RURAL | Planned |  | 8.00 | 254.0 | 0.014296 | 0.0000563 | No
14/11/2023 | 09:13 | LX31 | SHORT RURAL | Planned |  | 1.00 | 92,225.0 | 0.648848 | 0.0000070 | No
14/11/2023 | 09:18 | W24 | LONG RURAL | Unknown | Unknown | 2.00 | 192.0 | 0.002756 | 0.0000144 | No
14/11/2023 | 09:21 | MI32 | LONG RURAL | Planned |  | 4.00 | 124.0 | 0.003559 | 0.0000287 | No
14/11/2023 | 09:36 | HH386E | URBAN | Planned |  | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
14/11/2023 | 10:14 | SD33200 | LONG RURAL | Planned |  | 23.00 | 175.0 | 0.028885 | 0.0001651 | No
14/11/2023 | 10:19 | MI25 | LONG RURAL | Unknown | Unknown | 24.67 | 202.0 | 0.035757 | 0.0001770 | No
14/11/2023 | 11:08 | AP355D | URBAN | Asset failure | LV | 5.00 | 138.0 | 0.001064 | 0.0000077 | No
14/11/2023 | 11:37 | HH341C | URBAN | Asset failure | LV | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
14/11/2023 | 11:40 | AP125D | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
14/11/2023 | 11:53 | VH22 | SHORT RURAL | Planned |  | 387.00 | 2.0 | 0.005445 | 0.0027227 | No
14/11/2023 | 11:54 | MI01 | LONG RURAL | Weather |  | 12.00 | 189.0 | 0.016276 | 0.0000861 | No
14/11/2023 | 12:21 | AP149B | URBAN | Asset failure | LV | 41.00 | 153.0 | 0.009671 | 0.0000632 | No
14/11/2023 | 12:32 | SM349F | URBAN | Asset failure | LV | 62.00 | 336.0 | 0.032118 | 0.0000956 | No
14/11/2023 | 13:15 | MV64 | SHORT RURAL | Overloads |  | 1.00 | 100.0 | 0.000704 | 0.0000070 | No
14/11/2023 | 13:28 | AP424C | URBAN | Asset failure | LV | 16.00 | 556.0 | 0.013715 | 0.0000247 | No
14/11/2023 | 14:30 | MV33 | SHORT RURAL | Asset failure | LV | 1.00 | 458.0 | 0.003222 | 0.0000070 | No
14/11/2023 | 14:38 | HH145A | URBAN | Overloads |  | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
14/11/2023 | 15:12 | ST36 | LONG RURAL | Weather |  | 5.00 | 30.0 | 0.001076 | 0.0000359 | No
14/11/2023 | 15:19 | EL260A | URBAN | Overloads |  | 1.00 | 349.0 | 0.000538 | 0.0000015 | No
14/11/2023 | 15:46 | R08 | LONG RURAL | Weather |  | 17.00 | 123.0 | 0.015006 | 0.0001220 | No
14/11/2023 | 16:42 | VH22 | SHORT RURAL | Animal | Animal impact | 13.33 | 129.0 | 0.012101 | 0.0000938 | No
14/11/2023 | 16:42 | MT08 | LONG RURAL | Unknown | Unknown | 1.00 | 633.0 | 0.004543 | 0.0000072 | No
14/11/2023 | 16:49 | YK28 | LONG RURAL | Weather |  | 2.00 | 207.0 | 0.002971 | 0.0000144 | No
14/11/2023 | 17:15 | ST41 | LONG RURAL | Asset failure | LV | 1.00 | 63.0 | 0.000452 | 0.0000072 | No
14/11/2023 | 17:28 | BM55 | SHORT RURAL | Asset failure | LV | 14.00 | 76.0 | 0.007486 | 0.0000985 | No
14/11/2023 | 17:48 | NL210C | URBAN | Asset failure | LV | 1.00 | 303.0 | 0.000467 | 0.0000015 | No
14/11/2023 | 18:28 | MB22 | SHORT RURAL | Asset failure | LV | 1.00 | 211.0 | 0.001484 | 0.0000070 | No
14/11/2023 | 19:21 | KA01 | SHORT RURAL | Asset failure | LV | 1.00 | 236.0 | 0.001660 | 0.0000070 | No
14/11/2023 | 21:16 | YK12 | LONG RURAL | Asset failure | LV | 2.00 | 294.0 | 0.004220 | 0.0000144 | No
14/11/2023 | 21:57 | HH130F | URBAN | Asset failure | LV | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
15/11/2023 | 01:55 | MV31 | SHORT RURAL | Weather |  | 6.00 | 245.0 | 0.010342 | 0.0000422 | No
15/11/2023 | 05:54 | SD33200 | LONG RURAL | Unknown | Unknown | 16.00 | 159.0 | 0.018257 | 0.0001148 | No
15/11/2023 | 06:18 | HH102D | URBAN | Asset failure | LV | 20.00 | 213.0 | 0.006568 | 0.0000308 | No
15/11/2023 | 06:53 | WHY08 | URBAN | Animal | Animal impact | 80.00 | 121.0 | 0.014924 | 0.0001233 | No
15/11/2023 | 07:55 | VH15 | SHORT RURAL | Unknown | Unknown | 54.00 | 93.0 | 0.035332 | 0.0003799 | No
15/11/2023 | 07:58 | BT26 | LONG RURAL | Asset failure | LV | 1.00 | 555.0 | 0.003983 | 0.0000072 | No
15/11/2023 | 07:58 | VH12 | SHORT RURAL | Unknown | Unknown | 1.00 | 137.0 | 0.000964 | 0.0000070 | No
15/11/2023 | 08:05 | PL33 | LONG RURAL | Planned |  | 3.00 | 186.0 | 0.004004 | 0.0000215 | No
15/11/2023 | 08:23 | PL03 | URBAN | Planned |  | 233.00 | 247.1 | 0.088765 | 0.0003592 | No
15/11/2023 | 08:28 | SM126D | URBAN | Planned |  | 100.00 | 315.9 | 0.048696 | 0.0001542 | No
15/11/2023 | 09:07 | SD38200 | LONG RURAL | Planned |  | 5.00 | 270.0 | 0.009688 | 0.0000359 | No
15/11/2023 | 09:17 | PL06 | LONG RURAL | Unknown | Unknown | 1.00 | 110.0 | 0.000789 | 0.0000072 | No
15/11/2023 | 09:17 | PL06 | URBAN | Unknown | Unknown | 3,790.00 | 78.4 | 0.457973 | 0.0058432 | No
15/11/2023 | 09:27 | NU31 | LONG RURAL | Planned |  | 1.00 | 168.0 | 0.001206 | 0.0000072 | No
15/11/2023 | 09:35 | BT26 | LONG RURAL | Planned |  | 9.00 | 321.0 | 0.020732 | 0.0000646 | No
15/11/2023 | 09:50 | HH341K | URBAN | Planned |  | 39.00 | 321.1 | 0.019306 | 0.0000601 | No
15/11/2023 | 09:52 | MTB14 | SHORT RURAL | Planned |  | 445.00 | 406.4 | 1.272495 | 0.0031308 | No
15/11/2023 | 09:55 | R31 | LONG RURAL | Planned |  | 1.00 | 130.0 | 0.000933 | 0.0000072 | No
15/11/2023 | 10:06 | CN24 | LONG RURAL | Unknown | Unknown | 1.00 | 7,447.0 | 0.053442 | 0.0000072 | No
15/11/2023 | 10:35 | CV20 | LONG RURAL | Planned |  | 6.00 | 162.0 | 0.006975 | 0.0000431 | No
15/11/2023 | 10:35 | M04 | LONG RURAL | Other |  | 17.00 | 61.0 | 0.007442 | 0.0001220 | No
15/11/2023 | 11:52 | MTB71 | SHORT RURAL | Asset failure | LV | 2.00 | 58.0 | 0.000816 | 0.0000141 | No
15/11/2023 | 13:21 | VH12 | SHORT RURAL | Unknown | Unknown | 1.00 | 72.0 | 0.000507 | 0.0000070 | No
15/11/2023 | 14:06 | PL06 | URBAN | Asset failure | LV | 14.33 | 58.0 | 0.001282 | 0.0000221 | No
15/11/2023 | 14:12 | CN24 | LONG RURAL | Animal | Animal impact | 91.00 | 176.0 | 0.114936 | 0.0006530 | No
15/11/2023 | 14:16 | HH102B | URBAN | Asset failure | LV | 75.00 | 26.0 | 0.003006 | 0.0001156 | No
15/11/2023 | 15:36 | ST12 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 1,383.0 | 0.009730 | 0.0000070 | No
15/11/2023 | 16:14 | KI31 | SHORT RURAL | Asset failure | LV | 16.67 | 130.0 | 0.015244 | 0.0001173 | No
15/11/2023 | 18:05 | BT04 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 15.00 | 61.0 | 0.006566 | 0.0001076 | No
15/11/2023 | 19:22 | M11 | LONG RURAL | Asset failure | LV | 16.00 | 136.0 | 0.015616 | 0.0001148 | No
15/11/2023 | 19:30 | EL10 | URBAN | Asset failure | HV | 75.00 | 202.0 | 0.023358 | 0.0001156 | No
15/11/2023 | 22:30 | HH118E | URBAN | Planned |  | 133.00 | 392.4 | 0.080458 | 0.0002051 | No
15/11/2023 | 23:55 | AP829A | URBAN | Unknown | Unknown | 281.00 | 175.9 | 0.076197 | 0.0004332 | No
16/11/2023 | 00:29 | SA20 | URBAN | Asset failure | LV | 42.00 | 100.3 | 0.006497 | 0.0000648 | No
16/11/2023 | 01:05 | ME347H | URBAN | Planned |  | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
16/11/2023 | 03:53 | SM349E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 367.0 | 0.023199 | 0.0000632 | No
16/11/2023 | 07:55 | PA06 | LONG RURAL | Asset failure | HV | 946.00 | 122.3 | 0.830201 | 0.0067888 | No
16/11/2023 | 08:14 | NU01 | SHORT RURAL | Animal | Animal impact | 2.00 | 438.0 | 0.006163 | 0.0000141 | No
16/11/2023 | 08:33 | SM410C | URBAN | Planned |  | 161.00 | 253.0 | 0.062800 | 0.0002482 | No
16/11/2023 | 08:33 | PL34 | LONG RURAL | Planned |  | 41.00 | 177.0 | 0.052079 | 0.0002942 | No
16/11/2023 | 08:43 | BS0285 | URBAN | Planned |  | 1.00 | 411.0 | 0.000634 | 0.0000015 | No
16/11/2023 | 08:50 | HH118A | URBAN | Overloads |  | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
16/11/2023 | 09:00 | MG16 | LONG RURAL | Planned |  | 474.00 | 159.0 | 0.540851 | 0.0034016 | No
16/11/2023 | 09:09 | MV62 | SHORT RURAL | Planned |  | 135.00 | 335.7 | 0.318877 | 0.0009498 | No
16/11/2023 | 09:40 | WK61 | SHORT RURAL | Planned |  | 95.00 | 339.0 | 0.226606 | 0.0006684 | No
16/11/2023 | 10:00 | AP139B | URBAN | Planned |  | 31.00 | 363.0 | 0.017349 | 0.0000478 | No
16/11/2023 | 10:06 | GA36 | LONG RURAL | Planned |  | 2.00 | 51.0 | 0.000732 | 0.0000144 | No
16/11/2023 | 10:12 | VH12 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 95.00 | 91.7 | 0.061293 | 0.0006684 | No
16/11/2023 | 10:17 | CM15 | LONG RURAL | Planned |  | 1.00 | 88.0 | 0.000632 | 0.0000072 | No
16/11/2023 | 10:18 | VH12 | SHORT RURAL | Planned |  | 154.00 | 371.0 | 0.401966 | 0.0010835 | No
16/11/2023 | 10:27 | MB12 | SHORT RURAL | Asset failure | LV | 1.00 | 316.0 | 0.002223 | 0.0000070 | No
16/11/2023 | 10:35 | HH107C | URBAN | Asset failure | LV | 16.00 | 114.0 | 0.002812 | 0.0000247 | No
16/11/2023 | 10:54 | SD40800 | LONG RURAL | Planned |  | 44.00 | 235.0 | 0.074203 | 0.0003158 | No
16/11/2023 | 11:36 | HH107C | URBAN | Unknown | Unknown | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
16/11/2023 | 11:49 | AP227A | URBAN | Asset failure | LV | 1.00 | 402.0 | 0.000620 | 0.0000015 | No
16/11/2023 | 13:47 | BT18 | LONG RURAL | Asset failure | HV | 35.00 | 40.0 | 0.010047 | 0.0002512 | No
16/11/2023 | 13:47 | MTB14 | SHORT RURAL | Overloads |  | 4,348.00 | 63.0 | 1.928604 | 0.0305903 | No
16/11/2023 | 14:30 | MI20 | LONG RURAL | Weather |  | 155.00 | 48.0 | 0.053392 | 0.0011123 | No
16/11/2023 | 14:33 | SA18 | URBAN | Asset failure | LV | 1.00 | 4.0 | 0.000006 | 0.0000015 | No
16/11/2023 | 15:36 | AP424A | URBAN | Third Party | Vehicle impact | 87.00 | 228.0 | 0.030582 | 0.0001341 | No
16/11/2023 | 16:01 | VH15 | SHORT RURAL | Unknown | Unknown | 1.00 | 53.0 | 0.000373 | 0.0000070 | No
16/11/2023 | 16:04 | GA08 | LONG RURAL | Weather |  | 161.00 | 61.0 | 0.070479 | 0.0011554 | No
16/11/2023 | 16:11 | CN43 | LONG RURAL | Animal | Animal impact | 3.00 | 171.7 | 0.003696 | 0.0000215 | No
16/11/2023 | 16:21 | R36 | SHORT RURAL | Weather |  | 22.00 | 115.0 | 0.017800 | 0.0001548 | No
16/11/2023 | 16:44 | HH121G | URBAN | Overloads |  | 1.00 | 191.0 | 0.000294 | 0.0000015 | No
16/11/2023 | 16:56 | SM349H | URBAN | Asset failure | LV | 56.00 | 61.0 | 0.005267 | 0.0000863 | No
16/11/2023 | 19:19 | PL803C | URBAN | Asset failure | LV | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
16/11/2023 | 22:31 | AP132D | URBAN | Asset failure | LV | 101.00 | 83.0 | 0.012925 | 0.0001557 | No
17/11/2023 | 03:32 | HH118D | URBAN | Vegetation | Grow-in - NSP responsibility | 47.00 | 405.0 | 0.029347 | 0.0000725 | No
17/11/2023 | 08:54 | AP226C | URBAN | Planned |  | 264.00 | 67.0 | 0.027271 | 0.0004070 | No
17/11/2023 | 08:59 | CD15 | LONG RURAL | Planned |  | 1.00 | 167.0 | 0.001198 | 0.0000072 | No
17/11/2023 | 09:23 | CV18 | SHORT RURAL | Planned |  | 2.00 | 62.0 | 0.000872 | 0.0000141 | No
17/11/2023 | 09:35 | ST22 | SHORT RURAL | Asset failure | HV | 4.00 | 214.0 | 0.006022 | 0.0000281 | No
17/11/2023 | 09:43 | GA41 | LONG RURAL | Planned |  | 1.00 | 70.0 | 0.000502 | 0.0000072 | No
17/11/2023 | 10:10 | AP424F | URBAN | Planned |  | 436.00 | 9.0 | 0.006050 | 0.0006722 | No
17/11/2023 | 10:18 | SM216B | URBAN | Asset failure | LV | 8.00 | 172.0 | 0.002121 | 0.0000123 | No
17/11/2023 | 10:20 | AP227C | URBAN | Planned |  | 322.00 | 6.0 | 0.002979 | 0.0004964 | No
17/11/2023 | 10:22 | HH130F | URBAN | Asset failure | LV | 1.00 | 18.0 | 0.000028 | 0.0000015 | No
17/11/2023 | 10:27 | SM126E | URBAN | Asset failure | LV | 1.00 | 425.0 | 0.000655 | 0.0000015 | No
17/11/2023 | 10:38 | HH177G | URBAN | Overloads |  | 1.00 | 259.0 | 0.000399 | 0.0000015 | No
17/11/2023 | 10:39 | PL803C | URBAN | Planned |  | 28.00 | 368.7 | 0.015917 | 0.0000432 | No
17/11/2023 | 12:15 | GA31 | LONG RURAL | Planned |  | 13.00 | 43.0 | 0.004012 | 0.0000933 | No
17/11/2023 | 13:08 | MB62 | LONG RURAL | Asset failure | LV | 1.00 | 164.0 | 0.001177 | 0.0000072 | No
17/11/2023 | 13:17 | HH145A | URBAN | Unknown | Unknown | 44.00 | 55.0 | 0.003731 | 0.0000678 | No
17/11/2023 | 15:28 | BM13 | SHORT RURAL | Asset failure | LV | 1.00 | 169.0 | 0.001189 | 0.0000070 | No
17/11/2023 | 15:33 | BU11 | SHORT RURAL | Planned |  | 26.00 | 26.0 | 0.004756 | 0.0001829 | No
17/11/2023 | 18:19 | ST21 | SHORT RURAL | Unknown | Unknown | 29.00 | 200.0 | 0.040806 | 0.0002040 | No
17/11/2023 | 19:09 | NL115B | URBAN | Asset failure | LV | 1.00 | 161.0 | 0.000248 | 0.0000015 | No
17/11/2023 | 19:35 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 178.00 | 159.1 | 0.199231 | 0.0012523 | No
17/11/2023 | 19:35 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 1,453.0 | 0.020445 | 0.0000141 | No
17/11/2023 | 20:38 | HH386G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 849.00 | 64.0 | 0.083773 | 0.0013089 | No
17/11/2023 | 21:03 | HH118E | URBAN | Planned |  | 133.00 | 233.4 | 0.047868 | 0.0002051 | No
17/11/2023 | 21:58 | ST21 | SHORT RURAL | Overloads |  | 1.00 | 183.0 | 0.001287 | 0.0000070 | No
17/11/2023 | 22:23 | VH10 | SHORT RURAL | Asset failure | LV | 1.00 | 113.0 | 0.000795 | 0.0000070 | No
18/11/2023 | 00:22 | CD03 | SHORT RURAL | Asset failure | LV | 1.00 | 661.0 | 0.004650 | 0.0000070 | No
18/11/2023 | 07:18 | M81 | LONG RURAL | Animal | Animal impact | 2.00 | 358.0 | 0.005138 | 0.0000144 | No
18/11/2023 | 08:26 | HH409A | URBAN | Vegetation | Grow-in - NSP responsibility | 4.67 | 62.9 | 0.000452 | 0.0000072 | No
18/11/2023 | 08:38 | BS0356 | LONG RURAL | Planned |  | 1.00 | 3,333.0 | 0.023919 | 0.0000072 | No
18/11/2023 | 08:40 | VH44 | SHORT RURAL | Asset failure | HV | 185.67 | 307.6 | 0.401748 | 0.0013063 | No
18/11/2023 | 08:48 | PL33 | LONG RURAL | Planned |  | 20.00 | 294.0 | 0.042197 | 0.0001435 | No
18/11/2023 | 08:52 | HH130F | URBAN | Asset failure | LV | 1.00 | 4,447.0 | 0.006856 | 0.0000015 | No
18/11/2023 | 08:59 | CV30 | LONG RURAL | Unknown | Unknown | 1.00 | 634.0 | 0.004550 | 0.0000072 | No
18/11/2023 | 09:47 | CM05 | LONG RURAL | Asset failure | LV | 1.00 | 659.0 | 0.004729 | 0.0000072 | No
18/11/2023 | 09:52 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 453.0 | 0.003187 | 0.0000070 | No
18/11/2023 | 10:25 | YK07 | LONG RURAL | Unknown | Unknown | 1.00 | 188.0 | 0.001349 | 0.0000072 | No
18/11/2023 | 10:26 | HH409D | URBAN | Asset failure | LV | 60.00 | 111.0 | 0.010268 | 0.0000925 | No
18/11/2023 | 10:44 | SM216B | URBAN | Asset failure | LV | 87.00 | 145.0 | 0.019449 | 0.0001341 | No
18/11/2023 | 12:10 | AP425C | URBAN | Asset failure | LV | 17.67 | 163.0 | 0.004440 | 0.0000272 | No
18/11/2023 | 12:19 | VH23 | SHORT RURAL | Asset failure | LV | 2.00 | 306.0 | 0.004306 | 0.0000141 | No
18/11/2023 | 12:56 | WK41 | SHORT RURAL | Asset failure | LV | 2.00 | 215.0 | 0.003025 | 0.0000141 | No
18/11/2023 | 12:57 | CV30 | LONG RURAL | Unknown | Unknown | 8.00 | 256.0 | 0.014697 | 0.0000574 | No
18/11/2023 | 13:04 | GA50 | URBAN | Asset failure | LV | 1.00 | 307.0 | 0.000473 | 0.0000015 | No
18/11/2023 | 14:47 | KI56 | LONG RURAL | Asset failure | LV | 1.00 | 246.0 | 0.001765 | 0.0000072 | No
18/11/2023 | 16:07 | SA14 | URBAN | Asset failure | LV | 1.00 | 214.0 | 0.000330 | 0.0000015 | No
18/11/2023 | 22:36 | AP829A | URBAN | Animal | Animal impact | 281.00 | 164.3 | 0.071169 | 0.0004332 | No
19/11/2023 | 02:29 | SD40200 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 12.00 | 435.0 | 0.037460 | 0.0000861 | No
19/11/2023 | 03:41 | HH145A | URBAN | Overloads |  | 14.67 | 213.0 | 0.004816 | 0.0000226 | No
19/11/2023 | 06:08 | NA56 | LONG RURAL | Weather |  | 35.00 | 695.9 | 0.174780 | 0.0002512 | No
19/11/2023 | 06:26 | MI25 | LONG RURAL | Weather |  | 24.67 | 280.0 | 0.049565 | 0.0001770 | No
19/11/2023 | 08:17 | SD40800 | LONG RURAL | Planned |  | 63.00 | 322.7 | 0.145888 | 0.0004521 | No
19/11/2023 | 08:28 | HH121A | URBAN | Planned |  | 65.00 | 314.5 | 0.031521 | 0.0001002 | No
19/11/2023 | 08:40 | HH403A | URBAN | Planned |  | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
19/11/2023 | 08:56 | SM350F | URBAN | Planned |  | 42.00 | 309.0 | 0.020009 | 0.0000648 | No
19/11/2023 | 09:21 | HH145A | URBAN | Planned |  | 25.00 | 400.0 | 0.015418 | 0.0000385 | No
19/11/2023 | 10:09 | EL20 | URBAN | Unknown | Unknown | 4.00 | 1,432.0 | 0.008831 | 0.0000062 | No
19/11/2023 | 11:12 | NL451E | URBAN | Asset failure | LV | 1.00 | 428.0 | 0.000660 | 0.0000015 | No
19/11/2023 | 12:22 | KI16 | LONG RURAL | Third Party | Vehicle impact | 111.00 | 230.0 | 0.183212 | 0.0007966 | No
19/11/2023 | 12:23 | MG41 | URBAN | Unknown | Unknown | 1.00 | 73.0 | 0.000113 | 0.0000015 | No
19/11/2023 | 12:55 | SM126C | URBAN | Asset failure | LV | 1.00 | 402.0 | 0.000620 | 0.0000015 | No
19/11/2023 | 14:33 | AP139C | URBAN | Third Party | Vehicle impact | 102.00 | 496.3 | 0.078047 | 0.0001573 | No
19/11/2023 | 14:37 | NA56 | LONG RURAL | Weather |  | 40.00 | 5.0 | 0.001435 | 0.0002871 | No
19/11/2023 | 15:12 | SM411E | URBAN | Asset failure | LV | 1.00 | 316.0 | 0.000487 | 0.0000015 | No
19/11/2023 | 15:43 | CL07 | LONG RURAL | Asset failure | HV | 53.00 | 107.2 | 0.040754 | 0.0003803 | No
19/11/2023 | 16:31 | MG17 | LONG RURAL | Asset failure | LV | 1.33 | 321.0 | 0.003071 | 0.0000096 | No
19/11/2023 | 18:14 | NA03 | LONG RURAL | Asset failure | LV | 2.00 | 326.0 | 0.004679 | 0.0000144 | No
19/11/2023 | 19:00 | NL760B | URBAN | Asset failure | LV | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
19/11/2023 | 21:33 | HH121A | URBAN | Asset failure | LV | 26.00 | 35.0 | 0.001403 | 0.0000401 | No
19/11/2023 | 22:06 | HH118C | URBAN | Planned |  | 80.00 | 407.0 | 0.050200 | 0.0001233 | No
19/11/2023 | 23:06 | SD52300 | LONG RURAL | Animal | Animal impact | 2.00 | 49.0 | 0.000703 | 0.0000144 | No
19/11/2023 | 23:51 | HH102D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,064.00 | 60.0 | 0.098426 | 0.0016404 | No
20/11/2023 | 04:31 | HH107C | URBAN | Animal | Animal impact | 85.00 | 109.0 | 0.014284 | 0.0001310 | No
20/11/2023 | 06:55 | MI32 | LONG RURAL | Weather |  | 355.00 | 168.0 | 0.427996 | 0.0025476 | No
20/11/2023 | 06:55 | SG02 | SHORT RURAL | Asset failure | LV | 1.00 | 151.0 | 0.001062 | 0.0000070 | No
20/11/2023 | 07:06 | VH15 | SHORT RURAL | Overloads |  | 1.00 | 216.0 | 0.001520 | 0.0000070 | No
20/11/2023 | 07:11 | HH121D | URBAN | Unknown | Unknown | 258.00 | 19.1 | 0.007590 | 0.0003978 | No
20/11/2023 | 07:26 | VH34 | SHORT RURAL | Animal | Animal impact | 14.00 | 311.0 | 0.030633 | 0.0000985 | No
20/11/2023 | 07:26 | HH496G | URBAN | Asset failure | HV | 65.00 | 661.9 | 0.066335 | 0.0001002 | No
20/11/2023 | 07:33 | ST34 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 2.00 | 407.0 | 0.005842 | 0.0000144 | No
20/11/2023 | 07:54 | SD52300 | LONG RURAL | Animal | Animal impact | 2.00 | 439.0 | 0.006301 | 0.0000144 | No
20/11/2023 | 09:05 | KA02 | SHORT RURAL | Asset failure | LV | 6.00 | 316.0 | 0.013339 | 0.0000422 | No
20/11/2023 | 09:07 | R03 | LONG RURAL | Planned |  | 49.00 | 377.0 | 0.132568 | 0.0003516 | No
20/11/2023 | 09:29 | CM01 | LONG RURAL | Planned |  | 196.00 | 288.0 | 0.405089 | 0.0014066 | No
20/11/2023 | 09:31 | MB83 | LONG RURAL | Planned |  | 17.00 | 44.0 | 0.005368 | 0.0001220 | No
20/11/2023 | 09:35 | CD17 | LONG RURAL | Planned |  | 5.00 | 177.0 | 0.006351 | 0.0000359 | No
20/11/2023 | 10:43 | AP149E | URBAN | Animal | Animal impact | 21.00 | 71.0 | 0.002299 | 0.0000324 | No
20/11/2023 | 11:13 | MTB13 | SHORT RURAL | Animal | Animal impact | 1.00 | 213.0 | 0.001499 | 0.0000070 | No
20/11/2023 | 11:16 | SM350H | URBAN | Planned |  | 2.00 | 407.5 | 0.001257 | 0.0000031 | No
20/11/2023 | 11:35 | ST36 | LONG RURAL | Asset failure | HV | 29.67 | 61.0 | 0.012987 | 0.0002129 | No
20/11/2023 | 12:45 | NL111Q | URBAN | Asset failure | LV | 13.00 | 111.0 | 0.002225 | 0.0000200 | No
20/11/2023 | 14:34 | HH429A | URBAN | Asset failure | LV | 1.00 | 454.0 | 0.000700 | 0.0000015 | No
20/11/2023 | 14:37 | HH145A | URBAN | Overloads |  | 44.00 | 131.0 | 0.008887 | 0.0000678 | No
20/11/2023 | 15:03 | VH11 | URBAN | Asset failure | LV | 71.00 | 99.8 | 0.010920 | 0.0001095 | No
20/11/2023 | 15:19 | SM179A | URBAN | Asset failure | LV | 7.00 | 324.0 | 0.003497 | 0.0000108 | No
20/11/2023 | 16:21 | HH403A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
20/11/2023 | 18:24 | MB43 | LONG RURAL | Asset failure | HV | 2.00 | 54.0 | 0.000775 | 0.0000144 | No
20/11/2023 | 18:28 | ME131C | URBAN | Asset failure | LV | 83.00 | 133.0 | 0.017019 | 0.0001280 | No
20/11/2023 | 19:03 | HH121F | URBAN | Asset failure | LV | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
20/11/2023 | 21:28 | NU13 | LONG RURAL | Unknown | Unknown | 732.00 | 69.9 | 0.367184 | 0.0052531 | No
20/11/2023 | 21:40 | SM349F | URBAN | Planned |  | 147.00 | 402.9 | 0.091307 | 0.0002266 | No
21/11/2023 | 01:19 | HH177C | URBAN | Unknown | Unknown | 472.00 | 189.0 | 0.137537 | 0.0007277 | No
21/11/2023 | 05:17 | VH34 | SHORT RURAL | Overloads |  | 2.00 | 282.0 | 0.003968 | 0.0000141 | No
21/11/2023 | 05:48 | SD49200 | LONG RURAL | Weather |  | 47.00 | 349.0 | 0.117713 | 0.0003373 | No
21/11/2023 | 06:34 | LX21 | SHORT RURAL | Unknown | Unknown | 35.67 | 150.7 | 0.037827 | 0.0002509 | No
21/11/2023 | 08:35 | PL01 | URBAN | Asset failure | LV | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
21/11/2023 | 08:43 | VH44 | SHORT RURAL | Planned |  | 1.00 | 335.0 | 0.002357 | 0.0000070 | No
21/11/2023 | 08:59 | ME347B | URBAN | Planned |  | 183.00 | 340.0 | 0.095928 | 0.0002821 | No
21/11/2023 | 09:06 | GA800A | SHORT RURAL | Planned |  | 36.00 | 388.0 | 0.098272 | 0.0002533 | No
21/11/2023 | 09:09 | CN24 | LONG RURAL | Planned |  | 70.00 | 547.0 | 0.274782 | 0.0005023 | No
21/11/2023 | 09:11 | AP425D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 24.00 | 118.0 | 0.004366 | 0.0000370 | No
21/11/2023 | 09:11 | EL10 | URBAN | Planned |  | 97.00 | 350.0 | 0.052343 | 0.0001496 | No
21/11/2023 | 09:13 | ST12 | SHORT RURAL | Planned |  | 64.00 | 265.0 | 0.119322 | 0.0004503 | No
21/11/2023 | 09:23 | LM62 | LONG RURAL | Planned |  | 34.00 | 261.0 | 0.063683 | 0.0002440 | No
21/11/2023 | 09:33 | NU21 | LONG RURAL | Asset failure | LV | 1.00 | 296.0 | 0.002124 | 0.0000072 | No
21/11/2023 | 09:44 | YK07 | LONG RURAL | Planned |  | 56.00 | 257.4 | 0.103454 | 0.0004019 | No
21/11/2023 | 09:48 | NU14 | LONG RURAL | Planned |  | 1.00 | 95.0 | 0.000682 | 0.0000072 | No
21/11/2023 | 09:50 | PL07 | URBAN | Planned |  | 97.00 | 218.0 | 0.032602 | 0.0001496 | No
21/11/2023 | 09:52 | MI08 | LONG RURAL | Weather |  | 25.00 | 72.0 | 0.012917 | 0.0001794 | No
21/11/2023 | 09:54 | MTB53 | LONG RURAL | Planned |  | 91.00 | 375.9 | 0.245474 | 0.0006530 | No
21/11/2023 | 09:55 | NL111A | URBAN | Asset failure | LV | 16.00 | 92.0 | 0.002269 | 0.0000247 | No
21/11/2023 | 10:01 | WK65 | SHORT RURAL | Unknown | Unknown | 60.00 | 292.0 | 0.123262 | 0.0004221 | No
21/11/2023 | 10:14 | MV61 | URBAN | Asset failure | LV | 11.00 | 590.0 | 0.010006 | 0.0000170 | No
21/11/2023 | 10:15 | SB01 | LONG RURAL | Planned |  | 73.00 | 213.0 | 0.111585 | 0.0005239 | No
21/11/2023 | 10:36 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 164.0 | 0.001177 | 0.0000072 | No
21/11/2023 | 10:41 | SA11 | URBAN | Other |  | 1.00 | 694.0 | 0.001070 | 0.0000015 | No
21/11/2023 | 10:52 | HH522B | URBAN | Asset failure | LV | 1.00 | 38.0 | 0.000059 | 0.0000015 | No
21/11/2023 | 11:01 | HH177E | URBAN | Asset failure | LV | 1.00 | 97.0 | 0.000150 | 0.0000015 | No
21/11/2023 | 11:04 | HH121A | URBAN | Unknown | Unknown | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
21/11/2023 | 11:37 | MTB14 | SHORT RURAL | Asset failure | HV | 6.00 | 75.0 | 0.003166 | 0.0000422 | No
21/11/2023 | 12:07 | MV52 | SHORT RURAL | Asset failure | LV | 2.00 | 112.0 | 0.001576 | 0.0000141 | No
21/11/2023 | 12:09 | GA27 | LONG RURAL | Planned |  | 33.00 | 216.0 | 0.051153 | 0.0002368 | No
21/11/2023 | 12:28 | HH522B | URBAN | Asset failure | LV | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
21/11/2023 | 13:06 | SM349C | URBAN | Other |  | 93.00 | 115.0 | 0.016489 | 0.0001434 | No
21/11/2023 | 13:06 | SM349C | URBAN | Planned |  | 1,143.00 | 3.0 | 0.005287 | 0.0017622 | No
21/11/2023 | 13:32 | NL111A | URBAN | Unknown | Unknown | 8.00 | 163.0 | 0.002010 | 0.0000123 | No
21/11/2023 | 13:47 | SD40700 | LONG RURAL | Unknown | Unknown | 1.00 | 246.0 | 0.001765 | 0.0000072 | No
21/11/2023 | 14:23 | ME116C | URBAN | Asset failure | LV | 12.00 | 176.3 | 0.003261 | 0.0000185 | No
21/11/2023 | 15:26 | EL09 | URBAN | Asset failure | LV | 18.00 | 94.0 | 0.002609 | 0.0000278 | No
21/11/2023 | 15:32 | WK72 | SHORT RURAL | Unknown | Unknown | 2.00 | 1,380.0 | 0.019418 | 0.0000141 | No
21/11/2023 | 16:10 | SM349C | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
21/11/2023 | 18:11 | GA800C | SHORT RURAL | Asset failure | LV | 1.00 | 409.0 | 0.002878 | 0.0000070 | No
21/11/2023 | 19:06 | ME116C | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
21/11/2023 | 19:17 | HH386B | URBAN | Asset failure | LV | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
21/11/2023 | 20:12 | HH341A | URBAN | Asset failure | LV | 39.00 | 47.0 | 0.002826 | 0.0000601 | No
21/11/2023 | 21:49 | AP125B | URBAN | Planned |  | 6.00 | 5,608.7 | 0.051883 | 0.0000093 | No
21/11/2023 | 22:26 | YK24 | LONG RURAL | Asset failure | LV | 1.00 | 269.0 | 0.001930 | 0.0000072 | No
22/11/2023 | 07:44 | PA02 | URBAN | Asset failure | LV | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
22/11/2023 | 08:25 | CD03 | SHORT RURAL | Planned |  | 99.00 | 234.4 | 0.163230 | 0.0006965 | No
22/11/2023 | 08:34 | EL23 | URBAN | Planned |  | 64.00 | 293.0 | 0.028911 | 0.0000987 | No
22/11/2023 | 09:03 | MI08 | LONG RURAL | Asset failure | LV | 1.00 | 296.0 | 0.002124 | 0.0000072 | No
22/11/2023 | 09:12 | SG09 | SHORT RURAL | Planned |  | 12.00 | 205.5 | 0.017350 | 0.0000844 | No
22/11/2023 | 09:52 | CM02 | LONG RURAL | Planned |  | 5.00 | 242.0 | 0.008683 | 0.0000359 | No
22/11/2023 | 09:57 | CM15 | LONG RURAL | Planned |  | 59.00 | 157.0 | 0.066474 | 0.0004234 | No
22/11/2023 | 10:24 | KA03 | LONG RURAL | Planned |  | 37.00 | 146.0 | 0.038767 | 0.0002655 | No
22/11/2023 | 10:37 | NA56 | LONG RURAL | Planned |  | 1.00 | 66.0 | 0.000474 | 0.0000072 | No
22/11/2023 | 10:52 | PL06 | URBAN | Unknown | Unknown | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
22/11/2023 | 10:52 | M81 | LONG RURAL | Planned |  | 482.00 | 209.0 | 0.722929 | 0.0034590 | No
22/11/2023 | 11:00 | BM41 | SHORT RURAL | Asset failure | HV | 339.33 | 8.3 | 0.019840 | 0.0023874 | No
22/11/2023 | 11:23 | ME131C | URBAN | Third Party | Vehicle impact | 31.00 | 74.0 | 0.003537 | 0.0000478 | No
22/11/2023 | 11:32 | ME131E | URBAN | Asset failure | LV | 1.00 | 368.0 | 0.000567 | 0.0000015 | No
22/11/2023 | 11:54 | HH432B | URBAN | Unknown | Unknown | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
22/11/2023 | 12:21 | GA800A | SHORT RURAL | Planned |  | 12.00 | 134.0 | 0.011313 | 0.0000844 | No
22/11/2023 | 12:40 | AP139C | URBAN | Third Party | Vehicle impact | 43.00 | 590.4 | 0.039141 | 0.0000663 | No
22/11/2023 | 12:41 | MV62 | SHORT RURAL | Third Party | Vehicle impact | 185.00 | 236.5 | 0.307817 | 0.0013016 | No
22/11/2023 | 14:20 | MI15 | LONG RURAL | Unknown | Unknown | 28.00 | 166.0 | 0.033356 | 0.0002009 | No
22/11/2023 | 14:25 | SM350C | URBAN | Asset failure | HV | 48.67 | 169.0 | 0.012680 | 0.0000750 | No
22/11/2023 | 14:44 | NL111B | URBAN | Asset failure | LV | 1.00 | 387.0 | 0.000597 | 0.0000015 | No
22/11/2023 | 15:09 | HH177C | URBAN | Overloads |  | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
22/11/2023 | 16:58 | VH44 | SHORT RURAL | Asset failure | HV | 24.00 | 105.4 | 0.017800 | 0.0001689 | No
22/11/2023 | 17:46 | HH121E | URBAN | Asset failure | LV | 13.00 | 49.0 | 0.000982 | 0.0000200 | No
22/11/2023 | 17:46 | HH121E | URBAN | Asset failure | LV | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
22/11/2023 | 17:57 | HH121G | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
22/11/2023 | 18:01 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 543.00 | 65.0 | 0.054416 | 0.0008372 | No
22/11/2023 | 18:19 | SM179A | URBAN | Asset failure | LV | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
22/11/2023 | 18:57 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 40.00 | 101.0 | 0.006229 | 0.0000617 | No
22/11/2023 | 19:52 | HH177C | URBAN | Third Party | Other | 85.00 | 218.0 | 0.028569 | 0.0001310 | No
22/11/2023 | 20:01 | HH409F | URBAN | Vegetation | Grow-in - NSP responsibility | 60.00 | 13.9 | 0.001289 | 0.0000925 | No
22/11/2023 | 20:45 | MTB61 | SHORT RURAL | Asset failure | LV | 1.00 | 225.0 | 0.001583 | 0.0000070 | No
22/11/2023 | 21:17 | SM374E | URBAN | Third Party | Vehicle impact | 108.00 | 319.0 | 0.053117 | 0.0001665 | No
22/11/2023 | 21:39 | VH15 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 2,121.00 | 123.8 | 1.846922 | 0.0149223 | No
22/11/2023 | 23:06 | KI32 | SHORT RURAL | Planned |  | 64.00 | 347.5 | 0.156469 | 0.0004503 | No
22/11/2023 | 23:23 | SM411E | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
22/11/2023 | 23:27 | ST51 | SHORT RURAL | Asset failure | HV | 59.00 | 292.0 | 0.121207 | 0.0004151 | No
22/11/2023 | 23:36 | HH148A | URBAN | Asset failure | LV | 1.00 | 1,211.0 | 0.001867 | 0.0000015 | No
22/11/2023 | 23:39 | SM179D | URBAN | Asset failure | LV | 20.00 | 71.0 | 0.002189 | 0.0000308 | No
23/11/2023 | 00:04 | HH341A | URBAN | Unknown | Unknown | 2.00 | 153.0 | 0.000472 | 0.0000031 | No
23/11/2023 | 00:06 | MV13 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 485.00 | 95.1 | 0.324632 | 0.0034122 | No
23/11/2023 | 00:35 | HH148B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 53.00 | 828.0 | 0.067658 | 0.0000817 | No
23/11/2023 | 01:47 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 310.00 | 125.0 | 0.059743 | 0.0004779 | No
23/11/2023 | 03:09 | HH409A | URBAN | Unknown | Unknown | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
23/11/2023 | 03:12 | HH409D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
23/11/2023 | 03:41 | HH409E | URBAN | Unknown | Unknown | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
23/11/2023 | 03:50 | NL451C | URBAN | Vegetation | Grow-in - NSP responsibility | 24.33 | 373.0 | 0.013993 | 0.0000375 | No
23/11/2023 | 04:47 | HH386C | URBAN | Unknown | Unknown | 49.33 | 319.0 | 0.024263 | 0.0000761 | No
23/11/2023 | 05:34 | PA11 | LONG RURAL | Weather |  | 85.00 | 221.0 | 0.134807 | 0.0006100 | No
23/11/2023 | 06:17 | G16 | LONG RURAL | Weather |  | 22.00 | 255.3 | 0.040302 | 0.0001579 | No
23/11/2023 | 07:42 | HH118D | URBAN | Vegetation | Grow-in - NSP responsibility | 2.33 | 275.0 | 0.000989 | 0.0000036 | No
23/11/2023 | 07:43 | ST35 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 31.00 | 755.7 | 0.168120 | 0.0002225 | No
23/11/2023 | 08:18 | HH121E | URBAN | Planned |  | 255.00 | 319.3 | 0.125525 | 0.0003931 | No
23/11/2023 | 08:24 | CD03 | SHORT RURAL | Planned |  | 84.00 | 532.7 | 0.314824 | 0.0005910 | No
23/11/2023 | 08:50 | NL511A | URBAN | Planned |  | 84.00 | 123.0 | 0.015929 | 0.0001295 | No
23/11/2023 | 08:50 | KA04 | LONG RURAL | Planned |  | 1.00 | 255.0 | 0.001830 | 0.0000072 | No
23/11/2023 | 08:58 | R32 | LONG RURAL | Planned |  | 2.00 | 89.0 | 0.001277 | 0.0000144 | No
23/11/2023 | 08:58 | CM27 | LONG RURAL | Planned |  | 45.00 | 259.9 | 0.083934 | 0.0003229 | No
23/11/2023 | 09:01 | HH409E | URBAN | Other |  | 1.00 | 202.0 | 0.000311 | 0.0000015 | No
23/11/2023 | 09:02 | SD58200 | LONG RURAL | Asset failure | Subtransmission | 509.00 | 144.1 | 0.526377 | 0.0036528 | No
23/11/2023 | 09:06 | BM42 | SHORT RURAL | Asset failure | LV | 2.00 | 429.0 | 0.006036 | 0.0000141 | No
23/11/2023 | 09:20 | CV25 | LONG RURAL | Planned |  | 1.00 | 270.0 | 0.001938 | 0.0000072 | No
23/11/2023 | 09:21 | SD44200 | SHORT RURAL | Planned |  | 487.00 | 150.0 | 0.513943 | 0.0034263 | No
23/11/2023 | 09:23 | CN27 | LONG RURAL | Planned |  | 45.00 | 279.0 | 0.090099 | 0.0003229 | No
23/11/2023 | 09:32 | MB84 | LONG RURAL | Planned |  | 3.00 | 5.0 | 0.000108 | 0.0000215 | No
23/11/2023 | 09:58 | BT18 | LONG RURAL | Planned |  | 21.00 | 189.0 | 0.028483 | 0.0001507 | No
23/11/2023 | 10:01 | R02 | LONG RURAL | Asset failure | LV | 1.00 | 300.0 | 0.002153 | 0.0000072 | No
23/11/2023 | 10:27 | GU43 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 57.00 | 365.9 | 0.149670 | 0.0004091 | No
23/11/2023 | 10:42 | HH102B | URBAN | Asset failure | LV | 49.00 | 743.0 | 0.056131 | 0.0000755 | No
23/11/2023 | 11:04 | HH145B | URBAN | Planned |  | 280.00 | 91.1 | 0.039309 | 0.0004317 | No
23/11/2023 | 11:05 | SD40103 | LONG RURAL | Planned |  | 6.00 | 2.0 | 0.000086 | 0.0000431 | No
23/11/2023 | 11:10 | MT14 | SHORT RURAL | Weather |  | 76.00 | 214.1 | 0.114453 | 0.0005347 | No
23/11/2023 | 11:22 | AP424E | URBAN | Weather |  | 1,808.00 | 110.0 | 0.306572 | 0.0027875 | No
23/11/2023 | 11:28 | CBD103A | URBAN | Other |  | 2.00 | 22.0 | 0.000068 | 0.0000031 | No
23/11/2023 | 12:08 | SA744D | URBAN | Asset failure | LV | 37.00 | 507.0 | 0.028922 | 0.0000570 | No
23/11/2023 | 12:10 | BU13 | LONG RURAL | Asset failure | LV | 1.00 | 381.0 | 0.002734 | 0.0000072 | No
23/11/2023 | 12:10 | SA711C | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
23/11/2023 | 12:42 | MTB14 | SHORT RURAL | Planned |  | 34.00 | 71.0 | 0.016984 | 0.0002392 | No
23/11/2023 | 12:44 | VH22 | SHORT RURAL | Weather |  | 13.33 | 117.0 | 0.010975 | 0.0000938 | No
23/11/2023 | 12:45 | MT12 | LONG RURAL | Unknown | Unknown | 48.00 | 205.1 | 0.070644 | 0.0003445 | No
23/11/2023 | 13:08 | HH121B | URBAN | Third Party | Vehicle impact | 15.00 | 673.0 | 0.015564 | 0.0000231 | No
23/11/2023 | 13:17 | HH522C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 105.00 | 91.0 | 0.014731 | 0.0001619 | No
23/11/2023 | 13:30 | SD38200 | LONG RURAL | Overloads |  | 1.00 | 441.0 | 0.003165 | 0.0000072 | No
23/11/2023 | 13:35 | CN24 | LONG RURAL | Weather |  | 12.00 | 458.0 | 0.039441 | 0.0000861 | No
23/11/2023 | 13:43 | CD03 | SHORT RURAL | Weather |  | 656.00 | 36.0 | 0.166150 | 0.0046153 | No
23/11/2023 | 13:43 | SA744C | URBAN | Asset failure | LV | 7.00 | 577.0 | 0.006227 | 0.0000108 | No
23/11/2023 | 13:49 | HH386C | URBAN | Asset failure | LV | 1.00 | 470.0 | 0.000725 | 0.0000015 | No
23/11/2023 | 14:31 | GA22 | SHORT RURAL | Overloads |  | 2.00 | 147.0 | 0.002068 | 0.0000141 | No
23/11/2023 | 14:38 | SA32 | URBAN | Asset failure | LV | 1.00 | 617.0 | 0.000951 | 0.0000015 | No
23/11/2023 | 15:16 | EL02 | URBAN | Third Party | Unauthorised access | 1.00 | 338.0 | 0.000521 | 0.0000015 | No
23/11/2023 | 16:18 | EL07 | URBAN | Overloads |  | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
23/11/2023 | 17:13 | EL260A | URBAN | Asset failure | LV | 10.00 | 444.0 | 0.006845 | 0.0000154 | No
23/11/2023 | 20:07 | SM179A | URBAN | Third Party | Vehicle impact | 2.00 | 193.0 | 0.000595 | 0.0000031 | No
23/11/2023 | 20:48 | VH18 | SHORT RURAL | Weather |  | 5.00 | 41.0 | 0.001442 | 0.0000352 | No
23/11/2023 | 21:04 | W29 | LONG RURAL | Unknown | Unknown | 2.00 | 204.0 | 0.002928 | 0.0000144 | No
23/11/2023 | 22:26 | MI04 | LONG RURAL | Asset failure | HV | 2.00 | 149.0 | 0.002139 | 0.0000144 | No
23/11/2023 | 22:51 | KA03 | LONG RURAL | Weather |  | 962.00 | 99.1 | 0.684019 | 0.0069036 | No
23/11/2023 | 23:43 | SD40200 | LONG RURAL | Weather |  | 270.00 | 229.0 | 0.443712 | 0.0019376 | No
24/11/2023 | 00:06 | SB17 | LONG RURAL | Unknown | Unknown | 91.00 | 187.5 | 0.122471 | 0.0006530 | No
24/11/2023 | 01:40 | BT02 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 161.00 | 334.0 | 0.385900 | 0.0011554 | No
24/11/2023 | 01:47 | SA11 | URBAN | Network business | Switching and protection error | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
24/11/2023 | 01:48 | HH148B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 400.00 | 121.0 | 0.074621 | 0.0006167 | No
24/11/2023 | 03:09 | ST21 | SHORT RURAL | Weather |  | 933.00 | 275.9 | 1.810717 | 0.0065641 | No
24/11/2023 | 03:10 | YK18 | LONG RURAL | Weather |  | 48.00 | 396.0 | 0.136408 | 0.0003445 | No
24/11/2023 | 03:11 | SM374A | URBAN | Overloads |  | 49.00 | 56.0 | 0.004231 | 0.0000755 | No
24/11/2023 | 03:31 | SM172E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 3,008.00 | 11.5 | 0.053265 | 0.0046376 | No
24/11/2023 | 04:01 | PL24 | LONG RURAL | Unknown | Unknown | 31.00 | 373.0 | 0.082987 | 0.0002225 | No
24/11/2023 | 04:18 | LX71 | LONG RURAL | Weather |  | 126.00 | 331.8 | 0.300028 | 0.0009042 | No
24/11/2023 | 05:03 | VH33 | SHORT RURAL | Weather |  | 2.00 | 4,146.0 | 0.058338 | 0.0000141 | No
24/11/2023 | 05:06 | CN71 | LONG RURAL | Weather |  | 231.00 | 346.0 | 0.573575 | 0.0016577 | No
24/11/2023 | 05:45 | SD35200 | LONG RURAL | Unknown | Unknown | 45.00 | 327.0 | 0.105600 | 0.0003229 | No
24/11/2023 | 05:52 | LX63 | LONG RURAL | Weather |  | 59.00 | 531.1 | 0.224870 | 0.0004234 | No
24/11/2023 | 05:57 | SM374A | URBAN | Unknown | Unknown | 16.33 | 285.0 | 0.007177 | 0.0000252 | No
24/11/2023 | 06:04 | MV52 | SHORT RURAL | Overloads |  | 1.00 | 301.0 | 0.002118 | 0.0000070 | No
24/11/2023 | 06:05 | NL111C | URBAN | Unknown | Unknown | 1.00 | 404.0 | 0.000623 | 0.0000015 | No
24/11/2023 | 06:19 | SD44301 | LONG RURAL | Animal | Animal impact | 2,233.00 | 299.8 | 4.804122 | 0.0160247 | No
24/11/2023 | 06:19 | SD44301 | SHORT RURAL | Animal | Animal impact | 1,719.00 | 3.4 | 0.041664 | 0.0120940 | No
24/11/2023 | 06:41 | SB17 | LONG RURAL | Unknown | Unknown | 91.00 | 333.4 | 0.217751 | 0.0006530 | No
24/11/2023 | 06:56 | MG04 | SHORT RURAL | Weather |  | 665.00 | 246.6 | 1.153919 | 0.0046786 | No
24/11/2023 | 07:11 | BM44 | SHORT RURAL | Asset failure | LV | 5.00 | 473.0 | 0.016639 | 0.0000352 | No
24/11/2023 | 07:14 | R21 | LONG RURAL | Unknown | Unknown | 15.00 | 344.0 | 0.037030 | 0.0001076 | No
24/11/2023 | 07:16 | LX33 | SHORT RURAL | Unknown | Unknown | 2.00 | 375.0 | 0.005277 | 0.0000141 | No
24/11/2023 | 07:27 | MB32 | LONG RURAL | Asset failure | LV | 1.00 | 3,994.0 | 0.028662 | 0.0000072 | No
24/11/2023 | 07:29 | MTB32 | LONG RURAL | Unknown | Unknown | 234.00 | 48.2 | 0.080863 | 0.0016793 | No
24/11/2023 | 08:02 | MV52 | SHORT RURAL | Unknown | Unknown | 6.67 | 180.0 | 0.008443 | 0.0000469 | No
24/11/2023 | 08:03 | AP146B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 2,269.00 | 48.4 | 0.169192 | 0.0034982 | No
24/11/2023 | 08:15 | VH33 | SHORT RURAL | Weather |  | 33.33 | 98.4 | 0.023065 | 0.0002345 | No
24/11/2023 | 08:33 | ST16 | SHORT RURAL | Asset failure | LV | 2.00 | 487.0 | 0.006853 | 0.0000141 | No
24/11/2023 | 08:33 | AP146A | URBAN | Unknown | Unknown | 27.00 | 402.0 | 0.016734 | 0.0000416 | No
24/11/2023 | 08:43 | MTB14 | SHORT RURAL | Planned |  | 6.00 | 257.0 | 0.010849 | 0.0000422 | No
24/11/2023 | 08:48 | BM53 | SHORT RURAL | Asset failure | HV | 15.00 | 78.0 | 0.008232 | 0.0001055 | No
24/11/2023 | 08:50 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 189.0 | 0.001330 | 0.0000070 | No
24/11/2023 | 08:54 | W26 | LONG RURAL | Unknown | Unknown | 1.00 | 3,021.0 | 0.021680 | 0.0000072 | No
24/11/2023 | 09:20 | HH121E | URBAN | Asset failure | LV | 16.33 | 38.0 | 0.000957 | 0.0000252 | No
24/11/2023 | 09:26 | LX21 | SHORT RURAL | Animal | Animal impact | 19.00 | 157.0 | 0.020987 | 0.0001337 | No
24/11/2023 | 09:29 | SM374A | URBAN | Asset failure | LV | 21.33 | 71.0 | 0.002335 | 0.0000329 | No
24/11/2023 | 10:23 | NL111A | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
24/11/2023 | 10:30 | CV02 | LONG RURAL | Planned |  | 94.00 | 121.0 | 0.081624 | 0.0006746 | No
24/11/2023 | 10:32 | NA07 | LONG RURAL | Unknown | Unknown | 10.67 | 281.0 | 0.021510 | 0.0000765 | No
24/11/2023 | 10:39 | AP424F | URBAN | Unknown | Unknown | 1.00 | 26.0 | 0.000040 | 0.0000015 | No
24/11/2023 | 10:40 | ME131A | URBAN | Asset failure | LV | 18.67 | 224.0 | 0.006447 | 0.0000288 | No
24/11/2023 | 10:49 | HH409F | URBAN | Unknown | Unknown | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
24/11/2023 | 11:01 | ST42 | LONG RURAL | Animal | Animal impact | 2.00 | 254.0 | 0.003646 | 0.0000144 | No
24/11/2023 | 11:13 | AP146A | URBAN | Unknown | Unknown | 1.00 | 243.0 | 0.000375 | 0.0000015 | No
24/11/2023 | 11:46 | SD37301 | SHORT RURAL | Asset failure | Subtransmission | 1.00 | 58.0 | 0.000408 | 0.0000070 | No
24/11/2023 | 11:46 | MTB32 | LONG RURAL | Other |  | 1.00 | 202.0 | 0.001450 | 0.0000072 | No
24/11/2023 | 12:13 | SM126D | URBAN | Asset failure | LV | 1.00 | 91.0 | 0.000140 | 0.0000015 | No
24/11/2023 | 13:06 | HH107D | URBAN | Asset failure | LV | 32.00 | 100.0 | 0.004934 | 0.0000493 | No
24/11/2023 | 13:25 | SA14 | URBAN | Planned |  | 278.00 | 51.0 | 0.021859 | 0.0004286 | No
24/11/2023 | 13:42 | MT21 | LONG RURAL | Asset failure | LV | 22.00 | 59.0 | 0.009315 | 0.0001579 | No
24/11/2023 | 14:13 | PP10 | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1,637.00 | 79.0 | 0.199384 | 0.0025239 | No
24/11/2023 | 14:13 | AP425D | URBAN | Unknown | Unknown | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
24/11/2023 | 14:17 | AP125D | URBAN | Unknown | Unknown | 1.00 | 199.0 | 0.000307 | 0.0000015 | No
24/11/2023 | 14:24 | HH145C | URBAN | Asset failure | LV | 39.33 | 49.0 | 0.002971 | 0.0000606 | No
24/11/2023 | 14:37 | SD38100 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 65.0 | 0.000466 | 0.0000072 | No
24/11/2023 | 14:45 | MB71 | LONG RURAL | Asset failure | LV | 1.00 | 301.0 | 0.002160 | 0.0000072 | No
24/11/2023 | 14:55 | WK44 | SHORT RURAL | Weather |  | 17.00 | 45.0 | 0.005382 | 0.0001196 | No
24/11/2023 | 15:12 | YK07 | LONG RURAL | Asset failure | LV | 19.00 | 67.0 | 0.009135 | 0.0001364 | No
24/11/2023 | 15:57 | HH409E | URBAN | Asset failure | LV | 2.00 | 137.0 | 0.000422 | 0.0000031 | No
24/11/2023 | 16:10 | HH409A | URBAN | Asset failure | LV | 29.67 | 76.0 | 0.003476 | 0.0000457 | No
24/11/2023 | 16:21 | NA01 | LONG RURAL | Asset failure | LV | 29.00 | 121.0 | 0.025182 | 0.0002081 | No
24/11/2023 | 16:38 | MG42 | SHORT RURAL | Unknown | Unknown | 1.00 | 597.0 | 0.004200 | 0.0000070 | No
24/11/2023 | 17:08 | AP132E | URBAN | Asset failure | LV | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
24/11/2023 | 17:53 | MG28 | LONG RURAL | Unknown | Unknown | 199.00 | 81.8 | 0.116780 | 0.0014281 | No
24/11/2023 | 17:55 | MV52 | SHORT RURAL | Animal | Animal impact | 20.00 | 190.0 | 0.026735 | 0.0001407 | No
24/11/2023 | 18:04 | MV52 | SHORT RURAL | Animal | Animal impact | 1.00 | 190.0 | 0.001337 | 0.0000070 | No
24/11/2023 | 18:32 | MTB12 | SHORT RURAL | Unknown | Unknown | 30.00 | 311.0 | 0.065641 | 0.0002111 | No
24/11/2023 | 18:47 | MG24 | LONG RURAL | Weather |  | 1.00 | 329.0 | 0.002361 | 0.0000072 | No
24/11/2023 | 18:47 | MG24 | SHORT RURAL | Weather |  | 45.00 | 329.0 | 0.104160 | 0.0003166 | No
24/11/2023 | 18:58 | MI02 | SHORT RURAL | Asset failure | LV | 1.00 | 1,415.0 | 0.009955 | 0.0000070 | No
24/11/2023 | 19:04 | NL451C | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
24/11/2023 | 19:09 | MG26 | LONG RURAL | Weather |  | 12.00 | 504.0 | 0.043402 | 0.0000861 | No
24/11/2023 | 19:18 | SD49500 | LONG RURAL | Weather |  | 50.00 | 292.0 | 0.104774 | 0.0003588 | No
24/11/2023 | 19:25 | MI06 | LONG RURAL | Weather |  | 53.33 | 234.0 | 0.089561 | 0.0003827 | No
24/11/2023 | 19:50 | MG27 | LONG RURAL | Weather |  | 12.00 | 353.0 | 0.030399 | 0.0000861 | No
24/11/2023 | 20:20 | ME231A | URBAN | Asset failure | LV | 17.00 | 161.0 | 0.004220 | 0.0000262 | No
24/11/2023 | 20:20 | ST21 | SHORT RURAL | Asset failure | LV | 2.00 | 277.0 | 0.003898 | 0.0000141 | No
24/11/2023 | 20:46 | EL09 | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
24/11/2023 | 22:53 | SB17 | LONG RURAL | Unknown | Unknown | 91.00 | 214.7 | 0.140190 | 0.0006530 | No
24/11/2023 | 23:00 | SM350D | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
25/11/2023 | 05:27 | NA01 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 340.0 | 0.002440 | 0.0000072 | No
25/11/2023 | 06:15 | SD49100 | LONG RURAL | Unknown | Unknown | 216.33 | 188.0 | 0.291794 | 0.0015525 | No
25/11/2023 | 06:34 | MI04 | LONG RURAL | Weather |  | 1.00 | 617.0 | 0.004428 | 0.0000072 | No
25/11/2023 | 06:45 | KA27 | LONG RURAL | Unknown | Unknown | 1.00 | 197.0 | 0.001414 | 0.0000072 | No
25/11/2023 | 07:08 | PL24 | LONG RURAL | Animal | Animal impact | 11.00 | 255.5 | 0.020173 | 0.0000789 | No
25/11/2023 | 07:37 | MG29 | LONG RURAL | Weather |  | 1.00 | 493.0 | 0.003538 | 0.0000072 | No
25/11/2023 | 08:07 | KI32 | SHORT RURAL | Asset failure | LV | 1.00 | 195.0 | 0.001372 | 0.0000070 | No
25/11/2023 | 08:57 | NA32 | LONG RURAL | Unknown | Unknown | 8.00 | 107.0 | 0.006143 | 0.0000574 | No
25/11/2023 | 09:41 | MB12 | SHORT RURAL | Asset failure | LV | 10.33 | 270.0 | 0.019629 | 0.0000727 | No
25/11/2023 | 09:56 | SG02 | SHORT RURAL | Asset failure | LV | 1.00 | 150.0 | 0.001055 | 0.0000070 | No
25/11/2023 | 10:30 | KI32 | SHORT RURAL | Asset failure | LV | 1.00 | 54.0 | 0.000380 | 0.0000070 | No
25/11/2023 | 11:42 | AP146B | URBAN | Asset failure | LV | 15.33 | 154.0 | 0.003641 | 0.0000236 | No
25/11/2023 | 12:00 | PL10 | LONG RURAL | Overloads |  | 2.00 | 2,277.0 | 0.032681 | 0.0000144 | No
25/11/2023 | 12:16 | HH121G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 31.00 | 57.0 | 0.002724 | 0.0000478 | No
25/11/2023 | 14:36 | HH403B | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
25/11/2023 | 15:10 | MV32 | SHORT RURAL | Asset failure | LV | 5.00 | 527.0 | 0.018539 | 0.0000352 | No
25/11/2023 | 15:39 | W04 | LONG RURAL | Unknown | Unknown | 4.00 | 253.0 | 0.007262 | 0.0000287 | No
25/11/2023 | 15:39 | ST11 | SHORT RURAL | Weather |  | 292.00 | 45.8 | 0.094079 | 0.0020544 | No
25/11/2023 | 16:33 | ST36 | LONG RURAL | Weather |  | 1.00 | 113.0 | 0.000811 | 0.0000072 | No
25/11/2023 | 16:49 | ST36 | LONG RURAL | Weather |  | 12.67 | 133.0 | 0.012090 | 0.0000909 | No
25/11/2023 | 17:00 | HH145B | URBAN | Asset failure | LV | 25.33 | 93.0 | 0.003632 | 0.0000391 | No
25/11/2023 | 17:15 | ST11 | SHORT RURAL | Planned |  | 1.00 | 69.0 | 0.000485 | 0.0000070 | No
25/11/2023 | 17:57 | MV13 | SHORT RURAL | Asset failure | LV | 3.00 | 169.0 | 0.003567 | 0.0000211 | No
25/11/2023 | 19:12 | AP355H | URBAN | Asset failure | LV | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
26/11/2023 | 00:03 | CBD367N | CBD | Vegetation | Blow-in/Fall-in - NSP responsibility | 3.33 | 233.0 | 0.112211 | 0.0004816 | No
26/11/2023 | 01:35 | MB94 | LONG RURAL | Unknown | Unknown | 24.00 | 104.0 | 0.017912 | 0.0001722 | No
26/11/2023 | 06:14 | AP425B | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
26/11/2023 | 06:52 | YK08 | LONG RURAL | Unknown | Unknown | 48.00 | 250.1 | 0.086137 | 0.0003445 | No
26/11/2023 | 08:29 | VH22 | SHORT RURAL | Planned |  | 1.00 | 239.0 | 0.001681 | 0.0000070 | No
26/11/2023 | 08:46 | SM350B | URBAN | Planned |  | 83.00 | 372.7 | 0.047699 | 0.0001280 | No
26/11/2023 | 09:11 | SM126C | URBAN | Planned |  | 1.00 | 327.0 | 0.000504 | 0.0000015 | No
26/11/2023 | 11:51 | SD58101 | SHORT RURAL | Planned |  | 5.00 | 99.0 | 0.003483 | 0.0000352 | No
26/11/2023 | 11:58 | CD03 | SHORT RURAL | Planned |  | 3.00 | 85.0 | 0.001794 | 0.0000211 | No
26/11/2023 | 13:42 | AP139B | URBAN | Asset failure | LV | 1.00 | 291.0 | 0.000449 | 0.0000015 | No
26/11/2023 | 14:20 | ST42 | LONG RURAL | Asset failure | LV | 1.00 | 538.0 | 0.003861 | 0.0000072 | No
26/11/2023 | 14:22 | MV64 | SHORT RURAL | Asset failure | LV | 91.00 | 146.7 | 0.093924 | 0.0006402 | No
26/11/2023 | 14:37 | MB12 | SHORT RURAL | Unknown | Unknown | 1.00 | 53.0 | 0.000373 | 0.0000070 | No
26/11/2023 | 16:42 | KA04 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 79.0 | 0.000567 | 0.0000072 | No
26/11/2023 | 16:59 | MI16 | LONG RURAL | Asset failure | HV | 9.33 | 84.0 | 0.005626 | 0.0000670 | No
26/11/2023 | 17:18 | VH22 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 4.33 | 122.0 | 0.003719 | 0.0000305 | No
26/11/2023 | 19:00 | HH145D | URBAN | Asset failure | LV | 21.67 | 37.0 | 0.001236 | 0.0000334 | No
26/11/2023 | 21:27 | R32 | LONG RURAL | Asset failure | HV | 2.00 | 64.0 | 0.000919 | 0.0000144 | No
27/11/2023 | 00:39 | HH121A | URBAN | Unknown | Unknown | 5.00 | 136.0 | 0.001048 | 0.0000077 | No
27/11/2023 | 05:18 | HH121A | URBAN | Animal | Animal impact | 1.67 | 199.0 | 0.000511 | 0.0000026 | No
27/11/2023 | 05:34 | MTB14 | SHORT RURAL | Unknown | Unknown | 26.00 | 224.0 | 0.040975 | 0.0001829 | No
27/11/2023 | 06:49 | PL07 | URBAN | Asset failure | HV | 49.00 | 81.9 | 0.006186 | 0.0000755 | No
27/11/2023 | 08:02 | HH107B | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
27/11/2023 | 08:53 | MG11 | SHORT RURAL | Planned |  | 29.00 | 307.0 | 0.062637 | 0.0002040 | No
27/11/2023 | 08:55 | CBD367H | CBD | Overloads |  | 2.33 | 258.0 | 0.086975 | 0.0003371 | No
27/11/2023 | 08:55 | MI20 | LONG RURAL | Planned |  | 2.00 | 17.0 | 0.000244 | 0.0000144 | No
27/11/2023 | 08:56 | SA12 | URBAN | Asset failure | LV | 1.00 | 4,341.0 | 0.006693 | 0.0000015 | No
27/11/2023 | 08:59 | MV31 | SHORT RURAL | Planned |  | 22.00 | 327.0 | 0.050613 | 0.0001548 | No
27/11/2023 | 09:21 | MV31 | SHORT RURAL | Planned |  | 4.00 | 189.0 | 0.005319 | 0.0000281 | No
27/11/2023 | 09:23 | HH177F | URBAN | Asset failure | LV | 22.67 | 21.4 | 0.000746 | 0.0000349 | No
27/11/2023 | 09:27 | KI51 | LONG RURAL | Planned |  | 1.00 | 181.0 | 0.001299 | 0.0000072 | No
27/11/2023 | 09:42 | LC01 | SHORT RURAL | Asset failure | LV | 1.00 | 343.0 | 0.002413 | 0.0000070 | No
27/11/2023 | 09:44 | VH34 | SHORT RURAL | Planned |  | 25.00 | 202.0 | 0.035529 | 0.0001759 | No
27/11/2023 | 10:00 | VH43 | SHORT RURAL | Asset failure | LV | 1.00 | 171.0 | 0.001203 | 0.0000070 | No
27/11/2023 | 10:07 | R32 | LONG RURAL | Asset failure | HV | 2.00 | 235.0 | 0.003373 | 0.0000144 | No
27/11/2023 | 10:42 | MG10 | LONG RURAL | Overloads |  | 1.00 | 158.0 | 0.001134 | 0.0000072 | No
27/11/2023 | 10:44 | VH12 | SHORT RURAL | Asset failure | LV | 63.00 | 120.8 | 0.053561 | 0.0004432 | No
27/11/2023 | 11:03 | NL511A | URBAN | Asset failure | LV | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
27/11/2023 | 11:04 | HH130A | URBAN | Asset failure | LV | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
27/11/2023 | 12:58 | HH102B | URBAN | Overloads |  | 55.00 | 116.0 | 0.009836 | 0.0000848 | No
27/11/2023 | 13:01 | NA09 | LONG RURAL | Planned |  | 3.00 | 141.0 | 0.003036 | 0.0000215 | No
27/11/2023 | 13:24 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 100.0 | 0.000704 | 0.0000070 | No
27/11/2023 | 13:35 | SM411F | URBAN | Asset failure | LV | 66.00 | 166.0 | 0.016891 | 0.0001018 | No
27/11/2023 | 15:01 | HH177D | URBAN | Asset failure | LV | 1.00 | 31.0 | 0.000048 | 0.0000015 | No
27/11/2023 | 15:16 | PL07 | URBAN | Weather |  | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
27/11/2023 | 15:27 | PL07 | URBAN | Weather |  | 281.00 | 8.9 | 0.003859 | 0.0004332 | No
27/11/2023 | 16:44 | AP125A | URBAN | Third Party | Vehicle impact | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
27/11/2023 | 16:46 | KA19 | LONG RURAL | Unknown | Unknown | 15.00 | 176.0 | 0.018946 | 0.0001076 | No
27/11/2023 | 17:13 | G40 | LONG RURAL | Weather |  | 1.00 | 62.0 | 0.000445 | 0.0000072 | No
27/11/2023 | 17:17 | M04 | LONG RURAL | Planned |  | 57.00 | 37.0 | 0.015135 | 0.0004091 | No
27/11/2023 | 18:18 | SM216A | URBAN | Unknown | Unknown | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
27/11/2023 | 18:39 | KA03 | LONG RURAL | Weather |  | 5.00 | 279.0 | 0.010011 | 0.0000359 | No
27/11/2023 | 18:39 | SM179C | URBAN | Asset failure | LV | 13.00 | 143.0 | 0.002866 | 0.0000200 | No
27/11/2023 | 19:23 | SM374B | URBAN | Asset failure | LV | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
27/11/2023 | 19:24 | HH409C | URBAN | Vegetation | Grow-in - NSP responsibility | 24.00 | 31.0 | 0.001147 | 0.0000370 | No
27/11/2023 | 19:30 | VH12 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,585.0 | 0.011151 | 0.0000070 | No
27/11/2023 | 19:49 | KA03 | LONG RURAL | Weather |  | 1,916.00 | 23.3 | 0.320158 | 0.0137498 | No
27/11/2023 | 20:29 | PL30 | LONG RURAL | Weather |  | 19.00 | 191.0 | 0.026043 | 0.0001364 | No
27/11/2023 | 20:34 | PA05 | LONG RURAL | Asset failure | LV | 1.00 | 1,127.0 | 0.008088 | 0.0000072 | No
27/11/2023 | 20:58 | ME200A | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
27/11/2023 | 21:05 | PL07 | URBAN | Weather |  | 4.00 | 1,042.0 | 0.006426 | 0.0000062 | No
27/11/2023 | 21:07 | ME200G | URBAN | Asset failure | LV | 146.00 | 195.0 | 0.043894 | 0.0002251 | No
27/11/2023 | 21:24 | GA28 | LONG RURAL | Weather |  | 368.00 | 190.1 | 0.502020 | 0.0026409 | No
27/11/2023 | 21:44 | EL16 | URBAN | Unknown | Unknown | 322.00 | 77.0 | 0.038226 | 0.0004964 | No
27/11/2023 | 22:05 | CM12 | LONG RURAL | Weather |  | 13.00 | 935.5 | 0.087279 | 0.0000933 | No
27/11/2023 | 22:14 | SM179C | URBAN | Asset failure | LV | 1.00 | 93.0 | 0.000143 | 0.0000015 | No
27/11/2023 | 22:40 | SM349E | URBAN | Asset failure | LV | 25.33 | 129.0 | 0.005038 | 0.0000391 | No
27/11/2023 | 23:12 | CV15 | LONG RURAL | Weather |  | 8.00 | 1,012.0 | 0.058100 | 0.0000574 | No
27/11/2023 | 23:55 | HH386C | URBAN | Vegetation | Grow-in - NSP responsibility | 57.00 | 66.0 | 0.005800 | 0.0000879 | No
28/11/2023 | 00:02 | CV15 | LONG RURAL | Weather |  | 55.00 | 512.6 | 0.202322 | 0.0003947 | Yes
28/11/2023 | 00:47 | YK21 | LONG RURAL | Weather |  | 93.00 | 301.3 | 0.201081 | 0.0006674 | Yes
28/11/2023 | 01:08 | HH386F | URBAN | Weather |  | 22.33 | 183.0 | 0.006301 | 0.0000344 | Yes
28/11/2023 | 01:09 | HH386C | URBAN | Unknown | Unknown | 24.67 | 139.0 | 0.005286 | 0.0000380 | Yes
28/11/2023 | 01:10 | HH386D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 414.00 | 82.0 | 0.052339 | 0.0006383 | Yes
28/11/2023 | 01:48 | GA25 | SHORT RURAL | Unknown | Unknown | 1,180.00 | 163.5 | 1.357505 | 0.0083019 | Yes
28/11/2023 | 02:33 | NL210D | URBAN | Unknown | Unknown | 1.00 | 117.0 | 0.000180 | 0.0000015 | Yes
28/11/2023 | 02:35 | NL210D | URBAN | Unknown | Unknown | 1.00 | 113.0 | 0.000174 | 0.0000015 | Yes
28/11/2023 | 02:56 | NL210D | URBAN | Unknown | Unknown | 1.00 | 95.0 | 0.000146 | 0.0000015 | Yes
28/11/2023 | 03:02 | SSD395 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 7,295.00 | 93.0 | 4.868673 | 0.0523513 | Yes
28/11/2023 | 03:02 | SSD395 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 3,385.00 | 93.0 | 2.214808 | 0.0238151 | Yes
28/11/2023 | 03:22 | MT01 | LONG RURAL | Weather |  | 93.00 | 214.0 | 0.142823 | 0.0006674 | Yes
28/11/2023 | 03:28 | HH386D | URBAN | Unknown | Unknown | 1.00 | 87.0 | 0.000134 | 0.0000015 | Yes
28/11/2023 | 03:37 | KA15 | LONG RURAL | Weather |  | 86.00 | 425.8 | 0.262819 | 0.0006172 | Yes
28/11/2023 | 03:40 | GA13 | LONG RURAL | Weather |  | 182.00 | 427.8 | 0.558720 | 0.0013061 | Yes
28/11/2023 | 03:40 | GA13 | SHORT RURAL | Weather |  | 2.00 | 453.0 | 0.006374 | 0.0000141 | Yes
28/11/2023 | 03:42 | GA21 | LONG RURAL | Weather |  | 21.00 | 729.0 | 0.109862 | 0.0001507 | Yes
28/11/2023 | 03:52 | YK08 | LONG RURAL | Weather |  | 16.00 | 664.0 | 0.076241 | 0.0001148 | Yes
28/11/2023 | 03:56 | SD33200 | LONG RURAL | Weather |  | 357.00 | 383.5 | 0.982404 | 0.0025619 | Yes
28/11/2023 | 04:17 | EL19 | URBAN | Weather |  | 418.00 | 20.7 | 0.013336 | 0.0006445 | Yes
28/11/2023 | 04:35 | WK81 | SHORT RURAL | Weather |  | 3.33 | 683.0 | 0.016017 | 0.0000235 | Yes
28/11/2023 | 04:39 | GA800C | SHORT RURAL | Weather |  | 36.00 | 311.0 | 0.078769 | 0.0002533 | Yes
28/11/2023 | 04:39 | AP425C | URBAN | Weather |  | 53.00 | 366.0 | 0.029907 | 0.0000817 | Yes
28/11/2023 | 04:39 | KA17 | LONG RURAL | Weather |  | 49.00 | 571.2 | 0.200865 | 0.0003516 | Yes
28/11/2023 | 04:51 | R28 | LONG RURAL | Weather |  | 85.00 | 490.1 | 0.298966 | 0.0006100 | Yes
28/11/2023 | 05:04 | HH496E | URBAN | Unknown | Unknown | 29.00 | 323.0 | 0.014442 | 0.0000447 | Yes
28/11/2023 | 05:14 | KA29 | LONG RURAL | Weather |  | 67.00 | 363.0 | 0.174536 | 0.0004808 | Yes
28/11/2023 | 05:28 | VH44 | SHORT RURAL | Weather |  | 4.00 | 254.0 | 0.007148 | 0.0000281 | Yes
28/11/2023 | 05:28 | HH177C | URBAN | Weather |  | 1.00 | 238.0 | 0.000367 | 0.0000015 | Yes
28/11/2023 | 05:34 | BS0396 | SHORT RURAL | Unknown | Unknown | 1.00 | 777.0 | 0.005467 | 0.0000070 | Yes
28/11/2023 | 05:34 | GA800C | SHORT RURAL | Unknown | Unknown | 1.00 | 300.0 | 0.002111 | 0.0000070 | Yes
28/11/2023 | 05:34 | EL16 | URBAN | Weather |  | 322.00 | 780.5 | 0.387466 | 0.0004964 | Yes
28/11/2023 | 05:36 | EL15 | URBAN | Weather |  | 303.00 | 414.8 | 0.193780 | 0.0004672 | Yes
28/11/2023 | 05:41 | ME347E | URBAN | Weather |  | 239.00 | 200.0 | 0.073696 | 0.0003685 | Yes
28/11/2023 | 05:42 | SA744C | URBAN | Weather |  | 630.00 | 366.2 | 0.355715 | 0.0009713 | Yes
28/11/2023 | 05:50 | HH177C | URBAN | Weather |  | 15.00 | 216.0 | 0.004995 | 0.0000231 | Yes
28/11/2023 | 05:51 | SSD200 | URBAN | Weather |  | 2,824.00 | 93.2 | 0.405874 | 0.0043539 | Yes
28/11/2023 | 05:52 | HH409E | URBAN | Unknown | Unknown | 40.33 | 288.0 | 0.017909 | 0.0000622 | Yes
28/11/2023 | 05:57 | SSD168 | SHORT RURAL | Weather |  | 279.00 | 218.0 | 0.427913 | 0.0019629 | Yes
28/11/2023 | 05:58 | MTB32 | LONG RURAL | Weather |  | 1.00 | 531.0 | 0.003811 | 0.0000072 | Yes
28/11/2023 | 05:59 | NU03 | LONG RURAL | Weather |  | 29.00 | 560.1 | 0.116565 | 0.0002081 | Yes
28/11/2023 | 06:03 | SM126A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 196.0 | 0.000302 | 0.0000015 | Yes
28/11/2023 | 06:03 | R04 | LONG RURAL | Weather |  | 17.00 | 672.0 | 0.081982 | 0.0001220 | Yes
28/11/2023 | 06:04 | R01 | LONG RURAL | Weather |  | 2.00 | 347.0 | 0.004980 | 0.0000144 | Yes
28/11/2023 | 06:04 | GA22 | SHORT RURAL | Weather |  | 314.00 | 23.0 | 0.050895 | 0.0022091 | Yes
28/11/2023 | 06:05 | HH121C | URBAN | Weather |  | 2,339.00 | 14.6 | 0.052662 | 0.0036062 | Yes
28/11/2023 | 06:06 | HH403A | URBAN | Weather |  | 1,529.00 | 3.3 | 0.007713 | 0.0023573 | Yes
28/11/2023 | 06:07 | NL210A | URBAN | Unknown | Unknown | 1.00 | 168.0 | 0.000259 | 0.0000015 | Yes
28/11/2023 | 06:07 | SM410A | URBAN | Weather |  | 39.00 | 675.0 | 0.040587 | 0.0000601 | Yes
28/11/2023 | 06:08 | SD39100 | LONG RURAL | Weather |  | 2,528.00 | 216.0 | 3.918620 | 0.0181418 | Yes
28/11/2023 | 06:09 | HH121C | URBAN | Unknown | Unknown | 1.00 | 292.0 | 0.000450 | 0.0000015 | Yes
28/11/2023 | 06:10 | KA05 | LONG RURAL | Weather |  | 29.00 | 222.0 | 0.046201 | 0.0002081 | Yes
28/11/2023 | 06:10 | BM56 | SHORT RURAL | Unknown | Unknown | 71.00 | 154.0 | 0.076926 | 0.0004995 | Yes
28/11/2023 | 06:11 | NL210D | URBAN | Overloads |  | 1.00 | 243.0 | 0.000375 | 0.0000015 | Yes
28/11/2023 | 06:18 | CV16 | LONG RURAL | Weather |  | 38.00 | 596.2 | 0.162594 | 0.0002727 | Yes
28/11/2023 | 06:19 | ME231F | URBAN | Vegetation | Grow-in - NSP responsibility | 15.00 | 515.5 | 0.011921 | 0.0000231 | Yes
28/11/2023 | 06:19 | R01 | LONG RURAL | Weather |  | 132.00 | 300.0 | 0.284183 | 0.0009473 | Yes
28/11/2023 | 06:21 | BM53 | SHORT RURAL | Unknown | Unknown | 5.33 | 202.0 | 0.007580 | 0.0000375 | Yes
28/11/2023 | 06:22 | HH102B | URBAN | Asset failure | LV | 27.33 | 218.0 | 0.009187 | 0.0000421 | Yes
28/11/2023 | 06:26 | CM25 | LONG RURAL | Weather |  | 35.00 | 247.0 | 0.062039 | 0.0002512 | Yes
28/11/2023 | 06:28 | SM126C | URBAN | Unknown | Unknown | 1.00 | 322.0 | 0.000496 | 0.0000015 | Yes
28/11/2023 | 06:31 | KA03 | LONG RURAL | Unknown | Unknown | 5.00 | 427.0 | 0.015321 | 0.0000359 | Yes
28/11/2023 | 06:33 | NL210C | URBAN | Unknown | Unknown | 1.00 | 343.0 | 0.000529 | 0.0000015 | Yes
28/11/2023 | 06:33 | NL21 | URBAN | Weather |  | 260.00 | 529.0 | 0.212062 | 0.0004009 | Yes
28/11/2023 | 06:34 | MV14 | SHORT RURAL | Unknown | Unknown | 1.00 | 352.0 | 0.002476 | 0.0000070 | Yes
28/11/2023 | 06:37 | MV22 | SHORT RURAL | Unknown | Unknown | 1.00 | 286.0 | 0.002012 | 0.0000070 | Yes
28/11/2023 | 06:40 | HH121E | URBAN | Unknown | Unknown | 1.00 | 659.0 | 0.001016 | 0.0000015 | Yes
28/11/2023 | 06:40 | NL21 | URBAN | Weather |  | 126.00 | 217.0 | 0.042155 | 0.0001943 | Yes
28/11/2023 | 06:42 | GA10 | LONG RURAL | Weather |  | 19.00 | 645.0 | 0.087946 | 0.0001364 | Yes
28/11/2023 | 06:45 | NL760A | URBAN | Weather |  | 45.00 | 184.0 | 0.012766 | 0.0000694 | Yes
28/11/2023 | 06:48 | NU04 | SHORT RURAL | Weather |  | 34.00 | 432.0 | 0.103337 | 0.0002392 | Yes
28/11/2023 | 06:57 | SA18 | URBAN | Asset failure | LV | 21.00 | 139.0 | 0.004500 | 0.0000324 | Yes
28/11/2023 | 06:58 | LX53 | SHORT RURAL | Weather |  | 5.00 | 284.0 | 0.009990 | 0.0000352 | Yes
28/11/2023 | 07:00 | NL760A | URBAN | Weather |  | 6.00 | 314.0 | 0.002905 | 0.0000093 | Yes
28/11/2023 | 07:03 | CV23 | LONG RURAL | Unknown | Unknown | 21.00 | 344.0 | 0.051842 | 0.0001507 | Yes
28/11/2023 | 07:05 | SM126C | URBAN | Weather |  | 103.00 | 281.0 | 0.044623 | 0.0001588 | Yes
28/11/2023 | 07:07 | MV15 | SHORT RURAL | Weather |  | 9.00 | 274.0 | 0.017350 | 0.0000633 | Yes
28/11/2023 | 07:09 | NL234A | URBAN | Overloads |  | 1.00 | 526.0 | 0.000811 | 0.0000015 | Yes
28/11/2023 | 07:11 | SM126C | URBAN | Unknown | Unknown | 1.00 | 284.0 | 0.000438 | 0.0000015 | Yes
28/11/2023 | 07:15 | SSD400 | SHORT RURAL | Network business | Switching and protection error | 4.00 | 12.0 | 0.000338 | 0.0000281 | Yes
28/11/2023 | 07:16 | GU34 | LONG RURAL | Weather |  | 93.00 | 344.7 | 0.230030 | 0.0006674 | Yes
28/11/2023 | 07:21 | MTB41 | SHORT RURAL | Weather |  | 266.00 | 17.3 | 0.032420 | 0.0018714 | Yes
28/11/2023 | 07:21 | ME347C | URBAN | Asset failure | LV | 1.00 | 252.0 | 0.000389 | 0.0000015 | Yes
28/11/2023 | 07:25 | HH432C | URBAN | Weather |  | 78.00 | 293.0 | 0.035235 | 0.0001203 | Yes
28/11/2023 | 07:26 | NU14 | LONG RURAL | Weather |  | 5.00 | 755.0 | 0.027091 | 0.0000359 | Yes
28/11/2023 | 07:27 | HH409D | URBAN | Asset failure | LV | 1.00 | 281.0 | 0.000433 | 0.0000015 | Yes
28/11/2023 | 07:29 | SD36400 | LONG RURAL | Weather |  | 6.00 | 639.0 | 0.027514 | 0.0000431 | Yes
28/11/2023 | 07:31 | LX51 | SHORT RURAL | Unknown | Unknown | 64.67 | 204.0 | 0.092812 | 0.0004550 | Yes
28/11/2023 | 07:31 | NU31 | LONG RURAL | Weather |  | 12.00 | 635.0 | 0.054684 | 0.0000861 | Yes
28/11/2023 | 07:34 | SSD212 | SHORT RURAL | Network business | Switching and protection error | 4.00 | 48.0 | 0.001351 | 0.0000281 | Yes
28/11/2023 | 07:36 | NU10 | LONG RURAL | Weather |  | 98.00 | 360.0 | 0.253181 | 0.0007033 | Yes
28/11/2023 | 07:40 | LX41 | SHORT RURAL | Weather |  | 1.00 | 334.0 | 0.002350 | 0.0000070 | Yes
28/11/2023 | 07:40 | R06 | LONG RURAL | Weather |  | 1.00 | 1,954.0 | 0.014023 | 0.0000072 | Yes
28/11/2023 | 07:40 | NU25 | LONG RURAL | Weather |  | 5.00 | 1,642.0 | 0.058918 | 0.0000359 | Yes
28/11/2023 | 07:42 | HH386G | URBAN | Asset failure | LV | 1.00 | 455.0 | 0.000701 | 0.0000015 | Yes
28/11/2023 | 07:45 | NU13 | LONG RURAL | Weather |  | 3.00 | 1,497.0 | 0.032229 | 0.0000215 | Yes
28/11/2023 | 07:46 | MTB21 | SHORT RURAL | Unknown | Unknown | 2.00 | 213.0 | 0.002997 | 0.0000141 | Yes
28/11/2023 | 07:46 | HH386G | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | Yes
28/11/2023 | 07:58 | NU15 | LONG RURAL | Weather |  | 171.00 | 219.0 | 0.268746 | 0.0012272 | Yes
28/11/2023 | 08:01 | NL234C | URBAN | Weather |  | 32.67 | 81.3 | 0.004094 | 0.0000504 | Yes
28/11/2023 | 08:02 | NU20 | LONG RURAL | Weather |  | 3.00 | 458.0 | 0.009860 | 0.0000215 | Yes
28/11/2023 | 08:02 | BU02 | LONG RURAL | Weather |  | 93.00 | 432.2 | 0.288467 | 0.0006674 | Yes
28/11/2023 | 08:02 | ME200G | URBAN | Unknown | Unknown | 1.00 | 161.0 | 0.000248 | 0.0000015 | Yes
28/11/2023 | 08:05 | CM11 | LONG RURAL | Weather |  | 4.00 | 494.0 | 0.014180 | 0.0000287 | Yes
28/11/2023 | 08:06 | NU21 | LONG RURAL | Unknown | Unknown | 17.00 | 333.0 | 0.040625 | 0.0001220 | Yes
28/11/2023 | 08:06 | NU14 | LONG RURAL | Weather |  | 3.00 | 767.0 | 0.016513 | 0.0000215 | Yes
28/11/2023 | 08:06 | SM410A | URBAN | Vegetation | Grow-in - NSP responsibility | 56.00 | 628.0 | 0.054220 | 0.0000863 | Yes
28/11/2023 | 08:14 | MB71 | LONG RURAL | Unknown | Unknown | 149.00 | 181.0 | 0.193538 | 0.0010693 | Yes
28/11/2023 | 08:18 | SM216B | URBAN | Unknown | Unknown | 1.00 | 137.0 | 0.000211 | 0.0000015 | Yes
28/11/2023 | 08:19 | M21 | LONG RURAL | Unknown | Unknown | 748.00 | 25.6 | 0.137455 | 0.0053679 | Yes
28/11/2023 | 08:19 | SSD400 | SHORT RURAL | Unknown | Unknown | 423.00 | 170.0 | 0.505922 | 0.0029760 | Yes
28/11/2023 | 08:24 | R11 | LONG RURAL | Weather |  | 80.00 | 480.0 | 0.275571 | 0.0005741 | Yes
28/11/2023 | 08:24 | HH118C | URBAN | Overloads |  | 6.00 | 608.0 | 0.005624 | 0.0000093 | Yes
28/11/2023 | 08:33 | NL111C | URBAN | Unknown | Unknown | 1.00 | 282.0 | 0.000435 | 0.0000015 | Yes
28/11/2023 | 08:34 | NL760C | URBAN | Weather |  | 1.00 | 2,893.0 | 0.004460 | 0.0000015 | Yes
28/11/2023 | 08:37 | AP149C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,805.00 | 43.0 | 0.119663 | 0.0027829 | Yes
28/11/2023 | 08:46 | AP132A | URBAN | Overloads |  | 6.33 | 178.0 | 0.001738 | 0.0000098 | Yes
28/11/2023 | 08:47 | SM349E | URBAN | Unknown | Unknown | 1.00 | 93.0 | 0.000143 | 0.0000015 | Yes
28/11/2023 | 08:47 | EL23 | URBAN | Unknown | Unknown | 2.00 | 658.0 | 0.002029 | 0.0000031 | Yes
28/11/2023 | 08:51 | KA27 | LONG RURAL | Weather |  | 2.00 | 417.0 | 0.005985 | 0.0000144 | Yes
28/11/2023 | 08:52 | CD01 | SHORT RURAL | Planned |  | 29.00 | 114.0 | 0.023259 | 0.0002040 | Yes
28/11/2023 | 08:53 | NL21 | URBAN | Weather |  | 1.00 | 325.0 | 0.000501 | 0.0000015 | Yes
28/11/2023 | 08:54 | HH121G | URBAN | Unknown | Unknown | 1.00 | 558.0 | 0.000860 | 0.0000015 | Yes
28/11/2023 | 08:54 | AP226C | URBAN | Asset failure | LV | 8.33 | 235.0 | 0.003019 | 0.0000128 | Yes
28/11/2023 | 08:55 | EL02 | URBAN | Overloads |  | 1.00 | 608.0 | 0.000937 | 0.0000015 | Yes
28/11/2023 | 08:56 | AP149B | URBAN | Unknown | Unknown | 1.00 | 206.0 | 0.000318 | 0.0000015 | Yes
28/11/2023 | 08:56 | GA17 | LONG RURAL | Weather |  | 12.00 | 82.8 | 0.007126 | 0.0000861 | Yes
28/11/2023 | 08:58 | NU31 | LONG RURAL | Weather |  | 3.00 | 1,518.0 | 0.032681 | 0.0000215 | Yes
28/11/2023 | 09:06 | HH409F | URBAN | Asset failure | LV | 1.00 | 183.0 | 0.000282 | 0.0000015 | Yes
28/11/2023 | 09:15 | R17 | LONG RURAL | Weather |  | 70.00 | 323.4 | 0.162472 | 0.0005023 | Yes
28/11/2023 | 09:16 | HH429C | URBAN | Asset failure | LV | 1.00 | 81.0 | 0.000125 | 0.0000015 | Yes
28/11/2023 | 09:23 | GA800A | SHORT RURAL | Unknown | Unknown | 2.67 | 601.0 | 0.011276 | 0.0000188 | Yes
28/11/2023 | 09:23 | ME200E | URBAN | Unknown | Unknown | 2.00 | 249.0 | 0.000768 | 0.0000031 | Yes
28/11/2023 | 09:26 | SSD400 | SHORT RURAL | Weather |  | 2,865.00 | 7.0 | 0.141097 | 0.0201567 | Yes
28/11/2023 | 09:30 | SM126C | URBAN | Unknown | Unknown | 1.00 | 187.0 | 0.000288 | 0.0000015 | Yes
28/11/2023 | 09:31 | AP149B | URBAN | Asset failure | HV | 101.00 | 221.0 | 0.034413 | 0.0001557 | Yes
28/11/2023 | 09:34 | EL260A | URBAN | Unknown | Unknown | 3.33 | 388.0 | 0.001994 | 0.0000051 | Yes
28/11/2023 | 09:37 | SM374A | URBAN | Asset failure | LV | 21.33 | 192.0 | 0.006315 | 0.0000329 | Yes
28/11/2023 | 09:40 | M03 | SHORT RURAL | Network business | Switching and protection error | 4.00 | 253.0 | 0.007120 | 0.0000281 | Yes
28/11/2023 | 09:41 | LX62 | LONG RURAL | Weather |  | 11.00 | 397.0 | 0.031339 | 0.0000789 | Yes
28/11/2023 | 09:41 | BT20 | LONG RURAL | Planned |  | 60.00 | 324.0 | 0.139508 | 0.0004306 | Yes
28/11/2023 | 09:42 | GU32 | LONG RURAL | Weather |  | 30.00 | 392.0 | 0.084394 | 0.0002153 | Yes
28/11/2023 | 09:42 | HH428D | URBAN | Vegetation | Grow-in - NSP responsibility | 5.67 | 90.0 | 0.000786 | 0.0000087 | Yes
28/11/2023 | 09:42 | NU02 | LONG RURAL | Weather |  | 85.67 | 271.0 | 0.166603 | 0.0006148 | Yes
28/11/2023 | 09:43 | LX53 | SHORT RURAL | Unknown | Unknown | 14.00 | 176.0 | 0.017335 | 0.0000985 | Yes
28/11/2023 | 09:46 | SA17 | URBAN | Unknown | Unknown | 1.00 | 77.0 | 0.000119 | 0.0000015 | Yes
28/11/2023 | 09:52 | NL760B | URBAN | Unknown | Unknown | 1.00 | 2,817.0 | 0.004343 | 0.0000015 | Yes
28/11/2023 | 09:54 | SM349F | URBAN | Vegetation | Grow-in - NSP responsibility | 16.67 | 102.0 | 0.002621 | 0.0000257 | Yes
28/11/2023 | 09:54 | SD36400 | LONG RURAL | Weather |  | 5.00 | 557.0 | 0.019986 | 0.0000359 | Yes
28/11/2023 | 09:56 | NL760A | URBAN | Unknown | Unknown | 1.00 | 200.0 | 0.000308 | 0.0000015 | Yes
28/11/2023 | 09:58 | WK31 | SHORT RURAL | Weather |  | 1.00 | 476.0 | 0.003349 | 0.0000070 | Yes
28/11/2023 | 10:03 | HH118D | URBAN | Third Party | Other | 1.00 | 2,807.0 | 0.004328 | 0.0000015 | Yes
28/11/2023 | 10:06 | SM216E | URBAN | Unknown | Unknown | 1.00 | 123.0 | 0.000190 | 0.0000015 | Yes
28/11/2023 | 10:07 | MB12 | SHORT RURAL | Asset failure | LV | 20.67 | 328.0 | 0.047691 | 0.0001454 | Yes
28/11/2023 | 10:07 | NL451C | URBAN | Asset failure | LV | 14.00 | 849.0 | 0.018325 | 0.0000216 | Yes
28/11/2023 | 10:08 | WK41 | SHORT RURAL | Asset failure | LV | 1.00 | 534.0 | 0.003757 | 0.0000070 | Yes
28/11/2023 | 10:10 | ME347C | URBAN | Unknown | Unknown | 1.00 | 119.0 | 0.000183 | 0.0000015 | Yes
28/11/2023 | 10:11 | GU32 | LONG RURAL | Weather |  | 6.00 | 457.0 | 0.019677 | 0.0000431 | Yes
28/11/2023 | 10:13 | WK61 | SHORT RURAL | Weather |  | 1.00 | 257.0 | 0.001808 | 0.0000070 | Yes
28/11/2023 | 10:14 | SSD400 | SHORT RURAL | Weather |  | 435.00 | 243.0 | 0.743687 | 0.0030604 | Yes
28/11/2023 | 10:25 | GA26 | URBAN | Asset failure | LV | 17.00 | 180.0 | 0.004718 | 0.0000262 | Yes
28/11/2023 | 10:25 | ME231D | URBAN | Unknown | Unknown | 1.00 | 54.0 | 0.000083 | 0.0000015 | Yes
28/11/2023 | 10:29 | MTB22 | SHORT RURAL | Weather |  | 40.00 | 23.0 | 0.006473 | 0.0002814 | Yes
28/11/2023 | 10:29 | HH429A | URBAN | Asset failure | HV | 629.00 | 86.7 | 0.084109 | 0.0009698 | Yes
28/11/2023 | 10:34 | AP132A | URBAN | Overloads |  | 1.00 | 102.0 | 0.000157 | 0.0000015 | Yes
28/11/2023 | 10:40 | AP149E | URBAN | Asset failure | LV | 23.33 | 256.0 | 0.009209 | 0.0000360 | Yes
28/11/2023 | 10:42 | KA15 | LONG RURAL | Weather |  | 2.00 | 496.0 | 0.007119 | 0.0000144 | Yes
28/11/2023 | 10:45 | MB63 | LONG RURAL | Weather |  | 2.00 | 439.0 | 0.006301 | 0.0000144 | Yes
28/11/2023 | 10:45 | WK42 | SHORT RURAL | Weather |  | 378.00 | 86.3 | 0.229512 | 0.0026594 | Yes
28/11/2023 | 10:45 | SM137B | URBAN | Unknown | Unknown | 1.00 | 70.0 | 0.000108 | 0.0000015 | Yes
28/11/2023 | 10:46 | SD37301 | SHORT RURAL | Weather |  | 3.00 | 939.0 | 0.019819 | 0.0000211 | Yes
28/11/2023 | 10:48 | GA26 | URBAN | Vegetation | Grow-in - NSP responsibility | 13.00 | 191.0 | 0.003828 | 0.0000200 | Yes
28/11/2023 | 11:05 | R33 | LONG RURAL | Weather |  | 85.00 | 200.0 | 0.121998 | 0.0006100 | Yes
28/11/2023 | 11:16 | EL17 | URBAN | Weather |  | 1,596.00 | 264.6 | 0.651187 | 0.0024606 | Yes
28/11/2023 | 11:17 | SM350A | URBAN | Weather |  | 1.00 | 309.0 | 0.000476 | 0.0000015 | Yes
28/11/2023 | 11:22 | WK32 | SHORT RURAL | Weather |  | 9.67 | 549.0 | 0.037337 | 0.0000680 | Yes
28/11/2023 | 11:25 | KA21 | LONG RURAL | Weather |  | 2.00 | 373.0 | 0.005354 | 0.0000144 | Yes
28/11/2023 | 11:43 | MB91 | LONG RURAL | Weather |  | 102.00 | 253.0 | 0.185192 | 0.0007320 | Yes
28/11/2023 | 11:46 | CV15 | LONG RURAL | Asset failure | HV | 2.00 | 368.0 | 0.005282 | 0.0000144 | Yes
28/11/2023 | 11:50 | HH102B | URBAN | Unknown | Unknown | 1.00 | 112.0 | 0.000173 | 0.0000015 | Yes
28/11/2023 | 11:52 | SM126C | URBAN | Unknown | Unknown | 1.00 | 91.0 | 0.000140 | 0.0000015 | Yes
28/11/2023 | 11:58 | LX52 | LONG RURAL | Weather |  | 342.00 | 46.5 | 0.114032 | 0.0024543 | Yes
28/11/2023 | 11:59 | HH145B | URBAN | Weather |  | 167.00 | 199.0 | 0.051237 | 0.0002575 | Yes
28/11/2023 | 12:01 | CD03 | SHORT RURAL | Weather |  | 738.00 | 137.0 | 0.711302 | 0.0051922 | Yes
28/11/2023 | 12:04 | LX51 | SHORT RURAL | Weather |  | 1.00 | 123.0 | 0.000865 | 0.0000070 | Yes
28/11/2023 | 12:04 | SA36 | URBAN | Weather |  | 2.00 | 1,499.0 | 0.004622 | 0.0000031 | Yes
28/11/2023 | 12:08 | EL03 | URBAN | Asset failure | LV | 1.00 | 507.0 | 0.000782 | 0.0000015 | Yes
28/11/2023 | 12:08 | AP829A | URBAN | Asset failure | HV | 2.67 | 492.0 | 0.002023 | 0.0000041 | Yes
28/11/2023 | 12:14 | HH522C | URBAN | Overloads |  | 35.00 | 149.0 | 0.008040 | 0.0000540 | Yes
28/11/2023 | 12:20 | MB63 | LONG RURAL | Weather |  | 288.00 | 27.8 | 0.057418 | 0.0020668 | Yes
28/11/2023 | 12:20 | SM216E | URBAN | Weather |  | 1.00 | 246.0 | 0.000379 | 0.0000015 | Yes
28/11/2023 | 12:36 | MT18 | LONG RURAL | Weather |  | 3.00 | 292.0 | 0.006286 | 0.0000215 | Yes
28/11/2023 | 12:39 | SM402E | URBAN | Unknown | Unknown | 1.00 | 352.0 | 0.000543 | 0.0000015 | Yes
28/11/2023 | 12:41 | HH145B | URBAN | Third Party | Other | 48.00 | 263.0 | 0.019463 | 0.0000740 | Yes
28/11/2023 | 12:41 | HH145B | URBAN | Vegetation | Grow-in - NSP responsibility | 569.00 | 133.8 | 0.117400 | 0.0008773 | Yes
28/11/2023 | 12:48 | M03 | SHORT RURAL | Unknown | Unknown | 3.00 | 200.0 | 0.004221 | 0.0000211 | Yes
28/11/2023 | 12:49 | HH409E | URBAN | Asset failure | LV | 2.00 | 423.0 | 0.001304 | 0.0000031 | Yes
28/11/2023 | 12:50 | HH341B | URBAN | Unknown | Unknown | 1.00 | 446.0 | 0.000688 | 0.0000015 | Yes
28/11/2023 | 13:02 | AP829A | URBAN | Weather |  | 1.00 | 127.0 | 0.000196 | 0.0000015 | Yes
28/11/2023 | 13:07 | HH118C | URBAN | Unknown | Unknown | 1.00 | 396.0 | 0.000611 | 0.0000015 | Yes
28/11/2023 | 13:13 | HH432C | URBAN | Weather |  | 1.00 | 80.0 | 0.000123 | 0.0000015 | Yes
28/11/2023 | 13:17 | ME427D | URBAN | Unknown | Unknown | 1.00 | 232.0 | 0.000358 | 0.0000015 | Yes
28/11/2023 | 13:24 | SM402D | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 375.0 | 0.000578 | 0.0000015 | Yes
28/11/2023 | 13:24 | CL06 | LONG RURAL | Weather |  | 8.00 | 400.0 | 0.022964 | 0.0000574 | Yes
28/11/2023 | 13:25 | MG46 | SHORT RURAL | Overloads |  | 1.00 | 84.0 | 0.000591 | 0.0000070 | Yes
28/11/2023 | 13:28 | CL09 | LONG RURAL | Weather |  | 1.00 | 77.0 | 0.000553 | 0.0000072 | Yes
28/11/2023 | 13:33 | HH386C | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | Yes
28/11/2023 | 13:34 | HH130F | URBAN | Asset failure | LV | 24.67 | 180.0 | 0.006845 | 0.0000380 | Yes
28/11/2023 | 13:54 | WK65 | SHORT RURAL | Weather |  | 2.00 | 260.0 | 0.003658 | 0.0000141 | Yes
28/11/2023 | 13:55 | M44 | LONG RURAL | Asset failure | HV | 56.00 | 531.5 | 0.213611 | 0.0004019 | Yes
28/11/2023 | 13:57 | AP139D | URBAN | Asset failure | LV | 2.00 | 220.0 | 0.000678 | 0.0000031 | Yes
28/11/2023 | 14:02 | MB63 | LONG RURAL | Weather |  | 1.00 | 243.0 | 0.001744 | 0.0000072 | Yes
28/11/2023 | 14:05 | LX53 | SHORT RURAL | Weather |  | 1.00 | 212.0 | 0.001492 | 0.0000070 | Yes
28/11/2023 | 14:06 | SM349F | URBAN | Weather |  | 1.00 | 270.0 | 0.000416 | 0.0000015 | Yes
28/11/2023 | 14:12 | HH522C | URBAN | Unknown | Unknown | 224.33 | 71.0 | 0.024557 | 0.0003459 | Yes
28/11/2023 | 14:12 | HH386C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 85.00 | 74.0 | 0.009698 | 0.0001310 | Yes
28/11/2023 | 14:18 | NU02 | LONG RURAL | Weather |  | 1,724.00 | 100.2 | 1.239438 | 0.0123720 | Yes
28/11/2023 | 14:24 | MTB41 | SHORT RURAL | Weather |  | 2.00 | 273.0 | 0.003841 | 0.0000141 | Yes
28/11/2023 | 14:27 | SM349H | URBAN | Asset failure | LV | 46.00 | 128.0 | 0.009078 | 0.0000709 | Yes
28/11/2023 | 14:32 | WK81 | SHORT RURAL | Weather |  | 2.00 | 131.0 | 0.001843 | 0.0000141 | Yes
28/11/2023 | 14:46 | R30 | LONG RURAL | Weather |  | 2.00 | 1,474.0 | 0.021156 | 0.0000144 | Yes
28/11/2023 | 14:49 | SM216E | URBAN | Unknown | Unknown | 1.00 | 403.0 | 0.000621 | 0.0000015 | Yes
28/11/2023 | 14:50 | HH386G | URBAN | Unknown | Unknown | 1.00 | 432.0 | 0.000666 | 0.0000015 | Yes
28/11/2023 | 15:02 | G12 | LONG RURAL | Weather |  | 32.00 | 1,461.0 | 0.335501 | 0.0002296 | Yes
28/11/2023 | 15:06 | HH121C | URBAN | Asset failure | LV | 1.00 | 324.0 | 0.000500 | 0.0000015 | Yes
28/11/2023 | 15:17 | AP424D | URBAN | Unknown | Unknown | 1.00 | 59.0 | 0.000091 | 0.0000015 | Yes
28/11/2023 | 15:58 | HH432F | URBAN | Vegetation | Grow-in - NSP responsibility | 5.00 | 129.0 | 0.000994 | 0.0000077 | Yes
28/11/2023 | 16:01 | NU21 | LONG RURAL | Weather |  | 2.00 | 1,043.0 | 0.014970 | 0.0000144 | Yes
28/11/2023 | 16:16 | SD36400 | LONG RURAL | Weather |  | 2.67 | 238.0 | 0.004555 | 0.0000191 | Yes
28/11/2023 | 16:24 | NL760B | URBAN | Unknown | Unknown | 1.00 | 677.0 | 0.001044 | 0.0000015 | Yes
28/11/2023 | 16:30 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 283.0 | 0.001991 | 0.0000070 | Yes
28/11/2023 | 16:38 | HK05 | LONG RURAL | Weather |  | 3.00 | 111.0 | 0.002390 | 0.0000215 | Yes
28/11/2023 | 16:47 | ST22 | SHORT RURAL | Weather |  | 3.00 | 290.3 | 0.006128 | 0.0000211 | Yes
28/11/2023 | 17:30 | MTB13 | SHORT RURAL | Asset failure | LV | 1.00 | 85.0 | 0.000598 | 0.0000070 | Yes
28/11/2023 | 17:47 | SM126E | URBAN | Asset failure | LV | 1.00 | 204.0 | 0.000315 | 0.0000015 | Yes
28/11/2023 | 18:37 | GA13 | LONG RURAL | Weather |  | 1.00 | 84.0 | 0.000603 | 0.0000072 | Yes
28/11/2023 | 18:39 | CM03 | LONG RURAL | Weather |  | 7.00 | 524.7 | 0.026359 | 0.0000502 | Yes
28/11/2023 | 18:52 | WK42 | SHORT RURAL | Unknown | Unknown | 82.00 | 139.0 | 0.080191 | 0.0005769 | Yes
28/11/2023 | 18:54 | HH118C | URBAN | Asset failure | LV | 8.00 | 157.0 | 0.001936 | 0.0000123 | Yes
28/11/2023 | 19:38 | SD34400 | LONG RURAL | Weather |  | 1.00 | 76.0 | 0.000545 | 0.0000072 | Yes
28/11/2023 | 20:04 | SA19 | URBAN | Asset failure | LV | 4.00 | 165.0 | 0.001018 | 0.0000062 | Yes
28/11/2023 | 20:11 | SA33 | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | Yes
28/11/2023 | 20:31 | CBD27P | CBD | Planned |  | 2.00 | 7,308.0 | 2.111681 | 0.0002890 | Yes
28/11/2023 | 20:37 | EL01A | URBAN | Asset failure | LV | 21.00 | 147.0 | 0.004759 | 0.0000324 | Yes
28/11/2023 | 20:50 | SM411D | URBAN | Asset failure | HV | 636.67 | 3.5 | 0.003474 | 0.0009816 | Yes
28/11/2023 | 21:08 | SM216C | URBAN | Overloads |  | 1.00 | 36.0 | 0.000056 | 0.0000015 | Yes
28/11/2023 | 21:21 | CL28 | LONG RURAL | Asset failure | HV | 2.00 | 24.0 | 0.000344 | 0.0000144 | Yes
28/11/2023 | 21:27 | AP146C | URBAN | Asset failure | LV | 104.00 | 77.0 | 0.012346 | 0.0001603 | Yes
28/11/2023 | 21:35 | SA744C | URBAN | Unknown | Unknown | 12.67 | 13.2 | 0.000257 | 0.0000195 | Yes
29/11/2023 | 03:54 | BT01 | LONG RURAL | Asset failure | HV | 933.00 | 388.5 | 2.601362 | 0.0066955 | No
29/11/2023 | 04:01 | EL15 | URBAN | Weather |  | 3.00 | 48.0 | 0.000222 | 0.0000046 | No
29/11/2023 | 07:34 | SM172F | URBAN | Asset failure | HV | 2,183.00 | 16.3 | 0.054857 | 0.0033656 | No
29/11/2023 | 08:47 | EL15 | URBAN | Weather |  | 1.00 | 1,881.0 | 0.002900 | 0.0000015 | No
29/11/2023 | 08:51 | SD34405 | LONG RURAL | Weather |  | 2.00 | 257.0 | 0.003689 | 0.0000144 | No
29/11/2023 | 09:08 | NU31 | LONG RURAL | Weather |  | 11.00 | 2,706.0 | 0.213611 | 0.0000789 | No
29/11/2023 | 09:58 | SD39100 | LONG RURAL | Unknown | Unknown | 1.00 | 409.0 | 0.002935 | 0.0000072 | No
29/11/2023 | 10:22 | W18 | LONG RURAL | Planned |  | 14.00 | 245.0 | 0.024615 | 0.0001005 | No
29/11/2023 | 11:26 | GA10 | LONG RURAL | Weather |  | 19.00 | 288.6 | 0.039348 | 0.0001364 | No
29/11/2023 | 12:54 | GA15 | SHORT RURAL | Weather |  | 1.00 | 2,230.0 | 0.015689 | 0.0000070 | No
29/11/2023 | 13:39 | AP132A | URBAN | Asset failure | LV | 12.67 | 875.0 | 0.017088 | 0.0000195 | No
29/11/2023 | 14:27 | SD49100 | LONG RURAL | Network business | Switching and protection error | 6,484.00 | 5.0 | 0.232657 | 0.0465313 | No
29/11/2023 | 14:27 | HH496A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,472.00 | 128.9 | 0.292498 | 0.0022695 | No
29/11/2023 | 15:06 | AP149D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 93.00 | 1,263.0 | 0.181093 | 0.0001434 | No
29/11/2023 | 15:16 | CL05 | LONG RURAL | Animal | Animal impact | 8.00 | 177.0 | 0.010162 | 0.0000574 | No
29/11/2023 | 15:29 | WK71 | SHORT RURAL | Weather |  | 1.00 | 30.0 | 0.000211 | 0.0000070 | No
29/11/2023 | 15:35 | ST21 | SHORT RURAL | Asset failure | HV | 192.00 | 275.7 | 0.372445 | 0.0013508 | No
29/11/2023 | 16:03 | CD16 | SHORT RURAL | Unknown | Unknown | 60.00 | 261.6 | 0.110443 | 0.0004221 | No
29/11/2023 | 17:02 | EL16 | URBAN | Asset failure | HV | 12.00 | 194.9 | 0.003606 | 0.0000185 | No
30/11/2023 | 00:03 | EL01R | URBAN | Overloads |  | 22.00 | 33.0 | 0.001119 | 0.0000339 | No
30/11/2023 | 03:42 | NL210A | URBAN | Unknown | Unknown | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
30/11/2023 | 04:46 | HH177G | URBAN | Asset failure | LV | 1.00 | 1,038.0 | 0.001600 | 0.0000015 | No
30/11/2023 | 04:55 | SM126D | URBAN | Overloads |  | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
30/11/2023 | 05:10 | ST12 | SHORT RURAL | Asset failure | HV | 1,935.00 | 359.9 | 4.899452 | 0.0136137 | No
30/11/2023 | 05:52 | LX21 | SHORT RURAL | Animal | Animal impact | 43.00 | 121.1 | 0.036627 | 0.0003025 | No
30/11/2023 | 06:00 | LX21 | SHORT RURAL | Animal | Animal impact | 1.00 | 290.0 | 0.002040 | 0.0000070 | No
30/11/2023 | 06:41 | ST11 | SHORT RURAL | Asset failure | LV | 52.00 | 738.0 | 0.269994 | 0.0003658 | No
30/11/2023 | 07:56 | SM137B | URBAN | Animal | Animal nesting/burrowing, etc and other | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
30/11/2023 | 08:34 | HK04 | LONG RURAL | Planned |  | 30.00 | 280.0 | 0.060281 | 0.0002153 | No
30/11/2023 | 08:36 | SM126B | URBAN | Asset failure | LV | 1.00 | 675.0 | 0.001041 | 0.0000015 | No
30/11/2023 | 09:09 | SM137B | URBAN | Overloads |  | 1.00 | 329.0 | 0.000507 | 0.0000015 | No
30/11/2023 | 09:12 | EL04 | URBAN | Planned |  | 1.00 | 323.0 | 0.000498 | 0.0000015 | No
30/11/2023 | 09:28 | PP03 | URBAN | Planned |  | 159.00 | 225.4 | 0.055243 | 0.0002451 | No
30/11/2023 | 09:32 | HH522C | URBAN | Planned |  | 1.00 | 74.0 | 0.000114 | 0.0000015 | No
30/11/2023 | 09:33 | HH145E | URBAN | Asset failure | HV | 926.00 | 126.6 | 0.180717 | 0.0014277 | No
30/11/2023 | 09:45 | AP365E | URBAN | Asset failure | LV | 27.00 | 79.0 | 0.003289 | 0.0000416 | No
30/11/2023 | 09:52 | GA18 | LONG RURAL | Other |  | 1.00 | 223.0 | 0.001600 | 0.0000072 | No
30/11/2023 | 09:57 | EL01R | URBAN | Asset failure | LV | 1.00 | 381.0 | 0.000587 | 0.0000015 | No
30/11/2023 | 10:04 | NL210B | URBAN | Overloads |  | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
30/11/2023 | 11:02 | MTB14 | SHORT RURAL | Planned |  | 34.00 | 89.0 | 0.021289 | 0.0002392 | No
30/11/2023 | 11:05 | HH429B | URBAN | Asset failure | LV | 143.00 | 204.0 | 0.044973 | 0.0002205 | No
30/11/2023 | 11:17 | NL544B | URBAN | Overloads |  | 5.33 | 43.0 | 0.000354 | 0.0000082 | No
30/11/2023 | 11:19 | SD35100 | LONG RURAL | Weather |  | 154.00 | 5.0 | 0.005526 | 0.0011052 | No
30/11/2023 | 11:39 | MV15 | SHORT RURAL | Weather |  | 3.00 | 271.0 | 0.005720 | 0.0000211 | No
30/11/2023 | 12:13 | MG27 | LONG RURAL | Unknown | Unknown | 1.00 | 197.0 | 0.001414 | 0.0000072 | No
30/11/2023 | 12:52 | HH429B | URBAN | Asset failure | LV | 2.00 | 53.0 | 0.000163 | 0.0000031 | No
30/11/2023 | 13:05 | NA62 | LONG RURAL | Planned |  | 1.00 | 85.0 | 0.000610 | 0.0000072 | No
30/11/2023 | 13:24 | MB82 | LONG RURAL | Planned |  | 6.00 | 77.0 | 0.003315 | 0.0000431 | No
30/11/2023 | 13:36 | HH102D | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
30/11/2023 | 13:39 | HH107B | URBAN | Asset failure | LV | 93.00 | 65.0 | 0.009320 | 0.0001434 | No
30/11/2023 | 14:03 | KA07 | LONG RURAL | Planned |  | 2.00 | 17.0 | 0.000244 | 0.0000144 | No
30/11/2023 | 14:09 | MB23 | SHORT RURAL | Asset failure | LV | 1.00 | 272.0 | 0.001914 | 0.0000070 | No
30/11/2023 | 14:28 | BT02 | LONG RURAL | Unknown | Unknown | 221.00 | 4.4 | 0.006997 | 0.0015860 | No
30/11/2023 | 14:54 | BT02 | LONG RURAL | Unknown | Unknown | 1.00 | 133.0 | 0.000954 | 0.0000072 | No
30/11/2023 | 15:53 | SSD300 | SHORT RURAL | Weather |  | 3.00 | 33.0 | 0.000697 | 0.0000211 | No
30/11/2023 | 16:04 | BT02 | LONG RURAL | Asset failure | HV | 90.00 | 2.0 | 0.001292 | 0.0006459 | No
30/11/2023 | 16:16 | PP16 | SHORT RURAL | Other |  | 74.00 | 159.0 | 0.082780 | 0.0005206 | No
30/11/2023 | 16:17 | NA52 | LONG RURAL | Weather |  | 83.67 | 79.0 | 0.047433 | 0.0006004 | No
30/11/2023 | 17:05 | HH409A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 26.00 | 50.0 | 0.002004 | 0.0000401 | No
30/11/2023 | 17:18 | AP355F | URBAN | Asset failure | LV | 11.00 | 195.0 | 0.003307 | 0.0000170 | No
30/11/2023 | 17:49 | SM374A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 253.0 | 0.000390 | 0.0000015 | No
30/11/2023 | 18:36 | KI42 | LONG RURAL | Unknown | Unknown | 1.00 | 238.0 | 0.001708 | 0.0000072 | No
30/11/2023 | 19:30 | LX51 | SHORT RURAL | Asset failure | LV | 1.00 | 190.0 | 0.001337 | 0.0000070 | No
30/11/2023 | 19:54 | NL210D | URBAN | Asset failure | LV | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
30/11/2023 | 21:04 | ME200G | URBAN | Asset failure | LV | 155.00 | 198.0 | 0.047316 | 0.0002390 | No
30/11/2023 | 21:16 | SM402D | URBAN | Planned |  | 154.00 | 316.8 | 0.075224 | 0.0002374 | No
30/11/2023 | 22:34 | SA42 | URBAN | Animal | Animal impact | 44.00 | 258.0 | 0.017502 | 0.0000678 | No
30/11/2023 | 22:47 | SA42 | URBAN | Animal | Animal impact | 16.67 | 270.0 | 0.006938 | 0.0000257 | No
30/11/2023 | 23:29 | LM32 | LONG RURAL | Planned |  | 1.00 | 1.0 | 0.000007 | 0.0000072 | No
01/12/2023 | 00:39 | EL01R | URBAN | Asset failure | HV | 22.00 | 991.2 | 0.033621 | 0.0000339 | No
01/12/2023 | 00:51 | SM137A | URBAN | Asset failure | LV | 144.00 | 95.0 | 0.021091 | 0.0002220 | No
01/12/2023 | 03:13 | HH107C | URBAN | Other |  | 3.00 | 607.0 | 0.002808 | 0.0000046 | No
01/12/2023 | 03:59 | SA18 | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
01/12/2023 | 05:47 | ST12 | SHORT RURAL | Other |  | 1.00 | 187.0 | 0.001316 | 0.0000070 | No
01/12/2023 | 05:56 | SA42 | URBAN | Asset failure | LV | 1.00 | 648.0 | 0.000999 | 0.0000015 | No
01/12/2023 | 06:17 | NU31 | LONG RURAL | Weather |  | 1.00 | 3,058.0 | 0.021945 | 0.0000072 | No
01/12/2023 | 07:37 | CBD27D | CBD | Network business | Switching and protection error | 105.00 | 8.0 | 0.121361 | 0.0151701 | No
01/12/2023 | 09:00 | CV26 | LONG RURAL | Planned |  | 70.00 | 145.0 | 0.072840 | 0.0005023 | No
01/12/2023 | 09:01 | CL06 | LONG RURAL | Planned |  | 1.00 | 48.0 | 0.000344 | 0.0000072 | No
01/12/2023 | 09:22 | SM349B | URBAN | Planned |  | 46.00 | 285.0 | 0.020212 | 0.0000709 | No
01/12/2023 | 09:42 | GA22 | SHORT RURAL | Planned |  | 285.00 | 285.6 | 0.572605 | 0.0020051 | No
01/12/2023 | 09:42 | LM11 | LONG RURAL | Unknown | Unknown | 58.00 | 221.0 | 0.091986 | 0.0004162 | No
01/12/2023 | 10:55 | NL451A | URBAN | Asset failure | LV | 1.00 | 358.0 | 0.000552 | 0.0000015 | No
01/12/2023 | 11:04 | HH130A | URBAN | Asset failure | LV | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
01/12/2023 | 11:40 | ST35 | LONG RURAL | Weather |  | 16.67 | 54.0 | 0.006459 | 0.0001196 | No
01/12/2023 | 11:51 | HH102A | URBAN | Asset failure | LV | 7.00 | 118.0 | 0.001273 | 0.0000108 | No
01/12/2023 | 11:57 | NL234B | URBAN | Planned |  | 1,093.00 | 5.5 | 0.009206 | 0.0016851 | No
01/12/2023 | 12:36 | VH10 | SHORT RURAL | Asset failure | LV | 27.00 | 144.0 | 0.027354 | 0.0001900 | No
01/12/2023 | 12:50 | WK42 | SHORT RURAL | Unknown | Unknown | 1.00 | 116.0 | 0.000816 | 0.0000070 | No
01/12/2023 | 13:59 | HH496G | URBAN | Asset failure | LV | 3.00 | 232.0 | 0.001073 | 0.0000046 | No
01/12/2023 | 15:41 | SA16 | URBAN | Asset failure | LV | 1.00 | 739.0 | 0.001139 | 0.0000015 | No
01/12/2023 | 16:32 | VH23 | SHORT RURAL | Asset failure | LV | 28.33 | 69.0 | 0.013754 | 0.0001993 | No
01/12/2023 | 16:46 | SM350F | URBAN | Asset failure | LV | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
01/12/2023 | 16:58 | ST11 | SHORT RURAL | Animal | Animal impact | 48.00 | 22.0 | 0.007429 | 0.0003377 | No
01/12/2023 | 17:05 | PP18 | LONG RURAL | Asset failure | LV | 1.00 | 218.0 | 0.001564 | 0.0000072 | No
01/12/2023 | 20:41 | NL451C | URBAN | Asset failure | LV | 1.00 | 114.0 | 0.000176 | 0.0000015 | No
01/12/2023 | 20:53 | VH15 | SHORT RURAL | Asset failure | LV | 1.00 | 787.0 | 0.005537 | 0.0000070 | No
01/12/2023 | 21:01 | ME347B | URBAN | Asset failure | LV | 183.00 | 190.9 | 0.053861 | 0.0002821 | No
01/12/2023 | 21:29 | CBD366M | CBD | Planned |  | 1.00 | 761.0 | 0.109947 | 0.0001445 | No
02/12/2023 | 03:47 | EL09 | URBAN | Asset failure | LV | 19.00 | 290.0 | 0.008495 | 0.0000293 | No
02/12/2023 | 06:28 | G09 | LONG RURAL | Unknown | Unknown | 48.00 | 438.6 | 0.151090 | 0.0003445 | No
02/12/2023 | 08:55 | SM350A | URBAN | Planned |  | 217.00 | 327.1 | 0.109418 | 0.0003346 | No
02/12/2023 | 09:04 | MV41 | SHORT RURAL | Asset failure | HV | 14.00 | 283.0 | 0.027875 | 0.0000985 | No
02/12/2023 | 12:20 | EL25 | URBAN | Asset failure | LV | 29.00 | 53.0 | 0.002370 | 0.0000447 | No
02/12/2023 | 13:00 | MT12 | LONG RURAL | Asset failure | HV | 19.00 | 193.0 | 0.026316 | 0.0001364 | No
02/12/2023 | 14:04 | SM350H | URBAN | Asset failure | LV | 44.00 | 322.0 | 0.021844 | 0.0000678 | No
02/12/2023 | 15:28 | SM350H | URBAN | Asset failure | LV | 125.00 | 515.0 | 0.099250 | 0.0001927 | No
02/12/2023 | 15:37 | CN33 | LONG RURAL | Weather |  | 4.00 | 59.0 | 0.001694 | 0.0000287 | No
02/12/2023 | 15:59 | M11 | LONG RURAL | Overloads |  | 5.33 | 194.0 | 0.007425 | 0.0000383 | No
02/12/2023 | 16:27 | NL111B | URBAN | Asset failure | LV | 83.00 | 84.0 | 0.010749 | 0.0001280 | No
02/12/2023 | 17:42 | HH496A | URBAN | Unknown | Unknown | 117.33 | 50.8 | 0.009185 | 0.0001809 | No
02/12/2023 | 20:13 | NL111Q | URBAN | Asset failure | LV | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
02/12/2023 | 22:36 | SG07 | SHORT RURAL | Unknown | Unknown | 1.00 | 113.0 | 0.000795 | 0.0000070 | No
02/12/2023 | 22:47 | EL16 | URBAN | Third Party | Vehicle impact | 5.00 | 132.0 | 0.001018 | 0.0000077 | No
03/12/2023 | 01:35 | MV32 | SHORT RURAL | Asset failure | HV | 5.00 | 386.0 | 0.013578 | 0.0000352 | No
03/12/2023 | 06:39 | CD23 | LONG RURAL | Unknown | Unknown | 10.00 | 462.0 | 0.033155 | 0.0000718 | No
03/12/2023 | 08:34 | AP355E | URBAN | Planned |  | 42.00 | 315.0 | 0.020400 | 0.0000648 | No
03/12/2023 | 08:44 | SA744C | URBAN | Planned |  | 11.00 | 293.0 | 0.004969 | 0.0000170 | No
03/12/2023 | 09:59 | LX21 | SHORT RURAL | Unknown | Unknown | 44.00 | 60.2 | 0.018630 | 0.0003096 | No
03/12/2023 | 10:41 | SA14 | URBAN | Overloads |  | 1.00 | 177.0 | 0.000273 | 0.0000015 | No
03/12/2023 | 10:45 | HH177C | URBAN | Asset failure | LV | 16.33 | 130.0 | 0.003274 | 0.0000252 | No
03/12/2023 | 11:12 | AP344D | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
03/12/2023 | 11:41 | BM56 | SHORT RURAL | Other |  | 2.00 | 109.0 | 0.001534 | 0.0000141 | No
03/12/2023 | 12:10 | AP139C | URBAN | Asset failure | LV | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
03/12/2023 | 13:20 | NL210A | URBAN | Asset failure | LV | 9.33 | 157.0 | 0.002259 | 0.0000144 | No
03/12/2023 | 13:31 | NL111B | URBAN | Other |  | 5.00 | 57.0 | 0.000439 | 0.0000077 | No
03/12/2023 | 13:46 | MG49 | LONG RURAL | Asset failure | HV | 3.00 | 71.0 | 0.001529 | 0.0000215 | No
03/12/2023 | 14:31 | MG10 | LONG RURAL | Asset failure | HV | 18.33 | 29.0 | 0.003815 | 0.0001316 | No
03/12/2023 | 14:31 | SA42 | URBAN | Asset failure | HV | 3,182.00 | 34.9 | 0.171207 | 0.0049059 | No
03/12/2023 | 15:18 | MG10 | LONG RURAL | Unknown | Unknown | 14.67 | 20.0 | 0.002105 | 0.0001053 | No
03/12/2023 | 17:28 | HH496F | URBAN | Asset failure | LV | 3.33 | 151.0 | 0.000776 | 0.0000051 | No
03/12/2023 | 17:56 | ME200G | URBAN | Asset failure | LV | 1.00 | 327.0 | 0.000504 | 0.0000015 | No
03/12/2023 | 18:21 | NL111B | URBAN | Animal | Animal impact | 1,641.00 | 8.0 | 0.020282 | 0.0025300 | No
03/12/2023 | 18:46 | AP355B | URBAN | Asset failure | LV | 1.33 | 170.0 | 0.000349 | 0.0000021 | No
03/12/2023 | 19:00 | CBD412T | CBD | Overloads |  | 3.00 | 190.0 | 0.082352 | 0.0004334 | No
03/12/2023 | 21:23 | NL210E | URBAN | Overloads |  | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
03/12/2023 | 22:32 | HH341A | URBAN | Planned |  | 113.00 | 379.4 | 0.066090 | 0.0001742 | No
03/12/2023 | 23:55 | HH341A | URBAN | Planned |  | 47.00 | 295.0 | 0.021376 | 0.0000725 | No
04/12/2023 | 00:14 | GU42 | LONG RURAL | Animal | Animal impact | 42.00 | 140.0 | 0.042197 | 0.0003014 | No
04/12/2023 | 00:17 | HH121E | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
04/12/2023 | 00:20 | HH145C | URBAN | Vegetation | Grow-in - NSP responsibility | 44.00 | 225.0 | 0.015263 | 0.0000678 | No
04/12/2023 | 02:21 | MV22 | SHORT RURAL | Unknown | Unknown | 2.00 | 214.0 | 0.003011 | 0.0000141 | No
04/12/2023 | 07:33 | CBD103A | URBAN | Asset failure | LV | 2.00 | 221.0 | 0.000681 | 0.0000031 | No
04/12/2023 | 07:34 | HH386B | URBAN | Asset failure | LV | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
04/12/2023 | 08:26 | SA14 | URBAN | Planned |  | 84.00 | 20.5 | 0.002660 | 0.0001295 | No
04/12/2023 | 08:34 | SB16 | LONG RURAL | Planned |  | 36.00 | 132.0 | 0.034102 | 0.0002583 | No
04/12/2023 | 08:53 | MB15 | SHORT RURAL | Unknown | Unknown | 1.00 | 11,626.0 | 0.081795 | 0.0000070 | No
04/12/2023 | 09:00 | PL04 | URBAN | Planned |  | 9.00 | 310.6 | 0.004309 | 0.0000139 | No
04/12/2023 | 09:03 | SD45101 | LONG RURAL | Planned |  | 664.00 | 393.4 | 1.874464 | 0.0047651 | No
04/12/2023 | 10:10 | MV61 | URBAN | Third Party | Dig-in | 12.00 | 180.0 | 0.003330 | 0.0000185 | No
04/12/2023 | 11:23 | ST36 | LONG RURAL | Asset failure | HV | 9.00 | 120.0 | 0.007750 | 0.0000646 | No
04/12/2023 | 11:41 | GU43 | LONG RURAL | Planned |  | 2.00 | 172.0 | 0.002469 | 0.0000144 | No
04/12/2023 | 12:06 | HH121D | URBAN | Animal | Animal impact | 2.00 | 319.0 | 0.000984 | 0.0000031 | No
04/12/2023 | 12:17 | HH341K | URBAN | Overloads |  | 3.00 | 553.0 | 0.002558 | 0.0000046 | No
04/12/2023 | 12:34 | SM126D | URBAN | Asset failure | LV | 14.00 | 18.0 | 0.000389 | 0.0000216 | No
04/12/2023 | 12:49 | PA04 | URBAN | Unknown | Unknown | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
04/12/2023 | 14:00 | WK44 | SHORT RURAL | Asset failure | HV | 3.00 | 35.0 | 0.000739 | 0.0000211 | No
04/12/2023 | 15:25 | SD39200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
04/12/2023 | 15:25 | SD39100 | LONG RURAL | Asset failure | Subtransmission | 224.33 | 91.0 | 0.146500 | 0.0016099 | No
04/12/2023 | 15:25 | SD39100 | LONG RURAL | Planned |  | 1,466.33 | 5.0 | 0.052614 | 0.0105229 | No
04/12/2023 | 15:25 | SD39200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
04/12/2023 | 15:25 | SD39200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
04/12/2023 | 15:25 | SD39200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
04/12/2023 | 15:25 | SD39200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
04/12/2023 | 15:25 | SD39200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
04/12/2023 | 15:27 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 21.00 | 112.0 | 0.003626 | 0.0000324 | No
04/12/2023 | 15:27 | KA30 | SHORT RURAL | Unknown | Unknown | 47.00 | 160.1 | 0.052935 | 0.0003307 | No
04/12/2023 | 15:37 | EL13 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 43.33 | 128.0 | 0.008552 | 0.0000668 | No
04/12/2023 | 16:06 | BM43 | SHORT RURAL | Other |  | 13.00 | 225.0 | 0.020579 | 0.0000915 | No
04/12/2023 | 16:27 | G40 | LONG RURAL | Third Party | Vehicle impact | 18.00 | 232.0 | 0.029968 | 0.0001292 | No
04/12/2023 | 17:09 | W33 | LONG RURAL | Asset failure | HV | 34.00 | 701.6 | 0.171177 | 0.0002440 | No
04/12/2023 | 19:01 | SA16 | URBAN | Asset failure | LV | 13.00 | 97.0 | 0.001944 | 0.0000200 | No
04/12/2023 | 21:05 | SM179A | URBAN | Asset failure | LV | 157.00 | 176.3 | 0.042663 | 0.0002421 | No
04/12/2023 | 21:20 | EL02 | URBAN | Planned |  | 17.00 | 304.2 | 0.007972 | 0.0000262 | No
04/12/2023 | 22:18 | HH102C | URBAN | Asset failure | LV | 21.00 | 90.9 | 0.002943 | 0.0000324 | No
04/12/2023 | 22:20 | SM216G | URBAN | Overloads |  | 20.33 | 20.4 | 0.000639 | 0.0000313 | No
04/12/2023 | 22:51 | MV54 | SHORT RURAL | Animal | Animal impact | 1.00 | 187.0 | 0.001316 | 0.0000070 | No
05/12/2023 | 00:31 | HH409E | URBAN | Asset failure | LV | 58.00 | 60.2 | 0.005382 | 0.0000894 | No
05/12/2023 | 00:54 | ME200G | URBAN | Asset failure | LV | 63.00 | 125.0 | 0.012141 | 0.0000971 | No
05/12/2023 | 01:40 | MV53 | SHORT RURAL | Animal | Animal impact | 1.00 | 9.0 | 0.000063 | 0.0000070 | No
05/12/2023 | 02:20 | HH522A | URBAN | Asset failure | LV | 17.00 | 67.0 | 0.001756 | 0.0000262 | No
05/12/2023 | 02:56 | CL24 | LONG RURAL | Third Party | Vehicle impact | 51.00 | 174.3 | 0.063783 | 0.0003660 | No
05/12/2023 | 07:36 | MG09 | SHORT RURAL | Overloads |  | 1.00 | 99.0 | 0.000697 | 0.0000070 | No
05/12/2023 | 08:09 | MG17 | LONG RURAL | Planned |  | 754.00 | 503.8 | 2.725979 | 0.0054110 | No
05/12/2023 | 08:48 | SA20 | URBAN | Planned |  | 106.00 | 282.0 | 0.046086 | 0.0001634 | No
05/12/2023 | 08:50 | PL803C | URBAN | Planned |  | 1.00 | 284.0 | 0.000438 | 0.0000015 | No
05/12/2023 | 08:56 | SD40400 | LONG RURAL | Planned |  | 247.00 | 317.1 | 0.562122 | 0.0017726 | No
05/12/2023 | 09:46 | HH145A | URBAN | Planned |  | 73.00 | 223.0 | 0.025098 | 0.0001125 | No
05/12/2023 | 09:49 | CM35 | LONG RURAL | Planned |  | 1.00 | 112.0 | 0.000804 | 0.0000072 | No
05/12/2023 | 10:10 | HH177A | URBAN | Planned |  | 24.00 | 294.0 | 0.010879 | 0.0000370 | No
05/12/2023 | 10:29 | BT04 | LONG RURAL | Asset failure | LV | 1.00 | 259.0 | 0.001859 | 0.0000072 | No
05/12/2023 | 10:37 | ST36 | LONG RURAL | Planned |  | 46.00 | 100.0 | 0.033011 | 0.0003301 | No
05/12/2023 | 11:26 | SA14 | URBAN | Unknown | Unknown | 1.00 | 545.0 | 0.000840 | 0.0000015 | No
05/12/2023 | 12:05 | NU20 | LONG RURAL | Planned |  | 3.00 | 80.0 | 0.001722 | 0.0000215 | No
05/12/2023 | 12:14 | NL210A | URBAN | Asset failure | LV | 1.00 | 550.0 | 0.000848 | 0.0000015 | No
05/12/2023 | 12:16 | SM374E | URBAN | Other |  | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
05/12/2023 | 13:04 | YK02 | SHORT RURAL | Overloads |  | 9.33 | 91.0 | 0.005975 | 0.0000657 | No
05/12/2023 | 13:05 | PA04 | URBAN | Asset failure | LV | 2.00 | 131.0 | 0.000404 | 0.0000031 | No
05/12/2023 | 13:13 | EL09 | URBAN | Asset failure | LV | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
05/12/2023 | 13:18 | AP355A | URBAN | Overloads |  | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
05/12/2023 | 13:31 | SM349D | URBAN | Asset failure | LV | 1.00 | 569.0 | 0.000877 | 0.0000015 | No
05/12/2023 | 14:24 | R32 | LONG RURAL | Planned |  | 1.00 | 28.0 | 0.000201 | 0.0000072 | No
05/12/2023 | 15:40 | PP05 | LONG RURAL | Asset failure | LV | 2.00 | 137.0 | 0.001966 | 0.0000144 | No
05/12/2023 | 18:51 | HH177B | URBAN | Third Party | Unauthorised access | 4.00 | 70.0 | 0.000432 | 0.0000062 | No
05/12/2023 | 21:09 | HH177A | URBAN | Asset failure | HV | 24.00 | 204.0 | 0.007548 | 0.0000370 | No
05/12/2023 | 23:42 | SM350A | URBAN | Unknown | Unknown | 105.00 | 113.0 | 0.018293 | 0.0001619 | No
06/12/2023 | 00:00 | AP146C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 198.00 | 252.0 | 0.076927 | 0.0003053 | No
06/12/2023 | 02:07 | SG14 | SHORT RURAL | Animal | Animal impact | 1.00 | 147.0 | 0.001034 | 0.0000070 | No
06/12/2023 | 05:42 | SM402B | URBAN | Animal | Animal impact | 357.00 | 24.7 | 0.013600 | 0.0005504 | No
06/12/2023 | 05:42 | CM15 | LONG RURAL | Unknown | Unknown | 18.00 | 306.0 | 0.039527 | 0.0001292 | No
06/12/2023 | 05:57 | HH130B | URBAN | Unknown | Unknown | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
06/12/2023 | 08:08 | SA17 | URBAN | Asset failure | LV | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
06/12/2023 | 08:31 | CL05 | LONG RURAL | Planned |  | 20.00 | 255.0 | 0.036599 | 0.0001435 | No
06/12/2023 | 08:36 | LX21 | SHORT RURAL | Unknown | Unknown | 1.00 | 249.0 | 0.001752 | 0.0000070 | No
06/12/2023 | 08:36 | GA22 | SHORT RURAL | Planned |  | 3.00 | 105.0 | 0.002216 | 0.0000211 | No
06/12/2023 | 08:37 | PL14 | URBAN | Planned |  | 78.00 | 281.8 | 0.033888 | 0.0001203 | No
06/12/2023 | 09:18 | VH22 | SHORT RURAL | Planned |  | 38.00 | 511.0 | 0.136615 | 0.0002673 | No
06/12/2023 | 09:23 | NL21 | URBAN | Unknown | Unknown | 1.00 | 368.0 | 0.000567 | 0.0000015 | No
06/12/2023 | 09:54 | MV63 | SHORT RURAL | Planned |  | 7.00 | 447.0 | 0.022014 | 0.0000492 | No
06/12/2023 | 09:54 | HH522B | URBAN | Planned |  | 26.00 | 269.0 | 0.010783 | 0.0000401 | No
06/12/2023 | 10:03 | G02 | LONG RURAL | Planned |  | 52.00 | 245.0 | 0.091426 | 0.0003732 | No
06/12/2023 | 10:06 | SA14 | URBAN | Overloads |  | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
06/12/2023 | 10:11 | CV23 | LONG RURAL | Planned |  | 10.00 | 179.0 | 0.012846 | 0.0000718 | No
06/12/2023 | 10:15 | SG12 | SHORT RURAL | Planned |  | 12.00 | 204.0 | 0.017223 | 0.0000844 | No
06/12/2023 | 10:34 | AP829G | URBAN | Third Party | Vehicle impact | 12.00 | 96.0 | 0.001776 | 0.0000185 | No
06/12/2023 | 10:34 | CD03 | SHORT RURAL | Third Party | Vehicle impact | 12.00 | 232.0 | 0.019587 | 0.0000844 | No
06/12/2023 | 10:59 | EL01N | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | No
06/12/2023 | 11:03 | VH33 | SHORT RURAL | Overloads |  | 1.00 | 652.0 | 0.004587 | 0.0000070 | No
06/12/2023 | 11:23 | SM402B | URBAN | Animal | Animal impact | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
06/12/2023 | 11:25 | SM402C | URBAN | Animal | Animal impact | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
06/12/2023 | 11:25 | HH102B | URBAN | Asset failure | LV | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
06/12/2023 | 12:25 | AP351B | URBAN | Asset failure | LV | 2.00 | 774.0 | 0.002387 | 0.0000031 | No
06/12/2023 | 12:36 | BM56 | SHORT RURAL | Other |  | 2.00 | 264.0 | 0.003715 | 0.0000141 | No
06/12/2023 | 12:41 | HK04 | LONG RURAL | Unknown | Unknown | 9.00 | 246.0 | 0.015888 | 0.0000646 | No
06/12/2023 | 13:02 | SM411D | URBAN | Other |  | 1.00 | 158.0 | 0.000244 | 0.0000015 | No
06/12/2023 | 13:15 | HH386A | URBAN | Overloads |  | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
06/12/2023 | 13:19 | NU23 | LONG RURAL | Weather |  | 47.00 | 3.0 | 0.001012 | 0.0003373 | No
06/12/2023 | 13:47 | YK16 | LONG RURAL | Third Party | Dig-in | 3.00 | 113.0 | 0.002433 | 0.0000215 | No
06/12/2023 | 13:56 | VH15 | SHORT RURAL | Weather |  | 11.00 | 27.0 | 0.002090 | 0.0000774 | No
06/12/2023 | 14:12 | ST24 | SHORT RURAL | Planned |  | 65.00 | 52.0 | 0.023780 | 0.0004573 | No
06/12/2023 | 14:59 | SG08 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,118.0 | 0.007866 | 0.0000070 | No
06/12/2023 | 15:25 | BU02 | LONG RURAL | Weather |  | 9.00 | 47.0 | 0.003036 | 0.0000646 | No
06/12/2023 | 15:35 | SA12 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 415.00 | 91.0 | 0.058224 | 0.0006398 | No
06/12/2023 | 15:50 | SB01 | LONG RURAL | Asset failure | LV | 18.00 | 132.0 | 0.017051 | 0.0001292 | No
06/12/2023 | 15:57 | VH44 | SHORT RURAL | Weather |  | 2.67 | 99.0 | 0.001857 | 0.0000188 | No
06/12/2023 | 16:27 | SM350H | URBAN | Asset failure | LV | 21.67 | 79.0 | 0.002639 | 0.0000334 | No
06/12/2023 | 17:25 | NL21 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 109.0 | 0.000336 | 0.0000031 | No
06/12/2023 | 18:01 | NA01 | LONG RURAL | Asset failure | LV | 52.00 | 222.0 | 0.082844 | 0.0003732 | No
06/12/2023 | 18:27 | HH429B | URBAN | Asset failure | LV | 76.00 | 223.0 | 0.026130 | 0.0001172 | No
06/12/2023 | 18:38 | MG41 | URBAN | Overloads |  | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
06/12/2023 | 19:12 | AP365F | URBAN | Unknown | Unknown | 1.00 | 322.0 | 0.000496 | 0.0000015 | No
06/12/2023 | 19:13 | HH522B | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
06/12/2023 | 19:53 | NL451C | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
06/12/2023 | 19:58 | HH341H | URBAN | Asset failure | LV | 62.00 | 37.0 | 0.003537 | 0.0000956 | No
06/12/2023 | 23:10 | SM126B | URBAN | Animal | Animal impact | 385.00 | 92.0 | 0.054609 | 0.0005936 | No
07/12/2023 | 01:04 | KA32 | LONG RURAL | Asset failure | HV | 16.00 | 51.0 | 0.005856 | 0.0001148 | No
07/12/2023 | 07:03 | HH121E | URBAN | Animal | Animal impact | 4.00 | 352.0 | 0.002171 | 0.0000062 | No
07/12/2023 | 07:40 | PL04 | URBAN | Asset failure | HV | 31.00 | 309.0 | 0.014768 | 0.0000478 | No
07/12/2023 | 07:45 | SSD140 | LONG RURAL | Planned |  | 308.00 | 467.0 | 1.032215 | 0.0022103 | No
07/12/2023 | 07:45 | SSD140 | SHORT RURAL | Planned |  | 2.00 | 451.0 | 0.006346 | 0.0000141 | No
07/12/2023 | 08:12 | SA11 | URBAN | Planned |  | 409.00 | 327.4 | 0.206482 | 0.0006306 | No
07/12/2023 | 08:37 | HH145D | URBAN | Planned |  | 398.00 | 305.1 | 0.187223 | 0.0006136 | No
07/12/2023 | 08:45 | HH429C | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
07/12/2023 | 09:01 | MG46 | SHORT RURAL | Planned |  | 8.00 | 451.0 | 0.025384 | 0.0000563 | No
07/12/2023 | 09:07 | PL04 | URBAN | Unknown | Unknown | 32.00 | 337.0 | 0.016626 | 0.0000493 | No
07/12/2023 | 09:12 | CN12 | LONG RURAL | Planned |  | 37.00 | 256.0 | 0.067974 | 0.0002655 | No
07/12/2023 | 09:30 | KI21 | LONG RURAL | Planned |  | 3.00 | 127.0 | 0.002734 | 0.0000215 | No
07/12/2023 | 09:30 | HH386G | URBAN | Asset failure | LV | 1.00 | 253.0 | 0.000390 | 0.0000015 | No
07/12/2023 | 09:33 | ST35 | LONG RURAL | Planned |  | 9.00 | 262.2 | 0.016936 | 0.0000646 | No
07/12/2023 | 09:37 | CV19 | LONG RURAL | Planned |  | 49.00 | 191.0 | 0.067163 | 0.0003516 | No
07/12/2023 | 09:58 | MG27 | LONG RURAL | Unknown | Unknown | 1.00 | 267.0 | 0.001916 | 0.0000072 | No
07/12/2023 | 10:02 | CD22 | LONG RURAL | Planned |  | 10.00 | 107.0 | 0.007679 | 0.0000718 | No
07/12/2023 | 10:18 | GA36 | LONG RURAL | Planned |  | 3.00 | 81.0 | 0.001744 | 0.0000215 | No
07/12/2023 | 10:48 | MI08 | LONG RURAL | Planned |  | 8.00 | 254.0 | 0.014582 | 0.0000574 | No
07/12/2023 | 11:27 | EL18 | URBAN | Asset failure | LV | 1.00 | 302.0 | 0.000466 | 0.0000015 | No
07/12/2023 | 12:21 | LM33 | LONG RURAL | Asset failure | HV | 1.00 | 58.0 | 0.000416 | 0.0000072 | No
07/12/2023 | 12:22 | AP146E | URBAN | Unknown | Unknown | 3.00 | 123.0 | 0.000569 | 0.0000046 | No
07/12/2023 | 12:24 | VH15 | SHORT RURAL | Asset failure | HV | 7.00 | 87.0 | 0.004285 | 0.0000492 | No
07/12/2023 | 12:28 | GA25 | SHORT RURAL | Asset failure | LV | 4.33 | 113.0 | 0.003445 | 0.0000305 | No
07/12/2023 | 12:35 | MTB14 | SHORT RURAL | Asset failure | LV | 5.33 | 36.0 | 0.001351 | 0.0000375 | No
07/12/2023 | 12:40 | CBD27T | CBD | Asset failure | LV | 25.00 | 59.0 | 0.213104 | 0.0036119 | No
07/12/2023 | 14:50 | LX53 | SHORT RURAL | Unknown | Unknown | 1.00 | 406.0 | 0.002856 | 0.0000070 | No
07/12/2023 | 16:08 | W04 | LONG RURAL | Overloads |  | 1.00 | 365.0 | 0.002619 | 0.0000072 | No
07/12/2023 | 16:16 | MI18 | LONG RURAL | Asset failure | LV | 2.00 | 94.0 | 0.001349 | 0.0000144 | No
07/12/2023 | 16:43 | SD31300 | LONG RURAL | Unknown | Unknown | 1,170.00 | 141.0 | 1.183879 | 0.0083963 | No
07/12/2023 | 16:52 | SB19 | LONG RURAL | Asset failure | LV | 2.00 | 104.0 | 0.001493 | 0.0000144 | No
07/12/2023 | 16:59 | AP425D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 21.00 | 24.7 | 0.000799 | 0.0000324 | No
07/12/2023 | 17:09 | HH386F | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
07/12/2023 | 17:21 | M04 | LONG RURAL | Planned |  | 107.00 | 106.0 | 0.081394 | 0.0007679 | No
07/12/2023 | 17:26 | ST36 | LONG RURAL | Asset failure | LV | 4.00 | 95.0 | 0.002727 | 0.0000287 | No
07/12/2023 | 18:12 | HH177B | URBAN | Overloads |  | 1.00 | 289.0 | 0.000446 | 0.0000015 | No
07/12/2023 | 19:20 | G17 | LONG RURAL | Unknown | Unknown | 20.67 | 160.0 | 0.023730 | 0.0001483 | No
07/12/2023 | 19:49 | MG43 | URBAN | Asset failure | LV | 20.33 | 184.0 | 0.005768 | 0.0000313 | No
07/12/2023 | 20:37 | HH145A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
07/12/2023 | 20:53 | SM349C | URBAN | Asset failure | LV | 13.00 | 73.0 | 0.001463 | 0.0000200 | No
07/12/2023 | 21:48 | BM11 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 72.00 | 85.7 | 0.043423 | 0.0005066 | No
07/12/2023 | 22:53 | MG09 | SHORT RURAL | Animal | Animal impact | 6.00 | 92.0 | 0.003884 | 0.0000422 | No
07/12/2023 | 22:54 | G02 | LONG RURAL | Asset failure | LV | 13.00 | 115.0 | 0.010729 | 0.0000933 | No
07/12/2023 | 23:05 | MB02 | LONG RURAL | Unknown | Unknown | 1.00 | 1,326.0 | 0.009516 | 0.0000072 | No
08/12/2023 | 02:13 | HH102C | URBAN | Asset failure | LV | 47.00 | 71.0 | 0.005145 | 0.0000725 | Yes
08/12/2023 | 02:49 | R08 | LONG RURAL | Unknown | Unknown | 114.00 | 340.7 | 0.278714 | 0.0008181 | Yes
08/12/2023 | 02:59 | ME427F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 51.00 | 386.0 | 0.030351 | 0.0000786 | Yes
08/12/2023 | 05:04 | MTB11 | LONG RURAL | Unknown | Unknown | 2.00 | 12.0 | 0.000172 | 0.0000144 | Yes
08/12/2023 | 05:04 | MTB11 | SHORT RURAL | Unknown | Unknown | 2,092.00 | 46.9 | 0.690773 | 0.0147182 | Yes
08/12/2023 | 05:42 | CV23 | LONG RURAL | Weather |  | 69.00 | 575.0 | 0.284742 | 0.0004952 | Yes
08/12/2023 | 05:52 | CV02 | LONG RURAL | Weather |  | 53.00 | 323.6 | 0.123096 | 0.0003803 | Yes
08/12/2023 | 05:57 | PA25 | SHORT RURAL | Weather |  | 10.00 | 285.0 | 0.020051 | 0.0000704 | Yes
08/12/2023 | 06:28 | KA27 | LONG RURAL | Weather |  | 157.00 | 305.0 | 0.343639 | 0.0011267 | Yes
08/12/2023 | 06:35 | LX41 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 4.00 | 100.3 | 0.002821 | 0.0000281 | Yes
08/12/2023 | 06:38 | CV02 | LONG RURAL | Weather |  | 58.00 | 505.0 | 0.210195 | 0.0004162 | Yes
08/12/2023 | 06:42 | KA26 | LONG RURAL | Weather |  | 427.00 | 183.0 | 0.560766 | 0.0030643 | Yes
08/12/2023 | 06:43 | CV757A | LONG RURAL | Weather |  | 262.00 | 143.0 | 0.268868 | 0.0018802 | Yes
08/12/2023 | 06:46 | HK04 | LONG RURAL | Unknown | Unknown | 9.00 | 1,698.8 | 0.109719 | 0.0000646 | Yes
08/12/2023 | 06:51 | KA30 | SHORT RURAL | Weather |  | 70.00 | 815.0 | 0.401375 | 0.0004925 | Yes
08/12/2023 | 06:51 | KA30 | SHORT RURAL | Weather |  | 5.00 | 5,474.0 | 0.192561 | 0.0000352 | Yes
08/12/2023 | 07:22 | KA03 | LONG RURAL | Weather |  | 1,920.00 | 99.7 | 1.373894 | 0.0137786 | Yes
08/12/2023 | 07:32 | G34 | LONG RURAL | Weather |  | 72.00 | 283.0 | 0.146225 | 0.0005167 | Yes
08/12/2023 | 07:43 | VH32 | SHORT RURAL | Weather |  | 644.00 | 283.2 | 1.283006 | 0.0045309 | Yes
08/12/2023 | 07:44 | G13 | LONG RURAL | Weather |  | 102.00 | 1,771.7 | 1.296878 | 0.0007320 | Yes
08/12/2023 | 07:59 | SD31200 | LONG RURAL | Weather |  | 467.00 | 548.9 | 1.839530 | 0.0033513 | Yes
08/12/2023 | 08:08 | PP18 | LONG RURAL | Unknown | Unknown | 215.00 | 511.0 | 0.788427 | 0.0015429 | Yes
08/12/2023 | 08:31 | SSD528 | SHORT RURAL | Weather |  | 2.00 | 7,172.0 | 0.100917 | 0.0000141 | Yes
08/12/2023 | 09:06 | SD44400 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 100.0 | 0.000704 | 0.0000070 | Yes
08/12/2023 | 09:31 | NL511A | URBAN | Overloads |  | 1.00 | 132.0 | 0.000204 | 0.0000015 | Yes
08/12/2023 | 09:38 | SA20 | URBAN | Planned |  | 199.00 | 242.1 | 0.074291 | 0.0003068 | Yes
08/12/2023 | 09:39 | CV02 | LONG RURAL | Weather |  | 429.00 | 43.0 | 0.132382 | 0.0030786 | Yes
08/12/2023 | 09:43 | CV22 | LONG RURAL | Weather |  | 47.00 | 329.4 | 0.111090 | 0.0003373 | Yes
08/12/2023 | 09:49 | MT22 | LONG RURAL | Weather |  | 685.00 | 127.0 | 0.624305 | 0.0049158 | Yes
08/12/2023 | 09:51 | R10 | LONG RURAL | Unknown | Unknown | 69.00 | 455.0 | 0.225308 | 0.0004952 | Yes
08/12/2023 | 10:02 | MG46 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 249.0 | 0.001752 | 0.0000070 | Yes
08/12/2023 | 10:13 | KA17 | LONG RURAL | Weather |  | 34.00 | 385.0 | 0.093938 | 0.0002440 | Yes
08/12/2023 | 10:31 | MB72 | LONG RURAL | Planned |  | 161.00 | 93.4 | 0.107875 | 0.0011554 | Yes
08/12/2023 | 10:44 | SA19 | URBAN | Third Party | Other | 10.00 | 137.0 | 0.002112 | 0.0000154 | Yes
08/12/2023 | 10:49 | KA29 | LONG RURAL | Weather |  | 106.00 | 291.0 | 0.221361 | 0.0007607 | Yes
08/12/2023 | 10:51 | KA11 | LONG RURAL | Weather |  | 1.00 | 364.0 | 0.002612 | 0.0000072 | Yes
08/12/2023 | 10:52 | KA25 | LONG RURAL | Weather |  | 31.00 | 379.0 | 0.084315 | 0.0002225 | Yes
08/12/2023 | 10:54 | KA08 | LONG RURAL | Weather |  | 67.00 | 402.0 | 0.193287 | 0.0004808 | Yes
08/12/2023 | 10:56 | KA29 | LONG RURAL | Weather |  | 108.00 | 370.0 | 0.286766 | 0.0007750 | Yes
08/12/2023 | 11:12 | KA32 | LONG RURAL | Weather |  | 38.00 | 193.0 | 0.052631 | 0.0002727 | Yes
08/12/2023 | 11:18 | G05 | LONG RURAL | Weather |  | 621.00 | 190.6 | 0.849297 | 0.0044565 | Yes
08/12/2023 | 11:28 | G18 | LONG RURAL | Weather |  | 75.00 | 1,500.9 | 0.807832 | 0.0005382 | Yes
08/12/2023 | 11:38 | KA15 | LONG RURAL | Weather |  | 56.00 | 130.0 | 0.052244 | 0.0004019 | Yes
08/12/2023 | 11:39 | MT03 | LONG RURAL | Overloads |  | 1.00 | 62.0 | 0.000445 | 0.0000072 | Yes
08/12/2023 | 11:44 | SD31100 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 51.00 | 387.0 | 0.141639 | 0.0003660 | Yes
08/12/2023 | 11:44 | SD31100 | LONG RURAL | Unknown | Unknown | 1,828.00 | 448.4 | 5.882201 | 0.0131183 | Yes
08/12/2023 | 11:44 | G36 | LONG RURAL | Weather |  | 63.00 | 479.0 | 0.216560 | 0.0004521 | Yes
08/12/2023 | 11:44 | G36 | LONG RURAL | Weather |  | 5.00 | 5,541.0 | 0.198820 | 0.0000359 | Yes
08/12/2023 | 11:49 | VH15 | SHORT RURAL | Asset failure | LV | 1.00 | 170.0 | 0.001196 | 0.0000070 | Yes
08/12/2023 | 12:06 | NL234A | URBAN | Asset failure | LV | 41.00 | 139.0 | 0.008783 | 0.0000632 | Yes
08/12/2023 | 12:20 | ST34 | LONG RURAL | Unknown | Unknown | 539.00 | 249.0 | 0.962992 | 0.0038680 | Yes
08/12/2023 | 12:23 | SD31100 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 766.00 | 247.0 | 1.357776 | 0.0054971 | Yes
08/12/2023 | 12:33 | ST41 | LONG RURAL | Asset failure | HV | 373.00 | 361.2 | 0.966917 | 0.0026768 | Yes
08/12/2023 | 13:00 | BU01 | LONG RURAL | Overloads |  | 9.00 | 239.0 | 0.015436 | 0.0000646 | Yes
08/12/2023 | 13:08 | HH496A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,897.00 | 74.9 | 0.219076 | 0.0029247 | Yes
08/12/2023 | 13:15 | MV62 | SHORT RURAL | Asset failure | LV | 1.00 | 648.0 | 0.004559 | 0.0000070 | Yes
08/12/2023 | 13:18 | HH496E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 29.00 | 292.0 | 0.013056 | 0.0000447 | Yes
08/12/2023 | 13:24 | HH145A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 476.0 | 0.000734 | 0.0000015 | Yes
08/12/2023 | 13:53 | GA08 | LONG RURAL | Unknown | Unknown | 208.00 | 319.0 | 0.476164 | 0.0014927 | Yes
08/12/2023 | 13:59 | GA26 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 155.0 | 0.001091 | 0.0000070 | Yes
08/12/2023 | 13:59 | GA26 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,275.00 | 155.0 | 0.543661 | 0.0035075 | Yes
08/12/2023 | 14:03 | GA27 | LONG RURAL | Unknown | Unknown | 467.00 | 468.0 | 1.568430 | 0.0033513 | Yes
08/12/2023 | 14:13 | GA02 | SHORT RURAL | Unknown | Unknown | 1,747.00 | 234.3 | 2.879908 | 0.0122910 | Yes
08/12/2023 | 14:16 | GA05 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 473.00 | 368.6 | 1.226603 | 0.0033278 | Yes
08/12/2023 | 14:18 | NU05 | SHORT RURAL | Third Party | Other | 547.00 | 229.0 | 0.881287 | 0.0038484 | Yes
08/12/2023 | 14:27 | GA01 | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 2,014.00 | 134.0 | 0.416082 | 0.0031051 | Yes
08/12/2023 | 14:27 | SD37101 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 1,348.00 | 153.1 | 1.480993 | 0.0096737 | Yes
08/12/2023 | 14:27 | SD37200 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 3,047.00 | 232.6 | 5.085628 | 0.0218663 | Yes
08/12/2023 | 14:27 | SD37501 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 2,444.00 | 248.0 | 4.264886 | 0.0171947 | Yes
08/12/2023 | 14:27 | MB24 | SHORT RURAL | Unknown | Unknown | 860.00 | 205.0 | 1.240357 | 0.0060505 | Yes
08/12/2023 | 14:27 | SD52300 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 255.00 | 331.0 | 0.605718 | 0.0018300 | Yes
08/12/2023 | 14:27 | SD37402 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 1,507.00 | 320.7 | 3.468794 | 0.0108147 | Yes
08/12/2023 | 14:27 | SD37402 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 2.00 | 310.0 | 0.004362 | 0.0000141 | Yes
08/12/2023 | 14:27 | GA36 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 6.00 | 310.0 | 0.013348 | 0.0000431 | Yes
08/12/2023 | 14:34 | SD36300 | LONG RURAL | Weather |  | 1,240.00 | 73.0 | 0.649601 | 0.0088986 | Yes
08/12/2023 | 14:38 | GA800A | SHORT RURAL | Unknown | Unknown | 2.00 | 55.0 | 0.000774 | 0.0000141 | Yes
08/12/2023 | 14:54 | GA25 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 2,163.00 | 173.3 | 2.636831 | 0.0152178 | Yes
08/12/2023 | 16:06 | MV53 | SHORT RURAL | Unknown | Unknown | 281.00 | 150.0 | 0.296546 | 0.0019770 | Yes
08/12/2023 | 16:14 | R01 | LONG RURAL | Weather |  | 1.00 | 195.0 | 0.001399 | 0.0000072 | Yes
08/12/2023 | 16:38 | SG09 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 2.00 | 272.0 | 0.003827 | 0.0000141 | Yes
08/12/2023 | 17:06 | R01 | LONG RURAL | Weather |  | 7.00 | 137.0 | 0.006882 | 0.0000502 | Yes
08/12/2023 | 17:17 | R29 | LONG RURAL | Other |  | 2.00 | 1,021.0 | 0.014654 | 0.0000144 | Yes
08/12/2023 | 17:47 | NU34 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 25.00 | 1,329.0 | 0.238434 | 0.0001794 | Yes
08/12/2023 | 17:48 | CV29 | LONG RURAL | Asset failure | HV | 1.00 | 21.0 | 0.000151 | 0.0000072 | Yes
08/12/2023 | 18:11 | ME116C | URBAN | Asset failure | LV | 1.00 | 168.0 | 0.000259 | 0.0000015 | Yes
08/12/2023 | 20:02 | NL115F | URBAN | Asset failure | LV | 1.00 | 343.0 | 0.000529 | 0.0000015 | Yes
09/12/2023 | 01:53 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 177.0 | 0.000273 | 0.0000015 | No
09/12/2023 | 02:00 | SM349F | URBAN | Asset failure | LV | 8.33 | 173.6 | 0.002230 | 0.0000128 | No
09/12/2023 | 05:01 | HH145C | URBAN | Unknown | Unknown | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
09/12/2023 | 07:06 | GA10 | LONG RURAL | Unknown | Unknown | 87.00 | 117.3 | 0.073227 | 0.0006243 | No
09/12/2023 | 09:01 | AP372F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,209.00 | 30.2 | 0.056345 | 0.0018640 | No
09/12/2023 | 09:58 | SD36400 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 177.0 | 0.001270 | 0.0000072 | No
09/12/2023 | 10:24 | ST13 | SHORT RURAL | Asset failure | LV | 2.00 | 147.0 | 0.002068 | 0.0000141 | No
09/12/2023 | 11:04 | SM126D | URBAN | Asset failure | LV | 15.00 | 224.0 | 0.005180 | 0.0000231 | No
09/12/2023 | 11:24 | W18 | LONG RURAL | Weather |  | 14.00 | 401.0 | 0.040288 | 0.0001005 | No
09/12/2023 | 12:03 | NU33 | LONG RURAL | Overloads |  | 1.00 | 309.0 | 0.002217 | 0.0000072 | No
09/12/2023 | 12:03 | NU01 | SHORT RURAL | Third Party | Vehicle impact | 28.00 | 56.0 | 0.011032 | 0.0001970 | No
09/12/2023 | 12:44 | AP355A | URBAN | Asset failure | LV | 143.00 | 58.0 | 0.012787 | 0.0002205 | No
09/12/2023 | 13:07 | SM126B | URBAN | Planned |  | 166.00 | 1.0 | 0.000256 | 0.0002559 | No
09/12/2023 | 14:08 | VH72 | SHORT RURAL | Asset failure | HV | 16.00 | 402.0 | 0.045252 | 0.0001126 | No
09/12/2023 | 14:15 | HH121G | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
09/12/2023 | 14:19 | SM411F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
09/12/2023 | 14:34 | SM411F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 55.00 | 193.5 | 0.016409 | 0.0000848 | No
09/12/2023 | 14:59 | MB33 | LONG RURAL | Asset failure | HV | 50.00 | 276.1 | 0.099076 | 0.0003588 | No
09/12/2023 | 14:59 | MB33 | LONG RURAL | Asset failure | HV | 1.00 | 1,521.0 | 0.010915 | 0.0000072 | No
09/12/2023 | 15:27 | ST22 | SHORT RURAL | Asset failure | LV | 1.00 | 187.0 | 0.001316 | 0.0000070 | No
09/12/2023 | 16:08 | HK04 | LONG RURAL | Unknown | Unknown | 30.00 | 1,333.3 | 0.287046 | 0.0002153 | No
09/12/2023 | 16:58 | AP424D | URBAN | Asset failure | LV | 1.00 | 162.0 | 0.000250 | 0.0000015 | No
09/12/2023 | 17:12 | NL511B | URBAN | Asset failure | LV | 1.00 | 153.0 | 0.000236 | 0.0000015 | No
09/12/2023 | 17:17 | HH409E | URBAN | Other |  | 58.00 | 61.0 | 0.005455 | 0.0000894 | No
09/12/2023 | 17:25 | WHY10 | URBAN | Asset failure | LV | 1.00 | 216.0 | 0.000333 | 0.0000015 | No
09/12/2023 | 18:16 | MB32 | LONG RURAL | Asset failure | HV | 3.00 | 79.0 | 0.001701 | 0.0000215 | No
09/12/2023 | 18:19 | SA14 | URBAN | Overloads |  | 1.00 | 369.0 | 0.000569 | 0.0000015 | No
09/12/2023 | 19:29 | SM179D | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
09/12/2023 | 19:38 | HH428D | URBAN | Asset failure | LV | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
09/12/2023 | 21:08 | GA26 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 296.0 | 0.018711 | 0.0000632 | No
09/12/2023 | 21:26 | HH121D | URBAN | Asset failure | HV | 36.00 | 396.0 | 0.021979 | 0.0000555 | No
09/12/2023 | 22:24 | NL115A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
09/12/2023 | 22:30 | SM350B | URBAN | Asset failure | LV | 20.33 | 99.0 | 0.003104 | 0.0000313 | No
09/12/2023 | 22:35 | HH386B | URBAN | Other |  | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
09/12/2023 | 22:36 | HH121A | URBAN | Other |  | 36.00 | 254.0 | 0.014098 | 0.0000555 | No
09/12/2023 | 23:56 | SM374B | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | No
10/12/2023 | 00:27 | NL115F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
10/12/2023 | 01:07 | NL760B | URBAN | Unknown | Unknown | 45.00 | 157.0 | 0.010892 | 0.0000694 | No
10/12/2023 | 01:10 | R02 | LONG RURAL | Asset failure | LV | 1.00 | 627.0 | 0.004500 | 0.0000072 | No
10/12/2023 | 01:40 | SD56301 | URBAN | Asset failure | Subtransmission | 130.00 | 140.0 | 0.028060 | 0.0002004 | No
10/12/2023 | 03:21 | SD54101 | LONG RURAL | Asset failure | Subtransmission | 2,718.00 | 110.7 | 2.159121 | 0.0195053 | No
10/12/2023 | 03:42 | R05 | LONG RURAL | Unknown | Unknown | 30.00 | 371.0 | 0.079873 | 0.0002153 | No
10/12/2023 | 04:21 | CN27 | LONG RURAL | Asset failure | LV | 4.00 | 62.0 | 0.001780 | 0.0000287 | No
10/12/2023 | 06:09 | MV22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 26.67 | 419.0 | 0.078610 | 0.0001876 | No
10/12/2023 | 07:06 | SM137A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,268.00 | 243.1 | 0.475280 | 0.0019549 | No
10/12/2023 | 07:56 | HH386A | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
10/12/2023 | 08:42 | SM172E | URBAN | Animal | Animal impact | 3,008.00 | 116.5 | 0.540072 | 0.0046376 | No
10/12/2023 | 08:47 | SM410C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 137.00 | 298.0 | 0.062944 | 0.0002112 | No
10/12/2023 | 09:06 | GA22 | SHORT RURAL | Unknown | Unknown | 2.00 | 299.0 | 0.004207 | 0.0000141 | No
10/12/2023 | 09:13 | PL15 | LONG RURAL | Unknown | Unknown | 2.00 | 229.0 | 0.003287 | 0.0000144 | No
10/12/2023 | 09:14 | HH148A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
10/12/2023 | 09:55 | AP139B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
10/12/2023 | 10:12 | CBD366T | CBD | Overloads |  | 4.67 | 31.1 | 0.020997 | 0.0006742 | No
10/12/2023 | 11:13 | MT21 | LONG RURAL | Asset failure | LV | 1.00 | 209.0 | 0.001500 | 0.0000072 | No
10/12/2023 | 12:04 | SG14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 31.00 | 594.0 | 0.129552 | 0.0002181 | No
10/12/2023 | 12:09 | AP227A | URBAN | Overloads |  | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
10/12/2023 | 13:13 | MT06 | LONG RURAL | Asset failure | LV | 1.00 | 162.0 | 0.001163 | 0.0000072 | No
10/12/2023 | 13:34 | SD38100 | LONG RURAL | Animal | Animal impact | 11.00 | 236.0 | 0.018630 | 0.0000789 | No
10/12/2023 | 13:50 | CM28 | LONG RURAL | Asset failure | HV | 56.00 | 227.8 | 0.091563 | 0.0004019 | No
10/12/2023 | 14:24 | NU20 | LONG RURAL | Weather |  | 2.00 | 468.0 | 0.006717 | 0.0000144 | No
10/12/2023 | 14:29 | SA20 | URBAN | Asset failure | LV | 50.00 | 96.4 | 0.007434 | 0.0000771 | No
10/12/2023 | 14:30 | MV63 | SHORT RURAL | Asset failure | HV | 195.00 | 76.2 | 0.104606 | 0.0013719 | No
10/12/2023 | 14:53 | VH33 | SHORT RURAL | Asset failure | LV | 4.00 | 142.0 | 0.003996 | 0.0000281 | No
10/12/2023 | 14:55 | SD37102 | LONG RURAL | Third Party | Vehicle impact | 582.00 | 88.7 | 0.370277 | 0.0041766 | No
10/12/2023 | 15:35 | HH409A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 200.00 | 57.0 | 0.017576 | 0.0003084 | No
10/12/2023 | 15:56 | HH148A | URBAN | Asset failure | LV | 55.00 | 282.0 | 0.023913 | 0.0000848 | No
10/12/2023 | 15:59 | HH409F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 48.00 | 153.0 | 0.011323 | 0.0000740 | No
10/12/2023 | 16:00 | MV62 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 11.67 | 472.0 | 0.038742 | 0.0000821 | No
10/12/2023 | 16:01 | MV51 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 118.00 | 79.0 | 0.065550 | 0.0008302 | No
10/12/2023 | 16:03 | HH145D | URBAN | Asset failure | LV | 11.67 | 231.0 | 0.004155 | 0.0000180 | No
10/12/2023 | 16:19 | GA01 | URBAN | Overloads |  | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
10/12/2023 | 16:23 | NL111Q | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 839.00 | 52.0 | 0.067264 | 0.0012935 | No
10/12/2023 | 16:30 | HH432F | URBAN | Overloads |  | 1.00 | 325.0 | 0.000501 | 0.0000015 | No
10/12/2023 | 16:46 | HH409A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 13.00 | 152.0 | 0.003047 | 0.0000200 | No
10/12/2023 | 16:56 | SM402E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 295.0 | 0.000455 | 0.0000015 | No
10/12/2023 | 16:59 | GU12 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 33.00 | 237.0 | 0.056126 | 0.0002368 | No
10/12/2023 | 17:01 | NL451C | URBAN | Third Party | Other | 45.00 | 486.0 | 0.033718 | 0.0000694 | No
10/12/2023 | 17:08 | NL111P | URBAN | Asset failure | LV | 1.00 | 3,059.0 | 0.004716 | 0.0000015 | No
10/12/2023 | 17:14 | YK12 | LONG RURAL | Asset failure | HV | 80.00 | 197.1 | 0.113142 | 0.0005741 | No
10/12/2023 | 17:14 | YK12 | LONG RURAL | Weather |  | 1.00 | 12,540.0 | 0.089991 | 0.0000072 | No
10/12/2023 | 17:16 | NL115F | URBAN | Third Party | Other | 60.67 | 702.0 | 0.065660 | 0.0000935 | No
10/12/2023 | 17:36 | ME427E | URBAN | Overloads |  | 34.67 | 102.0 | 0.005452 | 0.0000534 | No
10/12/2023 | 17:40 | VH51 | SHORT RURAL | Asset failure | HV | 7.00 | 1,136.0 | 0.055946 | 0.0000492 | No
10/12/2023 | 17:47 | MV52 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 47.00 | 471.3 | 0.155836 | 0.0003307 | No
10/12/2023 | 17:55 | VH31 | SHORT RURAL | Asset failure | LV | 16.00 | 122.0 | 0.013733 | 0.0001126 | No
10/12/2023 | 17:58 | NL111Q | URBAN | Unknown | Unknown | 1.00 | 534.0 | 0.000823 | 0.0000015 | No
10/12/2023 | 18:00 | CBD366T | CBD | Asset failure | LV | 14.00 | 81.0 | 0.163837 | 0.0020227 | No
10/12/2023 | 18:02 | MV15 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1,147.00 | 99.0 | 0.798901 | 0.0080697 | No
10/12/2023 | 18:02 | MV15 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 21.00 | 2,893.9 | 0.427554 | 0.0001477 | No
10/12/2023 | 18:07 | HH121F | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
10/12/2023 | 18:11 | NL115D | URBAN | Asset failure | HV | 2,662.00 | 349.1 | 1.432761 | 0.0041041 | No
10/12/2023 | 18:24 | SM216C | URBAN | Unknown | Unknown | 108.00 | 301.0 | 0.050119 | 0.0001665 | No
10/12/2023 | 18:44 | MV64 | SHORT RURAL | Asset failure | LV | 17.00 | 364.0 | 0.043536 | 0.0001196 | No
10/12/2023 | 18:52 | SM350H | URBAN | Unknown | Unknown | 296.00 | 177.0 | 0.080776 | 0.0004564 | No
10/12/2023 | 18:56 | SM411D | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 366.0 | 0.000564 | 0.0000015 | No
10/12/2023 | 18:58 | MV34 | SHORT RURAL | Other |  | 66.00 | 193.0 | 0.089618 | 0.0004643 | No
10/12/2023 | 19:02 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 344.0 | 0.002420 | 0.0000070 | No
10/12/2023 | 19:06 | NL210C | URBAN | Overloads |  | 17.67 | 218.0 | 0.005938 | 0.0000272 | No
10/12/2023 | 19:14 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 764.00 | 343.0 | 0.404020 | 0.0011779 | No
10/12/2023 | 19:43 | NL210C | URBAN | Unknown | Unknown | 54.00 | 204.0 | 0.016984 | 0.0000833 | No
10/12/2023 | 19:52 | SM411A | URBAN | Vegetation | Grow-in - NSP responsibility | 28.00 | 74.0 | 0.003195 | 0.0000432 | No
10/12/2023 | 20:17 | SM137C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 54.00 | 270.0 | 0.022479 | 0.0000833 | No
10/12/2023 | 20:28 | HH522C | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
10/12/2023 | 20:37 | HH130B | URBAN | Asset failure | LV | 11.00 | 277.0 | 0.004698 | 0.0000170 | No
10/12/2023 | 20:39 | HH386D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 46.00 | 50.0 | 0.003546 | 0.0000709 | No
10/12/2023 | 21:09 | SM411B | URBAN | Asset failure | LV | 13.67 | 175.0 | 0.003687 | 0.0000211 | No
10/12/2023 | 21:10 | SM411A | URBAN | Asset failure | LV | 48.00 | 175.0 | 0.012951 | 0.0000740 | No
10/12/2023 | 21:37 | SM411B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 31.00 | 185.7 | 0.008874 | 0.0000478 | No
10/12/2023 | 21:42 | HH386D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 255.00 | 20.1 | 0.007885 | 0.0003931 | No
10/12/2023 | 22:19 | AP424F | URBAN | Asset failure | LV | 105.00 | 95.0 | 0.015379 | 0.0001619 | No
10/12/2023 | 22:54 | HH409F | URBAN | Overloads |  | 15.00 | 104.0 | 0.002405 | 0.0000231 | No
10/12/2023 | 23:00 | HH432F | URBAN | Asset failure | LV | 40.00 | 110.0 | 0.006784 | 0.0000617 | No
10/12/2023 | 23:25 | SD44200 | SHORT RURAL | Asset failure | Subtransmission | 693.00 | 581.8 | 2.836696 | 0.0048756 | No
10/12/2023 | 23:25 | LM51 | LONG RURAL | Unknown | Unknown | 104.00 | 791.0 | 0.590389 | 0.0007463 | No
10/12/2023 | 23:54 | HH341B | URBAN | Planned |  | 23.00 | 414.0 | 0.014681 | 0.0000355 | No
11/12/2023 | 00:36 | HH386B | URBAN | Asset failure | LV | 36.00 | 60.0 | 0.003330 | 0.0000555 | Yes
11/12/2023 | 00:44 | NL760B | URBAN | Weather |  | 12.00 | 151.0 | 0.002794 | 0.0000185 | Yes
11/12/2023 | 01:51 | GA745B | SHORT RURAL | Asset failure | LV | 1.00 | 87.0 | 0.000612 | 0.0000070 | Yes
11/12/2023 | 01:51 | SM411B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 49.00 | 38.0 | 0.002871 | 0.0000755 | Yes
11/12/2023 | 03:21 | HK06 | LONG RURAL | Weather |  | 6.00 | 5,475.0 | 0.235742 | 0.0000431 | Yes
11/12/2023 | 05:09 | PA22 | LONG RURAL | Weather |  | 70.00 | 427.5 | 0.214773 | 0.0005023 | Yes
11/12/2023 | 05:17 | GA16 | LONG RURAL | Weather |  | 39.00 | 286.0 | 0.080045 | 0.0002799 | Yes
11/12/2023 | 05:37 | HH341H | URBAN | Weather |  | 1,541.00 | 658.1 | 1.563624 | 0.0023758 | Yes
11/12/2023 | 05:39 | R04 | LONG RURAL | Weather |  | 5.00 | 237.0 | 0.008504 | 0.0000359 | Yes
11/12/2023 | 05:53 | HH145C | URBAN | Weather |  | 842.00 | 168.9 | 0.219217 | 0.0012982 | Yes
11/12/2023 | 06:23 | NL115C | URBAN | Unknown | Unknown | 1.00 | 1,622.0 | 0.002501 | 0.0000015 | Yes
11/12/2023 | 06:26 | HH409F | URBAN | Weather |  | 40.00 | 837.0 | 0.051618 | 0.0000617 | Yes
11/12/2023 | 06:30 | SD31100 | LONG RURAL | Weather |  | 603.00 | 1,003.1 | 4.340883 | 0.0043273 | Yes
11/12/2023 | 06:30 | SSD310 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 130.00 | 216.0 | 0.201511 | 0.0009329 | Yes
11/12/2023 | 06:30 | G32 | LONG RURAL | Weather |  | 1.00 | 5,348.0 | 0.038379 | 0.0000072 | Yes
11/12/2023 | 06:34 | AP139A | URBAN | Overloads |  | 1.00 | 1,322.0 | 0.002038 | 0.0000015 | Yes
11/12/2023 | 06:36 | SD31100 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 404.00 | 1,887.0 | 5.470861 | 0.0028992 | Yes
11/12/2023 | 06:36 | SD31100 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 215.00 | 1,888.0 | 2.913016 | 0.0015429 | Yes
11/12/2023 | 06:37 | M72 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 56.00 | 354.0 | 0.142264 | 0.0004019 | Yes
11/12/2023 | 06:44 | SM179C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,350.00 | 114.0 | 0.237276 | 0.0020814 | Yes
11/12/2023 | 06:48 | HH148A | URBAN | Unknown | Unknown | 298.00 | 221.0 | 0.101549 | 0.0004594 | Yes
11/12/2023 | 06:48 | SM350H | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,954.00 | 150.7 | 0.453886 | 0.0030126 | Yes
11/12/2023 | 06:50 | EL25 | URBAN | Unknown | Unknown | 13.00 | 660.0 | 0.013228 | 0.0000200 | Yes
11/12/2023 | 06:51 | ST51 | SHORT RURAL | Weather |  | 254.00 | 176.0 | 0.314515 | 0.0017870 | Yes
11/12/2023 | 06:51 | ST35 | LONG RURAL | Unknown | Unknown | 39.00 | 184.6 | 0.051662 | 0.0002799 | Yes
11/12/2023 | 06:54 | VH44 | SHORT RURAL | Unknown | Unknown | 326.00 | 205.0 | 0.470182 | 0.0022936 | Yes
11/12/2023 | 06:55 | SG02 | SHORT RURAL | Asset failure | LV | 1.00 | 1,815.0 | 0.012769 | 0.0000070 | Yes
11/12/2023 | 06:57 | SD54102 | LONG RURAL | Weather |  | 105.00 | 294.2 | 0.221698 | 0.0007535 | Yes
11/12/2023 | 07:16 | VH13 | SHORT RURAL | Weather |  | 29.00 | 409.0 | 0.083448 | 0.0002040 | Yes
11/12/2023 | 07:17 | HH148D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 858.00 | 55.2 | 0.072997 | 0.0013228 | Yes
11/12/2023 | 07:19 | PA15 | LONG RURAL | Weather |  | 27.00 | 1,458.7 | 0.282647 | 0.0001938 | Yes
11/12/2023 | 07:22 | BT23 | LONG RURAL | Weather |  | 1.00 | 334.0 | 0.002397 | 0.0000072 | Yes
11/12/2023 | 07:26 | HH522B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,444.00 | 697.3 | 2.627343 | 0.0037680 | Yes
11/12/2023 | 07:29 | HH341E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 86.00 | 2,441.0 | 0.323654 | 0.0001326 | Yes
11/12/2023 | 07:30 | HH118A | URBAN | Unknown | Unknown | 1,059.00 | 281.6 | 0.459845 | 0.0016327 | Yes
11/12/2023 | 07:43 | HH341K | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 928.00 | 246.5 | 0.352735 | 0.0014307 | Yes
11/12/2023 | 07:44 | SD44400 | SHORT RURAL | Asset failure | Subtransmission | 1.00 | 3,255.0 | 0.022900 | 0.0000070 | Yes
11/12/2023 | 07:49 | CL12 | LONG RURAL | Weather |  | 89.00 | 3,139.7 | 2.005289 | 0.0006387 | Yes
11/12/2023 | 07:49 | SA18 | URBAN | Weather |  | 356.00 | 114.0 | 0.062571 | 0.0005489 | Yes
11/12/2023 | 07:49 | SM350D | URBAN | Unknown | Unknown | 778.00 | 437.0 | 0.524175 | 0.0011995 | Yes
11/12/2023 | 07:51 | HH148B | URBAN | Weather |  | 830.00 | 548.8 | 0.702314 | 0.0012797 | Yes
11/12/2023 | 07:52 | SM137C | URBAN | Asset failure | LV | 7.00 | 2,418.0 | 0.026096 | 0.0000108 | Yes
11/12/2023 | 07:53 | HH341E | URBAN | Weather |  | 1,490.00 | 490.1 | 1.125921 | 0.0022972 | Yes
11/12/2023 | 07:54 | HH409D | URBAN | Asset failure | LV | 1.00 | 2,201.0 | 0.003393 | 0.0000015 | Yes
11/12/2023 | 07:56 | NA23 | LONG RURAL | Weather |  | 1.00 | 2,746.0 | 0.019706 | 0.0000072 | Yes
11/12/2023 | 07:58 | NU31 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 400.00 | 141.3 | 0.405534 | 0.0028705 | Yes
11/12/2023 | 08:01 | HH341C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 703.00 | 806.0 | 0.873585 | 0.0010839 | Yes
11/12/2023 | 08:05 | HH121E | URBAN | Unknown | Unknown | 22.00 | 1,673.0 | 0.056746 | 0.0000339 | Yes
11/12/2023 | 08:07 | SM402B | URBAN | Weather |  | 181.00 | 489.6 | 0.136630 | 0.0002791 | Yes
11/12/2023 | 08:09 | EL16 | URBAN | Asset failure | LV | 7.00 | 3,290.0 | 0.035507 | 0.0000108 | Yes
11/12/2023 | 08:11 | HH341J | URBAN | Weather |  | 1,632.00 | 577.4 | 1.452943 | 0.0025161 | Yes
11/12/2023 | 08:12 | HH409F | URBAN | Weather |  | 80.33 | 388.0 | 0.048055 | 0.0001239 | Yes
11/12/2023 | 08:13 | HH386C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,363.00 | 505.3 | 1.061945 | 0.0021014 | Yes
11/12/2023 | 08:19 | WK31 | SHORT RURAL | Animal | Animal impact | 542.00 | 195.0 | 0.743581 | 0.0038132 | Yes
11/12/2023 | 08:21 | HH130A | URBAN | Unknown | Unknown | 275.00 | 298.1 | 0.126370 | 0.0004240 | Yes
11/12/2023 | 08:26 | EL16 | URBAN | Weather |  | 319.00 | 99.1 | 0.048755 | 0.0004918 | Yes
11/12/2023 | 08:27 | MV14 | SHORT RURAL | Unknown | Unknown | 5.00 | 1,055.0 | 0.037112 | 0.0000352 | Yes
11/12/2023 | 08:31 | HH341F | URBAN | Third Party | Other | 1.00 | 2,379.0 | 0.003668 | 0.0000015 | Yes
11/12/2023 | 08:31 | KA21 | LONG RURAL | Weather |  | 77.00 | 1,458.6 | 0.806009 | 0.0005526 | Yes
11/12/2023 | 08:34 | KA14 | LONG RURAL | Weather |  | 79.00 | 1,568.5 | 0.889219 | 0.0005669 | Yes
11/12/2023 | 08:38 | HH121D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 173.00 | 718.0 | 0.191507 | 0.0002667 | Yes
11/12/2023 | 08:39 | HH130D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 2,729.0 | 0.004207 | 0.0000015 | Yes
11/12/2023 | 08:41 | SM137A | URBAN | Unknown | Unknown | 727.00 | 461.6 | 0.517399 | 0.0011209 | Yes
11/12/2023 | 08:41 | HH409F | URBAN | Unknown | Unknown | 80.00 | 1,299.0 | 0.160219 | 0.0001233 | Yes
11/12/2023 | 08:44 | HH409B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 940.00 | 171.0 | 0.247822 | 0.0014492 | Yes
11/12/2023 | 08:48 | SM216B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 616.00 | 298.0 | 0.283017 | 0.0009497 | Yes
11/12/2023 | 08:52 | HH409F | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 24.00 | 1,945.2 | 0.071977 | 0.0000370 | Yes
11/12/2023 | 08:58 | HH121C | URBAN | Unknown | Unknown | 20.00 | 1,044.0 | 0.032192 | 0.0000308 | Yes
11/12/2023 | 09:08 | MT12 | LONG RURAL | Weather |  | 62.00 | 2,142.0 | 0.953067 | 0.0004449 | Yes
11/12/2023 | 09:08 | MT12 | LONG RURAL | Weather |  | 2.00 | 4,479.0 | 0.064286 | 0.0000144 | Yes
11/12/2023 | 09:11 | NL210A | URBAN | Weather |  | 1.00 | 1,362.0 | 0.002100 | 0.0000015 | Yes
11/12/2023 | 09:12 | SG06 | SHORT RURAL | Weather |  | 3.33 | 352.0 | 0.008255 | 0.0000235 | Yes
11/12/2023 | 09:14 | PP13 | LONG RURAL | Weather |  | 70.00 | 924.1 | 0.464194 | 0.0005023 | Yes
11/12/2023 | 09:15 | SSD171 | LONG RURAL | Weather |  | 767.00 | 86.9 | 0.478446 | 0.0055042 | Yes
11/12/2023 | 09:15 | SSD171 | SHORT RURAL | Weather |  | 765.00 | 72.9 | 0.392580 | 0.0053822 | Yes
11/12/2023 | 09:15 | PP16 | SHORT RURAL | Weather |  | 73.00 | 2,473.5 | 1.270384 | 0.0005136 | Yes
11/12/2023 | 09:15 | PP16 | SHORT RURAL | Weather |  | 1.00 | 4,945.0 | 0.034791 | 0.0000070 | Yes
11/12/2023 | 09:17 | MT25 | LONG RURAL | Weather |  | 70.00 | 1,848.1 | 0.928373 | 0.0005023 | Yes
11/12/2023 | 09:17 | MT25 | LONG RURAL | Weather |  | 2.00 | 13,125.0 | 0.188379 | 0.0000144 | Yes
11/12/2023 | 09:17 | ST35 | LONG RURAL | Unknown | Unknown | 13.00 | 304.0 | 0.028361 | 0.0000933 | Yes
11/12/2023 | 09:28 | KA08 | LONG RURAL | Weather |  | 67.00 | 539.0 | 0.259159 | 0.0004808 | Yes
11/12/2023 | 09:29 | PP09 | LONG RURAL | Weather |  | 787.00 | 23.2 | 0.130796 | 0.0056478 | Yes
11/12/2023 | 09:30 | HH121E | URBAN | Weather |  | 1.00 | 3,134.0 | 0.004832 | 0.0000015 | Yes
11/12/2023 | 09:32 | MT14 | SHORT RURAL | Unknown | Unknown | 75.00 | 387.0 | 0.204205 | 0.0005277 | Yes
11/12/2023 | 09:33 | PP12 | LONG RURAL | Weather |  | 75.00 | 912.4 | 0.491091 | 0.0005382 | Yes
11/12/2023 | 09:35 | MV33 | SHORT RURAL | Weather |  | 285.00 | 29.2 | 0.058528 | 0.0020051 | Yes
11/12/2023 | 09:35 | PP04 | SHORT RURAL | Weather |  | 36.00 | 178.0 | 0.045083 | 0.0002533 | Yes
11/12/2023 | 09:36 | GA10 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 7.00 | 175.0 | 0.008791 | 0.0000502 | Yes
11/12/2023 | 09:44 | KA15 | LONG RURAL | Weather |  | 56.00 | 1,624.0 | 0.652644 | 0.0004019 | Yes
11/12/2023 | 09:49 | HH130A | URBAN | Third Party | Other | 10.00 | 1,763.0 | 0.027181 | 0.0000154 | Yes
11/12/2023 | 10:12 | R04 | LONG RURAL | Unknown | Unknown | 47.00 | 8.0 | 0.002698 | 0.0003373 | Yes
11/12/2023 | 10:15 | KA07 | LONG RURAL | Unknown | Unknown | 71.00 | 203.0 | 0.103432 | 0.0005095 | Yes
11/12/2023 | 10:54 | MV54 | SHORT RURAL | Unknown | Unknown | 127.00 | 389.0 | 0.347574 | 0.0008935 | Yes
11/12/2023 | 10:59 | KI43 | LONG RURAL | Weather |  | 1.00 | 1,606.0 | 0.011525 | 0.0000072 | Yes
11/12/2023 | 11:06 | G13 | LONG RURAL | Weather |  | 54.00 | 1,961.4 | 0.760074 | 0.0003875 | Yes
11/12/2023 | 11:06 | G13 | LONG RURAL | Weather |  | 46.00 | 3,073.3 | 1.014532 | 0.0003301 | Yes
11/12/2023 | 11:06 | G13 | LONG RURAL | Weather |  | 2.00 | 4,662.0 | 0.066912 | 0.0000144 | Yes
11/12/2023 | 11:08 | MV41 | SHORT RURAL | Weather |  | 2.00 | 1,514.0 | 0.021303 | 0.0000141 | Yes
11/12/2023 | 11:09 | KA32 | LONG RURAL | Unknown | Unknown | 38.00 | 1,737.6 | 0.473853 | 0.0002727 | Yes
11/12/2023 | 11:12 | SD36400 | LONG RURAL | Weather |  | 7.00 | 2,166.0 | 0.108808 | 0.0000502 | Yes
11/12/2023 | 11:12 | HH118D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 847.00 | 251.0 | 0.327772 | 0.0013059 | Yes
11/12/2023 | 11:13 | GA26 | URBAN | Overloads |  | 1.00 | 1,345.0 | 0.002074 | 0.0000015 | Yes
11/12/2023 | 11:14 | SSD381 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 4,454.00 | 199.0 | 6.360711 | 0.0319634 | Yes
11/12/2023 | 11:14 | SSD381 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 1.00 | 199.0 | 0.001400 | 0.0000070 | Yes
11/12/2023 | 11:16 | HH409F | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 10.67 | 1,947.8 | 0.032033 | 0.0000164 | Yes
11/12/2023 | 11:24 | NL115B | URBAN | Unknown | Unknown | 1.00 | 1,434.0 | 0.002211 | 0.0000015 | Yes
11/12/2023 | 11:29 | HH102C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,242.00 | 39.0 | 0.074679 | 0.0019149 | Yes
11/12/2023 | 11:30 | SD33200 | LONG RURAL | Weather |  | 792.00 | 368.0 | 2.091584 | 0.0056837 | Yes
11/12/2023 | 11:30 | SD33200 | LONG RURAL | Weather |  | 357.00 | 1,994.2 | 5.109159 | 0.0025619 | Yes
11/12/2023 | 11:30 | R33 | LONG RURAL | Weather |  | 29.00 | 1,878.0 | 0.390837 | 0.0002081 | Yes
11/12/2023 | 11:33 | SM349D | URBAN | Asset failure | HV | 726.00 | 511.6 | 0.572607 | 0.0011193 | Yes
11/12/2023 | 11:33 | PA23 | LONG RURAL | Unknown | Unknown | 14.00 | 2,957.0 | 0.297086 | 0.0001005 | Yes
11/12/2023 | 11:35 | R31 | LONG RURAL | Weather |  | 18.00 | 3,145.0 | 0.406252 | 0.0001292 | Yes
11/12/2023 | 11:35 | KI41 | LONG RURAL | Weather |  | 32.00 | 963.0 | 0.221146 | 0.0002296 | Yes
11/12/2023 | 11:35 | KI41 | LONG RURAL | Weather |  | 3.00 | 1,855.0 | 0.039936 | 0.0000215 | Yes
11/12/2023 | 11:35 | KI45 | LONG RURAL | Weather |  | 38.00 | 2,859.9 | 0.779902 | 0.0002727 | Yes
11/12/2023 | 11:35 | KI41 | LONG RURAL | Unknown | Unknown | 153.00 | 105.3 | 0.115618 | 0.0010980 | Yes
11/12/2023 | 11:35 | KI41 | LONG RURAL | Weather |  | 304.00 | 1,148.5 | 2.505615 | 0.0021816 | Yes
11/12/2023 | 11:35 | KI45 | LONG RURAL | Weather |  | 2.00 | 4,251.0 | 0.061013 | 0.0000144 | Yes
11/12/2023 | 11:35 | KI41 | LONG RURAL | Weather |  | 2.00 | 4,575.0 | 0.065663 | 0.0000144 | Yes
11/12/2023 | 11:35 | KI41 | LONG RURAL | Weather |  | 1.00 | 14,372.0 | 0.103138 | 0.0000072 | Yes
11/12/2023 | 11:44 | G36 | LONG RURAL | Weather |  | 63.00 | 5,633.5 | 2.546944 | 0.0004521 | Yes
11/12/2023 | 11:46 | R04 | LONG RURAL | Weather |  | 2.00 | 3,460.0 | 0.049660 | 0.0000144 | Yes
11/12/2023 | 11:51 | VH44 | SHORT RURAL | Asset failure | HV | 1.00 | 2,996.0 | 0.021078 | 0.0000070 | Yes
11/12/2023 | 11:52 | G17 | LONG RURAL | Weather |  | 72.00 | 3,007.2 | 1.553790 | 0.0005167 | Yes
11/12/2023 | 11:52 | G29 | LONG RURAL | Weather |  | 1.00 | 4,757.0 | 0.034138 | 0.0000072 | Yes
11/12/2023 | 12:08 | KA24 | LONG RURAL | Weather |  | 22.00 | 3,074.0 | 0.485321 | 0.0001579 | Yes
11/12/2023 | 12:09 | CL15 | LONG RURAL | Weather |  | 107.00 | 2,216.2 | 1.701759 | 0.0007679 | Yes
11/12/2023 | 12:16 | G32 | LONG RURAL | Weather |  | 77.00 | 3,169.4 | 1.751347 | 0.0005526 | Yes
11/12/2023 | 12:16 | G32 | LONG RURAL | Weather |  | 1.00 | 7,427.0 | 0.053299 | 0.0000072 | Yes
11/12/2023 | 12:16 | G32 | LONG RURAL | Weather |  | 14.00 | 6,087.4 | 0.611588 | 0.0001005 | Yes
11/12/2023 | 12:16 | G32 | LONG RURAL | Weather |  | 2.00 | 7,237.0 | 0.103870 | 0.0000144 | Yes
11/12/2023 | 12:18 | SM411E | URBAN | Unknown | Unknown | 1.00 | 2,079.0 | 0.003205 | 0.0000015 | Yes
11/12/2023 | 12:20 | G11 | LONG RURAL | Weather |  | 37.00 | 2,611.0 | 0.693284 | 0.0002655 | Yes
11/12/2023 | 12:22 | SG03 | SHORT RURAL | Overloads |  | 1.00 | 1,290.0 | 0.009076 | 0.0000070 | Yes
11/12/2023 | 12:31 | ST24 | SHORT RURAL | Unknown | Unknown | 65.00 | 293.0 | 0.133991 | 0.0004573 | Yes
11/12/2023 | 12:35 | HH148C | URBAN | Weather |  | 13.67 | 1,914.0 | 0.040329 | 0.0000211 | Yes
11/12/2023 | 12:40 | MT01 | LONG RURAL | Asset failure | LV | 1.00 | 3,220.0 | 0.023108 | 0.0000072 | Yes
11/12/2023 | 12:50 | NL111Q | URBAN | Asset failure | LV | 1.00 | 2,292.0 | 0.003534 | 0.0000015 | Yes
11/12/2023 | 13:04 | G15 | LONG RURAL | Weather |  | 2.00 | 3,256.0 | 0.046732 | 0.0000144 | Yes
11/12/2023 | 13:04 | G15 | LONG RURAL | Weather |  | 1.00 | 3,253.0 | 0.023345 | 0.0000072 | Yes
11/12/2023 | 13:15 | G12 | LONG RURAL | Weather |  | 63.00 | 4,176.9 | 1.888422 | 0.0004521 | Yes
11/12/2023 | 13:15 | G12 | LONG RURAL | Weather |  | 2.00 | 7,275.0 | 0.104416 | 0.0000144 | Yes
11/12/2023 | 13:15 | G12 | LONG RURAL | Weather |  | 1.00 | 7,364.0 | 0.052846 | 0.0000072 | Yes
11/12/2023 | 13:24 | G38 | LONG RURAL | Weather |  | 36.00 | 3,190.4 | 0.824245 | 0.0002583 | Yes
11/12/2023 | 13:26 | GA21 | LONG RURAL | Unknown | Unknown | 7.00 | 1,814.0 | 0.091125 | 0.0000502 | Yes
11/12/2023 | 13:32 | NU05 | SHORT RURAL | Weather |  | 1.00 | 1,360.0 | 0.009568 | 0.0000070 | Yes
11/12/2023 | 13:39 | KA29 | LONG RURAL | Weather |  | 110.00 | 236.0 | 0.186298 | 0.0007894 | Yes
11/12/2023 | 13:47 | PP14 | LONG RURAL | Weather |  | 18.00 | 1,635.0 | 0.211199 | 0.0001292 | Yes
11/12/2023 | 13:47 | HH409F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.67 | 664.0 | 0.029347 | 0.0000442 | Yes
11/12/2023 | 13:54 | G09 | LONG RURAL | Weather |  | 16.00 | 2,518.0 | 0.289120 | 0.0001148 | Yes
11/12/2023 | 13:57 | LX52 | LONG RURAL | Animal | Animal impact | 340.00 | 195.3 | 0.476609 | 0.0024400 | Yes
11/12/2023 | 14:00 | KA19 | LONG RURAL | Unknown | Unknown | 19.00 | 1,775.0 | 0.242022 | 0.0001364 | Yes
11/12/2023 | 14:02 | R26 | LONG RURAL | Weather |  | 46.00 | 993.4 | 0.327944 | 0.0003301 | Yes
11/12/2023 | 14:02 | R26 | LONG RURAL | Weather |  | 1.00 | 3,397.0 | 0.024378 | 0.0000072 | Yes
11/12/2023 | 14:07 | KA07 | LONG RURAL | Unknown | Unknown | 71.00 | 1,509.7 | 0.769216 | 0.0005095 | Yes
11/12/2023 | 14:18 | HH145D | URBAN | Asset failure | LV | 1.00 | 1,160.0 | 0.001788 | 0.0000015 | Yes
11/12/2023 | 14:20 | SSD331 | LONG RURAL | Asset failure | Zone substation | 329.00 | 1,221.8 | 2.884626 | 0.0023610 | Yes
11/12/2023 | 14:23 | CL10 | LONG RURAL | Weather |  | 82.00 | 1,596.1 | 0.939224 | 0.0005885 | Yes
11/12/2023 | 14:23 | CL10 | LONG RURAL | Weather |  | 19.00 | 469.0 | 0.063948 | 0.0001364 | Yes
11/12/2023 | 14:29 | SD34400 | LONG RURAL | Weather |  | 598.00 | 1,360.2 | 5.837104 | 0.0042914 | Yes
11/12/2023 | 14:30 | MV33 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,363.0 | 0.009589 | 0.0000070 | Yes
11/12/2023 | 14:40 | LM55 | LONG RURAL | Weather |  | 10.00 | 1,348.0 | 0.096737 | 0.0000718 | Yes
11/12/2023 | 14:42 | LM61 | LONG RURAL | Unknown | Unknown | 61.00 | 395.0 | 0.172914 | 0.0004378 | Yes
11/12/2023 | 14:43 | KA05 | LONG RURAL | Unknown | Unknown | 29.00 | 1,793.0 | 0.373148 | 0.0002081 | Yes
11/12/2023 | 14:44 | SD33100 | LONG RURAL | Weather |  | 1,012.00 | 417.9 | 3.035028 | 0.0072624 | Yes
11/12/2023 | 14:44 | G11 | LONG RURAL | Weather |  | 1.00 | 4,352.0 | 0.031231 | 0.0000072 | Yes
11/12/2023 | 14:51 | MV22 | SHORT RURAL | Weather |  | 19.00 | 175.0 | 0.023393 | 0.0001337 | Yes
11/12/2023 | 14:51 | MV22 | SHORT RURAL | Weather |  | 44.00 | 94.0 | 0.029099 | 0.0003096 | Yes
11/12/2023 | 14:52 | MV22 | SHORT RURAL | Unknown | Unknown | 34.00 | 35.0 | 0.008372 | 0.0002392 | Yes
11/12/2023 | 14:57 | G26 | LONG RURAL | Weather |  | 1.00 | 3,290.0 | 0.023610 | 0.0000072 | Yes
11/12/2023 | 14:59 | YK20 | LONG RURAL | Weather |  | 1.00 | 2,673.0 | 0.019182 | 0.0000072 | Yes
11/12/2023 | 15:04 | CL05 | LONG RURAL | Weather |  | 89.00 | 1,752.0 | 1.118991 | 0.0006387 | Yes
11/12/2023 | 15:15 | GU31 | LONG RURAL | Unknown | Unknown | 1,004.00 | 308.4 | 2.221892 | 0.0072050 | Yes
11/12/2023 | 15:18 | SD36400 | LONG RURAL | Weather |  | 36.67 | 1,842.0 | 0.484689 | 0.0002631 | Yes
11/12/2023 | 15:19 | SM172C | URBAN | Asset failure | LV | 2.00 | 1,477.0 | 0.004554 | 0.0000031 | Yes
11/12/2023 | 15:20 | NL511A | URBAN | Asset failure | HV | 1,634.00 | 231.7 | 0.583719 | 0.0025192 | Yes
11/12/2023 | 15:21 | GA27 | LONG RURAL | Weather |  | 468.00 | 266.0 | 0.893367 | 0.0033585 | Yes
11/12/2023 | 15:21 | SD37402 | LONG RURAL | Weather |  | 903.00 | 146.0 | 0.946120 | 0.0064802 | Yes
11/12/2023 | 15:27 | NL115C | URBAN | Unknown | Unknown | 81.33 | 179.0 | 0.022446 | 0.0001254 | Yes
11/12/2023 | 15:28 | EL19 | URBAN | Unknown | Unknown | 72.00 | 731.0 | 0.081146 | 0.0001110 | Yes
11/12/2023 | 15:31 | SD36400 | LONG RURAL | Unknown | Unknown | 39.00 | 2,369.1 | 0.663064 | 0.0002799 | Yes
11/12/2023 | 15:31 | SM411A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 2,038.0 | 0.003142 | 0.0000015 | Yes
11/12/2023 | 15:32 | HH121D | URBAN | Asset failure | LV | 1.00 | 1,167.0 | 0.001799 | 0.0000015 | Yes
11/12/2023 | 15:32 | AP125D | URBAN | Weather |  | 81.00 | 1,890.0 | 0.236027 | 0.0001249 | Yes
11/12/2023 | 15:32 | MTB17 | SHORT RURAL | Weather |  | 1,955.00 | 198.9 | 2.735237 | 0.0137544 | Yes
11/12/2023 | 15:33 | SD32200 | LONG RURAL | Weather |  | 1,106.00 | 1,094.0 | 8.683100 | 0.0079370 | Yes
11/12/2023 | 15:33 | G43 | LONG RURAL | Animal | Animal impact | 33.00 | 605.0 | 0.143275 | 0.0002368 | Yes
11/12/2023 | 15:35 | HH107C | URBAN | Weather |  | 695.00 | 186.7 | 0.200075 | 0.0010715 | Yes
11/12/2023 | 15:36 | HH409C | URBAN | Unknown | Unknown | 1.00 | 1,855.0 | 0.002860 | 0.0000015 | Yes
11/12/2023 | 15:37 | CL05 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 2.00 | 2,403.0 | 0.034489 | 0.0000144 | Yes
11/12/2023 | 15:38 | MT01 | LONG RURAL | Weather |  | 2.00 | 339.0 | 0.004866 | 0.0000144 | Yes
11/12/2023 | 15:39 | G17 | LONG RURAL | Weather |  | 475.00 | 1,813.0 | 6.180076 | 0.0034088 | Yes
11/12/2023 | 15:39 | G17 | LONG RURAL | Weather |  | 13.00 | 2,688.0 | 0.250770 | 0.0000933 | Yes
11/12/2023 | 15:39 | GA745B | SHORT RURAL | Weather |  | 6.00 | 1,599.0 | 0.067498 | 0.0000422 | Yes
11/12/2023 | 15:43 | NL234A | URBAN | Weather |  | 2,875.00 | 44.8 | 0.198362 | 0.0044325 | Yes
11/12/2023 | 15:44 | NL115C | URBAN | Unknown | Unknown | 43.33 | 226.0 | 0.015099 | 0.0000668 | Yes
11/12/2023 | 15:47 | EL19 | URBAN | Unknown | Unknown | 417.00 | 69.3 | 0.044546 | 0.0006429 | Yes
11/12/2023 | 15:53 | HH409F | URBAN | Asset failure | LV | 77.00 | 735.0 | 0.087256 | 0.0001187 | Yes
11/12/2023 | 16:02 | VH44 | SHORT RURAL | Animal | Animal impact | 326.00 | 1,685.0 | 3.864665 | 0.0022936 | Yes
11/12/2023 | 16:05 | HH409E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 33.00 | 1,838.0 | 0.093514 | 0.0000509 | Yes
11/12/2023 | 16:08 | KI42 | LONG RURAL | Weather |  | 71.00 | 338.0 | 0.172218 | 0.0005095 | Yes
11/12/2023 | 16:08 | SSD450 | LONG RURAL | Weather |  | 570.00 | 241.0 | 0.985985 | 0.0040905 | Yes
11/12/2023 | 16:13 | ST42 | LONG RURAL | Unknown | Unknown | 148.00 | 185.0 | 0.196488 | 0.0010621 | Yes
11/12/2023 | 16:13 | CL22 | LONG RURAL | Weather |  | 37.00 | 2,713.6 | 0.720539 | 0.0002655 | Yes
11/12/2023 | 16:15 | GU32 | LONG RURAL | Unknown | Unknown | 2.00 | 1,037.0 | 0.014884 | 0.0000144 | Yes
11/12/2023 | 16:16 | SD44302 | LONG RURAL | Weather |  | 141.00 | 1,199.5 | 1.213761 | 0.0010119 | Yes
11/12/2023 | 16:16 | HH496G | URBAN | Weather |  | 10.00 | 1,206.0 | 0.018594 | 0.0000154 | Yes
11/12/2023 | 16:17 | YK24 | LONG RURAL | Weather |  | 2.00 | 7,396.5 | 0.106159 | 0.0000144 | Yes
11/12/2023 | 16:17 | YK24 | LONG RURAL | Unknown | Unknown | 1.00 | 3,600.0 | 0.025835 | 0.0000072 | Yes
11/12/2023 | 16:18 | SD38100 | LONG RURAL | Weather |  | 211.00 | 1,380.1 | 2.089819 | 0.0015142 | Yes
11/12/2023 | 16:20 | MT14 | SHORT RURAL | Weather |  | 18.00 | 2,772.0 | 0.351043 | 0.0001266 | Yes
11/12/2023 | 16:22 | ST22 | SHORT RURAL | Unknown | Unknown | 313.00 | 266.0 | 0.585761 | 0.0022021 | Yes
11/12/2023 | 16:24 | MV15 | SHORT RURAL | Weather |  | 43.00 | 822.0 | 0.248676 | 0.0003025 | Yes
11/12/2023 | 16:24 | GA03 | LONG RURAL | Unknown | Unknown | 8.00 | 1,200.0 | 0.068893 | 0.0000574 | Yes
11/12/2023 | 16:25 | ST44 | LONG RURAL | Unknown | Unknown | 117.00 | 249.0 | 0.209068 | 0.0008396 | Yes
11/12/2023 | 16:27 | BT08 | LONG RURAL | Weather |  | 59.00 | 315.0 | 0.133372 | 0.0004234 | Yes
11/12/2023 | 16:28 | ST51 | SHORT RURAL | Unknown | Unknown | 254.00 | 219.0 | 0.391356 | 0.0017870 | Yes
11/12/2023 | 16:30 | BU05 | LONG RURAL | Unknown | Unknown | 24.00 | 2,864.0 | 0.493272 | 0.0001722 | Yes
11/12/2023 | 16:33 | SD36400 | LONG RURAL | Unknown | Unknown | 13.00 | 2,476.2 | 0.231013 | 0.0000933 | Yes
11/12/2023 | 16:34 | VH32 | SHORT RURAL | Asset failure | LV | 1.00 | 1,549.0 | 0.010898 | 0.0000070 | Yes
11/12/2023 | 16:44 | MTB41 | SHORT RURAL | Unknown | Unknown | 45.00 | 259.0 | 0.081999 | 0.0003166 | Yes
11/12/2023 | 16:50 | R34 | SHORT RURAL | Weather |  | 14.00 | 1,577.0 | 0.155330 | 0.0000985 | Yes
11/12/2023 | 16:54 | SG14 | SHORT RURAL | Weather |  | 3.00 | 960.0 | 0.020262 | 0.0000211 | Yes
11/12/2023 | 16:57 | GU31 | LONG RURAL | Weather |  | 146.00 | 231.0 | 0.242029 | 0.0010477 | Yes
11/12/2023 | 17:00 | CL05 | LONG RURAL | Unknown | Unknown | 16.33 | 2,771.0 | 0.324798 | 0.0001172 | Yes
11/12/2023 | 17:01 | VH32 | SHORT RURAL | Unknown | Unknown | 24.00 | 1,099.0 | 0.185568 | 0.0001689 | Yes
11/12/2023 | 17:01 | NL115F | URBAN | Asset failure | LV | 1.00 | 1,778.0 | 0.002741 | 0.0000015 | Yes
11/12/2023 | 17:05 | GA02 | SHORT RURAL | Weather |  | 515.00 | 211.5 | 0.766165 | 0.0036233 | Yes
11/12/2023 | 17:06 | NU14 | LONG RURAL | Unknown | Unknown | 257.00 | 994.0 | 1.833251 | 0.0018443 | Yes
11/12/2023 | 17:08 | MV33 | SHORT RURAL | Unknown | Unknown | 5.00 | 1,292.0 | 0.045449 | 0.0000352 | Yes
11/12/2023 | 17:15 | HH409A | URBAN | Unknown | Unknown | 1.00 | 1,033.0 | 0.001593 | 0.0000015 | Yes
11/12/2023 | 17:20 | MTB11 | SHORT RURAL | Weather |  | 1.00 | 1,139.0 | 0.008013 | 0.0000070 | Yes
11/12/2023 | 17:22 | NU02 | LONG RURAL | Weather |  | 3.00 | 1,829.0 | 0.039377 | 0.0000215 | Yes
11/12/2023 | 17:23 | MTB53 | LONG RURAL | Weather |  | 6.00 | 1,030.0 | 0.044350 | 0.0000431 | Yes
11/12/2023 | 17:23 | SD40400 | LONG RURAL | Weather |  | 130.00 | 293.6 | 0.273921 | 0.0009329 | Yes
11/12/2023 | 17:24 | SD34201 | SHORT RURAL | Weather |  | 418.00 | 445.2 | 1.309263 | 0.0029408 | Yes
11/12/2023 | 17:24 | SD39100 | LONG RURAL | Weather |  | 107.00 | 1,131.0 | 0.868458 | 0.0007679 | Yes
11/12/2023 | 17:24 | M04 | LONG RURAL | Weather |  | 1.00 | 2,719.0 | 0.019512 | 0.0000072 | Yes
11/12/2023 | 17:28 | BU08 | LONG RURAL | Weather |  | 48.00 | 4,126.8 | 1.421545 | 0.0003445 | Yes
11/12/2023 | 17:30 | SD37501 | SHORT RURAL | Weather |  | 1.00 | 2,832.0 | 0.019925 | 0.0000070 | Yes
11/12/2023 | 17:30 | M41 | LONG RURAL | Weather |  | 363.00 | 1,031.0 | 2.685763 | 0.0026050 | Yes
11/12/2023 | 17:31 | BM44 | SHORT RURAL | Weather |  | 487.00 | 242.8 | 0.831862 | 0.0034263 | Yes
11/12/2023 | 17:33 | SG09 | SHORT RURAL | Weather |  | 1.00 | 1,267.0 | 0.008914 | 0.0000070 | Yes
11/12/2023 | 17:34 | G24 | LONG RURAL | Weather |  | 1.00 | 4,262.0 | 0.030586 | 0.0000072 | Yes
11/12/2023 | 17:34 | VH34 | SHORT RURAL | Unknown | Unknown | 216.00 | 120.9 | 0.183732 | 0.0015197 | Yes
11/12/2023 | 17:35 | LM14 | LONG RURAL | Weather |  | 105.00 | 1,250.0 | 0.941893 | 0.0007535 | Yes
11/12/2023 | 17:43 | GU34 | LONG RURAL | Weather |  | 93.00 | 1,078.0 | 0.719456 | 0.0006674 | Yes
11/12/2023 | 17:44 | ST23 | SHORT RURAL | Unknown | Unknown | 178.00 | 250.0 | 0.313079 | 0.0012523 | Yes
11/12/2023 | 17:48 | BM55 | SHORT RURAL | Weather |  | 6.00 | 536.0 | 0.022626 | 0.0000422 | Yes
11/12/2023 | 17:53 | GU23 | LONG RURAL | Weather |  | 66.00 | 1,218.0 | 0.576891 | 0.0004736 | Yes
11/12/2023 | 17:55 | HH341D | URBAN | Unknown | Unknown | 1.00 | 1,091.0 | 0.001682 | 0.0000015 | Yes
11/12/2023 | 17:56 | GU32 | LONG RURAL | Unknown | Unknown | 978.00 | 483.8 | 3.395244 | 0.0070185 | Yes
11/12/2023 | 17:56 | GA03 | LONG RURAL | Weather |  | 2.00 | 1,535.0 | 0.022031 | 0.0000144 | Yes
11/12/2023 | 17:58 | GU41 | LONG RURAL | Weather |  | 1.00 | 1,255.0 | 0.009006 | 0.0000072 | Yes
11/12/2023 | 17:59 | AP149B | URBAN | Other |  | 1,482.00 | 5.0 | 0.011424 | 0.0022849 | Yes
11/12/2023 | 18:16 | SD38100 | LONG RURAL | Unknown | Unknown | 11.67 | 568.0 | 0.047555 | 0.0000837 | Yes
11/12/2023 | 18:19 | KI52 | LONG RURAL | Weather |  | 80.00 | 1,024.0 | 0.587885 | 0.0005741 | Yes
11/12/2023 | 18:20 | ST21 | SHORT RURAL | Unknown | Unknown | 3.00 | 1,421.0 | 0.029992 | 0.0000211 | Yes
11/12/2023 | 18:25 | AP132B | URBAN | Weather |  | 17.00 | 994.0 | 0.026053 | 0.0000262 | Yes
11/12/2023 | 18:28 | CN42 | LONG RURAL | Unknown | Unknown | 31.00 | 322.0 | 0.071634 | 0.0002225 | Yes
11/12/2023 | 18:35 | VH16 | SHORT RURAL | Weather |  | 117.00 | 1,143.0 | 0.940863 | 0.0008232 | Yes
11/12/2023 | 18:37 | EL11 | URBAN | Weather |  | 1,963.00 | 243.8 | 0.737880 | 0.0030265 | Yes
11/12/2023 | 18:40 | SD38100 | LONG RURAL | Weather |  | 1.00 | 1,652.0 | 0.011855 | 0.0000072 | Yes
11/12/2023 | 18:41 | HH409F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 95.00 | 1,196.0 | 0.175174 | 0.0001465 | Yes
11/12/2023 | 18:42 | CN43 | LONG RURAL | Animal | Animal impact | 4.00 | 1,204.5 | 0.034576 | 0.0000287 | Yes
11/12/2023 | 18:42 | VH18 | SHORT RURAL | Unknown | Unknown | 5.00 | 1,397.0 | 0.049143 | 0.0000352 | Yes
11/12/2023 | 18:42 | PA08 | LONG RURAL | Asset failure | LV | 1.00 | 978.0 | 0.007018 | 0.0000072 | Yes
11/12/2023 | 18:45 | KA08 | LONG RURAL | Weather |  | 1.00 | 2,929.0 | 0.021019 | 0.0000072 | Yes
11/12/2023 | 18:59 | M21 | LONG RURAL | Weather |  | 89.00 | 951.0 | 0.607397 | 0.0006387 | Yes
11/12/2023 | 19:03 | SD31300 | LONG RURAL | Weather |  | 2.00 | 3,989.0 | 0.057253 | 0.0000144 | Yes
11/12/2023 | 19:04 | SG09 | SHORT RURAL | Weather |  | 1.00 | 1,193.0 | 0.008393 | 0.0000070 | Yes
11/12/2023 | 19:08 | GU15 | LONG RURAL | Weather |  | 1.00 | 1,171.0 | 0.008403 | 0.0000072 | Yes
11/12/2023 | 19:11 | EL19 | URBAN | Weather |  | 1.00 | 1,830.0 | 0.002821 | 0.0000015 | Yes
11/12/2023 | 19:18 | LX41 | SHORT RURAL | Unknown | Unknown | 29.33 | 320.0 | 0.066040 | 0.0002064 | Yes
11/12/2023 | 19:33 | LC04 | LONG RURAL | Weather |  | 1.00 | 2,898.0 | 0.020797 | 0.0000072 | Yes
11/12/2023 | 19:36 | YK22 | SHORT RURAL | Unknown | Unknown | 82.00 | 179.0 | 0.103267 | 0.0005769 | Yes
11/12/2023 | 19:36 | SSD282 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 76.00 | 29.9 | 0.016305 | 0.0005454 | Yes
11/12/2023 | 19:36 | SSD282 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 769.00 | 181.6 | 0.982760 | 0.0054103 | Yes
11/12/2023 | 19:38 | SD32302 | LONG RURAL | Weather |  | 4.00 | 3,076.0 | 0.088298 | 0.0000287 | Yes
11/12/2023 | 19:55 | AP355H | URBAN | Weather |  | 30.00 | 4.0 | 0.000185 | 0.0000463 | Yes
11/12/2023 | 19:58 | AP125D | URBAN | Weather |  | 1.00 | 1,607.0 | 0.002478 | 0.0000015 | Yes
11/12/2023 | 20:03 | MB62 | LONG RURAL | Unknown | Unknown | 1.00 | 221.0 | 0.001586 | 0.0000072 | Yes
11/12/2023 | 20:05 | SD38200 | LONG RURAL | Weather |  | 1.00 | 1,385.0 | 0.009939 | 0.0000072 | Yes
11/12/2023 | 20:11 | ST51 | SHORT RURAL | Unknown | Unknown | 92.00 | 296.0 | 0.191590 | 0.0006473 | Yes
11/12/2023 | 20:11 | ST51 | SHORT RURAL | Weather |  | 254.00 | 804.3 | 1.437259 | 0.0017870 | Yes
11/12/2023 | 20:14 | HH145A | URBAN | Unknown | Unknown | 1.00 | 1,615.0 | 0.002490 | 0.0000015 | Yes
11/12/2023 | 20:22 | HH107B | URBAN | Unknown | Unknown | 177.00 | 136.2 | 0.037155 | 0.0002729 | Yes
11/12/2023 | 20:23 | MV41 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,157.0 | 0.008140 | 0.0000070 | Yes
11/12/2023 | 20:27 | HH341H | URBAN | Asset failure | LV | 1.00 | 1,177.0 | 0.001815 | 0.0000015 | Yes
11/12/2023 | 20:30 | SA711C | URBAN | Asset failure | LV | 44.00 | 496.0 | 0.033647 | 0.0000678 | Yes
11/12/2023 | 20:31 | MB123 | LONG RURAL | Unknown | Unknown | 76.00 | 336.0 | 0.183255 | 0.0005454 | Yes
11/12/2023 | 20:32 | SD40200 | LONG RURAL | Weather |  | 1.00 | 1,422.0 | 0.010205 | 0.0000072 | Yes
11/12/2023 | 20:35 | HH341A | URBAN | Unknown | Unknown | 1.00 | 853.0 | 0.001315 | 0.0000015 | Yes
11/12/2023 | 20:38 | SD32200 | LONG RURAL | Weather |  | 3.00 | 5,512.0 | 0.118668 | 0.0000215 | Yes
11/12/2023 | 20:39 | HH177D | URBAN | Asset failure | LV | 1.00 | 1,287.0 | 0.001984 | 0.0000015 | Yes
11/12/2023 | 20:46 | SD34300 | SHORT RURAL | Unknown | Unknown | 103.00 | 818.0 | 0.592768 | 0.0007247 | Yes
11/12/2023 | 20:48 | PL33 | LONG RURAL | Asset failure | HV | 1,450.00 | 138.6 | 1.441760 | 0.0104057 | Yes
11/12/2023 | 20:57 | VH72 | SHORT RURAL | Weather |  | 123.00 | 1,119.0 | 0.968344 | 0.0008654 | Yes
11/12/2023 | 20:58 | CN53 | LONG RURAL | Weather |  | 105.00 | 1,018.0 | 0.767099 | 0.0007535 | Yes
11/12/2023 | 20:58 | CN53 | LONG RURAL | Weather |  | 2.00 | 2,664.0 | 0.038235 | 0.0000144 | Yes
11/12/2023 | 21:02 | CN52 | LONG RURAL | Weather |  | 85.00 | 900.5 | 0.549305 | 0.0006100 | Yes
11/12/2023 | 21:29 | SD44302 | LONG RURAL | Unknown | Unknown | 363.00 | 21.0 | 0.054705 | 0.0026050 | Yes
11/12/2023 | 21:52 | SD32302 | LONG RURAL | Weather |  | 3.00 | 1,992.3 | 0.042893 | 0.0000215 | Yes
11/12/2023 | 21:59 | SA17 | URBAN | Overloads |  | 1.00 | 799.0 | 0.001232 | 0.0000015 | Yes
11/12/2023 | 22:03 | EL20 | URBAN | Overloads |  | 1,218.00 | 231.5 | 0.434705 | 0.0018779 | Yes
11/12/2023 | 22:17 | SD32400 | LONG RURAL | Weather |  | 163.00 | 608.9 | 0.712258 | 0.0011697 | Yes
11/12/2023 | 22:17 | PP09 | LONG RURAL | Weather |  | 1.00 | 6,592.0 | 0.047306 | 0.0000072 | Yes
11/12/2023 | 22:17 | PP09 | LONG RURAL | Weather |  | 1.00 | 6,471.0 | 0.046438 | 0.0000072 | Yes
11/12/2023 | 22:37 | MB03 | LONG RURAL | Weather |  | 93.00 | 1,111.0 | 0.741494 | 0.0006674 | Yes
11/12/2023 | 22:37 | MB03 | LONG RURAL | Weather |  | 1.00 | 2,732.0 | 0.019606 | 0.0000072 | Yes
11/12/2023 | 22:46 | HH341J | URBAN | Unknown | Unknown | 1.00 | 351.0 | 0.000541 | 0.0000015 | Yes
11/12/2023 | 22:57 | NL115A | URBAN | Asset failure | LV | 24.00 | 438.0 | 0.016208 | 0.0000370 | Yes
11/12/2023 | 23:02 | EL03 | URBAN | Unknown | Unknown | 1.00 | 642.0 | 0.000990 | 0.0000015 | Yes
11/12/2023 | 23:11 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 214.00 | 611.4 | 0.920552 | 0.0015056 | Yes
11/12/2023 | 23:16 | GU31 | LONG RURAL | Unknown | Unknown | 1.00 | 723.0 | 0.005188 | 0.0000072 | Yes
11/12/2023 | 23:17 | G20 | LONG RURAL | Weather |  | 49.00 | 2,886.7 | 1.015092 | 0.0003516 | Yes
11/12/2023 | 23:17 | SD31300 | LONG RURAL | Weather |  | 310.00 | 1,250.3 | 2.781438 | 0.0022247 | Yes
11/12/2023 | 23:17 | G10 | LONG RURAL | Weather |  | 29.00 | 1,326.8 | 0.276124 | 0.0002081 | Yes
11/12/2023 | 23:17 | G20 | LONG RURAL | Weather |  | 1.00 | 5,610.0 | 0.040259 | 0.0000072 | Yes
11/12/2023 | 23:17 | G20 | LONG RURAL | Weather |  | 2.00 | 5,405.0 | 0.077576 | 0.0000144 | Yes
11/12/2023 | 23:49 | CBD366P | CBD | Planned |  | 1.00 | 276.0 | 0.039876 | 0.0001445 | Yes
12/12/2023 | 00:01 | GU36 | LONG RURAL | Weather |  | 56.00 | 288.7 | 0.116027 | 0.0004019 | No
12/12/2023 | 00:01 | GU36 | LONG RURAL | Weather |  | 2.00 | 1,548.0 | 0.022218 | 0.0000144 | No
12/12/2023 | 00:01 | R29 | LONG RURAL | Weather |  | 81.00 | 1,407.0 | 0.817865 | 0.0005813 | No
12/12/2023 | 00:01 | R29 | LONG RURAL | Weather |  | 1.00 | 2,606.0 | 0.018702 | 0.0000072 | No
12/12/2023 | 00:25 | KA08 | LONG RURAL | Weather |  | 66.00 | 1,017.0 | 0.481690 | 0.0004736 | No
12/12/2023 | 00:50 | MI20 | LONG RURAL | Weather |  | 18.00 | 406.0 | 0.052445 | 0.0001292 | No
12/12/2023 | 01:13 | G31 | LONG RURAL | Weather |  | 1.00 | 4,146.0 | 0.029753 | 0.0000072 | No
12/12/2023 | 01:23 | MT14 | SHORT RURAL | Weather |  | 57.00 | 698.0 | 0.279914 | 0.0004010 | No
12/12/2023 | 01:25 | SSD457 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 6,996.00 | 47.7 | 2.395423 | 0.0502056 | No
12/12/2023 | 01:25 | SSD457 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 3,321.00 | 40.0 | 0.933757 | 0.0233649 | No
12/12/2023 | 01:57 | MT09 | LONG RURAL | Weather |  | 1.00 | 1,998.0 | 0.014338 | 0.0000072 | No
12/12/2023 | 02:07 | SD31200 | LONG RURAL | Weather |  | 84.00 | 2,474.5 | 1.491686 | 0.0006028 | No
12/12/2023 | 02:30 | YK05 | LONG RURAL | Weather |  | 1.00 | 2,627.0 | 0.018852 | 0.0000072 | No
12/12/2023 | 02:38 | NL511B | URBAN | Weather |  | 69.00 | 209.0 | 0.022234 | 0.0001064 | No
12/12/2023 | 03:22 | KA05 | LONG RURAL | Weather |  | 1,067.00 | 101.0 | 0.773372 | 0.0076571 | No
12/12/2023 | 04:05 | SD38100 | LONG RURAL | Weather |  | 3.33 | 18.0 | 0.000431 | 0.0000239 | No
12/12/2023 | 04:45 | LX31 | SHORT RURAL | Weather |  | 96.00 | 559.1 | 0.377623 | 0.0006754 | No
12/12/2023 | 05:00 | G09 | LONG RURAL | Weather |  | 2.00 | 2,407.0 | 0.034547 | 0.0000144 | No
12/12/2023 | 05:12 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 1,841.0 | 0.025905 | 0.0000141 | No
12/12/2023 | 05:34 | HH341E | URBAN | Weather |  | 31.00 | 839.0 | 0.040099 | 0.0000478 | No
12/12/2023 | 06:03 | EL25 | URBAN | Weather |  | 13.00 | 526.0 | 0.010543 | 0.0000200 | No
12/12/2023 | 06:14 | VH22 | SHORT RURAL | Unknown | Unknown | 387.00 | 35.8 | 0.097512 | 0.0027227 | No
12/12/2023 | 06:18 | VH23 | SHORT RURAL | Unknown | Unknown | 22.67 | 597.0 | 0.095204 | 0.0001595 | No
12/12/2023 | 06:34 | KI43 | LONG RURAL | Weather |  | 39.00 | 319.0 | 0.089281 | 0.0002799 | No
12/12/2023 | 06:36 | SD44200 | SHORT RURAL | Weather |  | 694.00 | 60.2 | 0.294055 | 0.0048826 | No
12/12/2023 | 06:37 | HH148C | URBAN | Asset failure | LV | 1.00 | 957.0 | 0.001475 | 0.0000015 | No
12/12/2023 | 06:50 | HH341E | URBAN | Weather |  | 45.00 | 485.0 | 0.033649 | 0.0000694 | No
12/12/2023 | 06:53 | SD58200 | LONG RURAL | Weather |  | 1,757.00 | 172.0 | 2.168716 | 0.0126088 | No
12/12/2023 | 06:53 | SD46400 | SHORT RURAL | Weather |  | 24.00 | 306.0 | 0.051669 | 0.0001689 | No
12/12/2023 | 07:01 | GA25 | SHORT RURAL | Asset failure | LV | 2.00 | 212.0 | 0.002983 | 0.0000141 | No
12/12/2023 | 07:08 | MV51 | SHORT RURAL | Unknown | Unknown | 7.00 | 259.0 | 0.012755 | 0.0000492 | No
12/12/2023 | 07:13 | MI28 | LONG RURAL | Weather |  | 50.00 | 155.0 | 0.055617 | 0.0003588 | No
12/12/2023 | 07:17 | GU31 | LONG RURAL | Weather |  | 2.00 | 1,276.0 | 0.018314 | 0.0000144 | No
12/12/2023 | 07:18 | LX41 | SHORT RURAL | Weather |  | 330.00 | 6.5 | 0.015070 | 0.0023217 | No
12/12/2023 | 07:32 | LX41 | SHORT RURAL | Weather |  | 1.00 | 211.0 | 0.001484 | 0.0000070 | No
12/12/2023 | 07:40 | ME231E | URBAN | Overloads |  | 4.67 | 101.0 | 0.000727 | 0.0000072 | No
12/12/2023 | 07:42 | SM172A | URBAN | Overloads |  | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
12/12/2023 | 07:42 | HH107B | URBAN | Asset failure | LV | 1.00 | 901.0 | 0.001389 | 0.0000015 | No
12/12/2023 | 07:44 | SD49900 | URBAN | Weather |  | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
12/12/2023 | 07:49 | MI32 | LONG RURAL | Weather |  | 44.00 | 127.5 | 0.040252 | 0.0003158 | No
12/12/2023 | 07:52 | AP214B | URBAN | Overloads |  | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
12/12/2023 | 07:58 | YK23 | LONG RURAL | Unknown | Unknown | 1.00 | 1,542.0 | 0.011066 | 0.0000072 | No
12/12/2023 | 07:59 | CL05 | LONG RURAL | Weather |  | 2.00 | 757.0 | 0.010865 | 0.0000144 | No
12/12/2023 | 08:00 | MI02 | SHORT RURAL | Weather |  | 3.00 | 474.0 | 0.010004 | 0.0000211 | No
12/12/2023 | 08:05 | SD39100 | LONG RURAL | Weather |  | 2,064.00 | 108.9 | 1.613296 | 0.0148119 | No
12/12/2023 | 08:10 | MI02 | SHORT RURAL | Weather |  | 5.00 | 355.0 | 0.012488 | 0.0000352 | No
12/12/2023 | 08:22 | BU11 | SHORT RURAL | Planned |  | 26.00 | 2.0 | 0.000366 | 0.0001829 | No
12/12/2023 | 08:22 | M21 | LONG RURAL | Weather |  | 1.00 | 2,133.0 | 0.015307 | 0.0000072 | No
12/12/2023 | 08:22 | ST14 | SHORT RURAL | Weather |  | 19.00 | 303.7 | 0.040595 | 0.0001337 | No
12/12/2023 | 08:22 | ST14 | SHORT RURAL | Weather |  | 3.00 | 862.7 | 0.018208 | 0.0000211 | No
12/12/2023 | 08:36 | MI20 | LONG RURAL | Weather |  | 101.00 | 207.3 | 0.150229 | 0.0007248 | No
12/12/2023 | 08:53 | SM349H | URBAN | Weather |  | 1.00 | 544.0 | 0.000839 | 0.0000015 | No
12/12/2023 | 08:54 | SG02 | SHORT RURAL | Third Party | Other | 18.00 | 308.0 | 0.039005 | 0.0001266 | No
12/12/2023 | 08:56 | LX21 | SHORT RURAL | Planned |  | 92.00 | 323.0 | 0.209067 | 0.0006473 | No
12/12/2023 | 09:06 | HH386D | URBAN | Asset failure | LV | 1.00 | 541.0 | 0.000834 | 0.0000015 | No
12/12/2023 | 09:12 | LC01 | SHORT RURAL | Weather |  | 2.00 | 1,747.0 | 0.024582 | 0.0000141 | No
12/12/2023 | 09:23 | HH386F | URBAN | Unknown | Unknown | 67.00 | 503.0 | 0.051959 | 0.0001033 | No
12/12/2023 | 09:24 | ST24 | SHORT RURAL | Overloads |  | 1.00 | 869.0 | 0.006114 | 0.0000070 | No
12/12/2023 | 09:31 | HH107C | URBAN | Asset failure | LV | 45.00 | 789.0 | 0.054740 | 0.0000694 | No
12/12/2023 | 09:31 | AP227D | URBAN | Asset failure | LV | 2.00 | 189.0 | 0.000583 | 0.0000031 | No
12/12/2023 | 09:40 | HH130E | URBAN | Unknown | Unknown | 1.00 | 553.0 | 0.000853 | 0.0000015 | No
12/12/2023 | 09:42 | MB92 | LONG RURAL | Weather |  | 255.00 | 14.0 | 0.025619 | 0.0018300 | No
12/12/2023 | 09:42 | MB92 | LONG RURAL | Weather |  | 259.00 | 47.6 | 0.088470 | 0.0018587 | No
12/12/2023 | 09:46 | PL07 | URBAN | Third Party | Vehicle impact | 10.00 | 140.0 | 0.002158 | 0.0000154 | No
12/12/2023 | 09:51 | HH148C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,071.0 | 0.001651 | 0.0000015 | No
12/12/2023 | 10:06 | PP08 | LONG RURAL | Unknown | Unknown | 2.00 | 3,536.0 | 0.050751 | 0.0000144 | No
12/12/2023 | 10:09 | GA41 | LONG RURAL | Weather |  | 51.00 | 630.0 | 0.230575 | 0.0003660 | No
12/12/2023 | 10:14 | R26 | LONG RURAL | Weather |  | 41.00 | 668.9 | 0.196804 | 0.0002942 | No
12/12/2023 | 10:19 | CD15 | LONG RURAL | Planned |  | 11.00 | 228.0 | 0.017998 | 0.0000789 | No
12/12/2023 | 10:19 | SD35100 | LONG RURAL | Unknown | Unknown | 2.00 | 561.0 | 0.008052 | 0.0000144 | No
12/12/2023 | 10:21 | GA18 | LONG RURAL | Weather |  | 59.00 | 390.4 | 0.165300 | 0.0004234 | No
12/12/2023 | 10:24 | AP424F | URBAN | Planned |  | 125.00 | 129.9 | 0.025037 | 0.0001927 | No
12/12/2023 | 10:45 | GU32 | LONG RURAL | Weather |  | 7.00 | 1,617.7 | 0.081265 | 0.0000502 | No
12/12/2023 | 10:46 | CM16 | LONG RURAL | Planned |  | 5.00 | 61.6 | 0.002210 | 0.0000359 | No
12/12/2023 | 10:57 | HH130E | URBAN | Asset failure | LV | 1.00 | 396.0 | 0.000611 | 0.0000015 | No
12/12/2023 | 11:01 | SD34300 | SHORT RURAL | Weather |  | 518.00 | 120.0 | 0.437326 | 0.0036444 | No
12/12/2023 | 11:01 | SD34400 | LONG RURAL | Weather |  | 1.00 | 48.0 | 0.000344 | 0.0000072 | No
12/12/2023 | 11:11 | MB01 | LONG RURAL | Third Party | Vehicle impact | 3.00 | 1,869.0 | 0.040238 | 0.0000215 | No
12/12/2023 | 11:24 | NL760B | URBAN | Unknown | Unknown | 1.00 | 852.0 | 0.001314 | 0.0000015 | No
12/12/2023 | 11:48 | R32 | LONG RURAL | Unknown | Unknown | 78.00 | 1,648.0 | 0.922474 | 0.0005598 | No
12/12/2023 | 11:54 | BM42 | SHORT RURAL | Weather |  | 2.00 | 273.0 | 0.003841 | 0.0000141 | No
12/12/2023 | 12:03 | ST23 | SHORT RURAL | Unknown | Unknown | 8.00 | 545.0 | 0.030675 | 0.0000563 | No
12/12/2023 | 12:05 | SA16 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
12/12/2023 | 12:21 | AP125D | URBAN | Asset failure | LV | 1.00 | 526.0 | 0.000811 | 0.0000015 | No
12/12/2023 | 12:22 | SD31200 | LONG RURAL | Weather |  | 2.00 | 3,223.0 | 0.046259 | 0.0000144 | No
12/12/2023 | 12:24 | KI41 | LONG RURAL | Weather |  | 118.00 | 36.0 | 0.030485 | 0.0008468 | No
12/12/2023 | 12:35 | HH121A | URBAN | Asset failure | LV | 56.00 | 87.6 | 0.007561 | 0.0000863 | No
12/12/2023 | 12:37 | MV51 | SHORT RURAL | Asset failure | LV | 1.00 | 643.0 | 0.004524 | 0.0000070 | No
12/12/2023 | 12:41 | MI03 | LONG RURAL | Asset failure | LV | 1.00 | 251.0 | 0.001801 | 0.0000072 | No
12/12/2023 | 12:42 | KI52 | LONG RURAL | Weather |  | 39.00 | 1,864.6 | 0.521863 | 0.0002799 | No
12/12/2023 | 12:45 | SA11 | URBAN | Asset failure | LV | 49.00 | 110.0 | 0.008310 | 0.0000755 | No
12/12/2023 | 12:48 | AP227D | URBAN | Overloads |  | 2.00 | 130.0 | 0.000401 | 0.0000031 | No
12/12/2023 | 12:53 | ST35 | LONG RURAL | Asset failure | LV | 1.00 | 327.0 | 0.002347 | 0.0000072 | No
12/12/2023 | 13:03 | CL05 | LONG RURAL | Weather |  | 364.00 | 406.1 | 1.060920 | 0.0026122 | No
12/12/2023 | 13:04 | ST12 | SHORT RURAL | Unknown | Unknown | 2.00 | 79.0 | 0.001112 | 0.0000141 | No
12/12/2023 | 13:05 | SM172E | URBAN | Weather |  | 3,006.00 | 21.3 | 0.098831 | 0.0046345 | No
12/12/2023 | 13:12 | NL234C | URBAN | Weather |  | 2,738.00 | 75.3 | 0.317657 | 0.0042213 | No
12/12/2023 | 13:12 | ME231B | URBAN | Unknown | Unknown | 1.00 | 385.0 | 0.000594 | 0.0000015 | No
12/12/2023 | 13:13 | SM410A | URBAN | Weather |  | 28.00 | 337.0 | 0.014548 | 0.0000432 | No
12/12/2023 | 13:14 | NL115C | URBAN | Weather |  | 2,295.00 | 77.8 | 0.275306 | 0.0035383 | No
12/12/2023 | 13:18 | MV53 | SHORT RURAL | Unknown | Unknown | 1.00 | 811.0 | 0.005706 | 0.0000070 | No
12/12/2023 | 13:19 | MV62 | SHORT RURAL | Weather |  | 64.00 | 689.7 | 0.310547 | 0.0004503 | No
12/12/2023 | 13:24 | NL115B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,344.0 | 0.002072 | 0.0000015 | No
12/12/2023 | 13:25 | GA03 | LONG RURAL | Weather |  | 137.00 | 15.1 | 0.014884 | 0.0009832 | No
12/12/2023 | 13:25 | MV62 | SHORT RURAL | Weather |  | 2,168.00 | 141.3 | 2.155259 | 0.0152529 | No
12/12/2023 | 13:26 | R33 | LONG RURAL | Unknown | Unknown | 56.00 | 309.0 | 0.124179 | 0.0004019 | No
12/12/2023 | 13:32 | MV15 | SHORT RURAL | Unknown | Unknown | 9.00 | 745.0 | 0.047173 | 0.0000633 | No
12/12/2023 | 13:36 | SM349F | URBAN | Weather |  | 33.33 | 174.0 | 0.008942 | 0.0000514 | No
12/12/2023 | 13:37 | MV33 | SHORT RURAL | Weather |  | 6.00 | 1,519.0 | 0.064121 | 0.0000422 | No
12/12/2023 | 13:38 | AP351E | URBAN | Unknown | Unknown | 1.00 | 649.0 | 0.001001 | 0.0000015 | No
12/12/2023 | 13:38 | GA21 | LONG RURAL | Weather |  | 1.00 | 226.0 | 0.001622 | 0.0000072 | No
12/12/2023 | 13:39 | MV63 | SHORT RURAL | Unknown | Unknown | 2.00 | 569.0 | 0.008006 | 0.0000141 | No
12/12/2023 | 13:39 | SM349F | URBAN | Unknown | Unknown | 50.00 | 64.7 | 0.004985 | 0.0000771 | No
12/12/2023 | 13:51 | NL451A | URBAN | Asset failure | LV | 1.00 | 543.0 | 0.000837 | 0.0000015 | No
12/12/2023 | 13:57 | BU11 | SHORT RURAL | Planned |  | 26.00 | 17.0 | 0.003110 | 0.0001829 | No
12/12/2023 | 14:06 | KA20 | LONG RURAL | Unknown | Unknown | 1.00 | 458.0 | 0.003287 | 0.0000072 | No
12/12/2023 | 14:40 | SD35200 | LONG RURAL | Weather |  | 61.00 | 77.3 | 0.033844 | 0.0004378 | No
12/12/2023 | 14:50 | SM410C | URBAN | Unknown | Unknown | 121.00 | 471.0 | 0.087866 | 0.0001866 | No
12/12/2023 | 14:56 | NL234A | URBAN | Weather |  | 1.00 | 596.0 | 0.000919 | 0.0000015 | No
12/12/2023 | 15:06 | KA17 | LONG RURAL | Weather |  | 49.00 | 1,136.2 | 0.399535 | 0.0003516 | No
12/12/2023 | 15:07 | G31 | LONG RURAL | Weather |  | 100.00 | 2,519.8 | 1.808284 | 0.0007176 | No
12/12/2023 | 15:10 | HH148D | URBAN | Weather |  | 16.00 | 417.0 | 0.010287 | 0.0000247 | No
12/12/2023 | 15:12 | SD33200 | LONG RURAL | Unknown | Unknown | 356.00 | 9.7 | 0.024902 | 0.0025548 | No
12/12/2023 | 15:15 | SM349D | URBAN | Weather |  | 1.00 | 996.0 | 0.001536 | 0.0000015 | No
12/12/2023 | 15:16 | CN75 | LONG RURAL | Weather |  | 41.00 | 356.0 | 0.104746 | 0.0002942 | No
12/12/2023 | 15:16 | CN75 | LONG RURAL | Weather |  | 19.00 | 1,306.0 | 0.178073 | 0.0001364 | No
12/12/2023 | 15:17 | SD33200 | LONG RURAL | Unknown | Unknown | 4.00 | 1,599.0 | 0.045900 | 0.0000287 | No
12/12/2023 | 15:19 | BM42 | SHORT RURAL | Weather |  | 1.00 | 106.0 | 0.000746 | 0.0000070 | No
12/12/2023 | 15:22 | KA24 | LONG RURAL | Weather |  | 30.00 | 1,359.1 | 0.292600 | 0.0002153 | No
12/12/2023 | 15:36 | EL03 | URBAN | Asset failure | LV | 1.00 | 325.0 | 0.000501 | 0.0000015 | No
12/12/2023 | 15:56 | VH34 | SHORT RURAL | Unknown | Unknown | 15.00 | 332.0 | 0.035037 | 0.0001055 | No
12/12/2023 | 15:58 | HH148C | URBAN | Unknown | Unknown | 1.00 | 431.0 | 0.000664 | 0.0000015 | No
12/12/2023 | 16:05 | SD35403 | SHORT RURAL | Weather |  | 55.00 | 347.6 | 0.134497 | 0.0003870 | No
12/12/2023 | 16:07 | SD33200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 1,815.0 | 0.013025 | 0.0000072 | No
12/12/2023 | 16:14 | SD33100 | LONG RURAL | Unknown | Unknown | 1.00 | 1,603.0 | 0.011504 | 0.0000072 | No
12/12/2023 | 16:22 | NA09 | LONG RURAL | Weather |  | 10.00 | 154.0 | 0.011052 | 0.0000718 | No
12/12/2023 | 16:30 | NA07 | LONG RURAL | Weather |  | 1.00 | 301.0 | 0.002160 | 0.0000072 | No
12/12/2023 | 16:31 | NA07 | LONG RURAL | Unknown | Unknown | 10.67 | 95.0 | 0.007272 | 0.0000765 | No
12/12/2023 | 16:44 | EL12 | URBAN | Weather |  | 1.00 | 586.0 | 0.000903 | 0.0000015 | No
12/12/2023 | 16:45 | MV61 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,089.0 | 0.001679 | 0.0000015 | No
12/12/2023 | 16:51 | GA28 | LONG RURAL | Weather |  | 39.00 | 77.0 | 0.021551 | 0.0002799 | No
12/12/2023 | 16:51 | KA07 | LONG RURAL | Weather |  | 71.00 | 1,222.0 | 0.622618 | 0.0005095 | No
12/12/2023 | 16:53 | SM349F | URBAN | Unknown | Unknown | 1.00 | 691.0 | 0.001065 | 0.0000015 | No
12/12/2023 | 16:56 | MG28 | LONG RURAL | Weather |  | 12.00 | 139.0 | 0.011970 | 0.0000861 | No
12/12/2023 | 16:56 | MG29 | LONG RURAL | Animal | Animal impact | 40.00 | 1,221.0 | 0.350492 | 0.0002871 | No
12/12/2023 | 16:59 | HH121C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 64.00 | 44.0 | 0.004342 | 0.0000987 | No
12/12/2023 | 17:01 | NL451E | URBAN | Asset failure | LV | 1.00 | 456.0 | 0.000703 | 0.0000015 | No
12/12/2023 | 17:10 | G15 | LONG RURAL | Weather |  | 79.00 | 1,234.4 | 0.699843 | 0.0005669 | No
12/12/2023 | 17:10 | G15 | LONG RURAL | Weather |  | 2.00 | 2,850.0 | 0.040905 | 0.0000144 | No
12/12/2023 | 17:12 | VH22 | SHORT RURAL | Asset failure | LV | 1.00 | 249.0 | 0.001752 | 0.0000070 | No
12/12/2023 | 17:17 | NL760A | URBAN | Unknown | Unknown | 432.00 | 14.1 | 0.009395 | 0.0006660 | No
12/12/2023 | 17:26 | MI06 | LONG RURAL | Unknown | Unknown | 58.00 | 829.0 | 0.345059 | 0.0004162 | No
12/12/2023 | 17:27 | NL115C | URBAN | Weather |  | 96.00 | 371.0 | 0.054911 | 0.0001480 | No
12/12/2023 | 17:30 | MI23 | LONG RURAL | Weather |  | 74.00 | 549.0 | 0.291546 | 0.0005310 | No
12/12/2023 | 17:31 | NL115C | URBAN | Unknown | Unknown | 65.00 | 356.0 | 0.035676 | 0.0001002 | No
12/12/2023 | 17:38 | NL115C | URBAN | Unknown | Unknown | 1.00 | 537.0 | 0.000828 | 0.0000015 | No
12/12/2023 | 17:38 | NA32 | LONG RURAL | Weather |  | 11.00 | 165.0 | 0.013025 | 0.0000789 | No
12/12/2023 | 17:42 | GA19 | LONG RURAL | Weather |  | 58.00 | 248.0 | 0.103224 | 0.0004162 | No
12/12/2023 | 17:45 | GA29 | LONG RURAL | Weather |  | 6.00 | 30.0 | 0.001292 | 0.0000431 | No
12/12/2023 | 17:45 | SM349D | URBAN | Weather |  | 274.00 | 106.4 | 0.044954 | 0.0004224 | No
12/12/2023 | 17:46 | G20 | LONG RURAL | Weather |  | 1.00 | 3,844.0 | 0.027586 | 0.0000072 | No
12/12/2023 | 17:49 | YK15 | LONG RURAL | Asset failure | LV | 1.00 | 1,270.0 | 0.009114 | 0.0000072 | No
12/12/2023 | 17:52 | KA32 | LONG RURAL | Weather |  | 38.00 | 147.0 | 0.040087 | 0.0002727 | No
12/12/2023 | 17:57 | G22 | LONG RURAL | Weather |  | 3.00 | 2,582.0 | 0.055588 | 0.0000215 | No
12/12/2023 | 17:58 | MI03 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 98.00 | 1,170.0 | 0.822838 | 0.0007033 | No
12/12/2023 | 18:02 | MI20 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 6.00 | 1,532.0 | 0.065965 | 0.0000431 | No
12/12/2023 | 18:18 | MG34 | LONG RURAL | Weather |  | 225.00 | 202.2 | 0.326501 | 0.0016147 | No
12/12/2023 | 18:18 | MG17 | LONG RURAL | Weather |  | 1.00 | 1,409.0 | 0.010111 | 0.0000072 | No
12/12/2023 | 18:18 | MG21 | LONG RURAL | Unknown | Unknown | 64.00 | 1,084.5 | 0.498109 | 0.0004593 | No
12/12/2023 | 18:18 | HH148D | URBAN | Asset failure | LV | 1.00 | 389.0 | 0.000600 | 0.0000015 | No
12/12/2023 | 18:38 | HK05 | LONG RURAL | Weather |  | 21.00 | 1,346.5 | 0.202925 | 0.0001507 | No
12/12/2023 | 18:47 | SG02 | SHORT RURAL | Weather |  | 1.00 | 660.0 | 0.004643 | 0.0000070 | No
12/12/2023 | 18:50 | MV31 | SHORT RURAL | Weather |  | 90.67 | 90.5 | 0.057717 | 0.0006379 | No
12/12/2023 | 18:54 | KA28 | LONG RURAL | Unknown | Unknown | 19.00 | 18.0 | 0.002454 | 0.0001364 | No
12/12/2023 | 19:09 | SD32103 | URBAN | Planned |  | 4.00 | 172.0 | 0.001061 | 0.0000062 | No
12/12/2023 | 19:29 | HH341D | URBAN | Asset failure | LV | 26.33 | 139.0 | 0.005643 | 0.0000406 | No
12/12/2023 | 19:38 | MI20 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 32.00 | 719.1 | 0.165127 | 0.0002296 | No
12/12/2023 | 19:38 | MI20 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 1,366.0 | 0.009803 | 0.0000072 | No
12/12/2023 | 19:43 | HH429C | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
12/12/2023 | 19:50 | HK04 | LONG RURAL | Weather |  | 5.00 | 700.0 | 0.025117 | 0.0000359 | No
12/12/2023 | 19:55 | MG05 | LONG RURAL | Weather |  | 2.00 | 1,175.0 | 0.016864 | 0.0000144 | No
12/12/2023 | 19:55 | AP529E | URBAN | Asset failure | LV | 39.00 | 204.7 | 0.012306 | 0.0000601 | No
12/12/2023 | 19:57 | NL511B | URBAN | Asset failure | LV | 55.00 | 52.0 | 0.004409 | 0.0000848 | No
12/12/2023 | 19:59 | EL07 | URBAN | Unknown | Unknown | 4.33 | 135.0 | 0.000902 | 0.0000067 | No
12/12/2023 | 20:02 | LX32 | SHORT RURAL | Weather |  | 4.00 | 116.0 | 0.003264 | 0.0000281 | No
12/12/2023 | 20:08 | VH44 | SHORT RURAL | Weather |  | 1.00 | 1,105.0 | 0.007774 | 0.0000070 | No
12/12/2023 | 20:12 | HH130C | URBAN | Asset failure | LV | 27.00 | 54.0 | 0.002248 | 0.0000416 | No
12/12/2023 | 20:20 | VH44 | SHORT RURAL | Unknown | Unknown | 7.00 | 166.0 | 0.008175 | 0.0000492 | No
12/12/2023 | 20:32 | SD40200 | LONG RURAL | Weather |  | 1.00 | 1,164.0 | 0.008353 | 0.0000072 | No
12/12/2023 | 20:33 | VH44 | SHORT RURAL | Weather |  | 1.00 | 894.0 | 0.006290 | 0.0000070 | No
12/12/2023 | 20:41 | HH409D | URBAN | Vegetation | Grow-in - NSP responsibility | 23.00 | 103.0 | 0.003652 | 0.0000355 | No
12/12/2023 | 20:44 | MI20 | LONG RURAL | Weather |  | 28.00 | 1,218.1 | 0.244770 | 0.0002009 | No
12/12/2023 | 20:48 | KI41 | LONG RURAL | Weather |  | 156.00 | 16.2 | 0.018084 | 0.0011195 | No
12/12/2023 | 20:55 | SM350C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
12/12/2023 | 21:01 | M93 | LONG RURAL | Unknown | Unknown | 2.00 | 340.0 | 0.004880 | 0.0000144 | No
12/12/2023 | 21:05 | BT08 | LONG RURAL | Weather |  | 59.00 | 235.4 | 0.099651 | 0.0004234 | No
12/12/2023 | 21:22 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 429.0 | 0.003018 | 0.0000070 | No
12/12/2023 | 21:22 | MG19 | LONG RURAL | Weather |  | 2.00 | 1,021.0 | 0.014654 | 0.0000144 | No
12/12/2023 | 21:24 | ME200G | URBAN | Asset failure | LV | 1.33 | 176.0 | 0.000362 | 0.0000021 | No
12/12/2023 | 21:35 | BT04 | LONG RURAL | Weather |  | 1.00 | 1,061.0 | 0.007614 | 0.0000072 | No
12/12/2023 | 22:24 | SM349A | URBAN | Asset failure | LV | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
12/12/2023 | 22:35 | WHY10 | URBAN | Asset failure | LV | 1.67 | 748.0 | 0.001922 | 0.0000026 | No
12/12/2023 | 22:35 | NA56 | LONG RURAL | Weather |  | 46.00 | 820.5 | 0.270863 | 0.0003301 | No
12/12/2023 | 22:46 | G02 | LONG RURAL | Weather |  | 4.00 | 1,045.0 | 0.029997 | 0.0000287 | No
12/12/2023 | 23:05 | HH121E | URBAN | Unknown | Unknown | 7.00 | 348.0 | 0.003756 | 0.0000108 | No
12/12/2023 | 23:22 | SA11 | URBAN | Asset failure | LV | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
12/12/2023 | 23:38 | NL115F | URBAN | Weather |  | 54.00 | 226.0 | 0.018816 | 0.0000833 | No
12/12/2023 | 23:50 | HH341C | URBAN | Asset failure | LV | 34.00 | 98.0 | 0.005137 | 0.0000524 | No
13/12/2023 | 01:57 | SM411B | URBAN | Asset failure | LV | 72.00 | 85.0 | 0.009436 | 0.0001110 | No
13/12/2023 | 03:33 | HH118B | URBAN | Animal | Animal impact | 1,148.00 | 47.0 | 0.083187 | 0.0017699 | No
13/12/2023 | 03:35 | SD40200 | LONG RURAL | Unknown | Unknown | 269.00 | 68.0 | 0.131269 | 0.0019304 | No
13/12/2023 | 03:44 | SD36400 | LONG RURAL | Unknown | Unknown | 36.67 | 607.0 | 0.159721 | 0.0002631 | No
13/12/2023 | 04:09 | AP351E | URBAN | Unknown | Unknown | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
13/12/2023 | 06:18 | LX51 | SHORT RURAL | Asset failure | LV | 1.00 | 316.0 | 0.002223 | 0.0000070 | No
13/12/2023 | 06:23 | G25 | LONG RURAL | Weather |  | 30.00 | 1,654.8 | 0.356269 | 0.0002153 | No
13/12/2023 | 06:23 | MV15 | SHORT RURAL | Weather |  | 1.00 | 500.0 | 0.003518 | 0.0000070 | No
13/12/2023 | 06:35 | G17 | LONG RURAL | Weather |  | 4.00 | 2,086.0 | 0.059879 | 0.0000287 | No
13/12/2023 | 06:49 | MG19 | LONG RURAL | Weather |  | 7.00 | 453.0 | 0.022756 | 0.0000502 | No
13/12/2023 | 06:54 | BT04 | LONG RURAL | Weather |  | 14.00 | 451.0 | 0.045311 | 0.0001005 | No
13/12/2023 | 06:57 | MI23 | LONG RURAL | Weather |  | 1.00 | 759.0 | 0.005447 | 0.0000072 | No
13/12/2023 | 07:09 | MV63 | SHORT RURAL | Asset failure | LV | 2.67 | 388.0 | 0.007279 | 0.0000188 | No
13/12/2023 | 07:18 | MI23 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 15.00 | 250.0 | 0.026911 | 0.0001076 | No
13/12/2023 | 07:20 | MG05 | LONG RURAL | Weather |  | 1.00 | 1,593.0 | 0.011432 | 0.0000072 | No
13/12/2023 | 07:24 | SM410C | URBAN | Unknown | Unknown | 5.00 | 95.0 | 0.000732 | 0.0000077 | No
13/12/2023 | 07:29 | MI23 | LONG RURAL | Weather |  | 59.00 | 423.0 | 0.179114 | 0.0004234 | No
13/12/2023 | 07:49 | MG22 | LONG RURAL | Weather |  | 1.00 | 1,565.0 | 0.011231 | 0.0000072 | No
13/12/2023 | 08:09 | G09 | LONG RURAL | Weather |  | 16.00 | 572.0 | 0.065678 | 0.0001148 | No
13/12/2023 | 08:27 | HH121A | URBAN | Asset failure | LV | 8.67 | 243.0 | 0.003247 | 0.0000134 | No
13/12/2023 | 08:31 | VH11 | URBAN | Asset failure | LV | 70.00 | 205.2 | 0.022149 | 0.0001079 | No
13/12/2023 | 08:33 | SM349H | URBAN | Asset failure | LV | 62.00 | 106.9 | 0.010220 | 0.0000956 | No
13/12/2023 | 08:44 | G28 | LONG RURAL | Weather |  | 3.00 | 3,344.0 | 0.071993 | 0.0000215 | No
13/12/2023 | 08:49 | EL14 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 358.00 | 74.0 | 0.040844 | 0.0005519 | No
13/12/2023 | 08:51 | NL111A | URBAN | Asset failure | LV | 1.00 | 650.0 | 0.001002 | 0.0000015 | No
13/12/2023 | 08:57 | WHY363A | SHORT RURAL | Planned |  | 55.00 | 340.0 | 0.131564 | 0.0003870 | No
13/12/2023 | 09:02 | GU32 | LONG RURAL | Weather |  | 607.00 | 270.5 | 1.178303 | 0.0043560 | No
13/12/2023 | 09:05 | MV15 | SHORT RURAL | Planned |  | 29.00 | 338.0 | 0.068962 | 0.0002040 | No
13/12/2023 | 09:38 | AP125D | URBAN | Weather |  | 1.00 | 367.0 | 0.000566 | 0.0000015 | No
13/12/2023 | 09:38 | G13 | LONG RURAL | Weather |  | 2.00 | 1,717.0 | 0.024644 | 0.0000144 | No
13/12/2023 | 09:43 | HH107B | URBAN | Planned |  | 118.00 | 264.5 | 0.048115 | 0.0001819 | No
13/12/2023 | 10:03 | KI58 | SHORT RURAL | Weather |  | 1.00 | 1,833.0 | 0.012896 | 0.0000070 | No
13/12/2023 | 10:30 | MTB81 | SHORT RURAL | Animal | Animal impact | 1.00 | 568.0 | 0.003996 | 0.0000070 | No
13/12/2023 | 10:33 | EL09 | URBAN | Asset failure | LV | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
13/12/2023 | 10:40 | MI20 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 1,421.0 | 0.020395 | 0.0000144 | No
13/12/2023 | 10:48 | LX31 | SHORT RURAL | Unknown | Unknown | 2.00 | 94.0 | 0.001323 | 0.0000141 | No
13/12/2023 | 11:24 | ME116C | URBAN | Asset failure | LV | 62.00 | 48.1 | 0.004594 | 0.0000956 | No
13/12/2023 | 11:38 | HH102D | URBAN | Asset failure | LV | 1.00 | 136.0 | 0.000210 | 0.0000015 | No
13/12/2023 | 11:49 | NL115C | URBAN | Asset failure | LV | 1.00 | 591.0 | 0.000911 | 0.0000015 | No
13/12/2023 | 11:52 | AP125D | URBAN | Weather |  | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
13/12/2023 | 11:56 | MG09 | SHORT RURAL | Unknown | Unknown | 1.00 | 429.0 | 0.003018 | 0.0000070 | No
13/12/2023 | 11:58 | MT14 | SHORT RURAL | Weather |  | 3.00 | 206.0 | 0.004348 | 0.0000211 | No
13/12/2023 | 12:08 | M93 | LONG RURAL | Animal | Animal impact | 51.00 | 316.9 | 0.115977 | 0.0003660 | No
13/12/2023 | 12:19 | NA32 | LONG RURAL | Weather |  | 3.00 | 1,546.0 | 0.033284 | 0.0000215 | No
13/12/2023 | 12:42 | SA20 | URBAN | Asset failure | LV | 1.00 | 384.0 | 0.000592 | 0.0000015 | No
13/12/2023 | 13:40 | VH23 | SHORT RURAL | Unknown | Unknown | 1.00 | 215.0 | 0.001513 | 0.0000070 | No
13/12/2023 | 13:48 | MI20 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 399.0 | 0.002863 | 0.0000072 | No
13/12/2023 | 14:03 | SM126A | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
13/12/2023 | 14:10 | MI06 | LONG RURAL | Weather |  | 1.00 | 1,106.0 | 0.007937 | 0.0000072 | No
13/12/2023 | 14:28 | SD33200 | LONG RURAL | Weather |  | 2.00 | 183.0 | 0.002627 | 0.0000144 | No
13/12/2023 | 14:49 | NA17 | LONG RURAL | Weather |  | 63.00 | 122.0 | 0.055157 | 0.0004521 | No
13/12/2023 | 15:19 | KA07 | LONG RURAL | Weather |  | 2.00 | 153.0 | 0.002196 | 0.0000144 | No
13/12/2023 | 15:48 | SM126B | URBAN | Unknown | Unknown | 37.00 | 383.0 | 0.021848 | 0.0000570 | No
13/12/2023 | 16:18 | VH15 | SHORT RURAL | Asset failure | HV | 366.00 | 252.0 | 0.648848 | 0.0025750 | No
13/12/2023 | 16:18 | VH15 | SHORT RURAL | Weather |  | 1.00 | 1,153.0 | 0.008112 | 0.0000070 | No
13/12/2023 | 16:27 | NA34 | LONG RURAL | Weather |  | 148.00 | 165.1 | 0.175346 | 0.0010621 | No
13/12/2023 | 16:43 | LX43 | SHORT RURAL | Other |  | 16.00 | 203.4 | 0.022893 | 0.0001126 | No
13/12/2023 | 17:03 | NL210A | URBAN | Third Party | Other | 1.00 | 327.0 | 0.000504 | 0.0000015 | No
13/12/2023 | 17:05 | SA20 | URBAN | Asset failure | LV | 73.00 | 75.8 | 0.008526 | 0.0001125 | No
13/12/2023 | 17:11 | AP125D | URBAN | Weather |  | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
13/12/2023 | 17:15 | MG19 | LONG RURAL | Weather |  | 2.00 | 107.0 | 0.001536 | 0.0000144 | No
13/12/2023 | 17:20 | AP425D | URBAN | Third Party | Other | 411.33 | 39.0 | 0.024733 | 0.0006342 | No
13/12/2023 | 18:03 | SA11 | URBAN | Asset failure | LV | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
13/12/2023 | 18:03 | HH403A | URBAN | Overloads |  | 1.00 | 547.0 | 0.000843 | 0.0000015 | No
13/12/2023 | 18:04 | SM126D | URBAN | Other |  | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
13/12/2023 | 18:11 | HH145A | URBAN | Unknown | Unknown | 301.00 | 112.0 | 0.051976 | 0.0004641 | No
13/12/2023 | 18:11 | AP424B | URBAN | Asset failure | LV | 98.00 | 88.1 | 0.013307 | 0.0001511 | No
13/12/2023 | 18:14 | BM11 | SHORT RURAL | Asset failure | LV | 2.00 | 248.0 | 0.003490 | 0.0000141 | No
13/12/2023 | 18:18 | HH121D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 609.00 | 93.9 | 0.088187 | 0.0009389 | No
13/12/2023 | 18:31 | KI15 | LONG RURAL | Weather |  | 21.00 | 326.0 | 0.049129 | 0.0001507 | No
13/12/2023 | 18:48 | AP226C | URBAN | Asset failure | LV | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
13/12/2023 | 18:48 | HH341E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 694.00 | 48.0 | 0.051331 | 0.0010700 | No
13/12/2023 | 19:06 | G14 | LONG RURAL | Weather |  | 5.00 | 79.0 | 0.002835 | 0.0000359 | No
13/12/2023 | 19:08 | R34 | SHORT RURAL | Weather |  | 1.00 | 80.0 | 0.000563 | 0.0000070 | No
13/12/2023 | 20:11 | G28 | LONG RURAL | Unknown | Unknown | 12.00 | 1,107.0 | 0.095330 | 0.0000861 | No
13/12/2023 | 20:14 | HH145A | URBAN | Asset failure | LV | 44.00 | 178.0 | 0.012075 | 0.0000678 | No
13/12/2023 | 20:20 | EL14 | URBAN | Asset failure | LV | 30.00 | 61.0 | 0.002821 | 0.0000463 | No
13/12/2023 | 20:34 | G36 | LONG RURAL | Weather |  | 63.00 | 1,018.5 | 0.460455 | 0.0004521 | No
13/12/2023 | 20:41 | SM349E | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
13/12/2023 | 20:52 | CBD366P | CBD | Planned |  | 1.00 | 436.0 | 0.062992 | 0.0001445 | No
13/12/2023 | 21:23 | GU32 | LONG RURAL | Unknown | Unknown | 1.00 | 965.0 | 0.006925 | 0.0000072 | No
13/12/2023 | 21:36 | CBD366G | CBD | Planned |  | 1.00 | 58.0 | 0.008380 | 0.0001445 | No
13/12/2023 | 21:59 | HH121A | URBAN | Asset failure | LV | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
13/12/2023 | 23:14 | HH177E | URBAN | Asset failure | LV | 42.00 | 104.0 | 0.006734 | 0.0000648 | No
13/12/2023 | 23:32 | M23 | LONG RURAL | Planned |  | 1.00 | 21.0 | 0.000151 | 0.0000072 | No
14/12/2023 | 01:12 | MV61 | URBAN | Asset failure | LV | 125.00 | 90.0 | 0.017345 | 0.0001927 | No
14/12/2023 | 04:03 | SD33100 | LONG RURAL | Weather |  | 613.00 | 207.9 | 0.914473 | 0.0043991 | No
14/12/2023 | 04:12 | NL115F | URBAN | Asset failure | LV | 85.00 | 34.0 | 0.004456 | 0.0001310 | No
14/12/2023 | 04:41 | NU06 | LONG RURAL | Unknown | Unknown | 1.00 | 319.0 | 0.002289 | 0.0000072 | No
14/12/2023 | 05:05 | R32 | LONG RURAL | Unknown | Unknown | 78.00 | 432.4 | 0.242058 | 0.0005598 | No
14/12/2023 | 05:15 | SD40200 | LONG RURAL | Weather |  | 1.00 | 496.0 | 0.003559 | 0.0000072 | No
14/12/2023 | 06:39 | NL210C | URBAN | Asset failure | LV | 54.00 | 494.0 | 0.041128 | 0.0000833 | No
14/12/2023 | 06:40 | SG01 | SHORT RURAL | Weather |  | 2.00 | 395.0 | 0.005558 | 0.0000141 | No
14/12/2023 | 07:03 | SG01 | SHORT RURAL | Weather |  | 28.00 | 160.5 | 0.031627 | 0.0001970 | No
14/12/2023 | 07:23 | NL760B | URBAN | Asset failure | LV | 1.00 | 223.0 | 0.000344 | 0.0000015 | No
14/12/2023 | 07:28 | EL01A | URBAN | Asset failure | HV | 18.00 | 559.0 | 0.015513 | 0.0000278 | No
14/12/2023 | 08:02 | AP355A | URBAN | Planned |  | 40.00 | 341.0 | 0.021030 | 0.0000617 | No
14/12/2023 | 08:08 | G13 | LONG RURAL | Weather |  | 98.00 | 259.4 | 0.182422 | 0.0007033 | No
14/12/2023 | 09:05 | EL260B | URBAN | Planned |  | 27.00 | 322.0 | 0.013404 | 0.0000416 | No
14/12/2023 | 09:14 | HH409C | URBAN | Planned |  | 94.00 | 378.0 | 0.054782 | 0.0001449 | No
14/12/2023 | 09:30 | MV34 | SHORT RURAL | Asset failure | LV | 14.00 | 288.0 | 0.028367 | 0.0000985 | No
14/12/2023 | 09:53 | CD23 | LONG RURAL | Planned |  | 37.00 | 211.0 | 0.056026 | 0.0002655 | No
14/12/2023 | 10:13 | PP03 | URBAN | Asset failure | LV | 1.00 | 1,430.0 | 0.002205 | 0.0000015 | No
14/12/2023 | 10:14 | SM350F | URBAN | Asset failure | LV | 1.00 | 541.0 | 0.000834 | 0.0000015 | No
14/12/2023 | 10:17 | HH432E | URBAN | Third Party | Vehicle impact | 35.33 | 61.0 | 0.003323 | 0.0000545 | No
14/12/2023 | 10:18 | CV18 | SHORT RURAL | Planned |  | 1.00 | 179.0 | 0.001259 | 0.0000070 | No
14/12/2023 | 10:33 | G05 | LONG RURAL | Asset failure | LV | 1.00 | 1,970.0 | 0.014137 | 0.0000072 | No
14/12/2023 | 10:42 | NA32 | LONG RURAL | Unknown | Unknown | 3.00 | 54.0 | 0.001163 | 0.0000215 | No
14/12/2023 | 10:45 | SM411E | URBAN | Asset failure | LV | 1.00 | 630.0 | 0.000971 | 0.0000015 | No
14/12/2023 | 10:48 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 252.0 | 0.001773 | 0.0000070 | No
14/12/2023 | 11:02 | KI52 | LONG RURAL | Weather |  | 2.00 | 112.0 | 0.001607 | 0.0000144 | No
14/12/2023 | 11:26 | HH386F | URBAN | Unknown | Unknown | 1.00 | 584.0 | 0.000900 | 0.0000015 | No
14/12/2023 | 11:42 | PP09 | LONG RURAL | Unknown | Unknown | 4.00 | 2,886.0 | 0.082844 | 0.0000287 | No
14/12/2023 | 12:17 | SG01 | SHORT RURAL | Weather |  | 1.00 | 60.0 | 0.000422 | 0.0000070 | No
14/12/2023 | 12:47 | BM55 | SHORT RURAL | Asset failure | LV | 2.00 | 183.0 | 0.002575 | 0.0000141 | No
14/12/2023 | 13:11 | HH177E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 61.00 | 309.0 | 0.029061 | 0.0000940 | No
14/12/2023 | 13:17 | VH16 | SHORT RURAL | Asset failure | LV | 1.00 | 104.0 | 0.000732 | 0.0000070 | No
14/12/2023 | 15:07 | G13 | LONG RURAL | Weather |  | 2.00 | 300.0 | 0.004306 | 0.0000144 | No
14/12/2023 | 15:08 | NL760B | URBAN | Asset failure | LV | 1.00 | 223.0 | 0.000344 | 0.0000015 | No
14/12/2023 | 16:05 | NL21 | URBAN | Asset failure | LV | 2.00 | 439.0 | 0.001354 | 0.0000031 | No
14/12/2023 | 16:15 | VH19 | SHORT RURAL | Weather |  | 66.00 | 208.1 | 0.096639 | 0.0004643 | No
14/12/2023 | 16:39 | SD49100 | LONG RURAL | Animal | Animal impact | 2.00 | 221.0 | 0.003172 | 0.0000144 | No
14/12/2023 | 17:03 | PP03 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 31.00 | 180.0 | 0.008603 | 0.0000478 | No
14/12/2023 | 17:03 | HH428F | URBAN | Asset failure | LV | 1.00 | 352.0 | 0.000543 | 0.0000015 | No
14/12/2023 | 17:36 | SA744D | URBAN | Asset failure | LV | 53.00 | 45.0 | 0.003677 | 0.0000817 | No
14/12/2023 | 17:45 | SM126C | URBAN | Weather |  | 73.00 | 86.0 | 0.009679 | 0.0001125 | No
14/12/2023 | 17:46 | LX42 | SHORT RURAL | Animal | Animal impact | 2.00 | 94.0 | 0.001323 | 0.0000141 | No
14/12/2023 | 17:58 | HH121D | URBAN | Asset failure | LV | 16.00 | 170.0 | 0.004194 | 0.0000247 | No
14/12/2023 | 17:58 | NL210C | URBAN | Asset failure | LV | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
14/12/2023 | 18:12 | MV62 | SHORT RURAL | Animal | Animal impact | 1.00 | 371.0 | 0.002610 | 0.0000070 | No
14/12/2023 | 18:40 | SA744D | URBAN | Overloads |  | 17.67 | 266.0 | 0.007245 | 0.0000272 | No
14/12/2023 | 19:38 | NU03 | LONG RURAL | Unknown | Unknown | 2.00 | 93.0 | 0.001335 | 0.0000144 | No
14/12/2023 | 20:27 | MV52 | SHORT RURAL | Animal | Animal impact | 7.00 | 246.0 | 0.012115 | 0.0000492 | No
14/12/2023 | 22:00 | G20 | LONG RURAL | Weather |  | 1.00 | 225.0 | 0.001615 | 0.0000072 | No
14/12/2023 | 22:10 | HH341D | URBAN | Asset failure | LV | 11.00 | 435.0 | 0.007377 | 0.0000170 | No
14/12/2023 | 23:03 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 172.0 | 0.001234 | 0.0000072 | No
15/12/2023 | 00:28 | MV62 | SHORT RURAL | Other |  | 1.00 | 44.0 | 0.000310 | 0.0000070 | No
15/12/2023 | 00:35 | VH17 | SHORT RURAL | Animal | Animal impact | 32.33 | 179.0 | 0.040719 | 0.0002275 | No
15/12/2023 | 02:19 | SM172B | URBAN | Asset failure | LV | 103.00 | 140.3 | 0.022272 | 0.0001588 | No
15/12/2023 | 05:06 | EL260A | URBAN | Unknown | Unknown | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
15/12/2023 | 05:24 | EL260A | URBAN | Unknown | Unknown | 1.00 | 316.0 | 0.000487 | 0.0000015 | No
15/12/2023 | 05:30 | G13 | LONG RURAL | Unknown | Unknown | 102.00 | 398.4 | 0.291603 | 0.0007320 | No
15/12/2023 | 06:08 | NL234C | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
15/12/2023 | 07:25 | MG52 | URBAN | Asset failure | LV | 1.00 | 203.0 | 0.000313 | 0.0000015 | No
15/12/2023 | 08:09 | SM411C | URBAN | Asset failure | LV | 1.00 | 807.0 | 0.001244 | 0.0000015 | No
15/12/2023 | 08:40 | HH386D | URBAN | Planned |  | 162.00 | 301.1 | 0.075194 | 0.0002498 | No
15/12/2023 | 08:51 | MTB53 | LONG RURAL | Network business | Switching and protection error | 2.00 | 184.0 | 0.002641 | 0.0000144 | No
15/12/2023 | 08:52 | NA33 | LONG RURAL | Planned |  | 2.00 | 8,762.5 | 0.125765 | 0.0000144 | No
15/12/2023 | 08:56 | MV62 | SHORT RURAL | Asset failure | LV | 2.00 | 357.0 | 0.005023 | 0.0000141 | No
15/12/2023 | 09:01 | EL01A | URBAN | Asset failure | HV | 18.00 | 183.0 | 0.005079 | 0.0000278 | No
15/12/2023 | 09:40 | KA32 | LONG RURAL | Weather |  | 1.00 | 2,108.0 | 0.015128 | 0.0000072 | No
15/12/2023 | 09:47 | AP529C | URBAN | Overloads |  | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
15/12/2023 | 09:48 | NL115A | URBAN | Third Party | Vehicle impact | 482.00 | 36.9 | 0.027412 | 0.0007431 | No
15/12/2023 | 10:07 | NL451A | URBAN | Planned |  | 89.00 | 290.0 | 0.039793 | 0.0001372 | No
15/12/2023 | 10:20 | GA20 | LONG RURAL | Planned |  | 5.00 | 95.0 | 0.003409 | 0.0000359 | No
15/12/2023 | 10:25 | SD36400 | LONG RURAL | Unknown | Unknown | 2.00 | 115.0 | 0.001651 | 0.0000144 | No
15/12/2023 | 11:06 | NA12 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 305.0 | 0.002189 | 0.0000072 | No
15/12/2023 | 11:28 | HH145B | URBAN | Asset failure | LV | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
15/12/2023 | 13:22 | MTB13 | SHORT RURAL | Asset failure | LV | 4.67 | 287.0 | 0.009423 | 0.0000328 | No
15/12/2023 | 13:31 | CL09 | LONG RURAL | Weather |  | 1.00 | 251.0 | 0.001801 | 0.0000072 | No
15/12/2023 | 13:50 | SM126D | URBAN | Third Party | Vehicle impact | 5.00 | 9.0 | 0.000069 | 0.0000077 | No
15/12/2023 | 13:59 | NU34 | LONG RURAL | Asset failure | LV | 24.00 | 62.0 | 0.010678 | 0.0001722 | No
15/12/2023 | 14:05 | BM54 | SHORT RURAL | Other |  | 2.00 | 109.0 | 0.001534 | 0.0000141 | No
15/12/2023 | 14:12 | CL13 | LONG RURAL | Weather |  | 2.00 | 199.5 | 0.002863 | 0.0000144 | No
15/12/2023 | 14:23 | KA17 | LONG RURAL | Asset failure | LV | 1.00 | 180.0 | 0.001292 | 0.0000072 | No
15/12/2023 | 14:53 | MI30 | LONG RURAL | Unknown | Unknown | 1.00 | 297.0 | 0.002131 | 0.0000072 | No
15/12/2023 | 16:48 | SM374B | URBAN | Asset failure | LV | 1.00 | 366.0 | 0.000564 | 0.0000015 | No
15/12/2023 | 18:14 | G32 | LONG RURAL | Weather |  | 17.00 | 128.0 | 0.015616 | 0.0001220 | No
15/12/2023 | 19:27 | NL111B | URBAN | Asset failure | LV | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
15/12/2023 | 22:26 | MB13 | SHORT RURAL | Unknown | Unknown | 7.00 | 105.0 | 0.005171 | 0.0000492 | No
16/12/2023 | 01:18 | NL544B | URBAN | Vegetation | Grow-in - NSP responsibility | 12.00 | 58.0 | 0.001073 | 0.0000185 | No
16/12/2023 | 07:40 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 288.0 | 0.002026 | 0.0000070 | No
16/12/2023 | 08:07 | SA520G | URBAN | Planned |  | 2.00 | 228.0 | 0.000703 | 0.0000031 | No
16/12/2023 | 09:49 | SD31200 | LONG RURAL | Unknown | Unknown | 1.00 | 44.0 | 0.000316 | 0.0000072 | No
16/12/2023 | 10:27 | MV14 | SHORT RURAL | Animal | Animal impact | 14.00 | 268.0 | 0.026397 | 0.0000985 | No
16/12/2023 | 11:47 | KA03 | LONG RURAL | Asset failure | LV | 1.00 | 614.0 | 0.004406 | 0.0000072 | No
16/12/2023 | 13:05 | SM179D | URBAN | Asset failure | LV | 2.00 | 207.0 | 0.000638 | 0.0000031 | No
16/12/2023 | 13:23 | ST12 | SHORT RURAL | Animal | Animal impact | 132.00 | 170.0 | 0.157876 | 0.0009287 | No
16/12/2023 | 13:26 | ME131E | URBAN | Asset failure | LV | 1.00 | 331.0 | 0.000510 | 0.0000015 | No
16/12/2023 | 14:47 | MB13 | SHORT RURAL | Asset failure | LV | 2.00 | 298.0 | 0.004193 | 0.0000141 | No
16/12/2023 | 15:14 | NL234A | URBAN | Overloads |  | 1.00 | 423.0 | 0.000652 | 0.0000015 | No
16/12/2023 | 16:12 | G12 | LONG RURAL | Weather |  | 2.00 | 24.0 | 0.000344 | 0.0000144 | No
16/12/2023 | 16:22 | ST11 | SHORT RURAL | Asset failure | LV | 22.00 | 175.0 | 0.027087 | 0.0001548 | No
16/12/2023 | 16:43 | ST41 | LONG RURAL | Overloads |  | 2.33 | 411.0 | 0.006882 | 0.0000167 | No
16/12/2023 | 17:34 | HH409C | URBAN | Asset failure | LV | 2.00 | 187.0 | 0.000577 | 0.0000031 | No
16/12/2023 | 18:12 | HH409C | URBAN | Asset failure | LV | 13.00 | 147.0 | 0.002946 | 0.0000200 | No
16/12/2023 | 18:32 | BT02 | LONG RURAL | Asset failure | LV | 1.00 | 261.0 | 0.001873 | 0.0000072 | No
16/12/2023 | 19:38 | VH43 | SHORT RURAL | Asset failure | HV | 8.00 | 501.1 | 0.028205 | 0.0000563 | No
16/12/2023 | 20:17 | MV64 | SHORT RURAL | Animal | Animal impact | 73.00 | 242.9 | 0.124746 | 0.0005136 | No
16/12/2023 | 20:26 | MV64 | SHORT RURAL | Asset failure | HV | 2,660.00 | 108.3 | 2.026524 | 0.0187144 | No
16/12/2023 | 20:44 | HH428A | URBAN | Asset failure | LV | 3.00 | 239.0 | 0.001105 | 0.0000046 | No
16/12/2023 | 21:09 | VH23 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,009.0 | 0.007099 | 0.0000070 | No
16/12/2023 | 22:53 | NL760C | URBAN | Asset failure | LV | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
17/12/2023 | 06:02 | MV33 | SHORT RURAL | Animal | Animal impact | 6.00 | 207.0 | 0.008738 | 0.0000422 | No
17/12/2023 | 07:43 | YK29 | LONG RURAL | Asset failure | LV | 17.00 | 43.0 | 0.005246 | 0.0001220 | No
17/12/2023 | 08:04 | GA17 | LONG RURAL | Asset failure | LV | 1.00 | 354.0 | 0.002540 | 0.0000072 | No
17/12/2023 | 08:49 | EL09 | URBAN | Asset failure | LV | 22.00 | 334.0 | 0.011329 | 0.0000339 | No
17/12/2023 | 08:56 | HH409D | URBAN | Asset failure | LV | 18.67 | 387.0 | 0.011138 | 0.0000288 | No
17/12/2023 | 09:33 | NL111Q | URBAN | Asset failure | LV | 1.00 | 249.0 | 0.000384 | 0.0000015 | No
17/12/2023 | 09:55 | SG12 | SHORT RURAL | Asset failure | LV | 1.00 | 531.0 | 0.003736 | 0.0000070 | No
17/12/2023 | 10:42 | SB15 | LONG RURAL | Third Party | Vehicle impact | 73.00 | 206.0 | 0.107918 | 0.0005239 | No
17/12/2023 | 10:44 | NL115A | URBAN | Asset failure | LV | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
17/12/2023 | 11:54 | SB23 | LONG RURAL | Asset failure | LV | 2.00 | 254.0 | 0.003646 | 0.0000144 | No
17/12/2023 | 12:16 | NL115F | URBAN | Unknown | Unknown | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
17/12/2023 | 12:53 | SM374B | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
17/12/2023 | 13:08 | GA50 | URBAN | Asset failure | LV | 102.00 | 154.2 | 0.024247 | 0.0001573 | No
17/12/2023 | 13:51 | CBD412N | URBAN | Overloads |  | 1.00 | 291.0 | 0.000449 | 0.0000015 | No
17/12/2023 | 15:02 | HH522A | URBAN | Asset failure | LV | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
17/12/2023 | 15:11 | HH148B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
17/12/2023 | 15:16 | ST24 | SHORT RURAL | Asset failure | HV | 65.00 | 450.8 | 0.206154 | 0.0004573 | No
17/12/2023 | 16:05 | VH11 | URBAN | Asset failure | LV | 1.00 | 593.0 | 0.000914 | 0.0000015 | No
17/12/2023 | 16:10 | NL115F | URBAN | Asset failure | LV | 1.00 | 212.0 | 0.000327 | 0.0000015 | No
17/12/2023 | 17:06 | EL16 | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 4.00 | 276.8 | 0.001707 | 0.0000062 | No
17/12/2023 | 17:21 | CV753A | LONG RURAL | Asset failure | LV | 23.00 | 50.0 | 0.008253 | 0.0001651 | No
17/12/2023 | 17:44 | SD38200 | LONG RURAL | Weather |  | 4,050.00 | 150.9 | 4.385283 | 0.0290641 | No
17/12/2023 | 19:07 | EL10 | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
17/12/2023 | 19:08 | SD38100 | LONG RURAL | Weather |  | 1,026.33 | 21.3 | 0.157169 | 0.0073653 | No
17/12/2023 | 20:35 | HH409D | URBAN | Unknown | Unknown | 1.00 | 1,588.0 | 0.002448 | 0.0000015 | No
17/12/2023 | 20:37 | AP214D | URBAN | Overloads |  | 24.67 | 187.0 | 0.007112 | 0.0000380 | No
17/12/2023 | 22:28 | MV15 | SHORT RURAL | Weather |  | 21.00 | 464.3 | 0.068603 | 0.0001477 | No
18/12/2023 | 02:44 | PL10 | LONG RURAL | Weather |  | 169.00 | 180.2 | 0.218577 | 0.0012128 | No
18/12/2023 | 03:33 | MT14 | SHORT RURAL | Unknown | Unknown | 75.00 | 373.5 | 0.197071 | 0.0005277 | No
18/12/2023 | 08:21 | LX41 | SHORT RURAL | Unknown | Unknown | 42.00 | 144.0 | 0.042551 | 0.0002955 | No
18/12/2023 | 08:43 | EL25 | URBAN | Planned |  | 667.00 | 64.9 | 0.066756 | 0.0010283 | No
18/12/2023 | 08:49 | R21 | LONG RURAL | Asset failure | LV | 28.00 | 188.3 | 0.037826 | 0.0002009 | No
18/12/2023 | 08:55 | PL04 | URBAN | Planned |  | 19.00 | 184.0 | 0.005390 | 0.0000293 | No
18/12/2023 | 09:05 | M14 | LONG RURAL | Planned |  | 1.00 | 125.0 | 0.000897 | 0.0000072 | No
18/12/2023 | 09:08 | HH145E | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
18/12/2023 | 09:12 | W29 | LONG RURAL | Unknown | Unknown | 14.00 | 214.0 | 0.021500 | 0.0001005 | No
18/12/2023 | 09:21 | NA34 | LONG RURAL | Unknown | Unknown | 2.00 | 200.0 | 0.002871 | 0.0000144 | No
18/12/2023 | 09:38 | GA800A | SHORT RURAL | Planned |  | 210.00 | 396.8 | 0.586204 | 0.0014775 | No
18/12/2023 | 09:52 | NU24 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 169.5 | 0.002433 | 0.0000144 | No
18/12/2023 | 10:09 | SM349E | URBAN | Unknown | Unknown | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
18/12/2023 | 10:12 | EL260B | URBAN | Animal | Animal impact | 438.00 | 65.0 | 0.043894 | 0.0006753 | No
18/12/2023 | 10:22 | GA22 | SHORT RURAL | Unknown | Unknown | 9.33 | 252.0 | 0.016547 | 0.0000657 | No
18/12/2023 | 10:36 | KI54 | LONG RURAL | Planned |  | 4.00 | 136.0 | 0.003904 | 0.0000287 | No
18/12/2023 | 10:47 | CBD366Q | URBAN | Unknown | Unknown | 1.00 | 692.0 | 0.001067 | 0.0000015 | No
18/12/2023 | 10:47 | MT08 | LONG RURAL | Overloads |  | 1.00 | 166.0 | 0.001191 | 0.0000072 | No
18/12/2023 | 12:08 | KA30 | SHORT RURAL | Asset failure | HV | 66.00 | 8.0 | 0.003715 | 0.0004643 | No
18/12/2023 | 12:08 | EL01R | URBAN | Overloads |  | 2.67 | 6.0 | 0.000025 | 0.0000041 | No
18/12/2023 | 12:12 | EL01P | URBAN | Asset failure | LV | 20.00 | 39.0 | 0.001203 | 0.0000308 | No
18/12/2023 | 12:24 | MT08 | LONG RURAL | Unknown | Unknown | 1.00 | 70.0 | 0.000502 | 0.0000072 | No
18/12/2023 | 13:12 | MB72 | LONG RURAL | Unknown | Unknown | 261.00 | 210.1 | 0.393485 | 0.0018730 | No
18/12/2023 | 13:15 | LX53 | SHORT RURAL | Asset failure | LV | 12.00 | 109.0 | 0.009202 | 0.0000844 | No
18/12/2023 | 13:17 | EL25 | URBAN | Planned |  | 667.00 | 34.0 | 0.034964 | 0.0010283 | No
18/12/2023 | 13:19 | AP227D | URBAN | Asset failure | LV | 75.00 | 98.0 | 0.011332 | 0.0001156 | No
18/12/2023 | 13:21 | MV52 | SHORT RURAL | Unknown | Unknown | 1.00 | 317.0 | 0.002230 | 0.0000070 | No
18/12/2023 | 13:50 | MV42 | SHORT RURAL | Asset failure | LV | 1.00 | 130.0 | 0.000915 | 0.0000070 | No
18/12/2023 | 13:51 | HH409E | URBAN | Asset failure | LV | 1.00 | 529.0 | 0.000816 | 0.0000015 | No
18/12/2023 | 13:59 | KI55 | LONG RURAL | Weather |  | 1.00 | 63.0 | 0.000452 | 0.0000072 | No
18/12/2023 | 14:16 | HH432C | URBAN | Asset failure | LV | 19.33 | 157.0 | 0.004680 | 0.0000298 | No
18/12/2023 | 14:49 | AP149E | URBAN | Asset failure | LV | 28.33 | 196.0 | 0.008562 | 0.0000437 | No
18/12/2023 | 16:15 | NA17 | LONG RURAL | Weather |  | 63.00 | 324.2 | 0.146584 | 0.0004521 | No
18/12/2023 | 16:30 | R26 | LONG RURAL | Weather |  | 88.00 | 247.1 | 0.156021 | 0.0006315 | No
18/12/2023 | 17:10 | GA16 | LONG RURAL | Other |  | 21.00 | 31.0 | 0.004672 | 0.0001507 | No
18/12/2023 | 17:38 | HH341C | URBAN | Unknown | Unknown | 53.00 | 194.0 | 0.015852 | 0.0000817 | No
18/12/2023 | 17:54 | BS0402 | URBAN | Unknown | Unknown | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
18/12/2023 | 18:17 | SA32 | URBAN | Asset failure | LV | 1.00 | 55.0 | 0.000085 | 0.0000015 | No
18/12/2023 | 18:51 | HH107C | URBAN | Overloads |  | 35.33 | 160.0 | 0.008716 | 0.0000545 | No
18/12/2023 | 21:27 | SA18 | URBAN | Overloads |  | 1.00 | 31.0 | 0.000048 | 0.0000015 | No
18/12/2023 | 21:51 | BT26 | LONG RURAL | Asset failure | HV | 56.00 | 245.0 | 0.098459 | 0.0004019 | No
18/12/2023 | 21:53 | SM374E | URBAN | Asset failure | LV | 32.00 | 54.0 | 0.002664 | 0.0000493 | No
18/12/2023 | 22:03 | GA52 | LONG RURAL | Asset failure | HV | 2.00 | 78.0 | 0.001120 | 0.0000144 | No
18/12/2023 | 22:51 | MV62 | SHORT RURAL | Weather |  | 519.00 | 139.8 | 0.510383 | 0.0036514 | No
19/12/2023 | 02:40 | HH145A | URBAN | Asset failure | LV | 44.00 | 74.0 | 0.005020 | 0.0000678 | No
19/12/2023 | 03:04 | KA28 | LONG RURAL | Unknown | Unknown | 19.00 | 399.0 | 0.054404 | 0.0001364 | No
19/12/2023 | 03:07 | G13 | LONG RURAL | Weather |  | 102.00 | 397.6 | 0.291007 | 0.0007320 | No
19/12/2023 | 05:23 | BS0186 | SHORT RURAL | Planned |  | 2.00 | 735.0 | 0.010342 | 0.0000141 | No
19/12/2023 | 05:28 | SSD528 | SHORT RURAL | Planned |  | 10.00 | 582.0 | 0.040947 | 0.0000704 | No
19/12/2023 | 06:27 | SG03 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 40.00 | 254.4 | 0.071600 | 0.0002814 | No
19/12/2023 | 06:43 | R09 | LONG RURAL | Unknown | Unknown | 2.00 | 282.0 | 0.004047 | 0.0000144 | No
19/12/2023 | 07:25 | SB01 | LONG RURAL | Asset failure | LV | 2.00 | 156.0 | 0.002239 | 0.0000144 | No
19/12/2023 | 07:42 | ST12 | SHORT RURAL | Asset failure | LV | 1.00 | 191.0 | 0.001344 | 0.0000070 | No
19/12/2023 | 08:05 | PL04 | URBAN | Planned |  | 133.00 | 523.0 | 0.107243 | 0.0002051 | No
19/12/2023 | 08:18 | CL13 | LONG RURAL | Asset failure | LV | 2.00 | 396.0 | 0.005684 | 0.0000144 | No
19/12/2023 | 08:51 | AP424E | URBAN | Planned |  | 359.00 | 195.3 | 0.108080 | 0.0005535 | No
19/12/2023 | 09:26 | GU15 | LONG RURAL | Planned |  | 7.00 | 368.0 | 0.018486 | 0.0000502 | No
19/12/2023 | 09:37 | ST15 | SHORT RURAL | Overloads |  | 1.00 | 19.0 | 0.000134 | 0.0000070 | No
19/12/2023 | 09:39 | CD24 | LONG RURAL | Planned |  | 8.00 | 289.0 | 0.016592 | 0.0000574 | No
19/12/2023 | 10:01 | WK41 | SHORT RURAL | Asset failure | LV | 9.33 | 357.0 | 0.023442 | 0.0000657 | No
19/12/2023 | 10:03 | KI54 | LONG RURAL | Planned |  | 10.00 | 169.0 | 0.012128 | 0.0000718 | No
19/12/2023 | 10:32 | MB123 | LONG RURAL | Planned |  | 76.00 | 151.0 | 0.082356 | 0.0005454 | No
19/12/2023 | 11:17 | PL803A | URBAN | Asset failure | LV | 9.67 | 411.0 | 0.006125 | 0.0000149 | No
19/12/2023 | 11:47 | HH341D | URBAN | Animal | Animal impact | 815.00 | 80.0 | 0.100522 | 0.0012565 | No
19/12/2023 | 11:57 | HH341C | URBAN | Asset failure | LV | 17.67 | 142.0 | 0.003868 | 0.0000272 | No
19/12/2023 | 12:06 | ME347C | URBAN | Weather |  | 1.00 | 603.0 | 0.000930 | 0.0000015 | No
19/12/2023 | 12:10 | NU23 | LONG RURAL | Planned |  | 1.00 | 52.0 | 0.000373 | 0.0000072 | No
19/12/2023 | 12:19 | SM374E | URBAN | Asset failure | LV | 37.00 | 150.1 | 0.008563 | 0.0000570 | No
19/12/2023 | 13:02 | MV54 | SHORT RURAL | Asset failure | HV | 5.00 | 151.0 | 0.005312 | 0.0000352 | No
19/12/2023 | 13:13 | HH429C | URBAN | Asset failure | LV | 18.67 | 100.0 | 0.002878 | 0.0000288 | No
19/12/2023 | 13:27 | G23 | LONG RURAL | Asset failure | HV | 2.00 | 28.0 | 0.000402 | 0.0000144 | No
19/12/2023 | 13:45 | NL115B | URBAN | Asset failure | HV | 15.00 | 486.0 | 0.011239 | 0.0000231 | No
19/12/2023 | 14:05 | HH386E | URBAN | Asset failure | LV | 1.00 | 155.0 | 0.000239 | 0.0000015 | No
19/12/2023 | 15:44 | EL20 | URBAN | Third Party | Vehicle impact | 7.00 | 120.0 | 0.001295 | 0.0000108 | No
19/12/2023 | 16:05 | NL760C | URBAN | Overloads |  | 1.00 | 429.0 | 0.000661 | 0.0000015 | No
19/12/2023 | 16:12 | AP425C | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | No
19/12/2023 | 16:36 | AP226E | URBAN | Asset failure | LV | 1.00 | 318.0 | 0.000490 | 0.0000015 | No
19/12/2023 | 16:37 | SM350A | URBAN | Asset failure | LV | 1.00 | 351.0 | 0.000541 | 0.0000015 | No
19/12/2023 | 17:08 | SM374B | URBAN | Asset failure | LV | 1.00 | 252.0 | 0.000389 | 0.0000015 | No
19/12/2023 | 18:24 | ME231A | URBAN | Asset failure | LV | 93.00 | 23.0 | 0.003298 | 0.0001434 | No
19/12/2023 | 18:35 | AP372F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 302.00 | 45.0 | 0.020952 | 0.0004656 | No
19/12/2023 | 18:38 | SG14 | SHORT RURAL | Overloads |  | 1.00 | 914.0 | 0.006430 | 0.0000070 | No
19/12/2023 | 18:42 | HH428B | URBAN | Third Party | Other | 1.00 | 47.0 | 0.000072 | 0.0000015 | No
19/12/2023 | 18:58 | HH428C | URBAN | Third Party | Other | 1.00 | 37.0 | 0.000057 | 0.0000015 | No
19/12/2023 | 19:21 | SM411F | URBAN | Asset failure | LV | 1.00 | 356.0 | 0.000549 | 0.0000015 | No
19/12/2023 | 19:47 | CM02 | LONG RURAL | Asset failure | HV | 9.00 | 79.0 | 0.005102 | 0.0000646 | No
19/12/2023 | 21:34 | HH341C | URBAN | Asset failure | LV | 67.00 | 40.0 | 0.004132 | 0.0001033 | No
19/12/2023 | 23:01 | CBD353M | CBD | Planned |  | 32.00 | 1.0 | 0.004623 | 0.0046233 | No
19/12/2023 | 23:04 | HH522C | URBAN | Overloads |  | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
19/12/2023 | 23:08 | ME131D | URBAN | Asset failure | LV | 1.00 | 307.0 | 0.000473 | 0.0000015 | No
19/12/2023 | 23:16 | CBD367P | CBD | Planned |  | 2.00 | 1.0 | 0.000289 | 0.0002890 | No
20/12/2023 | 00:55 | SA36 | URBAN | Asset failure | HV | 130.00 | 3.5 | 0.000703 | 0.0002004 | No
20/12/2023 | 02:45 | PA07 | LONG RURAL | Asset failure | LV | 1.00 | 95.0 | 0.000682 | 0.0000072 | No
20/12/2023 | 04:09 | EL07 | URBAN | Overloads |  | 1.00 | 351.0 | 0.000541 | 0.0000015 | No
20/12/2023 | 04:35 | MV22 | SHORT RURAL | Animal | Animal impact | 59.67 | 176.2 | 0.073950 | 0.0004198 | No
20/12/2023 | 07:31 | AP365F | URBAN | Asset failure | LV | 1.00 | 1,174.0 | 0.001810 | 0.0000015 | No
20/12/2023 | 08:10 | PP01 | URBAN | Planned |  | 2.00 | 1,523.0 | 0.004696 | 0.0000031 | No
20/12/2023 | 08:11 | AP146C | URBAN | Planned |  | 188.00 | 193.7 | 0.056141 | 0.0002898 | No
20/12/2023 | 08:51 | MV64 | SHORT RURAL | Planned |  | 491.00 | 142.0 | 0.490528 | 0.0034544 | No
20/12/2023 | 08:59 | GA22 | SHORT RURAL | Planned |  | 2.00 | 164.0 | 0.002308 | 0.0000141 | No
20/12/2023 | 09:00 | SD54300 | LONG RURAL | Planned |  | 1,949.00 | 4.0 | 0.056614 | 0.0139867 | No
20/12/2023 | 09:04 | KI53 | LONG RURAL | Planned |  | 5.00 | 94.0 | 0.003373 | 0.0000359 | No
20/12/2023 | 09:05 | HH145C | URBAN | Planned |  | 68.00 | 654.0 | 0.068565 | 0.0001048 | No
20/12/2023 | 09:08 | SG13 | SHORT RURAL | Planned |  | 82.00 | 259.6 | 0.149757 | 0.0005769 | No
20/12/2023 | 09:23 | AP355C | URBAN | Planned |  | 55.00 | 388.0 | 0.032901 | 0.0000848 | No
20/12/2023 | 09:29 | HH428B | URBAN | Planned |  | 13.00 | 30.0 | 0.000601 | 0.0000200 | No
20/12/2023 | 09:30 | EL01R | URBAN | Planned |  | 670.00 | 13.3 | 0.013749 | 0.0010330 | No
20/12/2023 | 09:38 | SG09 | SHORT RURAL | Planned |  | 96.00 | 263.1 | 0.177724 | 0.0006754 | No
20/12/2023 | 09:47 | WHY06 | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
20/12/2023 | 09:55 | SM349A | URBAN | Asset failure | LV | 15.00 | 48.0 | 0.001110 | 0.0000231 | No
20/12/2023 | 10:04 | AP424E | URBAN | Unknown | Unknown | 4.67 | 127.0 | 0.000914 | 0.0000072 | No
20/12/2023 | 10:13 | VH18 | SHORT RURAL | Planned |  | 1.00 | 228.0 | 0.001604 | 0.0000070 | No
20/12/2023 | 10:28 | HH102D | URBAN | Asset failure | LV | 25.00 | 122.0 | 0.004702 | 0.0000385 | No
20/12/2023 | 10:33 | SD40102 | LONG RURAL | Planned |  | 1.00 | 25.0 | 0.000179 | 0.0000072 | No
20/12/2023 | 10:47 | MB21 | URBAN | Unknown | Unknown | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
20/12/2023 | 12:19 | MB72 | LONG RURAL | Unknown | Unknown | 261.00 | 126.0 | 0.235979 | 0.0018730 | No
20/12/2023 | 12:30 | ST22 | SHORT RURAL | Other |  | 16.00 | 189.0 | 0.021275 | 0.0001126 | No
20/12/2023 | 14:23 | AP149E | URBAN | Asset failure | LV | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
20/12/2023 | 14:34 | HH118A | URBAN | Asset failure | LV | 11.67 | 197.0 | 0.003543 | 0.0000180 | No
20/12/2023 | 15:33 | LM41 | LONG RURAL | Third Party | Vehicle impact | 387.00 | 339.7 | 0.943415 | 0.0027772 | No
20/12/2023 | 15:33 | LM41 | LONG RURAL | Third Party | Vehicle impact | 484.00 | 262.8 | 0.912757 | 0.0034733 | No
20/12/2023 | 16:21 | KA02 | SHORT RURAL | Asset failure | LV | 1.00 | 161.0 | 0.001133 | 0.0000070 | No
20/12/2023 | 16:39 | LX21 | SHORT RURAL | Unknown | Unknown | 44.00 | 124.1 | 0.038421 | 0.0003096 | No
20/12/2023 | 17:45 | NL111B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 50.00 | 61.0 | 0.004702 | 0.0000771 | No
20/12/2023 | 18:05 | YK21 | LONG RURAL | Weather |  | 1.00 | 1,132.0 | 0.008124 | 0.0000072 | No
20/12/2023 | 18:29 | AP149E | URBAN | Unknown | Unknown | 85.00 | 185.0 | 0.024244 | 0.0001310 | No
20/12/2023 | 18:33 | WK43 | SHORT RURAL | Weather |  | 370.00 | 308.1 | 0.802109 | 0.0026031 | No
20/12/2023 | 20:01 | AP424E | URBAN | Third Party | Dig-in | 14.00 | 311.0 | 0.006713 | 0.0000216 | No
20/12/2023 | 20:32 | SA32 | URBAN | Asset failure | LV | 17.00 | 269.0 | 0.007050 | 0.0000262 | No
20/12/2023 | 20:43 | SA14 | URBAN | Asset failure | LV | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
20/12/2023 | 21:35 | SA16 | URBAN | Asset failure | LV | 113.00 | 102.7 | 0.017884 | 0.0001742 | No
21/12/2023 | 00:10 | WHY06 | URBAN | Asset failure | HV | 356.67 | 70.0 | 0.038492 | 0.0005499 | No
21/12/2023 | 01:34 | KA07 | LONG RURAL | Unknown | Unknown | 71.00 | 282.2 | 0.143806 | 0.0005095 | No
21/12/2023 | 02:02 | CBD367P | CBD | Planned |  | 2.00 | 1.0 | 0.000289 | 0.0002890 | No
21/12/2023 | 02:05 | SA32 | URBAN | Asset failure | LV | 2.00 | 155.0 | 0.000478 | 0.0000031 | No
21/12/2023 | 02:14 | CBD353M | CBD | Planned |  | 32.00 | 1.0 | 0.004623 | 0.0046233 | No
21/12/2023 | 03:48 | HH121E | URBAN | Unknown | Unknown | 100.00 | 252.0 | 0.038850 | 0.0001542 | No
21/12/2023 | 07:38 | M92 | LONG RURAL | Unknown | Unknown | 6.00 | 648.0 | 0.027902 | 0.0000431 | No
21/12/2023 | 08:20 | GA26 | URBAN | Vegetation | Grow-in - NSP responsibility | 20.00 | 45.3 | 0.001397 | 0.0000308 | No
21/12/2023 | 08:23 | AP146C | URBAN | Planned |  | 124.00 | 186.0 | 0.035554 | 0.0001912 | No
21/12/2023 | 08:35 | KA03 | LONG RURAL | Asset failure | LV | 23.00 | 101.0 | 0.016671 | 0.0001651 | No
21/12/2023 | 08:44 | GU35 | LONG RURAL | Planned |  | 19.00 | 381.0 | 0.051949 | 0.0001364 | No
21/12/2023 | 09:02 | GA22 | SHORT RURAL | Planned |  | 28.00 | 237.0 | 0.046688 | 0.0001970 | No
21/12/2023 | 09:17 | HH432B | URBAN | Asset failure | LV | 1.00 | 257.0 | 0.000396 | 0.0000015 | No
21/12/2023 | 09:17 | NL115A | URBAN | Planned |  | 117.00 | 333.0 | 0.060065 | 0.0001804 | No
21/12/2023 | 09:30 | HH177G | URBAN | Planned |  | 81.00 | 310.9 | 0.038823 | 0.0001249 | No
21/12/2023 | 09:32 | SD36400 | LONG RURAL | Unknown | Unknown | 1.00 | 163.0 | 0.001170 | 0.0000072 | No
21/12/2023 | 09:35 | NL760B | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
21/12/2023 | 09:41 | NL115A | URBAN | Planned |  | 46.00 | 318.9 | 0.022618 | 0.0000709 | No
21/12/2023 | 10:02 | YK01 | SHORT RURAL | Weather |  | 54.00 | 8.0 | 0.003039 | 0.0003799 | No
21/12/2023 | 10:16 | KA03 | LONG RURAL | Asset failure | LV | 13.00 | 119.0 | 0.011102 | 0.0000933 | No
21/12/2023 | 10:26 | WK11 | SHORT RURAL | Planned |  | 23.00 | 222.3 | 0.035965 | 0.0001618 | No
21/12/2023 | 13:03 | LX21 | SHORT RURAL | Asset failure | LV | 2.00 | 332.0 | 0.004672 | 0.0000141 | No
21/12/2023 | 13:17 | M92 | LONG RURAL | Animal | Animal impact | 418.00 | 264.4 | 0.793099 | 0.0029997 | No
21/12/2023 | 13:27 | MTB14 | SHORT RURAL | Planned |  | 153.00 | 33.0 | 0.035515 | 0.0010764 | No
21/12/2023 | 13:27 | MTB14 | SHORT RURAL | Unknown | Unknown | 1.00 | 176.0 | 0.001238 | 0.0000070 | No
21/12/2023 | 13:37 | BM41 | SHORT RURAL | Third Party | Vehicle impact | 68.00 | 151.0 | 0.072240 | 0.0004784 | No
21/12/2023 | 14:42 | BM56 | SHORT RURAL | Animal | Animal impact | 46.00 | 150.0 | 0.048545 | 0.0003236 | No
21/12/2023 | 15:42 | BU06 | LONG RURAL | Weather |  | 1.00 | 2,701.0 | 0.019383 | 0.0000072 | No
21/12/2023 | 16:57 | SD44400 | SHORT RURAL | Third Party | Vehicle impact | 65.00 | 247.0 | 0.112955 | 0.0004573 | No
21/12/2023 | 17:18 | LX41 | SHORT RURAL | Asset failure | LV | 1.00 | 119.0 | 0.000837 | 0.0000070 | No
21/12/2023 | 17:36 | HH428F | URBAN | Asset failure | LV | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
21/12/2023 | 18:51 | HH409D | URBAN | Asset failure | LV | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
21/12/2023 | 21:06 | KA07 | LONG RURAL | Weather |  | 46.00 | 180.0 | 0.059420 | 0.0003301 | No
21/12/2023 | 21:28 | EL10 | URBAN | Unknown | Unknown | 14.00 | 126.0 | 0.002720 | 0.0000216 | No
21/12/2023 | 22:20 | AP227D | URBAN | Asset failure | LV | 43.00 | 102.6 | 0.006801 | 0.0000663 | No
21/12/2023 | 23:26 | KA07 | LONG RURAL | Weather |  | 25.00 | 35.0 | 0.006279 | 0.0001794 | No
22/12/2023 | 02:57 | G13 | LONG RURAL | Unknown | Unknown | 102.00 | 332.3 | 0.243213 | 0.0007320 | No
22/12/2023 | 04:33 | MI03 | LONG RURAL | Unknown | Unknown | 99.00 | 242.8 | 0.172483 | 0.0007105 | No
22/12/2023 | 08:32 | SB22 | LONG RURAL | Planned |  | 2.00 | 193.0 | 0.002770 | 0.0000144 | No
22/12/2023 | 08:40 | LX75 | LONG RURAL | Third Party | Vehicle impact | 49.00 | 186.0 | 0.065412 | 0.0003516 | No
22/12/2023 | 09:03 | KI52 | LONG RURAL | Planned |  | 11.00 | 132.0 | 0.010420 | 0.0000789 | No
22/12/2023 | 10:12 | NA34 | LONG RURAL | Unknown | Unknown | 9.00 | 158.0 | 0.010205 | 0.0000646 | No
22/12/2023 | 11:27 | HH409F | URBAN | Asset failure | LV | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
22/12/2023 | 12:14 | MV64 | SHORT RURAL | Overloads |  | 1.00 | 246.0 | 0.001731 | 0.0000070 | No
22/12/2023 | 12:15 | MI08 | LONG RURAL | Asset failure | LV | 1.00 | 72.0 | 0.000517 | 0.0000072 | No
22/12/2023 | 12:20 | WK11 | SHORT RURAL | Overloads |  | 1.00 | 278.0 | 0.001956 | 0.0000070 | No
22/12/2023 | 13:03 | HH102A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 4.00 | 179.0 | 0.001104 | 0.0000062 | No
22/12/2023 | 14:30 | NU15 | LONG RURAL | Unknown | Unknown | 2.00 | 97.0 | 0.001392 | 0.0000144 | No
22/12/2023 | 15:15 | SG12 | SHORT RURAL | Asset failure | LV | 5.00 | 65.0 | 0.002287 | 0.0000352 | No
22/12/2023 | 18:25 | HH121C | URBAN | Overloads |  | 1.00 | 184.0 | 0.000284 | 0.0000015 | No
22/12/2023 | 21:33 | MTB53 | LONG RURAL | Asset failure | LV | 1.00 | 169.0 | 0.001213 | 0.0000072 | No
22/12/2023 | 21:33 | GA02 | SHORT RURAL | Unknown | Unknown | 2.00 | 160.0 | 0.002251 | 0.0000141 | No
23/12/2023 | 00:21 | MG05 | LONG RURAL | Asset failure | LV | 1.00 | 155.0 | 0.001112 | 0.0000072 | No
23/12/2023 | 00:59 | AP425A | URBAN | Asset failure | LV | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
23/12/2023 | 06:16 | MT14 | SHORT RURAL | Animal | Animal impact | 18.00 | 257.0 | 0.032546 | 0.0001266 | No
23/12/2023 | 07:03 | SA18 | URBAN | Asset failure | LV | 1.00 | 360.0 | 0.000555 | 0.0000015 | No
23/12/2023 | 07:58 | NU22 | LONG RURAL | Unknown | Unknown | 2.00 | 225.0 | 0.003229 | 0.0000144 | No
23/12/2023 | 08:06 | AP829K | URBAN | Planned |  | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
23/12/2023 | 08:42 | MV64 | SHORT RURAL | Asset failure | LV | 21.67 | 278.0 | 0.042377 | 0.0001524 | No
23/12/2023 | 11:24 | HH121E | URBAN | Asset failure | LV | 2.00 | 259.0 | 0.000799 | 0.0000031 | No
23/12/2023 | 11:32 | W29 | LONG RURAL | Weather |  | 14.00 | 311.0 | 0.031246 | 0.0001005 | No
23/12/2023 | 11:50 | PP03 | URBAN | Asset failure | LV | 14.00 | 36.6 | 0.000791 | 0.0000216 | No
23/12/2023 | 12:10 | MB33 | LONG RURAL | Asset failure | HV | 17.00 | 623.3 | 0.076040 | 0.0001220 | No
23/12/2023 | 12:39 | SM411A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 56.00 | 333.0 | 0.028751 | 0.0000863 | No
23/12/2023 | 12:43 | HH428F | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
23/12/2023 | 13:33 | NA09 | LONG RURAL | Asset failure | HV | 812.00 | 50.0 | 0.291359 | 0.0058272 | No
23/12/2023 | 15:37 | HH496G | URBAN | Overloads |  | 4.00 | 62.0 | 0.000382 | 0.0000062 | No
23/12/2023 | 19:07 | SM411A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
23/12/2023 | 21:47 | MB12 | SHORT RURAL | Unknown | Unknown | 1.00 | 973.0 | 0.006846 | 0.0000070 | No
23/12/2023 | 23:08 | GU32 | LONG RURAL | Animal | Animal impact | 1,073.00 | 239.0 | 1.840477 | 0.0077002 | No
24/12/2023 | 00:28 | ST36 | LONG RURAL | Asset failure | HV | 52.33 | 156.0 | 0.058588 | 0.0003756 | No
24/12/2023 | 00:47 | MTB61 | SHORT RURAL | Animal | Animal impact | 194.00 | 73.0 | 0.099637 | 0.0013649 | No
24/12/2023 | 04:07 | HH409F | URBAN | Animal | Animal impact | 160.67 | 98.0 | 0.024275 | 0.0002477 | No
24/12/2023 | 08:46 | HH496A | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
24/12/2023 | 11:20 | M61 | LONG RURAL | Weather |  | 4.00 | 35.0 | 0.001005 | 0.0000287 | No
24/12/2023 | 11:21 | EL20 | URBAN | Animal | Animal impact | 1.00 | 226.0 | 0.000348 | 0.0000015 | No
24/12/2023 | 11:31 | SD44200 | SHORT RURAL | Asset failure | Subtransmission | 693.00 | 64.6 | 0.314803 | 0.0048756 | No
24/12/2023 | 11:48 | NL451C | URBAN | Third Party | Other | 11.33 | 234.0 | 0.004089 | 0.0000175 | No
24/12/2023 | 12:05 | HH177D | URBAN | Asset failure | LV | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
24/12/2023 | 12:13 | NL210B | URBAN | Overloads |  | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
24/12/2023 | 12:25 | WK11 | SHORT RURAL | Overloads |  | 1.00 | 257.0 | 0.001808 | 0.0000070 | No
24/12/2023 | 12:34 | AP365F | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
24/12/2023 | 12:34 | AP365F | URBAN | Asset failure | LV | 1.00 | 162.0 | 0.000250 | 0.0000015 | No
24/12/2023 | 12:48 | HH177E | URBAN | Asset failure | LV | 1.00 | 741.0 | 0.001142 | 0.0000015 | No
24/12/2023 | 13:22 | SA11 | URBAN | Unknown | Unknown | 36.00 | 273.0 | 0.015152 | 0.0000555 | No
24/12/2023 | 13:41 | BT10 | LONG RURAL | Asset failure | HV | 34.00 | 183.0 | 0.044651 | 0.0002440 | No
24/12/2023 | 14:26 | NA12 | LONG RURAL | Weather |  | 60.00 | 227.0 | 0.097742 | 0.0004306 | No
24/12/2023 | 14:55 | SM410B | URBAN | Asset failure | LV | 86.00 | 607.0 | 0.080483 | 0.0001326 | No
24/12/2023 | 15:04 | G13 | LONG RURAL | Weather |  | 53.00 | 284.0 | 0.108018 | 0.0003803 | No
24/12/2023 | 15:10 | G11 | LONG RURAL | Weather |  | 57.00 | 194.1 | 0.079413 | 0.0004091 | No
24/12/2023 | 15:22 | R32 | LONG RURAL | Unknown | Unknown | 78.00 | 217.1 | 0.121524 | 0.0005598 | No
24/12/2023 | 15:35 | NA05 | LONG RURAL | Weather |  | 2.00 | 215.0 | 0.003086 | 0.0000144 | No
24/12/2023 | 15:48 | NA04 | LONG RURAL | Weather |  | 1.00 | 223.0 | 0.001600 | 0.0000072 | No
24/12/2023 | 16:00 | BT04 | LONG RURAL | Weather |  | 9.33 | 133.7 | 0.008956 | 0.0000670 | No
24/12/2023 | 16:14 | ME231B | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
24/12/2023 | 16:32 | LM31 | LONG RURAL | Weather |  | 79.00 | 1,506.2 | 0.853890 | 0.0005669 | No
24/12/2023 | 16:37 | MB63 | LONG RURAL | Asset failure | HV | 290.00 | 335.9 | 0.698996 | 0.0020811 | No
24/12/2023 | 16:48 | HH341C | URBAN | Unknown | Unknown | 8.00 | 136.0 | 0.001677 | 0.0000123 | No
24/12/2023 | 16:51 | SD40101 | LONG RURAL | Network business | Switching and protection error | 974.00 | 68.0 | 0.475159 | 0.0069897 | No
24/12/2023 | 17:15 | AP372B | URBAN | Unknown | Unknown | 1,215.00 | 132.0 | 0.247206 | 0.0018732 | No
24/12/2023 | 17:19 | MV64 | SHORT RURAL | Asset failure | HV | 1,038.00 | 88.1 | 0.643564 | 0.0073028 | No
24/12/2023 | 17:20 | MB123 | LONG RURAL | Unknown | Unknown | 17.00 | 1,500.0 | 0.182996 | 0.0001220 | No
24/12/2023 | 17:22 | LM33 | LONG RURAL | Weather |  | 65.00 | 1,620.8 | 0.756055 | 0.0004665 | No
24/12/2023 | 17:39 | AP149D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
24/12/2023 | 17:40 | HH386C | URBAN | Asset failure | LV | 1.00 | 370.0 | 0.000570 | 0.0000015 | No
24/12/2023 | 18:07 | SM349F | URBAN | Asset failure | LV | 22.67 | 191.0 | 0.006675 | 0.0000349 | No
24/12/2023 | 18:13 | M22 | LONG RURAL | Weather |  | 68.00 | 937.0 | 0.457233 | 0.0004880 | No
24/12/2023 | 18:14 | YK07 | LONG RURAL | Asset failure | LV | 1.00 | 168.0 | 0.001206 | 0.0000072 | No
24/12/2023 | 18:17 | VH10 | SHORT RURAL | Overloads |  | 1.00 | 333.0 | 0.002343 | 0.0000070 | No
24/12/2023 | 19:39 | NA05 | LONG RURAL | Weather |  | 14.67 | 179.0 | 0.018840 | 0.0001053 | No
24/12/2023 | 19:41 | LM32 | LONG RURAL | Weather |  | 72.00 | 2,893.0 | 1.494815 | 0.0005167 | No
24/12/2023 | 19:44 | AP372B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
24/12/2023 | 19:59 | VH22 | SHORT RURAL | Vegetation | Grow-in - NSP responsibility | 75.00 | 254.1 | 0.134096 | 0.0005277 | No
24/12/2023 | 20:02 | MB82 | LONG RURAL | Asset failure | LV | 1.00 | 100.0 | 0.000718 | 0.0000072 | No
24/12/2023 | 20:22 | EL260C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,056.00 | 139.0 | 0.226305 | 0.0016281 | No
24/12/2023 | 20:45 | EL10 | URBAN | Asset failure | LV | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
24/12/2023 | 20:57 | NL111Q | URBAN | Asset failure | LV | 1.00 | 383.0 | 0.000590 | 0.0000015 | No
24/12/2023 | 21:12 | MTB41 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 343.0 | 0.007240 | 0.0000211 | No
24/12/2023 | 21:18 | NL111Q | URBAN | Asset failure | LV | 17.00 | 314.0 | 0.008230 | 0.0000262 | No
24/12/2023 | 21:19 | NL111Q | URBAN | Asset failure | LV | 12.00 | 310.2 | 0.005738 | 0.0000185 | No
24/12/2023 | 21:30 | NL760B | URBAN | Asset failure | LV | 1.00 | 389.0 | 0.000600 | 0.0000015 | No
24/12/2023 | 21:54 | NL451E | URBAN | Asset failure | LV | 3.00 | 248.0 | 0.001147 | 0.0000046 | No
24/12/2023 | 22:48 | AP372F | URBAN | Asset failure | LV | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
25/12/2023 | 00:02 | CBD412M | URBAN | Unknown | Unknown | 7.00 | 87.0 | 0.000939 | 0.0000108 | No
25/12/2023 | 01:22 | VH15 | SHORT RURAL | Asset failure | HV | 11.00 | 53.0 | 0.004102 | 0.0000774 | No
25/12/2023 | 01:40 | R20 | LONG RURAL | Weather |  | 668.00 | 644.5 | 3.089812 | 0.0047938 | No
25/12/2023 | 03:58 | EL10 | URBAN | Asset failure | LV | 1.00 | 711.0 | 0.001096 | 0.0000015 | No
25/12/2023 | 04:28 | SA33 | URBAN | Unknown | Unknown | 33.33 | 229.0 | 0.011769 | 0.0000514 | No
25/12/2023 | 04:58 | HH496G | URBAN | Asset failure | LV | 12.00 | 781.3 | 0.014455 | 0.0000185 | No
25/12/2023 | 05:40 | SD48100 | SHORT RURAL | Unknown | Unknown | 611.00 | 68.0 | 0.292311 | 0.0042987 | No
25/12/2023 | 05:56 | MI21 | LONG RURAL | Unknown | Unknown | 2.00 | 423.0 | 0.006071 | 0.0000144 | No
25/12/2023 | 06:30 | R32 | LONG RURAL | Unknown | Unknown | 78.00 | 288.0 | 0.161209 | 0.0005598 | No
25/12/2023 | 06:33 | SM126C | URBAN | Unknown | Unknown | 178.00 | 264.0 | 0.072450 | 0.0002744 | No
25/12/2023 | 06:44 | SM126C | URBAN | Unknown | Unknown | 1.00 | 302.0 | 0.000466 | 0.0000015 | No
25/12/2023 | 08:39 | ST43 | SHORT RURAL | Asset failure | HV | 8.00 | 296.3 | 0.016674 | 0.0000563 | No
25/12/2023 | 09:34 | SM374A | URBAN | Asset failure | LV | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
25/12/2023 | 09:43 | NL210A | URBAN | Unknown | Unknown | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
25/12/2023 | 10:13 | ME200E | URBAN | Asset failure | LV | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
25/12/2023 | 10:35 | AP125C | URBAN | Asset failure | LV | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
25/12/2023 | 11:56 | AP355A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,090.00 | 139.0 | 0.447895 | 0.0032223 | No
25/12/2023 | 13:28 | HH432C | URBAN | Asset failure | LV | 35.00 | 75.0 | 0.004047 | 0.0000540 | No
25/12/2023 | 14:04 | MI20 | LONG RURAL | Asset failure | LV | 1.00 | 212.0 | 0.001521 | 0.0000072 | No
25/12/2023 | 14:25 | HH341D | URBAN | Animal | Animal impact | 392.67 | 7.7 | 0.004680 | 0.0006054 | No
25/12/2023 | 15:15 | EL02 | URBAN | Third Party | Vehicle impact | 107.00 | 244.0 | 0.040252 | 0.0001650 | No
25/12/2023 | 15:49 | MV54 | SHORT RURAL | Unknown | Unknown | 1.00 | 268.0 | 0.001886 | 0.0000070 | No
25/12/2023 | 16:47 | NL210D | URBAN | Overloads |  | 1.00 | 366.0 | 0.000564 | 0.0000015 | No
25/12/2023 | 17:34 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 163.0 | 0.001147 | 0.0000070 | No
25/12/2023 | 18:00 | R32 | LONG RURAL | Weather |  | 78.00 | 305.8 | 0.171148 | 0.0005598 | No
25/12/2023 | 18:15 | EL07 | URBAN | Asset failure | LV | 82.00 | 467.2 | 0.059065 | 0.0001264 | No
25/12/2023 | 18:18 | BM56 | SHORT RURAL | Asset failure | LV | 1.00 | 127.0 | 0.000894 | 0.0000070 | No
25/12/2023 | 18:44 | EL03 | URBAN | Unknown | Unknown | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
25/12/2023 | 18:55 | MB22 | SHORT RURAL | Asset failure | LV | 1.00 | 1,835.0 | 0.012910 | 0.0000070 | No
25/12/2023 | 19:30 | BM57 | SHORT RURAL | Asset failure | HV | 31.33 | 27.0 | 0.005952 | 0.0002204 | No
25/12/2023 | 20:26 | BM52 | URBAN | Asset failure | LV | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
25/12/2023 | 20:33 | GU31 | LONG RURAL | Overloads |  | 1.00 | 313.0 | 0.002246 | 0.0000072 | No
25/12/2023 | 21:42 | VH18 | SHORT RURAL | Unknown | Unknown | 78.00 | 694.4 | 0.381049 | 0.0005488 | No
25/12/2023 | 22:35 | VH19 | SHORT RURAL | Asset failure | LV | 4.33 | 318.8 | 0.009718 | 0.0000305 | No
26/12/2023 | 00:19 | HH121B | URBAN | Asset failure | LV | 2.00 | 153.0 | 0.000472 | 0.0000031 | No
26/12/2023 | 02:19 | AP365E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 170.0 | 0.000524 | 0.0000031 | No
26/12/2023 | 05:59 | AP139D | URBAN | Unknown | Unknown | 1,356.33 | 12.8 | 0.026682 | 0.0020911 | No
26/12/2023 | 06:55 | SM179C | URBAN | Asset failure | LV | 6.00 | 97.0 | 0.000897 | 0.0000093 | No
26/12/2023 | 07:06 | SA32 | URBAN | Overloads |  | 3.33 | 286.0 | 0.001470 | 0.0000051 | No
26/12/2023 | 07:40 | KA28 | LONG RURAL | Weather |  | 7.00 | 460.0 | 0.023108 | 0.0000502 | No
26/12/2023 | 08:16 | KA01 | SHORT RURAL | Asset failure | LV | 12.00 | 195.0 | 0.016463 | 0.0000844 | No
26/12/2023 | 08:19 | SA17 | URBAN | Asset failure | HV | 47.00 | 883.9 | 0.064046 | 0.0000725 | No
26/12/2023 | 08:35 | ME131C | URBAN | Overloads |  | 1.00 | 689.0 | 0.001062 | 0.0000015 | No
26/12/2023 | 08:59 | LM56 | LONG RURAL | Unknown | Unknown | 1.00 | 834.0 | 0.005985 | 0.0000072 | No
26/12/2023 | 08:59 | LM56 | LONG RURAL | Unknown | Unknown | 17.00 | 834.0 | 0.101746 | 0.0001220 | No
26/12/2023 | 09:26 | MG11 | SHORT RURAL | Asset failure | LV | 1.00 | 76.0 | 0.000535 | 0.0000070 | No
26/12/2023 | 10:11 | MV54 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,307.0 | 0.009195 | 0.0000070 | No
26/12/2023 | 10:11 | MG17 | LONG RURAL | Asset failure | LV | 1.00 | 170.0 | 0.001220 | 0.0000072 | No
26/12/2023 | 10:43 | SA16 | URBAN | Asset failure | LV | 1.00 | 428.0 | 0.000660 | 0.0000015 | No
26/12/2023 | 11:10 | AP424F | URBAN | Third Party | Vehicle impact | 1,033.00 | 234.1 | 0.372822 | 0.0015926 | No
26/12/2023 | 11:10 | HH386B | URBAN | Asset failure | LV | 90.00 | 63.0 | 0.008742 | 0.0001388 | No
26/12/2023 | 11:37 | SG09 | SHORT RURAL | Asset failure | LV | 1.00 | 595.0 | 0.004186 | 0.0000070 | No
26/12/2023 | 12:11 | SD35300 | LONG RURAL | Animal | Animal impact | 1,302.00 | 291.0 | 2.718982 | 0.0093436 | No
26/12/2023 | 12:17 | NL760B | URBAN | Asset failure | HV | 3.67 | 265.0 | 0.001498 | 0.0000057 | No
26/12/2023 | 12:40 | AP227A | URBAN | Asset failure | LV | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
26/12/2023 | 12:40 | SM411C | URBAN | Overloads |  | 1.00 | 308.0 | 0.000475 | 0.0000015 | No
26/12/2023 | 13:52 | EL10 | URBAN | Asset failure | LV | 14.00 | 165.0 | 0.003561 | 0.0000216 | No
26/12/2023 | 14:10 | AP214C | URBAN | Unknown | Unknown | 2.00 | 40.0 | 0.000123 | 0.0000031 | No
26/12/2023 | 15:39 | PL10 | LONG RURAL | Asset failure | LV | 1.00 | 333.0 | 0.002390 | 0.0000072 | No
26/12/2023 | 16:02 | ST51 | SHORT RURAL | Unknown | Unknown | 1.00 | 101.0 | 0.000711 | 0.0000070 | No
26/12/2023 | 17:08 | MG45 | URBAN | Overloads |  | 2.00 | 87.0 | 0.000268 | 0.0000031 | No
26/12/2023 | 17:17 | EL25 | URBAN | Asset failure | LV | 18.00 | 336.0 | 0.009325 | 0.0000278 | No
26/12/2023 | 20:41 | EL09 | URBAN | Asset failure | LV | 22.00 | 152.0 | 0.005156 | 0.0000339 | No
26/12/2023 | 21:02 | SA19 | URBAN | Overloads |  | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
26/12/2023 | 22:27 | SM349C | URBAN | Asset failure | LV | 1.00 | 302.0 | 0.000466 | 0.0000015 | No
27/12/2023 | 06:11 | VH18 | SHORT RURAL | Weather |  | 23.00 | 404.3 | 0.065430 | 0.0001618 | No
27/12/2023 | 06:21 | YK24 | LONG RURAL | Unknown | Unknown | 108.00 | 325.1 | 0.251947 | 0.0007750 | No
27/12/2023 | 07:44 | WHY06 | URBAN | Asset failure | LV | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
27/12/2023 | 08:46 | LX48 | SHORT RURAL | Overloads |  | 1.00 | 6.0 | 0.000042 | 0.0000070 | No
27/12/2023 | 08:57 | SD47200 | URBAN | Planned |  | 2.00 | 355.0 | 0.001095 | 0.0000031 | No
27/12/2023 | 09:53 | SM349A | URBAN | Asset failure | LV | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
27/12/2023 | 10:51 | NU05 | SHORT RURAL | Unknown | Unknown | 3.00 | 40.3 | 0.000851 | 0.0000211 | No
27/12/2023 | 11:08 | HH409E | URBAN | Asset failure | LV | 1.00 | 89.0 | 0.000137 | 0.0000015 | No
27/12/2023 | 11:33 | SM216B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 199.0 | 0.000307 | 0.0000015 | No
27/12/2023 | 12:06 | LM61 | LONG RURAL | Asset failure | LV | 1.00 | 479.0 | 0.003437 | 0.0000072 | No
27/12/2023 | 12:15 | NL234B | URBAN | Asset failure | LV | 1.00 | 351.0 | 0.000541 | 0.0000015 | No
27/12/2023 | 12:58 | VH11 | URBAN | Asset failure | LV | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
27/12/2023 | 13:20 | G11 | LONG RURAL | Weather |  | 21.00 | 59.0 | 0.008891 | 0.0001507 | No
27/12/2023 | 13:23 | R21 | LONG RURAL | Asset failure | LV | 1.00 | 283.0 | 0.002031 | 0.0000072 | No
27/12/2023 | 14:27 | MI16 | LONG RURAL | Asset failure | LV | 2.00 | 143.0 | 0.002052 | 0.0000144 | No
27/12/2023 | 14:31 | EL08D | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
27/12/2023 | 15:48 | SA17 | URBAN | Asset failure | LV | 1.00 | 347.0 | 0.000535 | 0.0000015 | No
27/12/2023 | 17:12 | PL803C | URBAN | Overloads |  | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
27/12/2023 | 18:12 | HH409C | URBAN | Asset failure | LV | 56.00 | 177.0 | 0.015282 | 0.0000863 | No
27/12/2023 | 19:18 | SD40800 | LONG RURAL | Planned |  | 938.00 | 3.0 | 0.020194 | 0.0067314 | No
27/12/2023 | 21:24 | HH429C | URBAN | Vegetation | Grow-in - NSP responsibility | 3.33 | 92.0 | 0.000473 | 0.0000051 | No
27/12/2023 | 21:37 | HH522B | URBAN | Asset failure | LV | 1.00 | 60.0 | 0.000093 | 0.0000015 | No
27/12/2023 | 22:33 | HH409D | URBAN | Asset failure | LV | 1.00 | 56.0 | 0.000086 | 0.0000015 | No
28/12/2023 | 03:18 | SSD400 | SHORT RURAL | Weather |  | 269.00 | 521.0 | 0.986017 | 0.0018925 | Yes
28/12/2023 | 05:57 | MI15 | LONG RURAL | Unknown | Unknown | 102.00 | 272.0 | 0.199100 | 0.0007320 | Yes
28/12/2023 | 06:13 | CN42 | LONG RURAL | Asset failure | HV | 26.00 | 546.0 | 0.101875 | 0.0001866 | Yes
28/12/2023 | 06:39 | SM126C | URBAN | Weather |  | 52.33 | 184.0 | 0.014846 | 0.0000807 | Yes
28/12/2023 | 08:16 | CBD412N | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | Yes
28/12/2023 | 10:07 | BM41 | SHORT RURAL | Third Party | Other | 1.00 | 97.0 | 0.000682 | 0.0000070 | Yes
28/12/2023 | 10:29 | CL19 | LONG RURAL | Third Party | Vehicle impact | 77.00 | 220.8 | 0.121990 | 0.0005526 | Yes
28/12/2023 | 12:23 | CV18 | SHORT RURAL | Unknown | Unknown | 58.00 | 188.0 | 0.076715 | 0.0004081 | Yes
28/12/2023 | 12:26 | SA11 | URBAN | Other |  | 10.00 | 120.0 | 0.001850 | 0.0000154 | Yes
28/12/2023 | 12:44 | NL210A | URBAN | Weather |  | 10.00 | 423.0 | 0.006522 | 0.0000154 | Yes
28/12/2023 | 12:47 | CV16 | LONG RURAL | Weather |  | 51.00 | 513.0 | 0.187754 | 0.0003660 | Yes
28/12/2023 | 12:58 | CV15 | LONG RURAL | Weather |  | 58.00 | 887.6 | 0.369423 | 0.0004162 | Yes
28/12/2023 | 13:13 | CM10 | LONG RURAL | Unknown | Unknown | 44.00 | 1,555.0 | 0.491004 | 0.0003158 | Yes
28/12/2023 | 13:25 | NL451A | URBAN | Asset failure | LV | 1.00 | 426.0 | 0.000657 | 0.0000015 | Yes
28/12/2023 | 13:36 | BT02 | LONG RURAL | Asset failure | HV | 1.00 | 24.0 | 0.000172 | 0.0000072 | Yes
28/12/2023 | 14:04 | PL21 | LONG RURAL | Weather |  | 1.00 | 1,504.0 | 0.010793 | 0.0000072 | Yes
28/12/2023 | 14:14 | SD32400 | LONG RURAL | Unknown | Unknown | 71.33 | 112.0 | 0.057334 | 0.0005119 | Yes
28/12/2023 | 14:22 | YK03 | LONG RURAL | Asset failure | LV | 1.00 | 2,750.0 | 0.019735 | 0.0000072 | Yes
28/12/2023 | 14:25 | CM17 | LONG RURAL | Weather |  | 17.00 | 1,742.4 | 0.212570 | 0.0001220 | Yes
28/12/2023 | 14:31 | CM29 | LONG RURAL | Weather |  | 65.00 | 312.0 | 0.145536 | 0.0004665 | Yes
28/12/2023 | 14:32 | PL07 | LONG RURAL | Weather |  | 1.00 | 153.0 | 0.001098 | 0.0000072 | Yes
28/12/2023 | 14:32 | PL07 | URBAN | Weather |  | 59.00 | 153.0 | 0.013917 | 0.0000910 | Yes
28/12/2023 | 14:32 | SA17 | URBAN | Overloads |  | 1.00 | 36.0 | 0.000056 | 0.0000015 | Yes
28/12/2023 | 14:45 | PL24 | LONG RURAL | Weather |  | 30.00 | 514.0 | 0.110659 | 0.0002153 | Yes
28/12/2023 | 14:48 | CM04 | LONG RURAL | Weather |  | 18.00 | 442.0 | 0.057095 | 0.0001292 | Yes
28/12/2023 | 14:53 | CM11 | LONG RURAL | Weather |  | 1.00 | 1,682.0 | 0.012071 | 0.0000072 | Yes
28/12/2023 | 14:58 | CM27 | LONG RURAL | Weather |  | 45.00 | 429.0 | 0.138539 | 0.0003229 | Yes
28/12/2023 | 15:06 | G09 | LONG RURAL | Weather |  | 57.00 | 430.0 | 0.175892 | 0.0004091 | Yes
28/12/2023 | 15:18 | PL11 | LONG RURAL | Unknown | Unknown | 13.00 | 1,399.0 | 0.130516 | 0.0000933 | Yes
28/12/2023 | 15:27 | SD35400 | SHORT RURAL | Weather |  | 185.00 | 262.0 | 0.341010 | 0.0013016 | Yes
28/12/2023 | 15:31 | PL33 | LONG RURAL | Weather |  | 148.00 | 1,238.0 | 1.314876 | 0.0010621 | Yes
28/12/2023 | 15:31 | PL33 | LONG RURAL | Weather |  | 127.00 | 156.0 | 0.142177 | 0.0009114 | Yes
28/12/2023 | 15:31 | YK27 | LONG RURAL | Weather |  | 1.00 | 312.0 | 0.002239 | 0.0000072 | Yes
28/12/2023 | 15:33 | BU08 | LONG RURAL | Weather |  | 47.00 | 3,043.0 | 1.026366 | 0.0003373 | Yes
28/12/2023 | 15:33 | BU08 | LONG RURAL | Weather |  | 1.00 | 8,423.0 | 0.060446 | 0.0000072 | Yes
28/12/2023 | 15:34 | PL22 | LONG RURAL | Weather |  | 13.00 | 1,431.0 | 0.133501 | 0.0000933 | Yes
28/12/2023 | 15:52 | MT14 | SHORT RURAL | Unknown | Unknown | 75.00 | 322.0 | 0.169886 | 0.0005277 | Yes
28/12/2023 | 15:54 | R01 | LONG RURAL | Weather |  | 134.00 | 31.6 | 0.030413 | 0.0009616 | Yes
28/12/2023 | 16:15 | SD34400 | LONG RURAL | Weather |  | 1,063.00 | 117.2 | 0.894006 | 0.0076284 | Yes
28/12/2023 | 16:15 | SD37402 | LONG RURAL | Weather |  | 72.00 | 814.6 | 0.420885 | 0.0005167 | Yes
28/12/2023 | 16:18 | SA744C | URBAN | Unknown | Unknown | 24.00 | 144.0 | 0.005328 | 0.0000370 | Yes
28/12/2023 | 16:22 | PP12 | LONG RURAL | Asset failure | HV | 75.00 | 1,219.2 | 0.656204 | 0.0005382 | Yes
28/12/2023 | 16:23 | EL11 | URBAN | Weather |  | 96.00 | 232.1 | 0.034360 | 0.0001480 | Yes
28/12/2023 | 16:23 | CV31 | LONG RURAL | Weather |  | 54.00 | 1,334.0 | 0.516954 | 0.0003875 | Yes
28/12/2023 | 16:26 | CL12 | LONG RURAL | Weather |  | 89.00 | 968.6 | 0.618664 | 0.0006387 | Yes
28/12/2023 | 16:29 | GU31 | LONG RURAL | Weather |  | 7.00 | 1,500.0 | 0.075351 | 0.0000502 | Yes
28/12/2023 | 16:30 | SD35200 | LONG RURAL | Weather |  | 3,125.00 | 263.8 | 5.916503 | 0.0224260 | Yes
28/12/2023 | 16:30 | SD35200 | URBAN | Weather |  | 5.00 | 133.0 | 0.001025 | 0.0000077 | Yes
28/12/2023 | 16:30 | MT09 | LONG RURAL | Unknown | Unknown | 62.00 | 434.5 | 0.193302 | 0.0004449 | Yes
28/12/2023 | 16:30 | SD35200 | LONG RURAL | Weather |  | 3.00 | 8,293.3 | 0.178547 | 0.0000215 | Yes
28/12/2023 | 16:34 | GA53 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,030.0 | 0.007247 | 0.0000070 | Yes
28/12/2023 | 16:34 | MTB61 | SHORT RURAL | Weather |  | 5.00 | 286.0 | 0.010061 | 0.0000352 | Yes
28/12/2023 | 16:38 | CL05 | LONG RURAL | Weather |  | 321.00 | 16.8 | 0.038645 | 0.0023036 | Yes
28/12/2023 | 16:40 | M71 | LONG RURAL | Asset failure | HV | 1.00 | 210.0 | 0.001507 | 0.0000072 | Yes
28/12/2023 | 16:47 | SG02 | SHORT RURAL | Animal | Animal impact | 7.33 | 142.0 | 0.007326 | 0.0000516 | Yes
28/12/2023 | 16:48 | NU08 | LONG RURAL | Weather |  | 30.00 | 563.0 | 0.121208 | 0.0002153 | Yes
28/12/2023 | 16:49 | NU07 | LONG RURAL | Weather |  | 56.00 | 693.8 | 0.278800 | 0.0004019 | Yes
28/12/2023 | 16:53 | CM12 | LONG RURAL | Weather |  | 15.00 | 1,681.0 | 0.180951 | 0.0001076 | Yes
28/12/2023 | 16:53 | NU15 | LONG RURAL | Weather |  | 1.00 | 501.0 | 0.003595 | 0.0000072 | Yes
28/12/2023 | 16:54 | NU11 | LONG RURAL | Weather |  | 106.00 | 944.4 | 0.718430 | 0.0007607 | Yes
28/12/2023 | 16:54 | GU31 | LONG RURAL | Weather |  | 8.00 | 1,511.0 | 0.086747 | 0.0000574 | Yes
28/12/2023 | 16:58 | SD39400 | SHORT RURAL | Weather |  | 416.00 | 272.0 | 0.796080 | 0.0029268 | Yes
28/12/2023 | 16:59 | NU14 | LONG RURAL | Weather |  | 2.00 | 1,952.0 | 0.028016 | 0.0000144 | Yes
28/12/2023 | 17:01 | NU15 | LONG RURAL | Weather |  | 1.00 | 2,703.0 | 0.019398 | 0.0000072 | Yes
28/12/2023 | 17:03 | R08 | LONG RURAL | Weather |  | 38.00 | 286.0 | 0.077992 | 0.0002727 | Yes
28/12/2023 | 17:06 | SD36400 | LONG RURAL | Unknown | Unknown | 2.00 | 2,442.0 | 0.035049 | 0.0000144 | Yes
28/12/2023 | 17:15 | MT19 | LONG RURAL | Weather |  | 35.00 | 1,718.6 | 0.431671 | 0.0002512 | Yes
28/12/2023 | 17:16 | R31 | SHORT RURAL | Weather |  | 36.00 | 2,516.8 | 0.637444 | 0.0002533 | Yes
28/12/2023 | 17:34 | NU35 | LONG RURAL | Weather |  | 73.00 | 1,668.6 | 0.874120 | 0.0005239 | Yes
28/12/2023 | 17:36 | YK02 | SHORT RURAL | Unknown | Unknown | 23.00 | 254.0 | 0.041101 | 0.0001618 | Yes
28/12/2023 | 17:58 | ME116C | URBAN | Asset failure | LV | 1.00 | 185.0 | 0.000285 | 0.0000015 | Yes
28/12/2023 | 18:05 | SG01 | SHORT RURAL | Weather |  | 1.00 | 106.0 | 0.000746 | 0.0000070 | Yes
28/12/2023 | 18:05 | SD33100 | LONG RURAL | Weather |  | 836.67 | 42.4 | 0.254418 | 0.0060042 | Yes
28/12/2023 | 18:12 | NU22 | LONG RURAL | Weather |  | 40.00 | 246.0 | 0.070615 | 0.0002871 | Yes
28/12/2023 | 18:12 | CL05 | LONG RURAL | Weather |  | 1.00 | 2.0 | 0.000014 | 0.0000072 | Yes
28/12/2023 | 18:15 | NU22 | LONG RURAL | Weather |  | 20.00 | 376.0 | 0.053966 | 0.0001435 | Yes
28/12/2023 | 18:16 | WK33 | SHORT RURAL | Weather |  | 115.00 | 1,304.0 | 1.055042 | 0.0008091 | Yes
28/12/2023 | 18:21 | GA09 | LONG RURAL | Weather |  | 949.00 | 114.2 | 0.778079 | 0.0068103 | Yes
28/12/2023 | 18:21 | KA14 | LONG RURAL | Weather |  | 12.00 | 2,455.0 | 0.211415 | 0.0000861 | Yes
28/12/2023 | 18:33 | NL210A | URBAN | Weather |  | 5.00 | 64.0 | 0.000493 | 0.0000077 | Yes
28/12/2023 | 18:34 | GA15 | SHORT RURAL | Weather |  | 348.00 | 373.7 | 0.914860 | 0.0024484 | Yes
28/12/2023 | 18:37 | SD52300 | LONG RURAL | Weather |  | 3.00 | 406.0 | 0.008741 | 0.0000215 | Yes
28/12/2023 | 18:38 | GU35 | LONG RURAL | Weather |  | 90.00 | 834.5 | 0.538971 | 0.0006459 | Yes
28/12/2023 | 18:39 | R16 | LONG RURAL | Weather |  | 2.00 | 572.0 | 0.008210 | 0.0000144 | Yes
28/12/2023 | 18:44 | CM11 | LONG RURAL | Weather |  | 21.00 | 1,474.4 | 0.222194 | 0.0001507 | Yes
28/12/2023 | 18:46 | WK42 | SHORT RURAL | Weather |  | 82.00 | 231.0 | 0.133266 | 0.0005769 | Yes
28/12/2023 | 18:48 | AP125D | URBAN | Unknown | Unknown | 1.00 | 271.0 | 0.000418 | 0.0000015 | Yes
28/12/2023 | 18:55 | HH177G | URBAN | Unknown | Unknown | 1.00 | 186.0 | 0.000287 | 0.0000015 | Yes
28/12/2023 | 18:55 | GA05 | SHORT RURAL | Weather |  | 36.33 | 302.0 | 0.077198 | 0.0002556 | Yes
28/12/2023 | 19:06 | GU32 | LONG RURAL | Weather |  | 7.00 | 1,488.0 | 0.074749 | 0.0000502 | Yes
28/12/2023 | 19:14 | KA11 | LONG RURAL | Weather |  | 29.00 | 1,765.4 | 0.367414 | 0.0002081 | Yes
28/12/2023 | 19:18 | WK33 | SHORT RURAL | Weather |  | 31.00 | 829.0 | 0.180805 | 0.0002181 | Yes
28/12/2023 | 19:20 | MT12 | LONG RURAL | Weather |  | 24.00 | 364.0 | 0.062692 | 0.0001722 | Yes
28/12/2023 | 19:21 | KA12 | LONG RURAL | Weather |  | 48.00 | 1,117.3 | 0.384881 | 0.0003445 | Yes
28/12/2023 | 19:36 | KA21 | LONG RURAL | Unknown | Unknown | 77.00 | 1,281.0 | 0.707830 | 0.0005526 | Yes
28/12/2023 | 19:44 | HH177G | URBAN | Weather |  | 1.00 | 91.0 | 0.000140 | 0.0000015 | Yes
28/12/2023 | 19:50 | CV23 | LONG RURAL | Weather |  | 69.00 | 988.0 | 0.489225 | 0.0004952 | Yes
28/12/2023 | 19:52 | R29 | LONG RURAL | Weather |  | 82.00 | 1,338.0 | 0.787358 | 0.0005885 | Yes
28/12/2023 | 20:05 | R04 | LONG RURAL | Weather |  | 53.67 | 2,456.4 | 0.946029 | 0.0003851 | Yes
28/12/2023 | 20:07 | VH23 | SHORT RURAL | Asset failure | LV | 17.00 | 140.0 | 0.016744 | 0.0001196 | Yes
28/12/2023 | 20:11 | R05 | LONG RURAL | Weather |  | 30.00 | 1,474.0 | 0.317337 | 0.0002153 | Yes
28/12/2023 | 20:53 | MV22 | SHORT RURAL | Weather |  | 34.00 | 279.0 | 0.066739 | 0.0002392 | Yes
28/12/2023 | 21:02 | CV29 | LONG RURAL | Weather |  | 93.00 | 1,435.9 | 0.958320 | 0.0006674 | Yes
28/12/2023 | 21:38 | GU118 | LONG RURAL | Weather |  | 41.00 | 983.1 | 0.289249 | 0.0002942 | Yes
28/12/2023 | 21:44 | KA08 | LONG RURAL | Weather |  | 60.00 | 768.0 | 0.330700 | 0.0004306 | Yes
28/12/2023 | 21:44 | KA08 | LONG RURAL | Weather |  | 1.00 | 2,426.0 | 0.017410 | 0.0000072 | Yes
28/12/2023 | 21:44 | KA08 | LONG RURAL | Weather |  | 16.00 | 923.1 | 0.105994 | 0.0001148 | Yes
28/12/2023 | 21:46 | W30 | LONG RURAL | Asset failure | HV | 1.00 | 68.0 | 0.000488 | 0.0000072 | Yes
28/12/2023 | 21:48 | R26 | LONG RURAL | Weather |  | 87.00 | 2,261.0 | 1.411634 | 0.0006243 | Yes
28/12/2023 | 21:51 | M44 | LONG RURAL | Weather |  | 56.00 | 853.8 | 0.343107 | 0.0004019 | Yes
28/12/2023 | 21:51 | M44 | LONG RURAL | Weather |  | 55.00 | 386.4 | 0.152519 | 0.0003947 | Yes
28/12/2023 | 21:54 | LM14 | LONG RURAL | Weather |  | 45.00 | 311.0 | 0.100433 | 0.0003229 | Yes
28/12/2023 | 21:56 | NU10 | LONG RURAL | Weather |  | 98.00 | 218.0 | 0.153315 | 0.0007033 | Yes
28/12/2023 | 21:58 | CL13 | LONG RURAL | Weather |  | 58.00 | 2,477.3 | 1.031117 | 0.0004162 | Yes
28/12/2023 | 22:04 | SD36101 | SHORT RURAL | Weather |  | 177.00 | 199.0 | 0.247790 | 0.0012453 | Yes
28/12/2023 | 22:04 | NL210A | URBAN | Unknown | Unknown | 74.33 | 18.4 | 0.002111 | 0.0001146 | Yes
28/12/2023 | 22:06 | KA07 | LONG RURAL | Unknown | Unknown | 71.00 | 1,269.0 | 0.646580 | 0.0005095 | Yes
28/12/2023 | 22:12 | CL10 | LONG RURAL | Weather |  | 84.00 | 2,163.4 | 1.304147 | 0.0006028 | Yes
28/12/2023 | 22:14 | R18 | LONG RURAL | Weather |  | 16.00 | 1,238.0 | 0.142149 | 0.0001148 | Yes
28/12/2023 | 22:15 | CV28 | LONG RURAL | Weather |  | 76.00 | 2,022.6 | 1.103131 | 0.0005454 | Yes
28/12/2023 | 22:18 | WK72 | SHORT RURAL | Weather |  | 465.00 | 275.3 | 0.900796 | 0.0032715 | Yes
28/12/2023 | 22:29 | HH107D | URBAN | Asset failure | LV | 1.00 | 185.0 | 0.000285 | 0.0000015 | Yes
28/12/2023 | 22:31 | HH386C | URBAN | Asset failure | LV | 9.67 | 786.0 | 0.011714 | 0.0000149 | Yes
28/12/2023 | 22:35 | CV30 | LONG RURAL | Unknown | Unknown | 9.00 | 1,333.0 | 0.086094 | 0.0000646 | Yes
28/12/2023 | 22:39 | LX41 | SHORT RURAL | Unknown | Unknown | 42.00 | 749.0 | 0.221322 | 0.0002955 | Yes
28/12/2023 | 22:46 | ME347C | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | Yes
28/12/2023 | 22:47 | LX53 | SHORT RURAL | Weather |  | 10.00 | 1,150.0 | 0.080908 | 0.0000704 | Yes
28/12/2023 | 22:57 | R35 | LONG RURAL | Unknown | Unknown | 68.00 | 946.0 | 0.461639 | 0.0004880 | Yes
28/12/2023 | 22:57 | LX41 | SHORT RURAL | Weather |  | 67.00 | 684.0 | 0.322422 | 0.0004714 | Yes
28/12/2023 | 23:05 | KA17 | LONG RURAL | Weather |  | 89.00 | 1,276.7 | 0.815418 | 0.0006387 | Yes
28/12/2023 | 23:20 | CV753A | LONG RURAL | Weather |  | 45.00 | 898.0 | 0.289995 | 0.0003229 | Yes
28/12/2023 | 23:24 | LX63 | LONG RURAL | Weather |  | 16.00 | 1,346.0 | 0.154549 | 0.0001148 | Yes
28/12/2023 | 23:32 | KA16 | LONG RURAL | Weather |  | 54.00 | 1,339.3 | 0.519007 | 0.0003875 | Yes
28/12/2023 | 23:35 | LX34 | SHORT RURAL | Weather |  | 6.00 | 1,231.0 | 0.051964 | 0.0000422 | Yes
28/12/2023 | 23:44 | GA10 | LONG RURAL | Weather |  | 19.00 | 12.0 | 0.001636 | 0.0001364 | Yes
28/12/2023 | 23:50 | PA25 | SHORT RURAL | Weather |  | 10.00 | 1,030.0 | 0.072466 | 0.0000704 | Yes
29/12/2023 | 00:04 | MT11 | LONG RURAL | Weather |  | 37.00 | 66.4 | 0.017632 | 0.0002655 | No
29/12/2023 | 00:16 | HH148A | URBAN | Weather |  | 529.00 | 98.8 | 0.080541 | 0.0008156 | No
29/12/2023 | 01:04 | CV32 | LONG RURAL | Unknown | Unknown | 18.00 | 2,135.0 | 0.275786 | 0.0001292 | No
29/12/2023 | 01:12 | WK65 | SHORT RURAL | Weather |  | 2.00 | 21.0 | 0.000295 | 0.0000141 | No
29/12/2023 | 01:51 | KA24 | LONG RURAL | Weather |  | 20.00 | 2,134.0 | 0.306286 | 0.0001435 | No
29/12/2023 | 01:59 | NU31 | LONG RURAL | Weather |  | 7.00 | 9.0 | 0.000452 | 0.0000502 | No
29/12/2023 | 02:03 | SD36400 | LONG RURAL | Weather |  | 713.00 | 650.0 | 3.325899 | 0.0051167 | No
29/12/2023 | 02:03 | CL09 | LONG RURAL | Weather |  | 1.00 | 5.0 | 0.000036 | 0.0000072 | No
29/12/2023 | 02:16 | R10 | LONG RURAL | Weather |  | 69.00 | 2,367.0 | 1.172060 | 0.0004952 | No
29/12/2023 | 02:36 | NU22 | LONG RURAL | Unknown | Unknown | 18.67 | 736.0 | 0.098593 | 0.0001340 | No
29/12/2023 | 03:03 | CL19 | LONG RURAL | Weather |  | 77.00 | 2,174.4 | 1.201533 | 0.0005526 | No
29/12/2023 | 03:48 | HH148A | URBAN | Weather |  | 88.00 | 326.9 | 0.044352 | 0.0001357 | No
29/12/2023 | 04:13 | R08 | LONG RURAL | Weather |  | 27.00 | 2,265.0 | 0.438868 | 0.0001938 | No
29/12/2023 | 04:29 | MTB32 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 104.00 | 269.5 | 0.201109 | 0.0007463 | No
29/12/2023 | 05:41 | KA18 | LONG RURAL | Weather |  | 2.00 | 751.0 | 0.010779 | 0.0000144 | No
29/12/2023 | 06:37 | SD38100 | LONG RURAL | Weather |  | 13.67 | 757.0 | 0.074244 | 0.0000981 | No
29/12/2023 | 06:37 | CL26 | LONG RURAL | Weather |  | 42.00 | 1,789.2 | 0.539287 | 0.0003014 | No
29/12/2023 | 06:47 | MT25 | LONG RURAL | Weather |  | 70.00 | 521.6 | 0.262022 | 0.0005023 | No
29/12/2023 | 06:49 | SD33200 | LONG RURAL | Unknown | Unknown | 2.00 | 1,564.0 | 0.022448 | 0.0000144 | No
29/12/2023 | 07:04 | SD45101 | LONG RURAL | Weather |  | 52.00 | 232.0 | 0.086575 | 0.0003732 | No
29/12/2023 | 07:07 | GA52 | LONG RURAL | Weather |  | 30.00 | 481.0 | 0.103554 | 0.0002153 | No
29/12/2023 | 07:15 | BM34 | SHORT RURAL | Weather |  | 2.00 | 712.0 | 0.010019 | 0.0000141 | No
29/12/2023 | 07:18 | BM34 | SHORT RURAL | Weather |  | 8.00 | 317.0 | 0.017842 | 0.0000563 | No
29/12/2023 | 07:40 | MT18 | LONG RURAL | Weather |  | 59.00 | 1,021.8 | 0.432632 | 0.0004234 | No
29/12/2023 | 07:41 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 178.0 | 0.001252 | 0.0000070 | No
29/12/2023 | 07:44 | CV30 | LONG RURAL | Weather |  | 70.00 | 539.2 | 0.270878 | 0.0005023 | No
29/12/2023 | 07:53 | NL115E | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
29/12/2023 | 08:01 | EL01A | URBAN | Third Party | Unauthorised access | 7.00 | 70.0 | 0.000755 | 0.0000108 | No
29/12/2023 | 08:01 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 412.0 | 0.002899 | 0.0000070 | No
29/12/2023 | 08:05 | LX41 | SHORT RURAL | Weather |  | 7.00 | 204.0 | 0.010047 | 0.0000492 | No
29/12/2023 | 08:14 | BM44 | SHORT RURAL | Weather |  | 67.00 | 60.0 | 0.028283 | 0.0004714 | No
29/12/2023 | 08:14 | BM44 | SHORT RURAL | Weather |  | 1.00 | 60.0 | 0.000422 | 0.0000070 | No
29/12/2023 | 08:15 | CM35 | LONG RURAL | Unknown | Unknown | 1.00 | 473.0 | 0.003394 | 0.0000072 | No
29/12/2023 | 08:19 | GA09 | LONG RURAL | Weather |  | 1.00 | 101.0 | 0.000725 | 0.0000072 | No
29/12/2023 | 08:37 | PP03 | URBAN | Weather |  | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
29/12/2023 | 08:45 | GU41 | LONG RURAL | Weather |  | 4.00 | 227.0 | 0.006516 | 0.0000287 | No
29/12/2023 | 08:51 | M13 | LONG RURAL | Unknown | Unknown | 1.33 | 6,140.0 | 0.058750 | 0.0000096 | No
29/12/2023 | 08:59 | SM350F | URBAN | Third Party | Vehicle impact | 55.00 | 232.0 | 0.019673 | 0.0000848 | No
29/12/2023 | 08:59 | SD34400 | LONG RURAL | Weather |  | 1.00 | 1,931.0 | 0.013857 | 0.0000072 | No
29/12/2023 | 09:09 | SD38100 | LONG RURAL | Weather |  | 2.00 | 739.0 | 0.010607 | 0.0000144 | No
29/12/2023 | 09:19 | M13 | LONG RURAL | Unknown | Unknown | 2.00 | 6,111.0 | 0.087709 | 0.0000144 | No
29/12/2023 | 10:03 | MT14 | SHORT RURAL | Unknown | Unknown | 18.00 | 1,735.8 | 0.219817 | 0.0001266 | No
29/12/2023 | 10:31 | GU13 | LONG RURAL | Weather |  | 1.00 | 110.0 | 0.000789 | 0.0000072 | No
29/12/2023 | 10:59 | MG48 | LONG RURAL | Unknown | Unknown | 1.00 | 122.0 | 0.000876 | 0.0000072 | No
29/12/2023 | 11:27 | GA29 | LONG RURAL | Weather |  | 8.00 | 321.0 | 0.018429 | 0.0000574 | No
29/12/2023 | 12:38 | EL20 | URBAN | Third Party | Other | 52.00 | 140.0 | 0.011224 | 0.0000802 | No
29/12/2023 | 12:46 | CL27 | LONG RURAL | Asset failure | LV | 2.00 | 185.0 | 0.002655 | 0.0000144 | No
29/12/2023 | 12:54 | KA05 | LONG RURAL | Unknown | Unknown | 2.00 | 1,394.0 | 0.020008 | 0.0000144 | No
29/12/2023 | 13:28 | SD35200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 188.0 | 0.001349 | 0.0000072 | No
29/12/2023 | 13:48 | GA02 | SHORT RURAL | Other |  | 32.00 | 35.0 | 0.007880 | 0.0002251 | No
29/12/2023 | 14:18 | VH51 | SHORT RURAL | Asset failure | HV | 11.00 | 78.3 | 0.006058 | 0.0000774 | No
29/12/2023 | 14:22 | MT01 | LONG RURAL | Unknown | Unknown | 2.00 | 1,691.0 | 0.024270 | 0.0000144 | No
29/12/2023 | 14:25 | HH432D | URBAN | Overloads |  | 1.00 | 523.0 | 0.000806 | 0.0000015 | No
29/12/2023 | 15:55 | GA21 | LONG RURAL | Unknown | Unknown | 7.00 | 1,358.0 | 0.068218 | 0.0000502 | No
29/12/2023 | 16:03 | HH177C | URBAN | Asset failure | LV | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
29/12/2023 | 17:17 | SD36400 | LONG RURAL | Unknown | Unknown | 2.00 | 955.0 | 0.013707 | 0.0000144 | No
29/12/2023 | 17:20 | AP424A | URBAN | Asset failure | LV | 1.00 | 232.0 | 0.000358 | 0.0000015 | No
29/12/2023 | 17:57 | GA03 | LONG RURAL | Asset failure | HV | 2.00 | 3,134.5 | 0.044988 | 0.0000144 | No
29/12/2023 | 18:03 | ST23 | SHORT RURAL | Asset failure | LV | 1.00 | 1,177.0 | 0.008281 | 0.0000070 | No
29/12/2023 | 20:46 | HH121D | URBAN | Unknown | Unknown | 4.33 | 153.0 | 0.001022 | 0.0000067 | No
29/12/2023 | 21:32 | CV29 | LONG RURAL | Weather |  | 72.00 | 930.7 | 0.480900 | 0.0005167 | No
29/12/2023 | 21:43 | NU15 | LONG RURAL | Unknown | Unknown | 3.00 | 1,000.0 | 0.021529 | 0.0000215 | No
29/12/2023 | 22:10 | NU27 | LONG RURAL | Weather |  | 1.00 | 7.0 | 0.000050 | 0.0000072 | No
29/12/2023 | 22:14 | AP125D | URBAN | Other |  | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
29/12/2023 | 22:17 | NL451A | URBAN | Asset failure | LV | 1.00 | 217.0 | 0.000335 | 0.0000015 | No
29/12/2023 | 22:35 | SD32400 | LONG RURAL | Asset failure | Subtransmission | 955.00 | 64.0 | 0.438876 | 0.0068534 | No
29/12/2023 | 22:41 | LX53 | SHORT RURAL | Weather |  | 1.00 | 3.0 | 0.000021 | 0.0000070 | No
29/12/2023 | 23:01 | VH44 | SHORT RURAL | Weather |  | 326.00 | 30.0 | 0.068751 | 0.0022936 | No
29/12/2023 | 23:31 | NU02 | LONG RURAL | Weather |  | 4.00 | 9.0 | 0.000258 | 0.0000287 | No
29/12/2023 | 23:38 | NU35 | LONG RURAL | Weather |  | 73.00 | 780.3 | 0.408771 | 0.0005239 | No
29/12/2023 | 23:40 | NU15 | LONG RURAL | Weather |  | 7.00 | 7.0 | 0.000352 | 0.0000502 | No
29/12/2023 | 23:45 | CV18 | SHORT RURAL | Weather |  | 58.00 | 994.7 | 0.405877 | 0.0004081 | No
30/12/2023 | 01:37 | EL20 | URBAN | Overloads |  | 4.00 | 279.0 | 0.001721 | 0.0000062 | No
30/12/2023 | 02:57 | CBD412S | URBAN | Asset failure | HV | 7.33 | 203.0 | 0.002295 | 0.0000113 | No
30/12/2023 | 03:32 | CBD412S | URBAN | Network business | Switching and protection error | 496.00 | 14.0 | 0.010706 | 0.0007647 | No
30/12/2023 | 07:19 | NL234E | URBAN | Asset failure | LV | 17.00 | 314.0 | 0.008230 | 0.0000262 | No
30/12/2023 | 07:59 | CL05 | LONG RURAL | Unknown | Unknown | 2.00 | 62.0 | 0.000890 | 0.0000144 | No
30/12/2023 | 08:19 | SD48200 | LONG RURAL | Planned |  | 1,851.00 | 42.2 | 0.560967 | 0.0132834 | No
30/12/2023 | 08:49 | WHY17 | SHORT RURAL | Planned |  | 52.00 | 172.0 | 0.062925 | 0.0003658 | No
30/12/2023 | 09:13 | PL10 | LONG RURAL | Weather |  | 1.00 | 67.0 | 0.000481 | 0.0000072 | No
30/12/2023 | 09:56 | WK72 | SHORT RURAL | Weather |  | 1.00 | 192.0 | 0.001351 | 0.0000070 | No
30/12/2023 | 10:17 | NU34 | LONG RURAL | Asset failure | LV | 1.00 | 468.0 | 0.003359 | 0.0000072 | No
30/12/2023 | 10:30 | R26 | LONG RURAL | Unknown | Unknown | 1.00 | 85.0 | 0.000610 | 0.0000072 | No
30/12/2023 | 10:31 | EL19 | URBAN | Unknown | Unknown | 72.00 | 226.6 | 0.025152 | 0.0001110 | No
30/12/2023 | 11:04 | SA16 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
30/12/2023 | 11:12 | SD34102 | LONG RURAL | Unknown | Unknown | 1.00 | 24.0 | 0.000172 | 0.0000072 | No
30/12/2023 | 12:37 | NU27 | LONG RURAL | Weather |  | 1.00 | 305.0 | 0.002189 | 0.0000072 | No
30/12/2023 | 13:00 | HH432F | URBAN | Asset failure | LV | 25.00 | 81.0 | 0.003122 | 0.0000385 | No
30/12/2023 | 13:00 | HH432F | URBAN | Asset failure | LV | 10.67 | 83.0 | 0.001365 | 0.0000164 | No
30/12/2023 | 13:03 | CM11 | LONG RURAL | Weather |  | 3.00 | 126.0 | 0.002713 | 0.0000215 | No
30/12/2023 | 13:29 | HH432C | URBAN | Asset failure | LV | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
30/12/2023 | 14:23 | HH409D | URBAN | Unknown | Unknown | 59.00 | 92.0 | 0.008369 | 0.0000910 | No
30/12/2023 | 14:32 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 464.0 | 0.003264 | 0.0000070 | No
30/12/2023 | 15:32 | EL260C | URBAN | Third Party | Vehicle impact | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
30/12/2023 | 16:02 | MT09 | LONG RURAL | Weather |  | 22.00 | 7.0 | 0.001105 | 0.0001579 | No
30/12/2023 | 16:35 | HH409D | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
30/12/2023 | 17:20 | HH432C | URBAN | Vegetation | Grow-in - NSP responsibility | 24.00 | 127.0 | 0.004699 | 0.0000370 | No
30/12/2023 | 18:07 | MV53 | SHORT RURAL | Asset failure | LV | 3.00 | 535.0 | 0.011292 | 0.0000211 | No
30/12/2023 | 18:08 | AP226D | URBAN | Asset failure | LV | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
30/12/2023 | 18:16 | MT19 | LONG RURAL | Weather |  | 12.00 | 88.0 | 0.007578 | 0.0000861 | No
31/12/2023 | 00:15 | R36 | SHORT RURAL | Weather |  | 34.00 | 708.8 | 0.169541 | 0.0002392 | No
31/12/2023 | 00:45 | HH121C | URBAN | Asset failure | LV | 1.00 | 303.0 | 0.000467 | 0.0000015 | No
31/12/2023 | 03:54 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 220.33 | 81.0 | 0.027516 | 0.0003397 | No
31/12/2023 | 06:46 | G31 | LONG RURAL | Unknown | Unknown | 54.00 | 420.9 | 0.163118 | 0.0003875 | No
31/12/2023 | 08:11 | KA14 | LONG RURAL | Weather |  | 79.00 | 144.0 | 0.081638 | 0.0005669 | No
31/12/2023 | 08:38 | EL01B | URBAN | Other |  | 2.00 | 222.0 | 0.000685 | 0.0000031 | No
31/12/2023 | 10:25 | G17 | LONG RURAL | Asset failure | LV | 1.00 | 487.0 | 0.003495 | 0.0000072 | No
31/12/2023 | 10:35 | BM43 | SHORT RURAL | Asset failure | LV | 1.00 | 98.0 | 0.000689 | 0.0000070 | No
31/12/2023 | 11:54 | VH22 | SHORT RURAL | Asset failure | HV | 1.00 | 37.0 | 0.000260 | 0.0000070 | No
31/12/2023 | 12:02 | GA10 | LONG RURAL | Unknown | Unknown | 14.33 | 5.0 | 0.000514 | 0.0001029 | No
31/12/2023 | 12:50 | SD33200 | LONG RURAL | Unknown | Unknown | 18.67 | 256.0 | 0.034293 | 0.0001340 | No
31/12/2023 | 13:06 | HH148B | URBAN | Asset failure | LV | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
31/12/2023 | 13:33 | SM349H | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
31/12/2023 | 13:42 | EL11 | URBAN | Asset failure | LV | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
31/12/2023 | 14:45 | M21 | LONG RURAL | Asset failure | LV | 1.00 | 258.0 | 0.001851 | 0.0000072 | No
31/12/2023 | 15:19 | CV15 | LONG RURAL | Weather |  | 11.00 | 76.0 | 0.005999 | 0.0000789 | No
31/12/2023 | 16:13 | HH177F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 58.00 | 268.0 | 0.023965 | 0.0000894 | No
31/12/2023 | 19:12 | AP344D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,351.00 | 84.8 | 0.176602 | 0.0020829 | No
31/12/2023 | 19:31 | AP149H | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
01/01/2024 | 07:37 | SM411C | URBAN | Animal | Animal impact | 4.00 | 190.0 | 0.001172 | 0.0000062 | No
01/01/2024 | 11:15 | GA10 | LONG RURAL | Unknown | Unknown | 14.33 | 7.0 | 0.000720 | 0.0001029 | No
01/01/2024 | 12:02 | KA14 | LONG RURAL | Asset failure | HV | 11.00 | 262.3 | 0.020704 | 0.0000789 | No
01/01/2024 | 12:02 | KA14 | LONG RURAL | Weather |  | 1.00 | 1,644.0 | 0.011798 | 0.0000072 | No
01/01/2024 | 12:51 | AP125D | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
01/01/2024 | 13:45 | BM42 | SHORT RURAL | Asset failure | HV | 120.33 | 30.0 | 0.025398 | 0.0008466 | No
01/01/2024 | 14:21 | EL10 | URBAN | Overloads |  | 1.00 | 262.0 | 0.000404 | 0.0000015 | No
01/01/2024 | 14:22 | SA20 | URBAN | Asset failure | LV | 16.00 | 498.0 | 0.012285 | 0.0000247 | No
01/01/2024 | 14:23 | WHY07 | URBAN | Asset failure | LV | 2.00 | 176.0 | 0.000543 | 0.0000031 | No
01/01/2024 | 15:28 | BM34 | SHORT RURAL | Animal | Animal impact | 107.00 | 104.0 | 0.078291 | 0.0007528 | No
01/01/2024 | 20:30 | G29 | LONG RURAL | Third Party | Other | 29.00 | 25.0 | 0.005203 | 0.0002081 | No
01/01/2024 | 21:08 | PL01 | URBAN | Asset failure | LV | 35.67 | 116.0 | 0.006379 | 0.0000550 | No
01/01/2024 | 21:29 | PA07 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 11.00 | 110.0 | 0.008683 | 0.0000789 | No
01/01/2024 | 23:05 | NL210A | URBAN | Asset failure | LV | 13.00 | 197.0 | 0.003948 | 0.0000200 | No
01/01/2024 | 23:12 | G17 | LONG RURAL | Asset failure | HV | 4.00 | 163.0 | 0.004679 | 0.0000287 | No
02/01/2024 | 06:07 | CD19 | LONG RURAL | Unknown | Unknown | 54.00 | 197.0 | 0.076342 | 0.0003875 | No
02/01/2024 | 06:51 | CD23 | LONG RURAL | Unknown | Unknown | 9.00 | 282.0 | 0.018214 | 0.0000646 | No
02/01/2024 | 08:06 | BS0189 | SHORT RURAL | Planned |  | 1.00 | 1,806.0 | 0.012706 | 0.0000070 | No
02/01/2024 | 08:14 | GA10 | LONG RURAL | Unknown | Unknown | 14.33 | 220.0 | 0.022629 | 0.0001029 | No
02/01/2024 | 08:20 | ME231F | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
02/01/2024 | 08:20 | BT15 | LONG RURAL | Asset failure | LV | 1.00 | 313.0 | 0.002246 | 0.0000072 | No
02/01/2024 | 08:57 | KI31 | SHORT RURAL | Planned |  | 1.00 | 99.0 | 0.000697 | 0.0000070 | No
02/01/2024 | 09:00 | ST44 | LONG RURAL | Planned |  | 6.00 | 118.0 | 0.005081 | 0.0000431 | No
02/01/2024 | 09:13 | GU17 | LONG RURAL | Unknown | Unknown | 14.00 | 6.0 | 0.000603 | 0.0001005 | No
02/01/2024 | 09:45 | HK04 | LONG RURAL | Weather |  | 2.00 | 307.0 | 0.004406 | 0.0000144 | No
02/01/2024 | 09:55 | MV15 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 11.00 | 73.5 | 0.005685 | 0.0000774 | No
02/01/2024 | 10:12 | HH121D | URBAN | Asset failure | LV | 54.00 | 81.1 | 0.006751 | 0.0000833 | No
02/01/2024 | 10:14 | SM216E | URBAN | Overloads |  | 1.00 | 85.0 | 0.000131 | 0.0000015 | No
02/01/2024 | 10:25 | AP344E | URBAN | Vegetation | Grow-in - NSP responsibility | 12.00 | 80.0 | 0.001480 | 0.0000185 | No
02/01/2024 | 11:17 | WK32 | SHORT RURAL | Unknown | Unknown | 1.00 | 320.0 | 0.002251 | 0.0000070 | No
02/01/2024 | 11:28 | KI31 | SHORT RURAL | Planned |  | 1.00 | 79.0 | 0.000556 | 0.0000070 | No
02/01/2024 | 12:35 | VH71 | SHORT RURAL | Overloads |  | 1.00 | 120.0 | 0.000844 | 0.0000070 | No
02/01/2024 | 12:36 | GA10 | LONG RURAL | Unknown | Unknown | 19.00 | 186.0 | 0.025361 | 0.0001364 | No
02/01/2024 | 12:47 | NL111Q | URBAN | Asset failure | LV | 1.00 | 309.0 | 0.000476 | 0.0000015 | No
02/01/2024 | 13:03 | EL09 | URBAN | Asset failure | LV | 1.00 | 365.0 | 0.000563 | 0.0000015 | No
02/01/2024 | 13:51 | MB62 | LONG RURAL | Asset failure | LV | 1.00 | 71.0 | 0.000510 | 0.0000072 | No
02/01/2024 | 14:16 | NL111B | URBAN | Asset failure | LV | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
02/01/2024 | 16:17 | NL760B | URBAN | Asset failure | LV | 1.00 | 234.0 | 0.000361 | 0.0000015 | No
02/01/2024 | 16:26 | EL01M | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | No
02/01/2024 | 17:26 | NA05 | LONG RURAL | Asset failure | HV | 1.00 | 89.0 | 0.000639 | 0.0000072 | No
02/01/2024 | 20:24 | MG09 | SHORT RURAL | Unknown | Unknown | 1.33 | 97.0 | 0.000910 | 0.0000094 | No
02/01/2024 | 21:23 | SG07 | SHORT RURAL | Overloads |  | 1.00 | 249.0 | 0.001752 | 0.0000070 | No
02/01/2024 | 21:40 | NA02 | LONG RURAL | Weather |  | 291.00 | 13.3 | 0.027859 | 0.0020883 | No
02/01/2024 | 21:58 | NA05 | LONG RURAL | Weather |  | 126.00 | 250.4 | 0.226456 | 0.0009042 | No
02/01/2024 | 22:06 | SA41 | URBAN | Asset failure | LV | 4.00 | 105.0 | 0.000648 | 0.0000062 | No
02/01/2024 | 22:19 | NA19 | LONG RURAL | Weather |  | 36.00 | 188.0 | 0.048569 | 0.0002583 | No
02/01/2024 | 22:27 | GU17 | LONG RURAL | Animal | Animal impact | 14.00 | 308.0 | 0.030944 | 0.0001005 | No
03/01/2024 | 01:22 | NA05 | LONG RURAL | Weather |  | 1.00 | 1,988.0 | 0.014267 | 0.0000072 | No
03/01/2024 | 01:33 | HH102C | URBAN | Asset failure | HV | 385.00 | 45.7 | 0.027127 | 0.0005936 | No
03/01/2024 | 05:09 | EL260C | URBAN | Asset failure | LV | 37.00 | 55.0 | 0.003137 | 0.0000570 | No
03/01/2024 | 07:44 | BM51 | URBAN | Asset failure | LV | 1.00 | 56.0 | 0.000086 | 0.0000015 | No
03/01/2024 | 08:38 | PL04 | URBAN | Planned |  | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
03/01/2024 | 08:43 | BM32 | SHORT RURAL | Planned |  | 9.00 | 339.9 | 0.021522 | 0.0000633 | No
03/01/2024 | 08:44 | GA25 | SHORT RURAL | Planned |  | 61.00 | 130.1 | 0.055841 | 0.0004292 | No
03/01/2024 | 08:50 | NA02 | LONG RURAL | Weather |  | 8.00 | 135.4 | 0.007772 | 0.0000574 | No
03/01/2024 | 09:02 | NA06 | LONG RURAL | Unknown | Unknown | 1.00 | 467.0 | 0.003351 | 0.0000072 | No
03/01/2024 | 09:04 | BT04 | LONG RURAL | Asset failure | LV | 1.00 | 1,531.0 | 0.010987 | 0.0000072 | No
03/01/2024 | 09:15 | KI54 | LONG RURAL | Planned |  | 5.00 | 139.0 | 0.004988 | 0.0000359 | No
03/01/2024 | 09:34 | ME131E | URBAN | Planned |  | 104.00 | 320.4 | 0.051370 | 0.0001603 | No
03/01/2024 | 09:56 | CN52 | LONG RURAL | Planned |  | 34.00 | 231.0 | 0.056363 | 0.0002440 | No
03/01/2024 | 10:19 | MV11 | SHORT RURAL | Planned |  | 1.00 | 12.0 | 0.000084 | 0.0000070 | No
03/01/2024 | 10:30 | NL115E | URBAN | Asset failure | LV | 37.00 | 126.0 | 0.007188 | 0.0000570 | No
03/01/2024 | 12:13 | PA10 | LONG RURAL | Planned |  | 64.00 | 32.0 | 0.014697 | 0.0004593 | No
03/01/2024 | 13:02 | PL13 | LONG RURAL | Asset failure | LV | 1.00 | 282.0 | 0.002024 | 0.0000072 | No
03/01/2024 | 13:53 | MG39 | SHORT RURAL | Asset failure | LV | 1.00 | 80.0 | 0.000563 | 0.0000070 | No
03/01/2024 | 14:26 | SG09 | SHORT RURAL | Asset failure | LV | 8.00 | 240.0 | 0.013508 | 0.0000563 | No
03/01/2024 | 14:29 | SD37200 | LONG RURAL | Weather |  | 3,048.00 | 114.0 | 2.493918 | 0.0218735 | No
03/01/2024 | 14:53 | GA10 | LONG RURAL | Unknown | Unknown | 14.33 | 181.0 | 0.018618 | 0.0001029 | No
03/01/2024 | 15:05 | EL08D | URBAN | Asset failure | LV | 13.00 | 268.0 | 0.005371 | 0.0000200 | No
03/01/2024 | 15:13 | WK61 | SHORT RURAL | Asset failure | LV | 9.00 | 166.0 | 0.010511 | 0.0000633 | No
03/01/2024 | 17:26 | MB82 | LONG RURAL | Animal | Animal impact | 42.00 | 116.0 | 0.034963 | 0.0003014 | No
03/01/2024 | 18:10 | AP226B | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
03/01/2024 | 18:30 | SM402B | URBAN | Third Party | Vehicle impact | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
03/01/2024 | 18:52 | MB61 | LONG RURAL | Unknown | Unknown | 1.00 | 235.0 | 0.001686 | 0.0000072 | No
03/01/2024 | 19:00 | NA35 | SHORT RURAL | Asset failure | HV | 23.00 | 195.2 | 0.031582 | 0.0001618 | No
03/01/2024 | 19:00 | NA35 | SHORT RURAL | Asset failure | HV | 9.00 | 275.1 | 0.017420 | 0.0000633 | No
03/01/2024 | 19:12 | HH177G | URBAN | Vegetation | Grow-in - NSP responsibility | 39.00 | 164.0 | 0.009861 | 0.0000601 | No
03/01/2024 | 19:23 | WHY09 | URBAN | Asset failure | LV | 1.00 | 2,292.0 | 0.003534 | 0.0000015 | No
03/01/2024 | 21:40 | SA35 | URBAN | Asset failure | LV | 1.00 | 29.0 | 0.000045 | 0.0000015 | No
03/01/2024 | 21:48 | ME427E | URBAN | Asset failure | LV | 1.00 | 255.0 | 0.000393 | 0.0000015 | No
03/01/2024 | 22:05 | AP372D | URBAN | Asset failure | HV | 871.00 | 120.1 | 0.161283 | 0.0013429 | No
03/01/2024 | 22:41 | CBD367P | CBD | Planned |  | 2.00 | 290.0 | 0.083797 | 0.0002890 | No
03/01/2024 | 23:11 | ST34 | LONG RURAL | Planned |  | 182.00 | 397.8 | 0.519552 | 0.0013061 | No
04/01/2024 | 00:43 | SA20 | URBAN | Asset failure | LV | 106.00 | 81.0 | 0.013237 | 0.0001634 | No
04/01/2024 | 01:17 | AP425D | URBAN | Other |  | 37.33 | 103.0 | 0.005929 | 0.0000576 | No
04/01/2024 | 06:34 | CM21 | LONG RURAL | Unknown | Unknown | 59.00 | 206.0 | 0.087228 | 0.0004234 | No
04/01/2024 | 06:57 | SG01 | SHORT RURAL | Animal | Animal impact | 3.00 | 110.0 | 0.002322 | 0.0000211 | No
04/01/2024 | 07:31 | NA36 | LONG RURAL | Asset failure | LV | 2.00 | 249.0 | 0.003574 | 0.0000144 | No
04/01/2024 | 07:33 | SA18 | URBAN | Overloads |  | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
04/01/2024 | 08:10 | PL24 | LONG RURAL | Unknown | Unknown | 1.00 | 142.0 | 0.001019 | 0.0000072 | No
04/01/2024 | 08:47 | HH121E | URBAN | Planned |  | 57.00 | 239.0 | 0.021003 | 0.0000879 | No
04/01/2024 | 09:25 | EL20 | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
04/01/2024 | 09:33 | HH429B | URBAN | Planned |  | 51.00 | 89.0 | 0.006998 | 0.0000786 | No
04/01/2024 | 10:18 | VH72 | SHORT RURAL | Unknown | Unknown | 1.00 | 176.0 | 0.001238 | 0.0000070 | No
04/01/2024 | 10:53 | SM411E | URBAN | Asset failure | LV | 15.00 | 101.0 | 0.002336 | 0.0000231 | No
04/01/2024 | 12:35 | HH341D | URBAN | Animal | Animal impact | 46.00 | 241.0 | 0.017092 | 0.0000709 | No
04/01/2024 | 13:17 | WHY08 | URBAN | Asset failure | LV | 1.00 | 2,580.0 | 0.003978 | 0.0000015 | No
04/01/2024 | 13:35 | HH107B | URBAN | Unknown | Unknown | 1.00 | 432.0 | 0.000666 | 0.0000015 | No
04/01/2024 | 14:10 | NL115E | URBAN | Asset failure | LV | 1.00 | 402.0 | 0.000620 | 0.0000015 | No
04/01/2024 | 15:14 | NU01 | SHORT RURAL | Overloads |  | 1.00 | 303.0 | 0.002132 | 0.0000070 | No
04/01/2024 | 16:00 | AP425C | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
04/01/2024 | 16:18 | LC01 | LONG RURAL | Weather |  | 49.00 | 423.0 | 0.148744 | 0.0003516 | No
04/01/2024 | 16:18 | LC01 | SHORT RURAL | Weather |  | 1.00 | 423.0 | 0.002976 | 0.0000070 | No
04/01/2024 | 16:36 | CBD103G | URBAN | Asset failure | LV | 1.00 | 31.0 | 0.000048 | 0.0000015 | No
04/01/2024 | 16:58 | HH177G | URBAN | Asset failure | LV | 1.00 | 35.0 | 0.000054 | 0.0000015 | No
04/01/2024 | 17:36 | CL01 | LONG RURAL | Unknown | Unknown | 1.00 | 325.0 | 0.002332 | 0.0000072 | No
04/01/2024 | 18:49 | BM44 | SHORT RURAL | Third Party | Vehicle impact | 94.00 | 25.0 | 0.016533 | 0.0006613 | No
04/01/2024 | 21:24 | AP146D | URBAN | Asset failure | LV | 58.00 | 74.0 | 0.006617 | 0.0000894 | No
04/01/2024 | 23:26 | MB62 | LONG RURAL | Asset failure | LV | 2.00 | 154.0 | 0.002210 | 0.0000144 | No
05/01/2024 | 00:44 | SM172F | URBAN | Asset failure | LV | 32.00 | 23.0 | 0.001135 | 0.0000493 | No
05/01/2024 | 04:40 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 148.00 | 274.7 | 0.062678 | 0.0002282 | No
05/01/2024 | 07:25 | MB82 | LONG RURAL | Animal | Animal impact | 42.00 | 208.0 | 0.062692 | 0.0003014 | No
05/01/2024 | 08:10 | MI08 | LONG RURAL | Asset failure | LV | 46.00 | 487.0 | 0.160764 | 0.0003301 | No
05/01/2024 | 08:23 | SD40200 | LONG RURAL | Planned |  | 111.00 | 221.0 | 0.176021 | 0.0007966 | No
05/01/2024 | 08:32 | BM55 | SHORT RURAL | Planned |  | 26.00 | 124.0 | 0.022682 | 0.0001829 | No
05/01/2024 | 09:15 | MTB32 | LONG RURAL | Overloads |  | 1.00 | 136.0 | 0.000976 | 0.0000072 | No
05/01/2024 | 09:16 | VH33 | SHORT RURAL | Planned |  | 8.00 | 176.0 | 0.009906 | 0.0000563 | No
05/01/2024 | 09:35 | HH386D | URBAN | Planned |  | 147.00 | 226.7 | 0.051373 | 0.0002266 | No
05/01/2024 | 10:22 | NL111B | URBAN | Asset failure | LV | 1.00 | 402.0 | 0.000620 | 0.0000015 | No
05/01/2024 | 11:36 | NU35 | LONG RURAL | Other |  | 1.00 | 192.0 | 0.001378 | 0.0000072 | No
05/01/2024 | 12:21 | CL05 | LONG RURAL | Weather |  | 2.00 | 318.0 | 0.004564 | 0.0000144 | No
05/01/2024 | 12:28 | MV64 | SHORT RURAL | Other |  | 1.00 | 60.0 | 0.000422 | 0.0000070 | No
05/01/2024 | 13:55 | KA16 | LONG RURAL | Unknown | Unknown | 54.00 | 162.9 | 0.063123 | 0.0003875 | No
05/01/2024 | 14:12 | CD03 | SHORT RURAL | Asset failure | HV | 441.00 | 82.2 | 0.254980 | 0.0031027 | No
05/01/2024 | 14:13 | CD22 | LONG RURAL | Unknown | Unknown | 10.00 | 352.0 | 0.025261 | 0.0000718 | No
05/01/2024 | 14:13 | CD24 | LONG RURAL | Unknown | Unknown | 8.00 | 283.3 | 0.016262 | 0.0000574 | No
05/01/2024 | 15:14 | G07 | LONG RURAL | Weather |  | 84.00 | 235.0 | 0.141661 | 0.0006028 | No
05/01/2024 | 15:15 | SA18 | URBAN | Asset failure | LV | 1.00 | 24.0 | 0.000037 | 0.0000015 | No
05/01/2024 | 15:23 | PP12 | LONG RURAL | Weather |  | 21.00 | 240.6 | 0.036255 | 0.0001507 | No
05/01/2024 | 15:41 | AP529E | URBAN | Asset failure | LV | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
05/01/2024 | 15:48 | CD17 | LONG RURAL | Weather |  | 7.00 | 1,251.0 | 0.062843 | 0.0000502 | No
05/01/2024 | 15:57 | MB28 | SHORT RURAL | Asset failure | LV | 1.00 | 395.0 | 0.002779 | 0.0000070 | No
05/01/2024 | 16:06 | SB21 | LONG RURAL | Weather |  | 77.00 | 417.4 | 0.230654 | 0.0005526 | No
05/01/2024 | 16:13 | W29 | LONG RURAL | Weather |  | 37.00 | 1,241.0 | 0.329516 | 0.0002655 | No
05/01/2024 | 16:18 | SB01 | LONG RURAL | Unknown | Unknown | 25.00 | 96.0 | 0.017223 | 0.0001794 | No
05/01/2024 | 16:22 | HH177E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,648.00 | 161.6 | 0.659892 | 0.0040826 | No
05/01/2024 | 16:28 | EL01Q | URBAN | Third Party | Unauthorised access | 1.00 | 19.0 | 0.000029 | 0.0000015 | No
05/01/2024 | 16:33 | CV21 | LONG RURAL | Weather |  | 55.00 | 1,213.0 | 0.478783 | 0.0003947 | No
05/01/2024 | 16:53 | SB01 | LONG RURAL | Weather |  | 6.00 | 1,187.0 | 0.051110 | 0.0000431 | No
05/01/2024 | 17:02 | G32 | LONG RURAL | Weather |  | 34.00 | 637.7 | 0.155597 | 0.0002440 | No
05/01/2024 | 17:07 | W24 | LONG RURAL | Weather |  | 64.00 | 1,596.9 | 0.733442 | 0.0004593 | No
05/01/2024 | 17:12 | SD31200 | LONG RURAL | Weather |  | 26.00 | 107.0 | 0.019965 | 0.0001866 | No
05/01/2024 | 17:12 | W32 | LONG RURAL | Weather |  | 18.00 | 1,389.7 | 0.179509 | 0.0001292 | No
05/01/2024 | 17:14 | G31 | LONG RURAL | Weather |  | 101.00 | 597.8 | 0.433264 | 0.0007248 | No
05/01/2024 | 17:20 | SA14 | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | No
05/01/2024 | 17:32 | CD17 | LONG RURAL | Weather |  | 31.00 | 1,146.3 | 0.255018 | 0.0002225 | No
05/01/2024 | 17:38 | EL11 | URBAN | Asset failure | LV | 2.00 | 228.0 | 0.000703 | 0.0000031 | No
05/01/2024 | 17:48 | G18 | LONG RURAL | Unknown | Unknown | 22.00 | 319.1 | 0.050378 | 0.0001579 | No
05/01/2024 | 17:58 | HH121B | URBAN | Overloads |  | 30.00 | 236.0 | 0.010916 | 0.0000463 | No
05/01/2024 | 18:14 | NL451D | URBAN | Third Party | Other | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
05/01/2024 | 18:26 | W04 | LONG RURAL | Unknown | Unknown | 1.00 | 1,188.0 | 0.008525 | 0.0000072 | No
05/01/2024 | 18:28 | LM32 | LONG RURAL | Unknown | Unknown | 21.00 | 1,498.6 | 0.225846 | 0.0001507 | No
05/01/2024 | 18:33 | SM410C | URBAN | Asset failure | LV | 40.33 | 50.0 | 0.003109 | 0.0000622 | No
05/01/2024 | 19:29 | SM172F | URBAN | Overloads |  | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
05/01/2024 | 20:34 | MV63 | SHORT RURAL | Animal | Animal impact | 8.33 | 287.0 | 0.016827 | 0.0000586 | No
05/01/2024 | 20:56 | CN53 | LONG RURAL | Asset failure | HV | 107.00 | 857.1 | 0.658120 | 0.0007679 | No
05/01/2024 | 22:37 | CBD412C | CBD | Planned |  | 16.00 | 11.1 | 0.025717 | 0.0023116 | No
06/01/2024 | 03:18 | PL07 | URBAN | Unknown | Unknown | 2.00 | 586.0 | 0.001807 | 0.0000031 | No
06/01/2024 | 03:51 | NL760B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
06/01/2024 | 04:53 | CV29 | LONG RURAL | Weather |  | 37.00 | 661.4 | 0.175626 | 0.0002655 | No
06/01/2024 | 07:17 | KA21 | LONG RURAL | Weather |  | 77.00 | 297.5 | 0.164403 | 0.0005526 | No
06/01/2024 | 07:21 | SD34405 | LONG RURAL | Weather |  | 38.00 | 585.3 | 0.159602 | 0.0002727 | No
06/01/2024 | 07:30 | EL11 | URBAN | Unknown | Unknown | 22.00 | 38.8 | 0.001317 | 0.0000339 | No
06/01/2024 | 07:39 | CV29 | LONG RURAL | Unknown | Unknown | 56.00 | 231.0 | 0.092833 | 0.0004019 | No
06/01/2024 | 08:16 | KA18 | LONG RURAL | Weather |  | 22.00 | 372.0 | 0.058731 | 0.0001579 | No
06/01/2024 | 08:23 | AP132A | URBAN | Asset failure | LV | 19.00 | 511.0 | 0.014969 | 0.0000293 | No
06/01/2024 | 08:29 | MT14 | SHORT RURAL | Unknown | Unknown | 18.00 | 446.5 | 0.056544 | 0.0001266 | No
06/01/2024 | 08:38 | KA16 | LONG RURAL | Weather |  | 54.00 | 415.6 | 0.161037 | 0.0003875 | No
06/01/2024 | 08:47 | CM35 | LONG RURAL | Weather |  | 651.00 | 237.0 | 1.107214 | 0.0046718 | No
06/01/2024 | 08:58 | R30 | LONG RURAL | Weather |  | 56.00 | 436.3 | 0.175346 | 0.0004019 | No
06/01/2024 | 09:11 | PL01 | URBAN | Weather |  | 69.00 | 343.0 | 0.036489 | 0.0001064 | No
06/01/2024 | 09:12 | NA07 | LONG RURAL | Unknown | Unknown | 1.33 | 341.0 | 0.003263 | 0.0000096 | No
06/01/2024 | 09:12 | GA38 | LONG RURAL | Weather |  | 25.00 | 454.9 | 0.081616 | 0.0001794 | No
06/01/2024 | 09:21 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 1,885.0 | 0.013527 | 0.0000072 | No
06/01/2024 | 09:37 | EL11 | URBAN | Asset failure | HV | 22.00 | 1,509.5 | 0.051200 | 0.0000339 | No
06/01/2024 | 09:39 | GA745B | SHORT RURAL | Weather |  | 6.00 | 453.0 | 0.019122 | 0.0000422 | No
06/01/2024 | 09:42 | GA18 | LONG RURAL | Weather |  | 59.00 | 477.8 | 0.202286 | 0.0004234 | No
06/01/2024 | 09:52 | NU31 | LONG RURAL | Unknown | Unknown | 12.00 | 564.0 | 0.048569 | 0.0000861 | No
06/01/2024 | 10:01 | SM216G | URBAN | Weather |  | 1,609.00 | 171.0 | 0.424197 | 0.0024807 | No
06/01/2024 | 10:03 | SM349H | URBAN | Unknown | Unknown | 45.00 | 160.2 | 0.011113 | 0.0000694 | No
06/01/2024 | 10:25 | SM126C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 118.67 | 142.0 | 0.025980 | 0.0001830 | No
06/01/2024 | 10:28 | EL19 | URBAN | Weather |  | 417.00 | 44.5 | 0.028632 | 0.0006429 | No
06/01/2024 | 10:31 | AP425D | URBAN | Asset failure | LV | 59.33 | 214.0 | 0.019576 | 0.0000915 | No
06/01/2024 | 10:52 | SA520D | URBAN | Asset failure | LV | 1.00 | 497.0 | 0.000766 | 0.0000015 | No
06/01/2024 | 10:55 | PL01 | URBAN | Weather |  | 50.00 | 207.0 | 0.015957 | 0.0000771 | No
06/01/2024 | 11:08 | BM34 | SHORT RURAL | Unknown | Unknown | 29.00 | 116.0 | 0.023667 | 0.0002040 | No
06/01/2024 | 11:17 | AP149B | URBAN | Other |  | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
06/01/2024 | 11:26 | MV54 | SHORT RURAL | Unknown | Unknown | 128.00 | 131.3 | 0.118196 | 0.0009005 | No
06/01/2024 | 11:27 | SA34 | URBAN | Asset failure | LV | 61.00 | 320.5 | 0.030146 | 0.0000940 | No
06/01/2024 | 11:27 | NU35 | LONG RURAL | Unknown | Unknown | 73.00 | 415.1 | 0.217443 | 0.0005239 | No
06/01/2024 | 11:37 | AP139C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 23.00 | 11.0 | 0.000390 | 0.0000355 | No
06/01/2024 | 11:37 | SM349H | URBAN | Unknown | Unknown | 3.00 | 321.0 | 0.001485 | 0.0000046 | No
06/01/2024 | 11:42 | VH32 | SHORT RURAL | Asset failure | LV | 11.67 | 233.0 | 0.019125 | 0.0000821 | No
06/01/2024 | 11:48 | R21 | LONG RURAL | Unknown | Unknown | 1.00 | 105.0 | 0.000754 | 0.0000072 | No
06/01/2024 | 12:04 | GA09 | LONG RURAL | Unknown | Unknown | 1.00 | 388.0 | 0.002784 | 0.0000072 | No
06/01/2024 | 12:10 | AP355H | URBAN | Vegetation | Grow-in - NSP responsibility | 1,592.00 | 51.0 | 0.125178 | 0.0024545 | No
06/01/2024 | 12:25 | NU19 | LONG RURAL | Unknown | Unknown | 50.67 | 265.0 | 0.096354 | 0.0003636 | No
06/01/2024 | 12:45 | SM350E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 203.0 | 0.000313 | 0.0000015 | No
06/01/2024 | 13:04 | HH102B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 330.0 | 0.000509 | 0.0000015 | No
06/01/2024 | 13:05 | HH102B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 76.00 | 82.6 | 0.009675 | 0.0001172 | No
06/01/2024 | 13:23 | SA711C | URBAN | Asset failure | LV | 56.00 | 224.6 | 0.019389 | 0.0000863 | No
06/01/2024 | 13:25 | SM350E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
06/01/2024 | 14:35 | SM137B | URBAN | Vegetation | Grow-in - NSP responsibility | 39.00 | 27.0 | 0.001623 | 0.0000601 | No
06/01/2024 | 14:48 | HH428F | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 386.0 | 0.000595 | 0.0000015 | No
06/01/2024 | 15:18 | MG05 | LONG RURAL | Unknown | Unknown | 281.00 | 86.0 | 0.173423 | 0.0020165 | No
06/01/2024 | 15:19 | W29 | LONG RURAL | Weather |  | 14.00 | 37.0 | 0.003717 | 0.0001005 | No
06/01/2024 | 15:49 | NA04 | LONG RURAL | Animal | Animal impact | 46.33 | 128.0 | 0.042560 | 0.0003325 | No
06/01/2024 | 15:50 | NA19 | LONG RURAL | Weather |  | 36.00 | 199.3 | 0.051497 | 0.0002583 | No
06/01/2024 | 15:52 | NA13 | LONG RURAL | Weather |  | 604.00 | 9.2 | 0.039778 | 0.0043345 | No
06/01/2024 | 15:54 | BT03 | LONG RURAL | Weather |  | 33.00 | 267.0 | 0.063231 | 0.0002368 | No
06/01/2024 | 15:55 | NA32 | LONG RURAL | Unknown | Unknown | 5.00 | 216.0 | 0.007750 | 0.0000359 | No
06/01/2024 | 16:00 | MI19 | LONG RURAL | Unknown | Unknown | 80.00 | 276.1 | 0.158511 | 0.0005741 | No
06/01/2024 | 16:01 | BM12 | SHORT RURAL | Asset failure | LV | 1.00 | 46.0 | 0.000324 | 0.0000070 | No
06/01/2024 | 16:38 | MI32 | LONG RURAL | Weather |  | 26.00 | 122.0 | 0.022763 | 0.0001866 | No
06/01/2024 | 16:57 | MV54 | SHORT RURAL | Weather |  | 3.00 | 10.0 | 0.000211 | 0.0000211 | No
06/01/2024 | 17:02 | MI02 | SHORT RURAL | Weather |  | 5.00 | 419.0 | 0.014739 | 0.0000352 | No
06/01/2024 | 17:45 | MV31 | SHORT RURAL | Asset failure | HV | 106.00 | 22.3 | 0.016660 | 0.0007458 | No
06/01/2024 | 18:01 | BM34 | SHORT RURAL | Unknown | Unknown | 6.00 | 57.0 | 0.002406 | 0.0000422 | No
06/01/2024 | 20:49 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 150.0 | 0.001055 | 0.0000070 | No
06/01/2024 | 20:53 | PA25 | SHORT RURAL | Weather |  | 10.00 | 926.0 | 0.065149 | 0.0000704 | No
06/01/2024 | 21:32 | CBD367T | CBD | Planned |  | 1.00 | 362.0 | 0.052301 | 0.0001445 | No
06/01/2024 | 21:40 | R36 | SHORT RURAL | Planned |  | 2.00 | 157.0 | 0.002209 | 0.0000141 | No
06/01/2024 | 23:35 | W24 | LONG RURAL | Weather |  | 64.00 | 873.0 | 0.400949 | 0.0004593 | No
07/01/2024 | 01:37 | MG05 | LONG RURAL | Weather |  | 310.00 | 104.0 | 0.231365 | 0.0022247 | No
07/01/2024 | 04:51 | WHY14 | URBAN | Weather |  | 105.00 | 352.4 | 0.057046 | 0.0001619 | No
07/01/2024 | 05:21 | M71 | LONG RURAL | Animal | Animal impact | 146.00 | 293.0 | 0.306989 | 0.0010477 | No
07/01/2024 | 06:18 | GA10 | LONG RURAL | Weather |  | 4.00 | 600.0 | 0.017223 | 0.0000287 | No
07/01/2024 | 06:22 | HK02 | LONG RURAL | Weather |  | 11.00 | 1,363.8 | 0.107659 | 0.0000789 | No
07/01/2024 | 06:23 | GA07 | LONG RURAL | Weather |  | 1,041.00 | 33.5 | 0.250059 | 0.0074706 | No
07/01/2024 | 06:44 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 562.0 | 0.003954 | 0.0000070 | No
07/01/2024 | 07:26 | SSD380 | LONG RURAL | Weather |  | 609.00 | 593.0 | 2.591638 | 0.0043704 | No
07/01/2024 | 07:31 | AP226D | URBAN | Asset failure | LV | 1.00 | 478.0 | 0.000737 | 0.0000015 | No
07/01/2024 | 08:27 | VH72 | SHORT RURAL | Unknown | Unknown | 38.00 | 284.0 | 0.075927 | 0.0002673 | No
07/01/2024 | 09:33 | MV54 | SHORT RURAL | Weather |  | 38.00 | 207.0 | 0.055341 | 0.0002673 | No
07/01/2024 | 09:45 | HH121D | URBAN | Asset failure | HV | 1,322.00 | 160.2 | 0.326562 | 0.0020382 | No
07/01/2024 | 10:01 | CM05 | LONG RURAL | Unknown | Unknown | 1.00 | 229.0 | 0.001643 | 0.0000072 | No
07/01/2024 | 10:08 | MB33 | LONG RURAL | Unknown | Unknown | 17.00 | 202.0 | 0.024644 | 0.0001220 | No
07/01/2024 | 10:19 | NL451C | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
07/01/2024 | 11:14 | HH428E | URBAN | Unknown | Unknown | 6.00 | 315.0 | 0.002914 | 0.0000093 | No
07/01/2024 | 11:41 | NA04 | LONG RURAL | Weather |  | 6.67 | 185.0 | 0.008851 | 0.0000478 | No
07/01/2024 | 11:42 | ME200E | URBAN | Asset failure | LV | 43.00 | 49.4 | 0.003273 | 0.0000663 | No
07/01/2024 | 11:44 | CM24 | LONG RURAL | Weather |  | 42.00 | 262.7 | 0.079169 | 0.0003014 | No
07/01/2024 | 12:01 | HH428D | URBAN | Asset failure | LV | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
07/01/2024 | 12:42 | AP425D | URBAN | Asset failure | LV | 32.67 | 122.0 | 0.006144 | 0.0000504 | No
07/01/2024 | 12:54 | KA24 | LONG RURAL | Other |  | 50.00 | 168.0 | 0.060296 | 0.0003588 | No
07/01/2024 | 13:20 | NL210E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 414.33 | 45.0 | 0.028746 | 0.0006388 | No
07/01/2024 | 13:57 | SA711C | URBAN | Overloads |  | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
07/01/2024 | 14:20 | G17 | LONG RURAL | Weather |  | 13.00 | 228.0 | 0.021271 | 0.0000933 | No
07/01/2024 | 14:27 | HH121G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 432.00 | 45.0 | 0.029972 | 0.0006660 | No
07/01/2024 | 14:49 | G29 | LONG RURAL | Weather |  | 29.00 | 1,351.0 | 0.281154 | 0.0002081 | No
07/01/2024 | 15:27 | SM349H | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
07/01/2024 | 15:46 | AP214A | URBAN | Asset failure | LV | 26.67 | 164.0 | 0.006743 | 0.0000411 | No
07/01/2024 | 15:49 | HH121C | URBAN | Unknown | Unknown | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
07/01/2024 | 16:00 | HH428D | URBAN | Other |  | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
07/01/2024 | 16:03 | AP214A | URBAN | Overloads |  | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
07/01/2024 | 16:04 | NL511B | URBAN | Unknown | Unknown | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
07/01/2024 | 16:32 | HH386D | URBAN | Asset failure | LV | 2.00 | 234.0 | 0.000722 | 0.0000031 | No
07/01/2024 | 16:51 | LX71 | LONG RURAL | Unknown | Unknown | 126.00 | 118.0 | 0.106698 | 0.0009042 | No
07/01/2024 | 17:37 | PA03 | URBAN | Overloads |  | 1.00 | 72.0 | 0.000111 | 0.0000015 | No
07/01/2024 | 18:28 | HK05 | LONG RURAL | Asset failure | LV | 1.00 | 1,049.0 | 0.007528 | 0.0000072 | No
07/01/2024 | 18:40 | SD40200 | LONG RURAL | Weather |  | 1.00 | 152.0 | 0.001091 | 0.0000072 | No
07/01/2024 | 18:49 | MG32 | LONG RURAL | Asset failure | LV | 1.00 | 129.0 | 0.000926 | 0.0000072 | No
07/01/2024 | 19:05 | LX71 | LONG RURAL | Asset failure | HV | 126.00 | 34.4 | 0.031074 | 0.0009042 | No
07/01/2024 | 20:27 | AP829D | URBAN | Unknown | Unknown | 216.00 | 18.7 | 0.006215 | 0.0003330 | No
07/01/2024 | 20:34 | AP139B | URBAN | Asset failure | LV | 33.00 | 118.0 | 0.006004 | 0.0000509 | No
07/01/2024 | 20:35 | NL760C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,556.00 | 71.0 | 0.170327 | 0.0023990 | No
07/01/2024 | 20:37 | PP10 | URBAN | Asset failure | LV | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
07/01/2024 | 20:53 | VH22 | SHORT RURAL | Asset failure | LV | 1.00 | 167.0 | 0.001175 | 0.0000070 | No
07/01/2024 | 21:37 | AP829D | URBAN | Unknown | Unknown | 4.00 | 179.0 | 0.001104 | 0.0000062 | No
07/01/2024 | 23:16 | CBD412C | CBD | Planned |  | 1.00 | 197.0 | 0.028462 | 0.0001445 | No
07/01/2024 | 23:47 | AP829D | URBAN | Unknown | Unknown | 1.00 | 414.0 | 0.000638 | 0.0000015 | No
08/01/2024 | 00:06 | NL210A | URBAN | Unknown | Unknown | 880.00 | 136.0 | 0.184517 | 0.0013567 | No
08/01/2024 | 04:31 | EL10 | URBAN | Asset failure | LV | 14.00 | 778.0 | 0.016793 | 0.0000216 | No
08/01/2024 | 04:49 | HH121A | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
08/01/2024 | 06:19 | NL210A | URBAN | Overloads |  | 1.00 | 259.0 | 0.000399 | 0.0000015 | No
08/01/2024 | 06:37 | GU13 | LONG RURAL | Asset failure | LV | 2.00 | 244.0 | 0.003502 | 0.0000144 | No
08/01/2024 | 07:01 | MG03 | SHORT RURAL | Unknown | Unknown | 27.67 | 95.0 | 0.018492 | 0.0001946 | No
08/01/2024 | 07:17 | MG11 | SHORT RURAL | Unknown | Unknown | 3.00 | 127.0 | 0.002681 | 0.0000211 | No
08/01/2024 | 07:59 | SD38100 | LONG RURAL | Unknown | Unknown | 5.00 | 244.0 | 0.008755 | 0.0000359 | No
08/01/2024 | 08:17 | HH102D | URBAN | Planned |  | 72.00 | 306.0 | 0.033968 | 0.0001110 | No
08/01/2024 | 08:36 | AP125D | URBAN | Planned |  | 78.00 | 285.0 | 0.034273 | 0.0001203 | No
08/01/2024 | 08:43 | MV33 | SHORT RURAL | Planned |  | 1.00 | 160.0 | 0.001126 | 0.0000070 | No
08/01/2024 | 08:44 | AP510D | URBAN | Planned |  | 3.00 | 106.0 | 0.000490 | 0.0000046 | No
08/01/2024 | 08:44 | PA05 | LONG RURAL | Weather |  | 282.00 | 153.2 | 0.309974 | 0.0020237 | No
08/01/2024 | 09:32 | MB22 | SHORT RURAL | Overloads |  | 1.00 | 364.0 | 0.002561 | 0.0000070 | No
08/01/2024 | 09:47 | NU13 | LONG RURAL | Planned |  | 48.00 | 188.0 | 0.064759 | 0.0003445 | No
08/01/2024 | 09:49 | VH71 | SHORT RURAL | Planned |  | 142.00 | 157.0 | 0.156849 | 0.0009990 | No
08/01/2024 | 09:57 | CV15 | LONG RURAL | Weather |  | 2.00 | 335.0 | 0.004808 | 0.0000144 | No
08/01/2024 | 10:22 | MB22 | SHORT RURAL | Overloads |  | 2.00 | 315.0 | 0.004432 | 0.0000141 | No
08/01/2024 | 10:26 | ST12 | SHORT RURAL | Planned |  | 330.00 | 29.1 | 0.067639 | 0.0023217 | No
08/01/2024 | 10:56 | HH429C | URBAN | Vegetation | Grow-in - NSP responsibility | 25.00 | 165.0 | 0.006360 | 0.0000385 | No
08/01/2024 | 11:16 | HH145B | URBAN | Planned |  | 368.00 | 41.5 | 0.023533 | 0.0005674 | No
08/01/2024 | 12:03 | ST36 | LONG RURAL | Planned |  | 2.00 | 46.0 | 0.000660 | 0.0000144 | No
08/01/2024 | 12:17 | SD33200 | LONG RURAL | Weather |  | 2.00 | 144.0 | 0.002067 | 0.0000144 | No
08/01/2024 | 12:18 | HH130B | URBAN | Asset failure | LV | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
08/01/2024 | 13:03 | HH409C | URBAN | Asset failure | LV | 5.00 | 230.0 | 0.001773 | 0.0000077 | No
08/01/2024 | 13:09 | HH121G | URBAN | Animal | Animal impact | 1.00 | 2,587.0 | 0.003989 | 0.0000015 | No
08/01/2024 | 13:17 | AP125C | URBAN | Asset failure | LV | 1.00 | 284.0 | 0.000438 | 0.0000015 | No
08/01/2024 | 13:19 | EL260A | URBAN | Third Party | Vehicle impact | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
08/01/2024 | 13:34 | SM172C | URBAN | Asset failure | LV | 3.00 | 97.0 | 0.000449 | 0.0000046 | No
08/01/2024 | 13:53 | NA30 | LONG RURAL | Asset failure | HV | 2.00 | 11.0 | 0.000158 | 0.0000144 | No
08/01/2024 | 16:28 | MV11 | SHORT RURAL | Asset failure | LV | 1.00 | 210.0 | 0.001477 | 0.0000070 | No
08/01/2024 | 16:53 | SD36400 | LONG RURAL | Unknown | Unknown | 2.00 | 257.0 | 0.003689 | 0.0000144 | No
08/01/2024 | 17:22 | GA22 | SHORT RURAL | Unknown | Unknown | 1.00 | 116.0 | 0.000816 | 0.0000070 | No
08/01/2024 | 19:44 | HH107D | URBAN | Asset failure | LV | 27.67 | 99.0 | 0.004223 | 0.0000427 | No
08/01/2024 | 22:36 | ME427C | URBAN | Unknown | Unknown | 1.00 | 162.0 | 0.000250 | 0.0000015 | No
08/01/2024 | 23:36 | HH121G | URBAN | Asset failure | LV | 1.00 | 592.0 | 0.000913 | 0.0000015 | No
09/01/2024 | 02:01 | HH428E | URBAN | Asset failure | LV | 1.00 | 94.0 | 0.000145 | 0.0000015 | No
09/01/2024 | 06:21 | MB82 | LONG RURAL | Animal | Animal impact | 42.00 | 193.0 | 0.058171 | 0.0003014 | No
09/01/2024 | 07:07 | MI14 | LONG RURAL | Asset failure | LV | 1.00 | 279.0 | 0.002002 | 0.0000072 | No
09/01/2024 | 07:24 | ME200E | URBAN | Asset failure | LV | 150.00 | 161.5 | 0.037343 | 0.0002313 | No
09/01/2024 | 07:36 | LX51 | SHORT RURAL | Asset failure | LV | 46.00 | 51.2 | 0.016555 | 0.0003236 | No
09/01/2024 | 07:57 | NL760C | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
09/01/2024 | 08:24 | LM41 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 879.0 | 0.006308 | 0.0000072 | No
09/01/2024 | 08:46 | EL20 | URBAN | Planned |  | 15.00 | 432.0 | 0.009991 | 0.0000231 | No
09/01/2024 | 08:48 | HH341G | URBAN | Planned |  | 340.00 | 302.6 | 0.158611 | 0.0005242 | No
09/01/2024 | 08:48 | KI56 | LONG RURAL | Planned |  | 1.00 | 286.0 | 0.002052 | 0.0000072 | No
09/01/2024 | 08:55 | M43 | LONG RURAL | Unknown | Unknown | 1.00 | 4,299.0 | 0.030851 | 0.0000072 | No
09/01/2024 | 09:01 | HH102D | URBAN | Planned |  | 50.00 | 84.2 | 0.006491 | 0.0000771 | No
09/01/2024 | 09:04 | HH341G | URBAN | Planned |  | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
09/01/2024 | 09:06 | AP510D | URBAN | Planned |  | 1.00 | 165.0 | 0.000254 | 0.0000015 | No
09/01/2024 | 09:08 | GA25 | SHORT RURAL | Planned |  | 57.00 | 26.0 | 0.010427 | 0.0004010 | No
09/01/2024 | 09:08 | GA25 | URBAN | Planned |  | 95.00 | 49.9 | 0.007313 | 0.0001465 | No
09/01/2024 | 09:10 | SM349F | URBAN | Asset failure | LV | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
09/01/2024 | 09:11 | MV31 | SHORT RURAL | Planned |  | 110.00 | 369.2 | 0.285725 | 0.0007739 | No
09/01/2024 | 09:15 | SD35200 | LONG RURAL | Planned |  | 65.00 | 49.6 | 0.023158 | 0.0004665 | No
09/01/2024 | 09:53 | HH107E | URBAN | Unknown | Unknown | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
09/01/2024 | 10:03 | G11 | LONG RURAL | Planned |  | 14.00 | 58.0 | 0.005827 | 0.0001005 | No
09/01/2024 | 10:09 | SB23 | LONG RURAL | Planned |  | 1.00 | 191.0 | 0.001371 | 0.0000072 | No
09/01/2024 | 10:15 | CV20 | LONG RURAL | Planned |  | 6.00 | 293.0 | 0.012616 | 0.0000431 | No
09/01/2024 | 10:35 | KI51 | LONG RURAL | Planned |  | 8.00 | 106.0 | 0.006086 | 0.0000574 | No
09/01/2024 | 11:09 | EL10 | URBAN | Asset failure | LV | 59.00 | 61.3 | 0.005580 | 0.0000910 | No
09/01/2024 | 11:52 | SM374E | URBAN | Other |  | 1.00 | 37.0 | 0.000057 | 0.0000015 | No
09/01/2024 | 13:16 | HH121D | URBAN | Planned |  | 122.00 | 25.0 | 0.004702 | 0.0001881 | No
09/01/2024 | 13:29 | WHY02 | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
09/01/2024 | 14:31 | PP03 | URBAN | Third Party | Vehicle impact | 28.00 | 161.9 | 0.006987 | 0.0000432 | No
09/01/2024 | 15:29 | GU31 | LONG RURAL | Asset failure | LV | 2.00 | 2,494.0 | 0.035796 | 0.0000144 | No
09/01/2024 | 15:53 | VH17 | SHORT RURAL | Weather |  | 592.00 | 37.6 | 0.156758 | 0.0041650 | No
09/01/2024 | 16:41 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 475.0 | 0.003342 | 0.0000070 | No
09/01/2024 | 17:00 | NU22 | LONG RURAL | Unknown | Unknown | 1.00 | 237.0 | 0.001701 | 0.0000072 | No
09/01/2024 | 17:12 | LX42 | SHORT RURAL | Asset failure | LV | 11.00 | 41.0 | 0.003173 | 0.0000774 | No
09/01/2024 | 17:34 | AP139C | URBAN | Asset failure | LV | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
09/01/2024 | 19:04 | BS0191 | URBAN | Planned |  | 1.00 | 697.0 | 0.001075 | 0.0000015 | No
09/01/2024 | 19:14 | SM172E | URBAN | Asset failure | LV | 49.00 | 62.0 | 0.004684 | 0.0000755 | No
09/01/2024 | 19:54 | NL115F | URBAN | Asset failure | LV | 1.00 | 230.0 | 0.000355 | 0.0000015 | No
09/01/2024 | 20:51 | SM126B | URBAN | Asset failure | LV | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
09/01/2024 | 21:10 | AP355E | URBAN | Planned |  | 85.00 | 364.6 | 0.047779 | 0.0001310 | No
09/01/2024 | 23:41 | NU14 | LONG RURAL | Animal | Animal impact | 17.33 | 177.0 | 0.022017 | 0.0001244 | No
10/01/2024 | 00:53 | SM411D | URBAN | Unknown | Unknown | 954.00 | 12.9 | 0.019007 | 0.0014708 | No
10/01/2024 | 07:13 | NU35 | LONG RURAL | Unknown | Unknown | 1.00 | 458.0 | 0.003287 | 0.0000072 | No
10/01/2024 | 08:36 | PL15 | LONG RURAL | Planned |  | 70.00 | 325.4 | 0.163448 | 0.0005023 | No
10/01/2024 | 08:53 | SD39300 | LONG RURAL | Planned |  | 2.00 | 2,968.0 | 0.042599 | 0.0000144 | No
10/01/2024 | 08:56 | GA53 | SHORT RURAL | Planned |  | 56.00 | 198.1 | 0.078066 | 0.0003940 | No
10/01/2024 | 09:13 | MG05 | LONG RURAL | Planned |  | 2.00 | 159.0 | 0.002282 | 0.0000144 | No
10/01/2024 | 09:37 | HH403D | URBAN | Other |  | 21.00 | 92.0 | 0.002979 | 0.0000324 | No
10/01/2024 | 09:37 | GA27 | LONG RURAL | Planned |  | 2.00 | 53.0 | 0.000761 | 0.0000144 | No
10/01/2024 | 09:44 | GA745B | SHORT RURAL | Planned |  | 4.00 | 251.0 | 0.007064 | 0.0000281 | No
10/01/2024 | 09:46 | HH145B | URBAN | Planned |  | 238.00 | 200.0 | 0.073391 | 0.0003669 | No
10/01/2024 | 09:46 | NA16 | LONG RURAL | Planned |  | 11.00 | 289.5 | 0.022857 | 0.0000789 | No
10/01/2024 | 10:51 | ST22 | SHORT RURAL | Unknown | Unknown | 2.00 | 98.0 | 0.001379 | 0.0000141 | No
10/01/2024 | 11:11 | WHY01 | SHORT RURAL | Asset failure | LV | 5.00 | 50.0 | 0.001759 | 0.0000352 | No
10/01/2024 | 11:34 | CV30 | LONG RURAL | Asset failure | HV | 1.00 | 162.0 | 0.001163 | 0.0000072 | No
10/01/2024 | 11:36 | GA53 | SHORT RURAL | Network business | Switching and protection error | 1.00 | 39.0 | 0.000274 | 0.0000070 | No
10/01/2024 | 11:45 | EL01L | URBAN | Third Party | Vehicle impact | 21.00 | 76.0 | 0.002461 | 0.0000324 | No
10/01/2024 | 11:48 | AP424E | URBAN | Asset failure | LV | 2.00 | 162.0 | 0.000500 | 0.0000031 | No
10/01/2024 | 12:09 | SM411A | URBAN | Asset failure | LV | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
10/01/2024 | 12:10 | SG09 | SHORT RURAL | Unknown | Unknown | 1.00 | 166.0 | 0.001168 | 0.0000070 | No
10/01/2024 | 13:27 | HH121G | URBAN | Overloads |  | 1.00 | 34.0 | 0.000052 | 0.0000015 | No
10/01/2024 | 13:46 | MG17 | LONG RURAL | Unknown | Unknown | 1.00 | 94.0 | 0.000675 | 0.0000072 | No
10/01/2024 | 13:57 | NL760C | URBAN | Asset failure | LV | 11.00 | 198.0 | 0.003358 | 0.0000170 | No
10/01/2024 | 14:17 | AP424D | URBAN | Asset failure | LV | 14.33 | 154.0 | 0.003403 | 0.0000221 | No
10/01/2024 | 14:18 | HH145E | URBAN | Asset failure | LV | 1.00 | 233.0 | 0.000359 | 0.0000015 | No
10/01/2024 | 14:19 | NL210C | URBAN | Asset failure | LV | 51.00 | 76.4 | 0.006004 | 0.0000786 | No
10/01/2024 | 17:06 | HH432B | URBAN | Asset failure | LV | 21.00 | 45.0 | 0.001457 | 0.0000324 | No
10/01/2024 | 18:20 | CN83 | LONG RURAL | Planned |  | 7.00 | 114.0 | 0.005727 | 0.0000502 | No
10/01/2024 | 19:23 | NL111C | URBAN | Asset failure | LV | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
10/01/2024 | 19:35 | NL111C | URBAN | Asset failure | LV | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
10/01/2024 | 22:11 | NL210E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,164.00 | 100.9 | 0.180996 | 0.0017946 | No
10/01/2024 | 23:39 | EL19 | URBAN | Unknown | Unknown | 1.00 | 627.0 | 0.000967 | 0.0000015 | No
11/01/2024 | 01:18 | EL14 | URBAN | Asset failure | HV | 2,084.00 | 233.6 | 0.750618 | 0.0032130 | No
11/01/2024 | 06:30 | AP829H | URBAN | Planned |  | 1.00 | 890.0 | 0.001372 | 0.0000015 | No
11/01/2024 | 06:32 | EL19 | URBAN | Unknown | Unknown | 15.33 | 170.9 | 0.004039 | 0.0000236 | No
11/01/2024 | 08:01 | KA06 | LONG RURAL | Planned |  | 29.00 | 171.0 | 0.035595 | 0.0002081 | No
11/01/2024 | 08:05 | GU32 | LONG RURAL | Planned |  | 124.00 | 405.3 | 0.360690 | 0.0008899 | No
11/01/2024 | 08:16 | GU32 | LONG RURAL | Planned |  | 610.00 | 429.0 | 1.877974 | 0.0043776 | No
11/01/2024 | 08:27 | HK04 | LONG RURAL | Planned |  | 30.00 | 300.0 | 0.064587 | 0.0002153 | No
11/01/2024 | 08:34 | SM216F | URBAN | Planned |  | 56.00 | 262.0 | 0.022621 | 0.0000863 | No
11/01/2024 | 08:42 | BT01 | LONG RURAL | Planned |  | 10.00 | 411.0 | 0.029495 | 0.0000718 | No
11/01/2024 | 08:53 | SA17 | URBAN | Planned |  | 376.00 | 309.6 | 0.179456 | 0.0005797 | No
11/01/2024 | 09:06 | BT02 | LONG RURAL | Unknown | Unknown | 3.00 | 474.0 | 0.010205 | 0.0000215 | No
11/01/2024 | 09:21 | CM20 | LONG RURAL | Planned |  | 29.00 | 312.0 | 0.064931 | 0.0002081 | No
11/01/2024 | 09:27 | EL20 | URBAN | Animal | Animal impact | 16.00 | 277.0 | 0.006833 | 0.0000247 | No
11/01/2024 | 09:42 | GA53 | SHORT RURAL | Planned |  | 6.00 | 93.2 | 0.003933 | 0.0000422 | No
11/01/2024 | 09:44 | HH341G | URBAN | Planned |  | 244.00 | 286.0 | 0.107590 | 0.0003762 | No
11/01/2024 | 09:47 | AP365A | URBAN | Third Party | Vehicle impact | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
11/01/2024 | 09:51 | GU13 | LONG RURAL | Overloads |  | 1.00 | 158.0 | 0.001134 | 0.0000072 | No
11/01/2024 | 09:56 | HH432B | URBAN | Asset failure | LV | 133.00 | 964.0 | 0.197671 | 0.0002051 | No
11/01/2024 | 10:34 | SM216F | URBAN | Unknown | Unknown | 1.00 | 8,513.0 | 0.013125 | 0.0000015 | No
11/01/2024 | 10:37 | HH121H | URBAN | Unknown | Unknown | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
11/01/2024 | 11:15 | HH429C | URBAN | Asset failure | LV | 2.00 | 164.0 | 0.000506 | 0.0000031 | No
11/01/2024 | 11:28 | CBD366P | CBD | Third Party | Unauthorised access | 2.00 | 92.0 | 0.026584 | 0.0002890 | No
11/01/2024 | 11:41 | WK41 | SHORT RURAL | Overloads |  | 1.00 | 148.0 | 0.001041 | 0.0000070 | No
11/01/2024 | 12:46 | NA07 | LONG RURAL | Asset failure | LV | 1.00 | 338.0 | 0.002426 | 0.0000072 | No
11/01/2024 | 13:00 | MG10 | LONG RURAL | Asset failure | LV | 1.00 | 36.0 | 0.000258 | 0.0000072 | No
11/01/2024 | 13:29 | MTB41 | SHORT RURAL | Unknown | Unknown | 35.00 | 69.0 | 0.016991 | 0.0002462 | No
11/01/2024 | 14:03 | MB42 | LONG RURAL | Planned |  | 2.00 | 239.0 | 0.003430 | 0.0000144 | No
11/01/2024 | 14:16 | LX53 | SHORT RURAL | Asset failure | LV | 5.00 | 314.0 | 0.011046 | 0.0000352 | No
11/01/2024 | 14:28 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 7.00 | 925.0 | 0.045555 | 0.0000492 | No
11/01/2024 | 14:43 | WHY01 | SHORT RURAL | Asset failure | LV | 1.00 | 83.0 | 0.000584 | 0.0000070 | No
11/01/2024 | 15:39 | MG48 | LONG RURAL | Asset failure | LV | 1.00 | 157.0 | 0.001127 | 0.0000072 | No
11/01/2024 | 17:16 | HH177F | URBAN | Asset failure | LV | 15.00 | 192.0 | 0.004440 | 0.0000231 | No
11/01/2024 | 17:19 | KA12 | LONG RURAL | Unknown | Unknown | 48.00 | 121.0 | 0.041680 | 0.0003445 | No
11/01/2024 | 18:54 | HH121F | URBAN | Asset failure | LV | 18.00 | 157.0 | 0.004357 | 0.0000278 | No
11/01/2024 | 19:09 | SA711C | URBAN | Asset failure | LV | 83.00 | 231.9 | 0.029680 | 0.0001280 | No
11/01/2024 | 20:11 | SA20 | URBAN | Unknown | Unknown | 16.00 | 104.0 | 0.002565 | 0.0000247 | No
11/01/2024 | 20:23 | SB17 | LONG RURAL | Asset failure | LV | 2.00 | 150.0 | 0.002153 | 0.0000144 | No
11/01/2024 | 20:42 | WHY04 | URBAN | Asset failure | LV | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
11/01/2024 | 23:15 | HH432B | URBAN | Asset failure | LV | 82.00 | 45.0 | 0.005689 | 0.0001264 | No
12/01/2024 | 07:57 | AP829A | URBAN | Asset failure | LV | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
12/01/2024 | 08:00 | MV32 | SHORT RURAL | Unknown | Unknown | 6.00 | 183.0 | 0.007725 | 0.0000422 | No
12/01/2024 | 08:00 | WK42 | SHORT RURAL | Planned |  | 4.00 | 180.0 | 0.005066 | 0.0000281 | No
12/01/2024 | 08:19 | AP214C | URBAN | Planned |  | 8.00 | 374.6 | 0.004621 | 0.0000123 | No
12/01/2024 | 08:20 | PL07 | URBAN | Planned |  | 121.00 | 300.0 | 0.055969 | 0.0001866 | No
12/01/2024 | 08:35 | PL21 | LONG RURAL | Planned |  | 12.00 | 167.2 | 0.014396 | 0.0000861 | No
12/01/2024 | 08:37 | SG03 | SHORT RURAL | Planned |  | 438.00 | 88.3 | 0.272168 | 0.0030815 | No
12/01/2024 | 08:58 | MTB82 | SHORT RURAL | Planned |  | 67.00 | 146.0 | 0.068821 | 0.0004714 | No
12/01/2024 | 09:47 | G11 | LONG RURAL | Planned |  | 4.00 | 97.0 | 0.002784 | 0.0000287 | No
12/01/2024 | 11:03 | AP214A | URBAN | Asset failure | LV | 24.00 | 870.0 | 0.032192 | 0.0000370 | No
12/01/2024 | 11:11 | HH428E | URBAN | Overloads |  | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
12/01/2024 | 11:21 | EL10 | URBAN | Planned |  | 75.00 | 23.0 | 0.002660 | 0.0001156 | No
12/01/2024 | 11:27 | HH432B | URBAN | Asset failure | LV | 133.00 | 722.0 | 0.148048 | 0.0002051 | No
12/01/2024 | 11:40 | MT25 | LONG RURAL | Asset failure | LV | 1.00 | 223.0 | 0.001600 | 0.0000072 | No
12/01/2024 | 11:44 | NL760C | URBAN | Asset failure | LV | 52.00 | 42.0 | 0.003367 | 0.0000802 | No
12/01/2024 | 11:49 | SG09 | SHORT RURAL | Asset failure | LV | 1.00 | 152.0 | 0.001069 | 0.0000070 | No
12/01/2024 | 11:52 | KA17 | LONG RURAL | Overloads |  | 1.00 | 157.0 | 0.001127 | 0.0000072 | No
12/01/2024 | 12:16 | HH130F | URBAN | Overloads |  | 1.00 | 74.0 | 0.000114 | 0.0000015 | No
12/01/2024 | 12:19 | SA33 | URBAN | Asset failure | LV | 1.00 | 589.0 | 0.000908 | 0.0000015 | No
12/01/2024 | 12:33 | HH409A | URBAN | Overloads |  | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
12/01/2024 | 12:37 | MTB32 | LONG RURAL | Overloads |  | 1.00 | 316.0 | 0.002268 | 0.0000072 | No
12/01/2024 | 12:39 | VH34 | SHORT RURAL | Overloads |  | 2.00 | 292.0 | 0.004109 | 0.0000141 | No
12/01/2024 | 13:38 | HH386D | URBAN | Third Party | Other | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
12/01/2024 | 13:41 | HH409E | URBAN | Asset failure | LV | 63.00 | 72.0 | 0.006993 | 0.0000971 | No
12/01/2024 | 13:57 | PA11 | LONG RURAL | Planned |  | 21.00 | 138.0 | 0.020797 | 0.0001507 | No
12/01/2024 | 14:20 | PA04 | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
12/01/2024 | 14:31 | HH107C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 364.0 | 0.000561 | 0.0000015 | No
12/01/2024 | 15:18 | EL07 | URBAN | Overloads |  | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
12/01/2024 | 16:02 | HH177C | URBAN | Asset failure | LV | 65.00 | 179.0 | 0.017938 | 0.0001002 | No
12/01/2024 | 16:17 | GA22 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 777.00 | 66.0 | 0.360794 | 0.0054666 | No
12/01/2024 | 16:40 | EL07 | URBAN | Overloads |  | 4.00 | 37.0 | 0.000228 | 0.0000062 | No
12/01/2024 | 18:28 | LX24 | SHORT RURAL | Other |  | 14.67 | 146.0 | 0.015065 | 0.0001032 | No
12/01/2024 | 19:18 | HH428A | URBAN | Asset failure | LV | 3.00 | 303.0 | 0.001401 | 0.0000046 | No
12/01/2024 | 19:29 | NU03 | LONG RURAL | Unknown | Unknown | 29.00 | 269.0 | 0.055983 | 0.0002081 | No
12/01/2024 | 20:37 | HH429C | URBAN | Asset failure | LV | 75.00 | 171.0 | 0.019773 | 0.0001156 | No
12/01/2024 | 22:28 | AP146B | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
12/01/2024 | 22:36 | NL210B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 947.00 | 27.5 | 0.040177 | 0.0014600 | No
12/01/2024 | 23:03 | SM137A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
12/01/2024 | 23:05 | HH386F | URBAN | Asset failure | LV | 22.33 | 174.0 | 0.005991 | 0.0000344 | No
12/01/2024 | 23:17 | HH121F | URBAN | Unknown | Unknown | 41.00 | 428.0 | 0.027055 | 0.0000632 | No
12/01/2024 | 23:55 | HH341H | URBAN | Unknown | Unknown | 1.00 | 2,475.0 | 0.003816 | 0.0000015 | No
13/01/2024 | 00:00 | HH145B | URBAN | Overloads |  | 28.67 | 144.0 | 0.006364 | 0.0000442 | No
13/01/2024 | 00:05 | HH496A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
13/01/2024 | 00:32 | HH409C | URBAN | Unknown | Unknown | 20.00 | 142.0 | 0.004379 | 0.0000308 | No
13/01/2024 | 00:38 | CM24 | LONG RURAL | Asset failure | HV | 42.00 | 580.0 | 0.174815 | 0.0003014 | No
13/01/2024 | 00:41 | HH145E | URBAN | Asset failure | LV | 67.00 | 64.0 | 0.006611 | 0.0001033 | No
13/01/2024 | 02:02 | HH121F | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 2,027.0 | 0.003125 | 0.0000015 | No
13/01/2024 | 02:30 | CBD366U | CBD | Asset failure | HV | 347.00 | 81.3 | 4.075706 | 0.0501336 | No
13/01/2024 | 02:55 | HH130B | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 791.00 | 12.0 | 0.014634 | 0.0012195 | No
13/01/2024 | 03:55 | SM350E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 55.00 | 204.0 | 0.017298 | 0.0000848 | No
13/01/2024 | 04:17 | HH409F | URBAN | Overloads |  | 19.00 | 300.0 | 0.008788 | 0.0000293 | No
13/01/2024 | 05:33 | SM179D | URBAN | Asset failure | LV | 66.00 | 44.0 | 0.004474 | 0.0001018 | No
13/01/2024 | 06:18 | M41 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 365.00 | 168.0 | 0.440053 | 0.0026194 | No
13/01/2024 | 06:37 | SM350E | URBAN | Asset failure | LV | 1.00 | 569.0 | 0.000877 | 0.0000015 | No
13/01/2024 | 06:57 | HH121G | URBAN | Asset failure | LV | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
13/01/2024 | 07:05 | HH409D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 449.0 | 0.000692 | 0.0000015 | No
13/01/2024 | 07:42 | HH409F | URBAN | Vegetation | Grow-in - NSP responsibility | 60.00 | 241.0 | 0.022294 | 0.0000925 | No
13/01/2024 | 07:48 | NL111C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 60.00 | 271.0 | 0.025069 | 0.0000925 | No
13/01/2024 | 07:57 | MB72 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 20.00 | 213.0 | 0.030571 | 0.0001435 | No
13/01/2024 | 08:21 | HH148C | URBAN | Vegetation | Grow-in - NSP responsibility | 53.00 | 156.0 | 0.012747 | 0.0000817 | No
13/01/2024 | 08:31 | NL210A | URBAN | Asset failure | LV | 13.00 | 303.0 | 0.006073 | 0.0000200 | No
13/01/2024 | 08:39 | HH130A | URBAN | Planned |  | 2.00 | 123.0 | 0.000379 | 0.0000031 | No
13/01/2024 | 09:01 | ME200E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
13/01/2024 | 09:22 | HH177C | URBAN | Asset failure | LV | 1.00 | 220.0 | 0.000339 | 0.0000015 | No
13/01/2024 | 09:51 | NL511B | URBAN | Asset failure | LV | 1.00 | 490.0 | 0.000755 | 0.0000015 | No
13/01/2024 | 09:59 | AP529B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,344.00 | 125.8 | 0.260672 | 0.0020721 | No
13/01/2024 | 11:17 | HH130D | URBAN | Overloads |  | 1.00 | 2,280.0 | 0.003515 | 0.0000015 | No
13/01/2024 | 11:25 | HH145B | URBAN | Overloads |  | 1.00 | 489.0 | 0.000754 | 0.0000015 | No
13/01/2024 | 11:43 | CD18 | LONG RURAL | Asset failure | HV | 36.00 | 258.8 | 0.066869 | 0.0002583 | No
13/01/2024 | 11:50 | AP529B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 307.0 | 0.000473 | 0.0000015 | No
13/01/2024 | 13:40 | MI01 | LONG RURAL | Third Party | Dig-in | 1.00 | 230.0 | 0.001651 | 0.0000072 | No
13/01/2024 | 14:52 | HH177E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 632.00 | 54.0 | 0.052617 | 0.0009744 | No
13/01/2024 | 15:38 | AP139C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 917.00 | 62.0 | 0.087655 | 0.0014138 | No
13/01/2024 | 15:47 | MB12 | SHORT RURAL | Animal | Animal impact | 2,065.00 | 46.1 | 0.670370 | 0.0145283 | No
13/01/2024 | 16:17 | NU31 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 400.00 | 53.0 | 0.152138 | 0.0028705 | No
13/01/2024 | 16:38 | SD31300 | LONG RURAL | Unknown | Unknown | 2.00 | 150.0 | 0.002153 | 0.0000144 | No
13/01/2024 | 16:57 | SD31300 | LONG RURAL | Unknown | Unknown | 3.00 | 160.0 | 0.003445 | 0.0000215 | No
13/01/2024 | 17:15 | CV24 | LONG RURAL | Other |  | 15.00 | 54.0 | 0.005813 | 0.0001076 | No
13/01/2024 | 17:36 | SD31300 | LONG RURAL | Unknown | Unknown | 6.00 | 159.0 | 0.006846 | 0.0000431 | No
13/01/2024 | 17:55 | NL111P | URBAN | Unknown | Unknown | 1.00 | 42.0 | 0.000065 | 0.0000015 | No
13/01/2024 | 18:32 | MB82 | LONG RURAL | Animal | Animal impact | 42.00 | 63.0 | 0.018989 | 0.0003014 | No
13/01/2024 | 18:43 | HH121D | URBAN | Asset failure | LV | 1.00 | 1,250.0 | 0.001927 | 0.0000015 | No
13/01/2024 | 19:08 | KA14 | LONG RURAL | Asset failure | HV | 79.00 | 537.0 | 0.304441 | 0.0005669 | No
13/01/2024 | 21:03 | HH432B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 33.00 | 84.0 | 0.004274 | 0.0000509 | No
13/01/2024 | 21:32 | HH130A | URBAN | Asset failure | LV | 62.00 | 119.0 | 0.011375 | 0.0000956 | No
13/01/2024 | 21:48 | HH386G | URBAN | Vegetation | Grow-in - NSP responsibility | 72.00 | 70.0 | 0.007770 | 0.0001110 | No
13/01/2024 | 21:57 | EL16 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 5.00 | 1,336.2 | 0.010300 | 0.0000077 | No
13/01/2024 | 22:47 | EL11 | URBAN | Unknown | Unknown | 655.00 | 42.6 | 0.043038 | 0.0010098 | No
13/01/2024 | 22:47 | EL12 | URBAN | Third Party | Other | 199.00 | 119.4 | 0.036631 | 0.0003068 | No
13/01/2024 | 22:57 | SD31300 | LONG RURAL | Weather |  | 4.00 | 854.8 | 0.024536 | 0.0000287 | No
13/01/2024 | 23:07 | HH409F | URBAN | Other |  | 1.00 | 52.0 | 0.000080 | 0.0000015 | No
13/01/2024 | 23:10 | HH409C | URBAN | Unknown | Unknown | 1.00 | 68.0 | 0.000105 | 0.0000015 | No
13/01/2024 | 23:47 | HH121H | URBAN | Overloads |  | 81.00 | 64.0 | 0.007992 | 0.0001249 | No
13/01/2024 | 23:48 | SM216C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 109.00 | 183.0 | 0.030753 | 0.0001681 | No
14/01/2024 | 00:05 | HH145C | URBAN | Overloads |  | 38.00 | 640.0 | 0.037495 | 0.0000586 | No
14/01/2024 | 00:06 | ME116D | URBAN | Other |  | 19.00 | 29.0 | 0.000850 | 0.0000293 | No
14/01/2024 | 00:14 | SM349C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 13.00 | 361.0 | 0.007235 | 0.0000200 | No
14/01/2024 | 00:24 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 72.00 | 203.0 | 0.022534 | 0.0001110 | No
14/01/2024 | 00:24 | MV22 | SHORT RURAL | Unknown | Unknown | 11.00 | 535.0 | 0.041404 | 0.0000774 | No
14/01/2024 | 00:31 | HH145D | URBAN | Overloads |  | 6.00 | 696.0 | 0.006438 | 0.0000093 | No
14/01/2024 | 01:06 | HH386A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 418.00 | 78.0 | 0.050267 | 0.0006445 | No
14/01/2024 | 01:18 | VH71 | SHORT RURAL | Weather |  | 352.00 | 310.0 | 0.767713 | 0.0024765 | No
14/01/2024 | 01:18 | VH71 | SHORT RURAL | Weather |  | 1.00 | 860.0 | 0.006051 | 0.0000070 | No
14/01/2024 | 01:20 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 337.00 | 121.0 | 0.062868 | 0.0005196 | No
14/01/2024 | 01:34 | HH145A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
14/01/2024 | 01:35 | SM179C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 16.00 | 60.0 | 0.001480 | 0.0000247 | No
14/01/2024 | 01:45 | MV22 | SHORT RURAL | Unknown | Unknown | 1.00 | 506.0 | 0.003560 | 0.0000070 | No
14/01/2024 | 03:36 | CBD103G | URBAN | Overloads |  | 1.00 | 4,609.0 | 0.007106 | 0.0000015 | No
14/01/2024 | 03:53 | HH409C | URBAN | Third Party | Other | 57.00 | 803.0 | 0.070568 | 0.0000879 | No
14/01/2024 | 04:34 | HH386A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 496.0 | 0.000765 | 0.0000015 | No
14/01/2024 | 04:38 | SM172B | URBAN | Planned |  | 925.00 | 7.0 | 0.009983 | 0.0014261 | No
14/01/2024 | 05:57 | HH148C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 654.0 | 0.001008 | 0.0000015 | No
14/01/2024 | 06:05 | SM402A | URBAN | Asset failure | LV | 6.00 | 378.0 | 0.003497 | 0.0000093 | No
14/01/2024 | 06:19 | BT02 | LONG RURAL | Animal | Animal impact | 509.00 | 81.6 | 0.298026 | 0.0036528 | No
14/01/2024 | 06:39 | SM411C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 279.0 | 0.000430 | 0.0000015 | No
14/01/2024 | 06:52 | NL210E | URBAN | Vegetation | Grow-in - NSP responsibility | 78.00 | 65.0 | 0.007817 | 0.0001203 | No
14/01/2024 | 07:23 | SM411B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
14/01/2024 | 07:33 | SM349C | URBAN | Overloads |  | 1.00 | 392.0 | 0.000604 | 0.0000015 | No
14/01/2024 | 07:46 | NU03 | LONG RURAL | Unknown | Unknown | 29.00 | 195.1 | 0.040604 | 0.0002081 | No
14/01/2024 | 07:51 | NL210C | URBAN | Asset failure | LV | 1.00 | 352.0 | 0.000543 | 0.0000015 | No
14/01/2024 | 08:04 | PP18 | LONG RURAL | Other |  | 1.00 | 723.0 | 0.005188 | 0.0000072 | No
14/01/2024 | 08:07 | AP355D | URBAN | Planned |  | 1.00 | 547.0 | 0.000843 | 0.0000015 | No
14/01/2024 | 08:10 | HH432E | URBAN | Planned |  | 66.00 | 401.8 | 0.040887 | 0.0001018 | No
14/01/2024 | 08:33 | ME427A | URBAN | Planned |  | 1.00 | 499.0 | 0.000769 | 0.0000015 | No
14/01/2024 | 08:40 | YK03 | LONG RURAL | Asset failure | LV | 1.00 | 110.0 | 0.000789 | 0.0000072 | No
14/01/2024 | 08:41 | AP365D2 | URBAN | Planned |  | 3.00 | 344.0 | 0.001591 | 0.0000046 | No
14/01/2024 | 08:44 | HH121H | URBAN | Planned |  | 191.00 | 119.9 | 0.035294 | 0.0002945 | No
14/01/2024 | 08:45 | G02 | LONG RURAL | Planned |  | 52.00 | 378.0 | 0.141058 | 0.0003732 | No
14/01/2024 | 09:37 | SM137B | URBAN | Overloads |  | 95.00 | 264.0 | 0.038667 | 0.0001465 | No
14/01/2024 | 10:04 | NL760B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 85.00 | 133.0 | 0.017430 | 0.0001310 | No
14/01/2024 | 10:09 | HH145B | URBAN | Overloads |  | 1.00 | 500.0 | 0.000771 | 0.0000015 | No
14/01/2024 | 10:38 | SA11 | URBAN | Asset failure | LV | 52.00 | 140.0 | 0.011224 | 0.0000802 | No
14/01/2024 | 10:53 | SA11 | URBAN | Asset failure | LV | 69.00 | 132.0 | 0.014042 | 0.0001064 | No
14/01/2024 | 10:55 | SA11 | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
14/01/2024 | 11:41 | HH341G | URBAN | Planned |  | 206.00 | 91.6 | 0.029091 | 0.0003176 | No
14/01/2024 | 11:52 | MG09 | SHORT RURAL | Asset failure | LV | 1.00 | 118.0 | 0.000830 | 0.0000070 | No
14/01/2024 | 12:09 | MB28 | SHORT RURAL | Asset failure | HV | 319.00 | 65.8 | 0.147717 | 0.0022443 | No
14/01/2024 | 12:25 | HH121G | URBAN | Planned |  | 1,986.00 | 4.0 | 0.012248 | 0.0030619 | No
14/01/2024 | 12:36 | EL01L | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
14/01/2024 | 13:11 | SM179A | URBAN | Asset failure | LV | 19.00 | 57.0 | 0.001670 | 0.0000293 | No
14/01/2024 | 13:30 | HH177G | URBAN | Overloads |  | 1.00 | 412.0 | 0.000635 | 0.0000015 | No
14/01/2024 | 14:01 | BM54 | SHORT RURAL | Animal | Animal impact | 33.00 | 89.0 | 0.020663 | 0.0002322 | No
14/01/2024 | 14:31 | SM137A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 11.00 | 186.9 | 0.003170 | 0.0000170 | No
14/01/2024 | 14:43 | MI01 | LONG RURAL | Asset failure | LV | 1.00 | 150.0 | 0.001076 | 0.0000072 | No
14/01/2024 | 15:13 | SD31300 | LONG RURAL | Weather |  | 1,190.00 | 52.0 | 0.444071 | 0.0085398 | No
14/01/2024 | 16:39 | HH145D | URBAN | Third Party | Other | 5.00 | 39.0 | 0.000301 | 0.0000077 | No
14/01/2024 | 17:13 | HH341F | URBAN | Other |  | 1.00 | 55.0 | 0.000085 | 0.0000015 | No
14/01/2024 | 17:54 | HH121G | URBAN | Asset failure | LV | 1.00 | 252.0 | 0.000389 | 0.0000015 | No
14/01/2024 | 18:34 | CV32 | LONG RURAL | Asset failure | LV | 2.00 | 229.0 | 0.003287 | 0.0000144 | No
14/01/2024 | 18:41 | HH428A | URBAN | Asset failure | LV | 2.00 | 273.0 | 0.000842 | 0.0000031 | No
14/01/2024 | 19:29 | WHY04 | URBAN | Other |  | 48.00 | 140.0 | 0.010361 | 0.0000740 | No
14/01/2024 | 20:47 | CD23 | LONG RURAL | Asset failure | LV | 1.00 | 220.0 | 0.001579 | 0.0000072 | No
14/01/2024 | 21:25 | HH386A | URBAN | Asset failure | LV | 6.00 | 154.0 | 0.001425 | 0.0000093 | No
14/01/2024 | 22:58 | EL16 | URBAN | Unknown | Unknown | 322.00 | 9.9 | 0.004934 | 0.0004964 | No
14/01/2024 | 23:01 | CBD367P | CBD | Planned |  | 1.00 | 4,253.0 | 0.614462 | 0.0001445 | No
15/01/2024 | 00:05 | HH409D | URBAN | Unknown | Unknown | 23.00 | 116.0 | 0.004113 | 0.0000355 | No
15/01/2024 | 01:37 | SM402C | URBAN | Unknown | Unknown | 329.00 | 111.0 | 0.056303 | 0.0005072 | No
15/01/2024 | 02:25 | SM350A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 8.00 | 91.1 | 0.001124 | 0.0000123 | No
15/01/2024 | 05:30 | AP214C | URBAN | Asset failure | HV | 1,419.00 | 266.8 | 0.583626 | 0.0021877 | No
15/01/2024 | 06:01 | MTB41 | SHORT RURAL | Unknown | Unknown | 1.00 | 161.0 | 0.001133 | 0.0000070 | No
15/01/2024 | 06:20 | HH341D | URBAN | Other |  | 19.00 | 66.4 | 0.001944 | 0.0000293 | No
15/01/2024 | 07:04 | MB82 | LONG RURAL | Animal | Animal impact | 42.00 | 358.0 | 0.107903 | 0.0003014 | No
15/01/2024 | 07:29 | AP424F | URBAN | Asset failure | LV | 7.00 | 809.0 | 0.008731 | 0.0000108 | No
15/01/2024 | 07:35 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 149.0 | 0.001069 | 0.0000072 | No
15/01/2024 | 08:08 | WHY05 | URBAN | Weather |  | 8.33 | 139.4 | 0.001791 | 0.0000128 | No
15/01/2024 | 08:32 | HH386A | URBAN | Overloads |  | 6.00 | 117.0 | 0.001082 | 0.0000093 | No
15/01/2024 | 08:47 | BT31 | LONG RURAL | Planned |  | 39.00 | 201.0 | 0.056255 | 0.0002799 | No
15/01/2024 | 09:09 | CM25 | LONG RURAL | Planned |  | 4.00 | 224.0 | 0.006430 | 0.0000287 | No
15/01/2024 | 09:24 | MB20 | SHORT RURAL | Overloads |  | 8.00 | 321.0 | 0.018067 | 0.0000563 | No
15/01/2024 | 09:27 | NL451A | URBAN | Planned |  | 88.00 | 136.0 | 0.018452 | 0.0001357 | No
15/01/2024 | 09:42 | G11 | LONG RURAL | Weather |  | 34.00 | 48.0 | 0.011712 | 0.0002440 | No
15/01/2024 | 09:47 | YK18 | LONG RURAL | Planned |  | 7.00 | 261.0 | 0.013111 | 0.0000502 | No
15/01/2024 | 10:00 | HH386F | URBAN | Overloads |  | 1.00 | 544.0 | 0.000839 | 0.0000015 | No
15/01/2024 | 10:03 | CBD412B | URBAN | Third Party | Other | 1.33 | 161.0 | 0.000331 | 0.0000021 | No
15/01/2024 | 10:08 | ME427B | URBAN | Unknown | Unknown | 1.00 | 375.0 | 0.000578 | 0.0000015 | No
15/01/2024 | 10:38 | LX75 | LONG RURAL | Unknown | Unknown | 49.00 | 326.0 | 0.114635 | 0.0003516 | No
15/01/2024 | 10:48 | GA17 | LONG RURAL | Planned |  | 114.00 | 204.4 | 0.167259 | 0.0008181 | No
15/01/2024 | 11:37 | GA11 | SHORT RURAL | Asset failure | HV | 1.00 | 52.0 | 0.000366 | 0.0000070 | No
15/01/2024 | 11:50 | G13 | LONG RURAL | Weather |  | 20.00 | 17.0 | 0.002440 | 0.0001435 | No
15/01/2024 | 12:17 | CN71 | LONG RURAL | Asset failure | LV | 38.00 | 406.0 | 0.110716 | 0.0002727 | No
15/01/2024 | 12:58 | CD01 | SHORT RURAL | Unknown | Unknown | 1.00 | 45.0 | 0.000317 | 0.0000070 | No
15/01/2024 | 13:05 | W28 | LONG RURAL | Planned |  | 35.00 | 81.0 | 0.020345 | 0.0002512 | No
15/01/2024 | 13:13 | WHY05 | URBAN | Unknown | Unknown | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
15/01/2024 | 13:34 | HH386A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
15/01/2024 | 14:09 | ME131C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
15/01/2024 | 14:12 | ST22 | SHORT RURAL | Asset failure | LV | 2.00 | 329.0 | 0.004629 | 0.0000141 | No
15/01/2024 | 14:13 | KA01 | SHORT RURAL | Asset failure | LV | 1.00 | 91.0 | 0.000640 | 0.0000070 | No
15/01/2024 | 16:06 | SD31300 | LONG RURAL | Unknown | Unknown | 5.33 | 355.0 | 0.013587 | 0.0000383 | No
15/01/2024 | 16:52 | MTB22 | SHORT RURAL | Unknown | Unknown | 17.00 | 199.0 | 0.023801 | 0.0001196 | No
15/01/2024 | 17:01 | AP227A | URBAN | Asset failure | LV | 1.00 | 358.0 | 0.000552 | 0.0000015 | No
15/01/2024 | 17:19 | MG04 | SHORT RURAL | Asset failure | LV | 1.00 | 145.0 | 0.001020 | 0.0000070 | No
15/01/2024 | 17:32 | R36 | SHORT RURAL | Asset failure | HV | 1.00 | 27.0 | 0.000190 | 0.0000070 | No
15/01/2024 | 19:21 | EL260B | URBAN | Overloads |  | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
15/01/2024 | 20:30 | NU03 | LONG RURAL | Unknown | Unknown | 14.00 | 337.0 | 0.033858 | 0.0001005 | No
15/01/2024 | 20:30 | NU03 | LONG RURAL | Overloads |  | 2.00 | 455.0 | 0.006530 | 0.0000144 | No
16/01/2024 | 06:49 | YK23 | LONG RURAL | Animal | Animal impact | 814.00 | 53.4 | 0.311869 | 0.0058415 | No
16/01/2024 | 07:13 | CBD412S | URBAN | Planned |  | 2.00 | 449.0 | 0.001384 | 0.0000031 | No
16/01/2024 | 07:27 | CN71 | LONG RURAL | Asset failure | LV | 1.00 | 1,484.0 | 0.010650 | 0.0000072 | No
16/01/2024 | 08:12 | BT26 | LONG RURAL | Planned |  | 3.00 | 265.0 | 0.005705 | 0.0000215 | No
16/01/2024 | 08:30 | LX24 | SHORT RURAL | Asset failure | LV | 1.00 | 205.0 | 0.001442 | 0.0000070 | No
16/01/2024 | 08:34 | KI42 | LONG RURAL | Unknown | Unknown | 14.00 | 192.0 | 0.019290 | 0.0001005 | No
16/01/2024 | 08:41 | MG06 | SHORT RURAL | Animal | Animal impact | 373.00 | 18.1 | 0.047539 | 0.0026242 | No
16/01/2024 | 08:42 | MG42 | SHORT RURAL | Planned |  | 30.00 | 46.0 | 0.009709 | 0.0002111 | No
16/01/2024 | 08:50 | CV25 | LONG RURAL | Planned |  | 45.00 | 134.0 | 0.043273 | 0.0003229 | No
16/01/2024 | 08:58 | AP829A | URBAN | Planned |  | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
16/01/2024 | 09:02 | WK41 | SHORT RURAL | Planned |  | 1.00 | 46.0 | 0.000324 | 0.0000070 | No
16/01/2024 | 09:05 | MV63 | SHORT RURAL | Planned |  | 7.00 | 391.7 | 0.019291 | 0.0000492 | No
16/01/2024 | 09:13 | SM350G | URBAN | Planned |  | 120.00 | 264.8 | 0.048991 | 0.0001850 | No
16/01/2024 | 09:19 | G02 | LONG RURAL | Weather |  | 1.00 | 299.0 | 0.002146 | 0.0000072 | No
16/01/2024 | 09:26 | SM410A | URBAN | Planned |  | 1.00 | 402.0 | 0.000620 | 0.0000015 | No
16/01/2024 | 09:36 | HH341G | URBAN | Planned |  | 74.00 | 126.4 | 0.014420 | 0.0001141 | No
16/01/2024 | 09:40 | MG10 | LONG RURAL | Weather |  | 410.00 | 10.3 | 0.030334 | 0.0029423 | No
16/01/2024 | 09:45 | MG03 | SHORT RURAL | Weather |  | 27.67 | 93.0 | 0.018102 | 0.0001946 | No
16/01/2024 | 09:50 | MG46 | SHORT RURAL | Asset failure | HV | 102.67 | 184.0 | 0.132905 | 0.0007223 | No
16/01/2024 | 09:51 | CM12 | LONG RURAL | Planned |  | 1.00 | 172.0 | 0.001234 | 0.0000072 | No
16/01/2024 | 10:14 | HH386G | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 96.0 | 0.000148 | 0.0000015 | No
16/01/2024 | 10:55 | ME131E | URBAN | Asset failure | LV | 1.00 | 1,261.0 | 0.001944 | 0.0000015 | No
16/01/2024 | 12:09 | WK72 | SHORT RURAL | Weather |  | 1.00 | 444.0 | 0.003124 | 0.0000070 | No
16/01/2024 | 12:21 | NU35 | LONG RURAL | Weather |  | 29.00 | 259.3 | 0.053966 | 0.0002081 | No
16/01/2024 | 12:41 | HH386G | URBAN | Asset failure | LV | 1.00 | 1,158.0 | 0.001785 | 0.0000015 | No
16/01/2024 | 12:53 | EL11 | URBAN | Asset failure | LV | 1.00 | 81.0 | 0.000125 | 0.0000015 | No
16/01/2024 | 12:54 | R12 | LONG RURAL | Asset failure | HV | 86.00 | 296.9 | 0.183255 | 0.0006172 | No
16/01/2024 | 13:00 | R10 | LONG RURAL | Unknown | Unknown | 69.00 | 431.4 | 0.213603 | 0.0004952 | No
16/01/2024 | 13:19 | MTB32 | LONG RURAL | Asset failure | LV | 1.00 | 768.0 | 0.005511 | 0.0000072 | No
16/01/2024 | 13:51 | BM21 | SHORT RURAL | Weather |  | 1,016.00 | 123.0 | 0.879211 | 0.0071481 | No
16/01/2024 | 14:01 | BM31 | SHORT RURAL | Weather |  | 454.00 | 321.0 | 1.025310 | 0.0031941 | No
16/01/2024 | 14:02 | WK31 | SHORT RURAL | Unknown | Unknown | 462.00 | 121.6 | 0.395240 | 0.0032504 | No
16/01/2024 | 14:05 | BM13 | SHORT RURAL | Unknown | Unknown | 19.00 | 346.0 | 0.046251 | 0.0001337 | No
16/01/2024 | 14:06 | BM34 | SHORT RURAL | Unknown | Unknown | 148.00 | 373.0 | 0.388387 | 0.0010413 | No
16/01/2024 | 14:06 | HH386G | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
16/01/2024 | 14:08 | SB03 | LONG RURAL | Weather |  | 3.00 | 329.0 | 0.007083 | 0.0000215 | No
16/01/2024 | 14:09 | BM44 | SHORT RURAL | Weather |  | 968.00 | 118.8 | 0.808863 | 0.0068104 | No
16/01/2024 | 14:12 | WK31 | SHORT RURAL | Unknown | Unknown | 60.67 | 297.0 | 0.126766 | 0.0004268 | No
16/01/2024 | 14:21 | WK32 | SHORT RURAL | Unknown | Unknown | 8.00 | 405.0 | 0.022795 | 0.0000563 | No
16/01/2024 | 14:22 | VH71 | SHORT RURAL | Third Party | Vehicle impact | 11.00 | 84.0 | 0.006501 | 0.0000774 | No
16/01/2024 | 14:24 | BM33 | SHORT RURAL | Weather |  | 32.00 | 282.2 | 0.063538 | 0.0002251 | No
16/01/2024 | 14:30 | LX43 | SHORT RURAL | Asset failure | LV | 1.00 | 370.0 | 0.002603 | 0.0000070 | No
16/01/2024 | 14:30 | WK65 | SHORT RURAL | Weather |  | 41.67 | 320.0 | 0.093807 | 0.0002931 | No
16/01/2024 | 14:44 | ME427F | URBAN | Asset failure | LV | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
16/01/2024 | 14:44 | KA12 | LONG RURAL | Weather |  | 13.00 | 25.0 | 0.002332 | 0.0000933 | No
16/01/2024 | 15:20 | HH386D | URBAN | Unknown | Unknown | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
16/01/2024 | 15:23 | BM34 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.33 | 367.0 | 0.008607 | 0.0000235 | No
16/01/2024 | 15:28 | WK44 | SHORT RURAL | Weather |  | 7.00 | 328.0 | 0.016153 | 0.0000492 | No
16/01/2024 | 15:50 | BT23 | LONG RURAL | Weather |  | 53.00 | 272.9 | 0.103813 | 0.0003803 | No
16/01/2024 | 16:03 | BM13 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 3.67 | 308.0 | 0.007945 | 0.0000258 | No
16/01/2024 | 16:13 | SA744D | URBAN | Asset failure | LV | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
16/01/2024 | 16:18 | GA53 | SHORT RURAL | Unknown | Unknown | 4.67 | 67.0 | 0.002200 | 0.0000328 | No
16/01/2024 | 16:31 | BM54 | SHORT RURAL | Unknown | Unknown | 275.00 | 22.9 | 0.044267 | 0.0019348 | No
16/01/2024 | 16:31 | PL20 | LONG RURAL | Weather |  | 39.00 | 1,142.9 | 0.319878 | 0.0002799 | No
16/01/2024 | 16:35 | HH121D | URBAN | Asset failure | LV | 1.00 | 278.0 | 0.000429 | 0.0000015 | No
16/01/2024 | 16:49 | NL234D | URBAN | Overloads |  | 6.00 | 76.0 | 0.000703 | 0.0000093 | No
16/01/2024 | 16:53 | AP424B | URBAN | Asset failure | LV | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
16/01/2024 | 17:12 | PL32 | URBAN | Weather |  | 4,080.00 | 14.0 | 0.088264 | 0.0062904 | No
16/01/2024 | 18:01 | PP03 | URBAN | Asset failure | LV | 1.00 | 1,137.0 | 0.001753 | 0.0000015 | No
16/01/2024 | 18:02 | BM33 | SHORT RURAL | Asset failure | LV | 10.00 | 164.0 | 0.011538 | 0.0000704 | No
16/01/2024 | 18:25 | AP529A | URBAN | Asset failure | LV | 1.00 | 155.0 | 0.000239 | 0.0000015 | No
16/01/2024 | 18:27 | SM172C | URBAN | Asset failure | LV | 33.00 | 207.0 | 0.010532 | 0.0000509 | No
16/01/2024 | 18:36 | ST35 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 166.0 | 0.002383 | 0.0000144 | No
16/01/2024 | 19:03 | PP08 | LONG RURAL | Weather |  | 76.00 | 253.9 | 0.138484 | 0.0005454 | No
16/01/2024 | 19:07 | BM21 | SHORT RURAL | Asset failure | LV | 1.00 | 1,021.0 | 0.007183 | 0.0000070 | No
16/01/2024 | 19:11 | SM350B | URBAN | Asset failure | LV | 56.00 | 57.0 | 0.004921 | 0.0000863 | No
16/01/2024 | 19:36 | PA14 | LONG RURAL | Asset failure | LV | 1.00 | 121.0 | 0.000868 | 0.0000072 | No
16/01/2024 | 19:38 | WK31 | SHORT RURAL | Unknown | Unknown | 1.00 | 49.0 | 0.000345 | 0.0000070 | No
16/01/2024 | 19:46 | NL210B | URBAN | Asset failure | LV | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
16/01/2024 | 20:22 | HH102C | URBAN | Overloads |  | 28.00 | 102.0 | 0.004403 | 0.0000432 | No
16/01/2024 | 20:48 | GA53 | SHORT RURAL | Asset failure | LV | 7.00 | 190.0 | 0.009357 | 0.0000492 | No
16/01/2024 | 20:56 | CBD103G | URBAN | Overloads |  | 10.00 | 83.0 | 0.001280 | 0.0000154 | No
16/01/2024 | 20:58 | NU35 | LONG RURAL | Weather |  | 29.00 | 573.0 | 0.119249 | 0.0002081 | No
16/01/2024 | 21:45 | CM04 | LONG RURAL | Weather |  | 17.00 | 794.6 | 0.096945 | 0.0001220 | No
16/01/2024 | 21:45 | CM04 | LONG RURAL | Weather |  | 1.00 | 2,275.0 | 0.016326 | 0.0000072 | No
16/01/2024 | 21:55 | HH107D | URBAN | Planned |  | 15.00 | 401.0 | 0.009274 | 0.0000231 | No
16/01/2024 | 22:17 | YK28 | LONG RURAL | Unknown | Unknown | 58.00 | 254.1 | 0.105743 | 0.0004162 | No
16/01/2024 | 22:27 | GA800A | SHORT RURAL | Planned |  | 3.00 | 304.0 | 0.006416 | 0.0000211 | No
16/01/2024 | 23:20 | MG03 | SHORT RURAL | Unknown | Unknown | 2.00 | 143.0 | 0.002012 | 0.0000141 | No
16/01/2024 | 23:47 | VH31 | SHORT RURAL | Weather |  | 821.00 | 80.8 | 0.466509 | 0.0057761 | No
17/01/2024 | 00:08 | GU43 | LONG RURAL | Weather |  | 124.00 | 700.5 | 0.623350 | 0.0008899 | No
17/01/2024 | 00:09 | SM216B | URBAN | Unknown | Unknown | 616.00 | 93.0 | 0.088324 | 0.0009497 | No
17/01/2024 | 00:32 | GU41 | LONG RURAL | Unknown | Unknown | 1.00 | 819.0 | 0.005877 | 0.0000072 | No
17/01/2024 | 00:38 | HH341G | URBAN | Unknown | Unknown | 48.00 | 114.0 | 0.008436 | 0.0000740 | No
17/01/2024 | 01:47 | AP125D | URBAN | Vegetation | Grow-in - NSP responsibility | 675.00 | 87.0 | 0.090539 | 0.0010407 | No
17/01/2024 | 01:53 | HH432E | URBAN | Unknown | Unknown | 8.00 | 110.0 | 0.001357 | 0.0000123 | No
17/01/2024 | 02:57 | SG13 | SHORT RURAL | Overloads |  | 1.00 | 849.0 | 0.005973 | 0.0000070 | No
17/01/2024 | 05:20 | MG03 | SHORT RURAL | Weather |  | 135.67 | 170.3 | 0.162550 | 0.0009545 | No
17/01/2024 | 05:42 | G01 | LONG RURAL | Overloads |  | 68.00 | 385.0 | 0.187876 | 0.0004880 | No
17/01/2024 | 06:25 | MG03 | SHORT RURAL | Weather |  | 1.00 | 192.0 | 0.001351 | 0.0000070 | No
17/01/2024 | 06:57 | AP529D | URBAN | Asset failure | LV | 1.00 | 331.0 | 0.000510 | 0.0000015 | No
17/01/2024 | 07:43 | ST35 | LONG RURAL | Weather |  | 11.67 | 413.0 | 0.034578 | 0.0000837 | No
17/01/2024 | 07:56 | CM21 | LONG RURAL | Weather |  | 9.00 | 421.0 | 0.027191 | 0.0000646 | No
17/01/2024 | 08:11 | BT26 | LONG RURAL | Planned |  | 9.00 | 246.0 | 0.015888 | 0.0000646 | No
17/01/2024 | 08:38 | AP424B | URBAN | Planned |  | 166.00 | 364.5 | 0.093282 | 0.0002559 | No
17/01/2024 | 08:43 | SA40 | URBAN | Asset failure | LV | 11.00 | 286.0 | 0.004850 | 0.0000170 | No
17/01/2024 | 08:48 | EL16 | URBAN | Planned |  | 3.00 | 370.0 | 0.001711 | 0.0000046 | No
17/01/2024 | 08:52 | AP149E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 217.0 | 0.000669 | 0.0000031 | No
17/01/2024 | 09:03 | SB18 | LONG RURAL | Planned |  | 7.00 | 146.0 | 0.007334 | 0.0000502 | No
17/01/2024 | 09:07 | AP829H | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 123.00 | 86.0 | 0.016309 | 0.0001896 | No
17/01/2024 | 09:24 | GA53 | SHORT RURAL | Asset failure | LV | 57.00 | 443.5 | 0.177871 | 0.0004010 | No
17/01/2024 | 09:51 | AP125B | URBAN | Planned |  | 2.00 | 193.0 | 0.000595 | 0.0000031 | No
17/01/2024 | 09:54 | ME231E | URBAN | Planned |  | 52.00 | 160.0 | 0.012827 | 0.0000802 | No
17/01/2024 | 10:57 | MG31 | LONG RURAL | Planned |  | 4.00 | 213.0 | 0.006114 | 0.0000287 | No
17/01/2024 | 12:37 | ST35 | LONG RURAL | Weather |  | 39.00 | 59.0 | 0.016513 | 0.0002799 | No
17/01/2024 | 12:52 | WHY10 | URBAN | Asset failure | LV | 1.00 | 103.0 | 0.000159 | 0.0000015 | No
17/01/2024 | 13:17 | HH341B | URBAN | Overloads |  | 1.00 | 266.0 | 0.000410 | 0.0000015 | No
17/01/2024 | 13:40 | MV52 | SHORT RURAL | Planned |  | 34.00 | 46.0 | 0.011004 | 0.0002392 | No
17/01/2024 | 13:43 | SB01 | LONG RURAL | Asset failure | LV | 1.00 | 2,064.0 | 0.014812 | 0.0000072 | No
17/01/2024 | 14:18 | AP146B | URBAN | Asset failure | LV | 96.00 | 54.0 | 0.007991 | 0.0001480 | No
17/01/2024 | 14:45 | SM349C | URBAN | Asset failure | LV | 34.00 | 110.9 | 0.005811 | 0.0000524 | No
17/01/2024 | 14:51 | AP125D | URBAN | Asset failure | LV | 1.00 | 404.0 | 0.000623 | 0.0000015 | No
17/01/2024 | 15:15 | HH386G | URBAN | Vegetation | Grow-in - NSP responsibility | 15.33 | 230.0 | 0.005437 | 0.0000236 | No
17/01/2024 | 16:08 | LM62 | LONG RURAL | Asset failure | LV | 2.00 | 16.0 | 0.000230 | 0.0000144 | No
17/01/2024 | 16:13 | AP344B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 264.0 | 0.000407 | 0.0000015 | No
17/01/2024 | 17:13 | SA14 | URBAN | Asset failure | LV | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
17/01/2024 | 17:31 | AP510D | URBAN | Third Party | Vehicle impact | 3.00 | 280.3 | 0.001297 | 0.0000046 | No
17/01/2024 | 17:45 | M71 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 277.0 | 0.001988 | 0.0000072 | No
17/01/2024 | 18:08 | SM411A | URBAN | Asset failure | LV | 3.00 | 59.0 | 0.000273 | 0.0000046 | No
17/01/2024 | 18:23 | BM54 | SHORT RURAL | Asset failure | LV | 4.00 | 59.0 | 0.001660 | 0.0000281 | No
17/01/2024 | 18:47 | SA711C | URBAN | Asset failure | LV | 39.00 | 378.5 | 0.022756 | 0.0000601 | No
17/01/2024 | 21:10 | SM374A | URBAN | Planned |  | 244.00 | 289.7 | 0.108979 | 0.0003762 | No
17/01/2024 | 22:23 | GA800A | SHORT RURAL | Planned |  | 28.00 | 396.0 | 0.078010 | 0.0001970 | No
18/01/2024 | 00:39 | VH15 | SHORT RURAL | Animal | Animal impact | 29.67 | 169.0 | 0.035274 | 0.0002087 | No
18/01/2024 | 01:02 | SM411C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.00 | 128.0 | 0.005526 | 0.0000432 | No
18/01/2024 | 06:19 | EL20 | URBAN | Asset failure | LV | 35.00 | 174.0 | 0.009389 | 0.0000540 | No
18/01/2024 | 07:52 | CN32 | LONG RURAL | Asset failure | HV | 7.00 | 723.0 | 0.036319 | 0.0000502 | No
18/01/2024 | 08:12 | AP125C | URBAN | Planned |  | 139.00 | 177.8 | 0.038109 | 0.0002143 | No
18/01/2024 | 08:17 | MG42 | SHORT RURAL | Planned |  | 115.00 | 71.6 | 0.057902 | 0.0008091 | No
18/01/2024 | 08:21 | LM61 | LONG RURAL | Planned |  | 2.00 | 467.5 | 0.006710 | 0.0000144 | No
18/01/2024 | 08:30 | EL19 | URBAN | Planned |  | 2.00 | 98.5 | 0.000304 | 0.0000031 | No
18/01/2024 | 08:40 | LM63 | LONG RURAL | Animal | Animal impact | 2.00 | 2,141.0 | 0.030729 | 0.0000144 | No
18/01/2024 | 08:46 | KA07 | LONG RURAL | Planned |  | 10.00 | 103.0 | 0.007392 | 0.0000718 | No
18/01/2024 | 08:51 | MG06 | SHORT RURAL | Planned |  | 15.00 | 174.0 | 0.018363 | 0.0001055 | No
18/01/2024 | 08:51 | WK61 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 398.0 | 0.002800 | 0.0000070 | No
18/01/2024 | 08:51 | R26 | LONG RURAL | Asset failure | LV | 1.00 | 187.0 | 0.001342 | 0.0000072 | No
18/01/2024 | 09:04 | BT15 | LONG RURAL | Asset failure | HV | 3.00 | 571.0 | 0.012293 | 0.0000215 | No
18/01/2024 | 09:06 | HH409B | URBAN | Planned |  | 102.00 | 187.3 | 0.029454 | 0.0001573 | No
18/01/2024 | 09:15 | MTB12 | SHORT RURAL | Planned |  | 1.00 | 302.0 | 0.002125 | 0.0000070 | No
18/01/2024 | 09:20 | GU21 | LONG RURAL | Planned |  | 34.00 | 361.0 | 0.088082 | 0.0002440 | No
18/01/2024 | 09:33 | MTB11 | SHORT RURAL | Planned |  | 1.00 | 173.0 | 0.001217 | 0.0000070 | No
18/01/2024 | 09:35 | NL234A | URBAN | Planned |  | 104.00 | 344.3 | 0.055213 | 0.0001603 | No
18/01/2024 | 09:37 | HH522B | URBAN | Third Party | Dig-in | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
18/01/2024 | 09:38 | ST51 | SHORT RURAL | Planned |  | 1.00 | 267.0 | 0.001878 | 0.0000070 | No
18/01/2024 | 10:17 | YK15 | LONG RURAL | Asset failure | LV | 1.00 | 274.0 | 0.001966 | 0.0000072 | No
18/01/2024 | 10:29 | EL01L | URBAN | Animal | Animal impact | 1,234.00 | 91.0 | 0.173130 | 0.0019025 | No
18/01/2024 | 10:48 | ST36 | LONG RURAL | Asset failure | HV | 10.00 | 117.0 | 0.008396 | 0.0000718 | No
18/01/2024 | 10:49 | MG42 | SHORT RURAL | Planned |  | 17.00 | 84.0 | 0.010047 | 0.0001196 | No
18/01/2024 | 11:34 | EL20 | URBAN | Asset failure | LV | 2.00 | 609.0 | 0.001878 | 0.0000031 | No
18/01/2024 | 11:37 | EL19 | URBAN | Planned |  | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
18/01/2024 | 11:37 | EL19 | URBAN | Planned |  | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
18/01/2024 | 12:58 | SA14 | URBAN | Unknown | Unknown | 1.00 | 1,536.0 | 0.002368 | 0.0000015 | No
18/01/2024 | 13:01 | HH130B | URBAN | Third Party | Vehicle impact | 62.00 | 446.6 | 0.042694 | 0.0000956 | No
18/01/2024 | 13:25 | CV25 | LONG RURAL | Planned |  | 2.00 | 15.0 | 0.000215 | 0.0000144 | No
18/01/2024 | 13:33 | SD52300 | LONG RURAL | Planned |  | 25.00 | 15.0 | 0.002691 | 0.0001794 | No
18/01/2024 | 13:36 | SM216C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 19.00 | 272.0 | 0.007968 | 0.0000293 | No
18/01/2024 | 13:51 | AP355H | URBAN | Asset failure | LV | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
18/01/2024 | 14:30 | HH130B | URBAN | Unknown | Unknown | 1.00 | 390.0 | 0.000601 | 0.0000015 | No
18/01/2024 | 15:04 | SSD157 | LONG RURAL | Asset failure | Zone substation | 313.00 | 5.0 | 0.011231 | 0.0022462 | No
18/01/2024 | 16:04 | HH121F | URBAN | Overloads |  | 1.00 | 392.0 | 0.000604 | 0.0000015 | No
18/01/2024 | 16:24 | BM34 | SHORT RURAL | Overloads |  | 1.00 | 298.0 | 0.002097 | 0.0000070 | No
18/01/2024 | 16:45 | SM137D | URBAN | Asset failure | LV | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
18/01/2024 | 16:46 | MB12 | SHORT RURAL | Asset failure | HV | 888.00 | 6.0 | 0.037654 | 0.0062475 | No
18/01/2024 | 17:04 | BM56 | SHORT RURAL | Asset failure | LV | 4.00 | 135.0 | 0.003799 | 0.0000281 | No
18/01/2024 | 17:58 | SA17 | URBAN | Asset failure | LV | 10.00 | 93.0 | 0.001434 | 0.0000154 | No
18/01/2024 | 18:14 | AP355A | URBAN | Asset failure | LV | 24.67 | 62.0 | 0.002358 | 0.0000380 | No
18/01/2024 | 19:43 | NL451A | URBAN | Overloads |  | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
18/01/2024 | 20:30 | AP149E | URBAN | Unknown | Unknown | 2.00 | 149.0 | 0.000459 | 0.0000031 | No
18/01/2024 | 20:59 | AP149D | URBAN | Asset failure | LV | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
18/01/2024 | 21:14 | PP10 | URBAN | Asset failure | LV | 1.00 | 214.0 | 0.000330 | 0.0000015 | No
19/01/2024 | 00:56 | HH107C | URBAN | Asset failure | LV | 197.00 | 91.0 | 0.027639 | 0.0003037 | No
19/01/2024 | 08:07 | SA38 | URBAN | Unknown | Unknown | 2.00 | 75.0 | 0.000231 | 0.0000031 | No
19/01/2024 | 08:11 | HH341F | URBAN | Third Party | Vehicle impact | 26.00 | 88.0 | 0.003528 | 0.0000401 | No
19/01/2024 | 08:17 | SM349C | URBAN | Asset failure | LV | 83.00 | 200.0 | 0.025593 | 0.0001280 | No
19/01/2024 | 08:21 | ME427C | URBAN | Asset failure | LV | 69.00 | 54.5 | 0.005802 | 0.0001064 | No
19/01/2024 | 08:23 | AP125C | URBAN | Planned |  | 75.00 | 121.1 | 0.014005 | 0.0001156 | No
19/01/2024 | 08:46 | GA22 | SHORT RURAL | Planned |  | 39.00 | 284.9 | 0.078178 | 0.0002744 | No
19/01/2024 | 08:55 | NL210F | URBAN | Planned |  | 45.00 | 204.4 | 0.014183 | 0.0000694 | No
19/01/2024 | 09:14 | SSD529 | URBAN | Network business | Switching and protection error | 1.00 | 33.0 | 0.000051 | 0.0000015 | No
19/01/2024 | 09:18 | MV15 | SHORT RURAL | Planned |  | 41.00 | 305.0 | 0.087979 | 0.0002885 | No
19/01/2024 | 09:24 | AP125B | URBAN | Planned |  | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
19/01/2024 | 09:46 | R32 | LONG RURAL | Third Party | Vehicle impact | 78.00 | 260.0 | 0.145536 | 0.0005598 | No
19/01/2024 | 09:49 | NU01 | SHORT RURAL | Planned |  | 5.00 | 154.0 | 0.005417 | 0.0000352 | No
19/01/2024 | 10:08 | GA19 | LONG RURAL | Planned |  | 2.00 | 50.0 | 0.000718 | 0.0000144 | No
19/01/2024 | 10:10 | SA38 | URBAN | Unknown | Unknown | 2.00 | 32.0 | 0.000099 | 0.0000031 | No
19/01/2024 | 10:21 | EL01Z | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
19/01/2024 | 10:25 | WK91 | SHORT RURAL | Third Party | Vehicle impact | 50.00 | 197.0 | 0.069300 | 0.0003518 | No
19/01/2024 | 10:32 | KA17 | LONG RURAL | Planned |  | 49.00 | 202.0 | 0.071031 | 0.0003516 | No
19/01/2024 | 11:00 | KI54 | LONG RURAL | Planned |  | 2.00 | 35.0 | 0.000502 | 0.0000144 | No
19/01/2024 | 11:37 | NA12 | LONG RURAL | Weather |  | 4.00 | 8,847.0 | 0.253956 | 0.0000287 | No
19/01/2024 | 11:56 | W28 | LONG RURAL | Planned |  | 6.00 | 65.0 | 0.002799 | 0.0000431 | No
19/01/2024 | 11:57 | AP125A | URBAN | Planned |  | 6.00 | 6.0 | 0.000056 | 0.0000093 | No
19/01/2024 | 12:15 | KI54 | LONG RURAL | Planned |  | 2.00 | 21.0 | 0.000301 | 0.0000144 | No
19/01/2024 | 13:27 | SM411E | URBAN | Asset failure | LV | 8.00 | 103.0 | 0.001270 | 0.0000123 | No
19/01/2024 | 14:02 | SA20 | URBAN | Asset failure | LV | 25.00 | 683.0 | 0.026325 | 0.0000385 | No
19/01/2024 | 14:13 | HH341H | URBAN | Asset failure | LV | 1.00 | 428.0 | 0.000660 | 0.0000015 | No
19/01/2024 | 14:14 | G11 | LONG RURAL | Planned |  | 21.00 | 103.0 | 0.015522 | 0.0001507 | No
19/01/2024 | 17:07 | NL210E | URBAN | Asset failure | LV | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
19/01/2024 | 18:39 | HH177E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 632.00 | 25.0 | 0.024360 | 0.0009744 | No
19/01/2024 | 19:40 | HH496G | URBAN | Unknown | Unknown | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
19/01/2024 | 22:11 | LM31 | LONG RURAL | Planned |  | 2.00 | 37.0 | 0.000531 | 0.0000144 | No
20/01/2024 | 00:36 | HH428F | URBAN | Asset failure | LV | 45.00 | 49.0 | 0.003400 | 0.0000694 | No
20/01/2024 | 01:06 | HH121D | URBAN | Asset failure | LV | 13.00 | 318.0 | 0.006374 | 0.0000200 | No
20/01/2024 | 08:04 | VH23 | SHORT RURAL | Unknown | Unknown | 1.00 | 165.0 | 0.001161 | 0.0000070 | No
20/01/2024 | 09:57 | ME200A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 302.67 | 68.8 | 0.032126 | 0.0004666 | No
20/01/2024 | 10:29 | MT24 | LONG RURAL | Weather |  | 234.00 | 296.3 | 0.497592 | 0.0016793 | No
20/01/2024 | 10:49 | GA43 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 706.00 | 94.0 | 0.466903 | 0.0049671 | No
20/01/2024 | 12:10 | GU42 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 9.00 | 151.0 | 0.009753 | 0.0000646 | No
20/01/2024 | 12:58 | VH22 | SHORT RURAL | Unknown | Unknown | 30.00 | 243.0 | 0.051289 | 0.0002111 | No
20/01/2024 | 13:32 | GU14 | LONG RURAL | Overloads |  | 1.67 | 385.0 | 0.004605 | 0.0000120 | No
20/01/2024 | 14:48 | SA20 | URBAN | Overloads |  | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
20/01/2024 | 15:41 | MB41 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 486.00 | 233.0 | 0.812633 | 0.0034877 | No
20/01/2024 | 16:51 | AP372F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 303.00 | 87.0 | 0.040639 | 0.0004672 | No
20/01/2024 | 18:03 | BM12 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 5.0 | 0.000035 | 0.0000070 | No
20/01/2024 | 18:11 | AP424A | URBAN | Asset failure | LV | 1.00 | 402.0 | 0.000620 | 0.0000015 | No
20/01/2024 | 18:13 | AP149H | URBAN | Asset failure | LV | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
20/01/2024 | 18:29 | SA11 | URBAN | Overloads |  | 1.00 | 330.0 | 0.000509 | 0.0000015 | No
20/01/2024 | 18:47 | GA22 | SHORT RURAL | Asset failure | LV | 1.00 | 212.0 | 0.001492 | 0.0000070 | No
20/01/2024 | 19:06 | CN52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 6.0 | 0.000043 | 0.0000072 | No
20/01/2024 | 20:11 | AP424F | URBAN | Asset failure | LV | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
20/01/2024 | 21:16 | AP139A | URBAN | Asset failure | LV | 30.00 | 156.0 | 0.007215 | 0.0000463 | No
20/01/2024 | 21:22 | NL115C | URBAN | Third Party | Vehicle impact | 14.00 | 507.0 | 0.010943 | 0.0000216 | No
20/01/2024 | 21:43 | BM56 | SHORT RURAL | Other |  | 3.00 | 61.0 | 0.001287 | 0.0000211 | No
20/01/2024 | 22:13 | MG26 | LONG RURAL | Animal | Animal impact | 11.00 | 570.0 | 0.044996 | 0.0000789 | No
21/01/2024 | 05:21 | GA745A | SHORT RURAL | Asset failure | LV | 5.00 | 76.0 | 0.002673 | 0.0000352 | No
21/01/2024 | 06:22 | GA800A | SHORT RURAL | Asset failure | LV | 1.00 | 342.0 | 0.002406 | 0.0000070 | No
21/01/2024 | 07:48 | HH386F | URBAN | Unknown | Unknown | 2.00 | 145.0 | 0.000447 | 0.0000031 | No
21/01/2024 | 08:29 | NA01 | LONG RURAL | Planned |  | 55.00 | 327.7 | 0.129332 | 0.0003947 | No
21/01/2024 | 10:19 | SM411A | URBAN | Third Party | Vehicle impact | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
21/01/2024 | 11:51 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
21/01/2024 | 15:47 | AP149E | URBAN | Asset failure | LV | 28.33 | 175.0 | 0.007645 | 0.0000437 | No
21/01/2024 | 16:00 | AP139C | URBAN | Vegetation | Grow-in - NSP responsibility | 2.67 | 48.0 | 0.000197 | 0.0000041 | No
21/01/2024 | 16:06 | ME116D | URBAN | Asset failure | LV | 2.00 | 71.0 | 0.000219 | 0.0000031 | No
21/01/2024 | 16:07 | SM172A | URBAN | Asset failure | LV | 15.67 | 158.0 | 0.003816 | 0.0000242 | No
21/01/2024 | 17:38 | SD39400 | SHORT RURAL | Other |  | 6.00 | 4.0 | 0.000169 | 0.0000422 | No
21/01/2024 | 18:34 | GA50 | URBAN | Overloads |  | 24.00 | 122.0 | 0.004514 | 0.0000370 | No
21/01/2024 | 19:17 | HH432E | URBAN | Planned |  | 3.00 | 483.0 | 0.002234 | 0.0000046 | No
21/01/2024 | 19:32 | HH428D | URBAN | Asset failure | LV | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
21/01/2024 | 20:01 | EL15 | URBAN | Animal | Animal impact | 2.67 | 69.0 | 0.000284 | 0.0000041 | No
21/01/2024 | 20:27 | HH145A | URBAN | Asset failure | LV | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
21/01/2024 | 20:30 | HH177F | URBAN | Asset failure | LV | 54.00 | 49.0 | 0.004079 | 0.0000833 | No
21/01/2024 | 20:56 | KA06 | LONG RURAL | Planned |  | 8.00 | 238.0 | 0.013664 | 0.0000574 | No
21/01/2024 | 21:07 | AP372A | URBAN | Overloads |  | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
21/01/2024 | 21:18 | AP132A | URBAN | Planned |  | 97.00 | 351.7 | 0.052603 | 0.0001496 | No
21/01/2024 | 22:03 | CBD366B | CBD | Planned |  | 10.00 | 363.0 | 0.524453 | 0.0014448 | No
21/01/2024 | 23:37 | ST35 | LONG RURAL | Asset failure | HV | 175.00 | 459.3 | 0.576776 | 0.0012559 | No
22/01/2024 | 05:11 | HH409F | URBAN | Unknown | Unknown | 1,082.00 | 25.6 | 0.042701 | 0.0016682 | No
22/01/2024 | 06:17 | HH409D | URBAN | Overloads |  | 18.00 | 334.0 | 0.009269 | 0.0000278 | No
22/01/2024 | 06:19 | HH428B | URBAN | Third Party | Other | 1.00 | 136.0 | 0.000210 | 0.0000015 | No
22/01/2024 | 06:40 | SM402C | URBAN | Asset failure | HV | 94.00 | 204.6 | 0.029654 | 0.0001449 | No
22/01/2024 | 07:58 | GA01 | URBAN | Asset failure | LV | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
22/01/2024 | 08:18 | CL05 | LONG RURAL | Planned |  | 20.00 | 409.5 | 0.058774 | 0.0001435 | No
22/01/2024 | 08:28 | EL16 | URBAN | Planned |  | 41.00 | 46.0 | 0.002909 | 0.0000632 | No
22/01/2024 | 08:39 | AP125D | URBAN | Planned |  | 166.00 | 153.8 | 0.039369 | 0.0002559 | No
22/01/2024 | 09:06 | EL08G | URBAN | Asset failure | LV | 1.00 | 1,119.0 | 0.001725 | 0.0000015 | No
22/01/2024 | 09:07 | VH18 | SHORT RURAL | Planned |  | 8.00 | 311.5 | 0.017532 | 0.0000563 | No
22/01/2024 | 09:10 | SD49900 | URBAN | Planned |  | 1.00 | 4,668.0 | 0.007197 | 0.0000015 | No
22/01/2024 | 09:20 | HH341D | URBAN | Vegetation | Grow-in - NSP responsibility | 10.67 | 98.0 | 0.001612 | 0.0000164 | No
22/01/2024 | 09:27 | SA18 | URBAN | Planned |  | 59.00 | 17.0 | 0.001546 | 0.0000910 | No
22/01/2024 | 09:27 | R04 | LONG RURAL | Planned |  | 194.00 | 311.2 | 0.433264 | 0.0013922 | No
22/01/2024 | 09:31 | MI32 | LONG RURAL | Planned |  | 55.00 | 310.0 | 0.122356 | 0.0003947 | No
22/01/2024 | 09:33 | VH34 | SHORT RURAL | Planned |  | 36.00 | 295.0 | 0.074717 | 0.0002533 | No
22/01/2024 | 09:45 | CM12 | LONG RURAL | Planned |  | 1.00 | 170.0 | 0.001220 | 0.0000072 | No
22/01/2024 | 10:09 | AP125D | URBAN | Asset failure | LV | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
22/01/2024 | 10:17 | SM402C | URBAN | Asset failure | LV | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
22/01/2024 | 11:36 | HH496A | URBAN | Asset failure | HV | 594.00 | 302.2 | 0.276788 | 0.0009158 | No
22/01/2024 | 12:02 | KA28 | LONG RURAL | Planned |  | 1.00 | 49.0 | 0.000352 | 0.0000072 | No
22/01/2024 | 12:12 | VH22 | SHORT RURAL | Unknown | Unknown | 30.00 | 182.0 | 0.038414 | 0.0002111 | No
22/01/2024 | 13:25 | SA11 | URBAN | Asset failure | LV | 1.00 | 683.0 | 0.001053 | 0.0000015 | No
22/01/2024 | 14:04 | MG12 | LONG RURAL | Animal | Animal impact | 2.00 | 35.0 | 0.000502 | 0.0000144 | No
22/01/2024 | 14:34 | SG04 | SHORT RURAL | Third Party | Vehicle impact | 15.00 | 57.0 | 0.006015 | 0.0001055 | No
22/01/2024 | 15:39 | MB13 | SHORT RURAL | Asset failure | LV | 58.00 | 114.0 | 0.046505 | 0.0004081 | No
22/01/2024 | 16:14 | NL760A | URBAN | Asset failure | LV | 2.00 | 57.0 | 0.000176 | 0.0000031 | No
22/01/2024 | 18:59 | SM126A | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
22/01/2024 | 19:09 | HH428F | URBAN | Asset failure | LV | 47.33 | 178.0 | 0.012990 | 0.0000730 | No
22/01/2024 | 19:17 | AP829D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 215.00 | 181.5 | 0.060167 | 0.0003315 | No
22/01/2024 | 19:31 | HH107A | URBAN | Asset failure | LV | 59.00 | 279.0 | 0.025379 | 0.0000910 | No
22/01/2024 | 20:08 | CBD366B | CBD | Planned |  | 10.00 | 424.0 | 0.612584 | 0.0014448 | No
22/01/2024 | 22:20 | HH496D | URBAN | Third Party | Vehicle impact | 366.00 | 140.4 | 0.079249 | 0.0005643 | No
22/01/2024 | 22:28 | HH145B | URBAN | Asset failure | LV | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
23/01/2024 | 00:31 | AP226C | URBAN | Asset failure | LV | 1.00 | 192.0 | 0.000296 | 0.0000015 | No
23/01/2024 | 04:12 | PP03 | URBAN | Asset failure | LV | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
23/01/2024 | 04:45 | SM126C | URBAN | Animal | Animal impact | 61.33 | 424.0 | 0.040094 | 0.0000946 | No
23/01/2024 | 06:06 | WK71 | SHORT RURAL | Unknown | Unknown | 113.00 | 267.0 | 0.212268 | 0.0007950 | No
23/01/2024 | 08:08 | CL04 | LONG RURAL | Planned |  | 51.00 | 160.0 | 0.058573 | 0.0003660 | No
23/01/2024 | 08:56 | ST43 | LONG RURAL | Planned |  | 13.00 | 81.0 | 0.007557 | 0.0000933 | No
23/01/2024 | 08:57 | SA17 | URBAN | Overloads |  | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
23/01/2024 | 09:00 | SA14 | URBAN | Planned |  | 1.00 | 362.0 | 0.000558 | 0.0000015 | No
23/01/2024 | 09:17 | HH496C | URBAN | Planned |  | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
23/01/2024 | 09:40 | AP149D | URBAN | Unknown | Unknown | 4.00 | 854.0 | 0.005267 | 0.0000062 | No
23/01/2024 | 09:42 | NL115C | URBAN | Overloads |  | 4.67 | 130.0 | 0.000935 | 0.0000072 | No
23/01/2024 | 10:25 | HH341E | URBAN | Asset failure | LV | 91.00 | 25.0 | 0.003507 | 0.0001403 | No
23/01/2024 | 10:50 | SA520H | URBAN | Overloads |  | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
23/01/2024 | 10:53 | GU32 | LONG RURAL | Overloads |  | 2.00 | 148.0 | 0.002124 | 0.0000144 | No
23/01/2024 | 11:36 | NA51 | LONG RURAL | Unknown | Unknown | 64.33 | 59.0 | 0.027239 | 0.0004617 | No
23/01/2024 | 11:40 | VH22 | SHORT RURAL | Asset failure | HV | 32.00 | 283.0 | 0.063713 | 0.0002251 | No
23/01/2024 | 14:30 | SM179A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,643.00 | 101.5 | 0.257115 | 0.0025331 | No
23/01/2024 | 14:37 | PL24 | LONG RURAL | Weather |  | 11.00 | 163.0 | 0.012867 | 0.0000789 | No
23/01/2024 | 16:01 | MTB62 | SHORT RURAL | Asset failure | LV | 1.00 | 1,251.0 | 0.008801 | 0.0000070 | No
23/01/2024 | 16:17 | NL111Q | URBAN | Asset failure | LV | 23.00 | 175.0 | 0.006206 | 0.0000355 | No
23/01/2024 | 16:18 | BT04 | LONG RURAL | Asset failure | LV | 5.00 | 679.0 | 0.024364 | 0.0000359 | No
23/01/2024 | 16:21 | BT28 | LONG RURAL | Planned |  | 1.00 | 4.0 | 0.000029 | 0.0000072 | No
23/01/2024 | 17:05 | HH403B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 73.00 | 193.0 | 0.021722 | 0.0001125 | No
23/01/2024 | 18:09 | SA744C | URBAN | Overloads |  | 1.00 | 337.0 | 0.000520 | 0.0000015 | No
23/01/2024 | 18:12 | VH44 | SHORT RURAL | Asset failure | LV | 1.00 | 236.0 | 0.001660 | 0.0000070 | No
23/01/2024 | 18:20 | BM13 | SHORT RURAL | Unknown | Unknown | 1.00 | 907.0 | 0.006381 | 0.0000070 | No
23/01/2024 | 18:32 | EL14 | URBAN | Asset failure | HV | 2,115.00 | 85.8 | 0.279725 | 0.0032608 | No
23/01/2024 | 18:34 | SM349B | URBAN | Unknown | Unknown | 1.00 | 288.0 | 0.000444 | 0.0000015 | No
23/01/2024 | 18:48 | SM349E | URBAN | Asset failure | LV | 76.00 | 177.0 | 0.020740 | 0.0001172 | No
23/01/2024 | 19:11 | SA744C | URBAN | Overloads |  | 1.00 | 279.0 | 0.000430 | 0.0000015 | No
23/01/2024 | 19:24 | MG04 | SHORT RURAL | Asset failure | HV | 2.00 | 114.0 | 0.001604 | 0.0000141 | No
23/01/2024 | 19:28 | ST11 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,047.0 | 0.007366 | 0.0000070 | No
23/01/2024 | 19:36 | AP424F | URBAN | Asset failure | HV | 1,459.00 | 192.9 | 0.433873 | 0.0022494 | No
23/01/2024 | 19:40 | HH341D | URBAN | Asset failure | LV | 20.67 | 166.0 | 0.005289 | 0.0000319 | No
23/01/2024 | 19:46 | GA15 | SHORT RURAL | Overloads |  | 10.00 | 332.0 | 0.023358 | 0.0000704 | No
23/01/2024 | 19:46 | ME131B | URBAN | Overloads |  | 24.33 | 138.0 | 0.005177 | 0.0000375 | No
23/01/2024 | 19:57 | SM349C | URBAN | Overloads |  | 1.00 | 165.0 | 0.000254 | 0.0000015 | No
23/01/2024 | 19:59 | SM349C | URBAN | Unknown | Unknown | 31.00 | 153.0 | 0.007313 | 0.0000478 | No
23/01/2024 | 20:13 | NU02 | LONG RURAL | Unknown | Unknown | 2.00 | 124.0 | 0.001780 | 0.0000144 | No
23/01/2024 | 20:15 | HH145C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 89.0 | 0.000137 | 0.0000015 | No
23/01/2024 | 20:23 | AP425D | URBAN | Unknown | Unknown | 95.00 | 285.0 | 0.041743 | 0.0001465 | No
23/01/2024 | 20:42 | HH121G | URBAN | Unknown | Unknown | 31.00 | 123.0 | 0.005879 | 0.0000478 | No
23/01/2024 | 20:48 | HH107B | URBAN | Unknown | Unknown | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
23/01/2024 | 20:51 | CL04 | LONG RURAL | Asset failure | LV | 1.00 | 171.0 | 0.001227 | 0.0000072 | No
23/01/2024 | 20:53 | AP146C | URBAN | Asset failure | LV | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
23/01/2024 | 20:54 | AP372B | URBAN | Overloads |  | 55.00 | 133.0 | 0.011278 | 0.0000848 | No
23/01/2024 | 20:55 | HH121G | URBAN | Unknown | Unknown | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
23/01/2024 | 21:53 | PP06 | LONG RURAL | Overloads |  | 2.67 | 148.0 | 0.002832 | 0.0000191 | No
23/01/2024 | 22:21 | NU34 | LONG RURAL | Third Party | Other | 1.00 | 784.0 | 0.005626 | 0.0000072 | No
23/01/2024 | 23:19 | AP139C | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
24/01/2024 | 00:41 | GA11 | SHORT RURAL | Asset failure | HV | 96.00 | 88.0 | 0.059436 | 0.0006754 | No
24/01/2024 | 00:56 | CV16 | LONG RURAL | Weather |  | 51.00 | 237.3 | 0.086855 | 0.0003660 | No
24/01/2024 | 01:56 | MV31 | SHORT RURAL | Weather |  | 90.67 | 276.1 | 0.176131 | 0.0006379 | No
24/01/2024 | 01:58 | CM03 | LONG RURAL | Weather |  | 12.67 | 457.0 | 0.041541 | 0.0000909 | No
24/01/2024 | 02:15 | VH34 | SHORT RURAL | Weather |  | 147.00 | 587.8 | 0.607909 | 0.0010342 | No
24/01/2024 | 02:18 | YK08 | LONG RURAL | Weather |  | 48.00 | 305.0 | 0.105061 | 0.0003445 | No
24/01/2024 | 02:20 | NA17 | LONG RURAL | Weather |  | 63.00 | 140.0 | 0.063295 | 0.0004521 | No
24/01/2024 | 02:28 | NA61 | LONG RURAL | Weather |  | 96.00 | 492.8 | 0.339491 | 0.0006889 | No
24/01/2024 | 02:28 | NA61 | LONG RURAL | Weather |  | 2.00 | 2,009.0 | 0.028834 | 0.0000144 | No
24/01/2024 | 02:40 | PP06 | LONG RURAL | Overloads |  | 2.67 | 416.0 | 0.007961 | 0.0000191 | No
24/01/2024 | 03:01 | SD40400 | LONG RURAL | Unknown | Unknown | 160.00 | 59.8 | 0.068606 | 0.0011482 | No
24/01/2024 | 03:12 | MG52 | URBAN | Unknown | Unknown | 19.00 | 269.0 | 0.007880 | 0.0000293 | No
24/01/2024 | 03:14 | MG05 | LONG RURAL | Weather |  | 20.00 | 600.4 | 0.086166 | 0.0001435 | No
24/01/2024 | 03:20 | NL760B | URBAN | Weather |  | 45.00 | 129.0 | 0.008950 | 0.0000694 | No
24/01/2024 | 03:23 | VH13 | SHORT RURAL | Weather |  | 10.00 | 682.0 | 0.047982 | 0.0000704 | No
24/01/2024 | 03:28 | SD44200 | SHORT RURAL | Weather |  | 107.00 | 382.2 | 0.287737 | 0.0007528 | No
24/01/2024 | 03:36 | VH45 | SHORT RURAL | Weather |  | 102.00 | 533.0 | 0.382491 | 0.0007176 | No
24/01/2024 | 03:45 | VH21 | SHORT RURAL | Weather |  | 3,067.00 | 198.2 | 4.275960 | 0.0215778 | No
24/01/2024 | 03:55 | CN81 | LONG RURAL | Animal | Animal impact | 13.00 | 397.0 | 0.037037 | 0.0000933 | No
24/01/2024 | 04:01 | EL17 | URBAN | Unknown | Unknown | 21.00 | 299.0 | 0.009681 | 0.0000324 | No
24/01/2024 | 04:05 | HH341A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 232.0 | 0.000358 | 0.0000015 | No
24/01/2024 | 04:11 | MG17 | LONG RURAL | Unknown | Unknown | 1.00 | 282.0 | 0.002024 | 0.0000072 | No
24/01/2024 | 04:39 | EL03 | URBAN | Unknown | Unknown | 18.00 | 357.0 | 0.009907 | 0.0000278 | No
24/01/2024 | 04:42 | HH409E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 34.00 | 220.9 | 0.011580 | 0.0000524 | No
24/01/2024 | 04:43 | AP214C | URBAN | Asset failure | LV | 1.00 | 276.0 | 0.000426 | 0.0000015 | No
24/01/2024 | 04:57 | MG09 | SHORT RURAL | Weather |  | 4.00 | 439.0 | 0.012354 | 0.0000281 | No
24/01/2024 | 05:24 | EL03 | URBAN | Unknown | Unknown | 54.00 | 342.0 | 0.028473 | 0.0000833 | No
24/01/2024 | 05:39 | MI02 | SHORT RURAL | Weather |  | 5.00 | 267.0 | 0.009392 | 0.0000352 | No
24/01/2024 | 06:06 | MG42 | SHORT RURAL | Weather |  | 17.00 | 222.8 | 0.026643 | 0.0001196 | No
24/01/2024 | 06:16 | MI15 | LONG RURAL | Weather |  | 102.00 | 369.0 | 0.270103 | 0.0007320 | No
24/01/2024 | 06:21 | NA21 | LONG RURAL | Weather |  | 56.00 | 192.6 | 0.077390 | 0.0004019 | No
24/01/2024 | 06:29 | MG26 | LONG RURAL | Weather |  | 11.00 | 392.0 | 0.030944 | 0.0000789 | No
24/01/2024 | 06:52 | HH409D | URBAN | Overloads |  | 1.00 | 481.0 | 0.000742 | 0.0000015 | No
24/01/2024 | 07:02 | YK24 | LONG RURAL | Weather |  | 67.00 | 220.2 | 0.105894 | 0.0004808 | No
24/01/2024 | 07:13 | MG10 | LONG RURAL | Unknown | Unknown | 9.00 | 90.0 | 0.005813 | 0.0000646 | No
24/01/2024 | 07:23 | NA09 | LONG RURAL | Weather |  | 8.67 | 311.1 | 0.019347 | 0.0000622 | No
24/01/2024 | 07:29 | HH177A | URBAN | Asset failure | LV | 20.00 | 194.0 | 0.005982 | 0.0000308 | No
24/01/2024 | 07:33 | MG51 | LONG RURAL | Weather |  | 16.00 | 149.0 | 0.017108 | 0.0001148 | No
24/01/2024 | 07:33 | SM402D | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
24/01/2024 | 07:56 | MV34 | SHORT RURAL | Asset failure | LV | 48.00 | 340.0 | 0.114819 | 0.0003377 | No
24/01/2024 | 08:11 | BT04 | LONG RURAL | Weather |  | 9.33 | 406.0 | 0.027194 | 0.0000670 | No
24/01/2024 | 08:15 | VH18 | SHORT RURAL | Weather |  | 5.00 | 360.0 | 0.012664 | 0.0000352 | No
24/01/2024 | 08:15 | GA26 | URBAN | Asset failure | LV | 1.00 | 161.0 | 0.000248 | 0.0000015 | No
24/01/2024 | 08:19 | CL05 | LONG RURAL | Planned |  | 20.00 | 332.3 | 0.047687 | 0.0001435 | No
24/01/2024 | 08:21 | VH15 | SHORT RURAL | Weather |  | 1,168.00 | 25.9 | 0.212606 | 0.0082175 | No
24/01/2024 | 08:22 | MG05 | LONG RURAL | Unknown | Unknown | 311.00 | 3.0 | 0.006696 | 0.0022318 | No
24/01/2024 | 08:37 | HH432B | URBAN | Planned |  | 88.00 | 390.0 | 0.052913 | 0.0001357 | No
24/01/2024 | 08:43 | AP132B | URBAN | Planned |  | 19.00 | 216.0 | 0.006327 | 0.0000293 | No
24/01/2024 | 08:45 | HH341G | URBAN | Planned |  | 287.00 | 208.0 | 0.092029 | 0.0004425 | No
24/01/2024 | 08:53 | VH15 | SHORT RURAL | Asset failure | LV | 1.00 | 256.0 | 0.001801 | 0.0000070 | No
24/01/2024 | 08:53 | ME231B | URBAN | Planned |  | 10.00 | 278.0 | 0.004286 | 0.0000154 | No
24/01/2024 | 08:56 | NL234A | URBAN | Planned |  | 112.00 | 310.0 | 0.053530 | 0.0001727 | No
24/01/2024 | 09:01 | HH341G | URBAN | Unknown | Unknown | 1.00 | 379.0 | 0.000584 | 0.0000015 | No
24/01/2024 | 09:20 | HH145C | URBAN | Planned |  | 27.00 | 315.5 | 0.013133 | 0.0000416 | No
24/01/2024 | 09:28 | GA02 | SHORT RURAL | Planned |  | 21.00 | 63.0 | 0.009308 | 0.0001477 | No
24/01/2024 | 09:44 | AP424A | URBAN | Planned |  | 437.00 | 344.5 | 0.232116 | 0.0006737 | No
24/01/2024 | 09:52 | AP355E | URBAN | Overloads |  | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
24/01/2024 | 10:15 | AP214C | URBAN | Asset failure | HV | 338.00 | 7.0 | 0.003642 | 0.0005211 | No
24/01/2024 | 10:26 | ST21 | SHORT RURAL | Weather |  | 3.33 | 288.0 | 0.006754 | 0.0000235 | No
24/01/2024 | 10:37 | NL451E | URBAN | Third Party | Dig-in | 53.00 | 417.0 | 0.034074 | 0.0000817 | No
24/01/2024 | 10:37 | CN25 | LONG RURAL | Weather |  | 17.00 | 1,396.9 | 0.170423 | 0.0001220 | No
24/01/2024 | 10:38 | SA36 | URBAN | Unknown | Unknown | 2.00 | 382.0 | 0.001178 | 0.0000031 | No
24/01/2024 | 10:44 | NA21 | LONG RURAL | Asset failure | HV | 56.00 | 246.8 | 0.099170 | 0.0004019 | No
24/01/2024 | 10:50 | NL451E | URBAN | Third Party | Dig-in | 51.00 | 404.0 | 0.031766 | 0.0000786 | No
24/01/2024 | 10:51 | KI55 | LONG RURAL | Planned |  | 3.00 | 197.0 | 0.004241 | 0.0000215 | No
24/01/2024 | 11:01 | EL16 | URBAN | Unknown | Unknown | 16.33 | 380.0 | 0.009569 | 0.0000252 | No
24/01/2024 | 11:07 | NL451E | URBAN | Third Party | Dig-in | 1,617.00 | 14.0 | 0.034902 | 0.0024930 | No
24/01/2024 | 11:13 | AP132D | URBAN | Vegetation | Grow-in - NSP responsibility | 34.00 | 211.0 | 0.011061 | 0.0000524 | No
24/01/2024 | 11:17 | WHY07 | URBAN | Asset failure | LV | 18.00 | 53.3 | 0.001479 | 0.0000278 | No
24/01/2024 | 11:20 | AP226C | URBAN | Asset failure | LV | 10.67 | 662.0 | 0.010887 | 0.0000164 | No
24/01/2024 | 12:05 | CM22 | LONG RURAL | Unknown | Unknown | 2.00 | 40.0 | 0.000574 | 0.0000144 | No
24/01/2024 | 12:31 | MG38 | SHORT RURAL | Weather |  | 1.00 | 235.0 | 0.001653 | 0.0000070 | No
24/01/2024 | 12:35 | SA14 | URBAN | Weather |  | 16.67 | 177.0 | 0.004548 | 0.0000257 | No
24/01/2024 | 12:36 | GA800C | SHORT RURAL | Planned |  | 1.00 | 80.0 | 0.000563 | 0.0000070 | No
24/01/2024 | 13:31 | MI16 | LONG RURAL | Asset failure | LV | 11.33 | 24.6 | 0.001997 | 0.0000813 | No
24/01/2024 | 13:34 | NL511A | URBAN | Unknown | Unknown | 1.00 | 363.0 | 0.000560 | 0.0000015 | No
24/01/2024 | 13:56 | CM02 | LONG RURAL | Asset failure | HV | 74.00 | 68.0 | 0.036111 | 0.0005310 | No
24/01/2024 | 14:28 | VH34 | SHORT RURAL | Unknown | Unknown | 2.00 | 194.0 | 0.002730 | 0.0000141 | No
24/01/2024 | 14:59 | SG09 | SHORT RURAL | Third Party | Vehicle impact | 13.00 | 194.0 | 0.017744 | 0.0000915 | No
24/01/2024 | 15:58 | CV01 | SHORT RURAL | Unknown | Unknown | 1.00 | 6,741.0 | 0.047426 | 0.0000070 | No
24/01/2024 | 16:32 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 171.0 | 0.001203 | 0.0000070 | No
24/01/2024 | 17:04 | HH177G | URBAN | Asset failure | LV | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
24/01/2024 | 17:51 | CM22 | LONG RURAL | Asset failure | HV | 2.00 | 65.0 | 0.000933 | 0.0000144 | No
24/01/2024 | 18:15 | HH107B | URBAN | Asset failure | LV | 1.00 | 449.0 | 0.000692 | 0.0000015 | No
24/01/2024 | 18:23 | AP227B | URBAN | Unknown | Unknown | 1.00 | 459.0 | 0.000708 | 0.0000015 | No
24/01/2024 | 18:55 | AP365E | URBAN | Third Party | Vehicle impact | 54.00 | 550.0 | 0.045790 | 0.0000833 | No
24/01/2024 | 19:19 | AP424B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 35.67 | 201.0 | 0.011053 | 0.0000550 | No
24/01/2024 | 19:38 | SA14 | URBAN | Overloads |  | 5.67 | 194.0 | 0.001695 | 0.0000087 | No
24/01/2024 | 21:59 | HH177G | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
24/01/2024 | 23:08 | AP424B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 35.67 | 27.0 | 0.001485 | 0.0000550 | No
25/01/2024 | 05:46 | EL14 | URBAN | Planned |  | 160.00 | 70.0 | 0.017268 | 0.0002467 | No
25/01/2024 | 07:52 | MI15 | LONG RURAL | Weather |  | 28.00 | 156.0 | 0.031346 | 0.0002009 | No
25/01/2024 | 08:28 | EL19 | URBAN | Planned |  | 2.00 | 181.5 | 0.000560 | 0.0000031 | No
25/01/2024 | 08:59 | NU21 | LONG RURAL | Planned |  | 3.00 | 252.0 | 0.005425 | 0.0000215 | No
25/01/2024 | 09:10 | SG06 | SHORT RURAL | Planned |  | 60.00 | 244.5 | 0.103225 | 0.0004221 | No
25/01/2024 | 09:16 | VH23 | SHORT RURAL | Animal | Animal impact | 22.67 | 88.0 | 0.014033 | 0.0001595 | No
25/01/2024 | 09:17 | WK44 | SHORT RURAL | Planned |  | 3.00 | 140.0 | 0.002955 | 0.0000211 | No
25/01/2024 | 09:24 | HH121D | URBAN | Planned |  | 135.00 | 312.0 | 0.064939 | 0.0002081 | No
25/01/2024 | 09:25 | VH44 | SHORT RURAL | Weather |  | 215.00 | 199.8 | 0.302266 | 0.0015126 | No
25/01/2024 | 09:30 | GU15 | LONG RURAL | Asset failure | HV | 98.00 | 53.0 | 0.037274 | 0.0007033 | No
25/01/2024 | 09:44 | YK18 | LONG RURAL | Planned |  | 7.00 | 56.0 | 0.002813 | 0.0000502 | No
25/01/2024 | 09:48 | PL20 | LONG RURAL | Weather |  | 39.00 | 265.0 | 0.074167 | 0.0002799 | No
25/01/2024 | 09:49 | GA41 | LONG RURAL | Planned |  | 2.00 | 48.0 | 0.000689 | 0.0000144 | No
25/01/2024 | 09:53 | ST21 | SHORT RURAL | Unknown | Unknown | 3.33 | 520.0 | 0.012195 | 0.0000235 | No
25/01/2024 | 09:54 | SB21 | LONG RURAL | Weather |  | 77.00 | 215.4 | 0.119012 | 0.0005526 | No
25/01/2024 | 09:55 | MG13 | SHORT RURAL | Animal | Animal impact | 8.00 | 133.5 | 0.007514 | 0.0000563 | No
25/01/2024 | 10:43 | EL14 | URBAN | Overloads |  | 44.00 | 33.0 | 0.002239 | 0.0000678 | No
25/01/2024 | 11:08 | VH34 | SHORT RURAL | Weather |  | 147.00 | 380.0 | 0.393003 | 0.0010342 | No
25/01/2024 | 11:10 | MT16 | LONG RURAL | Asset failure | LV | 1.00 | 244.0 | 0.001751 | 0.0000072 | No
25/01/2024 | 11:16 | SA14 | URBAN | Asset failure | LV | 25.00 | 784.0 | 0.030218 | 0.0000385 | No
25/01/2024 | 11:27 | VH22 | SHORT RURAL | Weather |  | 2,356.00 | 64.8 | 1.074326 | 0.0165756 | No
25/01/2024 | 11:29 | MB12 | SHORT RURAL | Asset failure | LV | 1.00 | 235.0 | 0.001653 | 0.0000070 | No
25/01/2024 | 11:42 | W26 | LONG RURAL | Weather |  | 92.00 | 331.7 | 0.219014 | 0.0006602 | No
25/01/2024 | 11:45 | HH386A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 198.00 | 293.4 | 0.089576 | 0.0003053 | No
25/01/2024 | 11:48 | HH121D | URBAN | Overloads |  | 10.00 | 145.0 | 0.002236 | 0.0000154 | No
25/01/2024 | 11:59 | PL30 | LONG RURAL | Weather |  | 19.00 | 507.7 | 0.069223 | 0.0001364 | No
25/01/2024 | 12:21 | CN33 | LONG RURAL | Weather |  | 7.00 | 227.0 | 0.011403 | 0.0000502 | No
25/01/2024 | 12:28 | HH429B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
25/01/2024 | 12:53 | VH15 | SHORT RURAL | Weather |  | 195.00 | 336.7 | 0.461901 | 0.0013719 | No
25/01/2024 | 13:48 | VH44 | SHORT RURAL | Weather |  | 111.00 | 4.0 | 0.003124 | 0.0007809 | No
25/01/2024 | 14:21 | HH341G | URBAN | Asset failure | LV | 35.67 | 473.0 | 0.026010 | 0.0000550 | No
25/01/2024 | 14:35 | BM15 | SHORT RURAL | Asset failure | LV | 9.00 | 58.9 | 0.003729 | 0.0000633 | No
25/01/2024 | 14:49 | HH386B | URBAN | Third Party | Other | 15.00 | 75.8 | 0.001753 | 0.0000231 | No
25/01/2024 | 15:02 | YK22 | SHORT RURAL | Weather |  | 82.00 | 142.9 | 0.082442 | 0.0005769 | No
25/01/2024 | 15:08 | AP372F | URBAN | Asset failure | LV | 1.00 | 557.0 | 0.000859 | 0.0000015 | No
25/01/2024 | 15:23 | PL21 | LONG RURAL | Weather |  | 1.00 | 50.0 | 0.000359 | 0.0000072 | No
25/01/2024 | 15:29 | VH15 | SHORT RURAL | Weather |  | 1,824.00 | 67.0 | 0.860314 | 0.0128327 | No
25/01/2024 | 15:51 | PL10 | LONG RURAL | Asset failure | LV | 1.00 | 1,195.0 | 0.008576 | 0.0000072 | No
25/01/2024 | 16:12 | HH432C | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
25/01/2024 | 16:57 | AP424E | URBAN | Third Party | Unauthorised access | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
25/01/2024 | 17:39 | VH16 | SHORT RURAL | Weather |  | 1.00 | 246.0 | 0.001731 | 0.0000070 | No
25/01/2024 | 18:28 | HH409A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 604.00 | 67.8 | 0.063104 | 0.0009312 | No
25/01/2024 | 18:51 | PL07 | URBAN | Asset failure | LV | 1.00 | 943.0 | 0.001454 | 0.0000015 | No
25/01/2024 | 19:18 | MV64 | SHORT RURAL | Asset failure | LV | 22.00 | 265.0 | 0.041017 | 0.0001548 | No
25/01/2024 | 20:21 | YK04 | SHORT RURAL | Weather |  | 13.00 | 50.0 | 0.004573 | 0.0000915 | No
25/01/2024 | 20:23 | SD37301 | SHORT RURAL | Weather |  | 3.00 | 940.3 | 0.019847 | 0.0000211 | No
25/01/2024 | 21:24 | AP355A | URBAN | Asset failure | LV | 25.00 | 131.0 | 0.005049 | 0.0000385 | No
25/01/2024 | 23:29 | ME231B | URBAN | Asset failure | LV | 107.00 | 97.5 | 0.016080 | 0.0001650 | No
26/01/2024 | 00:17 | SM411C | URBAN | Unknown | Unknown | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
26/01/2024 | 03:07 | SD40400 | LONG RURAL | Unknown | Unknown | 160.00 | 72.6 | 0.083317 | 0.0011482 | No
26/01/2024 | 06:59 | HH130F | URBAN | Overloads |  | 44.00 | 275.0 | 0.018655 | 0.0000678 | No
26/01/2024 | 07:55 | WHY06 | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
26/01/2024 | 09:57 | NL111Q | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 570.00 | 241.7 | 0.212398 | 0.0008788 | No
26/01/2024 | 09:58 | AP424F | URBAN | Asset failure | LV | 1.00 | 613.0 | 0.000945 | 0.0000015 | No
26/01/2024 | 10:40 | MTB41 | SHORT RURAL | Other |  | 1.00 | 182.0 | 0.001280 | 0.0000070 | No
26/01/2024 | 10:44 | SM402E | URBAN | Weather |  | 479.00 | 119.4 | 0.088170 | 0.0007385 | No
26/01/2024 | 10:51 | AP424C | URBAN | Asset failure | LV | 79.00 | 312.0 | 0.038001 | 0.0001218 | No
26/01/2024 | 11:03 | SA16 | URBAN | Unknown | Unknown | 47.00 | 152.0 | 0.011014 | 0.0000725 | No
26/01/2024 | 11:31 | SD49500 | LONG RURAL | Unknown | Unknown | 1.00 | 218.0 | 0.001564 | 0.0000072 | No
26/01/2024 | 11:48 | HH177C | URBAN | Overloads |  | 1.00 | 375.0 | 0.000578 | 0.0000015 | No
26/01/2024 | 12:04 | AP424C | URBAN | Asset failure | LV | 17.00 | 75.0 | 0.001966 | 0.0000262 | No
26/01/2024 | 12:04 | PA25 | SHORT RURAL | Unknown | Unknown | 10.00 | 222.0 | 0.015619 | 0.0000704 | No
26/01/2024 | 14:39 | NL115C | URBAN | Asset failure | LV | 71.00 | 64.5 | 0.007057 | 0.0001095 | No
26/01/2024 | 14:40 | HH145E | URBAN | Overloads |  | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
26/01/2024 | 17:23 | SA35 | URBAN | Overloads |  | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
26/01/2024 | 17:55 | ME200E | URBAN | Planned |  | 14.00 | 797.0 | 0.017203 | 0.0000216 | No
26/01/2024 | 18:00 | NL210A | URBAN | Asset failure | LV | 147.00 | 166.7 | 0.037781 | 0.0002266 | No
26/01/2024 | 20:42 | AP425A | URBAN | Asset failure | LV | 87.00 | 88.0 | 0.011804 | 0.0001341 | No
27/01/2024 | 04:13 | G31 | LONG RURAL | Unknown | Unknown | 54.00 | 370.0 | 0.143383 | 0.0003875 | No
27/01/2024 | 07:06 | VH43 | SHORT RURAL | Unknown | Unknown | 12.00 | 169.0 | 0.014268 | 0.0000844 | No
27/01/2024 | 08:20 | PP03 | URBAN | Asset failure | LV | 16.00 | 262.0 | 0.006463 | 0.0000247 | No
27/01/2024 | 09:21 | W06 | LONG RURAL | Asset failure | LV | 1.00 | 390.0 | 0.002799 | 0.0000072 | No
27/01/2024 | 10:33 | GA25 | SHORT RURAL | Asset failure | LV | 57.00 | 99.0 | 0.039701 | 0.0004010 | No
27/01/2024 | 10:45 | SG07 | SHORT RURAL | Other |  | 1.00 | 223.0 | 0.001569 | 0.0000070 | No
27/01/2024 | 11:37 | NA36 | LONG RURAL | Weather |  | 28.00 | 70.0 | 0.014066 | 0.0002009 | No
27/01/2024 | 13:01 | SA20 | URBAN | Asset failure | LV | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
27/01/2024 | 13:15 | AP424C | URBAN | Asset failure | LV | 19.33 | 219.0 | 0.006528 | 0.0000298 | No
27/01/2024 | 13:41 | ME427E | URBAN | Asset failure | LV | 10.00 | 257.0 | 0.003962 | 0.0000154 | No
27/01/2024 | 16:05 | HH341J | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
27/01/2024 | 17:11 | HH130B | URBAN | Overloads |  | 1.00 | 329.0 | 0.000507 | 0.0000015 | No
27/01/2024 | 17:56 | NL111Q | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
27/01/2024 | 18:49 | HH496A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 207.33 | 111.0 | 0.035482 | 0.0003197 | No
27/01/2024 | 18:52 | GU13 | LONG RURAL | Asset failure | LV | 2.67 | 176.0 | 0.003368 | 0.0000191 | No
27/01/2024 | 19:32 | SM374A | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
27/01/2024 | 19:57 | EL09 | URBAN | Third Party | Vehicle impact | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
27/01/2024 | 21:25 | HH145B | URBAN | Third Party | Other | 76.00 | 16.0 | 0.001875 | 0.0001172 | No
27/01/2024 | 21:51 | AP146A | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
28/01/2024 | 00:23 | PP04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 179.0 | 0.001259 | 0.0000070 | No
28/01/2024 | 00:50 | SM350B | URBAN | Animal | Animal impact | 1,754.00 | 85.0 | 0.229860 | 0.0027042 | No
28/01/2024 | 01:07 | HH386E | URBAN | Animal | Animal impact | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
28/01/2024 | 02:18 | SA14 | URBAN | Asset failure | LV | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
28/01/2024 | 08:20 | VH23 | SHORT RURAL | Animal | Animal impact | 1,400.00 | 71.7 | 0.705730 | 0.0098497 | No
28/01/2024 | 09:11 | HH107B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 25.0 | 0.000039 | 0.0000015 | No
28/01/2024 | 09:17 | ME116B | URBAN | Animal | Animal impact | 1.00 | 52.0 | 0.000080 | 0.0000015 | No
28/01/2024 | 09:41 | HH107B | URBAN | Asset failure | LV | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
28/01/2024 | 09:49 | ME116B | URBAN | Asset failure | LV | 168.00 | 73.0 | 0.018908 | 0.0002590 | No
28/01/2024 | 11:26 | AP125D | URBAN | Asset failure | LV | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
28/01/2024 | 11:36 | CN25 | LONG RURAL | Planned |  | 73.00 | 158.0 | 0.082772 | 0.0005239 | No
28/01/2024 | 14:46 | SM410D | URBAN | Asset failure | LV | 83.00 | 112.0 | 0.014332 | 0.0001280 | No
28/01/2024 | 14:46 | SM410B | URBAN | Asset failure | LV | 86.00 | 113.0 | 0.014983 | 0.0001326 | No
28/01/2024 | 15:35 | MG09 | SHORT RURAL | Overloads |  | 1.00 | 189.0 | 0.001330 | 0.0000070 | No
28/01/2024 | 15:52 | SM410B | URBAN | Asset failure | LV | 1.00 | 62.0 | 0.000096 | 0.0000015 | No
28/01/2024 | 16:01 | HH403B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
28/01/2024 | 16:55 | HH409A | URBAN | Asset failure | LV | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
28/01/2024 | 17:16 | G06 | LONG RURAL | Unknown | Unknown | 66.00 | 397.9 | 0.188443 | 0.0004736 | No
28/01/2024 | 18:33 | SM216E | URBAN | Asset failure | LV | 7.33 | 210.0 | 0.002374 | 0.0000113 | No
28/01/2024 | 18:55 | M51 | SHORT RURAL | Asset failure | LV | 1.00 | 1,113.0 | 0.007831 | 0.0000070 | No
28/01/2024 | 19:52 | SD40800 | LONG RURAL | Unknown | Unknown | 3.00 | 313.0 | 0.006739 | 0.0000215 | No
28/01/2024 | 20:13 | VH23 | SHORT RURAL | Weather |  | 17.00 | 55.0 | 0.006578 | 0.0001196 | No
28/01/2024 | 21:33 | YK13 | SHORT RURAL | Weather |  | 1.00 | 385.0 | 0.002709 | 0.0000070 | No
28/01/2024 | 22:45 | WK32 | SHORT RURAL | Asset failure | LV | 1.00 | 760.0 | 0.005347 | 0.0000070 | No
28/01/2024 | 22:48 | SM411B | URBAN | Asset failure | LV | 72.00 | 84.0 | 0.009325 | 0.0001110 | No
28/01/2024 | 23:13 | NU15 | LONG RURAL | Unknown | Unknown | 1.00 | 185.0 | 0.001328 | 0.0000072 | No
28/01/2024 | 23:26 | WK52 | SHORT RURAL | Unknown | Unknown | 123.00 | 27.2 | 0.023576 | 0.0008654 | No
29/01/2024 | 06:35 | HH522B | URBAN | Asset failure | LV | 1.00 | 479.0 | 0.000739 | 0.0000015 | No
29/01/2024 | 06:44 | CBD103C | URBAN | Overloads |  | 1.00 | 150.0 | 0.000231 | 0.0000015 | No
29/01/2024 | 07:20 | NL115B | URBAN | Asset failure | LV | 1.00 | 446.0 | 0.000688 | 0.0000015 | No
29/01/2024 | 08:26 | WK52 | SHORT RURAL | Animal | Animal impact | 1.00 | 179.0 | 0.001259 | 0.0000070 | No
29/01/2024 | 08:36 | MB14 | SHORT RURAL | Asset failure | HV | 107.00 | 87.7 | 0.065986 | 0.0007528 | No
29/01/2024 | 08:57 | GA20 | LONG RURAL | Planned |  | 1.00 | 321.0 | 0.002304 | 0.0000072 | No
29/01/2024 | 09:01 | HH522C | URBAN | Planned |  | 58.00 | 131.0 | 0.011714 | 0.0000894 | No
29/01/2024 | 09:22 | SG07 | SHORT RURAL | Planned |  | 13.00 | 309.2 | 0.028276 | 0.0000915 | No
29/01/2024 | 09:37 | MV14 | SHORT RURAL | Other |  | 3.00 | 120.0 | 0.002533 | 0.0000211 | No
29/01/2024 | 09:38 | YK12 | LONG RURAL | Planned |  | 50.00 | 276.0 | 0.099033 | 0.0003588 | No
29/01/2024 | 10:07 | EL260C | URBAN | Third Party | Dig-in | 2,472.00 | 37.6 | 0.143420 | 0.0038112 | No
29/01/2024 | 10:09 | MI14 | LONG RURAL | Planned |  | 6.00 | 313.0 | 0.013477 | 0.0000431 | No
29/01/2024 | 10:12 | CD17 | LONG RURAL | Planned |  | 1.00 | 156.0 | 0.001120 | 0.0000072 | No
29/01/2024 | 10:29 | VH10 | SHORT RURAL | Overloads |  | 1.00 | 290.0 | 0.002040 | 0.0000070 | No
29/01/2024 | 11:02 | W28 | LONG RURAL | Planned |  | 1.00 | 190.0 | 0.001364 | 0.0000072 | No
29/01/2024 | 11:06 | VH17 | SHORT RURAL | Weather |  | 592.00 | 7.1 | 0.029444 | 0.0041650 | No
29/01/2024 | 11:23 | SA17 | URBAN | Overloads |  | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
29/01/2024 | 11:35 | NU33 | LONG RURAL | Asset failure | LV | 1.00 | 68.0 | 0.000488 | 0.0000072 | No
29/01/2024 | 12:18 | R09 | LONG RURAL | Planned |  | 4.00 | 53.0 | 0.001521 | 0.0000287 | No
29/01/2024 | 12:51 | CBD367N | CBD | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 592.0 | 0.171061 | 0.0002890 | No
29/01/2024 | 13:14 | HH130B | URBAN | Asset failure | LV | 1.00 | 477.0 | 0.000735 | 0.0000015 | No
29/01/2024 | 13:15 | NL544B | URBAN | Asset failure | LV | 1.00 | 427.0 | 0.000658 | 0.0000015 | No
29/01/2024 | 13:57 | SM411C | URBAN | Planned |  | 124.00 | 3.0 | 0.000574 | 0.0001912 | No
29/01/2024 | 14:11 | CM24 | LONG RURAL | Planned |  | 1.00 | 17.0 | 0.000122 | 0.0000072 | No
29/01/2024 | 14:27 | HH522A | URBAN | Asset failure | LV | 4.00 | 327.0 | 0.002017 | 0.0000062 | No
29/01/2024 | 14:33 | HH496C | URBAN | Overloads |  | 1.00 | 376.0 | 0.000580 | 0.0000015 | No
29/01/2024 | 14:34 | ST11 | SHORT RURAL | Weather |  | 9.33 | 34.0 | 0.002233 | 0.0000657 | No
29/01/2024 | 16:31 | HH386B | URBAN | Asset failure | LV | 63.00 | 32.0 | 0.003108 | 0.0000971 | No
29/01/2024 | 17:09 | VH21 | SHORT RURAL | Asset failure | LV | 47.00 | 107.0 | 0.035381 | 0.0003307 | No
29/01/2024 | 17:30 | PA02 | URBAN | Asset failure | LV | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
29/01/2024 | 17:31 | ST13 | SHORT RURAL | Asset failure | HV | 318.00 | 130.6 | 0.292114 | 0.0022373 | No
29/01/2024 | 19:10 | EL11 | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
29/01/2024 | 19:23 | EL15 | URBAN | Animal | Animal impact | 4.00 | 48.0 | 0.000296 | 0.0000062 | No
29/01/2024 | 19:32 | MV64 | SHORT RURAL | Asset failure | LV | 48.67 | 129.0 | 0.044169 | 0.0003424 | No
29/01/2024 | 20:00 | HH386E | URBAN | Asset failure | LV | 42.00 | 88.5 | 0.005731 | 0.0000648 | No
29/01/2024 | 20:37 | SM349C | URBAN | Asset failure | LV | 74.00 | 121.0 | 0.013805 | 0.0001141 | No
29/01/2024 | 21:28 | HH428F | URBAN | Asset failure | LV | 34.00 | 48.0 | 0.002516 | 0.0000524 | No
29/01/2024 | 22:45 | NL760A | URBAN | Asset failure | LV | 19.00 | 346.0 | 0.010135 | 0.0000293 | No
29/01/2024 | 23:43 | HH107C | URBAN | Animal | Animal impact | 692.00 | 99.0 | 0.105622 | 0.0010669 | No
30/01/2024 | 00:12 | SSD369 | LONG RURAL | Unknown | Unknown | 3,040.00 | 93.0 | 2.028892 | 0.0218160 | No
30/01/2024 | 00:12 | SSD369 | SHORT RURAL | Unknown | Unknown | 4,934.00 | 93.7 | 3.250889 | 0.0347131 | No
30/01/2024 | 00:19 | GA53 | SHORT RURAL | Asset failure | HV | 170.00 | 144.9 | 0.173284 | 0.0011960 | No
30/01/2024 | 06:13 | MV34 | SHORT RURAL | Asset failure | LV | 17.33 | 257.0 | 0.031341 | 0.0001219 | No
30/01/2024 | 07:31 | BM21 | SHORT RURAL | Asset failure | LV | 1.00 | 45.0 | 0.000317 | 0.0000070 | No
30/01/2024 | 07:59 | HH121D | URBAN | Overloads |  | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
30/01/2024 | 08:08 | MG12 | LONG RURAL | Animal | Animal impact | 4.00 | 51.0 | 0.001464 | 0.0000287 | No
30/01/2024 | 08:14 | MV15 | SHORT RURAL | Planned |  | 23.00 | 375.5 | 0.060766 | 0.0001618 | No
30/01/2024 | 08:23 | CL06 | LONG RURAL | Planned |  | 6.00 | 420.0 | 0.018084 | 0.0000431 | No
30/01/2024 | 08:59 | MG15 | SHORT RURAL | Planned |  | 11.00 | 385.0 | 0.029795 | 0.0000774 | No
30/01/2024 | 09:06 | EL260B | URBAN | Planned |  | 24.00 | 297.4 | 0.011005 | 0.0000370 | No
30/01/2024 | 09:12 | NL21 | URBAN | Asset failure | LV | 1.00 | 746.0 | 0.001150 | 0.0000015 | No
30/01/2024 | 09:22 | CD24 | LONG RURAL | Planned |  | 8.00 | 188.0 | 0.010793 | 0.0000574 | No
30/01/2024 | 09:24 | EL11 | URBAN | Planned |  | 219.00 | 225.0 | 0.075970 | 0.0003376 | No
30/01/2024 | 09:26 | HH102B | URBAN | Planned |  | 132.00 | 448.0 | 0.091173 | 0.0002035 | No
30/01/2024 | 09:32 | HH341F | URBAN | Planned |  | 125.00 | 403.2 | 0.077709 | 0.0001927 | No
30/01/2024 | 09:33 | VH16 | SHORT RURAL | Planned |  | 81.00 | 193.0 | 0.109993 | 0.0005699 | No
30/01/2024 | 09:43 | VH45 | SHORT RURAL | Planned |  | 171.00 | 186.9 | 0.224805 | 0.0012031 | No
30/01/2024 | 09:59 | NL544B | URBAN | Asset failure | LV | 31.67 | 124.0 | 0.006054 | 0.0000488 | No
30/01/2024 | 09:59 | W27 | LONG RURAL | Planned |  | 62.00 | 292.0 | 0.129920 | 0.0004449 | No
30/01/2024 | 10:32 | KI53 | LONG RURAL | Planned |  | 1.00 | 67.0 | 0.000481 | 0.0000072 | No
30/01/2024 | 10:59 | VH23 | SHORT RURAL | Unknown | Unknown | 240.00 | 166.6 | 0.281286 | 0.0016885 | No
30/01/2024 | 11:12 | VH11 | URBAN | Unknown | Unknown | 3.00 | 4,205.0 | 0.019449 | 0.0000046 | No
30/01/2024 | 12:09 | KA06 | LONG RURAL | Unknown | Unknown | 2.00 | 138.0 | 0.001981 | 0.0000144 | No
30/01/2024 | 12:09 | AP425B | URBAN | Asset failure | LV | 1.00 | 865.0 | 0.001334 | 0.0000015 | No
30/01/2024 | 12:23 | NL111Q | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 21.33 | 95.0 | 0.003125 | 0.0000329 | No
30/01/2024 | 12:37 | VH17 | SHORT RURAL | Unknown | Unknown | 1.00 | 293.0 | 0.002061 | 0.0000070 | No
30/01/2024 | 12:42 | SG13 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,127.0 | 0.007929 | 0.0000070 | No
30/01/2024 | 13:13 | G12 | LONG RURAL | Planned |  | 2.00 | 71.0 | 0.001019 | 0.0000144 | No
30/01/2024 | 13:46 | SG13 | SHORT RURAL | Other |  | 1.00 | 342.0 | 0.002406 | 0.0000070 | No
30/01/2024 | 14:41 | EL19 | URBAN | Animal | Animal impact | 1.00 | 1,225.0 | 0.001889 | 0.0000015 | No
30/01/2024 | 15:37 | AP125D | URBAN | Overloads |  | 1.00 | 159.0 | 0.000245 | 0.0000015 | No
30/01/2024 | 15:41 | VH15 | SHORT RURAL | Unknown | Unknown | 1.00 | 205.0 | 0.001442 | 0.0000070 | No
30/01/2024 | 16:07 | MG10 | LONG RURAL | Overloads |  | 1.00 | 96.0 | 0.000689 | 0.0000072 | No
30/01/2024 | 16:13 | SM216C | URBAN | Network business | Switching and protection error | 1.00 | 44.0 | 0.000068 | 0.0000015 | No
30/01/2024 | 17:15 | AP424A | URBAN | Third Party | Dig-in | 86.00 | 185.0 | 0.024529 | 0.0001326 | No
30/01/2024 | 17:21 | NL115B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 6.00 | 139.0 | 0.001286 | 0.0000093 | No
30/01/2024 | 18:00 | R32 | LONG RURAL | Asset failure | LV | 1.00 | 327.0 | 0.002347 | 0.0000072 | No
30/01/2024 | 18:59 | ME427E | URBAN | Other |  | 41.00 | 232.0 | 0.014665 | 0.0000632 | No
30/01/2024 | 19:39 | SM350D | URBAN | Asset failure | LV | 24.00 | 73.0 | 0.002701 | 0.0000370 | No
30/01/2024 | 20:08 | HH341G | URBAN | Asset failure | LV | 136.00 | 182.7 | 0.038302 | 0.0002097 | No
30/01/2024 | 20:20 | WK33 | SHORT RURAL | Asset failure | LV | 1.00 | 142.0 | 0.000999 | 0.0000070 | No
30/01/2024 | 20:35 | YK22 | SHORT RURAL | Weather |  | 24.00 | 110.0 | 0.018574 | 0.0001689 | No
30/01/2024 | 22:34 | HH409F | URBAN | Third Party | Vehicle impact | 1.00 | 283.0 | 0.000436 | 0.0000015 | No
31/01/2024 | 08:02 | VH21 | SHORT RURAL | Planned |  | 526.00 | 231.0 | 0.854854 | 0.0037007 | No
31/01/2024 | 08:15 | EL14 | URBAN | Asset failure | LV | 97.00 | 64.0 | 0.009571 | 0.0001496 | No
31/01/2024 | 08:56 | EL14 | URBAN | Planned |  | 53.00 | 365.0 | 0.029825 | 0.0000817 | No
31/01/2024 | 09:08 | SD35100 | LONG RURAL | Planned |  | 2.00 | 170.0 | 0.002440 | 0.0000144 | No
31/01/2024 | 09:08 | BT26 | LONG RURAL | Planned |  | 2.00 | 275.0 | 0.003947 | 0.0000144 | No
31/01/2024 | 09:12 | VH43 | SHORT RURAL | Planned |  | 5.00 | 160.0 | 0.005628 | 0.0000352 | No
31/01/2024 | 09:24 | MV64 | SHORT RURAL | Planned |  | 62.00 | 342.0 | 0.149181 | 0.0004362 | No
31/01/2024 | 09:26 | GA25 | SHORT RURAL | Planned |  | 136.00 | 172.2 | 0.164743 | 0.0009568 | No
31/01/2024 | 09:30 | SA520E | URBAN | Weather |  | 1.00 | 114.0 | 0.000176 | 0.0000015 | No
31/01/2024 | 09:34 | EL25 | URBAN | Planned |  | 14.00 | 8.0 | 0.000173 | 0.0000216 | No
31/01/2024 | 09:35 | EL10 | URBAN | Planned |  | 134.00 | 303.2 | 0.062641 | 0.0002066 | No
31/01/2024 | 09:36 | VH22 | SHORT RURAL | Planned |  | 8.00 | 299.4 | 0.016850 | 0.0000563 | No
31/01/2024 | 09:43 | MV42 | SHORT RURAL | Planned |  | 36.00 | 155.0 | 0.039258 | 0.0002533 | No
31/01/2024 | 09:45 | CV753A | LONG RURAL | Planned |  | 6.00 | 316.0 | 0.013606 | 0.0000431 | No
31/01/2024 | 10:03 | M13 | LONG RURAL | Asset failure | HV | 1.00 | 25.0 | 0.000179 | 0.0000072 | No
31/01/2024 | 10:15 | SA14 | URBAN | Asset failure | LV | 1.00 | 415.0 | 0.000640 | 0.0000015 | No
31/01/2024 | 10:47 | AP226B | URBAN | Overloads |  | 3.00 | 152.0 | 0.000703 | 0.0000046 | No
31/01/2024 | 10:56 | PP04 | SHORT RURAL | Asset failure | LV | 4.00 | 121.0 | 0.003405 | 0.0000281 | No
31/01/2024 | 12:13 | R26 | LONG RURAL | Planned |  | 1.00 | 82.0 | 0.000588 | 0.0000072 | No
31/01/2024 | 12:16 | MG17 | LONG RURAL | Planned |  | 3.00 | 65.3 | 0.001407 | 0.0000215 | No
31/01/2024 | 14:54 | SM350F | URBAN | Asset failure | LV | 1.00 | 239.0 | 0.000368 | 0.0000015 | No
31/01/2024 | 14:55 | NL451A | URBAN | Asset failure | HV | 470.00 | 114.4 | 0.082895 | 0.0007246 | No
31/01/2024 | 15:21 | KA01 | SHORT RURAL | Asset failure | LV | 1.00 | 175.0 | 0.001231 | 0.0000070 | No
31/01/2024 | 17:27 | ME131C | URBAN | Asset failure | LV | 32.00 | 143.0 | 0.007055 | 0.0000493 | No
31/01/2024 | 19:27 | SM350E | URBAN | Asset failure | LV | 1.00 | 285.0 | 0.000439 | 0.0000015 | No
31/01/2024 | 20:50 | CBD412C | CBD | Planned |  | 15.00 | 1.0 | 0.002167 | 0.0021672 | No
31/01/2024 | 20:59 | CBD412D | CBD | Planned |  | 121.00 | 440.1 | 7.693419 | 0.0174818 | No
31/01/2024 | 21:12 | AP132A | URBAN | Planned |  | 97.00 | 359.5 | 0.053769 | 0.0001496 | No
01/02/2024 | 03:05 | SSD831 | SHORT RURAL | Asset failure | Zone substation | 818.00 | 130.7 | 0.752207 | 0.0057550 | No
01/02/2024 | 04:23 | CBD412C | CBD | Planned |  | 15.00 | 1.0 | 0.002167 | 0.0021672 | No
01/02/2024 | 07:16 | SG06 | SHORT RURAL | Unknown | Unknown | 1.00 | 117.0 | 0.000823 | 0.0000070 | No
01/02/2024 | 08:26 | SM179C | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
01/02/2024 | 08:27 | BM12 | SHORT RURAL | Planned |  | 113.00 | 412.5 | 0.327931 | 0.0007950 | No
01/02/2024 | 08:36 | VH10 | SHORT RURAL | Planned |  | 1,352.00 | 94.3 | 0.897306 | 0.0095120 | No
01/02/2024 | 08:44 | SA711C | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
01/02/2024 | 08:59 | VH44 | SHORT RURAL | Asset failure | HV | 2.00 | 107.0 | 0.001506 | 0.0000141 | No
01/02/2024 | 09:06 | MV31 | SHORT RURAL | Planned |  | 79.00 | 181.0 | 0.100600 | 0.0005558 | No
01/02/2024 | 09:20 | HH145E | URBAN | Planned |  | 78.00 | 238.0 | 0.028621 | 0.0001203 | No
01/02/2024 | 09:21 | VH35 | SHORT RURAL | Asset failure | LV | 1.00 | 613.0 | 0.004313 | 0.0000070 | No
01/02/2024 | 09:29 | MV41 | SHORT RURAL | Planned |  | 13.00 | 228.8 | 0.020924 | 0.0000915 | No
01/02/2024 | 09:34 | G16 | LONG RURAL | Planned |  | 22.00 | 75.0 | 0.011841 | 0.0001579 | No
01/02/2024 | 09:39 | SA33 | URBAN | Overloads |  | 5.00 | 188.0 | 0.001449 | 0.0000077 | No
01/02/2024 | 09:40 | CN52 | LONG RURAL | Planned |  | 12.00 | 271.0 | 0.023337 | 0.0000861 | No
01/02/2024 | 10:12 | ST11 | SHORT RURAL | Weather |  | 1.33 | 294.0 | 0.002758 | 0.0000094 | No
01/02/2024 | 10:31 | NL451E | URBAN | Third Party | Vehicle impact | 363.00 | 56.1 | 0.031396 | 0.0005597 | No
01/02/2024 | 10:46 | VH44 | SHORT RURAL | Planned |  | 65.00 | 171.0 | 0.078199 | 0.0004573 | No
01/02/2024 | 11:11 | PL01 | URBAN | Planned |  | 229.00 | 7.0 | 0.002471 | 0.0003531 | No
01/02/2024 | 11:13 | G07 | LONG RURAL | Other |  | 84.00 | 93.0 | 0.056061 | 0.0006028 | No
01/02/2024 | 11:32 | KI31 | SHORT RURAL | Planned |  | 5.00 | 188.0 | 0.006613 | 0.0000352 | No
01/02/2024 | 12:01 | HH145C | URBAN | Planned |  | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
01/02/2024 | 12:46 | G13 | LONG RURAL | Other |  | 20.00 | 54.0 | 0.007750 | 0.0001435 | No
01/02/2024 | 14:41 | SA744C | URBAN | Asset failure | LV | 2.00 | 229.0 | 0.000706 | 0.0000031 | No
01/02/2024 | 16:10 | WK33 | SHORT RURAL | Asset failure | LV | 1.00 | 207.0 | 0.001456 | 0.0000070 | No
01/02/2024 | 16:17 | KA25 | LONG RURAL | Asset failure | LV | 1.00 | 185.0 | 0.001328 | 0.0000072 | No
01/02/2024 | 16:46 | HH177G | URBAN | Overloads |  | 1.00 | 436.0 | 0.000672 | 0.0000015 | No
01/02/2024 | 16:49 | NL115F | URBAN | Asset failure | LV | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
01/02/2024 | 16:50 | NA52 | LONG RURAL | Weather |  | 1.00 | 1,178.0 | 0.008454 | 0.0000072 | No
01/02/2024 | 16:56 | SA19 | URBAN | Asset failure | LV | 2.00 | 267.0 | 0.000823 | 0.0000031 | No
01/02/2024 | 17:57 | CBD103C | URBAN | Asset failure | LV | 62.00 | 161.0 | 0.015390 | 0.0000956 | No
01/02/2024 | 19:06 | GA02 | SHORT RURAL | Unknown | Unknown | 32.00 | 290.0 | 0.065289 | 0.0002251 | No
01/02/2024 | 19:08 | GA02 | SHORT RURAL | Unknown | Unknown | 1.00 | 312.0 | 0.002195 | 0.0000070 | No
01/02/2024 | 20:20 | ME347B | URBAN | Asset failure | LV | 15.00 | 47.0 | 0.001087 | 0.0000231 | No
01/02/2024 | 21:17 | NL210D | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
01/02/2024 | 22:10 | HH409C | URBAN | Planned |  | 95.00 | 401.6 | 0.058827 | 0.0001465 | No
01/02/2024 | 22:42 | MG32 | LONG RURAL | Weather |  | 1.00 | 377.0 | 0.002705 | 0.0000072 | No
01/02/2024 | 22:44 | MG32 | LONG RURAL | Weather |  | 1.00 | 377.0 | 0.002705 | 0.0000072 | No
01/02/2024 | 22:59 | HH121C | URBAN | Overloads |  | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
01/02/2024 | 23:29 | M51 | SHORT RURAL | Asset failure | LV | 14.00 | 153.0 | 0.015070 | 0.0000985 | No
01/02/2024 | 23:33 | MG32 | LONG RURAL | Weather |  | 1.00 | 330.0 | 0.002368 | 0.0000072 | No
02/02/2024 | 00:55 | SM350F | URBAN | Planned |  | 912.33 | 6.3 | 0.008882 | 0.0014066 | No
02/02/2024 | 01:46 | NL234C | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
02/02/2024 | 03:22 | MG32 | LONG RURAL | Weather |  | 12.33 | 42.0 | 0.003717 | 0.0000885 | No
02/02/2024 | 06:43 | NL111D | URBAN | Asset failure | LV | 4.00 | 199.0 | 0.001227 | 0.0000062 | No
02/02/2024 | 07:17 | EL14 | URBAN | Planned |  | 423.00 | 63.5 | 0.041387 | 0.0006522 | No
02/02/2024 | 07:21 | VH23 | SHORT RURAL | Weather |  | 322.00 | 183.0 | 0.414573 | 0.0022654 | No
02/02/2024 | 07:56 | SA33 | URBAN | Unknown | Unknown | 5.00 | 138.0 | 0.001064 | 0.0000077 | No
02/02/2024 | 08:47 | AP132C | URBAN | Unknown | Unknown | 284.00 | 217.2 | 0.095122 | 0.0004379 | No
02/02/2024 | 08:54 | AP355D | URBAN | Overloads |  | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
02/02/2024 | 08:54 | BT37 | LONG RURAL | Planned |  | 1.00 | 44.0 | 0.000316 | 0.0000072 | No
02/02/2024 | 09:07 | CD15 | LONG RURAL | Planned |  | 8.00 | 346.0 | 0.019864 | 0.0000574 | No
02/02/2024 | 09:09 | VH61 | SHORT RURAL | Planned |  | 38.00 | 179.0 | 0.047855 | 0.0002673 | No
02/02/2024 | 09:10 | NL451C | URBAN | Planned |  | 204.00 | 279.2 | 0.087803 | 0.0003145 | No
02/02/2024 | 09:10 | CM17 | LONG RURAL | Planned |  | 4.00 | 146.0 | 0.004191 | 0.0000287 | No
02/02/2024 | 09:17 | NL451D | URBAN | Unknown | Unknown | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
02/02/2024 | 09:25 | SB18 | LONG RURAL | Planned |  | 7.00 | 110.0 | 0.005526 | 0.0000502 | No
02/02/2024 | 09:25 | MTB11 | SHORT RURAL | Third Party | Vehicle impact | 6.00 | 110.0 | 0.004643 | 0.0000422 | No
02/02/2024 | 09:43 | WK11 | SHORT RURAL | Planned |  | 14.00 | 176.0 | 0.017335 | 0.0000985 | No
02/02/2024 | 10:05 | M81 | LONG RURAL | Unknown | Unknown | 2.00 | 511.0 | 0.007334 | 0.0000144 | No
02/02/2024 | 10:16 | CN83 | LONG RURAL | Planned |  | 1.00 | 21.0 | 0.000151 | 0.0000072 | No
02/02/2024 | 10:18 | NL111B | URBAN | Asset failure | LV | 1.00 | 228.0 | 0.000352 | 0.0000015 | No
02/02/2024 | 11:02 | CV30 | LONG RURAL | Planned |  | 2.00 | 87.0 | 0.001249 | 0.0000144 | No
02/02/2024 | 12:34 | AP146A | URBAN | Overloads |  | 2.00 | 59.0 | 0.000182 | 0.0000031 | No
02/02/2024 | 12:46 | SD40400 | LONG RURAL | Unknown | Unknown | 130.67 | 90.5 | 0.084901 | 0.0009377 | No
02/02/2024 | 13:19 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 90.0 | 0.000633 | 0.0000070 | No
02/02/2024 | 13:59 | SD51200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 21.0 | 0.000151 | 0.0000072 | No
02/02/2024 | 15:02 | BM56 | SHORT RURAL | Animal | Animal impact | 14.00 | 134.0 | 0.013199 | 0.0000985 | No
02/02/2024 | 17:23 | SM349H | URBAN | Overloads |  | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
02/02/2024 | 18:42 | BU13 | LONG RURAL | Asset failure | HV | 15.00 | 134.0 | 0.014424 | 0.0001076 | No
02/02/2024 | 19:07 | SA744D | URBAN | Asset failure | LV | 23.00 | 287.0 | 0.010177 | 0.0000355 | No
03/02/2024 | 00:08 | GA05 | SHORT RURAL | Unknown | Unknown | 473.00 | 214.0 | 0.712146 | 0.0033278 | No
03/02/2024 | 02:10 | HH341G | URBAN | Animal | Animal impact | 204.00 | 126.8 | 0.039879 | 0.0003145 | No
03/02/2024 | 02:18 | HH341G | URBAN | Animal | Animal impact | 1.00 | 120.0 | 0.000185 | 0.0000015 | No
03/02/2024 | 03:01 | ME131B | URBAN | Animal | Animal impact | 704.00 | 138.0 | 0.149784 | 0.0010854 | No
03/02/2024 | 06:05 | SA744D | URBAN | Asset failure | LV | 1.00 | 243.0 | 0.000375 | 0.0000015 | No
03/02/2024 | 08:26 | VH23 | SHORT RURAL | Planned |  | 525.00 | 374.8 | 1.384479 | 0.0036936 | No
03/02/2024 | 09:24 | CBD103C | URBAN | Unknown | Unknown | 1.00 | 230.0 | 0.000355 | 0.0000015 | No
03/02/2024 | 09:35 | SM349E | URBAN | Asset failure | LV | 47.00 | 455.0 | 0.032970 | 0.0000725 | No
03/02/2024 | 10:22 | MV61 | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
03/02/2024 | 10:45 | HH409D | URBAN | Asset failure | LV | 3.00 | 476.7 | 0.002205 | 0.0000046 | No
03/02/2024 | 10:50 | WK32 | SHORT RURAL | Overloads |  | 1.00 | 458.0 | 0.003222 | 0.0000070 | No
03/02/2024 | 11:45 | G16 | LONG RURAL | Planned |  | 5.00 | 79.0 | 0.002835 | 0.0000359 | No
03/02/2024 | 12:48 | AP214A | URBAN | Asset failure | LV | 1.00 | 1,356.0 | 0.002091 | 0.0000015 | No
03/02/2024 | 14:10 | SM349C | URBAN | Third Party | Vehicle impact | 169.00 | 370.8 | 0.096622 | 0.0002606 | No
03/02/2024 | 14:33 | SM349C | URBAN | Third Party | Vehicle impact | 101.00 | 25.0 | 0.003893 | 0.0001557 | No
03/02/2024 | 14:35 | MI01 | LONG RURAL | Weather |  | 461.00 | 199.0 | 0.658392 | 0.0033083 | No
03/02/2024 | 15:12 | SM350B | URBAN | Asset failure | LV | 1.00 | 203.0 | 0.000313 | 0.0000015 | No
03/02/2024 | 17:07 | WHY01 | SHORT RURAL | Asset failure | LV | 1.00 | 209.0 | 0.001470 | 0.0000070 | No
03/02/2024 | 17:21 | ST36 | LONG RURAL | Third Party | Dig-in | 1.00 | 260.0 | 0.001866 | 0.0000072 | No
03/02/2024 | 17:41 | EL25 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,390.00 | 59.6 | 0.219789 | 0.0036848 | No
03/02/2024 | 17:58 | AP344D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,300.00 | 120.0 | 0.240514 | 0.0020043 | No
03/02/2024 | 19:43 | GA800A | SHORT RURAL | Overloads |  | 1.00 | 128.0 | 0.000901 | 0.0000070 | No
03/02/2024 | 20:08 | MV11 | SHORT RURAL | Asset failure | LV | 17.33 | 265.0 | 0.032316 | 0.0001219 | No
03/02/2024 | 20:28 | EL19 | URBAN | Overloads |  | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
03/02/2024 | 20:37 | AP227A | URBAN | Asset failure | LV | 24.00 | 126.0 | 0.004662 | 0.0000370 | No
03/02/2024 | 20:39 | NU34 | LONG RURAL | Asset failure | LV | 1.00 | 170.0 | 0.001220 | 0.0000072 | No
03/02/2024 | 22:00 | ME200G | URBAN | Third Party | Other | 111.00 | 20.5 | 0.003501 | 0.0001711 | No
03/02/2024 | 23:03 | LX51 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 116.00 | 141.0 | 0.115072 | 0.0008161 | No
03/02/2024 | 23:26 | SM349E | URBAN | Asset failure | LV | 13.00 | 952.0 | 0.019081 | 0.0000200 | No
04/02/2024 | 01:54 | MB13 | SHORT RURAL | Asset failure | LV | 1.00 | 260.0 | 0.001829 | 0.0000070 | No
04/02/2024 | 02:25 | HH432D | URBAN | Animal | Animal impact | 730.00 | 147.0 | 0.165446 | 0.0011255 | No
04/02/2024 | 02:32 | VH14 | SHORT RURAL | Unknown | Unknown | 5.00 | 478.0 | 0.016815 | 0.0000352 | No
04/02/2024 | 04:29 | SM126A | URBAN | Unknown | Unknown | 459.00 | 141.0 | 0.099781 | 0.0007077 | No
04/02/2024 | 04:37 | MB13 | SHORT RURAL | Asset failure | HV | 79.00 | 43.0 | 0.023900 | 0.0005558 | No
04/02/2024 | 04:45 | HH409C | URBAN | Unknown | Unknown | 82.67 | 334.0 | 0.042569 | 0.0001275 | No
04/02/2024 | 05:20 | SM126D | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 2,143.00 | 50.1 | 0.165450 | 0.0033040 | No
04/02/2024 | 05:29 | AP355H | URBAN | Unknown | Unknown | 1.00 | 212.0 | 0.000327 | 0.0000015 | No
04/02/2024 | 05:48 | AP146C | URBAN | Third Party | Unauthorised access | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
04/02/2024 | 06:24 | AP355H | URBAN | Unknown | Unknown | 2.00 | 162.0 | 0.000500 | 0.0000031 | No
04/02/2024 | 06:39 | R04 | LONG RURAL | Animal | Animal impact | 582.00 | 192.0 | 0.801912 | 0.0041766 | No
04/02/2024 | 06:56 | SD38200 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 3,508.00 | 289.1 | 7.277767 | 0.0251746 | No
04/02/2024 | 08:18 | VH16 | SHORT RURAL | Planned |  | 109.00 | 264.6 | 0.202932 | 0.0007669 | No
04/02/2024 | 08:29 | VH11 | URBAN | Planned |  | 29.00 | 162.8 | 0.007277 | 0.0000447 | No
04/02/2024 | 08:30 | HH341G | URBAN | Network business | Switching and protection error | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
04/02/2024 | 08:40 | ME347B | URBAN | Planned |  | 4.00 | 351.0 | 0.002165 | 0.0000062 | No
04/02/2024 | 08:48 | HH341G | URBAN | Planned |  | 453.00 | 382.9 | 0.267422 | 0.0006984 | No
04/02/2024 | 08:58 | NL210E | URBAN | Planned |  | 25.00 | 242.0 | 0.009328 | 0.0000385 | No
04/02/2024 | 09:03 | MV13 | SHORT RURAL | Unknown | Unknown | 4.67 | 253.0 | 0.008307 | 0.0000328 | No
04/02/2024 | 09:24 | VH16 | SHORT RURAL | Planned |  | 1.00 | 232.0 | 0.001632 | 0.0000070 | No
04/02/2024 | 09:34 | SG07 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 152.0 | 0.002139 | 0.0000141 | No
04/02/2024 | 09:37 | SM179C | URBAN | Asset failure | LV | 1.00 | 398.0 | 0.000614 | 0.0000015 | No
04/02/2024 | 09:52 | SD40400 | LONG RURAL | Unknown | Unknown | 161.00 | 23.8 | 0.027507 | 0.0011554 | No
04/02/2024 | 10:06 | SM216C | URBAN | Asset failure | LV | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
04/02/2024 | 10:27 | NL111C | URBAN | Asset failure | LV | 3.00 | 159.0 | 0.000735 | 0.0000046 | No
04/02/2024 | 10:48 | EL10 | URBAN | Asset failure | LV | 1.00 | 433.0 | 0.000668 | 0.0000015 | No
04/02/2024 | 10:54 | HH409C | URBAN | Network business | Switching and protection error | 1.00 | 48.0 | 0.000074 | 0.0000015 | No
04/02/2024 | 11:14 | KI31 | SHORT RURAL | Asset failure | HV | 21.00 | 34.0 | 0.005023 | 0.0001477 | No
04/02/2024 | 11:24 | NU34 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1,629.00 | 106.0 | 1.239166 | 0.0116902 | No
04/02/2024 | 12:17 | SA18 | URBAN | Asset failure | LV | 23.67 | 236.0 | 0.008611 | 0.0000365 | No
04/02/2024 | 12:52 | HH341H | URBAN | Asset failure | LV | 45.00 | 43.0 | 0.002983 | 0.0000694 | No
04/02/2024 | 13:48 | HH341D | URBAN | Asset failure | LV | 1.67 | 200.0 | 0.000514 | 0.0000026 | No
04/02/2024 | 13:59 | SM137A | URBAN | Third Party | Other | 2,646.00 | 105.1 | 0.428882 | 0.0040795 | No
04/02/2024 | 14:30 | HH145A | URBAN | Overloads |  | 19.00 | 228.0 | 0.006679 | 0.0000293 | No
04/02/2024 | 14:42 | SM350H | URBAN | Asset failure | LV | 1.00 | 538.0 | 0.000829 | 0.0000015 | No
04/02/2024 | 14:43 | SM349H | URBAN | Overloads |  | 1.00 | 619.0 | 0.000954 | 0.0000015 | No
04/02/2024 | 15:23 | BM31 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 7.00 | 124.0 | 0.006107 | 0.0000492 | No
04/02/2024 | 15:23 | SM350H | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
04/02/2024 | 15:24 | SM172E | URBAN | Unknown | Unknown | 46.00 | 401.0 | 0.028439 | 0.0000709 | No
04/02/2024 | 15:46 | MB82 | LONG RURAL | Asset failure | HV | 147.00 | 219.7 | 0.231781 | 0.0010549 | No
04/02/2024 | 16:07 | VH23 | SHORT RURAL | Asset failure | HV | 1,722.00 | 143.3 | 1.736676 | 0.0121151 | No
04/02/2024 | 16:29 | HH428B | URBAN | Overloads |  | 1.00 | 37.0 | 0.000057 | 0.0000015 | No
04/02/2024 | 16:37 | KA30 | SHORT RURAL | Asset failure | LV | 1.00 | 55.0 | 0.000387 | 0.0000070 | No
04/02/2024 | 16:53 | HH429C | URBAN | Asset failure | LV | 15.00 | 82.0 | 0.001896 | 0.0000231 | No
04/02/2024 | 17:08 | NU13 | LONG RURAL | Overloads |  | 1.00 | 265.0 | 0.001902 | 0.0000072 | No
04/02/2024 | 18:04 | SM349A | URBAN | Overloads |  | 26.67 | 157.0 | 0.006455 | 0.0000411 | No
04/02/2024 | 18:06 | GA02 | SHORT RURAL | Unknown | Unknown | 1,744.00 | 147.6 | 1.810963 | 0.0122699 | No
04/02/2024 | 18:47 | BS0191 | URBAN | Planned |  | 1.00 | 676.0 | 0.001042 | 0.0000015 | No
04/02/2024 | 19:01 | SA16 | URBAN | Asset failure | LV | 47.00 | 437.0 | 0.031666 | 0.0000725 | No
04/02/2024 | 19:09 | HH121B | URBAN | Asset failure | LV | 20.00 | 198.0 | 0.006105 | 0.0000308 | No
04/02/2024 | 19:20 | ME427D | URBAN | Unknown | Unknown | 1.00 | 767.0 | 0.001183 | 0.0000015 | No
04/02/2024 | 19:41 | ME427D | URBAN | Asset failure | LV | 5.33 | 142.0 | 0.001168 | 0.0000082 | No
04/02/2024 | 19:57 | NU20 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 1,009.00 | 166.0 | 1.201920 | 0.0072409 | No
04/02/2024 | 20:06 | EL08G | URBAN | Overloads |  | 1.00 | 26.0 | 0.000040 | 0.0000015 | No
04/02/2024 | 20:19 | HH145A | URBAN | Unknown | Unknown | 34.00 | 442.0 | 0.023169 | 0.0000524 | No
04/02/2024 | 21:02 | HH121B | URBAN | Asset failure | LV | 28.67 | 113.0 | 0.004994 | 0.0000442 | No
04/02/2024 | 21:19 | HH145D | URBAN | Asset failure | LV | 1.00 | 430.0 | 0.000663 | 0.0000015 | No
04/02/2024 | 22:41 | SB01 | LONG RURAL | Asset failure | HV | 3.00 | 129.0 | 0.002777 | 0.0000215 | No
04/02/2024 | 23:19 | ME347C | URBAN | Overloads |  | 45.00 | 97.0 | 0.006730 | 0.0000694 | No
04/02/2024 | 23:20 | HH130F | URBAN | Animal | Animal impact | 725.00 | 67.0 | 0.074891 | 0.0011178 | No
05/02/2024 | 00:30 | EL13 | URBAN | Unknown | Unknown | 1.00 | 157.0 | 0.000242 | 0.0000015 | No
05/02/2024 | 02:21 | HH130F | URBAN | Asset failure | LV | 1.00 | 38.0 | 0.000059 | 0.0000015 | No
05/02/2024 | 04:15 | SM411C | URBAN | Animal | Animal impact | 323.00 | 205.9 | 0.102553 | 0.0004980 | No
05/02/2024 | 05:51 | HH130A | URBAN | Unknown | Unknown | 75.00 | 163.0 | 0.018848 | 0.0001156 | No
05/02/2024 | 06:14 | SM410D | URBAN | Asset failure | LV | 3.00 | 323.0 | 0.001494 | 0.0000046 | No
05/02/2024 | 06:41 | AP372A | URBAN | Asset failure | LV | 88.00 | 139.0 | 0.018859 | 0.0001357 | No
05/02/2024 | 06:45 | SM349B | URBAN | Asset failure | LV | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
05/02/2024 | 07:12 | AP149D | URBAN | Unknown | Unknown | 18.00 | 94.0 | 0.002609 | 0.0000278 | No
05/02/2024 | 08:36 | VH22 | SHORT RURAL | Planned |  | 376.00 | 164.8 | 0.435863 | 0.0026453 | No
05/02/2024 | 08:40 | VH15 | SHORT RURAL | Planned |  | 2.00 | 150.5 | 0.002118 | 0.0000141 | No
05/02/2024 | 09:08 | MV33 | SHORT RURAL | Planned |  | 82.00 | 272.8 | 0.157405 | 0.0005769 | No
05/02/2024 | 09:21 | SM411E | URBAN | Planned |  | 99.00 | 189.5 | 0.028922 | 0.0001526 | No
05/02/2024 | 09:35 | HH496G | URBAN | Planned |  | 30.00 | 314.0 | 0.014523 | 0.0000463 | No
05/02/2024 | 09:35 | NA06 | LONG RURAL | Planned |  | 41.00 | 284.1 | 0.083597 | 0.0002942 | No
05/02/2024 | 09:41 | EL07 | URBAN | Overloads |  | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
05/02/2024 | 09:51 | EL04 | URBAN | Weather |  | 59.00 | 4.5 | 0.000407 | 0.0000910 | No
05/02/2024 | 09:51 | BT02 | LONG RURAL | Unknown | Unknown | 1.00 | 94.0 | 0.000675 | 0.0000072 | No
05/02/2024 | 09:53 | PL01 | URBAN | Planned |  | 9.00 | 223.0 | 0.003094 | 0.0000139 | No
05/02/2024 | 10:01 | G17 | LONG RURAL | Planned |  | 81.00 | 220.3 | 0.128076 | 0.0005813 | No
05/02/2024 | 10:02 | PL28 | LONG RURAL | Planned |  | 72.00 | 139.0 | 0.071821 | 0.0005167 | No
05/02/2024 | 10:06 | AP125B | URBAN | Third Party | Vehicle impact | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
05/02/2024 | 10:37 | SD31100 | LONG RURAL | Asset failure | Subtransmission | 980.00 | 186.4 | 1.310950 | 0.0070328 | No
05/02/2024 | 12:42 | MTB72 | LONG RURAL | Unknown | Unknown | 125.00 | 247.1 | 0.221619 | 0.0008970 | No
05/02/2024 | 13:11 | MT19 | LONG RURAL | Unknown | Unknown | 46.00 | 217.6 | 0.071828 | 0.0003301 | No
05/02/2024 | 13:23 | PA11 | LONG RURAL | Planned |  | 1.00 | 259.0 | 0.001859 | 0.0000072 | No
05/02/2024 | 13:28 | WHY06 | URBAN | Asset failure | LV | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
05/02/2024 | 13:58 | MTB11 | SHORT RURAL | Other |  | 2.00 | 55.0 | 0.000774 | 0.0000141 | No
05/02/2024 | 14:04 | HH428A | URBAN | Asset failure | LV | 134.00 | 434.0 | 0.089662 | 0.0002066 | No
05/02/2024 | 14:41 | BT02 | LONG RURAL | Unknown | Unknown | 1.00 | 131.0 | 0.000940 | 0.0000072 | No
05/02/2024 | 14:58 | HH496G | URBAN | Overloads |  | 2,868.00 | 8.4 | 0.037045 | 0.0044217 | No
05/02/2024 | 15:07 | AP355D | URBAN | Overloads |  | 1.00 | 453.0 | 0.000698 | 0.0000015 | No
05/02/2024 | 15:21 | EL09 | URBAN | Unknown | Unknown | 22.00 | 253.0 | 0.008581 | 0.0000339 | No
05/02/2024 | 15:28 | HH177B | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
05/02/2024 | 16:26 | WK31 | SHORT RURAL | Animal | Animal impact | 138.00 | 223.0 | 0.216510 | 0.0009709 | No
05/02/2024 | 16:49 | R04 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 295.0 | 0.002117 | 0.0000072 | No
05/02/2024 | 16:57 | ME427E | URBAN | Other |  | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
05/02/2024 | 17:24 | SA744C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 24.00 | 516.8 | 0.019122 | 0.0000370 | No
05/02/2024 | 22:34 | HH496A | URBAN | Asset failure | LV | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
06/02/2024 | 01:29 | HH409C | URBAN | Animal | Animal impact | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
06/02/2024 | 01:36 | HH409C | URBAN | Animal | Animal impact | 82.67 | 85.0 | 0.010833 | 0.0001275 | No
06/02/2024 | 01:43 | HH341G | URBAN | Animal | Animal impact | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
06/02/2024 | 02:04 | HH409C | URBAN | Animal | Animal impact | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
06/02/2024 | 02:29 | HH121F | URBAN | Animal | Animal impact | 240.00 | 86.0 | 0.031822 | 0.0003700 | No
06/02/2024 | 03:49 | SM374B | URBAN | Animal | Animal impact | 2,156.00 | 58.8 | 0.195507 | 0.0033240 | No
06/02/2024 | 07:50 | ME347F | URBAN | Third Party | Unauthorised access | 2.00 | 47.0 | 0.000145 | 0.0000031 | No
06/02/2024 | 08:03 | MB72 | LONG RURAL | Asset failure | HV | 195.67 | 4.7 | 0.006640 | 0.0014042 | No
06/02/2024 | 08:31 | NA09 | LONG RURAL | Planned |  | 513.00 | 294.7 | 1.084939 | 0.0036815 | No
06/02/2024 | 08:32 | MV34 | SHORT RURAL | Planned |  | 135.00 | 234.6 | 0.222779 | 0.0009498 | No
06/02/2024 | 08:33 | BT08 | LONG RURAL | Planned |  | 29.00 | 295.0 | 0.061393 | 0.0002081 | No
06/02/2024 | 09:34 | YK20 | LONG RURAL | Planned |  | 90.00 | 226.0 | 0.145967 | 0.0006459 | No
06/02/2024 | 09:59 | AP146B | URBAN | Planned |  | 89.00 | 297.0 | 0.040753 | 0.0001372 | No
06/02/2024 | 10:21 | MB71 | LONG RURAL | Asset failure | LV | 1.00 | 160.0 | 0.001148 | 0.0000072 | No
06/02/2024 | 11:23 | BM54 | SHORT RURAL | Asset failure | LV | 16.00 | 27.0 | 0.003039 | 0.0001126 | No
06/02/2024 | 12:32 | HH121C | URBAN | Asset failure | LV | 1.00 | 86.0 | 0.000133 | 0.0000015 | No
06/02/2024 | 12:57 | HH341D | URBAN | Asset failure | LV | 1.00 | 103.0 | 0.000159 | 0.0000015 | No
06/02/2024 | 13:05 | AP424B | URBAN | Asset failure | LV | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
06/02/2024 | 13:41 | HH496G | URBAN | Asset failure | LV | 9.00 | 307.0 | 0.004260 | 0.0000139 | No
06/02/2024 | 14:03 | M22 | LONG RURAL | Planned |  | 2.00 | 9.0 | 0.000129 | 0.0000144 | No
06/02/2024 | 14:21 | HH403A | URBAN | Asset failure | LV | 1.00 | 228.0 | 0.000352 | 0.0000015 | No
06/02/2024 | 14:37 | NL234C | URBAN | Asset failure | LV | 1.00 | 320.0 | 0.000493 | 0.0000015 | No
06/02/2024 | 14:41 | ST24 | SHORT RURAL | Animal | Animal impact | 65.00 | 21.0 | 0.009603 | 0.0004573 | No
06/02/2024 | 16:10 | WHY07 | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
06/02/2024 | 16:23 | HH409C | URBAN | Animal | Animal impact | 15.00 | 32.0 | 0.000740 | 0.0000231 | No
06/02/2024 | 18:30 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 226.0 | 0.001590 | 0.0000070 | No
06/02/2024 | 19:16 | HH496G | URBAN | Asset failure | LV | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
06/02/2024 | 19:32 | MB72 | LONG RURAL | Planned |  | 256.00 | 2.0 | 0.003674 | 0.0018371 | No
06/02/2024 | 19:32 | MB72 | LONG RURAL | Third Party | Other | 2.00 | 60.0 | 0.000861 | 0.0000144 | No
06/02/2024 | 21:24 | HH121A | URBAN | Overloads |  | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
06/02/2024 | 21:38 | SM126A | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 14.00 | 391.0 | 0.008440 | 0.0000216 | No
06/02/2024 | 21:49 | VH15 | SHORT RURAL | Asset failure | LV | 29.33 | 189.0 | 0.039005 | 0.0002064 | No
06/02/2024 | 22:41 | EL19 | URBAN | Asset failure | HV | 36.00 | 266.0 | 0.014764 | 0.0000555 | No
06/02/2024 | 23:13 | SA17 | URBAN | Asset failure | LV | 15.00 | 317.0 | 0.007331 | 0.0000231 | No
06/02/2024 | 23:41 | MV14 | SHORT RURAL | Planned |  | 200.00 | 1.0 | 0.001407 | 0.0014071 | No
06/02/2024 | 23:54 | MV22 | SHORT RURAL | Planned |  | 162.00 | 273.8 | 0.312052 | 0.0011397 | No
07/02/2024 | 03:20 | HH118B | URBAN | Animal | Animal impact | 88.00 | 13.0 | 0.001764 | 0.0001357 | No
07/02/2024 | 07:17 | MG32 | LONG RURAL | Unknown | Unknown | 19.00 | 399.0 | 0.054404 | 0.0001364 | No
07/02/2024 | 08:15 | PP10 | URBAN | Planned |  | 102.00 | 102.0 | 0.016040 | 0.0001573 | No
07/02/2024 | 08:59 | WK42 | SHORT RURAL | Asset failure | LV | 4.00 | 514.0 | 0.014465 | 0.0000281 | No
07/02/2024 | 09:05 | KI53 | LONG RURAL | Planned |  | 6.00 | 263.0 | 0.011324 | 0.0000431 | No
07/02/2024 | 09:07 | PA24 | LONG RURAL | Asset failure | LV | 2.00 | 79.0 | 0.001134 | 0.0000144 | No
07/02/2024 | 09:11 | HH496D | URBAN | Planned |  | 722.00 | 59.9 | 0.066644 | 0.0011131 | No
07/02/2024 | 09:24 | HH496G | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
07/02/2024 | 09:30 | VH43 | SHORT RURAL | Planned |  | 23.00 | 118.0 | 0.019094 | 0.0001618 | No
07/02/2024 | 09:36 | SD40300 | LONG RURAL | Planned |  | 80.00 | 234.0 | 0.134341 | 0.0005741 | No
07/02/2024 | 10:01 | HH118B | URBAN | Third Party | Vehicle impact | 2.00 | 335.0 | 0.001033 | 0.0000031 | No
07/02/2024 | 10:03 | SD46400 | SHORT RURAL | Planned |  | 24.00 | 144.0 | 0.024315 | 0.0001689 | No
07/02/2024 | 10:19 | SG11 | SHORT RURAL | Asset failure | HV | 92.00 | 75.0 | 0.048545 | 0.0006473 | No
07/02/2024 | 10:40 | HH496C | URBAN | Asset failure | HV | 28.00 | 138.0 | 0.005957 | 0.0000432 | No
07/02/2024 | 13:17 | VH21 | SHORT RURAL | Overloads |  | 29.33 | 60.0 | 0.012382 | 0.0002064 | No
07/02/2024 | 13:31 | SA520J | URBAN | Asset failure | LV | 1.00 | 57.0 | 0.000088 | 0.0000015 | No
07/02/2024 | 13:59 | HH118E | URBAN | Asset failure | LV | 1.00 | 523.0 | 0.000806 | 0.0000015 | No
07/02/2024 | 14:26 | W24 | LONG RURAL | Other |  | 2.00 | 191.0 | 0.002741 | 0.0000144 | No
07/02/2024 | 14:53 | ME347G | URBAN | Asset failure | LV | 2.00 | 48.0 | 0.000148 | 0.0000031 | No
07/02/2024 | 14:53 | CM10 | LONG RURAL | Unknown | Unknown | 1.00 | 81.0 | 0.000581 | 0.0000072 | No
07/02/2024 | 14:57 | SB17 | LONG RURAL | Unknown | Unknown | 91.00 | 239.0 | 0.156078 | 0.0006530 | No
07/02/2024 | 15:12 | M91 | LONG RURAL | Overloads |  | 2.00 | 448.0 | 0.006430 | 0.0000144 | No
07/02/2024 | 15:14 | NA29 | LONG RURAL | Planned |  | 1.00 | 29.0 | 0.000208 | 0.0000072 | No
07/02/2024 | 15:29 | AP149D | URBAN | Asset failure | LV | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
07/02/2024 | 18:14 | SM411A | URBAN | Asset failure | LV | 80.00 | 128.0 | 0.015788 | 0.0001233 | No
07/02/2024 | 18:18 | SM350H | URBAN | Overloads |  | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
07/02/2024 | 19:57 | SD33200 | LONG RURAL | Animal | Animal impact | 1.00 | 84.0 | 0.000603 | 0.0000072 | No
07/02/2024 | 20:16 | PA10 | LONG RURAL | Planned |  | 125.00 | 337.6 | 0.302841 | 0.0008970 | No
07/02/2024 | 20:46 | SA744D | URBAN | Asset failure | LV | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
07/02/2024 | 22:58 | SA20 | URBAN | Unknown | Unknown | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
07/02/2024 | 23:28 | SM179B | URBAN | Third Party | Other | 14.00 | 171.0 | 0.003691 | 0.0000216 | No
07/02/2024 | 23:40 | MTB21 | SHORT RURAL | Asset failure | HV | 10.00 | 189.0 | 0.013297 | 0.0000704 | No
08/02/2024 | 01:10 | ME427D | URBAN | Animal | Animal impact | 1,024.00 | 45.0 | 0.071044 | 0.0015788 | No
08/02/2024 | 05:17 | HH386G | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 400.00 | 379.1 | 0.233787 | 0.0006167 | No
08/02/2024 | 06:32 | NA04 | LONG RURAL | Animal | Animal impact | 46.33 | 170.0 | 0.056526 | 0.0003325 | No
08/02/2024 | 06:56 | NL760B | URBAN | Asset failure | LV | 89.00 | 125.0 | 0.017152 | 0.0001372 | No
08/02/2024 | 07:21 | ME347F | URBAN | Third Party | Unauthorised access | 6.00 | 187.0 | 0.001730 | 0.0000093 | No
08/02/2024 | 07:54 | HH341G | URBAN | Asset failure | LV | 1.00 | 273.0 | 0.000421 | 0.0000015 | No
08/02/2024 | 08:09 | NU03 | LONG RURAL | Animal | Animal impact | 2.00 | 124.0 | 0.001780 | 0.0000144 | No
08/02/2024 | 08:16 | NL234B | URBAN | Asset failure | LV | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
08/02/2024 | 08:28 | CV32 | LONG RURAL | Planned |  | 2.00 | 83.0 | 0.001191 | 0.0000144 | No
08/02/2024 | 08:31 | HH145A | URBAN | Asset failure | LV | 1.00 | 381.0 | 0.000587 | 0.0000015 | No
08/02/2024 | 08:38 | EL19 | URBAN | Planned |  | 2.00 | 233.5 | 0.000720 | 0.0000031 | No
08/02/2024 | 08:38 | EL19 | URBAN | Asset failure | HV | 416.00 | 210.2 | 0.134836 | 0.0006414 | No
08/02/2024 | 08:41 | GA01 | URBAN | Planned |  | 158.00 | 326.5 | 0.079533 | 0.0002436 | No
08/02/2024 | 08:51 | VH12 | SHORT RURAL | Planned |  | 46.00 | 69.0 | 0.022331 | 0.0003236 | No
08/02/2024 | 09:00 | MG03 | SHORT RURAL | Planned |  | 15.00 | 351.0 | 0.037042 | 0.0001055 | No
08/02/2024 | 09:05 | ST11 | SHORT RURAL | Planned |  | 11.00 | 327.0 | 0.025307 | 0.0000774 | No
08/02/2024 | 09:21 | SM216A | URBAN | Planned |  | 111.00 | 173.0 | 0.029606 | 0.0001711 | No
08/02/2024 | 09:22 | VH45 | SHORT RURAL | Planned |  | 41.00 | 181.2 | 0.052274 | 0.0002885 | No
08/02/2024 | 09:33 | WK61 | SHORT RURAL | Planned |  | 3.00 | 333.0 | 0.007028 | 0.0000211 | No
08/02/2024 | 09:50 | NL451A | URBAN | Planned |  | 241.00 | 64.2 | 0.023837 | 0.0003716 | No
08/02/2024 | 09:54 | CV32 | LONG RURAL | Planned |  | 1.00 | 42.0 | 0.000301 | 0.0000072 | No
08/02/2024 | 10:39 | CV32 | LONG RURAL | Planned |  | 2.00 | 17.0 | 0.000244 | 0.0000144 | No
08/02/2024 | 10:48 | CD22 | LONG RURAL | Planned |  | 1.00 | 12.0 | 0.000086 | 0.0000072 | No
08/02/2024 | 10:56 | SG11 | SHORT RURAL | Planned |  | 92.00 | 144.0 | 0.093206 | 0.0006473 | No
08/02/2024 | 11:19 | HH403B | URBAN | Asset failure | LV | 1.00 | 477.0 | 0.000735 | 0.0000015 | No
08/02/2024 | 11:44 | MI10 | LONG RURAL | Planned |  | 1.00 | 152.0 | 0.001091 | 0.0000072 | No
08/02/2024 | 11:45 | CD23 | LONG RURAL | Planned |  | 1.00 | 26.0 | 0.000187 | 0.0000072 | No
08/02/2024 | 12:09 | VH72 | SHORT RURAL | Overloads |  | 1.00 | 129.0 | 0.000908 | 0.0000070 | No
08/02/2024 | 12:36 | PP03 | URBAN | Asset failure | LV | 50.00 | 44.0 | 0.003392 | 0.0000771 | No
08/02/2024 | 12:46 | AP226C | URBAN | Asset failure | LV | 20.00 | 263.5 | 0.008125 | 0.0000308 | No
08/02/2024 | 12:46 | GA41 | LONG RURAL | Asset failure | HV | 51.00 | 80.0 | 0.029279 | 0.0003660 | No
08/02/2024 | 13:09 | AP214A | URBAN | Unknown | Unknown | 22.00 | 139.0 | 0.004715 | 0.0000339 | No
08/02/2024 | 14:04 | SM411E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 366.00 | 44.0 | 0.024828 | 0.0005643 | No
08/02/2024 | 15:03 | AP344D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,300.00 | 84.0 | 0.168292 | 0.0020043 | No
08/02/2024 | 15:17 | R04 | LONG RURAL | Asset failure | HV | 2.00 | 95.0 | 0.001364 | 0.0000144 | No
08/02/2024 | 15:45 | G13 | LONG RURAL | Asset failure | HV | 12.00 | 56.0 | 0.004822 | 0.0000861 | No
08/02/2024 | 16:19 | HH107C | URBAN | Asset failure | LV | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
08/02/2024 | 16:35 | MG27 | LONG RURAL | Asset failure | LV | 1.00 | 187.0 | 0.001342 | 0.0000072 | No
08/02/2024 | 16:41 | M23 | LONG RURAL | Planned |  | 18.00 | 53.0 | 0.006846 | 0.0001292 | No
08/02/2024 | 16:43 | MT19 | LONG RURAL | Asset failure | HV | 2.00 | 55.0 | 0.000789 | 0.0000144 | No
08/02/2024 | 16:50 | HH428B | URBAN | Overloads |  | 1.00 | 68.0 | 0.000105 | 0.0000015 | No
08/02/2024 | 16:51 | ST12 | SHORT RURAL | Planned |  | 61.00 | 104.0 | 0.044633 | 0.0004292 | No
08/02/2024 | 16:59 | NU05 | SHORT RURAL | Unknown | Unknown | 2.00 | 1,460.0 | 0.020544 | 0.0000141 | No
08/02/2024 | 17:33 | AP529C | URBAN | Overloads |  | 1.00 | 315.0 | 0.000486 | 0.0000015 | No
08/02/2024 | 17:55 | W24 | LONG RURAL | Unknown | Unknown | 14.00 | 1,068.0 | 0.107300 | 0.0001005 | No
08/02/2024 | 18:11 | HH177E | URBAN | Asset failure | LV | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
08/02/2024 | 18:55 | PP09 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 785.00 | 103.0 | 0.580271 | 0.0056334 | No
08/02/2024 | 19:13 | SM411C | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
08/02/2024 | 19:44 | MTB53 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 65.00 | 192.5 | 0.089805 | 0.0004665 | No
08/02/2024 | 20:36 | WK65 | SHORT RURAL | Unknown | Unknown | 61.00 | 223.0 | 0.095704 | 0.0004292 | No
08/02/2024 | 21:57 | HH341E | URBAN | Animal | Animal impact | 955.00 | 61.0 | 0.089815 | 0.0014724 | No
08/02/2024 | 22:02 | SM411B | URBAN | Unknown | Unknown | 1.00 | 667.0 | 0.001028 | 0.0000015 | No
09/02/2024 | 07:13 | ME347A | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
09/02/2024 | 08:23 | VH15 | SHORT RURAL | Planned |  | 77.00 | 139.0 | 0.075301 | 0.0005417 | No
09/02/2024 | 08:29 | PL07 | URBAN | Planned |  | 91.00 | 22.0 | 0.003087 | 0.0001403 | No
09/02/2024 | 08:39 | WHY10 | URBAN | Asset failure | LV | 1.00 | 234.0 | 0.000361 | 0.0000015 | No
09/02/2024 | 09:00 | EL16 | URBAN | Planned |  | 7.00 | 142.0 | 0.001533 | 0.0000108 | No
09/02/2024 | 09:11 | G07 | LONG RURAL | Planned |  | 27.00 | 53.0 | 0.010269 | 0.0001938 | No
09/02/2024 | 09:12 | CM04 | LONG RURAL | Planned |  | 21.00 | 237.0 | 0.035717 | 0.0001507 | No
09/02/2024 | 09:13 | GU41 | LONG RURAL | Asset failure | LV | 1.00 | 390.0 | 0.002799 | 0.0000072 | No
09/02/2024 | 09:25 | VH22 | SHORT RURAL | Planned |  | 3.00 | 298.0 | 0.006290 | 0.0000211 | No
09/02/2024 | 09:25 | KI55 | LONG RURAL | Planned |  | 2.00 | 132.0 | 0.001895 | 0.0000144 | No
09/02/2024 | 09:48 | WK72 | SHORT RURAL | Planned |  | 7.00 | 109.0 | 0.005368 | 0.0000492 | No
09/02/2024 | 09:50 | VH51 | SHORT RURAL | Planned |  | 28.00 | 108.0 | 0.021275 | 0.0001970 | No
09/02/2024 | 09:54 | CV21 | LONG RURAL | Planned |  | 18.00 | 103.0 | 0.013305 | 0.0001292 | No
09/02/2024 | 10:20 | KI42 | LONG RURAL | Planned |  | 2.00 | 179.0 | 0.002569 | 0.0000144 | No
09/02/2024 | 10:28 | YK19 | LONG RURAL | Planned |  | 40.00 | 124.0 | 0.035595 | 0.0002871 | No
09/02/2024 | 10:32 | SM126B | URBAN | Asset failure | LV | 1.00 | 91.0 | 0.000140 | 0.0000015 | No
09/02/2024 | 11:08 | HH130F | URBAN | Asset failure | LV | 29.33 | 121.0 | 0.005472 | 0.0000452 | No
09/02/2024 | 11:40 | CM22 | LONG RURAL | Planned |  | 16.00 | 70.0 | 0.008037 | 0.0001148 | No
09/02/2024 | 12:28 | NL234B | URBAN | Unknown | Unknown | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
09/02/2024 | 12:46 | G16 | LONG RURAL | Unknown | Unknown | 1.00 | 33.0 | 0.000237 | 0.0000072 | No
09/02/2024 | 12:56 | PL803C | URBAN | Asset failure | LV | 15.00 | 105.0 | 0.002428 | 0.0000231 | No
09/02/2024 | 14:54 | NL760B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 89.00 | 153.0 | 0.020994 | 0.0001372 | No
09/02/2024 | 15:49 | SG07 | SHORT RURAL | Asset failure | LV | 1.00 | 499.0 | 0.003511 | 0.0000070 | No
09/02/2024 | 15:53 | HH429C | URBAN | Overloads |  | 1.00 | 161.0 | 0.000248 | 0.0000015 | No
09/02/2024 | 15:55 | EL20 | URBAN | Unknown | Unknown | 1.00 | 3,729.0 | 0.005749 | 0.0000015 | No
09/02/2024 | 16:01 | NA01 | LONG RURAL | Asset failure | LV | 80.00 | 58.0 | 0.033298 | 0.0005741 | No
09/02/2024 | 16:02 | PP07 | LONG RURAL | Asset failure | HV | 88.00 | 73.6 | 0.046503 | 0.0006315 | No
09/02/2024 | 16:35 | CN74 | LONG RURAL | Planned |  | 1.00 | 136.0 | 0.000976 | 0.0000072 | No
09/02/2024 | 18:22 | ST12 | SHORT RURAL | Planned |  | 58.00 | 121.0 | 0.049375 | 0.0004081 | No
09/02/2024 | 19:14 | HH403B | URBAN | Asset failure | LV | 137.00 | 189.4 | 0.040010 | 0.0002112 | No
09/02/2024 | 19:25 | HH428B | URBAN | Unknown | Unknown | 2.00 | 534.0 | 0.001647 | 0.0000031 | No
09/02/2024 | 19:54 | SM411B | URBAN | Asset failure | LV | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
09/02/2024 | 20:51 | NU06 | LONG RURAL | Asset failure | LV | 1.00 | 282.0 | 0.002024 | 0.0000072 | No
09/02/2024 | 21:59 | HH341B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 820.00 | 174.8 | 0.221035 | 0.0012642 | No
10/02/2024 | 00:04 | SA744D | URBAN | Asset failure | LV | 71.00 | 100.0 | 0.010946 | 0.0001095 | No
10/02/2024 | 00:52 | W04 | LONG RURAL | Asset failure | HV | 1.00 | 547.0 | 0.003925 | 0.0000072 | No
10/02/2024 | 01:02 | MG48 | LONG RURAL | Unknown | Unknown | 1.00 | 135.0 | 0.000969 | 0.0000072 | No
10/02/2024 | 01:11 | HH148D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 442.00 | 72.0 | 0.049065 | 0.0006815 | No
10/02/2024 | 03:57 | HH428B | URBAN | Other |  | 188.00 | 63.7 | 0.018461 | 0.0002898 | No
10/02/2024 | 04:59 | ME200A | URBAN | Animal | Animal impact | 561.00 | 97.0 | 0.083898 | 0.0008649 | No
10/02/2024 | 05:24 | VH71 | SHORT RURAL | Asset failure | HV | 352.00 | 189.6 | 0.469633 | 0.0024765 | No
10/02/2024 | 07:27 | HH341D | URBAN | Asset failure | LV | 56.00 | 157.0 | 0.013555 | 0.0000863 | No
10/02/2024 | 07:40 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 361.0 | 0.002540 | 0.0000070 | No
10/02/2024 | 07:44 | BM54 | SHORT RURAL | Animal | Animal impact | 32.00 | 48.0 | 0.010807 | 0.0002251 | No
10/02/2024 | 08:09 | NU03 | LONG RURAL | Animal | Animal impact | 5.00 | 262.8 | 0.009430 | 0.0000359 | No
10/02/2024 | 08:29 | PA07 | LONG RURAL | Planned |  | 5.00 | 62.0 | 0.002225 | 0.0000359 | No
10/02/2024 | 08:41 | HH121B | URBAN | Asset failure | LV | 23.33 | 348.0 | 0.012519 | 0.0000360 | No
10/02/2024 | 09:14 | HH386F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 375.0 | 0.000578 | 0.0000015 | No
10/02/2024 | 11:36 | NL760B | URBAN | Asset failure | LV | 1.00 | 350.0 | 0.000540 | 0.0000015 | No
10/02/2024 | 11:47 | MG10 | LONG RURAL | Unknown | Unknown | 3.00 | 256.0 | 0.005511 | 0.0000215 | No
10/02/2024 | 11:59 | MV33 | SHORT RURAL | Third Party | Vehicle impact | 279.00 | 65.8 | 0.129200 | 0.0019629 | No
10/02/2024 | 12:09 | GA53 | SHORT RURAL | Asset failure | LV | 1.00 | 530.0 | 0.003729 | 0.0000070 | No
10/02/2024 | 13:03 | ME200G | URBAN | Asset failure | LV | 48.67 | 115.0 | 0.008629 | 0.0000750 | No
10/02/2024 | 15:14 | MB62 | LONG RURAL | Unknown | Unknown | 698.00 | 54.4 | 0.272327 | 0.0050091 | No
10/02/2024 | 15:27 | HH403A | URBAN | Animal | Animal impact | 46.00 | 70.0 | 0.004964 | 0.0000709 | No
10/02/2024 | 15:36 | SD34102 | LONG RURAL | Other |  | 1.00 | 447.0 | 0.003208 | 0.0000072 | No
10/02/2024 | 16:33 | SA18 | URBAN | Unknown | Unknown | 1.00 | 415.0 | 0.000640 | 0.0000015 | No
10/02/2024 | 16:57 | PL07 | URBAN | Asset failure | LV | 2.00 | 114.0 | 0.000352 | 0.0000031 | No
10/02/2024 | 16:59 | HH403A | URBAN | Asset failure | LV | 41.00 | 40.3 | 0.002550 | 0.0000632 | No
10/02/2024 | 17:56 | AP125D | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
10/02/2024 | 19:07 | SM172C | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
10/02/2024 | 20:59 | MB62 | LONG RURAL | Unknown | Unknown | 1.00 | 159.0 | 0.001141 | 0.0000072 | No
10/02/2024 | 21:24 | HH496D | URBAN | Unknown | Unknown | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
10/02/2024 | 21:38 | NU21 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 135.0 | 0.000969 | 0.0000072 | No
10/02/2024 | 21:39 | NU21 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 132.0 | 0.000947 | 0.0000072 | No
10/02/2024 | 22:15 | KI42 | LONG RURAL | Animal | Animal impact | 1.00 | 153.0 | 0.001098 | 0.0000072 | No
11/02/2024 | 01:38 | HH403B | URBAN | Unknown | Unknown | 45.00 | 75.0 | 0.005203 | 0.0000694 | No
11/02/2024 | 01:44 | HH403B | URBAN | Unknown | Unknown | 1,203.00 | 6.1 | 0.011258 | 0.0018547 | No
11/02/2024 | 01:56 | HH403B | URBAN | Unknown | Unknown | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
11/02/2024 | 01:59 | HH341B | URBAN | Animal | Animal impact | 20.67 | 121.0 | 0.003855 | 0.0000319 | No
11/02/2024 | 03:18 | HH107B | URBAN | Animal | Animal impact | 1,871.00 | 80.0 | 0.230770 | 0.0028846 | No
11/02/2024 | 05:09 | MG27 | LONG RURAL | Unknown | Unknown | 26.00 | 208.0 | 0.038810 | 0.0001866 | No
11/02/2024 | 05:20 | HH118C | URBAN | Animal | Animal impact | 575.00 | 61.0 | 0.054077 | 0.0008865 | No
11/02/2024 | 06:29 | MI28 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 51.00 | 256.0 | 0.093694 | 0.0003660 | No
11/02/2024 | 07:11 | NU15 | LONG RURAL | Planned |  | 2.00 | 226.0 | 0.003244 | 0.0000144 | No
11/02/2024 | 07:51 | EL14 | URBAN | Planned |  | 5.00 | 194.6 | 0.001500 | 0.0000077 | No
11/02/2024 | 08:27 | AP139C | URBAN | Planned |  | 39.00 | 374.3 | 0.022508 | 0.0000601 | No
11/02/2024 | 08:40 | ME131D | URBAN | Planned |  | 7.00 | 67.9 | 0.000732 | 0.0000108 | No
11/02/2024 | 11:36 | EL20 | URBAN | Overloads |  | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
11/02/2024 | 13:09 | MI16 | LONG RURAL | Weather |  | 17.67 | 39.0 | 0.004944 | 0.0001268 | No
11/02/2024 | 13:39 | GA11 | SHORT RURAL | Unknown | Unknown | 1.00 | 268.0 | 0.001886 | 0.0000070 | No
11/02/2024 | 15:27 | MG16 | LONG RURAL | Weather |  | 352.33 | 35.5 | 0.089642 | 0.0025285 | No
11/02/2024 | 15:57 | ME347C | URBAN | Asset failure | LV | 52.00 | 46.5 | 0.003731 | 0.0000802 | No
11/02/2024 | 16:37 | WK61 | SHORT RURAL | Unknown | Unknown | 71.67 | 176.0 | 0.088741 | 0.0005042 | No
11/02/2024 | 17:06 | MTB52 | LONG RURAL | Animal | Animal impact | 68.00 | 240.9 | 0.117577 | 0.0004880 | No
11/02/2024 | 17:06 | MTB52 | SHORT RURAL | Animal | Animal impact | 1.00 | 299.0 | 0.002104 | 0.0000070 | No
11/02/2024 | 17:45 | MTB11 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 139.0 | 0.001995 | 0.0000144 | No
11/02/2024 | 17:45 | MTB11 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 139.0 | 0.001956 | 0.0000141 | No
11/02/2024 | 19:16 | NL111B | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
11/02/2024 | 20:25 | MG06 | SHORT RURAL | Unknown | Unknown | 33.67 | 165.0 | 0.039082 | 0.0002369 | No
11/02/2024 | 21:29 | M92 | LONG RURAL | Overloads |  | 3.00 | 239.0 | 0.005145 | 0.0000215 | No
11/02/2024 | 22:03 | HH386B | URBAN | Planned |  | 144.00 | 308.0 | 0.068380 | 0.0002220 | No
11/02/2024 | 22:03 | AP355A | URBAN | Asset failure | LV | 1.00 | 458.0 | 0.000706 | 0.0000015 | No
11/02/2024 | 22:13 | VH15 | SHORT RURAL | Planned |  | 103.00 | 395.0 | 0.286246 | 0.0007247 | No
11/02/2024 | 23:45 | HH428F | URBAN | Animal | Animal impact | 610.00 | 170.7 | 0.160551 | 0.0009405 | No
12/02/2024 | 00:00 | HH386F | URBAN | Animal | Animal impact | 554.00 | 130.0 | 0.111037 | 0.0008541 | No
12/02/2024 | 01:07 | NL111E | URBAN | Third Party | Dig-in | 1.00 | 2,153.0 | 0.003319 | 0.0000015 | No
12/02/2024 | 01:21 | HH102A | URBAN | Animal | Animal impact | 53.33 | 282.0 | 0.023188 | 0.0000822 | No
12/02/2024 | 05:34 | HH102D | URBAN | Animal | Animal impact | 1,062.00 | 62.0 | 0.101515 | 0.0016373 | No
12/02/2024 | 06:24 | YK24 | LONG RURAL | Weather |  | 1.00 | 284.0 | 0.002038 | 0.0000072 | No
12/02/2024 | 06:41 | MG19 | LONG RURAL | Unknown | Unknown | 9.00 | 107.0 | 0.006911 | 0.0000646 | No
12/02/2024 | 06:46 | CD23 | LONG RURAL | Unknown | Unknown | 10.00 | 398.0 | 0.028562 | 0.0000718 | No
12/02/2024 | 06:50 | BM11 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 162.0 | 0.002279 | 0.0000141 | No
12/02/2024 | 08:06 | HH341B | URBAN | Third Party | Other | 1.00 | 387.0 | 0.000597 | 0.0000015 | No
12/02/2024 | 08:33 | PL34 | LONG RURAL | Unknown | Unknown | 2.00 | 98.0 | 0.001407 | 0.0000144 | No
12/02/2024 | 09:37 | MG11 | SHORT RURAL | Planned |  | 2.00 | 116.0 | 0.001632 | 0.0000141 | No
12/02/2024 | 09:45 | SM126E | URBAN | Planned |  | 27.00 | 190.0 | 0.007909 | 0.0000416 | No
12/02/2024 | 09:52 | NA06 | LONG RURAL | Asset failure | LV | 1.00 | 89.0 | 0.000639 | 0.0000072 | No
12/02/2024 | 10:00 | SM137D | URBAN | Asset failure | LV | 2.00 | 245.0 | 0.000755 | 0.0000031 | No
12/02/2024 | 10:24 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 285.0 | 0.002005 | 0.0000070 | No
12/02/2024 | 10:28 | PP12 | LONG RURAL | Asset failure | HV | 1.00 | 171.0 | 0.001227 | 0.0000072 | No
12/02/2024 | 11:08 | AP132B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 69.00 | 80.0 | 0.008510 | 0.0001064 | No
12/02/2024 | 11:48 | CM20 | LONG RURAL | Planned |  | 10.00 | 132.0 | 0.009473 | 0.0000718 | No
12/02/2024 | 11:59 | NL234E | URBAN | Third Party | Vehicle impact | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
12/02/2024 | 13:04 | HH428F | URBAN | Animal | Animal impact | 1.00 | 87.0 | 0.000134 | 0.0000015 | No
12/02/2024 | 13:16 | HH341A | URBAN | Unknown | Unknown | 1.00 | 12,909.0 | 0.019902 | 0.0000015 | No
12/02/2024 | 13:31 | MI14 | LONG RURAL | Asset failure | LV | 1.00 | 150.0 | 0.001076 | 0.0000072 | No
12/02/2024 | 13:52 | HH429C | URBAN | Other |  | 1.00 | 381.0 | 0.000587 | 0.0000015 | No
12/02/2024 | 14:07 | HH121A | URBAN | Asset failure | LV | 8.00 | 68.5 | 0.000845 | 0.0000123 | No
12/02/2024 | 14:34 | SM216E | URBAN | Network business | Switching and protection error | 4,204.00 | 4.0 | 0.025926 | 0.0064815 | No
12/02/2024 | 14:57 | WHY17 | SHORT RURAL | Other |  | 8.00 | 45.0 | 0.002533 | 0.0000563 | No
12/02/2024 | 15:58 | SM411B | URBAN | Asset failure | LV | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
12/02/2024 | 16:00 | MTB17 | SHORT RURAL | Unknown | Unknown | 2,193.00 | 182.3 | 2.812620 | 0.0154288 | No
12/02/2024 | 17:20 | MV52 | SHORT RURAL | Asset failure | LV | 1.00 | 309.0 | 0.002174 | 0.0000070 | No
12/02/2024 | 17:34 | G20 | LONG RURAL | Other |  | 12.00 | 21.0 | 0.001808 | 0.0000861 | No
12/02/2024 | 17:52 | CM15 | LONG RURAL | Asset failure | HV | 6.00 | 385.0 | 0.016577 | 0.0000431 | No
12/02/2024 | 18:38 | SM411A | URBAN | Asset failure | LV | 37.33 | 162.0 | 0.009325 | 0.0000576 | No
12/02/2024 | 18:40 | CBD27K | CBD | Asset failure | HV | 3.00 | 20.0 | 0.008669 | 0.0004334 | No
12/02/2024 | 19:01 | ME231C | URBAN | Overloads |  | 16.00 | 116.0 | 0.002861 | 0.0000247 | No
12/02/2024 | 19:20 | SM216E | URBAN | Asset failure | LV | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
12/02/2024 | 19:37 | HH341C | URBAN | Asset failure | LV | 118.00 | 396.0 | 0.072043 | 0.0001819 | No
12/02/2024 | 20:11 | HH121F | URBAN | Asset failure | LV | 23.33 | 93.0 | 0.003346 | 0.0000360 | No
12/02/2024 | 20:15 | MTB11 | LONG RURAL | Asset failure | HV | 3.00 | 35.0 | 0.000754 | 0.0000215 | No
12/02/2024 | 20:15 | MTB11 | SHORT RURAL | Asset failure | HV | 1,647.00 | 106.9 | 1.239041 | 0.0115875 | No
12/02/2024 | 20:21 | HH121F | URBAN | Overloads |  | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
12/02/2024 | 20:53 | HH121D | URBAN | Asset failure | LV | 69.00 | 102.0 | 0.010851 | 0.0001064 | No
12/02/2024 | 21:04 | AP149F | URBAN | Asset failure | LV | 86.00 | 99.0 | 0.013126 | 0.0001326 | No
12/02/2024 | 21:19 | NL234C | URBAN | Asset failure | LV | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
12/02/2024 | 21:19 | HH177F | URBAN | Overloads |  | 1.00 | 47.0 | 0.000072 | 0.0000015 | No
12/02/2024 | 21:31 | HH118D | URBAN | Third Party | Vehicle impact | 100.00 | 307.0 | 0.047332 | 0.0001542 | No
12/02/2024 | 21:42 | CV29 | LONG RURAL | Asset failure | HV | 13.00 | 545.0 | 0.050844 | 0.0000933 | No
12/02/2024 | 22:01 | HH145A | URBAN | Overloads |  | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
12/02/2024 | 23:58 | HH107A | URBAN | Overloads |  | 9.67 | 125.0 | 0.001863 | 0.0000149 | No
13/02/2024 | 00:53 | CV29 | LONG RURAL | Asset failure | LV | 1.00 | 710.0 | 0.005095 | 0.0000072 | No
13/02/2024 | 01:24 | SM179A | URBAN | Animal | Animal impact | 1,640.00 | 107.0 | 0.270547 | 0.0025285 | No
13/02/2024 | 01:25 | GA33 | SHORT RURAL | Asset failure | HV | 2.00 | 153.0 | 0.002153 | 0.0000141 | No
13/02/2024 | 01:25 | SA20 | URBAN | Overloads |  | 1.00 | 2,677.0 | 0.004127 | 0.0000015 | No
13/02/2024 | 01:37 | SM179C | URBAN | Animal | Animal impact | 1.00 | 126.0 | 0.000194 | 0.0000015 | No
13/02/2024 | 02:21 | YK24 | LONG RURAL | Unknown | Unknown | 67.00 | 392.0 | 0.188479 | 0.0004808 | No
13/02/2024 | 03:34 | HH429C | URBAN | Animal | Animal impact | 2,802.00 | 90.0 | 0.388747 | 0.0043200 | No
13/02/2024 | 03:39 | SM179A | URBAN | Unknown | Unknown | 9.00 | 33.0 | 0.000458 | 0.0000139 | No
13/02/2024 | 03:40 | SM179A | URBAN | Unknown | Unknown | 6.00 | 33.0 | 0.000305 | 0.0000093 | No
13/02/2024 | 04:10 | CD19 | LONG RURAL | Unknown | Unknown | 54.00 | 279.4 | 0.108262 | 0.0003875 | No
13/02/2024 | 06:29 | WHY17 | SHORT RURAL | Weather |  | 52.00 | 516.0 | 0.188776 | 0.0003658 | No
13/02/2024 | 08:12 | MG19 | LONG RURAL | Planned |  | 181.00 | 417.7 | 0.542509 | 0.0012989 | No
13/02/2024 | 08:20 | MG19 | LONG RURAL | Asset failure | HV | 1.00 | 1,200.0 | 0.008612 | 0.0000072 | No
13/02/2024 | 08:24 | SG06 | SHORT RURAL | Asset failure | LV | 1.00 | 145.0 | 0.001020 | 0.0000070 | No
13/02/2024 | 08:28 | NA52 | LONG RURAL | Overloads |  | 8.00 | 300.0 | 0.017223 | 0.0000574 | No
13/02/2024 | 08:56 | AP365E | URBAN | Planned |  | 59.00 | 358.7 | 0.032628 | 0.0000910 | No
13/02/2024 | 09:07 | MV63 | SHORT RURAL | Planned |  | 7.00 | 353.0 | 0.017385 | 0.0000492 | No
13/02/2024 | 09:30 | CL07 | LONG RURAL | Weather |  | 53.00 | 338.0 | 0.128557 | 0.0003803 | No
13/02/2024 | 10:54 | R18 | LONG RURAL | Unknown | Unknown | 38.00 | 200.0 | 0.054540 | 0.0002727 | No
13/02/2024 | 11:05 | R18 | LONG RURAL | Unknown | Unknown | 1.00 | 188.0 | 0.001349 | 0.0000072 | No
13/02/2024 | 11:08 | SM374B | URBAN | Asset failure | LV | 3.00 | 673.0 | 0.003113 | 0.0000046 | No
13/02/2024 | 11:10 | BM12 | SHORT RURAL | Asset failure | LV | 1.00 | 186.0 | 0.001309 | 0.0000070 | No
13/02/2024 | 11:20 | LX34 | SHORT RURAL | Asset failure | LV | 2.00 | 337.0 | 0.004742 | 0.0000141 | No
13/02/2024 | 11:36 | EL12 | URBAN | Asset failure | LV | 1.00 | 389.0 | 0.000600 | 0.0000015 | No
13/02/2024 | 12:05 | WK23 | SHORT RURAL | Weather |  | 2.00 | 573.0 | 0.008063 | 0.0000141 | No
13/02/2024 | 12:09 | WHY04 | URBAN | Asset failure | LV | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
13/02/2024 | 12:46 | SM349F | URBAN | Asset failure | LV | 35.33 | 113.0 | 0.006156 | 0.0000545 | No
13/02/2024 | 13:06 | LX43 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 92.0 | 0.000647 | 0.0000070 | No
13/02/2024 | 13:13 | VH45 | SHORT RURAL | Asset failure | LV | 12.33 | 68.0 | 0.005900 | 0.0000868 | No
13/02/2024 | 13:16 | YK25 | LONG RURAL | Planned |  | 334.00 | 89.0 | 0.213324 | 0.0023969 | No
13/02/2024 | 13:33 | HH409C | URBAN | Asset failure | LV | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
13/02/2024 | 13:55 | GU31 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 1,557.0 | 0.011174 | 0.0000072 | No
13/02/2024 | 13:59 | ME427F | URBAN | Asset failure | LV | 15.00 | 54.0 | 0.001249 | 0.0000231 | No
13/02/2024 | 14:20 | LX21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 44.00 | 164.7 | 0.050993 | 0.0003096 | No
13/02/2024 | 14:48 | BT23 | LONG RURAL | Asset failure | LV | 2.00 | 251.0 | 0.003603 | 0.0000144 | No
13/02/2024 | 14:59 | G14 | LONG RURAL | Asset failure | HV | 1.00 | 80.0 | 0.000574 | 0.0000072 | No
13/02/2024 | 15:37 | LX24 | SHORT RURAL | Unknown | Unknown | 317.00 | 190.0 | 0.423748 | 0.0022303 | No
13/02/2024 | 16:13 | MTB12 | SHORT RURAL | Overloads |  | 1.00 | 193.0 | 0.001358 | 0.0000070 | No
13/02/2024 | 16:15 | LX21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 165.00 | 48.3 | 0.056108 | 0.0011609 | No
13/02/2024 | 16:27 | SM350F | URBAN | Asset failure | LV | 1.00 | 350.0 | 0.000540 | 0.0000015 | No
13/02/2024 | 17:01 | VH21 | SHORT RURAL | Asset failure | HV | 353.67 | 81.0 | 0.201546 | 0.0024882 | No
13/02/2024 | 17:01 | VH21 | SHORT RURAL | Asset failure | LV | 84.00 | 81.0 | 0.047869 | 0.0005910 | No
13/02/2024 | 17:55 | SM349A | URBAN | Asset failure | LV | 14.33 | 190.0 | 0.004199 | 0.0000221 | No
13/02/2024 | 18:10 | SM349A | URBAN | Asset failure | LV | 2.00 | 182.0 | 0.000561 | 0.0000031 | No
13/02/2024 | 18:38 | M91 | LONG RURAL | Asset failure | LV | 3.33 | 106.0 | 0.002536 | 0.0000239 | No
13/02/2024 | 19:02 | VH23 | SHORT RURAL | Asset failure | LV | 14.00 | 145.6 | 0.014345 | 0.0000985 | No
13/02/2024 | 19:19 | WK23 | SHORT RURAL | Asset failure | HV | 4.00 | 953.0 | 0.026819 | 0.0000281 | No
13/02/2024 | 19:25 | NU02 | LONG RURAL | Asset failure | LV | 2.00 | 481.0 | 0.006904 | 0.0000144 | No
13/02/2024 | 19:43 | LX24 | SHORT RURAL | Asset failure | HV | 1.00 | 127.0 | 0.000894 | 0.0000070 | No
13/02/2024 | 19:43 | LX24 | SHORT RURAL | Weather |  | 3.00 | 1,104.0 | 0.023302 | 0.0000211 | No
13/02/2024 | 20:22 | HH121F | URBAN | Animal | Animal impact | 1.00 | 159.0 | 0.000245 | 0.0000015 | No
13/02/2024 | 20:37 | LX24 | SHORT RURAL | Asset failure | HV | 313.00 | 5.0 | 0.011011 | 0.0022021 | No
13/02/2024 | 21:06 | LX21 | SHORT RURAL | Weather |  | 208.00 | 375.9 | 0.550077 | 0.0014634 | No
13/02/2024 | 21:18 | HH341B | URBAN | Asset failure | LV | 1.00 | 357.0 | 0.000550 | 0.0000015 | No
13/02/2024 | 23:03 | SM374B | URBAN | Asset failure | LV | 3.00 | 675.0 | 0.003122 | 0.0000046 | No
13/02/2024 | 23:44 | HH107C | URBAN | Asset failure | LV | 84.00 | 267.0 | 0.034578 | 0.0001295 | No
14/02/2024 | 00:28 | YK08 | LONG RURAL | Weather |  | 48.00 | 321.0 | 0.110573 | 0.0003445 | No
14/02/2024 | 00:37 | HH341B | URBAN | Animal | Animal impact | 820.00 | 81.0 | 0.102403 | 0.0012642 | No
14/02/2024 | 06:20 | EL01Z | URBAN | Asset failure | LV | 1.00 | 773.0 | 0.001192 | 0.0000015 | No
14/02/2024 | 07:08 | MI16 | LONG RURAL | Asset failure | LV | 1.00 | 394.0 | 0.002827 | 0.0000072 | No
14/02/2024 | 07:14 | NA05 | LONG RURAL | Unknown | Unknown | 1.00 | 200.0 | 0.001435 | 0.0000072 | No
14/02/2024 | 08:54 | AP132B | URBAN | Planned |  | 2.00 | 212.0 | 0.000654 | 0.0000031 | No
14/02/2024 | 09:01 | M92 | LONG RURAL | Planned |  | 776.00 | 480.0 | 2.673039 | 0.0055688 | No
14/02/2024 | 09:28 | SD33200 | LONG RURAL | Planned |  | 2.00 | 252.0 | 0.003617 | 0.0000144 | No
14/02/2024 | 09:32 | HH428D | URBAN | Planned |  | 59.00 | 416.0 | 0.037841 | 0.0000910 | No
14/02/2024 | 09:33 | R06 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 1,804.0 | 0.012946 | 0.0000072 | No
14/02/2024 | 09:41 | G15 | LONG RURAL | Planned |  | 1.00 | 51.0 | 0.000366 | 0.0000072 | No
14/02/2024 | 09:57 | CV29 | LONG RURAL | Planned |  | 1.00 | 160.0 | 0.001148 | 0.0000072 | No
14/02/2024 | 09:58 | GA50 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 58.0 | 0.000179 | 0.0000031 | No
14/02/2024 | 10:12 | MV54 | SHORT RURAL | Asset failure | HV | 1.00 | 81.0 | 0.000570 | 0.0000070 | No
14/02/2024 | 10:35 | SA33 | URBAN | Asset failure | LV | 67.00 | 275.0 | 0.028407 | 0.0001033 | No
14/02/2024 | 11:14 | NA04 | LONG RURAL | Planned |  | 3.00 | 84.0 | 0.001808 | 0.0000215 | No
14/02/2024 | 14:06 | MG45 | URBAN | Asset failure | LV | 2.00 | 984.0 | 0.003034 | 0.0000031 | No
14/02/2024 | 14:13 | SM374B | URBAN | Asset failure | LV | 6.00 | 87.0 | 0.000805 | 0.0000093 | No
14/02/2024 | 14:20 | GU31 | LONG RURAL | Unknown | Unknown | 71.00 | 16.6 | 0.008482 | 0.0005095 | No
14/02/2024 | 14:31 | GA38 | LONG RURAL | Asset failure | HV | 25.00 | 39.0 | 0.006997 | 0.0001794 | No
14/02/2024 | 14:41 | NA05 | LONG RURAL | Unknown | Unknown | 2.00 | 18.0 | 0.000258 | 0.0000144 | No
14/02/2024 | 15:20 | GA800C | SHORT RURAL | Overloads |  | 1.00 | 127.0 | 0.000894 | 0.0000070 | No
14/02/2024 | 18:37 | AP149H | URBAN | Animal | Animal impact | 30.00 | 97.0 | 0.004487 | 0.0000463 | No
14/02/2024 | 20:09 | SM349A | URBAN | Asset failure | LV | 3.00 | 200.0 | 0.000925 | 0.0000046 | No
14/02/2024 | 21:22 | VH22 | SHORT RURAL | Overloads |  | 1.00 | 130.0 | 0.000915 | 0.0000070 | No
14/02/2024 | 22:08 | ME347E | URBAN | Planned |  | 12.00 | 342.0 | 0.006327 | 0.0000185 | No
15/02/2024 | 00:45 | HH121H | URBAN | Animal | Animal impact | 2,563.00 | 54.6 | 0.215893 | 0.0039515 | No
15/02/2024 | 00:46 | G31 | LONG RURAL | Unknown | Unknown | 54.00 | 675.5 | 0.261764 | 0.0003875 | No
15/02/2024 | 01:07 | GA20 | LONG RURAL | Other |  | 25.00 | 82.0 | 0.014704 | 0.0001794 | No
15/02/2024 | 05:13 | SM179D | URBAN | Animal | Animal impact | 78.00 | 330.0 | 0.039685 | 0.0001203 | No
15/02/2024 | 08:09 | CD02 | LONG RURAL | Planned |  | 6.00 | 213.0 | 0.009171 | 0.0000431 | No
15/02/2024 | 08:14 | ME116B | URBAN | Animal | Animal impact | 1,103.00 | 67.0 | 0.113937 | 0.0017006 | No
15/02/2024 | 08:33 | HH121B | URBAN | Planned |  | 99.00 | 277.0 | 0.042280 | 0.0001526 | No
15/02/2024 | 08:45 | BT07 | LONG RURAL | Planned |  | 40.00 | 229.4 | 0.065850 | 0.0002871 | No
15/02/2024 | 08:59 | SD35200 | LONG RURAL | Planned |  | 35.00 | 37.0 | 0.009293 | 0.0002512 | No
15/02/2024 | 09:01 | ST12 | SHORT RURAL | Planned |  | 58.00 | 92.0 | 0.037541 | 0.0004081 | No
15/02/2024 | 09:25 | HH386G | URBAN | Planned |  | 263.00 | 304.0 | 0.123266 | 0.0004055 | No
15/02/2024 | 09:43 | MV33 | SHORT RURAL | Planned |  | 54.00 | 290.2 | 0.110253 | 0.0003799 | No
15/02/2024 | 09:48 | W27 | LONG RURAL | Planned |  | 11.00 | 299.5 | 0.023639 | 0.0000789 | No
15/02/2024 | 09:53 | GU21 | LONG RURAL | Planned |  | 11.00 | 338.9 | 0.026753 | 0.0000789 | No
15/02/2024 | 10:13 | GA43 | SHORT RURAL | Asset failure | LV | 3.00 | 113.0 | 0.002385 | 0.0000211 | No
15/02/2024 | 10:17 | R09 | LONG RURAL | Planned |  | 114.00 | 318.0 | 0.260156 | 0.0008181 | No
15/02/2024 | 10:31 | NL111C | URBAN | Asset failure | LV | 81.00 | 164.0 | 0.020481 | 0.0001249 | No
15/02/2024 | 10:36 | HH121B | URBAN | Asset failure | LV | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
15/02/2024 | 10:36 | SD40400 | LONG RURAL | Asset failure | Subtransmission | 161.00 | 15.0 | 0.017331 | 0.0011554 | No
15/02/2024 | 10:54 | GA800A | SHORT RURAL | Asset failure | LV | 2.00 | 317.0 | 0.004461 | 0.0000141 | No
15/02/2024 | 11:08 | HH386A | URBAN | Planned |  | 7.00 | 294.6 | 0.003179 | 0.0000108 | No
15/02/2024 | 11:29 | G11 | LONG RURAL | Asset failure | LV | 2.00 | 1,622.0 | 0.023280 | 0.0000144 | No
15/02/2024 | 11:52 | MG17 | LONG RURAL | Asset failure | HV | 49.00 | 33.0 | 0.011604 | 0.0003516 | No
15/02/2024 | 12:00 | MG19 | LONG RURAL | Asset failure | HV | 1.00 | 22.0 | 0.000158 | 0.0000072 | No
15/02/2024 | 12:09 | GU43 | LONG RURAL | Unknown | Unknown | 34.00 | 106.0 | 0.025863 | 0.0002440 | No
15/02/2024 | 12:28 | CN32 | LONG RURAL | Planned |  | 17.00 | 174.0 | 0.021228 | 0.0001220 | No
15/02/2024 | 12:29 | HH177E | URBAN | Overloads |  | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
15/02/2024 | 14:05 | SB17 | LONG RURAL | Network business | Switching and protection error | 91.00 | 310.0 | 0.202444 | 0.0006530 | No
15/02/2024 | 16:42 | ME131A | URBAN | Asset failure | LV | 3.33 | 270.0 | 0.001388 | 0.0000051 | No
15/02/2024 | 17:35 | EL01L | URBAN | Asset failure | LV | 1.00 | 211.0 | 0.000325 | 0.0000015 | No
15/02/2024 | 19:29 | HH429A | URBAN | Other |  | 1.00 | 263.0 | 0.000405 | 0.0000015 | No
15/02/2024 | 20:15 | GU31 | LONG RURAL | Asset failure | HV | 71.00 | 342.5 | 0.174514 | 0.0005095 | No
15/02/2024 | 21:30 | ME427A | URBAN | Asset failure | LV | 110.00 | 64.0 | 0.010854 | 0.0001696 | No
15/02/2024 | 23:56 | WHY03 | URBAN | Third Party | Vehicle impact | 39.00 | 214.0 | 0.012867 | 0.0000601 | No
16/02/2024 | 02:56 | EL01N | URBAN | Asset failure | LV | 18.00 | 264.0 | 0.007326 | 0.0000278 | No
16/02/2024 | 06:14 | SG04 | SHORT RURAL | Asset failure | LV | 1.00 | 181.0 | 0.001273 | 0.0000070 | No
16/02/2024 | 06:52 | EL19 | URBAN | Unknown | Unknown | 26.00 | 163.0 | 0.006534 | 0.0000401 | No
16/02/2024 | 07:25 | SB17 | LONG RURAL | Unknown | Unknown | 35.00 | 242.0 | 0.060784 | 0.0002512 | No
16/02/2024 | 08:37 | GA25 | SHORT RURAL | Asset failure | LV | 18.33 | 301.0 | 0.038824 | 0.0001290 | No
16/02/2024 | 08:41 | CN41 | LONG RURAL | Planned |  | 28.00 | 482.9 | 0.097038 | 0.0002009 | No
16/02/2024 | 08:54 | CL06 | LONG RURAL | Planned |  | 8.00 | 149.0 | 0.008554 | 0.0000574 | No
16/02/2024 | 08:56 | SSD090 | SHORT RURAL | Planned |  | 55.00 | 1.0 | 0.000387 | 0.0003870 | No
16/02/2024 | 09:08 | HH177E | URBAN | Asset failure | LV | 93.00 | 59.4 | 0.008521 | 0.0001434 | No
16/02/2024 | 09:18 | WK11 | SHORT RURAL | Planned |  | 23.00 | 149.9 | 0.024258 | 0.0001618 | No
16/02/2024 | 09:19 | MV33 | SHORT RURAL | Planned |  | 148.00 | 268.8 | 0.279900 | 0.0010413 | No
16/02/2024 | 09:24 | SA520D | URBAN | Overloads |  | 1.00 | 294.0 | 0.000453 | 0.0000015 | No
16/02/2024 | 09:35 | MT08 | LONG RURAL | Planned |  | 193.00 | 299.4 | 0.414734 | 0.0013850 | No
16/02/2024 | 10:15 | M01 | LONG RURAL | Planned |  | 2.00 | 156.0 | 0.002239 | 0.0000144 | No
16/02/2024 | 10:36 | G18 | LONG RURAL | Planned |  | 59.00 | 49.0 | 0.020747 | 0.0004234 | No
16/02/2024 | 10:38 | NL234A | URBAN | Planned |  | 112.00 | 126.0 | 0.021757 | 0.0001727 | No
16/02/2024 | 11:29 | BM13 | SHORT RURAL | Asset failure | LV | 55.00 | 218.0 | 0.084356 | 0.0003870 | No
16/02/2024 | 11:35 | NA06 | LONG RURAL | Asset failure | LV | 3.00 | 232.0 | 0.004995 | 0.0000215 | No
16/02/2024 | 12:29 | R14 | LONG RURAL | Planned |  | 2.00 | 78.0 | 0.001120 | 0.0000144 | No
16/02/2024 | 14:24 | SM126A | URBAN | Asset failure | LV | 28.00 | 76.6 | 0.003309 | 0.0000432 | No
16/02/2024 | 17:17 | R18 | LONG RURAL | Unknown | Unknown | 14.00 | 240.0 | 0.024112 | 0.0001005 | No
16/02/2024 | 19:02 | AP365A | URBAN | Asset failure | LV | 89.00 | 63.0 | 0.008645 | 0.0001372 | No
16/02/2024 | 19:29 | SA17 | URBAN | Asset failure | LV | 1.00 | 97.0 | 0.000150 | 0.0000015 | No
16/02/2024 | 20:34 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 137.0 | 0.000964 | 0.0000070 | No
16/02/2024 | 21:43 | MG22 | LONG RURAL | Unknown | Unknown | 137.00 | 21.5 | 0.021149 | 0.0009832 | No
16/02/2024 | 23:46 | SA11 | URBAN | Asset failure | LV | 64.00 | 74.3 | 0.007333 | 0.0000987 | No
17/02/2024 | 00:35 | SG13 | SHORT RURAL | Animal | Animal impact | 1.00 | 80.0 | 0.000563 | 0.0000070 | No
17/02/2024 | 01:11 | MI32 | LONG RURAL | Animal | Animal impact | 49.33 | 207.0 | 0.073285 | 0.0003540 | No
17/02/2024 | 01:44 | AP529E | URBAN | Vegetation | Grow-in - NSP responsibility | 54.00 | 142.0 | 0.011822 | 0.0000833 | No
17/02/2024 | 02:45 | SM350G | URBAN | Asset failure | HV | 685.00 | 239.9 | 0.253352 | 0.0010561 | No
17/02/2024 | 04:23 | SD37301 | SHORT RURAL | Unknown | Unknown | 2.67 | 199.0 | 0.003734 | 0.0000188 | No
17/02/2024 | 04:35 | HH386C | URBAN | Animal | Animal impact | 1,435.00 | 107.0 | 0.236729 | 0.0022124 | No
17/02/2024 | 04:37 | HH177G | URBAN | Asset failure | LV | 18.00 | 599.0 | 0.016623 | 0.0000278 | No
17/02/2024 | 05:06 | SM411C | URBAN | Animal | Animal impact | 256.67 | 146.0 | 0.057777 | 0.0003957 | No
17/02/2024 | 05:06 | SM350B | URBAN | Animal | Animal impact | 1,756.00 | 256.0 | 0.693074 | 0.0027073 | No
17/02/2024 | 05:40 | HH341E | URBAN | Animal | Animal impact | 953.00 | 99.0 | 0.145460 | 0.0014693 | No
17/02/2024 | 05:47 | HH409E | URBAN | Third Party | Other | 72.00 | 546.0 | 0.060609 | 0.0001110 | No
17/02/2024 | 07:19 | NU13 | LONG RURAL | Unknown | Unknown | 4.00 | 146.0 | 0.004191 | 0.0000287 | No
17/02/2024 | 07:28 | HH121H | URBAN | Asset failure | LV | 52.00 | 259.0 | 0.020764 | 0.0000802 | No
17/02/2024 | 08:08 | HH409E | URBAN | Third Party | Other | 2.00 | 484.0 | 0.001492 | 0.0000031 | No
17/02/2024 | 09:07 | MTB17 | SHORT RURAL | Animal | Animal impact | 10.33 | 131.0 | 0.009524 | 0.0000727 | No
17/02/2024 | 09:57 | HH107E | URBAN | Asset failure | LV | 1.00 | 303.0 | 0.000467 | 0.0000015 | No
17/02/2024 | 10:31 | ME116D | URBAN | Asset failure | LV | 68.00 | 77.0 | 0.008073 | 0.0001048 | No
17/02/2024 | 11:45 | SM350B | URBAN | Asset failure | LV | 16.00 | 125.0 | 0.003084 | 0.0000247 | No
17/02/2024 | 18:22 | KA08 | LONG RURAL | Unknown | Unknown | 2.00 | 101.0 | 0.001450 | 0.0000144 | No
17/02/2024 | 20:59 | WK41 | SHORT RURAL | Asset failure | LV | 1.00 | 207.0 | 0.001456 | 0.0000070 | No
18/02/2024 | 00:01 | HH403A | URBAN | Unknown | Unknown | 1,531.00 | 90.0 | 0.212438 | 0.0023604 | No
18/02/2024 | 03:07 | HH102C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
18/02/2024 | 04:04 | HH102A | URBAN | Animal | Animal impact | 1,053.00 | 70.0 | 0.113643 | 0.0016235 | No
18/02/2024 | 06:22 | LX51 | SHORT RURAL | Animal | Animal impact | 1.00 | 273.0 | 0.001921 | 0.0000070 | No
18/02/2024 | 06:32 | MG09 | SHORT RURAL | Unknown | Unknown | 1.33 | 223.0 | 0.002092 | 0.0000094 | No
18/02/2024 | 07:28 | MV22 | SHORT RURAL | Asset failure | HV | 58.67 | 230.3 | 0.095045 | 0.0004127 | No
18/02/2024 | 08:13 | PA13 | LONG RURAL | Planned |  | 4.00 | 179.0 | 0.005138 | 0.0000287 | No
18/02/2024 | 08:18 | CBD366E | URBAN | Planned |  | 646.00 | 227.4 | 0.226519 | 0.0009960 | No
18/02/2024 | 08:27 | SD32200 | LONG RURAL | Planned |  | 3.00 | 54.0 | 0.001163 | 0.0000215 | No
18/02/2024 | 08:32 | CN32 | LONG RURAL | Planned |  | 20.00 | 294.9 | 0.042326 | 0.0001435 | No
18/02/2024 | 08:39 | HH341F | URBAN | Planned |  | 103.00 | 366.0 | 0.058121 | 0.0001588 | No
18/02/2024 | 09:09 | NL115A | URBAN | Asset failure | LV | 1.00 | 406.0 | 0.000626 | 0.0000015 | No
18/02/2024 | 09:51 | HH341J | URBAN | Asset failure | LV | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
18/02/2024 | 10:53 | SM349H | URBAN | Asset failure | LV | 1.00 | 372.0 | 0.000574 | 0.0000015 | No
18/02/2024 | 11:06 | PA02 | URBAN | Asset failure | LV | 50.00 | 122.0 | 0.009405 | 0.0000771 | No
18/02/2024 | 11:50 | SA711C | URBAN | Overloads |  | 1.00 | 488.0 | 0.000752 | 0.0000015 | No
18/02/2024 | 15:35 | ME200G | URBAN | Asset failure | LV | 1.00 | 445.0 | 0.000686 | 0.0000015 | No
18/02/2024 | 15:54 | SA16 | URBAN | Unknown | Unknown | 1.00 | 247.0 | 0.000381 | 0.0000015 | No
18/02/2024 | 16:32 | SA32 | URBAN | Third Party | Other | 851.00 | 56.0 | 0.073474 | 0.0013120 | No
18/02/2024 | 17:11 | SG01 | SHORT RURAL | Asset failure | LV | 1.33 | 476.0 | 0.004465 | 0.0000094 | No
18/02/2024 | 17:45 | MT05 | LONG RURAL | Asset failure | LV | 1.00 | 439.0 | 0.003150 | 0.0000072 | No
18/02/2024 | 18:39 | HH409F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 717.00 | 121.0 | 0.133758 | 0.0011054 | No
18/02/2024 | 19:59 | HH522B | URBAN | Overloads |  | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
18/02/2024 | 20:34 | SA711C | URBAN | Asset failure | LV | 6.00 | 124.0 | 0.001147 | 0.0000093 | No
18/02/2024 | 20:58 | ME347F | URBAN | Asset failure | LV | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
18/02/2024 | 21:18 | SD44200 | SHORT RURAL | Planned |  | 296.00 | 52.0 | 0.108290 | 0.0020825 | No
18/02/2024 | 22:05 | NL210C | URBAN | Asset failure | LV | 1.00 | 264.0 | 0.000407 | 0.0000015 | No
19/02/2024 | 01:05 | ME231D | URBAN | Animal | Animal impact | 1,666.00 | 119.0 | 0.305659 | 0.0025686 | No
19/02/2024 | 02:54 | NL111B | URBAN | Asset failure | HV | 1,971.00 | 132.3 | 0.401935 | 0.0030388 | No
19/02/2024 | 03:30 | SA520D | URBAN | Overloads |  | 1.00 | 369.0 | 0.000569 | 0.0000015 | No
19/02/2024 | 07:23 | VH15 | SHORT RURAL | Unknown | Unknown | 194.33 | 81.0 | 0.110746 | 0.0013672 | No
19/02/2024 | 08:28 | PL24 | LONG RURAL | Planned |  | 39.00 | 308.0 | 0.086202 | 0.0002799 | No
19/02/2024 | 08:51 | LX31 | SHORT RURAL | Asset failure | HV | 3.00 | 167.3 | 0.003532 | 0.0000211 | No
19/02/2024 | 08:56 | MT14 | SHORT RURAL | Planned |  | 1.00 | 112.0 | 0.000788 | 0.0000070 | No
19/02/2024 | 09:06 | EL06H11 | URBAN | Planned |  | 1.00 | 4,458.0 | 0.006873 | 0.0000015 | No
19/02/2024 | 09:20 | SA18 | URBAN | Asset failure | LV | 77.00 | 145.0 | 0.017214 | 0.0001187 | No
19/02/2024 | 09:29 | HH341F | URBAN | Planned |  | 123.00 | 213.5 | 0.040491 | 0.0001896 | No
19/02/2024 | 09:55 | AP226C | URBAN | Planned |  | 434.00 | 9.0 | 0.006022 | 0.0006691 | No
19/02/2024 | 10:25 | AP424F | URBAN | Planned |  | 73.00 | 8.0 | 0.000900 | 0.0001125 | No
19/02/2024 | 10:50 | ME427D | URBAN | Overloads |  | 6.00 | 193.0 | 0.001785 | 0.0000093 | No
19/02/2024 | 12:26 | ME200G | URBAN | Third Party | Other | 1.00 | 603.0 | 0.000930 | 0.0000015 | No
19/02/2024 | 12:29 | NL760B | URBAN | Unknown | Unknown | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
19/02/2024 | 12:32 | CM12 | LONG RURAL | Planned |  | 7.00 | 242.0 | 0.012157 | 0.0000502 | No
19/02/2024 | 12:47 | AP149F | URBAN | Asset failure | LV | 104.00 | 266.0 | 0.042651 | 0.0001603 | No
19/02/2024 | 12:49 | MG48 | LONG RURAL | Planned |  | 1.00 | 50.0 | 0.000359 | 0.0000072 | No
19/02/2024 | 12:59 | AP424F | URBAN | Overloads |  | 43.00 | 202.0 | 0.013392 | 0.0000663 | No
19/02/2024 | 13:08 | NL111Q | URBAN | Asset failure | LV | 110.00 | 316.0 | 0.053591 | 0.0001696 | No
19/02/2024 | 14:12 | CBD103C | URBAN | Asset failure | LV | 1.00 | 688.0 | 0.001061 | 0.0000015 | No
19/02/2024 | 14:13 | CBD103C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 137.00 | 86.0 | 0.018165 | 0.0002112 | No
19/02/2024 | 14:14 | CBD103C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 7.00 | 309.0 | 0.003335 | 0.0000108 | No
19/02/2024 | 14:22 | CBD103G | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 22.00 | 290.0 | 0.009836 | 0.0000339 | No
19/02/2024 | 14:37 | EL18 | URBAN | Overloads |  | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
19/02/2024 | 15:04 | AP355F | URBAN | Third Party | Unauthorised access | 2.00 | 84.0 | 0.000259 | 0.0000031 | No
19/02/2024 | 15:17 | HH428D | URBAN | Asset failure | LV | 2.00 | 390.0 | 0.001203 | 0.0000031 | No
19/02/2024 | 16:41 | HH130F | URBAN | Animal | Animal impact | 1.00 | 35.0 | 0.000054 | 0.0000015 | No
19/02/2024 | 16:46 | HH341A | URBAN | Asset failure | LV | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
19/02/2024 | 16:48 | ME200G | URBAN | Asset failure | LV | 3.00 | 317.0 | 0.001466 | 0.0000046 | No
19/02/2024 | 17:02 | MG48 | LONG RURAL | Asset failure | LV | 1.00 | 259.0 | 0.001859 | 0.0000072 | No
19/02/2024 | 17:25 | AP365A | URBAN | Third Party | Vehicle impact | 291.00 | 271.5 | 0.121791 | 0.0004487 | No
19/02/2024 | 18:48 | BM55 | SHORT RURAL | Asset failure | LV | 1.00 | 192.0 | 0.001351 | 0.0000070 | No
19/02/2024 | 19:30 | CM35 | LONG RURAL | Animal | Animal impact | 650.00 | 175.0 | 0.816307 | 0.0046646 | No
19/02/2024 | 20:08 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
19/02/2024 | 20:20 | MV63 | SHORT RURAL | Asset failure | LV | 5.00 | 600.0 | 0.021106 | 0.0000352 | No
19/02/2024 | 22:41 | ME347B | URBAN | Asset failure | LV | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
19/02/2024 | 23:36 | SA18 | URBAN | Asset failure | LV | 35.00 | 16.0 | 0.000863 | 0.0000540 | No
20/02/2024 | 01:12 | SA14 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 654.00 | 132.9 | 0.133981 | 0.0010083 | No
20/02/2024 | 01:54 | SM411C | URBAN | Unknown | Unknown | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
20/02/2024 | 01:56 | SM411C | URBAN | Unknown | Unknown | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
20/02/2024 | 03:02 | SA14 | URBAN | Unknown | Unknown | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
20/02/2024 | 05:46 | SD34102 | LONG RURAL | Unknown | Unknown | 51.33 | 164.0 | 0.060415 | 0.0003684 | No
20/02/2024 | 07:37 | EL17 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 12.33 | 148.0 | 0.002814 | 0.0000190 | No
20/02/2024 | 08:09 | SG02 | SHORT RURAL | Asset failure | LV | 1.00 | 80.0 | 0.000563 | 0.0000070 | No
20/02/2024 | 08:28 | NU05 | SHORT RURAL | Planned |  | 39.00 | 434.6 | 0.119237 | 0.0002744 | No
20/02/2024 | 08:28 | CN32 | LONG RURAL | Planned |  | 1.00 | 271.0 | 0.001945 | 0.0000072 | No
20/02/2024 | 08:30 | CBD103C | URBAN | Third Party | Vehicle impact | 3.00 | 248.3 | 0.001149 | 0.0000046 | No
20/02/2024 | 08:39 | NU05 | SHORT RURAL | Planned |  | 1.00 | 155.0 | 0.001091 | 0.0000070 | No
20/02/2024 | 08:51 | KI41 | LONG RURAL | Planned |  | 15.00 | 305.0 | 0.032832 | 0.0001076 | No
20/02/2024 | 08:54 | WK31 | SHORT RURAL | Animal | Animal impact | 544.00 | 46.9 | 0.179504 | 0.0038273 | No
20/02/2024 | 09:20 | CM18 | LONG RURAL | Planned |  | 48.00 | 435.3 | 0.149957 | 0.0003445 | No
20/02/2024 | 09:46 | SA744C | URBAN | Third Party | Other | 15.00 | 156.0 | 0.003608 | 0.0000231 | No
20/02/2024 | 09:57 | VH11 | URBAN | Planned |  | 138.00 | 277.4 | 0.059023 | 0.0002128 | No
20/02/2024 | 10:27 | HH177D | URBAN | Asset failure | LV | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
20/02/2024 | 11:03 | CL20 | LONG RURAL | Planned |  | 1.00 | 248.0 | 0.001780 | 0.0000072 | No
20/02/2024 | 11:07 | MG06 | SHORT RURAL | Weather |  | 33.67 | 41.0 | 0.009711 | 0.0002369 | No
20/02/2024 | 11:17 | MV11 | SHORT RURAL | Planned |  | 1.00 | 104.0 | 0.000732 | 0.0000070 | No
20/02/2024 | 11:50 | ST12 | SHORT RURAL | Unknown | Unknown | 2.00 | 133.0 | 0.001871 | 0.0000141 | No
20/02/2024 | 12:47 | WHY17 | SHORT RURAL | Asset failure | LV | 8.00 | 366.0 | 0.020600 | 0.0000563 | No
20/02/2024 | 12:49 | HH177E | URBAN | Overloads |  | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
20/02/2024 | 12:52 | NL210B | URBAN | Asset failure | LV | 1.00 | 685.0 | 0.001056 | 0.0000015 | No
20/02/2024 | 13:21 | AP424F | URBAN | Overloads |  | 43.00 | 555.0 | 0.036794 | 0.0000663 | No
20/02/2024 | 13:25 | HH386D | URBAN | Overloads |  | 1.00 | 214.0 | 0.000330 | 0.0000015 | No
20/02/2024 | 13:50 | HH145E | URBAN | Asset failure | LV | 17.00 | 76.0 | 0.001992 | 0.0000262 | No
20/02/2024 | 14:16 | BM56 | SHORT RURAL | Asset failure | LV | 12.00 | 47.0 | 0.003968 | 0.0000844 | No
20/02/2024 | 14:35 | SD33100 | LONG RURAL | Unknown | Unknown | 5.00 | 155.0 | 0.005562 | 0.0000359 | No
20/02/2024 | 14:45 | SD40700 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 248.0 | 0.001780 | 0.0000072 | No
20/02/2024 | 14:49 | AP424C | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
20/02/2024 | 14:58 | LX25 | SHORT RURAL | Asset failure | LV | 37.00 | 49.0 | 0.012748 | 0.0002603 | No
20/02/2024 | 15:15 | HH130F | URBAN | Vegetation | Grow-in - NSP responsibility | 101.00 | 223.0 | 0.034725 | 0.0001557 | No
20/02/2024 | 16:07 | EL10 | URBAN | Overloads |  | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
20/02/2024 | 16:11 | SA18 | URBAN | Overloads |  | 2.00 | 584.0 | 0.001801 | 0.0000031 | No
20/02/2024 | 16:33 | SM374B | URBAN | Asset failure | LV | 1.00 | 355.0 | 0.000547 | 0.0000015 | No
20/02/2024 | 16:55 | SM374A | URBAN | Asset failure | LV | 1.00 | 368.0 | 0.000567 | 0.0000015 | No
20/02/2024 | 16:57 | KA08 | LONG RURAL | Overloads |  | 2.00 | 1,330.0 | 0.019089 | 0.0000144 | No
20/02/2024 | 16:58 | MG32 | LONG RURAL | Planned |  | 28.00 | 92.0 | 0.018486 | 0.0002009 | No
20/02/2024 | 17:37 | AP424F | URBAN | Overloads |  | 56.00 | 529.0 | 0.045673 | 0.0000863 | No
20/02/2024 | 18:10 | SM350E | URBAN | Animal | Animal impact | 590.00 | 45.0 | 0.040934 | 0.0009096 | No
20/02/2024 | 18:14 | AP125D | URBAN | Asset failure | LV | 28.00 | 275.0 | 0.011872 | 0.0000432 | No
20/02/2024 | 18:19 | SM179B | URBAN | Animal | Animal impact | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
20/02/2024 | 18:19 | SM350E | URBAN | Animal | Animal impact | 1.00 | 64.0 | 0.000099 | 0.0000015 | No
20/02/2024 | 18:54 | VH16 | SHORT RURAL | Animal | Animal impact | 6.00 | 134.0 | 0.005657 | 0.0000422 | No
20/02/2024 | 19:21 | SM350E | URBAN | Unknown | Unknown | 1.00 | 453.0 | 0.000698 | 0.0000015 | No
20/02/2024 | 20:26 | CM21 | LONG RURAL | Asset failure | HV | 11.00 | 408.0 | 0.032207 | 0.0000789 | No
20/02/2024 | 21:24 | NU06 | LONG RURAL | Unknown | Unknown | 2.00 | 178.0 | 0.002555 | 0.0000144 | No
21/02/2024 | 02:44 | SM172A | URBAN | Third Party | Vehicle impact | 131.00 | 420.5 | 0.084921 | 0.0002020 | No
21/02/2024 | 02:45 | HH341G | URBAN | Asset failure | LV | 24.67 | 353.0 | 0.013425 | 0.0000380 | No
21/02/2024 | 03:09 | MG51 | LONG RURAL | Unknown | Unknown | 9.00 | 364.0 | 0.023510 | 0.0000646 | No
21/02/2024 | 03:45 | YK19 | LONG RURAL | Asset failure | LV | 1.00 | 441.0 | 0.003165 | 0.0000072 | No
21/02/2024 | 06:56 | MTB52 | LONG RURAL | Asset failure | LV | 1.00 | 103.0 | 0.000739 | 0.0000072 | No
21/02/2024 | 07:29 | CV24 | LONG RURAL | Unknown | Unknown | 2.00 | 598.0 | 0.008583 | 0.0000144 | No
21/02/2024 | 07:38 | MG51 | LONG RURAL | Unknown | Unknown | 1.00 | 97.0 | 0.000696 | 0.0000072 | No
21/02/2024 | 07:43 | MG12 | LONG RURAL | Animal | Animal impact | 2.00 | 134.0 | 0.001923 | 0.0000144 | No
21/02/2024 | 08:38 | CN32 | LONG RURAL | Planned |  | 2.00 | 377.0 | 0.005411 | 0.0000144 | No
21/02/2024 | 08:49 | HH145E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 66.00 | 156.0 | 0.015874 | 0.0001018 | No
21/02/2024 | 08:57 | MG17 | LONG RURAL | Unknown | Unknown | 6.00 | 10.0 | 0.000431 | 0.0000431 | No
21/02/2024 | 09:07 | BM55 | SHORT RURAL | Overloads |  | 2.00 | 231.0 | 0.003250 | 0.0000141 | No
21/02/2024 | 09:22 | EL15 | URBAN | Planned |  | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
21/02/2024 | 09:28 | MG19 | LONG RURAL | Planned |  | 181.00 | 422.2 | 0.548451 | 0.0012989 | No
21/02/2024 | 09:31 | MV41 | SHORT RURAL | Animal | Animal impact | 10.67 | 204.0 | 0.015309 | 0.0000750 | No
21/02/2024 | 09:32 | PL24 | LONG RURAL | Planned |  | 31.00 | 247.0 | 0.054949 | 0.0002225 | No
21/02/2024 | 09:34 | KI32 | SHORT RURAL | Overloads |  | 10.00 | 300.0 | 0.021106 | 0.0000704 | No
21/02/2024 | 09:39 | WK72 | SHORT RURAL | Planned |  | 20.00 | 208.2 | 0.029296 | 0.0001407 | No
21/02/2024 | 09:42 | ME131C | URBAN | Asset failure | LV | 1.00 | 838.0 | 0.001292 | 0.0000015 | No
21/02/2024 | 09:43 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 1,782.0 | 0.012537 | 0.0000070 | No
21/02/2024 | 09:43 | KI11 | LONG RURAL | Planned |  | 179.00 | 118.0 | 0.151578 | 0.0012846 | No
21/02/2024 | 10:06 | CM12 | LONG RURAL | Planned |  | 67.00 | 183.0 | 0.087989 | 0.0004808 | No
21/02/2024 | 10:23 | PP16 | SHORT RURAL | Planned |  | 30.00 | 84.0 | 0.017729 | 0.0002111 | No
21/02/2024 | 10:34 | ME427E | URBAN | Asset failure | LV | 90.00 | 80.8 | 0.011212 | 0.0001388 | No
21/02/2024 | 10:59 | MTB10 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.00 | 184.0 | 0.007943 | 0.0000432 | No
21/02/2024 | 11:02 | HH403A | URBAN | Asset failure | LV | 78.00 | 150.0 | 0.018043 | 0.0001203 | No
21/02/2024 | 11:51 | SM126C | URBAN | Asset failure | LV | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
21/02/2024 | 11:59 | HH145A | URBAN | Asset failure | HV | 89.00 | 123.8 | 0.016993 | 0.0001372 | No
21/02/2024 | 12:03 | SA744D | URBAN | Unknown | Unknown | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
21/02/2024 | 12:25 | HH145A | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
21/02/2024 | 12:49 | SM402D | URBAN | Asset failure | LV | 1.00 | 274.0 | 0.000422 | 0.0000015 | No
21/02/2024 | 13:11 | HH121D | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
21/02/2024 | 13:21 | LX25 | SHORT RURAL | Asset failure | LV | 37.00 | 51.0 | 0.013276 | 0.0002603 | No
21/02/2024 | 15:23 | MTB52 | LONG RURAL | Third Party | Other | 989.00 | 51.8 | 0.367952 | 0.0070974 | No
21/02/2024 | 15:23 | MTB52 | SHORT RURAL | Third Party | Other | 1.00 | 85.0 | 0.000598 | 0.0000070 | No
21/02/2024 | 15:46 | BM33 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 17.00 | 83.0 | 0.009927 | 0.0001196 | No
21/02/2024 | 16:06 | HH386D | URBAN | Asset failure | LV | 15.00 | 172.0 | 0.003978 | 0.0000231 | No
21/02/2024 | 16:39 | MB20 | SHORT RURAL | Asset failure | LV | 1.00 | 960.0 | 0.006754 | 0.0000070 | No
21/02/2024 | 17:55 | G20 | LONG RURAL | Asset failure | HV | 90.00 | 101.0 | 0.065233 | 0.0006459 | No
21/02/2024 | 18:04 | HH121C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 10.67 | 101.0 | 0.001661 | 0.0000164 | No
21/02/2024 | 18:07 | GA23 | SHORT RURAL | Overloads |  | 20.00 | 64.0 | 0.009005 | 0.0001407 | No
21/02/2024 | 18:09 | MB32 | LONG RURAL | Asset failure | HV | 698.00 | 241.1 | 1.207561 | 0.0050091 | No
21/02/2024 | 18:23 | SM179A | URBAN | Asset failure | LV | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
21/02/2024 | 19:04 | AP149F | URBAN | Asset failure | LV | 43.33 | 140.0 | 0.009353 | 0.0000668 | No
21/02/2024 | 19:10 | HH409C | URBAN | Asset failure | LV | 15.33 | 169.0 | 0.003995 | 0.0000236 | No
21/02/2024 | 20:50 | MTB52 | LONG RURAL | Asset failure | LV | 1.00 | 282.0 | 0.002024 | 0.0000072 | No
21/02/2024 | 21:01 | HH386A | URBAN | Asset failure | LV | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
21/02/2024 | 22:09 | GA05 | SHORT RURAL | Animal | Animal impact | 473.00 | 176.2 | 0.586204 | 0.0033278 | No
21/02/2024 | 22:11 | CBD366M | CBD | Planned |  | 1.00 | 1.0 | 0.000144 | 0.0001445 | No
21/02/2024 | 22:36 | SM126B | URBAN | Planned |  | 11.00 | 198.0 | 0.003358 | 0.0000170 | No
21/02/2024 | 22:57 | BM56 | SHORT RURAL | Unknown | Unknown | 785.00 | 164.0 | 0.905749 | 0.0055229 | No
21/02/2024 | 23:00 | ST44 | LONG RURAL | Asset failure | HV | 2.00 | 828.0 | 0.011884 | 0.0000144 | No
21/02/2024 | 23:03 | YK19 | LONG RURAL | Weather |  | 2.00 | 348.0 | 0.004995 | 0.0000144 | No
21/02/2024 | 23:28 | CBD353P | CBD | Planned |  | 13.00 | 2.0 | 0.003756 | 0.0018782 | No
21/02/2024 | 23:33 | HH432B | URBAN | Asset failure | LV | 82.00 | 152.0 | 0.019216 | 0.0001264 | No
22/02/2024 | 00:17 | HH386F | URBAN | Animal | Animal impact | 556.00 | 68.7 | 0.058932 | 0.0008572 | No
22/02/2024 | 00:41 | SM411C | URBAN | Animal | Animal impact | 323.00 | 87.0 | 0.043325 | 0.0004980 | No
22/02/2024 | 00:58 | ME200F | URBAN | Animal | Animal impact | 938.00 | 116.5 | 0.168475 | 0.0014462 | No
22/02/2024 | 02:09 | YK19 | LONG RURAL | Weather |  | 2.00 | 72.0 | 0.001033 | 0.0000144 | No
22/02/2024 | 02:44 | HH121A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 54.00 | 585.0 | 0.048704 | 0.0000833 | No
22/02/2024 | 03:11 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 93.00 | 408.1 | 0.267039 | 0.0006543 | No
22/02/2024 | 03:23 | CBD353P | CBD | Planned |  | 13.00 | 1.0 | 0.001878 | 0.0018782 | No
22/02/2024 | 03:29 | HH121A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 15.67 | 557.0 | 0.013454 | 0.0000242 | No
22/02/2024 | 04:05 | CBD366M | CBD | Planned |  | 1.00 | 1.0 | 0.000144 | 0.0001445 | No
22/02/2024 | 06:14 | ME200F | URBAN | Asset failure | LV | 15.33 | 375.0 | 0.008865 | 0.0000236 | No
22/02/2024 | 07:17 | GA53 | SHORT RURAL | Asset failure | LV | 1.00 | 251.0 | 0.001766 | 0.0000070 | No
22/02/2024 | 07:56 | M73 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 72.00 | 724.4 | 0.374296 | 0.0005167 | No
22/02/2024 | 08:13 | SA18 | URBAN | Planned |  | 116.00 | 195.7 | 0.034998 | 0.0001788 | No
22/02/2024 | 08:21 | YK19 | LONG RURAL | Unknown | Unknown | 7.00 | 223.0 | 0.011202 | 0.0000502 | No
22/02/2024 | 08:45 | AP149C | URBAN | Planned |  | 39.00 | 301.0 | 0.018099 | 0.0000601 | No
22/02/2024 | 08:55 | CN32 | LONG RURAL | Planned |  | 2.00 | 430.0 | 0.006172 | 0.0000144 | No
22/02/2024 | 09:10 | HH341J | URBAN | Planned |  | 169.00 | 313.8 | 0.081765 | 0.0002606 | No
22/02/2024 | 09:10 | CM18 | LONG RURAL | Planned |  | 48.00 | 400.4 | 0.137915 | 0.0003445 | No
22/02/2024 | 09:13 | KI58 | SHORT RURAL | Planned |  | 2.00 | 232.0 | 0.003264 | 0.0000141 | No
22/02/2024 | 09:38 | CD19 | LONG RURAL | Planned |  | 1.00 | 86.0 | 0.000617 | 0.0000072 | No
22/02/2024 | 10:00 | HH341G | URBAN | Asset failure | LV | 60.00 | 74.0 | 0.006845 | 0.0000925 | No
22/02/2024 | 10:46 | CV26 | LONG RURAL | Unknown | Unknown | 70.00 | 398.2 | 0.200033 | 0.0005023 | No
22/02/2024 | 11:23 | G18 | LONG RURAL | Asset failure | HV | 22.00 | 287.0 | 0.045311 | 0.0001579 | No
22/02/2024 | 11:58 | MI01 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 51.00 | 114.2 | 0.041802 | 0.0003660 | No
22/02/2024 | 12:04 | SA19 | URBAN | Asset failure | LV | 57.00 | 126.0 | 0.011073 | 0.0000879 | No
22/02/2024 | 12:29 | BT08 | LONG RURAL | Planned |  | 16.00 | 85.0 | 0.009760 | 0.0001148 | No
22/02/2024 | 13:01 | MV62 | SHORT RURAL | Asset failure | LV | 1.00 | 130.0 | 0.000915 | 0.0000070 | No
22/02/2024 | 13:09 | MV62 | SHORT RURAL | Asset failure | LV | 3.33 | 70.0 | 0.001642 | 0.0000235 | No
22/02/2024 | 13:36 | AP214D | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
22/02/2024 | 14:21 | PP16 | SHORT RURAL | Planned |  | 4.00 | 41.0 | 0.001154 | 0.0000281 | No
22/02/2024 | 14:42 | MG03 | SHORT RURAL | Third Party | Vehicle impact | 364.00 | 88.0 | 0.225361 | 0.0025609 | No
22/02/2024 | 14:45 | SM350E | URBAN | Unknown | Unknown | 32.00 | 25.3 | 0.001250 | 0.0000493 | No
22/02/2024 | 14:52 | ST22 | SHORT RURAL | Asset failure | HV | 94.00 | 65.5 | 0.043289 | 0.0006613 | No
22/02/2024 | 14:53 | NL234B | URBAN | Asset failure | LV | 18.00 | 174.0 | 0.004829 | 0.0000278 | No
22/02/2024 | 14:56 | MTB33 | SHORT RURAL | Asset failure | LV | 1.00 | 98.0 | 0.000689 | 0.0000070 | No
22/02/2024 | 15:10 | M21 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 367.00 | 88.0 | 0.231767 | 0.0026337 | No
22/02/2024 | 15:23 | AP226E | URBAN | Overloads |  | 1.00 | 504.0 | 0.000777 | 0.0000015 | No
22/02/2024 | 15:52 | VH10 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 10.00 | 35.0 | 0.002462 | 0.0000704 | No
22/02/2024 | 16:15 | AP425D | URBAN | Unknown | Unknown | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
22/02/2024 | 16:23 | GU13 | LONG RURAL | Asset failure | LV | 14.00 | 312.4 | 0.031382 | 0.0001005 | No
22/02/2024 | 16:29 | HH409E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 35.00 | 38.0 | 0.002051 | 0.0000540 | No
22/02/2024 | 17:14 | SM126B | URBAN | Asset failure | LV | 4.00 | 113.0 | 0.000697 | 0.0000062 | No
22/02/2024 | 17:20 | M61 | LONG RURAL | Asset failure | LV | 1.00 | 1,360.0 | 0.009760 | 0.0000072 | No
22/02/2024 | 17:22 | WK31 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 544.00 | 252.5 | 0.966458 | 0.0038273 | No
22/02/2024 | 17:32 | HH409E | URBAN | Asset failure | LV | 19.33 | 186.0 | 0.005544 | 0.0000298 | No
22/02/2024 | 18:11 | SM349A | URBAN | Asset failure | LV | 1.00 | 452.0 | 0.000697 | 0.0000015 | No
22/02/2024 | 19:33 | ME347A | URBAN | Asset failure | LV | 8.00 | 131.5 | 0.001622 | 0.0000123 | No
22/02/2024 | 20:41 | AP355F | URBAN | Asset failure | LV | 5.00 | 360.0 | 0.002775 | 0.0000077 | No
22/02/2024 | 21:11 | GA800A | SHORT RURAL | Asset failure | HV | 262.00 | 208.2 | 0.383814 | 0.0018433 | No
22/02/2024 | 21:30 | SG02 | SHORT RURAL | Other |  | 1.00 | 333.0 | 0.002343 | 0.0000070 | No
22/02/2024 | 23:30 | ME116A | URBAN | Asset failure | LV | 27.00 | 75.0 | 0.003124 | 0.0000416 | No
22/02/2024 | 23:55 | HH121H | URBAN | Third Party | Other | 69.00 | 381.0 | 0.040531 | 0.0001064 | No
23/02/2024 | 01:07 | HH341K | URBAN | Animal | Animal impact | 382.00 | 74.0 | 0.043582 | 0.0005889 | No
23/02/2024 | 02:26 | GA08 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 31.00 | 590.0 | 0.131255 | 0.0002225 | No
23/02/2024 | 04:41 | SM350E | URBAN | Animal | Animal impact | 386.00 | 38.0 | 0.022614 | 0.0005951 | No
23/02/2024 | 06:08 | SM349D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
23/02/2024 | 08:20 | HH341J | URBAN | Planned |  | 128.00 | 88.3 | 0.017422 | 0.0001973 | No
23/02/2024 | 08:49 | HH341J | URBAN | Planned |  | 1.00 | 68.0 | 0.000105 | 0.0000015 | No
23/02/2024 | 08:49 | AP425C | URBAN | Planned |  | 104.00 | 278.0 | 0.044575 | 0.0001603 | No
23/02/2024 | 08:56 | AP424F | URBAN | Planned |  | 73.00 | 88.0 | 0.009904 | 0.0001125 | No
23/02/2024 | 09:01 | CD17 | LONG RURAL | Planned |  | 3.00 | 93.0 | 0.002002 | 0.0000215 | No
23/02/2024 | 09:01 | CM28 | LONG RURAL | Planned |  | 54.00 | 369.7 | 0.143275 | 0.0003875 | No
23/02/2024 | 09:02 | HH121B | URBAN | Planned |  | 152.00 | 245.4 | 0.057501 | 0.0002343 | No
23/02/2024 | 09:12 | SG12 | SHORT RURAL | Planned |  | 3.00 | 289.0 | 0.006100 | 0.0000211 | No
23/02/2024 | 09:36 | KI51 | LONG RURAL | Planned |  | 17.00 | 204.0 | 0.024888 | 0.0001220 | No
23/02/2024 | 09:37 | SM411C | URBAN | Planned |  | 70.00 | 137.9 | 0.014887 | 0.0001079 | No
23/02/2024 | 09:58 | LX48 | SHORT RURAL | Planned |  | 1.00 | 290.0 | 0.002040 | 0.0000070 | No
23/02/2024 | 10:21 | MV33 | SHORT RURAL | Planned |  | 3.00 | 169.0 | 0.003567 | 0.0000211 | No
23/02/2024 | 10:42 | SD58200 | LONG RURAL | Animal | Animal impact | 507.00 | 24.6 | 0.089539 | 0.0036384 | No
23/02/2024 | 10:47 | AP226C | URBAN | Planned |  | 434.00 | 10.0 | 0.006691 | 0.0006691 | No
23/02/2024 | 11:09 | CM16 | LONG RURAL | Planned |  | 21.00 | 65.5 | 0.009867 | 0.0001507 | No
23/02/2024 | 11:20 | CD17 | LONG RURAL | Planned |  | 1.00 | 82.0 | 0.000588 | 0.0000072 | No
23/02/2024 | 12:39 | MG10 | LONG RURAL | Asset failure | LV | 1.00 | 280.0 | 0.002009 | 0.0000072 | No
23/02/2024 | 12:40 | SM349F | URBAN | Asset failure | LV | 11.00 | 353.0 | 0.005987 | 0.0000170 | No
23/02/2024 | 13:16 | MI23 | LONG RURAL | Other |  | 23.00 | 78.0 | 0.012874 | 0.0001651 | No
23/02/2024 | 14:03 | GA800A | SHORT RURAL | Asset failure | LV | 1.00 | 397.0 | 0.002793 | 0.0000070 | No
23/02/2024 | 14:29 | LX53 | SHORT RURAL | Unknown | Unknown | 50.00 | 18.0 | 0.006332 | 0.0003518 | No
23/02/2024 | 14:37 | HH130C | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
23/02/2024 | 16:23 | AP149C | URBAN | Asset failure | LV | 1.00 | 34.0 | 0.000052 | 0.0000015 | No
23/02/2024 | 16:37 | MG30 | LONG RURAL | Animal | Animal impact | 65.00 | 129.0 | 0.060174 | 0.0004665 | No
23/02/2024 | 17:33 | ME200F | URBAN | Asset failure | LV | 10.00 | 128.0 | 0.001973 | 0.0000154 | No
23/02/2024 | 19:49 | PL803A | URBAN | Asset failure | LV | 15.00 | 54.5 | 0.001261 | 0.0000231 | No
23/02/2024 | 21:18 | SM374B | URBAN | Animal | Animal impact | 897.00 | 81.0 | 0.112019 | 0.0013830 | No
23/02/2024 | 23:07 | HH145C | URBAN | Animal | Animal impact | 693.00 | 68.0 | 0.072654 | 0.0010684 | No
24/02/2024 | 03:07 | HH341J | URBAN | Animal | Animal impact | 449.00 | 93.0 | 0.064379 | 0.0006922 | No
24/02/2024 | 03:40 | ME231E | URBAN | Planned |  | 1,270.00 | 3.0 | 0.005874 | 0.0019580 | No
24/02/2024 | 06:03 | HH102B | URBAN | Third Party | Vehicle impact | 138.00 | 422.6 | 0.089915 | 0.0002128 | No
24/02/2024 | 09:10 | PL01 | URBAN | Asset failure | LV | 1.00 | 432.0 | 0.000666 | 0.0000015 | No
24/02/2024 | 13:38 | PL07 | URBAN | Asset failure | LV | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
24/02/2024 | 14:23 | MG10 | LONG RURAL | Asset failure | HV | 5.00 | 17.0 | 0.000610 | 0.0000359 | No
24/02/2024 | 15:38 | NL210C | URBAN | Overloads |  | 1.00 | 308.0 | 0.000475 | 0.0000015 | No
24/02/2024 | 17:19 | SM411F | URBAN | Asset failure | LV | 1.00 | 162.0 | 0.000250 | 0.0000015 | No
24/02/2024 | 17:48 | SA16 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 45.0 | 0.000069 | 0.0000015 | No
24/02/2024 | 17:56 | SG14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 6.00 | 1,708.0 | 0.072100 | 0.0000422 | No
24/02/2024 | 18:10 | PP03 | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
24/02/2024 | 20:30 | HH130B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 12.00 | 55.0 | 0.001018 | 0.0000185 | No
24/02/2024 | 20:43 | GA33 | SHORT RURAL | Animal | Animal impact | 2.00 | 134.0 | 0.001886 | 0.0000141 | No
24/02/2024 | 21:19 | SM350B | URBAN | Animal | Animal impact | 1,756.00 | 29.0 | 0.078512 | 0.0027073 | No
25/02/2024 | 01:17 | HH341G | URBAN | Animal | Animal impact | 47.33 | 131.0 | 0.009560 | 0.0000730 | No
25/02/2024 | 02:36 | MG19 | LONG RURAL | Unknown | Unknown | 4.00 | 147.0 | 0.004220 | 0.0000287 | No
25/02/2024 | 04:48 | HH522A | URBAN | Asset failure | HV | 681.00 | 107.8 | 0.113217 | 0.0010499 | No
25/02/2024 | 06:01 | HH121B | URBAN | Planned |  | 31.00 | 118.0 | 0.005640 | 0.0000478 | No
25/02/2024 | 06:22 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 1,001.0 | 0.007043 | 0.0000070 | No
25/02/2024 | 07:07 | WHY07 | URBAN | Unknown | Unknown | 1.00 | 298.0 | 0.000459 | 0.0000015 | No
25/02/2024 | 07:12 | WHY14 | URBAN | Unknown | Unknown | 2.00 | 289.0 | 0.000891 | 0.0000031 | No
25/02/2024 | 07:41 | NA04 | LONG RURAL | Asset failure | HV | 262.00 | 140.0 | 0.263228 | 0.0018802 | No
25/02/2024 | 08:00 | MV31 | SHORT RURAL | Unknown | Unknown | 6.00 | 321.0 | 0.013550 | 0.0000422 | No
25/02/2024 | 08:22 | YK12 | LONG RURAL | Weather |  | 79.00 | 185.5 | 0.105148 | 0.0005669 | No
25/02/2024 | 08:28 | AP355E | URBAN | Planned |  | 19.00 | 250.2 | 0.007329 | 0.0000293 | No
25/02/2024 | 08:28 | PA07 | LONG RURAL | Planned |  | 3.00 | 366.0 | 0.007880 | 0.0000215 | No
25/02/2024 | 08:59 | BS0340 | CBD | Planned |  | 1.00 | 1,075.0 | 0.155313 | 0.0001445 | No
25/02/2024 | 09:00 | SA14 | URBAN | Planned |  | 36.00 | 321.0 | 0.017817 | 0.0000555 | No
25/02/2024 | 09:03 | CBD103E | URBAN | Planned |  | 67.00 | 407.9 | 0.042139 | 0.0001033 | No
25/02/2024 | 09:14 | NL760B | URBAN | Planned |  | 17.00 | 313.0 | 0.008204 | 0.0000262 | No
25/02/2024 | 10:23 | WHY17 | SHORT RURAL | Planned |  | 2.00 | 159.0 | 0.002237 | 0.0000141 | No
25/02/2024 | 10:42 | MTB12 | SHORT RURAL | Third Party | Vehicle impact | 147.00 | 551.1 | 0.569952 | 0.0010342 | No
25/02/2024 | 11:36 | AP425D | URBAN | Asset failure | LV | 1.00 | 252.0 | 0.000389 | 0.0000015 | No
25/02/2024 | 12:21 | SG13 | SHORT RURAL | Unknown | Unknown | 198.67 | 11.0 | 0.015337 | 0.0013977 | No
25/02/2024 | 12:27 | CM12 | LONG RURAL | Asset failure | HV | 48.00 | 80.0 | 0.027557 | 0.0003445 | No
25/02/2024 | 14:47 | SM350F | URBAN | Asset failure | LV | 1.00 | 164.0 | 0.000253 | 0.0000015 | No
25/02/2024 | 15:38 | SM349F | URBAN | Asset failure | LV | 1.00 | 401.0 | 0.000618 | 0.0000015 | No
25/02/2024 | 15:41 | HH341E | URBAN | Animal | Animal impact | 401.00 | 113.8 | 0.070327 | 0.0006182 | No
25/02/2024 | 17:18 | PP09 | LONG RURAL | Asset failure | HV | 8.00 | 52.0 | 0.002985 | 0.0000574 | No
25/02/2024 | 17:21 | ME427D | URBAN | Asset failure | LV | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
25/02/2024 | 18:06 | SD35400 | SHORT RURAL | Weather |  | 1.00 | 79.0 | 0.000556 | 0.0000070 | No
25/02/2024 | 18:23 | NL210B | URBAN | Asset failure | LV | 67.00 | 157.0 | 0.016218 | 0.0001033 | No
25/02/2024 | 19:10 | VH21 | SHORT RURAL | Unknown | Unknown | 1.00 | 2,786.0 | 0.019601 | 0.0000070 | No
25/02/2024 | 19:27 | SM410D | URBAN | Overloads |  | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
25/02/2024 | 20:03 | SA31 | URBAN | Asset failure | LV | 1.00 | 191.0 | 0.000294 | 0.0000015 | No
25/02/2024 | 20:45 | SM350H | URBAN | Unknown | Unknown | 1.00 | 460.0 | 0.000709 | 0.0000015 | No
25/02/2024 | 20:50 | SM216B | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 216.0 | 0.000333 | 0.0000015 | No
25/02/2024 | 20:52 | ME347B | URBAN | Asset failure | LV | 3.00 | 62.0 | 0.000287 | 0.0000046 | No
25/02/2024 | 21:13 | PA02 | URBAN | Weather |  | 732.00 | 125.3 | 0.141370 | 0.0011286 | No
25/02/2024 | 22:04 | ME131E | URBAN | Animal | Animal impact | 435.33 | 33.0 | 0.022149 | 0.0006712 | No
25/02/2024 | 23:07 | MI16 | LONG RURAL | Weather |  | 308.00 | 165.9 | 0.366624 | 0.0022103 | No
25/02/2024 | 23:47 | ME231C | URBAN | Asset failure | LV | 1.00 | 33.0 | 0.000051 | 0.0000015 | No
26/02/2024 | 01:29 | SM350A | URBAN | Animal | Animal impact | 489.00 | 109.0 | 0.082177 | 0.0007539 | No
26/02/2024 | 02:04 | HH429C | URBAN | Animal | Animal impact | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
26/02/2024 | 02:22 | HH429C | URBAN | Animal | Animal impact | 28.00 | 80.0 | 0.003454 | 0.0000432 | No
26/02/2024 | 03:02 | HH386F | URBAN | Animal | Animal impact | 520.00 | 67.0 | 0.053715 | 0.0008017 | No
26/02/2024 | 03:30 | HH341E | URBAN | Animal | Animal impact | 308.00 | 56.0 | 0.026592 | 0.0004749 | No
26/02/2024 | 04:15 | AP214C | URBAN | Animal | Animal impact | 65.67 | 50.0 | 0.005062 | 0.0001012 | No
26/02/2024 | 06:29 | VH51 | SHORT RURAL | Weather |  | 169.00 | 185.2 | 0.220246 | 0.0011890 | No
26/02/2024 | 06:36 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
26/02/2024 | 08:51 | MI20 | LONG RURAL | Planned |  | 101.00 | 168.5 | 0.122163 | 0.0007248 | No
26/02/2024 | 08:52 | MB13 | SHORT RURAL | Overloads |  | 1.00 | 413.0 | 0.002906 | 0.0000070 | No
26/02/2024 | 08:55 | NL451A | URBAN | Planned |  | 2,044.00 | 31.9 | 0.100681 | 0.0031513 | No
26/02/2024 | 09:01 | HH107B | URBAN | Planned |  | 129.00 | 322.0 | 0.064041 | 0.0001989 | No
26/02/2024 | 09:18 | PP08 | LONG RURAL | Planned |  | 405.00 | 319.0 | 0.927103 | 0.0029064 | No
26/02/2024 | 09:24 | R21 | LONG RURAL | Planned |  | 2.00 | 181.0 | 0.002598 | 0.0000144 | No
26/02/2024 | 09:35 | MTB32 | LONG RURAL | Asset failure | HV | 10.67 | 67.0 | 0.005129 | 0.0000765 | No
26/02/2024 | 10:03 | SD33200 | LONG RURAL | Planned |  | 2.00 | 108.0 | 0.001550 | 0.0000144 | No
26/02/2024 | 10:05 | ST12 | SHORT RURAL | Unknown | Unknown | 1.00 | 164.0 | 0.001154 | 0.0000070 | No
26/02/2024 | 10:22 | SM216E | URBAN | Asset failure | LV | 37.00 | 47.8 | 0.002729 | 0.0000570 | No
26/02/2024 | 12:01 | NL544A | URBAN | Asset failure | LV | 79.00 | 96.0 | 0.011693 | 0.0001218 | No
26/02/2024 | 12:07 | ME200C | URBAN | Overloads |  | 1.00 | 283.0 | 0.000436 | 0.0000015 | No
26/02/2024 | 12:33 | KA19 | LONG RURAL | Other |  | 1.00 | 21.0 | 0.000151 | 0.0000072 | No
26/02/2024 | 12:49 | SM411E | URBAN | Asset failure | LV | 1.00 | 374.0 | 0.000577 | 0.0000015 | No
26/02/2024 | 13:28 | NA34 | LONG RURAL | Asset failure | LV | 5.00 | 213.0 | 0.007643 | 0.0000359 | No
26/02/2024 | 13:28 | NL760C | URBAN | Asset failure | LV | 6.33 | 144.0 | 0.001406 | 0.0000098 | No
26/02/2024 | 13:37 | NL451A | URBAN | Planned |  | 2,044.00 | 27.0 | 0.084957 | 0.0031513 | No
26/02/2024 | 13:59 | HH145D | URBAN | Asset failure | LV | 31.33 | 1,245.0 | 0.060144 | 0.0000483 | No
26/02/2024 | 14:09 | BT22 | LONG RURAL | Planned |  | 1.00 | 23.0 | 0.000165 | 0.0000072 | No
26/02/2024 | 14:09 | YK16 | LONG RURAL | Overloads |  | 1.00 | 359.0 | 0.002576 | 0.0000072 | No
26/02/2024 | 14:30 | MV63 | SHORT RURAL | Asset failure | HV | 191.00 | 41.0 | 0.055095 | 0.0013438 | No
26/02/2024 | 15:10 | MI20 | LONG RURAL | Asset failure | LV | 6.00 | 183.0 | 0.007880 | 0.0000431 | No
26/02/2024 | 15:22 | ST22 | SHORT RURAL | Weather |  | 58.00 | 56.0 | 0.022851 | 0.0004081 | No
26/02/2024 | 15:27 | HH145A | URBAN | Overloads |  | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
26/02/2024 | 15:44 | MT21 | LONG RURAL | Asset failure | LV | 1.00 | 178.0 | 0.001277 | 0.0000072 | No
26/02/2024 | 15:54 | SA35 | URBAN | Third Party | Unauthorised access | 1.00 | 42.0 | 0.000065 | 0.0000015 | No
26/02/2024 | 16:25 | PL29 | LONG RURAL | Animal | Animal impact | 2.00 | 24.0 | 0.000344 | 0.0000144 | No
26/02/2024 | 17:51 | PL22 | LONG RURAL | Weather |  | 42.00 | 61.0 | 0.018386 | 0.0003014 | No
26/02/2024 | 18:51 | SM402D | URBAN | Asset failure | LV | 4.00 | 211.0 | 0.001301 | 0.0000062 | No
26/02/2024 | 21:01 | AP372B | URBAN | Asset failure | LV | 11.00 | 80.3 | 0.001361 | 0.0000170 | No
26/02/2024 | 21:24 | SM172B | URBAN | Animal | Animal impact | 920.00 | 58.0 | 0.082268 | 0.0014184 | No
26/02/2024 | 23:19 | HH429C | URBAN | Animal | Animal impact | 2,803.00 | 48.0 | 0.207434 | 0.0043215 | No
26/02/2024 | 23:52 | SM216G | URBAN | Asset failure | LV | 7.00 | 14.0 | 0.000151 | 0.0000108 | No
27/02/2024 | 01:09 | LM63 | LONG RURAL | Asset failure | HV | 2.00 | 40.0 | 0.000574 | 0.0000144 | No
27/02/2024 | 01:56 | SG08 | SHORT RURAL | Animal | Animal impact | 53.67 | 217.0 | 0.081933 | 0.0003776 | No
27/02/2024 | 01:58 | HH177B | URBAN | Asset failure | LV | 84.00 | 220.0 | 0.028492 | 0.0001295 | No
27/02/2024 | 02:02 | ME231D | URBAN | Animal | Animal impact | 52.67 | 106.0 | 0.008607 | 0.0000812 | No
27/02/2024 | 04:49 | SM126C | URBAN | Weather |  | 73.00 | 456.4 | 0.051365 | 0.0001125 | No
27/02/2024 | 05:33 | SM126C | URBAN | Weather |  | 1.00 | 566.0 | 0.000873 | 0.0000015 | No
27/02/2024 | 06:37 | MTB52 | LONG RURAL | Unknown | Unknown | 2.00 | 116.0 | 0.001665 | 0.0000144 | No
27/02/2024 | 07:43 | VH15 | SHORT RURAL | Third Party | Vehicle impact | 12.33 | 106.0 | 0.009198 | 0.0000868 | No
27/02/2024 | 08:49 | SD32400 | LONG RURAL | Network business | Switching and protection error | 21.00 | 32.0 | 0.004822 | 0.0001507 | No
27/02/2024 | 08:56 | AP529C | URBAN | Asset failure | LV | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
27/02/2024 | 09:00 | HH341E | URBAN | Planned |  | 262.00 | 70.3 | 0.028399 | 0.0004039 | No
27/02/2024 | 09:01 | HH102B | URBAN | Planned |  | 151.00 | 229.5 | 0.053425 | 0.0002328 | No
27/02/2024 | 09:03 | GU43 | LONG RURAL | Unknown | Unknown | 124.00 | 70.0 | 0.062291 | 0.0008899 | No
27/02/2024 | 09:14 | AP214C | URBAN | Asset failure | LV | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
27/02/2024 | 09:28 | BT15 | LONG RURAL | Planned |  | 3.00 | 290.0 | 0.006243 | 0.0000215 | No
27/02/2024 | 09:28 | GA37 | LONG RURAL | Third Party | Vehicle impact | 22.00 | 196.2 | 0.030973 | 0.0001579 | No
27/02/2024 | 10:12 | GA02 | SHORT RURAL | Asset failure | LV | 1.00 | 102.0 | 0.000718 | 0.0000070 | No
27/02/2024 | 10:29 | WHY17 | SHORT RURAL | Weather |  | 52.00 | 107.0 | 0.039145 | 0.0003658 | No
27/02/2024 | 10:37 | HH341J | URBAN | Asset failure | LV | 65.00 | 139.0 | 0.013930 | 0.0001002 | No
27/02/2024 | 11:39 | R18 | LONG RURAL | Unknown | Unknown | 1.00 | 321.0 | 0.002304 | 0.0000072 | No
27/02/2024 | 12:12 | MI23 | LONG RURAL | Weather |  | 23.00 | 104.0 | 0.017166 | 0.0001651 | No
27/02/2024 | 12:26 | MTB61 | SHORT RURAL | Unknown | Unknown | 1.00 | 167.0 | 0.001175 | 0.0000070 | No
27/02/2024 | 12:30 | NU15 | LONG RURAL | Weather |  | 17.00 | 124.0 | 0.015128 | 0.0001220 | No
27/02/2024 | 13:25 | AP829D | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 28.00 | 109.5 | 0.004729 | 0.0000432 | No
27/02/2024 | 14:16 | SM126C | URBAN | Asset failure | HV | 102.00 | 392.4 | 0.061712 | 0.0001573 | No
27/02/2024 | 14:25 | HH341G | URBAN | Asset failure | LV | 1.00 | 783.0 | 0.001207 | 0.0000015 | No
27/02/2024 | 15:39 | HH130B | URBAN | Asset failure | LV | 1.00 | 615.0 | 0.000948 | 0.0000015 | No
27/02/2024 | 15:53 | NL115C | URBAN | Asset failure | LV | 1.00 | 429.0 | 0.000661 | 0.0000015 | No
27/02/2024 | 16:11 | VH22 | SHORT RURAL | Asset failure | LV | 2.00 | 4,079.0 | 0.057396 | 0.0000141 | No
27/02/2024 | 17:44 | MV22 | SHORT RURAL | Asset failure | LV | 1.00 | 134.0 | 0.000943 | 0.0000070 | No
27/02/2024 | 17:54 | ME427F | URBAN | Asset failure | LV | 25.67 | 143.0 | 0.005659 | 0.0000396 | No
27/02/2024 | 17:55 | HH102D | URBAN | Asset failure | LV | 9.67 | 233.0 | 0.003473 | 0.0000149 | No
27/02/2024 | 18:42 | CD16 | SHORT RURAL | Asset failure | HV | 60.00 | 746.0 | 0.314909 | 0.0004221 | No
27/02/2024 | 18:52 | MT08 | LONG RURAL | Overloads |  | 15.67 | 95.0 | 0.010681 | 0.0001124 | No
27/02/2024 | 18:57 | GA15 | SHORT RURAL | Asset failure | LV | 1.00 | 434.0 | 0.003053 | 0.0000070 | No
27/02/2024 | 19:08 | GA23 | SHORT RURAL | Unknown | Unknown | 6.00 | 155.0 | 0.006543 | 0.0000422 | No
27/02/2024 | 19:20 | GA15 | SHORT RURAL | Asset failure | HV | 293.00 | 211.8 | 0.436573 | 0.0020614 | No
27/02/2024 | 19:26 | PP04 | SHORT RURAL | Overloads |  | 21.00 | 241.0 | 0.035607 | 0.0001477 | No
27/02/2024 | 19:43 | NU04 | SHORT RURAL | Unknown | Unknown | 1.00 | 122.0 | 0.000858 | 0.0000070 | No
27/02/2024 | 21:06 | AP125D | URBAN | Asset failure | LV | 53.00 | 121.0 | 0.009887 | 0.0000817 | No
27/02/2024 | 21:16 | MI20 | LONG RURAL | Asset failure | LV | 1.00 | 134.0 | 0.000962 | 0.0000072 | No
27/02/2024 | 21:18 | EL19 | URBAN | Asset failure | LV | 1.00 | 429.0 | 0.000661 | 0.0000015 | No
27/02/2024 | 21:35 | EL08D | URBAN | Asset failure | LV | 20.00 | 349.0 | 0.010761 | 0.0000308 | No
27/02/2024 | 21:38 | AP424B | URBAN | Planned |  | 107.00 | 380.0 | 0.062688 | 0.0001650 | No
27/02/2024 | 21:41 | MV53 | SHORT RURAL | Asset failure | LV | 1.00 | 276.0 | 0.001942 | 0.0000070 | No
27/02/2024 | 21:51 | AP226D | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
27/02/2024 | 21:53 | HH177B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 167.0 | 0.000515 | 0.0000031 | No
27/02/2024 | 22:02 | SM137B | URBAN | Planned |  | 21.00 | 260.0 | 0.008418 | 0.0000324 | No
27/02/2024 | 22:12 | MV63 | SHORT RURAL | Planned |  | 6.00 | 393.0 | 0.016590 | 0.0000422 | No
27/02/2024 | 23:06 | R15 | LONG RURAL | Unknown | Unknown | 94.00 | 503.5 | 0.339634 | 0.0006746 | No
27/02/2024 | 23:16 | G18 | LONG RURAL | Asset failure | HV | 1.00 | 19.0 | 0.000136 | 0.0000072 | No
28/02/2024 | 00:54 | MTB32 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 642.00 | 35.0 | 0.161424 | 0.0046072 | No
28/02/2024 | 00:54 | MTB32 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 3.00 | 36.0 | 0.000760 | 0.0000211 | No
28/02/2024 | 00:54 | MTB32 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 62.00 | 297.0 | 0.132145 | 0.0004449 | No
28/02/2024 | 00:59 | GU31 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 145.00 | 629.0 | 0.654517 | 0.0010406 | No
28/02/2024 | 01:05 | SA520D | URBAN | Asset failure | LV | 1.00 | 28.0 | 0.000043 | 0.0000015 | No
28/02/2024 | 02:17 | VH17 | SHORT RURAL | Asset failure | HV | 290.00 | 703.8 | 1.435887 | 0.0020403 | No
28/02/2024 | 02:17 | VH17 | SHORT RURAL | Network business | Switching and protection error | 300.00 | 11.0 | 0.023217 | 0.0021106 | No
28/02/2024 | 03:18 | MTB52 | LONG RURAL | Animal | Animal impact | 989.00 | 93.6 | 0.664521 | 0.0070974 | No
28/02/2024 | 03:18 | MTB52 | SHORT RURAL | Animal | Animal impact | 1.00 | 12.0 | 0.000084 | 0.0000070 | No
28/02/2024 | 03:53 | HH341H | URBAN | Vegetation | Grow-in - NSP responsibility | 490.00 | 103.0 | 0.077812 | 0.0007555 | No
28/02/2024 | 04:08 | EL08D | URBAN | Asset failure | LV | 20.00 | 600.0 | 0.018501 | 0.0000308 | No
28/02/2024 | 06:08 | HH121B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 484.00 | 98.4 | 0.073446 | 0.0007462 | No
28/02/2024 | 06:16 | NU28 | LONG RURAL | Unknown | Unknown | 47.00 | 383.0 | 0.129181 | 0.0003373 | No
28/02/2024 | 06:58 | ME347G | URBAN | Asset failure | LV | 46.00 | 349.0 | 0.024751 | 0.0000709 | No
28/02/2024 | 07:14 | NL111C | URBAN | Asset failure | LV | 1.00 | 114.0 | 0.000176 | 0.0000015 | No
28/02/2024 | 07:55 | KI41 | LONG RURAL | Asset failure | HV | 2.00 | 275.0 | 0.003947 | 0.0000144 | No
28/02/2024 | 08:35 | M61 | LONG RURAL | Network business | Switching and protection error | 2.00 | 21.0 | 0.000301 | 0.0000144 | No
28/02/2024 | 08:35 | M61 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 144.00 | 238.0 | 0.245947 | 0.0010334 | No
28/02/2024 | 08:55 | EL260A | URBAN | Planned |  | 22.00 | 384.8 | 0.013052 | 0.0000339 | No
28/02/2024 | 08:56 | MG11 | SHORT RURAL | Asset failure | LV | 3.00 | 248.0 | 0.005234 | 0.0000211 | No
28/02/2024 | 08:58 | W06 | LONG RURAL | Asset failure | HV | 1.00 | 522.0 | 0.003746 | 0.0000072 | No
28/02/2024 | 09:12 | HH121C | URBAN | Unknown | Unknown | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
28/02/2024 | 09:12 | MG02 | LONG RURAL | Overloads |  | 2.00 | 233.0 | 0.003344 | 0.0000144 | No
28/02/2024 | 09:18 | CM22 | LONG RURAL | Planned |  | 15.00 | 61.0 | 0.006566 | 0.0001076 | No
28/02/2024 | 09:47 | VH31 | SHORT RURAL | Planned |  | 1,224.00 | 192.2 | 1.655022 | 0.0086114 | No
28/02/2024 | 10:37 | PA02 | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
28/02/2024 | 10:58 | MG11 | SHORT RURAL | Asset failure | LV | 3.00 | 67.0 | 0.001414 | 0.0000211 | No
28/02/2024 | 11:27 | SM350F | URBAN | Asset failure | LV | 51.00 | 91.0 | 0.007158 | 0.0000786 | No
28/02/2024 | 11:29 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 2,903.0 | 0.020424 | 0.0000070 | No
28/02/2024 | 11:40 | MV41 | SHORT RURAL | Planned |  | 13.00 | 144.0 | 0.013170 | 0.0000915 | No
28/02/2024 | 11:43 | SM216D | URBAN | Asset failure | LV | 29.67 | 156.0 | 0.007135 | 0.0000457 | No
28/02/2024 | 11:56 | NL544B | URBAN | Asset failure | HV | 496.00 | 559.5 | 0.427840 | 0.0007647 | No
28/02/2024 | 12:00 | HH145B | URBAN | Unknown | Unknown | 2,524.00 | 10.0 | 0.038828 | 0.0038914 | No
28/02/2024 | 12:01 | SM179C | URBAN | Overloads |  | 1.00 | 726.0 | 0.001119 | 0.0000015 | No
28/02/2024 | 12:46 | MTB21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 68.0 | 0.000478 | 0.0000070 | No
28/02/2024 | 13:08 | MI16 | LONG RURAL | Asset failure | HV | 17.00 | 77.0 | 0.009394 | 0.0001220 | No
28/02/2024 | 13:56 | ME347B | URBAN | Asset failure | LV | 1.00 | 720.0 | 0.001110 | 0.0000015 | No
28/02/2024 | 14:06 | MG44 | URBAN | Unknown | Unknown | 91.00 | 90.0 | 0.012627 | 0.0001403 | No
28/02/2024 | 14:15 | ST41 | LONG RURAL | Asset failure | HV | 523.00 | 299.6 | 1.124603 | 0.0037532 | No
28/02/2024 | 14:17 | MI14 | LONG RURAL | Asset failure | LV | 33.00 | 145.0 | 0.034339 | 0.0002368 | No
28/02/2024 | 14:52 | MG34 | LONG RURAL | Asset failure | LV | 1.00 | 1,003.0 | 0.007198 | 0.0000072 | No
28/02/2024 | 15:13 | MG34 | LONG RURAL | Asset failure | HV | 9.00 | 144.0 | 0.009301 | 0.0000646 | No
28/02/2024 | 15:48 | SM349F | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
28/02/2024 | 16:07 | NA04 | LONG RURAL | Planned |  | 139.00 | 1.0 | 0.000998 | 0.0009975 | No
28/02/2024 | 16:09 | NL115D | URBAN | Unknown | Unknown | 9.00 | 454.0 | 0.006300 | 0.0000139 | No
28/02/2024 | 16:27 | GA11 | SHORT RURAL | Asset failure | LV | 2.00 | 208.0 | 0.002927 | 0.0000141 | No
28/02/2024 | 16:44 | HH409D | URBAN | Asset failure | LV | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
28/02/2024 | 17:07 | SM137A | URBAN | Unknown | Unknown | 15.33 | 154.0 | 0.003641 | 0.0000236 | No
28/02/2024 | 17:10 | SD48100 | SHORT RURAL | Unknown | Unknown | 611.00 | 64.0 | 0.275116 | 0.0042987 | No
28/02/2024 | 17:22 | MB41 | LONG RURAL | Asset failure | LV | 1.00 | 89.0 | 0.000639 | 0.0000072 | No
28/02/2024 | 17:34 | R17 | LONG RURAL | Asset failure | LV | 1.00 | 1,032.0 | 0.007406 | 0.0000072 | No
28/02/2024 | 17:40 | SM410D | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
28/02/2024 | 17:42 | KI54 | LONG RURAL | Asset failure | HV | 10.00 | 86.0 | 0.006172 | 0.0000718 | No
28/02/2024 | 17:44 | MG52 | URBAN | Vegetation | Grow-in - NSP responsibility | 3.00 | 51.7 | 0.000239 | 0.0000046 | No
28/02/2024 | 18:39 | AP351C | URBAN | Asset failure | LV | 1.00 | 404.0 | 0.000623 | 0.0000015 | No
28/02/2024 | 19:06 | SM411E | URBAN | Overloads |  | 1.00 | 203.0 | 0.000313 | 0.0000015 | No
28/02/2024 | 19:21 | BM44 | SHORT RURAL | Unknown | Unknown | 487.00 | 73.6 | 0.252173 | 0.0034263 | No
28/02/2024 | 19:47 | HH102B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 134.00 | 457.7 | 0.094565 | 0.0002066 | No
28/02/2024 | 19:57 | BM56 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 71.00 | 173.0 | 0.086417 | 0.0004995 | No
28/02/2024 | 20:00 | R27 | LONG RURAL | Asset failure | HV | 2.00 | 71.0 | 0.001019 | 0.0000144 | No
28/02/2024 | 21:05 | AP146B | URBAN | Planned |  | 101.00 | 453.0 | 0.070540 | 0.0001557 | No
28/02/2024 | 21:20 | HH118D | URBAN | Animal | Animal impact | 1,642.00 | 116.9 | 0.295896 | 0.0025316 | No
28/02/2024 | 21:52 | SM402D | URBAN | Planned |  | 4.00 | 313.0 | 0.001930 | 0.0000062 | No
28/02/2024 | 22:26 | SM402D | URBAN | Asset failure | LV | 46.00 | 227.0 | 0.016099 | 0.0000709 | No
28/02/2024 | 22:33 | NA01 | LONG RURAL | Animal | Animal impact | 2,076.00 | 202.3 | 3.014453 | 0.0148981 | No
28/02/2024 | 22:35 | NL451C | URBAN | Asset failure | LV | 1.00 | 295.0 | 0.000455 | 0.0000015 | No
28/02/2024 | 23:47 | PP08 | LONG RURAL | Asset failure | LV | 1.00 | 153.0 | 0.001098 | 0.0000072 | No
28/02/2024 | 23:56 | HH341E | URBAN | Animal | Animal impact | 463.33 | 50.0 | 0.035717 | 0.0007143 | No
29/02/2024 | 01:33 | HH130B | URBAN | Animal | Animal impact | 2,106.00 | 124.8 | 0.405353 | 0.0032469 | No
29/02/2024 | 01:52 | CBD367N | CBD | Animal | Animal impact | 17.33 | 116.0 | 0.290496 | 0.0025043 | No
29/02/2024 | 02:28 | NU28 | LONG RURAL | Asset failure | HV | 3.00 | 177.0 | 0.003811 | 0.0000215 | No
29/02/2024 | 03:13 | SSD400 | SHORT RURAL | Weather |  | 434.00 | 307.5 | 0.938928 | 0.0030534 | No
29/02/2024 | 03:56 | NL210D | URBAN | Animal | Animal impact | 52.67 | 503.0 | 0.040843 | 0.0000812 | No
29/02/2024 | 04:44 | HH130B | URBAN | Asset failure | LV | 24.33 | 211.0 | 0.007916 | 0.0000375 | No
29/02/2024 | 05:50 | SM350B | URBAN | Planned |  | 1,121.33 | 2.0 | 0.003458 | 0.0017288 | No
29/02/2024 | 05:50 | SM350B | URBAN | Animal | Animal impact | 53.33 | 274.0 | 0.022530 | 0.0000822 | No
29/02/2024 | 05:55 | HH102B | URBAN | Unknown | Unknown | 1.00 | 349.0 | 0.000538 | 0.0000015 | No
29/02/2024 | 06:56 | NA52 | LONG RURAL | Asset failure | LV | 1.00 | 3,988.0 | 0.028619 | 0.0000072 | No
29/02/2024 | 09:01 | WK31 | SHORT RURAL | Planned |  | 544.00 | 5.0 | 0.019137 | 0.0038273 | No
29/02/2024 | 09:15 | R25 | LONG RURAL | Planned |  | 105.00 | 291.0 | 0.219273 | 0.0007535 | No
29/02/2024 | 09:16 | HH121C | URBAN | Overloads |  | 18.00 | 44.0 | 0.001221 | 0.0000278 | No
29/02/2024 | 09:24 | YK15 | LONG RURAL | Asset failure | LV | 1.00 | 429.0 | 0.003079 | 0.0000072 | No
29/02/2024 | 09:24 | YK15 | LONG RURAL | Asset failure | LV | 1.00 | 428.0 | 0.003071 | 0.0000072 | No
29/02/2024 | 09:25 | YK15 | LONG RURAL | Asset failure | LV | 1.00 | 395.0 | 0.002835 | 0.0000072 | No
29/02/2024 | 09:28 | PP04 | SHORT RURAL | Planned |  | 93.00 | 436.0 | 0.285275 | 0.0006543 | No
29/02/2024 | 09:40 | SD44200 | SHORT RURAL | Planned |  | 476.00 | 452.6 | 1.515705 | 0.0033489 | No
29/02/2024 | 09:42 | YK11 | LONG RURAL | Asset failure | HV | 74.00 | 164.0 | 0.087092 | 0.0005310 | No
29/02/2024 | 09:46 | MTB54 | LONG RURAL | Planned |  | 15.00 | 165.0 | 0.017761 | 0.0001076 | No
29/02/2024 | 10:00 | W31 | SHORT RURAL | Planned |  | 30.00 | 277.0 | 0.058465 | 0.0002111 | No
29/02/2024 | 10:19 | HH121C | URBAN | Asset failure | LV | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
29/02/2024 | 10:31 | SM350B | URBAN | Animal | Animal impact | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
29/02/2024 | 10:54 | CBD412S | URBAN | Planned |  | 59.00 | 181.0 | 0.016464 | 0.0000910 | No
29/02/2024 | 11:01 | SM350G | URBAN | Third Party | Vehicle impact | 7.00 | 533.0 | 0.005752 | 0.0000108 | No
29/02/2024 | 11:25 | NU33 | LONG RURAL | Asset failure | LV | 1.00 | 140.0 | 0.001005 | 0.0000072 | No
29/02/2024 | 11:31 | ST11 | SHORT RURAL | Network business | Switching and protection error | 2,061.00 | 40.1 | 0.580998 | 0.0145001 | No
29/02/2024 | 11:41 | HH121C | URBAN | Asset failure | LV | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
29/02/2024 | 12:00 | WHY04 | URBAN | Overloads |  | 44.00 | 173.0 | 0.011736 | 0.0000678 | No
29/02/2024 | 12:23 | HH386F | URBAN | Asset failure | LV | 1.00 | 294.0 | 0.000453 | 0.0000015 | No
29/02/2024 | 12:57 | AP149E | URBAN | Asset failure | LV | 26.00 | 110.0 | 0.004409 | 0.0000401 | No
29/02/2024 | 13:08 | CBD412M | URBAN | Asset failure | LV | 2.00 | 7,002.0 | 0.021591 | 0.0000031 | No
29/02/2024 | 13:35 | AP829A | URBAN | Asset failure | LV | 1.00 | 290.0 | 0.000447 | 0.0000015 | No
29/02/2024 | 14:12 | SM137B | URBAN | Third Party | Vehicle impact | 2.00 | 87.0 | 0.000268 | 0.0000031 | No
29/02/2024 | 14:30 | HH386B | URBAN | Unknown | Unknown | 1.00 | 1,340.0 | 0.002066 | 0.0000015 | No
29/02/2024 | 14:57 | EL19 | URBAN | Third Party | Vehicle impact | 2.33 | 121.4 | 0.000437 | 0.0000036 | No
29/02/2024 | 16:06 | HH130B | URBAN | Asset failure | LV | 1.00 | 251.0 | 0.000387 | 0.0000015 | No
29/02/2024 | 17:25 | LX21 | SHORT RURAL | Unknown | Unknown | 2.00 | 292.0 | 0.004109 | 0.0000141 | No
29/02/2024 | 17:55 | MG17 | LONG RURAL | Asset failure | LV | 2.00 | 2,311.0 | 0.033169 | 0.0000144 | No
29/02/2024 | 18:34 | G04 | LONG RURAL | Other |  | 1.00 | 31.0 | 0.000222 | 0.0000072 | No
29/02/2024 | 18:47 | BM52 | URBAN | Asset failure | LV | 1.00 | 266.0 | 0.000410 | 0.0000015 | No
29/02/2024 | 19:08 | NL210C | URBAN | Asset failure | LV | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
29/02/2024 | 20:32 | HH341H | URBAN | Overloads |  | 1.00 | 409.0 | 0.000631 | 0.0000015 | No
29/02/2024 | 21:28 | BM43 | SHORT RURAL | Weather |  | 10.00 | 166.0 | 0.011679 | 0.0000704 | No
01/03/2024 | 00:20 | HH130F | URBAN | Animal | Animal impact | 457.00 | 66.0 | 0.046502 | 0.0007046 | No
01/03/2024 | 00:43 | LC01 | LONG RURAL | Unknown | Unknown | 49.00 | 1,165.0 | 0.409661 | 0.0003516 | No
01/03/2024 | 00:43 | LC01 | SHORT RURAL | Unknown | Unknown | 1.00 | 1,165.0 | 0.008196 | 0.0000070 | No
01/03/2024 | 01:09 | AP424B | URBAN | Asset failure | LV | 58.00 | 101.0 | 0.009032 | 0.0000894 | No
01/03/2024 | 01:13 | ME427F | URBAN | Asset failure | LV | 48.00 | 67.0 | 0.004958 | 0.0000740 | No
01/03/2024 | 02:48 | CN25 | LONG RURAL | Unknown | Unknown | 53.00 | 578.0 | 0.219840 | 0.0003803 | No
01/03/2024 | 03:04 | ME131B | URBAN | Overloads |  | 84.00 | 155.0 | 0.020074 | 0.0001295 | No
01/03/2024 | 06:18 | SD59100 | LONG RURAL | Weather |  | 334.00 | 1,833.8 | 4.395473 | 0.0023969 | No
01/03/2024 | 06:18 | SD59100 | LONG RURAL | Weather |  | 1.00 | 4,616.0 | 0.033126 | 0.0000072 | No
01/03/2024 | 06:33 | HH341F | URBAN | Third Party | Vehicle impact | 78.00 | 433.0 | 0.052071 | 0.0001203 | No
01/03/2024 | 06:45 | HH341B | URBAN | Asset failure | LV | 48.00 | 206.0 | 0.015245 | 0.0000740 | No
01/03/2024 | 06:47 | LC01 | LONG RURAL | Weather |  | 23.00 | 1,734.0 | 0.286206 | 0.0001651 | No
01/03/2024 | 07:15 | SB17 | LONG RURAL | Weather |  | 35.00 | 243.1 | 0.061063 | 0.0002512 | No
01/03/2024 | 08:31 | ST51 | SHORT RURAL | Planned |  | 32.00 | 176.5 | 0.039736 | 0.0002251 | No
01/03/2024 | 09:20 | SM349B | URBAN | Asset failure | LV | 1.00 | 312.0 | 0.000481 | 0.0000015 | No
01/03/2024 | 09:24 | CV18 | SHORT RURAL | Planned |  | 1.00 | 157.0 | 0.001105 | 0.0000070 | No
01/03/2024 | 09:28 | HK06 | LONG RURAL | Weather |  | 6.00 | 1,932.0 | 0.083188 | 0.0000431 | No
01/03/2024 | 09:35 | MV15 | SHORT RURAL | Asset failure | LV | 1.00 | 272.0 | 0.001914 | 0.0000070 | No
01/03/2024 | 09:35 | GU14 | LONG RURAL | Planned |  | 11.00 | 233.0 | 0.018393 | 0.0000789 | No
01/03/2024 | 10:02 | R25 | LONG RURAL | Planned |  | 1.00 | 151.0 | 0.001084 | 0.0000072 | No
01/03/2024 | 10:20 | GA15 | SHORT RURAL | Planned |  | 6.00 | 126.0 | 0.005319 | 0.0000422 | No
01/03/2024 | 10:51 | CD18 | LONG RURAL | Weather |  | 36.00 | 1,620.8 | 0.418724 | 0.0002583 | No
01/03/2024 | 11:03 | G18 | LONG RURAL | Planned |  | 23.00 | 79.0 | 0.013039 | 0.0001651 | No
01/03/2024 | 12:00 | MI14 | LONG RURAL | Animal | Animal impact | 14.00 | 33.0 | 0.003315 | 0.0001005 | No
01/03/2024 | 12:08 | CD17 | LONG RURAL | Weather |  | 38.00 | 397.9 | 0.108513 | 0.0002727 | No
01/03/2024 | 12:55 | CD02 | LONG RURAL | Weather |  | 59.00 | 1,567.8 | 0.663818 | 0.0004234 | No
01/03/2024 | 13:11 | ME131B | URBAN | Unknown | Unknown | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
01/03/2024 | 13:18 | CD02 | LONG RURAL | Weather |  | 72.00 | 1,400.5 | 0.723647 | 0.0005167 | No
01/03/2024 | 13:38 | HH341D | URBAN | Asset failure | LV | 46.00 | 681.0 | 0.048297 | 0.0000709 | No
01/03/2024 | 14:04 | G20 | LONG RURAL | Third Party | Vehicle impact | 89.00 | 402.0 | 0.256755 | 0.0006387 | No
01/03/2024 | 14:04 | G20 | LONG RURAL | Asset failure | HV | 1.00 | 1,409.0 | 0.010111 | 0.0000072 | No
01/03/2024 | 14:08 | PA23 | LONG RURAL | Weather |  | 14.00 | 1,546.0 | 0.155324 | 0.0001005 | No
01/03/2024 | 14:15 | G04 | LONG RURAL | Planned |  | 11.00 | 299.0 | 0.023603 | 0.0000789 | No
01/03/2024 | 14:56 | NL511B | URBAN | Asset failure | LV | 55.00 | 383.0 | 0.032477 | 0.0000848 | No
01/03/2024 | 15:20 | SM216B | URBAN | Asset failure | LV | 1.00 | 471.0 | 0.000726 | 0.0000015 | No
01/03/2024 | 15:22 | LC01 | LONG RURAL | Asset failure | HV | 99.00 | 165.5 | 0.117570 | 0.0007105 | No
01/03/2024 | 15:22 | LC01 | SHORT RURAL | Asset failure | HV | 229.00 | 524.5 | 0.844962 | 0.0016111 | No
01/03/2024 | 15:39 | PA17 | LONG RURAL | Unknown | Unknown | 10.00 | 2,744.0 | 0.196918 | 0.0000718 | No
01/03/2024 | 15:45 | SM179D | URBAN | Asset failure | LV | 1.00 | 352.0 | 0.000543 | 0.0000015 | No
01/03/2024 | 15:53 | HH428B | URBAN | Asset failure | LV | 75.00 | 129.0 | 0.014916 | 0.0001156 | No
01/03/2024 | 16:37 | CD26 | LONG RURAL | Asset failure | HV | 18.00 | 1,432.7 | 0.185063 | 0.0001292 | No
01/03/2024 | 17:25 | BM44 | SHORT RURAL | Unknown | Unknown | 2.00 | 387.0 | 0.005445 | 0.0000141 | No
01/03/2024 | 17:33 | MI08 | LONG RURAL | Unknown | Unknown | 1.00 | 185.0 | 0.001328 | 0.0000072 | No
01/03/2024 | 17:37 | PA26 | LONG RURAL | Weather |  | 1.00 | 158.0 | 0.001134 | 0.0000072 | No
01/03/2024 | 17:39 | PA25 | SHORT RURAL | Weather |  | 10.00 | 2,567.4 | 0.180629 | 0.0000704 | No
01/03/2024 | 17:54 | BS0402 | URBAN | Unknown | Unknown | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
01/03/2024 | 18:20 | PA24 | LONG RURAL | Weather |  | 31.00 | 1,317.9 | 0.293196 | 0.0002225 | No
01/03/2024 | 18:54 | HH386D | URBAN | Third Party | Vehicle impact | 1.00 | 119.0 | 0.000183 | 0.0000015 | No
01/03/2024 | 19:54 | PA19 | LONG RURAL | Weather |  | 28.00 | 1,481.8 | 0.297746 | 0.0002009 | No
01/03/2024 | 21:07 | AP149F | URBAN | Overloads |  | 50.00 | 129.0 | 0.009944 | 0.0000771 | No
01/03/2024 | 21:20 | AP365D2 | URBAN | Planned |  | 8.00 | 6.0 | 0.000074 | 0.0000123 | No
01/03/2024 | 21:20 | AP365D2 | URBAN | Unknown | Unknown | 2.00 | 1,182.5 | 0.003646 | 0.0000031 | No
02/03/2024 | 01:16 | ME200A | URBAN | Animal | Animal impact | 518.00 | 52.0 | 0.041529 | 0.0007986 | No
02/03/2024 | 01:42 | ME131A | URBAN | Animal | Animal impact | 2.00 | 101.0 | 0.000311 | 0.0000031 | No
02/03/2024 | 06:55 | VH22 | SHORT RURAL | Unknown | Unknown | 32.00 | 12.0 | 0.002702 | 0.0002251 | No
02/03/2024 | 07:02 | GA41 | LONG RURAL | Unknown | Unknown | 51.00 | 197.3 | 0.072223 | 0.0003660 | No
02/03/2024 | 08:54 | YK29 | LONG RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 2.00 | 172.0 | 0.002469 | 0.0000144 | No
02/03/2024 | 09:17 | VH15 | SHORT RURAL | Planned |  | 101.00 | 208.0 | 0.147802 | 0.0007106 | No
02/03/2024 | 11:44 | MB12 | SHORT RURAL | Overloads |  | 2.00 | 117.0 | 0.001646 | 0.0000141 | No
02/03/2024 | 13:52 | NL111Q | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
02/03/2024 | 14:08 | SM216A | URBAN | Vegetation | Grow-in - NSP responsibility | 131.00 | 42.4 | 0.008570 | 0.0002020 | No
02/03/2024 | 14:45 | MG41 | URBAN | Network business | Switching and protection error | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
02/03/2024 | 15:20 | SM216A | URBAN | Asset failure | LV | 4.00 | 148.0 | 0.000913 | 0.0000062 | No
02/03/2024 | 15:29 | SD54300 | LONG RURAL | Unknown | Unknown | 3.00 | 11.0 | 0.000237 | 0.0000215 | No
02/03/2024 | 15:41 | HH107C | URBAN | Asset failure | LV | 1.00 | 122.0 | 0.000188 | 0.0000015 | No
02/03/2024 | 17:37 | AP214D | URBAN | Asset failure | LV | 5.00 | 97.0 | 0.000748 | 0.0000077 | No
02/03/2024 | 17:44 | SM410D | URBAN | Asset failure | LV | 21.00 | 363.0 | 0.011753 | 0.0000324 | No
02/03/2024 | 18:18 | HH148B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 829.00 | 44.5 | 0.056902 | 0.0012781 | No
02/03/2024 | 20:22 | HH145A | URBAN | Asset failure | LV | 1.00 | 262.0 | 0.000404 | 0.0000015 | No
02/03/2024 | 21:09 | AP139C | URBAN | Asset failure | LV | 10.00 | 57.0 | 0.000879 | 0.0000154 | No
02/03/2024 | 21:49 | NL210B | URBAN | Asset failure | LV | 9.00 | 72.0 | 0.000999 | 0.0000139 | No
02/03/2024 | 22:29 | NL210B | URBAN | Asset failure | LV | 13.00 | 36.0 | 0.000722 | 0.0000200 | No
02/03/2024 | 23:16 | SA20 | URBAN | Asset failure | LV | 127.00 | 142.5 | 0.027903 | 0.0001958 | No
02/03/2024 | 23:35 | SA20 | URBAN | Asset failure | LV | 25.00 | 253.0 | 0.009752 | 0.0000385 | No
03/03/2024 | 00:24 | HH130B | URBAN | Unknown | Unknown | 2,683.00 | 31.4 | 0.129867 | 0.0041365 | No
03/03/2024 | 00:57 | SM350E | URBAN | Animal | Animal impact | 590.00 | 41.0 | 0.037295 | 0.0009096 | No
03/03/2024 | 02:15 | SM374E | URBAN | Animal | Animal impact | 1,311.00 | 58.0 | 0.117232 | 0.0020212 | No
03/03/2024 | 06:07 | ME131C | URBAN | Unknown | Unknown | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
03/03/2024 | 08:03 | HH341G | URBAN | Planned |  | 55.00 | 75.0 | 0.006360 | 0.0000848 | No
03/03/2024 | 08:40 | ST12 | SHORT RURAL | Planned |  | 85.00 | 196.8 | 0.117704 | 0.0005980 | No
03/03/2024 | 08:49 | SM411E | URBAN | Planned |  | 116.00 | 384.0 | 0.068676 | 0.0001788 | No
03/03/2024 | 08:56 | AP132E | URBAN | Planned |  | 10.00 | 301.0 | 0.004641 | 0.0000154 | No
03/03/2024 | 10:21 | GU34 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 209.0 | 0.001500 | 0.0000072 | No
03/03/2024 | 12:53 | HK05 | LONG RURAL | Unknown | Unknown | 1.00 | 127.0 | 0.000911 | 0.0000072 | No
03/03/2024 | 12:55 | PA25 | SHORT RURAL | Weather |  | 4.00 | 263.0 | 0.007401 | 0.0000281 | No
03/03/2024 | 12:55 | PA25 | SHORT RURAL | Weather |  | 6.00 | 4,510.8 | 0.190416 | 0.0000422 | No
03/03/2024 | 12:57 | SM411C | URBAN | Vegetation | Grow-in - NSP responsibility | 6.00 | 43.0 | 0.000398 | 0.0000093 | No
03/03/2024 | 13:08 | SD49100 | LONG RURAL | Asset failure | Subtransmission | 3.00 | 145.0 | 0.003122 | 0.0000215 | No
03/03/2024 | 13:50 | KA04 | LONG RURAL | Unknown | Unknown | 241.00 | 78.0 | 0.134901 | 0.0017295 | No
03/03/2024 | 14:04 | SA20 | URBAN | Overloads |  | 21.33 | 208.0 | 0.006841 | 0.0000329 | No
03/03/2024 | 14:21 | HH130B | URBAN | Asset failure | LV | 17.00 | 90.0 | 0.002359 | 0.0000262 | No
03/03/2024 | 15:18 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 73.0 | 0.000524 | 0.0000072 | No
03/03/2024 | 16:20 | NA02 | LONG RURAL | Asset failure | LV | 2.00 | 112.0 | 0.001607 | 0.0000144 | No
03/03/2024 | 17:13 | HK05 | LONG RURAL | Unknown | Unknown | 3.00 | 191.0 | 0.004112 | 0.0000215 | No
03/03/2024 | 17:31 | SA744D | URBAN | Asset failure | LV | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
03/03/2024 | 18:14 | NU02 | LONG RURAL | Asset failure | LV | 1.00 | 131.0 | 0.000940 | 0.0000072 | No
03/03/2024 | 18:19 | EL09 | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
03/03/2024 | 19:03 | NL111Q | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
03/03/2024 | 19:22 | PA15 | LONG RURAL | Planned |  | 2.00 | 250.0 | 0.003588 | 0.0000144 | No
03/03/2024 | 20:02 | AP226E | URBAN | Weather |  | 44.00 | 44.0 | 0.002985 | 0.0000678 | No
03/03/2024 | 20:20 | CN21 | LONG RURAL | Planned |  | 167.00 | 216.0 | 0.258865 | 0.0011984 | No
03/03/2024 | 20:21 | SD40300 | LONG RURAL | Planned |  | 1,073.00 | 200.3 | 1.542696 | 0.0077002 | No
03/03/2024 | 20:26 | NU02 | LONG RURAL | Asset failure | LV | 12.00 | 198.0 | 0.017051 | 0.0000861 | No
03/03/2024 | 20:52 | SM350E | URBAN | Overloads |  | 1.00 | 168.0 | 0.000259 | 0.0000015 | No
03/03/2024 | 22:52 | ST11 | SHORT RURAL | Unknown | Unknown | 35.00 | 173.0 | 0.042600 | 0.0002462 | No
03/03/2024 | 23:38 | GA800A | SHORT RURAL | Asset failure | LV | 7.00 | 151.0 | 0.007437 | 0.0000492 | No
04/03/2024 | 07:19 | W19 | LONG RURAL | Asset failure | HV | 12.00 | 314.7 | 0.027098 | 0.0000861 | No
04/03/2024 | 07:25 | MV54 | SHORT RURAL | Asset failure | LV | 1.00 | 114.0 | 0.000802 | 0.0000070 | No
04/03/2024 | 07:41 | AP139C | URBAN | Third Party | Vehicle impact | 918.00 | 84.5 | 0.119561 | 0.0014153 | No
04/03/2024 | 07:43 | HH409E | URBAN | Asset failure | LV | 1.00 | 168.0 | 0.000259 | 0.0000015 | No
04/03/2024 | 07:59 | MG19 | LONG RURAL | Unknown | Unknown | 123.00 | 120.0 | 0.105923 | 0.0008827 | No
04/03/2024 | 08:42 | ST11 | SHORT RURAL | Asset failure | LV | 6.00 | 92.7 | 0.003912 | 0.0000422 | No
04/03/2024 | 08:44 | HH341G | URBAN | Planned |  | 281.00 | 205.7 | 0.089132 | 0.0004332 | No
04/03/2024 | 08:59 | ST12 | SHORT RURAL | Planned |  | 166.00 | 329.3 | 0.384630 | 0.0011679 | No
04/03/2024 | 09:03 | CM02 | LONG RURAL | Planned |  | 448.00 | 350.4 | 1.126397 | 0.0032150 | No
04/03/2024 | 09:06 | KA06 | LONG RURAL | Unknown | Unknown | 1.00 | 23.0 | 0.000165 | 0.0000072 | No
04/03/2024 | 09:25 | NA17 | LONG RURAL | Planned |  | 3.00 | 90.0 | 0.001938 | 0.0000215 | No
04/03/2024 | 09:29 | AP355E | URBAN | Animal | Animal impact | 14.00 | 107.0 | 0.002310 | 0.0000216 | No
04/03/2024 | 09:36 | MTB51 | LONG RURAL | Asset failure | LV | 1.00 | 201.0 | 0.001442 | 0.0000072 | No
04/03/2024 | 09:45 | BT13 | LONG RURAL | Planned |  | 20.00 | 80.0 | 0.011482 | 0.0001435 | No
04/03/2024 | 10:05 | VH33 | SHORT RURAL | Planned |  | 8.00 | 95.0 | 0.005347 | 0.0000563 | No
04/03/2024 | 10:08 | HH386B | URBAN | Overloads |  | 2.00 | 134.0 | 0.000413 | 0.0000031 | No
04/03/2024 | 10:56 | PA25 | SHORT RURAL | Weather |  | 4.00 | 909.0 | 0.025581 | 0.0000281 | No
04/03/2024 | 11:02 | MI08 | LONG RURAL | Planned |  | 55.00 | 286.8 | 0.113199 | 0.0003947 | No
04/03/2024 | 11:03 | NL511A | URBAN | Asset failure | LV | 27.00 | 73.1 | 0.003043 | 0.0000416 | No
04/03/2024 | 11:27 | SD31100 | LONG RURAL | Unknown | Unknown | 2.00 | 29.0 | 0.000416 | 0.0000144 | No
04/03/2024 | 11:40 | MB62 | LONG RURAL | Overloads |  | 1.00 | 200.0 | 0.001435 | 0.0000072 | No
04/03/2024 | 14:19 | AP226C | URBAN | Third Party | Unauthorised access | 1.00 | 68.0 | 0.000105 | 0.0000015 | No
04/03/2024 | 14:46 | CD26 | LONG RURAL | Weather |  | 18.00 | 303.0 | 0.039140 | 0.0001292 | No
04/03/2024 | 15:00 | MV14 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 125.0 | 0.000879 | 0.0000070 | No
04/03/2024 | 15:20 | WK52 | SHORT RURAL | Asset failure | HV | 2.00 | 35.0 | 0.000492 | 0.0000141 | No
04/03/2024 | 17:13 | MG42 | SHORT RURAL | Third Party | Vehicle impact | 17.00 | 253.9 | 0.030365 | 0.0001196 | No
04/03/2024 | 17:24 | HH409C | URBAN | Other |  | 47.00 | 58.0 | 0.004203 | 0.0000725 | No
04/03/2024 | 19:34 | MG34 | LONG RURAL | Asset failure | HV | 2.00 | 533.0 | 0.007650 | 0.0000144 | No
04/03/2024 | 19:46 | AP132C | URBAN | Asset failure | LV | 6.00 | 129.0 | 0.001193 | 0.0000093 | No
04/03/2024 | 19:59 | MB72 | LONG RURAL | Asset failure | HV | 158.00 | 120.5 | 0.136680 | 0.0011339 | No
04/03/2024 | 22:51 | ME131B | URBAN | Animal | Animal impact | 52.67 | 85.0 | 0.006902 | 0.0000812 | No
04/03/2024 | 23:44 | HH341G | URBAN | Animal | Animal impact | 98.00 | 111.0 | 0.016771 | 0.0001511 | No
05/03/2024 | 01:11 | NU04 | SHORT RURAL | Third Party | Vehicle impact | 9.00 | 112.0 | 0.007092 | 0.0000633 | No
05/03/2024 | 03:24 | HH121C | URBAN | Animal | Animal impact | 55.00 | 113.0 | 0.009582 | 0.0000848 | No
05/03/2024 | 05:06 | SD35500 | LONG RURAL | Weather |  | 77.00 | 232.0 | 0.128198 | 0.0005526 | No
05/03/2024 | 07:46 | EL09 | URBAN | Asset failure | LV | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
05/03/2024 | 08:12 | CL05 | LONG RURAL | Planned |  | 20.00 | 531.8 | 0.076320 | 0.0001435 | No
05/03/2024 | 08:37 | CD01 | SHORT RURAL | Planned |  | 88.00 | 372.0 | 0.230314 | 0.0006191 | No
05/03/2024 | 08:42 | MI20 | LONG RURAL | Planned |  | 12.00 | 412.0 | 0.035480 | 0.0000861 | No
05/03/2024 | 08:59 | AP125B | URBAN | Planned |  | 2.00 | 342.0 | 0.001055 | 0.0000031 | No
05/03/2024 | 09:23 | NU20 | LONG RURAL | Planned |  | 107.00 | 123.0 | 0.094448 | 0.0007679 | No
05/03/2024 | 09:33 | CM18 | LONG RURAL | Planned |  | 41.00 | 351.0 | 0.103275 | 0.0002942 | No
05/03/2024 | 09:43 | VH33 | SHORT RURAL | Planned |  | 9.00 | 158.0 | 0.010004 | 0.0000633 | No
05/03/2024 | 09:44 | VH33 | SHORT RURAL | Planned |  | 1.00 | 65.0 | 0.000457 | 0.0000070 | No
05/03/2024 | 09:49 | VH15 | SHORT RURAL | Asset failure | HV | 1,303.00 | 125.1 | 1.146827 | 0.0091672 | No
05/03/2024 | 09:49 | SA17 | URBAN | Overloads |  | 1.00 | 724.0 | 0.001116 | 0.0000015 | No
05/03/2024 | 09:52 | G23 | LONG RURAL | Asset failure | LV | 2.00 | 84.0 | 0.001206 | 0.0000144 | No
05/03/2024 | 10:03 | MV63 | SHORT RURAL | Animal | Animal impact | 62.00 | 133.0 | 0.058015 | 0.0004362 | No
05/03/2024 | 10:07 | PA19 | LONG RURAL | Weather |  | 8.00 | 113.0 | 0.006487 | 0.0000574 | No
05/03/2024 | 10:21 | PA19 | LONG RURAL | Weather |  | 11.00 | 97.0 | 0.007657 | 0.0000789 | No
05/03/2024 | 11:18 | MV15 | SHORT RURAL | Planned |  | 7.00 | 150.0 | 0.007387 | 0.0000492 | No
05/03/2024 | 11:47 | YK15 | LONG RURAL | Asset failure | HV | 2.00 | 106.0 | 0.001521 | 0.0000144 | No
05/03/2024 | 12:17 | AP132B | URBAN | Unknown | Unknown | 69.00 | 33.2 | 0.003534 | 0.0001064 | No
05/03/2024 | 14:52 | MTB82 | SHORT RURAL | Asset failure | LV | 1.00 | 411.0 | 0.002892 | 0.0000070 | No
05/03/2024 | 16:29 | WHY17 | SHORT RURAL | Asset failure | LV | 1.00 | 197.0 | 0.001386 | 0.0000070 | No
05/03/2024 | 17:00 | CD01 | SHORT RURAL | Asset failure | LV | 1.00 | 287.0 | 0.002019 | 0.0000070 | No
05/03/2024 | 17:34 | AP424E | URBAN | Asset failure | HV | 2,090.00 | 64.5 | 0.207935 | 0.0032223 | No
05/03/2024 | 18:08 | HH429C | URBAN | Asset failure | LV | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
05/03/2024 | 18:17 | SA520D | URBAN | Overloads |  | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
05/03/2024 | 18:50 | NA09 | LONG RURAL | Asset failure | HV | 106.00 | 309.7 | 0.235549 | 0.0007607 | No
05/03/2024 | 19:51 | GU32 | LONG RURAL | Overloads |  | 1.00 | 324.0 | 0.002325 | 0.0000072 | No
05/03/2024 | 20:15 | MG05 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 232.0 | 0.001665 | 0.0000072 | No
05/03/2024 | 20:21 | AP529C | URBAN | Asset failure | LV | 64.00 | 69.0 | 0.006808 | 0.0000987 | No
05/03/2024 | 20:25 | LX41 | SHORT RURAL | Asset failure | LV | 9.00 | 268.0 | 0.016970 | 0.0000633 | No
06/03/2024 | 03:23 | KI13 | LONG RURAL | Weather |  | 6.00 | 68.0 | 0.002928 | 0.0000431 | No
06/03/2024 | 05:56 | MI16 | LONG RURAL | Unknown | Unknown | 308.00 | 231.0 | 0.510581 | 0.0022103 | No
06/03/2024 | 08:03 | WK61 | SHORT RURAL | Planned |  | 14.00 | 309.0 | 0.030436 | 0.0000985 | No
06/03/2024 | 08:14 | CL04 | LONG RURAL | Planned |  | 51.00 | 183.0 | 0.066977 | 0.0003660 | No
06/03/2024 | 08:20 | ST21 | SHORT RURAL | Planned |  | 596.00 | 136.4 | 0.572112 | 0.0041932 | No
06/03/2024 | 08:41 | GA43 | SHORT RURAL | Planned |  | 11.00 | 290.0 | 0.022443 | 0.0000774 | No
06/03/2024 | 08:45 | HH341G | URBAN | Planned |  | 207.00 | 332.2 | 0.106034 | 0.0003191 | No
06/03/2024 | 08:59 | PL34 | LONG RURAL | Weather |  | 223.00 | 186.0 | 0.297660 | 0.0016003 | No
06/03/2024 | 08:59 | CM02 | LONG RURAL | Planned |  | 381.00 | 337.6 | 0.923185 | 0.0027342 | No
06/03/2024 | 09:11 | SM410D | URBAN | Planned |  | 137.00 | 125.0 | 0.026403 | 0.0002112 | No
06/03/2024 | 09:12 | HH102D | URBAN | Asset failure | LV | 108.00 | 158.0 | 0.026308 | 0.0001665 | No
06/03/2024 | 09:43 | MB23 | SHORT RURAL | Overloads |  | 1.00 | 71.0 | 0.000500 | 0.0000070 | No
06/03/2024 | 11:26 | SD48101 | LONG RURAL | Network business | Switching and protection error | 1,348.00 | 25.0 | 0.241849 | 0.0096737 | No
06/03/2024 | 11:26 | SD48101 | URBAN | Network business | Switching and protection error | 2,596.00 | 27.7 | 0.110935 | 0.0040024 | No
06/03/2024 | 12:08 | SM349A | URBAN | Asset failure | LV | 1.00 | 215.0 | 0.000331 | 0.0000015 | No
06/03/2024 | 12:30 | ST36 | LONG RURAL | Unknown | Unknown | 2.00 | 377.0 | 0.005411 | 0.0000144 | No
06/03/2024 | 12:59 | W25 | LONG RURAL | Asset failure | HV | 2.00 | 115.0 | 0.001651 | 0.0000144 | No
06/03/2024 | 13:40 | SA34 | URBAN | Asset failure | LV | 2.67 | 48.0 | 0.000197 | 0.0000041 | No
06/03/2024 | 14:34 | NL234C | URBAN | Asset failure | LV | 1.00 | 150.0 | 0.000231 | 0.0000015 | No
06/03/2024 | 16:04 | SA20 | URBAN | Overloads |  | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
06/03/2024 | 16:28 | HH341D | URBAN | Asset failure | LV | 52.00 | 254.8 | 0.020427 | 0.0000802 | No
06/03/2024 | 16:48 | HH428F | URBAN | Overloads |  | 1.00 | 202.0 | 0.000311 | 0.0000015 | No
06/03/2024 | 17:18 | VH21 | SHORT RURAL | Asset failure | LV | 62.00 | 122.7 | 0.053540 | 0.0004362 | No
06/03/2024 | 18:12 | NL210B | URBAN | Third Party | Other | 33.00 | 67.0 | 0.003409 | 0.0000509 | No
06/03/2024 | 18:32 | KA27 | LONG RURAL | Animal | Animal impact | 157.00 | 111.1 | 0.125198 | 0.0011267 | No
06/03/2024 | 18:44 | AP372F | URBAN | Overloads |  | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
06/03/2024 | 19:40 | HH177G | URBAN | Overloads |  | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
06/03/2024 | 20:45 | MI16 | LONG RURAL | Weather |  | 308.00 | 186.0 | 0.411146 | 0.0022103 | No
06/03/2024 | 23:02 | GA41 | LONG RURAL | Asset failure | HV | 1.00 | 92.0 | 0.000660 | 0.0000072 | No
07/03/2024 | 00:56 | NL115E | URBAN | Unknown | Unknown | 175.00 | 117.0 | 0.031567 | 0.0002698 | No
07/03/2024 | 05:38 | SD38100 | LONG RURAL | Weather |  | 2,786.00 | 46.9 | 0.937458 | 0.0199933 | No
07/03/2024 | 05:38 | SD38100 | LONG RURAL | Weather |  | 9.00 | 511.0 | 0.033004 | 0.0000646 | No
07/03/2024 | 07:18 | NL760C | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
07/03/2024 | 07:39 | ST35 | LONG RURAL | Overloads |  | 2.00 | 131.0 | 0.001880 | 0.0000144 | No
07/03/2024 | 08:04 | EL15 | URBAN | Planned |  | 5.00 | 391.6 | 0.003019 | 0.0000077 | No
07/03/2024 | 08:18 | BM31 | SHORT RURAL | Planned |  | 10.00 | 226.4 | 0.015928 | 0.0000704 | No
07/03/2024 | 08:20 | CL05 | LONG RURAL | Planned |  | 20.00 | 330.1 | 0.047371 | 0.0001435 | No
07/03/2024 | 08:25 | KA04 | LONG RURAL | Planned |  | 7.00 | 203.4 | 0.010219 | 0.0000502 | No
07/03/2024 | 08:26 | ST35 | LONG RURAL | Overloads |  | 1.00 | 87.0 | 0.000624 | 0.0000072 | No
07/03/2024 | 08:38 | ST11 | SHORT RURAL | Planned |  | 16.00 | 144.0 | 0.016210 | 0.0001126 | No
07/03/2024 | 08:41 | NU02 | LONG RURAL | Unknown | Unknown | 1.00 | 4,115.0 | 0.029531 | 0.0000072 | No
07/03/2024 | 08:42 | HH341G | URBAN | Planned |  | 72.00 | 176.8 | 0.019627 | 0.0001110 | No
07/03/2024 | 09:02 | NA02 | LONG RURAL | Asset failure | HV | 1.00 | 62.0 | 0.000445 | 0.0000072 | No
07/03/2024 | 09:02 | NA02 | LONG RURAL | Asset failure | HV | 1.00 | 10,424.0 | 0.074806 | 0.0000072 | No
07/03/2024 | 09:06 | R25 | LONG RURAL | Planned |  | 12.00 | 152.0 | 0.013090 | 0.0000861 | No
07/03/2024 | 09:17 | CM18 | LONG RURAL | Planned |  | 31.00 | 348.1 | 0.077447 | 0.0002225 | No
07/03/2024 | 09:41 | LX52 | LONG RURAL | Asset failure | LV | 1.00 | 200.0 | 0.001435 | 0.0000072 | No
07/03/2024 | 09:56 | G18 | LONG RURAL | Planned |  | 23.00 | 154.0 | 0.025419 | 0.0001651 | No
07/03/2024 | 10:14 | BT04 | LONG RURAL | Planned |  | 13.00 | 96.0 | 0.008956 | 0.0000933 | No
07/03/2024 | 10:34 | MTB53 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 6.00 | 205.0 | 0.008827 | 0.0000431 | No
07/03/2024 | 10:37 | MG03 | SHORT RURAL | Unknown | Unknown | 1.00 | 84.0 | 0.000591 | 0.0000070 | No
07/03/2024 | 10:42 | M51 | SHORT RURAL | Other |  | 1.00 | 1,728.0 | 0.012157 | 0.0000070 | No
07/03/2024 | 11:29 | NA17 | LONG RURAL | Planned |  | 2.00 | 74.0 | 0.001062 | 0.0000144 | No
07/03/2024 | 11:45 | W26 | LONG RURAL | Planned |  | 2.00 | 191.0 | 0.002741 | 0.0000144 | No
07/03/2024 | 11:53 | HK06 | LONG RURAL | Asset failure | HV | 4.00 | 113.0 | 0.003244 | 0.0000287 | No
07/03/2024 | 12:06 | NA17 | LONG RURAL | Planned |  | 3.00 | 130.0 | 0.002799 | 0.0000215 | No
07/03/2024 | 12:35 | HH145C | URBAN | Unknown | Unknown | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
07/03/2024 | 12:35 | ST21 | SHORT RURAL | Asset failure | LV | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
07/03/2024 | 13:04 | SM350H | URBAN | Asset failure | LV | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
07/03/2024 | 13:18 | MTB22 | SHORT RURAL | Overloads |  | 2.00 | 574.0 | 0.008077 | 0.0000141 | No
07/03/2024 | 14:37 | GU43 | LONG RURAL | Planned |  | 4.00 | 16.0 | 0.000459 | 0.0000287 | No
07/03/2024 | 16:34 | AP425D | URBAN | Unknown | Unknown | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
07/03/2024 | 16:45 | SA17 | URBAN | Asset failure | LV | 1.00 | 282.0 | 0.000435 | 0.0000015 | No
07/03/2024 | 17:23 | NL210A | URBAN | Asset failure | LV | 1.00 | 680.0 | 0.001048 | 0.0000015 | No
07/03/2024 | 20:49 | MB72 | LONG RURAL | Asset failure | HV | 3.00 | 34.7 | 0.000746 | 0.0000215 | No
07/03/2024 | 21:04 | HH107E | URBAN | Asset failure | LV | 1.00 | 232.0 | 0.000358 | 0.0000015 | No
07/03/2024 | 21:20 | SM350F | URBAN | Asset failure | LV | 1.00 | 306.0 | 0.000472 | 0.0000015 | No
08/03/2024 | 02:45 | BM32 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 1.00 | 2,113.0 | 0.014866 | 0.0000070 | No
08/03/2024 | 04:50 | HH145B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 49.00 | 597.0 | 0.045101 | 0.0000755 | No
08/03/2024 | 07:02 | AP149E | URBAN | Asset failure | LV | 27.00 | 111.0 | 0.004621 | 0.0000416 | No
08/03/2024 | 07:47 | MT18 | LONG RURAL | Asset failure | HV | 2.00 | 144.0 | 0.002067 | 0.0000144 | No
08/03/2024 | 07:53 | LX71 | LONG RURAL | Unknown | Unknown | 1.00 | 557.0 | 0.003997 | 0.0000072 | No
08/03/2024 | 08:01 | LX43 | SHORT RURAL | Planned |  | 26.00 | 236.0 | 0.043170 | 0.0001829 | No
08/03/2024 | 08:40 | SB16 | LONG RURAL | Planned |  | 5.00 | 166.0 | 0.005956 | 0.0000359 | No
08/03/2024 | 08:48 | M13 | LONG RURAL | Overloads |  | 16.67 | 539.0 | 0.064467 | 0.0001196 | No
08/03/2024 | 08:51 | CM28 | LONG RURAL | Planned |  | 4.00 | 101.0 | 0.002899 | 0.0000287 | No
08/03/2024 | 09:17 | VH44 | SHORT RURAL | Planned |  | 3.00 | 275.0 | 0.005804 | 0.0000211 | No
08/03/2024 | 09:50 | HH121G | URBAN | Overloads |  | 1.00 | 43.0 | 0.000066 | 0.0000015 | No
08/03/2024 | 10:26 | YK04 | LONG RURAL | Planned |  | 4.00 | 173.0 | 0.004966 | 0.0000287 | No
08/03/2024 | 10:34 | NU02 | LONG RURAL | Planned |  | 9.00 | 88.0 | 0.005684 | 0.0000646 | No
08/03/2024 | 10:43 | SM402C | URBAN | Asset failure | LV | 36.00 | 148.0 | 0.008214 | 0.0000555 | No
08/03/2024 | 11:45 | MI12 | LONG RURAL | Planned |  | 1.00 | 147.0 | 0.001055 | 0.0000072 | No
08/03/2024 | 12:31 | VH15 | SHORT RURAL | Asset failure | LV | 2.00 | 5,474.0 | 0.077025 | 0.0000141 | No
08/03/2024 | 12:46 | HH102D | URBAN | Overloads |  | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
08/03/2024 | 13:28 | GA800C | SHORT RURAL | Unknown | Unknown | 1.00 | 284.0 | 0.001998 | 0.0000070 | No
08/03/2024 | 15:14 | SA711C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
08/03/2024 | 15:32 | MTB82 | SHORT RURAL | Asset failure | HV | 67.00 | 60.0 | 0.028283 | 0.0004714 | No
08/03/2024 | 17:51 | CV753A | LONG RURAL | Overloads |  | 2.00 | 205.0 | 0.002942 | 0.0000144 | No
08/03/2024 | 17:57 | SM126D | URBAN | Asset failure | LV | 1.00 | 333.0 | 0.000513 | 0.0000015 | No
08/03/2024 | 18:03 | HH428C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,164.00 | 54.0 | 0.096908 | 0.0017946 | No
08/03/2024 | 18:24 | PL02 | URBAN | Planned |  | 5.00 | 323.2 | 0.002491 | 0.0000077 | No
08/03/2024 | 19:32 | HH341J | URBAN | Asset failure | LV | 44.00 | 106.0 | 0.007191 | 0.0000678 | No
08/03/2024 | 19:49 | ME131C | URBAN | Third Party | Vehicle impact | 4.00 | 412.0 | 0.002541 | 0.0000062 | No
08/03/2024 | 19:50 | SM411A | URBAN | Asset failure | LV | 37.00 | 142.0 | 0.008100 | 0.0000570 | No
08/03/2024 | 19:53 | CM24 | LONG RURAL | Unknown | Unknown | 28.00 | 1,007.7 | 0.202487 | 0.0002009 | No
08/03/2024 | 19:58 | MV42 | SHORT RURAL | Asset failure | LV | 4.67 | 153.0 | 0.005023 | 0.0000328 | No
08/03/2024 | 20:13 | NL511A | URBAN | Asset failure | LV | 114.00 | 388.0 | 0.068195 | 0.0001758 | No
08/03/2024 | 20:24 | SG03 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 14.00 | 126.6 | 0.012467 | 0.0000985 | No
08/03/2024 | 20:39 | HH145E | URBAN | Overloads |  | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
08/03/2024 | 21:58 | KA04 | LONG RURAL | Overloads |  | 1.00 | 156.0 | 0.001120 | 0.0000072 | No
09/03/2024 | 00:31 | SM179D | URBAN | Asset failure | LV | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
09/03/2024 | 01:28 | NA17 | LONG RURAL | Unknown | Unknown | 63.00 | 193.0 | 0.087257 | 0.0004521 | No
09/03/2024 | 05:50 | R18 | LONG RURAL | Unknown | Unknown | 12.00 | 94.0 | 0.008095 | 0.0000861 | No
09/03/2024 | 06:43 | NA09 | LONG RURAL | Unknown | Unknown | 267.00 | 336.1 | 0.644025 | 0.0019161 | No
09/03/2024 | 07:13 | HH177B | URBAN | Asset failure | LV | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
09/03/2024 | 07:32 | AP355A | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
09/03/2024 | 08:35 | HH145E | URBAN | Asset failure | LV | 2.00 | 435.0 | 0.001341 | 0.0000031 | No
09/03/2024 | 09:59 | MTB11 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 5.00 | 106.0 | 0.003803 | 0.0000359 | No
09/03/2024 | 09:59 | MTB11 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 2,090.00 | 105.6 | 1.552831 | 0.0147042 | No
09/03/2024 | 11:11 | SM216A | URBAN | Other |  | 1,133.00 | 208.5 | 0.364145 | 0.0017468 | No
09/03/2024 | 12:01 | NL210C | URBAN | Third Party | Dig-in | 1.00 | 313.0 | 0.000483 | 0.0000015 | No
09/03/2024 | 12:04 | CD23 | LONG RURAL | Asset failure | HV | 49.00 | 488.0 | 0.171600 | 0.0003516 | No
09/03/2024 | 12:08 | MG06 | SHORT RURAL | Asset failure | HV | 13.00 | 44.0 | 0.004024 | 0.0000915 | No
09/03/2024 | 12:26 | GU34 | LONG RURAL | Overloads |  | 2.00 | 282.0 | 0.004047 | 0.0000144 | No
09/03/2024 | 12:41 | EL11 | URBAN | Overloads |  | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
09/03/2024 | 12:43 | HH341H | URBAN | Asset failure | LV | 1.00 | 352.0 | 0.000543 | 0.0000015 | No
09/03/2024 | 12:57 | EL01Q | URBAN | Overloads |  | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
09/03/2024 | 12:57 | NL115F | URBAN | Asset failure | LV | 6.00 | 208.0 | 0.001924 | 0.0000093 | No
09/03/2024 | 13:17 | HH386E | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 914.00 | 58.0 | 0.081731 | 0.0014092 | No
09/03/2024 | 14:07 | NL115E | URBAN | Asset failure | LV | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
09/03/2024 | 15:32 | G02 | LONG RURAL | Asset failure | LV | 19.00 | 64.0 | 0.008726 | 0.0001364 | No
09/03/2024 | 15:56 | VH34 | SHORT RURAL | Asset failure | HV | 231.00 | 164.9 | 0.268038 | 0.0016252 | No
09/03/2024 | 16:08 | NL451C | URBAN | Asset failure | LV | 1.00 | 749.0 | 0.001155 | 0.0000015 | No
09/03/2024 | 16:49 | SD35400 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 853.00 | 172.0 | 1.032310 | 0.0060013 | No
09/03/2024 | 16:57 | MTB11 | LONG RURAL | Unknown | Unknown | 5.00 | 86.0 | 0.003086 | 0.0000359 | No
09/03/2024 | 16:57 | MTB11 | SHORT RURAL | Unknown | Unknown | 2,090.00 | 86.0 | 1.264559 | 0.0147042 | No
09/03/2024 | 17:09 | CD16 | SHORT RURAL | Unknown | Unknown | 60.00 | 1,112.2 | 0.469506 | 0.0004221 | No
09/03/2024 | 17:11 | M91 | LONG RURAL | Asset failure | LV | 4.00 | 478.0 | 0.013721 | 0.0000287 | No
09/03/2024 | 17:16 | MTB81 | SHORT RURAL | Unknown | Unknown | 1.00 | 507.0 | 0.003567 | 0.0000070 | No
09/03/2024 | 17:20 | NL210A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 54.00 | 119.0 | 0.009907 | 0.0000833 | No
09/03/2024 | 17:24 | MV62 | SHORT RURAL | Asset failure | HV | 1.00 | 953.0 | 0.006705 | 0.0000070 | No
09/03/2024 | 17:47 | AP424B | URBAN | Asset failure | LV | 64.67 | 556.0 | 0.055433 | 0.0000997 | No
09/03/2024 | 17:55 | HH386D | URBAN | Asset failure | LV | 1.00 | 1,019.0 | 0.001571 | 0.0000015 | No
09/03/2024 | 18:06 | SM216A | URBAN | Other |  | 105.00 | 318.0 | 0.051479 | 0.0001619 | No
09/03/2024 | 18:10 | MB32 | LONG RURAL | Overloads |  | 2.00 | 7.0 | 0.000100 | 0.0000144 | No
09/03/2024 | 18:24 | HH428C | URBAN | Overloads |  | 1.00 | 38.0 | 0.000059 | 0.0000015 | No
09/03/2024 | 18:24 | SM216A | URBAN | Asset failure | LV | 36.00 | 570.0 | 0.031637 | 0.0000555 | No
09/03/2024 | 18:25 | W28 | LONG RURAL | Asset failure | LV | 2.00 | 362.0 | 0.005196 | 0.0000144 | No
09/03/2024 | 18:27 | HH428B | URBAN | Overloads |  | 11.00 | 53.0 | 0.000899 | 0.0000170 | No
09/03/2024 | 18:28 | SM216A | URBAN | Other |  | 2.00 | 441.0 | 0.001360 | 0.0000031 | No
09/03/2024 | 18:35 | ME131B | URBAN | Asset failure | LV | 26.67 | 300.0 | 0.012334 | 0.0000411 | No
09/03/2024 | 18:40 | ME131B | URBAN | Asset failure | LV | 1.00 | 300.0 | 0.000463 | 0.0000015 | No
09/03/2024 | 18:40 | SM216B | URBAN | Asset failure | LV | 32.33 | 588.0 | 0.029312 | 0.0000498 | No
09/03/2024 | 18:44 | SM137B | URBAN | Unknown | Unknown | 32.33 | 370.0 | 0.018444 | 0.0000498 | No
09/03/2024 | 18:46 | SM216B | URBAN | Unknown | Unknown | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
09/03/2024 | 18:48 | SM216C | URBAN | Unknown | Unknown | 26.33 | 177.0 | 0.007186 | 0.0000406 | No
09/03/2024 | 18:52 | AP424E | URBAN | Asset failure | LV | 37.33 | 412.0 | 0.023714 | 0.0000576 | No
09/03/2024 | 18:59 | SM350B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,755.00 | 69.0 | 0.186699 | 0.0027058 | No
09/03/2024 | 19:01 | SM410D | URBAN | Vegetation | Grow-in - NSP responsibility | 272.00 | 202.0 | 0.084727 | 0.0004194 | No
09/03/2024 | 19:02 | SM216A | URBAN | Asset failure | LV | 22.00 | 689.0 | 0.023370 | 0.0000339 | No
09/03/2024 | 19:22 | AP365A | URBAN | Third Party | Vehicle impact | 798.00 | 194.8 | 0.239659 | 0.0012303 | No
09/03/2024 | 19:28 | HH428F | URBAN | Overloads |  | 27.00 | 850.0 | 0.035383 | 0.0000416 | No
09/03/2024 | 19:33 | AP424B | URBAN | Overloads |  | 1.00 | 899.0 | 0.001386 | 0.0000015 | No
09/03/2024 | 19:34 | MTB11 | SHORT RURAL | Asset failure | LV | 1.00 | 340.0 | 0.002392 | 0.0000070 | No
09/03/2024 | 20:04 | AP424A | URBAN | Overloads |  | 15.00 | 330.0 | 0.007632 | 0.0000231 | No
09/03/2024 | 20:23 | ME116B | URBAN | Overloads |  | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
09/03/2024 | 20:30 | BM41 | SHORT RURAL | Overloads |  | 1.00 | 158.0 | 0.001112 | 0.0000070 | No
09/03/2024 | 20:50 | GA46 | LONG RURAL | Unknown | Unknown | 87.00 | 170.0 | 0.106138 | 0.0006243 | No
09/03/2024 | 20:55 | VH21 | SHORT RURAL | Overloads |  | 2.00 | 3,534.0 | 0.049727 | 0.0000141 | No
09/03/2024 | 21:08 | HH386C | URBAN | Asset failure | HV | 161.00 | 499.2 | 0.123908 | 0.0002482 | No
09/03/2024 | 21:10 | SM216A | URBAN | Other |  | 1.00 | 2,915.0 | 0.004494 | 0.0000015 | No
09/03/2024 | 21:11 | MV22 | SHORT RURAL | Unknown | Unknown | 1.00 | 185.0 | 0.001302 | 0.0000070 | No
09/03/2024 | 21:45 | PL06 | URBAN | Overloads |  | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
09/03/2024 | 22:06 | M92 | LONG RURAL | Asset failure | LV | 2.00 | 186.0 | 0.002670 | 0.0000144 | No
09/03/2024 | 22:21 | HH121H | URBAN | Overloads |  | 23.00 | 141.0 | 0.005000 | 0.0000355 | No
09/03/2024 | 22:52 | SA14 | URBAN | Overloads |  | 5.67 | 238.0 | 0.002079 | 0.0000087 | No
10/03/2024 | 00:43 | EL11 | URBAN | Third Party | Other | 12.00 | 511.0 | 0.009454 | 0.0000185 | No
10/03/2024 | 03:07 | CD02 | LONG RURAL | Asset failure | LV | 1.00 | 326.0 | 0.002339 | 0.0000072 | No
10/03/2024 | 03:16 | AP424B | URBAN | Unknown | Unknown | 64.67 | 396.0 | 0.039481 | 0.0000997 | No
10/03/2024 | 06:34 | SA11 | URBAN | Asset failure | LV | 1.00 | 212.0 | 0.000327 | 0.0000015 | No
10/03/2024 | 07:59 | NL760C | URBAN | Asset failure | LV | 1.00 | 360.0 | 0.000555 | 0.0000015 | No
10/03/2024 | 09:41 | MTB63 | SHORT RURAL | Unknown | Unknown | 4.00 | 269.0 | 0.007570 | 0.0000281 | No
10/03/2024 | 10:07 | AP149H | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
10/03/2024 | 12:07 | HH341D | URBAN | Overloads |  | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
10/03/2024 | 12:38 | BM33 | SHORT RURAL | Overloads |  | 2.00 | 195.0 | 0.002744 | 0.0000141 | No
10/03/2024 | 12:50 | AP125D | URBAN | Asset failure | LV | 1.00 | 325.0 | 0.000501 | 0.0000015 | No
10/03/2024 | 12:51 | MT06 | LONG RURAL | Overloads |  | 1.00 | 209.0 | 0.001500 | 0.0000072 | No
10/03/2024 | 12:55 | YK27 | LONG RURAL | Overloads |  | 1.00 | 160.0 | 0.001148 | 0.0000072 | No
10/03/2024 | 13:55 | SA520D | URBAN | Asset failure | LV | 1.00 | 276.0 | 0.000426 | 0.0000015 | No
10/03/2024 | 14:18 | HH428F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 620.00 | 82.0 | 0.078383 | 0.0009559 | No
10/03/2024 | 15:00 | HH409C | URBAN | Third Party | Other | 21.00 | 373.4 | 0.012090 | 0.0000324 | No
10/03/2024 | 16:19 | CV26 | LONG RURAL | Other |  | 3.00 | 310.0 | 0.006674 | 0.0000215 | No
10/03/2024 | 16:40 | MT08 | LONG RURAL | Asset failure | LV | 1.00 | 157.0 | 0.001127 | 0.0000072 | No
10/03/2024 | 16:43 | HH121C | URBAN | Overloads |  | 39.33 | 310.0 | 0.018799 | 0.0000606 | No
10/03/2024 | 16:45 | HH145A | URBAN | Overloads |  | 2.00 | 449.0 | 0.001384 | 0.0000031 | No
10/03/2024 | 17:02 | EL09 | URBAN | Unknown | Unknown | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
10/03/2024 | 17:05 | SG05 | SHORT RURAL | Third Party | Other | 33.00 | 48.2 | 0.011196 | 0.0002322 | No
10/03/2024 | 17:34 | HH341H | URBAN | Overloads |  | 19.67 | 214.0 | 0.006489 | 0.0000303 | No
10/03/2024 | 17:37 | SM172C | URBAN | Asset failure | LV | 42.00 | 91.0 | 0.005893 | 0.0000648 | No
10/03/2024 | 17:45 | HH403B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,446.00 | 84.0 | 0.316775 | 0.0037711 | No
10/03/2024 | 17:46 | BM41 | SHORT RURAL | Overloads |  | 1.00 | 138.0 | 0.000971 | 0.0000070 | No
10/03/2024 | 17:54 | ST35 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 169.0 | 0.001213 | 0.0000072 | No
10/03/2024 | 17:59 | AP425B | URBAN | Asset failure | LV | 1.00 | 288.0 | 0.000444 | 0.0000015 | No
10/03/2024 | 18:19 | NU13 | LONG RURAL | Animal | Animal impact | 62.00 | 229.6 | 0.102148 | 0.0004449 | No
10/03/2024 | 18:32 | W28 | LONG RURAL | Unknown | Unknown | 4.00 | 135.5 | 0.003890 | 0.0000287 | No
10/03/2024 | 18:40 | HH432F | URBAN | Overloads |  | 56.00 | 198.0 | 0.017095 | 0.0000863 | No
10/03/2024 | 18:41 | ME131E | URBAN | Asset failure | LV | 1.00 | 477.0 | 0.000735 | 0.0000015 | No
10/03/2024 | 18:52 | HH432F | URBAN | Overloads |  | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
10/03/2024 | 18:54 | MTB62 | SHORT RURAL | Overloads |  | 1.00 | 223.0 | 0.001569 | 0.0000070 | No
10/03/2024 | 18:55 | SM216A | URBAN | Asset failure | LV | 1.00 | 251.0 | 0.000387 | 0.0000015 | No
10/03/2024 | 18:55 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 2,211.0 | 0.015555 | 0.0000070 | No
10/03/2024 | 19:02 | SA14 | URBAN | Overloads |  | 5.67 | 40.0 | 0.000349 | 0.0000087 | No
10/03/2024 | 19:12 | HH341E | URBAN | Overloads |  | 28.00 | 209.0 | 0.009022 | 0.0000432 | No
10/03/2024 | 19:14 | SM216A | URBAN | Asset failure | LV | 16.33 | 254.0 | 0.006396 | 0.0000252 | No
10/03/2024 | 20:01 | MB72 | LONG RURAL | Overloads |  | 2.00 | 289.0 | 0.004148 | 0.0000144 | No
10/03/2024 | 20:11 | SA14 | URBAN | Overloads |  | 5.67 | 54.0 | 0.000472 | 0.0000087 | No
10/03/2024 | 20:14 | HH341G | URBAN | Overloads |  | 25.00 | 238.0 | 0.009173 | 0.0000385 | No
10/03/2024 | 20:25 | HH432F | URBAN | Overloads |  | 1.00 | 95.0 | 0.000146 | 0.0000015 | No
10/03/2024 | 20:27 | SG10 | SHORT RURAL | Asset failure | LV | 1.00 | 216.0 | 0.001520 | 0.0000070 | No
10/03/2024 | 20:30 | HH386D | URBAN | Overloads |  | 1.00 | 439.0 | 0.000677 | 0.0000015 | No
10/03/2024 | 22:04 | CBD412F | URBAN | Overloads |  | 15.00 | 170.0 | 0.003931 | 0.0000231 | No
10/03/2024 | 22:10 | CBD412J | URBAN | Overloads |  | 12.00 | 179.0 | 0.003312 | 0.0000185 | No
10/03/2024 | 22:20 | SA20 | URBAN | Overloads |  | 164.00 | 299.0 | 0.075603 | 0.0002528 | No
10/03/2024 | 22:29 | SG05 | SHORT RURAL | Third Party | Other | 3.00 | 1,458.0 | 0.030773 | 0.0000211 | No
10/03/2024 | 23:46 | AP132D | URBAN | Overloads |  | 1.00 | 168.0 | 0.000259 | 0.0000015 | No
11/03/2024 | 00:55 | SA20 | URBAN | Asset failure | LV | 1.00 | 280.0 | 0.000432 | 0.0000015 | No
11/03/2024 | 02:23 | SA32 | URBAN | Asset failure | LV | 1.00 | 581.0 | 0.000896 | 0.0000015 | No
11/03/2024 | 03:08 | NL115F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 65.00 | 301.8 | 0.030245 | 0.0001002 | No
11/03/2024 | 06:45 | HH341C | URBAN | Asset failure | LV | 2.00 | 254.0 | 0.000783 | 0.0000031 | No
11/03/2024 | 07:38 | MV51 | SHORT RURAL | Asset failure | LV | 1.00 | 283.0 | 0.001991 | 0.0000070 | No
11/03/2024 | 08:02 | BM12 | SHORT RURAL | Asset failure | LV | 1.00 | 159.0 | 0.001119 | 0.0000070 | No
11/03/2024 | 09:28 | MTB12 | SHORT RURAL | Asset failure | HV | 64.00 | 455.7 | 0.205183 | 0.0004503 | No
11/03/2024 | 09:44 | WHY02 | URBAN | Asset failure | LV | 1.00 | 238.0 | 0.000367 | 0.0000015 | No
11/03/2024 | 10:24 | M13 | LONG RURAL | Overloads |  | 2.00 | 167.0 | 0.002397 | 0.0000144 | No
11/03/2024 | 10:29 | SM349E | URBAN | Asset failure | LV | 1.00 | 450.0 | 0.000694 | 0.0000015 | No
11/03/2024 | 10:32 | ME231A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 9.00 | 95.0 | 0.001318 | 0.0000139 | No
11/03/2024 | 10:35 | NU05 | SHORT RURAL | Overloads |  | 1.00 | 366.0 | 0.002575 | 0.0000070 | No
11/03/2024 | 11:58 | NL760C | URBAN | Overloads |  | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
11/03/2024 | 12:30 | ME116D | URBAN | Asset failure | LV | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
11/03/2024 | 12:50 | AP214B | URBAN | Asset failure | LV | 2.00 | 86.0 | 0.000265 | 0.0000031 | No
11/03/2024 | 13:57 | NU04 | SHORT RURAL | Third Party | Other | 3.00 | 166.0 | 0.003504 | 0.0000211 | No
11/03/2024 | 14:37 | AP214B | URBAN | Vegetation | Grow-in - NSP responsibility | 2.00 | 288.0 | 0.000888 | 0.0000031 | No
11/03/2024 | 14:42 | HH496A | URBAN | Asset failure | LV | 1.00 | 447.0 | 0.000689 | 0.0000015 | No
11/03/2024 | 15:39 | SA43 | URBAN | Asset failure | LV | 8.00 | 504.0 | 0.006216 | 0.0000123 | No
11/03/2024 | 16:20 | AP227A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,866.00 | 74.0 | 0.212892 | 0.0028769 | No
11/03/2024 | 17:10 | SM411A | URBAN | Network business | Switching and protection error | 37.00 | 145.0 | 0.008272 | 0.0000570 | No
11/03/2024 | 17:15 | AP355A | URBAN | Overloads |  | 1.00 | 616.0 | 0.000950 | 0.0000015 | No
11/03/2024 | 17:20 | ME116D | URBAN | Asset failure | LV | 16.33 | 117.0 | 0.002946 | 0.0000252 | No
11/03/2024 | 17:53 | EL10 | URBAN | Overloads |  | 1.00 | 150.0 | 0.000231 | 0.0000015 | No
11/03/2024 | 17:54 | SM349E | URBAN | Asset failure | LV | 83.00 | 292.0 | 0.037366 | 0.0001280 | No
11/03/2024 | 17:57 | AP355A | URBAN | Overloads |  | 33.00 | 153.0 | 0.007784 | 0.0000509 | No
11/03/2024 | 18:01 | SA16 | URBAN | Overloads |  | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
11/03/2024 | 18:08 | AP227D | URBAN | Asset failure | LV | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
11/03/2024 | 18:10 | SM349E | URBAN | Asset failure | LV | 8.00 | 401.0 | 0.004946 | 0.0000123 | No
11/03/2024 | 18:20 | AP424E | URBAN | Asset failure | LV | 34.00 | 204.0 | 0.010694 | 0.0000524 | No
11/03/2024 | 18:31 | NL115C | URBAN | Asset failure | LV | 2.00 | 151.0 | 0.000466 | 0.0000031 | No
11/03/2024 | 18:37 | HH148B | URBAN | Overloads |  | 16.67 | 96.0 | 0.002467 | 0.0000257 | No
11/03/2024 | 18:40 | SM216G | URBAN | Overloads |  | 27.00 | 326.0 | 0.013571 | 0.0000416 | No
11/03/2024 | 18:55 | BT27 | LONG RURAL | Asset failure | LV | 2.00 | 293.0 | 0.004205 | 0.0000144 | No
11/03/2024 | 18:59 | AP344D | URBAN | Overloads |  | 1.00 | 257.0 | 0.000396 | 0.0000015 | No
11/03/2024 | 19:05 | SD57100 | LONG RURAL | Asset failure | Subtransmission | 1,236.00 | 532.0 | 4.718810 | 0.0088699 | No
11/03/2024 | 19:05 | SD57100 | SHORT RURAL | Asset failure | Subtransmission | 1.00 | 532.0 | 0.003743 | 0.0000070 | No
11/03/2024 | 19:10 | SM410A | URBAN | Asset failure | LV | 23.33 | 140.0 | 0.005036 | 0.0000360 | No
11/03/2024 | 19:16 | HH409F | URBAN | Overloads |  | 32.00 | 123.0 | 0.006068 | 0.0000493 | No
11/03/2024 | 19:21 | SA14 | URBAN | Overloads |  | 5.67 | 117.0 | 0.001022 | 0.0000087 | No
11/03/2024 | 19:21 | ME116D | URBAN | Asset failure | LV | 49.00 | 119.0 | 0.008990 | 0.0000755 | No
11/03/2024 | 19:34 | AP139B | URBAN | Overloads |  | 21.00 | 179.0 | 0.005795 | 0.0000324 | No
11/03/2024 | 19:40 | HH341H | URBAN | Overloads |  | 40.33 | 403.0 | 0.025060 | 0.0000622 | No
11/03/2024 | 19:57 | SM411A | URBAN | Asset failure | LV | 11.67 | 176.0 | 0.003166 | 0.0000180 | No
11/03/2024 | 19:57 | SM411B | URBAN | Asset failure | LV | 90.00 | 26.0 | 0.003608 | 0.0001388 | No
11/03/2024 | 20:16 | HH386C | URBAN | Asset failure | HV | 1,433.00 | 63.6 | 0.140576 | 0.0022093 | No
11/03/2024 | 20:38 | SM216A | URBAN | Network business | Switching and protection error | 35.00 | 321.0 | 0.017322 | 0.0000540 | No
11/03/2024 | 21:31 | SM410A | URBAN | Overloads |  | 23.33 | 267.0 | 0.009605 | 0.0000360 | No
11/03/2024 | 21:34 | AP149F | URBAN | Unknown | Unknown | 250.33 | 113.0 | 0.043613 | 0.0003860 | No
11/03/2024 | 21:41 | SA20 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 47.00 | 17.0 | 0.001232 | 0.0000725 | No
11/03/2024 | 21:50 | AP149F | URBAN | Unknown | Unknown | 2.00 | 128.0 | 0.000395 | 0.0000031 | No
11/03/2024 | 22:01 | EL07 | URBAN | Overloads |  | 1.00 | 55.0 | 0.000085 | 0.0000015 | No
11/03/2024 | 23:05 | HH118C | URBAN | Overloads |  | 4.33 | 311.0 | 0.002078 | 0.0000067 | No
11/03/2024 | 23:06 | AP139C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 918.00 | 93.0 | 0.131626 | 0.0014153 | No
11/03/2024 | 23:07 | CBD412H | URBAN | Overloads |  | 21.00 | 48.0 | 0.001554 | 0.0000324 | No
12/03/2024 | 00:02 | GU23 | LONG RURAL | Asset failure | LV | 1.00 | 350.0 | 0.002512 | 0.0000072 | No
12/03/2024 | 00:07 | GU33 | LONG RURAL | Asset failure | LV | 1.00 | 344.0 | 0.002469 | 0.0000072 | No
12/03/2024 | 00:30 | HH130A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,040.00 | 136.4 | 0.428990 | 0.0031452 | No
12/03/2024 | 02:31 | SD38100 | LONG RURAL | Asset failure | Subtransmission | 165.00 | 151.0 | 0.178798 | 0.0011841 | No
12/03/2024 | 06:07 | GU31 | LONG RURAL | Asset failure | LV | 1.00 | 224.0 | 0.001607 | 0.0000072 | No
12/03/2024 | 06:34 | SA18 | URBAN | Asset failure | LV | 1.00 | 315.0 | 0.000486 | 0.0000015 | No
12/03/2024 | 06:42 | SM374E | URBAN | Asset failure | LV | 1.00 | 453.0 | 0.000698 | 0.0000015 | No
12/03/2024 | 08:14 | SA14 | URBAN | Asset failure | LV | 2.00 | 372.0 | 0.001147 | 0.0000031 | No
12/03/2024 | 08:24 | HH145A | URBAN | Planned |  | 66.00 | 285.8 | 0.029085 | 0.0001018 | No
12/03/2024 | 09:15 | MG05 | LONG RURAL | Planned |  | 12.00 | 159.0 | 0.013692 | 0.0000861 | No
12/03/2024 | 09:26 | GU41 | LONG RURAL | Asset failure | LV | 1.00 | 172.0 | 0.001234 | 0.0000072 | No
12/03/2024 | 09:33 | GA02 | SHORT RURAL | Planned |  | 4.00 | 219.5 | 0.006177 | 0.0000281 | No
12/03/2024 | 09:53 | HH118C | URBAN | Overloads |  | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
12/03/2024 | 10:05 | MI03 | LONG RURAL | Planned |  | 2.00 | 122.0 | 0.001751 | 0.0000144 | No
12/03/2024 | 10:09 | SA11 | URBAN | Asset failure | LV | 19.00 | 173.9 | 0.005095 | 0.0000293 | No
12/03/2024 | 10:29 | R27 | LONG RURAL | Planned |  | 2.00 | 86.0 | 0.001234 | 0.0000144 | No
12/03/2024 | 11:39 | BT04 | LONG RURAL | Planned |  | 2.00 | 119.0 | 0.001708 | 0.0000144 | No
12/03/2024 | 11:45 | NL451D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,284.00 | 77.0 | 0.271145 | 0.0035214 | No
12/03/2024 | 11:53 | VH33 | SHORT RURAL | Asset failure | HV | 4.00 | 268.0 | 0.007542 | 0.0000281 | No
12/03/2024 | 12:40 | NU15 | LONG RURAL | Weather |  | 855.00 | 103.0 | 0.631983 | 0.0061358 | No
12/03/2024 | 12:40 | AP146E | URBAN | Unknown | Unknown | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
12/03/2024 | 14:50 | PA12 | LONG RURAL | Unknown | Unknown | 44.00 | 224.1 | 0.070773 | 0.0003158 | No
12/03/2024 | 14:50 | PA12 | LONG RURAL | Asset failure | HV | 1.00 | 2,954.0 | 0.021199 | 0.0000072 | No
12/03/2024 | 14:50 | PA12 | LONG RURAL | Asset failure | HV | 1.00 | 1,587.0 | 0.011389 | 0.0000072 | No
12/03/2024 | 15:07 | HH341E | URBAN | Asset failure | LV | 1.00 | 519.0 | 0.000800 | 0.0000015 | No
12/03/2024 | 16:39 | AP424B | URBAN | Overloads |  | 29.33 | 365.0 | 0.016507 | 0.0000452 | No
12/03/2024 | 18:12 | MG19 | LONG RURAL | Asset failure | HV | 279.00 | 160.0 | 0.320351 | 0.0020022 | No
12/03/2024 | 18:12 | MG19 | LONG RURAL | Asset failure | LV | 1.00 | 1,173.0 | 0.008418 | 0.0000072 | No
12/03/2024 | 18:20 | SD35400 | SHORT RURAL | Weather |  | 853.00 | 151.1 | 0.906804 | 0.0060013 | No
12/03/2024 | 18:36 | LX43 | SHORT RURAL | Overloads |  | 5.00 | 239.0 | 0.008407 | 0.0000352 | No
12/03/2024 | 18:44 | HH145A | URBAN | Asset failure | LV | 1.00 | 631.0 | 0.000973 | 0.0000015 | No
12/03/2024 | 19:21 | SM410A | URBAN | Asset failure | LV | 1.00 | 160.0 | 0.000247 | 0.0000015 | No
12/03/2024 | 19:24 | HH432C | URBAN | Overloads |  | 47.00 | 86.0 | 0.006232 | 0.0000725 | No
12/03/2024 | 19:43 | HH121C | URBAN | Asset failure | LV | 17.33 | 99.0 | 0.002646 | 0.0000267 | No
12/03/2024 | 19:47 | EL17 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,024.00 | 74.0 | 0.116828 | 0.0015788 | No
12/03/2024 | 20:13 | GU23 | LONG RURAL | Asset failure | HV | 3.00 | 62.0 | 0.001335 | 0.0000215 | No
12/03/2024 | 21:10 | CBD366N | CBD | Planned |  | 26.00 | 446.7 | 1.678104 | 0.0037564 | No
12/03/2024 | 22:25 | HH121G | URBAN | Asset failure | LV | 1.00 | 522.0 | 0.000805 | 0.0000015 | No
12/03/2024 | 22:26 | HH409C | URBAN | Overloads |  | 2.00 | 116.0 | 0.000358 | 0.0000031 | No
12/03/2024 | 22:44 | HH118B | URBAN | Vegetation | Grow-in - NSP responsibility | 1,146.00 | 54.0 | 0.095410 | 0.0017668 | No
13/03/2024 | 01:29 | HH522B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 263.0 | 0.000405 | 0.0000015 | No
13/03/2024 | 01:34 | GA03 | LONG RURAL | Asset failure | HV | 2.00 | 581.5 | 0.008346 | 0.0000144 | No
13/03/2024 | 01:56 | AP214B | URBAN | Overloads |  | 28.00 | 163.0 | 0.007037 | 0.0000432 | No
13/03/2024 | 02:44 | AP372A | URBAN | Overloads |  | 1.00 | 117.0 | 0.000180 | 0.0000015 | No
13/03/2024 | 06:28 | HH522B | URBAN | Asset failure | HV | 1,565.00 | 58.9 | 0.142159 | 0.0024128 | No
13/03/2024 | 08:02 | WK33 | SHORT RURAL | Planned |  | 31.00 | 168.0 | 0.036641 | 0.0002181 | No
13/03/2024 | 08:21 | SA14 | URBAN | Overloads |  | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
13/03/2024 | 08:44 | MV42 | SHORT RURAL | Planned |  | 130.00 | 343.2 | 0.313853 | 0.0009146 | No
13/03/2024 | 08:46 | SA36 | URBAN | Planned |  | 54.00 | 185.7 | 0.015458 | 0.0000833 | No
13/03/2024 | 09:15 | MI10 | LONG RURAL | Planned |  | 47.00 | 326.0 | 0.109956 | 0.0003373 | No
13/03/2024 | 09:18 | KI15 | LONG RURAL | Other |  | 1.00 | 179.0 | 0.001285 | 0.0000072 | No
13/03/2024 | 09:18 | SA11 | URBAN | Planned |  | 2.00 | 1,787.0 | 0.005510 | 0.0000031 | No
13/03/2024 | 09:27 | GU32 | LONG RURAL | Planned |  | 9.00 | 299.0 | 0.019312 | 0.0000646 | No
13/03/2024 | 09:31 | HH496G | URBAN | Third Party | Dig-in | 1.00 | 239.0 | 0.000368 | 0.0000015 | No
13/03/2024 | 09:45 | HH496D | URBAN | Planned |  | 490.00 | 129.3 | 0.097645 | 0.0007555 | No
13/03/2024 | 09:45 | W28 | LONG RURAL | Overloads |  | 2.67 | 116.0 | 0.002220 | 0.0000191 | No
13/03/2024 | 09:47 | G21 | LONG RURAL | Asset failure | HV | 1.00 | 62.0 | 0.000445 | 0.0000072 | No
13/03/2024 | 10:03 | CN42 | LONG RURAL | Planned |  | 75.00 | 228.0 | 0.122715 | 0.0005382 | No
13/03/2024 | 10:44 | SM349B | URBAN | Network business | Switching and protection error | 1.00 | 37.0 | 0.000057 | 0.0000015 | No
13/03/2024 | 10:47 | HH341K | URBAN | Planned |  | 34.00 | 21.0 | 0.001101 | 0.0000524 | No
13/03/2024 | 10:54 | GA22 | SHORT RURAL | Planned |  | 18.00 | 188.2 | 0.023836 | 0.0001266 | No
13/03/2024 | 11:12 | NL115C | URBAN | Asset failure | LV | 1.00 | 334.0 | 0.000515 | 0.0000015 | No
13/03/2024 | 11:19 | GU43 | LONG RURAL | Planned |  | 123.00 | 234.0 | 0.206549 | 0.0008827 | No
13/03/2024 | 11:32 | ME131E | URBAN | Planned |  | 22.00 | 3.0 | 0.000102 | 0.0000339 | No
13/03/2024 | 11:40 | SA20 | URBAN | Overloads |  | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
13/03/2024 | 12:52 | VH22 | SHORT RURAL | Unknown | Unknown | 1.00 | 275.0 | 0.001935 | 0.0000070 | No
13/03/2024 | 13:27 | ME116B | URBAN | Asset failure | LV | 35.00 | 39.5 | 0.002134 | 0.0000540 | No
13/03/2024 | 14:23 | KI42 | LONG RURAL | Planned |  | 1,028.00 | 124.3 | 0.916984 | 0.0073773 | No
13/03/2024 | 15:35 | SA520A | URBAN | Asset failure | LV | 18.00 | 29.0 | 0.000805 | 0.0000278 | No
13/03/2024 | 17:53 | EL260A | URBAN | Asset failure | HV | 238.67 | 69.7 | 0.025651 | 0.0003680 | No
13/03/2024 | 18:00 | EL10 | URBAN | Asset failure | HV | 619.00 | 168.4 | 0.160691 | 0.0009543 | No
13/03/2024 | 18:25 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,582.00 | 77.1 | 0.306902 | 0.0039808 | No
13/03/2024 | 18:27 | AP214C | URBAN | Overloads |  | 1.00 | 383.0 | 0.000590 | 0.0000015 | No
13/03/2024 | 21:19 | HH121E | URBAN | Asset failure | LV | 1.00 | 257.0 | 0.000396 | 0.0000015 | No
13/03/2024 | 21:37 | SM137B | URBAN | Planned |  | 16.00 | 357.1 | 0.008810 | 0.0000247 | No
13/03/2024 | 22:38 | AP424C | URBAN | Asset failure | LV | 1.00 | 521.0 | 0.000803 | 0.0000015 | No
13/03/2024 | 23:03 | EL10 | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
14/03/2024 | 05:24 | MG43 | URBAN | Asset failure | LV | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
14/03/2024 | 06:17 | NA02 | LONG RURAL | Weather |  | 85.00 | 160.4 | 0.097828 | 0.0006100 | No
14/03/2024 | 06:17 | SD46300 | LONG RURAL | Network business | Switching and protection error | 4,567.00 | 54.8 | 1.795216 | 0.0327743 | No
14/03/2024 | 07:00 | MI13 | LONG RURAL | Unknown | Unknown | 24.00 | 162.0 | 0.027902 | 0.0001722 | No
14/03/2024 | 07:12 | PL11 | LONG RURAL | Weather |  | 69.00 | 192.6 | 0.095388 | 0.0004952 | No
14/03/2024 | 07:21 | SM411C | URBAN | Overloads |  | 1.00 | 288.0 | 0.000444 | 0.0000015 | No
14/03/2024 | 07:38 | CN33 | LONG RURAL | Unknown | Unknown | 34.00 | 131.8 | 0.032150 | 0.0002440 | No
14/03/2024 | 07:50 | NL234C | URBAN | Unknown | Unknown | 2,736.00 | 66.4 | 0.280231 | 0.0042182 | No
14/03/2024 | 07:52 | YK24 | LONG RURAL | Weather |  | 3.00 | 381.0 | 0.008203 | 0.0000215 | No
14/03/2024 | 08:01 | MTB17 | SHORT RURAL | Weather |  | 223.00 | 274.8 | 0.431205 | 0.0015689 | No
14/03/2024 | 08:01 | NL234E | URBAN | Unknown | Unknown | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
14/03/2024 | 08:06 | VH22 | SHORT RURAL | Weather |  | 1,585.00 | 240.8 | 2.685025 | 0.0111513 | No
14/03/2024 | 08:25 | BM13 | SHORT RURAL | Network business | Switching and protection error | 1,558.00 | 6.0 | 0.065768 | 0.0109613 | No
14/03/2024 | 08:45 | VH22 | SHORT RURAL | Weather |  | 822.00 | 93.3 | 0.539495 | 0.0057832 | No
14/03/2024 | 08:49 | BT04 | LONG RURAL | Asset failure | LV | 5.00 | 398.0 | 0.014281 | 0.0000359 | No
14/03/2024 | 08:51 | M21 | LONG RURAL | Weather |  | 69.33 | 209.3 | 0.104157 | 0.0004976 | No
14/03/2024 | 08:52 | MB72 | LONG RURAL | Animal | Animal impact | 2.00 | 864.0 | 0.012401 | 0.0000144 | No
14/03/2024 | 09:12 | MB32 | LONG RURAL | Weather |  | 697.00 | 381.9 | 1.910461 | 0.0050019 | No
14/03/2024 | 09:20 | SB23 | LONG RURAL | Planned |  | 7.00 | 281.3 | 0.014130 | 0.0000502 | No
14/03/2024 | 09:22 | AP125D | URBAN | Planned |  | 264.00 | 156.8 | 0.063839 | 0.0004070 | No
14/03/2024 | 09:24 | AP125D | URBAN | Planned |  | 94.00 | 186.0 | 0.026956 | 0.0001449 | No
14/03/2024 | 09:33 | AP132A | URBAN | Planned |  | 11.00 | 188.0 | 0.003188 | 0.0000170 | No
14/03/2024 | 09:38 | CN25 | LONG RURAL | Unknown | Unknown | 53.00 | 1,656.8 | 0.630139 | 0.0003803 | No
14/03/2024 | 10:00 | HH341G | URBAN | Planned |  | 138.00 | 150.0 | 0.031924 | 0.0002128 | No
14/03/2024 | 10:07 | HH341G | URBAN | Planned |  | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
14/03/2024 | 10:09 | VH33 | SHORT RURAL | Planned |  | 24.00 | 169.5 | 0.028620 | 0.0001689 | No
14/03/2024 | 10:51 | NL234C | URBAN | Weather |  | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
14/03/2024 | 10:52 | NL234C | URBAN | Weather |  | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
14/03/2024 | 11:50 | PL04 | URBAN | Overloads |  | 2.00 | 207.0 | 0.000638 | 0.0000031 | No
14/03/2024 | 12:08 | YK04 | SHORT RURAL | Weather |  | 13.00 | 36.0 | 0.003293 | 0.0000915 | No
14/03/2024 | 12:33 | NL234C | URBAN | Weather |  | 387.00 | 85.2 | 0.050862 | 0.0005967 | No
14/03/2024 | 12:34 | SD39300 | LONG RURAL | Asset failure | Subtransmission | 17.00 | 581.0 | 0.070881 | 0.0001220 | No
14/03/2024 | 14:06 | CBD27L | CBD | Asset failure | LV | 1.00 | 75.0 | 0.010836 | 0.0001445 | No
14/03/2024 | 14:26 | SA16 | URBAN | Asset failure | LV | 1.00 | 278.0 | 0.000429 | 0.0000015 | No
14/03/2024 | 14:27 | AP425C | URBAN | Other |  | 1.00 | 661.0 | 0.001019 | 0.0000015 | No
14/03/2024 | 15:31 | VH15 | SHORT RURAL | Weather |  | 154.67 | 52.8 | 0.057405 | 0.0010882 | No
14/03/2024 | 15:48 | YK03 | LONG RURAL | Asset failure | LV | 9.00 | 334.0 | 0.021572 | 0.0000646 | No
14/03/2024 | 16:03 | BM52 | URBAN | Asset failure | LV | 33.00 | 60.0 | 0.003053 | 0.0000509 | No
14/03/2024 | 16:28 | GA03 | LONG RURAL | Planned |  | 1.00 | 6.0 | 0.000043 | 0.0000072 | No
14/03/2024 | 18:30 | GA09 | LONG RURAL | Asset failure | LV | 1.00 | 475.0 | 0.003409 | 0.0000072 | No
14/03/2024 | 18:46 | ME116D | URBAN | Unknown | Unknown | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
14/03/2024 | 18:48 | PP03 | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
14/03/2024 | 19:21 | EL25 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 463.0 | 0.000714 | 0.0000015 | No
14/03/2024 | 20:17 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 220.0 | 0.001548 | 0.0000070 | No
14/03/2024 | 20:19 | EL03 | URBAN | Overloads |  | 1.00 | 405.0 | 0.000624 | 0.0000015 | No
14/03/2024 | 20:39 | CM05 | LONG RURAL | Third Party | Vehicle impact | 3.00 | 55.0 | 0.001184 | 0.0000215 | No
14/03/2024 | 20:59 | AP146A | URBAN | Asset failure | LV | 58.67 | 70.0 | 0.006331 | 0.0000904 | No
14/03/2024 | 21:09 | MV53 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 5.00 | 313.0 | 0.011011 | 0.0000352 | No
14/03/2024 | 22:00 | HH386A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 60.00 | 74.0 | 0.006845 | 0.0000925 | No
14/03/2024 | 23:37 | SD37501 | SHORT RURAL | Network business | Switching and protection error | 2,442.00 | 51.0 | 0.875876 | 0.0171807 | No
15/03/2024 | 00:17 | SA31 | URBAN | Asset failure | LV | 14.00 | 38.0 | 0.000820 | 0.0000216 | No
15/03/2024 | 00:43 | HH432F | URBAN | Weather |  | 128.00 | 128.7 | 0.025389 | 0.0001973 | No
15/03/2024 | 00:49 | HH432F | URBAN | Asset failure | LV | 25.00 | 127.0 | 0.004895 | 0.0000385 | No
15/03/2024 | 03:10 | AP344D | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
15/03/2024 | 03:56 | HH341B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 820.00 | 65.0 | 0.082175 | 0.0012642 | No
15/03/2024 | 06:52 | YK17 | LONG RURAL | Asset failure | LV | 1.00 | 204.0 | 0.001464 | 0.0000072 | No
15/03/2024 | 07:05 | ST21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 5.00 | 178.0 | 0.006262 | 0.0000352 | No
15/03/2024 | 07:57 | CV18 | SHORT RURAL | Unknown | Unknown | 57.00 | 152.9 | 0.061328 | 0.0004010 | No
15/03/2024 | 08:38 | CL10 | LONG RURAL | Planned |  | 14.00 | 190.0 | 0.019089 | 0.0001005 | No
15/03/2024 | 08:45 | AP372B | URBAN | Planned |  | 137.00 | 174.1 | 0.036768 | 0.0002112 | No
15/03/2024 | 08:57 | HH341G | URBAN | Planned |  | 220.00 | 173.0 | 0.058679 | 0.0003392 | No
15/03/2024 | 09:05 | HH428B | URBAN | Asset failure | LV | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
15/03/2024 | 09:14 | ME200D | URBAN | Third Party | Unauthorised access | 1.00 | 52.0 | 0.000080 | 0.0000015 | No
15/03/2024 | 09:15 | VH22 | SHORT RURAL | Planned |  | 21.00 | 261.0 | 0.038562 | 0.0001477 | No
15/03/2024 | 09:15 | GA48 | SHORT RURAL | Planned |  | 1.00 | 172.0 | 0.001210 | 0.0000070 | No
15/03/2024 | 09:34 | GA53 | SHORT RURAL | Asset failure | LV | 1.00 | 337.0 | 0.002371 | 0.0000070 | No
15/03/2024 | 09:42 | CV29 | LONG RURAL | Unknown | Unknown | 36.00 | 349.3 | 0.090242 | 0.0002583 | No
15/03/2024 | 10:06 | NU34 | LONG RURAL | Asset failure | LV | 1.00 | 308.0 | 0.002210 | 0.0000072 | No
15/03/2024 | 10:58 | WK33 | SHORT RURAL | Asset failure | LV | 2.00 | 394.0 | 0.005544 | 0.0000141 | No
15/03/2024 | 12:27 | MI12 | LONG RURAL | Weather |  | 151.00 | 62.0 | 0.067185 | 0.0010836 | No
15/03/2024 | 12:53 | AP351D | URBAN | Planned |  | 81.00 | 53.0 | 0.006619 | 0.0001249 | No
15/03/2024 | 13:42 | MB23 | SHORT RURAL | Asset failure | LV | 1.00 | 1,361.0 | 0.009575 | 0.0000070 | No
15/03/2024 | 14:10 | NL210C | URBAN | Planned |  | 962.00 | 48.6 | 0.072045 | 0.0014832 | No
15/03/2024 | 15:40 | NA02 | LONG RURAL | Weather |  | 10.00 | 35.0 | 0.002512 | 0.0000718 | No
15/03/2024 | 15:58 | BU13 | LONG RURAL | Asset failure | HV | 4.00 | 175.0 | 0.005023 | 0.0000287 | No
15/03/2024 | 16:27 | HH177C | URBAN | Asset failure | LV | 23.33 | 88.0 | 0.003166 | 0.0000360 | No
15/03/2024 | 17:23 | BU08 | LONG RURAL | Unknown | Unknown | 2.00 | 1,069.0 | 0.015343 | 0.0000144 | No
15/03/2024 | 17:42 | SD34201 | SHORT RURAL | Third Party | Vehicle impact | 44.67 | 87.0 | 0.027340 | 0.0003143 | No
15/03/2024 | 17:47 | YK04 | SHORT RURAL | Weather |  | 177.00 | 123.0 | 0.153170 | 0.0012453 | No
15/03/2024 | 18:03 | HH496F | URBAN | Asset failure | LV | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
15/03/2024 | 18:12 | WK41 | SHORT RURAL | Asset failure | LV | 2.00 | 69.0 | 0.000971 | 0.0000141 | No
15/03/2024 | 18:45 | SM374E | URBAN | Asset failure | LV | 1.00 | 268.0 | 0.000413 | 0.0000015 | No
15/03/2024 | 19:01 | NL234C | URBAN | Asset failure | LV | 10.33 | 19.0 | 0.000303 | 0.0000159 | No
15/03/2024 | 20:59 | NL210C | URBAN | Planned |  | 857.00 | 3.0 | 0.003964 | 0.0013213 | No
15/03/2024 | 21:08 | AP372F | URBAN | Asset failure | LV | 19.33 | 107.0 | 0.003189 | 0.0000298 | No
15/03/2024 | 21:37 | MV42 | SHORT RURAL | Asset failure | HV | 2.67 | 38.0 | 0.000713 | 0.0000188 | No
15/03/2024 | 22:05 | MT01 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 148.0 | 0.001062 | 0.0000072 | No
15/03/2024 | 22:51 | GA800A | SHORT RURAL | Asset failure | HV | 43.00 | 161.6 | 0.048883 | 0.0003025 | No
16/03/2024 | 00:52 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 46.00 | 52.0 | 0.003688 | 0.0000709 | No
16/03/2024 | 01:51 | SD53100 | LONG RURAL | Weather |  | 1,135.00 | 515.5 | 4.198885 | 0.0081451 | No
16/03/2024 | 06:05 | CN33 | LONG RURAL | Weather |  | 8.00 | 422.0 | 0.024227 | 0.0000574 | No
16/03/2024 | 06:21 | SD55100 | LONG RURAL | Asset failure | Subtransmission | 372.00 | 282.0 | 0.752826 | 0.0026696 | No
16/03/2024 | 07:33 | VH12 | SHORT RURAL | Unknown | Unknown | 1.00 | 269.0 | 0.001893 | 0.0000070 | No
16/03/2024 | 07:50 | AP425D | URBAN | Asset failure | LV | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
16/03/2024 | 08:58 | CV18 | SHORT RURAL | Unknown | Unknown | 29.00 | 218.0 | 0.044478 | 0.0002040 | No
16/03/2024 | 09:06 | PA17 | LONG RURAL | Unknown | Unknown | 10.00 | 474.0 | 0.034016 | 0.0000718 | No
16/03/2024 | 09:17 | AP365D2 | URBAN | Planned |  | 3.00 | 380.7 | 0.001761 | 0.0000046 | No
16/03/2024 | 09:24 | HH130A | URBAN | Overloads |  | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
16/03/2024 | 09:33 | G09 | LONG RURAL | Unknown | Unknown | 48.00 | 339.5 | 0.116945 | 0.0003445 | No
16/03/2024 | 09:40 | BM13 | SHORT RURAL | Unknown | Unknown | 1.00 | 219.0 | 0.001541 | 0.0000070 | No
16/03/2024 | 09:57 | WHY17 | SHORT RURAL | Unknown | Unknown | 52.00 | 141.0 | 0.051584 | 0.0003658 | No
16/03/2024 | 10:01 | HH341G | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
16/03/2024 | 10:32 | CV753A | LONG RURAL | Unknown | Unknown | 1.00 | 2,664.0 | 0.019118 | 0.0000072 | No
16/03/2024 | 10:41 | SM349D | URBAN | Overloads |  | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
16/03/2024 | 11:13 | CV17 | LONG RURAL | Unknown | Unknown | 26.00 | 163.0 | 0.030413 | 0.0001866 | No
16/03/2024 | 13:09 | WHY10 | URBAN | Asset failure | LV | 30.00 | 654.0 | 0.030249 | 0.0000463 | No
16/03/2024 | 14:13 | ST34 | LONG RURAL | Weather |  | 49.33 | 298.0 | 0.105502 | 0.0003540 | No
16/03/2024 | 16:14 | EL01N | URBAN | Asset failure | LV | 1.00 | 197.0 | 0.000304 | 0.0000015 | No
16/03/2024 | 16:17 | M11 | LONG RURAL | Unknown | Unknown | 763.00 | 170.8 | 0.935148 | 0.0054755 | No
16/03/2024 | 16:27 | VH15 | SHORT RURAL | Weather |  | 1,302.00 | 122.6 | 1.123300 | 0.0091602 | No
16/03/2024 | 16:59 | M21 | LONG RURAL | Unknown | Unknown | 92.00 | 309.0 | 0.204009 | 0.0006602 | No
16/03/2024 | 17:20 | ST44 | LONG RURAL | Asset failure | LV | 2.00 | 330.0 | 0.004736 | 0.0000144 | No
16/03/2024 | 17:51 | PA17 | LONG RURAL | Weather |  | 10.00 | 1,138.4 | 0.081695 | 0.0000718 | No
16/03/2024 | 18:20 | M21 | LONG RURAL | Weather |  | 3.00 | 319.0 | 0.006868 | 0.0000215 | No
16/03/2024 | 20:37 | AP425A | URBAN | Overloads |  | 28.67 | 194.0 | 0.008574 | 0.0000442 | No
16/03/2024 | 22:12 | YK28 | LONG RURAL | Unknown | Unknown | 58.00 | 345.9 | 0.143979 | 0.0004162 | No
16/03/2024 | 22:31 | NL111Q | URBAN | Unknown | Unknown | 9.00 | 87.0 | 0.001207 | 0.0000139 | No
16/03/2024 | 23:33 | BS0356 | LONG RURAL | Unknown | Unknown | 1.00 | 15.0 | 0.000108 | 0.0000072 | No
17/03/2024 | 01:29 | GA45 | SHORT RURAL | Unknown | Unknown | 58.00 | 246.0 | 0.100382 | 0.0004081 | No
17/03/2024 | 03:38 | SD56301 | URBAN | Unknown | Unknown | 130.00 | 326.0 | 0.065340 | 0.0002004 | No
17/03/2024 | 04:05 | WHY17 | SHORT RURAL | Weather |  | 52.00 | 422.0 | 0.154387 | 0.0003658 | No
17/03/2024 | 06:16 | MG52 | URBAN | Planned |  | 6.00 | 113.0 | 0.001045 | 0.0000093 | No
17/03/2024 | 06:58 | SM216B | URBAN | Asset failure | LV | 69.00 | 304.0 | 0.032340 | 0.0001064 | No
17/03/2024 | 07:11 | SD35100 | LONG RURAL | Planned |  | 2,018.00 | 190.0 | 2.750845 | 0.0144818 | No
17/03/2024 | 07:39 | NL111C | URBAN | Planned |  | 206.00 | 445.0 | 0.141333 | 0.0003176 | No
17/03/2024 | 08:06 | HH386D | URBAN | Asset failure | LV | 1.00 | 230.0 | 0.000355 | 0.0000015 | No
17/03/2024 | 08:14 | BM53 | SHORT RURAL | Planned |  | 15.00 | 394.2 | 0.041601 | 0.0001055 | No
17/03/2024 | 08:18 | W03 | LONG RURAL | Planned |  | 391.00 | 391.5 | 1.098445 | 0.0028059 | No
17/03/2024 | 08:20 | AP351E | URBAN | Planned |  | 5.00 | 282.4 | 0.002177 | 0.0000077 | No
17/03/2024 | 08:24 | NA02 | LONG RURAL | Unknown | Unknown | 8.00 | 170.0 | 0.009760 | 0.0000574 | No
17/03/2024 | 08:29 | HH121H | URBAN | Planned |  | 191.00 | 182.2 | 0.053639 | 0.0002945 | No
17/03/2024 | 09:51 | WK73 | SHORT RURAL | Weather |  | 14.00 | 401.1 | 0.039504 | 0.0000985 | No
17/03/2024 | 10:54 | SD59100 | LONG RURAL | Weather |  | 9.00 | 433.0 | 0.027966 | 0.0000646 | No
17/03/2024 | 11:46 | HH107D | URBAN | Unknown | Unknown | 1.00 | 469.0 | 0.000723 | 0.0000015 | No
17/03/2024 | 12:19 | HH130D | URBAN | Asset failure | LV | 3.00 | 235.0 | 0.001087 | 0.0000046 | No
17/03/2024 | 14:21 | MG44 | URBAN | Planned |  | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
17/03/2024 | 14:56 | EL09 | URBAN | Asset failure | LV | 1.00 | 386.0 | 0.000595 | 0.0000015 | No
17/03/2024 | 15:03 | R03 | LONG RURAL | Unknown | Unknown | 108.00 | 117.3 | 0.090910 | 0.0007750 | No
17/03/2024 | 15:32 | AP372F | URBAN | Third Party | Other | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
17/03/2024 | 16:28 | SA744C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 891.00 | 116.7 | 0.160267 | 0.0013737 | No
17/03/2024 | 17:01 | GA15 | SHORT RURAL | Asset failure | LV | 1.00 | 310.0 | 0.002181 | 0.0000070 | No
17/03/2024 | 17:12 | SA42 | URBAN | Overloads |  | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
17/03/2024 | 17:35 | HH121F | URBAN | Asset failure | HV | 69.00 | 523.0 | 0.055637 | 0.0001064 | No
17/03/2024 | 17:35 | HH121F | URBAN | Planned |  | 662.00 | 4.0 | 0.004083 | 0.0010206 | No
17/03/2024 | 18:29 | M81 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 255.00 | 179.9 | 0.329178 | 0.0018300 | No
17/03/2024 | 18:33 | BU13 | LONG RURAL | Overloads |  | 2.00 | 117.0 | 0.001679 | 0.0000144 | No
17/03/2024 | 18:38 | BU03 | LONG RURAL | Planned |  | 2.00 | 35.0 | 0.000502 | 0.0000144 | No
17/03/2024 | 18:54 | EL01R | URBAN | Overloads |  | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
17/03/2024 | 20:35 | ST15 | SHORT RURAL | Weather |  | 9.00 | 23.0 | 0.001456 | 0.0000633 | No
17/03/2024 | 21:07 | KI43 | LONG RURAL | Unknown | Unknown | 74.00 | 328.0 | 0.174184 | 0.0005310 | No
17/03/2024 | 21:27 | AP146B | URBAN | Asset failure | LV | 36.67 | 74.0 | 0.004183 | 0.0000565 | No
17/03/2024 | 22:05 | HH121D | URBAN | Planned |  | 148.00 | 240.4 | 0.054843 | 0.0002282 | No
17/03/2024 | 22:58 | MTB54 | LONG RURAL | Overloads |  | 1.00 | 89.0 | 0.000639 | 0.0000072 | No
17/03/2024 | 23:40 | SB17 | LONG RURAL | Unknown | Unknown | 56.00 | 213.9 | 0.085951 | 0.0004019 | No
18/03/2024 | 06:00 | WHY17 | SHORT RURAL | Unknown | Unknown | 52.00 | 168.0 | 0.061462 | 0.0003658 | No
18/03/2024 | 07:47 | CV24 | LONG RURAL | Unknown | Unknown | 2.00 | 751.0 | 0.010779 | 0.0000144 | No
18/03/2024 | 08:42 | MT11 | LONG RURAL | Planned |  | 2.00 | 36.0 | 0.000517 | 0.0000144 | No
18/03/2024 | 08:48 | VH16 | SHORT RURAL | Planned |  | 175.00 | 359.7 | 0.442884 | 0.0012312 | No
18/03/2024 | 08:50 | SA17 | URBAN | Asset failure | LV | 1.00 | 150.0 | 0.000231 | 0.0000015 | No
18/03/2024 | 09:08 | R27 | LONG RURAL | Planned |  | 2.00 | 166.0 | 0.002383 | 0.0000144 | No
18/03/2024 | 09:46 | SD35300 | LONG RURAL | Planned |  | 106.00 | 217.0 | 0.165070 | 0.0007607 | No
18/03/2024 | 09:46 | BM41 | SHORT RURAL | Planned |  | 4.00 | 174.0 | 0.004897 | 0.0000281 | No
18/03/2024 | 10:49 | KI13 | LONG RURAL | Weather |  | 1.00 | 70.0 | 0.000502 | 0.0000072 | No
18/03/2024 | 10:57 | MG03 | SHORT RURAL | Asset failure | LV | 1.00 | 90.0 | 0.000633 | 0.0000070 | No
18/03/2024 | 10:59 | KA14 | LONG RURAL | Planned |  | 2.00 | 34.0 | 0.000488 | 0.0000144 | No
18/03/2024 | 11:32 | CM15 | LONG RURAL | Asset failure | HV | 2.00 | 75.0 | 0.001076 | 0.0000144 | No
18/03/2024 | 11:33 | GU43 | LONG RURAL | Unknown | Unknown | 123.00 | 45.0 | 0.039721 | 0.0008827 | No
18/03/2024 | 12:14 | MI30 | LONG RURAL | Planned |  | 1.00 | 19.0 | 0.000136 | 0.0000072 | No
18/03/2024 | 13:35 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 100.0 | 0.000704 | 0.0000070 | No
18/03/2024 | 14:10 | SD39300 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 282.0 | 0.002024 | 0.0000072 | No
18/03/2024 | 14:22 | SM402D | URBAN | Asset failure | LV | 15.00 | 149.0 | 0.003446 | 0.0000231 | No
18/03/2024 | 14:25 | VH45 | SHORT RURAL | Asset failure | HV | 2.00 | 161.0 | 0.002265 | 0.0000141 | No
18/03/2024 | 14:33 | SA11 | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 20.33 | 125.0 | 0.003919 | 0.0000313 | No
18/03/2024 | 14:38 | HH107A | URBAN | Asset failure | LV | 4.67 | 157.0 | 0.001130 | 0.0000072 | No
18/03/2024 | 14:54 | SA20 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 659.0 | 0.001016 | 0.0000015 | No
18/03/2024 | 15:22 | AP132E | URBAN | Asset failure | LV | 1.00 | 113.0 | 0.000174 | 0.0000015 | No
18/03/2024 | 15:23 | M21 | LONG RURAL | Asset failure | HV | 2.00 | 109.0 | 0.001564 | 0.0000144 | No
18/03/2024 | 15:33 | SM172A | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
18/03/2024 | 16:09 | HH432D | URBAN | Overloads |  | 1.00 | 522.0 | 0.000805 | 0.0000015 | No
18/03/2024 | 17:36 | HH341J | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
18/03/2024 | 18:14 | MV63 | SHORT RURAL | Asset failure | HV | 1.00 | 18.0 | 0.000127 | 0.0000070 | No
18/03/2024 | 19:48 | WHY02 | URBAN | Overloads |  | 4.00 | 114.0 | 0.000703 | 0.0000062 | No
18/03/2024 | 19:53 | VH33 | SHORT RURAL | Planned |  | 11.00 | 102.3 | 0.007915 | 0.0000774 | No
18/03/2024 | 20:01 | SM126D | URBAN | Overloads |  | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
18/03/2024 | 22:04 | CN25 | LONG RURAL | Weather |  | 53.00 | 543.0 | 0.206528 | 0.0003803 | No
18/03/2024 | 22:22 | HH148D | URBAN | Unknown | Unknown | 15.00 | 221.0 | 0.005111 | 0.0000231 | No
18/03/2024 | 22:40 | SA31 | URBAN | Asset failure | HV | 51.00 | 124.7 | 0.009806 | 0.0000786 | No
19/03/2024 | 01:03 | SM126D | URBAN | Asset failure | LV | 19.33 | 132.0 | 0.003935 | 0.0000298 | No
19/03/2024 | 02:10 | MT01 | LONG RURAL | Asset failure | HV | 544.00 | 482.5 | 1.883528 | 0.0039039 | No
19/03/2024 | 05:03 | MI23 | LONG RURAL | Unknown | Unknown | 60.00 | 837.0 | 0.360395 | 0.0004306 | No
19/03/2024 | 06:03 | MG17 | LONG RURAL | Unknown | Unknown | 1.00 | 248.0 | 0.001780 | 0.0000072 | No
19/03/2024 | 06:53 | M43 | LONG RURAL | Unknown | Unknown | 35.00 | 743.6 | 0.186764 | 0.0002512 | No
19/03/2024 | 08:01 | NA02 | LONG RURAL | Weather |  | 2.00 | 286.0 | 0.004105 | 0.0000144 | No
19/03/2024 | 08:15 | NA02 | LONG RURAL | Weather |  | 8.00 | 246.0 | 0.014123 | 0.0000574 | No
19/03/2024 | 08:16 | MG17 | LONG RURAL | Unknown | Unknown | 1.00 | 411.0 | 0.002949 | 0.0000072 | No
19/03/2024 | 08:23 | MG32 | LONG RURAL | Weather |  | 175.67 | 85.0 | 0.107155 | 0.0012606 | No
19/03/2024 | 08:47 | YK28 | LONG RURAL | Weather |  | 2.00 | 495.0 | 0.007105 | 0.0000144 | No
19/03/2024 | 08:53 | CN41 | LONG RURAL | Planned |  | 19.00 | 260.0 | 0.035451 | 0.0001364 | No
19/03/2024 | 08:56 | R25 | LONG RURAL | Planned |  | 26.00 | 256.0 | 0.047766 | 0.0001866 | No
19/03/2024 | 09:05 | VH34 | SHORT RURAL | Planned |  | 5.00 | 125.2 | 0.004404 | 0.0000352 | No
19/03/2024 | 09:09 | MG17 | LONG RURAL | Unknown | Unknown | 1.00 | 352.0 | 0.002526 | 0.0000072 | No
19/03/2024 | 09:12 | KI52 | LONG RURAL | Planned |  | 2.00 | 131.0 | 0.001880 | 0.0000144 | No
19/03/2024 | 09:19 | CD04 | SHORT RURAL | Planned |  | 193.00 | 319.0 | 0.433154 | 0.0013578 | No
19/03/2024 | 09:32 | G31 | LONG RURAL | Asset failure | LV | 1.00 | 571.0 | 0.004098 | 0.0000072 | No
19/03/2024 | 09:37 | EL15 | URBAN | Planned |  | 2.00 | 297.0 | 0.000916 | 0.0000031 | No
19/03/2024 | 09:42 | SD38200 | LONG RURAL | Planned |  | 68.00 | 325.5 | 0.158827 | 0.0004880 | No
19/03/2024 | 09:45 | AP355A | URBAN | Planned |  | 144.00 | 99.0 | 0.021979 | 0.0002220 | No
19/03/2024 | 10:08 | MG32 | LONG RURAL | Asset failure | LV | 10.00 | 384.0 | 0.027557 | 0.0000718 | No
19/03/2024 | 10:12 | CBD412E | CBD | Asset failure | LV | 1.00 | 283.0 | 0.040887 | 0.0001445 | No
19/03/2024 | 10:13 | EL10 | URBAN | Asset failure | LV | 71.00 | 24.0 | 0.002629 | 0.0001095 | No
19/03/2024 | 10:41 | HH130F | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
19/03/2024 | 10:42 | ST13 | SHORT RURAL | Planned |  | 7.00 | 73.0 | 0.003595 | 0.0000492 | No
19/03/2024 | 11:13 | NL234A | URBAN | Planned |  | 113.00 | 180.0 | 0.031359 | 0.0001742 | No
19/03/2024 | 12:08 | SM411D | URBAN | Asset failure | LV | 1.00 | 362.0 | 0.000558 | 0.0000015 | No
19/03/2024 | 12:21 | MG10 | LONG RURAL | Unknown | Unknown | 130.00 | 97.0 | 0.090494 | 0.0009329 | No
19/03/2024 | 13:08 | HH130A | URBAN | Asset failure | LV | 18.00 | 63.0 | 0.001748 | 0.0000278 | No
19/03/2024 | 13:21 | AP372B | URBAN | Overloads |  | 1.00 | 377.0 | 0.000581 | 0.0000015 | No
19/03/2024 | 14:03 | NL115C | URBAN | Asset failure | LV | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
19/03/2024 | 14:13 | SM126C | URBAN | Unknown | Unknown | 1.00 | 480.0 | 0.000740 | 0.0000015 | No
19/03/2024 | 14:28 | MG11 | SHORT RURAL | Weather |  | 32.00 | 33.6 | 0.007561 | 0.0002251 | No
19/03/2024 | 14:33 | SD54300 | LONG RURAL | Asset failure | Subtransmission | 1,031.00 | 129.7 | 0.959267 | 0.0073988 | No
19/03/2024 | 14:46 | PA07 | LONG RURAL | Asset failure | LV | 1.00 | 220.0 | 0.001579 | 0.0000072 | No
19/03/2024 | 15:12 | GA22 | SHORT RURAL | Asset failure | LV | 9.00 | 33.0 | 0.002090 | 0.0000633 | No
19/03/2024 | 15:49 | SM349D | URBAN | Overloads |  | 1.00 | 277.0 | 0.000427 | 0.0000015 | No
19/03/2024 | 16:10 | CV31 | LONG RURAL | Asset failure | HV | 1.00 | 75.0 | 0.000538 | 0.0000072 | No
19/03/2024 | 16:14 | MG10 | LONG RURAL | Unknown | Unknown | 130.00 | 338.0 | 0.315328 | 0.0009329 | No
19/03/2024 | 16:37 | NA20 | LONG RURAL | Unknown | Unknown | 63.00 | 212.8 | 0.096220 | 0.0004521 | No
19/03/2024 | 16:45 | VH71 | SHORT RURAL | Asset failure | LV | 7.00 | 178.0 | 0.008766 | 0.0000492 | No
19/03/2024 | 16:46 | MG10 | LONG RURAL | Weather |  | 263.00 | 235.4 | 0.444380 | 0.0018874 | No
19/03/2024 | 16:47 | MG21 | LONG RURAL | Unknown | Unknown | 1.00 | 1,243.0 | 0.008920 | 0.0000072 | No
19/03/2024 | 16:49 | MG17 | LONG RURAL | Unknown | Unknown | 1.00 | 348.0 | 0.002497 | 0.0000072 | No
19/03/2024 | 16:54 | G23 | LONG RURAL | Asset failure | HV | 1.00 | 195.0 | 0.001399 | 0.0000072 | No
19/03/2024 | 17:20 | ME427F | URBAN | Asset failure | LV | 3.00 | 194.0 | 0.000897 | 0.0000046 | No
19/03/2024 | 18:03 | MV61 | URBAN | Third Party | Unauthorised access | 12.00 | 55.0 | 0.001018 | 0.0000185 | No
19/03/2024 | 18:32 | HH145B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 24.00 | 19.0 | 0.000703 | 0.0000370 | No
19/03/2024 | 20:25 | AP149A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
19/03/2024 | 21:25 | MG37 | LONG RURAL | Asset failure | LV | 10.00 | 864.0 | 0.062003 | 0.0000718 | No
19/03/2024 | 21:48 | WHY07 | URBAN | Asset failure | LV | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
19/03/2024 | 23:42 | KI41 | LONG RURAL | Asset failure | HV | 94.00 | 667.1 | 0.449999 | 0.0006746 | No
20/03/2024 | 00:21 | MG10 | LONG RURAL | Unknown | Unknown | 130.00 | 202.0 | 0.188450 | 0.0009329 | No
20/03/2024 | 00:41 | M43 | LONG RURAL | Unknown | Unknown | 35.00 | 181.1 | 0.045498 | 0.0002512 | No
20/03/2024 | 01:33 | AP372D | URBAN | Asset failure | LV | 67.00 | 150.0 | 0.015495 | 0.0001033 | No
20/03/2024 | 05:55 | R03 | LONG RURAL | Asset failure | HV | 108.00 | 328.1 | 0.254300 | 0.0007750 | No
20/03/2024 | 06:41 | GU43 | LONG RURAL | Animal | Animal impact | 2.00 | 492.0 | 0.007062 | 0.0000144 | No
20/03/2024 | 07:46 | VH15 | SHORT RURAL | Asset failure | LV | 22.00 | 129.0 | 0.019967 | 0.0001548 | No
20/03/2024 | 07:55 | VH21 | SHORT RURAL | Asset failure | LV | 20.33 | 110.0 | 0.015736 | 0.0001431 | No
20/03/2024 | 08:49 | LX31 | SHORT RURAL | Planned |  | 7.00 | 155.7 | 0.007669 | 0.0000492 | No
20/03/2024 | 08:53 | MG10 | LONG RURAL | Weather |  | 130.00 | 73.4 | 0.068477 | 0.0009329 | No
20/03/2024 | 09:00 | WHY04 | URBAN | Unknown | Unknown | 1,101.00 | 96.4 | 0.163603 | 0.0016975 | No
20/03/2024 | 09:09 | HH341J | URBAN | Planned |  | 144.00 | 84.6 | 0.018788 | 0.0002220 | No
20/03/2024 | 09:10 | HH121G | URBAN | Planned |  | 117.00 | 374.0 | 0.067464 | 0.0001804 | No
20/03/2024 | 09:33 | SM126E | URBAN | Third Party | Vehicle impact | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
20/03/2024 | 09:35 | MV31 | SHORT RURAL | Planned |  | 22.00 | 244.0 | 0.037767 | 0.0001548 | No
20/03/2024 | 09:35 | MT20 | LONG RURAL | Planned |  | 2.00 | 227.0 | 0.003258 | 0.0000144 | No
20/03/2024 | 09:59 | R35 | LONG RURAL | Planned |  | 69.00 | 168.0 | 0.083188 | 0.0004952 | No
20/03/2024 | 10:11 | ME116B | URBAN | Planned |  | 95.00 | 136.0 | 0.019919 | 0.0001465 | No
20/03/2024 | 10:19 | CV29 | LONG RURAL | Planned |  | 8.00 | 220.0 | 0.012630 | 0.0000574 | No
20/03/2024 | 10:30 | MI30 | LONG RURAL | Planned |  | 1.00 | 205.0 | 0.001471 | 0.0000072 | No
20/03/2024 | 10:57 | HH145E | URBAN | Asset failure | LV | 12.00 | 937.0 | 0.017335 | 0.0000185 | No
20/03/2024 | 11:06 | SG03 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 52.00 | 89.1 | 0.032588 | 0.0003658 | No
20/03/2024 | 11:54 | NA20 | LONG RURAL | Asset failure | HV | 19.00 | 60.0 | 0.008181 | 0.0001364 | No
20/03/2024 | 12:01 | G23 | LONG RURAL | Planned |  | 2.00 | 246.0 | 0.003531 | 0.0000144 | No
20/03/2024 | 12:09 | ME116D | URBAN | Asset failure | LV | 1.00 | 146.0 | 0.000225 | 0.0000015 | No
20/03/2024 | 12:34 | MG10 | LONG RURAL | Asset failure | LV | 1.00 | 100.0 | 0.000718 | 0.0000072 | No
20/03/2024 | 12:58 | SA36 | URBAN | Asset failure | HV | 31.00 | 81.0 | 0.003871 | 0.0000478 | No
20/03/2024 | 13:11 | SD32302 | LONG RURAL | Asset failure | Subtransmission | 4.00 | 304.0 | 0.008726 | 0.0000287 | No
20/03/2024 | 13:51 | SM374A | URBAN | Unknown | Unknown | 1.00 | 49.0 | 0.000076 | 0.0000015 | No
20/03/2024 | 14:22 | HH102B | URBAN | Unknown | Unknown | 86.00 | 226.0 | 0.029966 | 0.0001326 | No
20/03/2024 | 14:50 | AP372D | URBAN | Third Party | Other | 1.00 | 264.0 | 0.000407 | 0.0000015 | No
20/03/2024 | 15:11 | SM126D | URBAN | Asset failure | LV | 1.00 | 57.0 | 0.000088 | 0.0000015 | No
20/03/2024 | 17:20 | EL260A | URBAN | Third Party | Unauthorised access | 1.00 | 246.0 | 0.000379 | 0.0000015 | No
20/03/2024 | 19:47 | CL09 | LONG RURAL | Animal | Animal impact | 22.00 | 142.0 | 0.022419 | 0.0001579 | No
20/03/2024 | 21:08 | MI02 | SHORT RURAL | Asset failure | HV | 224.00 | 86.0 | 0.135532 | 0.0015759 | No
20/03/2024 | 23:35 | AP344D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 28.00 | 438.0 | 0.018908 | 0.0000432 | No
21/03/2024 | 03:01 | SD59100 | LONG RURAL | Planned |  | 334.00 | 317.0 | 0.759815 | 0.0023969 | No
21/03/2024 | 07:36 | AP344D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 354.0 | 0.000546 | 0.0000015 | No
21/03/2024 | 07:43 | SM216C | URBAN | Weather |  | 1.00 | 192.0 | 0.000296 | 0.0000015 | No
21/03/2024 | 07:49 | LC03 | LONG RURAL | Unknown | Unknown | 2.00 | 3,600.0 | 0.051670 | 0.0000144 | No
21/03/2024 | 08:15 | HH121G | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 400.0 | 0.000617 | 0.0000015 | No
21/03/2024 | 08:17 | VH16 | SHORT RURAL | Asset failure | LV | 118.00 | 351.0 | 0.291396 | 0.0008302 | No
21/03/2024 | 08:33 | CN32 | LONG RURAL | Planned |  | 20.00 | 399.1 | 0.057281 | 0.0001435 | No
21/03/2024 | 08:37 | EL25 | URBAN | Planned |  | 7.00 | 38.1 | 0.000412 | 0.0000108 | No
21/03/2024 | 08:38 | PA18 | LONG RURAL | Planned |  | 63.00 | 232.0 | 0.104889 | 0.0004521 | No
21/03/2024 | 08:51 | GA53 | SHORT RURAL | Planned |  | 2.00 | 228.5 | 0.003215 | 0.0000141 | No
21/03/2024 | 09:03 | GU43 | LONG RURAL | Planned |  | 60.00 | 119.2 | 0.051339 | 0.0004306 | No
21/03/2024 | 09:20 | PL20 | LONG RURAL | Planned |  | 39.00 | 304.0 | 0.085083 | 0.0002799 | No
21/03/2024 | 09:31 | EL15 | URBAN | Planned |  | 2.00 | 335.0 | 0.001033 | 0.0000031 | No
21/03/2024 | 09:55 | ST44 | LONG RURAL | Planned |  | 6.00 | 259.0 | 0.011152 | 0.0000431 | No
21/03/2024 | 10:27 | ME116D | URBAN | Asset failure | LV | 2.00 | 183.0 | 0.000564 | 0.0000031 | No
21/03/2024 | 10:28 | AP365D2 | URBAN | Third Party | Vehicle impact | 12.00 | 53.3 | 0.000987 | 0.0000185 | No
21/03/2024 | 13:09 | G02 | LONG RURAL | Asset failure | LV | 21.00 | 84.0 | 0.012659 | 0.0001507 | No
21/03/2024 | 14:34 | MG13 | SHORT RURAL | Planned |  | 116.00 | 28.0 | 0.022851 | 0.0008161 | No
21/03/2024 | 14:34 | MG13 | SHORT RURAL | Asset failure | HV | 118.00 | 28.0 | 0.023245 | 0.0008302 | No
21/03/2024 | 14:41 | LX41 | SHORT RURAL | Third Party | Vehicle impact | 11.00 | 198.0 | 0.015323 | 0.0000774 | No
21/03/2024 | 14:53 | NA02 | LONG RURAL | Weather |  | 78.33 | 4.0 | 0.002249 | 0.0005621 | No
21/03/2024 | 16:43 | ME347F | URBAN | Third Party | Vehicle impact | 8.00 | 337.0 | 0.004157 | 0.0000123 | No
21/03/2024 | 17:16 | MG19 | LONG RURAL | Asset failure | HV | 2.00 | 35.0 | 0.000502 | 0.0000144 | No
21/03/2024 | 17:42 | CM15 | LONG RURAL | Weather |  | 19.00 | 54.0 | 0.007363 | 0.0001364 | No
21/03/2024 | 17:43 | PL06 | URBAN | Unknown | Unknown | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
21/03/2024 | 21:46 | AP372A | URBAN | Planned |  | 4.00 | 67.0 | 0.000413 | 0.0000062 | No
21/03/2024 | 22:07 | AP372A | URBAN | Planned |  | 5.00 | 385.8 | 0.002974 | 0.0000077 | No
21/03/2024 | 23:12 | NL234C | URBAN | Asset failure | LV | 58.00 | 120.0 | 0.010731 | 0.0000894 | No
21/03/2024 | 23:37 | PP18 | LONG RURAL | Unknown | Unknown | 1.00 | 672.0 | 0.004822 | 0.0000072 | No
22/03/2024 | 01:08 | ME200C | URBAN | Asset failure | LV | 14.00 | 22.0 | 0.000475 | 0.0000216 | No
22/03/2024 | 01:23 | ME200D | URBAN | Planned |  | 1.00 | 1.0 | 0.000002 | 0.0000015 | No
22/03/2024 | 04:06 | GA45 | SHORT RURAL | Asset failure | HV | 1.00 | 127.0 | 0.000894 | 0.0000070 | No
22/03/2024 | 05:16 | MG09 | SHORT RURAL | Animal | Animal nesting/burrowing, etc and other | 13.00 | 208.0 | 0.019024 | 0.0000915 | No
22/03/2024 | 08:23 | MT19 | LONG RURAL | Planned |  | 1.00 | 26.0 | 0.000187 | 0.0000072 | No
22/03/2024 | 09:00 | SG04 | SHORT RURAL | Planned |  | 214.00 | 1.0 | 0.001506 | 0.0015056 | No
22/03/2024 | 09:22 | NU11 | LONG RURAL | Planned |  | 4.00 | 226.0 | 0.006487 | 0.0000287 | No
22/03/2024 | 09:38 | PL22 | LONG RURAL | Planned |  | 5.00 | 159.0 | 0.005705 | 0.0000359 | No
22/03/2024 | 09:39 | HH341H | URBAN | Asset failure | LV | 13.00 | 160.0 | 0.003207 | 0.0000200 | No
22/03/2024 | 09:41 | MI30 | LONG RURAL | Planned |  | 1.00 | 173.0 | 0.001242 | 0.0000072 | No
22/03/2024 | 10:09 | VH16 | SHORT RURAL | Overloads |  | 1.00 | 33.0 | 0.000232 | 0.0000070 | No
22/03/2024 | 10:43 | HH130A | URBAN | Asset failure | LV | 86.00 | 302.0 | 0.040042 | 0.0001326 | No
22/03/2024 | 11:06 | SG03 | SHORT RURAL | Planned |  | 40.00 | 63.0 | 0.017729 | 0.0002814 | No
22/03/2024 | 11:17 | MT18 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 7.0 | 0.000050 | 0.0000072 | No
22/03/2024 | 11:23 | LX41 | SHORT RURAL | Weather |  | 33.00 | 93.0 | 0.021592 | 0.0002322 | No
22/03/2024 | 11:30 | CM26 | LONG RURAL | Planned |  | 4.00 | 2.0 | 0.000057 | 0.0000287 | No
22/03/2024 | 11:37 | CM15 | LONG RURAL | Planned |  | 10.00 | 148.0 | 0.010621 | 0.0000718 | No
22/03/2024 | 12:30 | CM26 | LONG RURAL | Other |  | 17.00 | 89.0 | 0.010858 | 0.0001220 | No
22/03/2024 | 14:24 | EL260A | URBAN | Third Party | Other | 14.00 | 223.0 | 0.004813 | 0.0000216 | No
22/03/2024 | 16:16 | SM216F | URBAN | Asset failure | LV | 3.00 | 127.0 | 0.000587 | 0.0000046 | No
22/03/2024 | 16:19 | MB65 | LONG RURAL | Asset failure | HV | 1.00 | 11.0 | 0.000079 | 0.0000072 | No
22/03/2024 | 17:10 | SM216C | URBAN | Asset failure | LV | 1.00 | 508.0 | 0.000783 | 0.0000015 | No
22/03/2024 | 18:34 | SA35 | URBAN | Asset failure | LV | 1.00 | 81.0 | 0.000125 | 0.0000015 | No
22/03/2024 | 19:43 | SA17 | URBAN | Unknown | Unknown | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
22/03/2024 | 19:46 | CD15 | LONG RURAL | Asset failure | HV | 759.00 | 167.0 | 0.909621 | 0.0054468 | No
22/03/2024 | 21:31 | SM126C | URBAN | Asset failure | LV | 1.00 | 12,186.0 | 0.018788 | 0.0000015 | No
22/03/2024 | 23:18 | SM350B | URBAN | Third Party | Other | 49.00 | 150.0 | 0.011332 | 0.0000755 | No
23/03/2024 | 01:24 | HH386G | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 452.00 | 105.0 | 0.073172 | 0.0006969 | No
23/03/2024 | 04:30 | CBD367N | CBD | Vegetation | Blow-in/Fall-in - Other responsible party | 25.00 | 203.0 | 0.733223 | 0.0036119 | No
23/03/2024 | 07:24 | HH130A | URBAN | Asset failure | LV | 24.00 | 107.0 | 0.003959 | 0.0000370 | No
23/03/2024 | 08:03 | PA03 | URBAN | Planned |  | 1.00 | 347.0 | 0.000535 | 0.0000015 | No
23/03/2024 | 08:10 | BS0186 | SHORT RURAL | Planned |  | 1.00 | 297.0 | 0.002090 | 0.0000070 | No
23/03/2024 | 08:14 | NA02 | LONG RURAL | Weather |  | 8.00 | 272.0 | 0.015616 | 0.0000574 | No
23/03/2024 | 08:14 | PA25 | SHORT RURAL | Planned |  | 10.00 | 294.0 | 0.020684 | 0.0000704 | No
23/03/2024 | 09:35 | MG21 | LONG RURAL | Weather |  | 87.67 | 120.2 | 0.075603 | 0.0006291 | No
23/03/2024 | 10:37 | HH177D | URBAN | Asset failure | LV | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
23/03/2024 | 11:04 | SM172E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
23/03/2024 | 11:08 | LX25 | SHORT RURAL | Overloads |  | 7.00 | 95.0 | 0.004679 | 0.0000492 | No
23/03/2024 | 12:38 | SM350B | URBAN | Asset failure | LV | 1.00 | 220.0 | 0.000339 | 0.0000015 | No
23/03/2024 | 14:07 | GA02 | SHORT RURAL | Asset failure | LV | 31.33 | 470.0 | 0.103609 | 0.0002204 | No
23/03/2024 | 14:21 | G05 | LONG RURAL | Planned |  | 2.00 | 151.0 | 0.002167 | 0.0000144 | No
23/03/2024 | 14:43 | PA03 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,075.00 | 74.7 | 0.123827 | 0.0016574 | No
23/03/2024 | 16:09 | HH386F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 3.00 | 110.0 | 0.000509 | 0.0000046 | No
23/03/2024 | 16:13 | ST11 | SHORT RURAL | Asset failure | HV | 7.00 | 51.0 | 0.002512 | 0.0000492 | No
23/03/2024 | 16:38 | AP214A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
23/03/2024 | 16:38 | SA36 | URBAN | Third Party | Other | 7.67 | 161.3 | 0.001907 | 0.0000118 | No
23/03/2024 | 17:08 | SM349H | URBAN | Third Party | Other | 1,562.00 | 55.0 | 0.132452 | 0.0024082 | No
23/03/2024 | 17:40 | MG28 | LONG RURAL | Third Party | Vehicle impact | 2.00 | 136.0 | 0.001952 | 0.0000144 | No
23/03/2024 | 17:44 | PA03 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 22.0 | 0.000034 | 0.0000015 | No
23/03/2024 | 19:23 | SB01 | LONG RURAL | Asset failure | HV | 25.00 | 567.0 | 0.101732 | 0.0001794 | No
23/03/2024 | 21:19 | HH341K | URBAN | Planned |  | 931.00 | 3.0 | 0.004306 | 0.0014354 | No
23/03/2024 | 21:31 | HH429C | URBAN | Asset failure | LV | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
23/03/2024 | 21:45 | HH429C | URBAN | Asset failure | LV | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
23/03/2024 | 22:02 | AP529A | URBAN | Animal | Animal impact | 1,329.00 | 123.7 | 0.253486 | 0.0020490 | No
23/03/2024 | 22:22 | MTB21 | SHORT RURAL | Asset failure | HV | 1,265.00 | 605.8 | 5.391859 | 0.0088999 | No
24/03/2024 | 01:44 | YK23 | LONG RURAL | Other |  | 2.00 | 166.0 | 0.002383 | 0.0000144 | No
24/03/2024 | 07:37 | NU13 | LONG RURAL | Asset failure | LV | 1.33 | 339.0 | 0.003244 | 0.0000096 | No
24/03/2024 | 08:22 | KI44 | LONG RURAL | Unknown | Unknown | 91.00 | 175.2 | 0.114419 | 0.0006530 | No
24/03/2024 | 08:26 | SG13 | SHORT RURAL | Asset failure | HV | 48.00 | 446.9 | 0.150911 | 0.0003377 | No
24/03/2024 | 10:17 | G36 | LONG RURAL | Planned |  | 2.00 | 150.0 | 0.002153 | 0.0000144 | No
24/03/2024 | 11:53 | AP214A | URBAN | Third Party | Other | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
24/03/2024 | 12:13 | SM216G | URBAN | Unknown | Unknown | 1.00 | 489.0 | 0.000754 | 0.0000015 | No
24/03/2024 | 13:23 | SM172B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 20.00 | 191.0 | 0.005889 | 0.0000308 | No
24/03/2024 | 18:13 | AP529A | URBAN | Animal | Animal impact | 36.00 | 148.0 | 0.008214 | 0.0000555 | No
24/03/2024 | 18:45 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 60.0 | 0.000422 | 0.0000070 | No
24/03/2024 | 18:51 | HH432F | URBAN | Third Party | Vehicle impact | 274.00 | 628.8 | 0.265616 | 0.0004224 | No
24/03/2024 | 19:01 | MTB21 | SHORT RURAL | Asset failure | LV | 1.00 | 45.0 | 0.000317 | 0.0000070 | No
24/03/2024 | 19:17 | MTB21 | SHORT RURAL | Asset failure | HV | 312.67 | 4.0 | 0.008799 | 0.0021998 | No
24/03/2024 | 19:48 | EL07 | URBAN | Asset failure | LV | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
24/03/2024 | 21:03 | HH341G | URBAN | Planned |  | 365.00 | 295.1 | 0.166047 | 0.0005627 | No
24/03/2024 | 21:16 | HH341G | URBAN | Unknown | Unknown | 2.00 | 126.0 | 0.000389 | 0.0000031 | No
24/03/2024 | 21:24 | MTB54 | LONG RURAL | Animal | Animal impact | 245.33 | 5.0 | 0.008803 | 0.0017606 | No
24/03/2024 | 22:14 | HH409C | URBAN | Planned |  | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
25/03/2024 | 03:57 | HH428C | URBAN | Animal | Animal impact | 1,172.00 | 120.0 | 0.216832 | 0.0018069 | No
25/03/2024 | 04:48 | MTB32 | LONG RURAL | Asset failure | HV | 84.33 | 191.4 | 0.115814 | 0.0006052 | No
25/03/2024 | 08:51 | HH428C | URBAN | Asset failure | LV | 1.00 | 98.0 | 0.000151 | 0.0000015 | No
25/03/2024 | 08:55 | VH22 | SHORT RURAL | Planned |  | 14.00 | 294.1 | 0.028972 | 0.0000985 | No
25/03/2024 | 09:02 | WK52 | SHORT RURAL | Planned |  | 2.00 | 218.0 | 0.003067 | 0.0000141 | No
25/03/2024 | 09:10 | KI13 | LONG RURAL | Planned |  | 17.00 | 209.0 | 0.025497 | 0.0001220 | No
25/03/2024 | 09:14 | AP132C | URBAN | Overloads |  | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
25/03/2024 | 09:32 | BT06 | LONG RURAL | Planned |  | 2.00 | 123.0 | 0.001765 | 0.0000144 | No
25/03/2024 | 09:37 | GA26 | URBAN | Planned |  | 128.00 | 268.0 | 0.052888 | 0.0001973 | No
25/03/2024 | 09:40 | AP149B | URBAN | Asset failure | LV | 102.00 | 35.4 | 0.005566 | 0.0001573 | No
25/03/2024 | 09:48 | YK08 | LONG RURAL | Unknown | Unknown | 21.00 | 224.0 | 0.033757 | 0.0001507 | No
25/03/2024 | 10:12 | WK21 | SHORT RURAL | Unknown | Unknown | 3.00 | 345.0 | 0.007282 | 0.0000211 | No
25/03/2024 | 10:35 | AP132D | URBAN | Overloads |  | 2.33 | 114.0 | 0.000410 | 0.0000036 | No
25/03/2024 | 10:36 | CV15 | LONG RURAL | Planned |  | 59.00 | 279.0 | 0.118130 | 0.0004234 | No
25/03/2024 | 10:45 | SD36300 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 296.0 | 0.002124 | 0.0000072 | No
25/03/2024 | 10:53 | PA07 | LONG RURAL | Asset failure | HV | 630.00 | 170.3 | 0.770056 | 0.0045211 | No
25/03/2024 | 10:55 | MG03 | SHORT RURAL | Planned |  | 4.00 | 198.0 | 0.005572 | 0.0000281 | No
25/03/2024 | 11:16 | CM15 | LONG RURAL | Asset failure | HV | 18.00 | 118.0 | 0.015243 | 0.0001292 | No
25/03/2024 | 11:40 | MV33 | SHORT RURAL | Asset failure | LV | 2.00 | 376.0 | 0.005291 | 0.0000141 | No
25/03/2024 | 11:50 | HH177B | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
25/03/2024 | 12:11 | HH522A | URBAN | Asset failure | LV | 6.33 | 8.0 | 0.000078 | 0.0000098 | No
25/03/2024 | 13:16 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 208.0 | 0.001463 | 0.0000070 | No
25/03/2024 | 15:10 | GA48 | SHORT RURAL | Asset failure | HV | 16.00 | 149.0 | 0.016773 | 0.0001126 | No
25/03/2024 | 15:54 | ST24 | SHORT RURAL | Weather |  | 10.00 | 52.3 | 0.003680 | 0.0000704 | No
25/03/2024 | 15:59 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 344.0 | 0.002469 | 0.0000072 | No
25/03/2024 | 16:21 | R21 | LONG RURAL | Animal | Animal impact | 22.33 | 73.7 | 0.011807 | 0.0001603 | No
25/03/2024 | 16:58 | HH121A | URBAN | Third Party | Vehicle impact | 263.00 | 281.3 | 0.114060 | 0.0004055 | No
25/03/2024 | 17:08 | AP214A | URBAN | Asset failure | LV | 5.33 | 309.0 | 0.002541 | 0.0000082 | No
25/03/2024 | 17:14 | VH15 | SHORT RURAL | Overloads |  | 1.00 | 255.0 | 0.001794 | 0.0000070 | No
25/03/2024 | 17:42 | MV63 | SHORT RURAL | Network business | Switching and protection error | 2.00 | 68.0 | 0.000957 | 0.0000141 | No
25/03/2024 | 17:44 | SM411A | URBAN | Unknown | Unknown | 1.00 | 131.0 | 0.000202 | 0.0000015 | No
25/03/2024 | 18:14 | HH341B | URBAN | Vegetation | Grow-in - NSP responsibility | 11.00 | 133.0 | 0.002256 | 0.0000170 | No
25/03/2024 | 18:19 | HH121E | URBAN | Unknown | Unknown | 2.00 | 129.0 | 0.000398 | 0.0000031 | No
25/03/2024 | 18:25 | HH341G | URBAN | Asset failure | LV | 48.00 | 173.0 | 0.012803 | 0.0000740 | No
25/03/2024 | 19:36 | GA26 | URBAN | Asset failure | LV | 15.00 | 153.0 | 0.003538 | 0.0000231 | No
25/03/2024 | 19:47 | BM11 | SHORT RURAL | Unknown | Unknown | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
25/03/2024 | 20:01 | YK06 | SHORT RURAL | Asset failure | HV | 55.00 | 162.6 | 0.062932 | 0.0003870 | No
25/03/2024 | 23:18 | GU43 | LONG RURAL | Animal | Animal impact | 250.00 | 148.3 | 0.266127 | 0.0017941 | No
26/03/2024 | 02:24 | MTB52 | LONG RURAL | Animal | Animal impact | 992.00 | 60.0 | 0.426855 | 0.0071189 | No
26/03/2024 | 02:24 | MTB52 | SHORT RURAL | Animal | Animal impact | 1.00 | 134.0 | 0.000943 | 0.0000070 | No
26/03/2024 | 03:59 | GA50 | URBAN | Asset failure | HV | 33.00 | 201.0 | 0.010226 | 0.0000509 | No
26/03/2024 | 06:07 | MB72 | LONG RURAL | Unknown | Unknown | 260.00 | 357.0 | 0.666107 | 0.0018658 | No
26/03/2024 | 06:35 | SD34102 | LONG RURAL | Unknown | Unknown | 1,056.00 | 319.0 | 2.417447 | 0.0075782 | No
26/03/2024 | 06:35 | SD34102 | SHORT RURAL | Unknown | Unknown | 460.00 | 431.0 | 1.394730 | 0.0032363 | No
26/03/2024 | 06:52 | CV29 | LONG RURAL | Unknown | Unknown | 19.00 | 290.8 | 0.039649 | 0.0001364 | No
26/03/2024 | 07:22 | AP829B | URBAN | Overloads |  | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
26/03/2024 | 08:52 | MI30 | LONG RURAL | Planned |  | 42.00 | 421.5 | 0.127035 | 0.0003014 | No
26/03/2024 | 08:57 | CV16 | LONG RURAL | Planned |  | 47.00 | 384.0 | 0.129518 | 0.0003373 | No
26/03/2024 | 09:01 | MI26 | LONG RURAL | Planned |  | 72.00 | 329.8 | 0.170423 | 0.0005167 | No
26/03/2024 | 09:14 | LM43 | LONG RURAL | Planned |  | 88.00 | 16.0 | 0.010104 | 0.0006315 | No
26/03/2024 | 09:22 | NL234A | URBAN | Planned |  | 54.00 | 353.0 | 0.029389 | 0.0000833 | No
26/03/2024 | 09:32 | PA12 | LONG RURAL | Planned |  | 2.00 | 9.0 | 0.000129 | 0.0000144 | No
26/03/2024 | 09:58 | NU13 | LONG RURAL | Planned |  | 1.00 | 241.0 | 0.001729 | 0.0000072 | No
26/03/2024 | 10:15 | NL210B | URBAN | Asset failure | LV | 1.00 | 273.0 | 0.000421 | 0.0000015 | No
26/03/2024 | 10:24 | CD26 | LONG RURAL | Planned |  | 2.00 | 79.0 | 0.001134 | 0.0000144 | No
26/03/2024 | 11:50 | EL01L | URBAN | Asset failure | LV | 10.00 | 30.0 | 0.000463 | 0.0000154 | No
26/03/2024 | 12:05 | W02 | LONG RURAL | Planned |  | 37.00 | 49.0 | 0.013011 | 0.0002655 | No
26/03/2024 | 12:21 | GU12 | LONG RURAL | Planned |  | 11.00 | 46.0 | 0.003631 | 0.0000789 | No
26/03/2024 | 13:05 | LM43 | LONG RURAL | Planned |  | 88.00 | 7.0 | 0.004421 | 0.0006315 | No
26/03/2024 | 13:31 | GU12 | LONG RURAL | Planned |  | 3.00 | 44.0 | 0.000947 | 0.0000215 | No
26/03/2024 | 14:39 | EL20 | URBAN | Animal | Animal impact | 16.00 | 142.0 | 0.003503 | 0.0000247 | No
26/03/2024 | 15:32 | WK53 | SHORT RURAL | Unknown | Unknown | 1.00 | 86.0 | 0.000605 | 0.0000070 | No
26/03/2024 | 16:47 | PA05 | LONG RURAL | Asset failure | LV | 2.00 | 451.0 | 0.006473 | 0.0000144 | No
26/03/2024 | 16:52 | MV61 | URBAN | Third Party | Dig-in | 20.00 | 194.0 | 0.005982 | 0.0000308 | No
26/03/2024 | 17:29 | AP227A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 162.00 | 99.0 | 0.024714 | 0.0002498 | No
26/03/2024 | 18:38 | MB13 | SHORT RURAL | Asset failure | LV | 1.00 | 245.0 | 0.001724 | 0.0000070 | No
26/03/2024 | 19:58 | SA41 | URBAN | Asset failure | LV | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
26/03/2024 | 19:58 | NL210B | URBAN | Asset failure | LV | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
27/03/2024 | 00:23 | EL01L | URBAN | Asset failure | LV | 17.00 | 630.0 | 0.016512 | 0.0000262 | No
27/03/2024 | 00:27 | AP139C | URBAN | Third Party | Vehicle impact | 62.00 | 405.3 | 0.038743 | 0.0000956 | No
27/03/2024 | 04:11 | NL210A | URBAN | Asset failure | LV | 1.00 | 361.0 | 0.000557 | 0.0000015 | No
27/03/2024 | 06:47 | CV29 | LONG RURAL | Unknown | Unknown | 19.00 | 275.4 | 0.037554 | 0.0001364 | No
27/03/2024 | 08:10 | W30 | LONG RURAL | Weather |  | 2.00 | 1,457.0 | 0.020912 | 0.0000144 | No
27/03/2024 | 08:48 | HH121B | URBAN | Planned |  | 37.00 | 337.0 | 0.019224 | 0.0000570 | No
27/03/2024 | 09:08 | SM374A | URBAN | Planned |  | 119.00 | 336.0 | 0.061645 | 0.0001835 | No
27/03/2024 | 09:08 | BM55 | SHORT RURAL | Planned |  | 48.00 | 141.0 | 0.047616 | 0.0003377 | No
27/03/2024 | 09:23 | MG24 | SHORT RURAL | Vegetation | Blow-in/Fall-in - NSP responsibility | 122.00 | 102.0 | 0.087550 | 0.0008583 | No
27/03/2024 | 09:26 | CM20 | LONG RURAL | Planned |  | 2.00 | 210.0 | 0.003014 | 0.0000144 | No
27/03/2024 | 09:31 | NA07 | LONG RURAL | Overloads |  | 1.00 | 148.0 | 0.001062 | 0.0000072 | No
27/03/2024 | 09:31 | CD17 | LONG RURAL | Planned |  | 32.00 | 260.3 | 0.059786 | 0.0002296 | No
27/03/2024 | 09:33 | CV15 | LONG RURAL | Planned |  | 55.00 | 346.0 | 0.136566 | 0.0003947 | No
27/03/2024 | 09:37 | YK08 | LONG RURAL | Planned |  | 48.00 | 221.0 | 0.076127 | 0.0003445 | No
27/03/2024 | 09:39 | NL111C | URBAN | Planned |  | 503.00 | 246.0 | 0.190774 | 0.0007755 | No
27/03/2024 | 09:40 | BU01 | LONG RURAL | Planned |  | 97.00 | 341.1 | 0.237458 | 0.0006961 | No
27/03/2024 | 09:42 | CN25 | LONG RURAL | Unknown | Unknown | 53.00 | 4.1 | 0.001564 | 0.0003803 | No
27/03/2024 | 09:45 | W02 | LONG RURAL | Planned |  | 37.00 | 231.9 | 0.061573 | 0.0002655 | No
27/03/2024 | 09:45 | CM27 | LONG RURAL | Planned |  | 3.00 | 222.0 | 0.004779 | 0.0000215 | No
27/03/2024 | 10:24 | NU21 | LONG RURAL | Unknown | Unknown | 1.00 | 107.0 | 0.000768 | 0.0000072 | No
27/03/2024 | 11:00 | EL07 | URBAN | Unknown | Unknown | 1.00 | 213.0 | 0.000328 | 0.0000015 | No
27/03/2024 | 11:32 | BT03 | LONG RURAL | Planned |  | 33.00 | 68.0 | 0.016104 | 0.0002368 | No
27/03/2024 | 11:41 | GA51 | SHORT RURAL | Weather |  | 27.00 | 47.0 | 0.008928 | 0.0001900 | No
27/03/2024 | 11:46 | G06 | LONG RURAL | Weather |  | 33.00 | 145.0 | 0.034339 | 0.0002368 | No
27/03/2024 | 11:50 | SM350G | URBAN | Asset failure | LV | 2.00 | 199.0 | 0.000614 | 0.0000031 | No
27/03/2024 | 12:15 | SD52300 | LONG RURAL | Overloads |  | 2.00 | 176.0 | 0.002526 | 0.0000144 | No
27/03/2024 | 13:07 | AP149E | URBAN | Asset failure | LV | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
27/03/2024 | 13:19 | NL760C | URBAN | Asset failure | LV | 1.00 | 49.0 | 0.000076 | 0.0000015 | No
27/03/2024 | 13:29 | HH121H | URBAN | Asset failure | LV | 69.00 | 77.0 | 0.008191 | 0.0001064 | No
27/03/2024 | 14:14 | AP226A | URBAN | Asset failure | LV | 4.00 | 68.0 | 0.000419 | 0.0000062 | No
27/03/2024 | 16:06 | BM53 | SHORT RURAL | Asset failure | LV | 1.00 | 89.0 | 0.000626 | 0.0000070 | No
27/03/2024 | 16:06 | MTB52 | LONG RURAL | Animal | Animal impact | 994.00 | 67.2 | 0.479135 | 0.0071333 | No
27/03/2024 | 16:06 | MTB52 | SHORT RURAL | Animal | Animal impact | 3.00 | 314.0 | 0.006627 | 0.0000211 | No
27/03/2024 | 16:32 | CM05 | LONG RURAL | Weather |  | 99.00 | 72.5 | 0.051505 | 0.0007105 | No
27/03/2024 | 16:59 | NL544B | URBAN | Third Party | Vehicle impact | 6.00 | 138.0 | 0.001277 | 0.0000093 | No
27/03/2024 | 17:20 | W30 | LONG RURAL | Weather |  | 25.00 | 21.0 | 0.003768 | 0.0001794 | No
27/03/2024 | 18:19 | M51 | SHORT RURAL | Asset failure | LV | 1.00 | 522.0 | 0.003673 | 0.0000070 | No
27/03/2024 | 18:27 | AP227D | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
27/03/2024 | 20:29 | GA15 | SHORT RURAL | Weather |  | 225.00 | 11.3 | 0.017948 | 0.0015830 | No
27/03/2024 | 21:38 | EL260C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,080.00 | 129.0 | 0.214797 | 0.0016651 | No
28/03/2024 | 01:23 | GU43 | LONG RURAL | Unknown | Unknown | 30.67 | 193.0 | 0.042474 | 0.0002201 | No
28/03/2024 | 03:19 | HH522B | URBAN | Asset failure | LV | 15.33 | 151.0 | 0.003570 | 0.0000236 | No
28/03/2024 | 06:02 | EL01Q | URBAN | Asset failure | HV | 643.00 | 172.7 | 0.171201 | 0.0009913 | No
28/03/2024 | 07:05 | HH432G | URBAN | Unknown | Unknown | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
28/03/2024 | 07:06 | SM126D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 360.0 | 0.000555 | 0.0000015 | No
28/03/2024 | 07:27 | HH432E | URBAN | Unknown | Unknown | 1.00 | 53.0 | 0.000082 | 0.0000015 | No
28/03/2024 | 08:31 | HH522A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 41.00 | 354.0 | 0.022377 | 0.0000632 | No
28/03/2024 | 08:31 | MG31 | LONG RURAL | Planned |  | 4.00 | 121.0 | 0.003473 | 0.0000287 | No
28/03/2024 | 08:37 | HH130C | URBAN | Planned |  | 23.00 | 359.0 | 0.012730 | 0.0000355 | No
28/03/2024 | 09:02 | KI14 | LONG RURAL | Planned |  | 11.00 | 282.9 | 0.022333 | 0.0000789 | No
28/03/2024 | 09:08 | CV16 | LONG RURAL | Planned |  | 30.00 | 317.2 | 0.068283 | 0.0002153 | No
28/03/2024 | 09:12 | GU42 | LONG RURAL | Planned |  | 4.00 | 243.0 | 0.006975 | 0.0000287 | No
28/03/2024 | 09:13 | NU13 | LONG RURAL | Asset failure | LV | 2.00 | 466.0 | 0.006688 | 0.0000144 | No
28/03/2024 | 09:14 | SM349H | URBAN | Asset failure | LV | 2.00 | 349.0 | 0.001076 | 0.0000031 | No
28/03/2024 | 09:17 | VH45 | SHORT RURAL | Planned |  | 3.00 | 121.0 | 0.002554 | 0.0000211 | No
28/03/2024 | 09:22 | EL10 | URBAN | Planned |  | 202.00 | 308.6 | 0.096101 | 0.0003114 | No
28/03/2024 | 09:49 | MV13 | SHORT RURAL | Planned |  | 16.00 | 350.0 | 0.039399 | 0.0001126 | No
28/03/2024 | 09:50 | PL803A | URBAN | Planned |  | 35.00 | 121.0 | 0.006529 | 0.0000540 | No
28/03/2024 | 10:17 | LX41 | SHORT RURAL | Planned |  | 24.00 | 145.5 | 0.024568 | 0.0001689 | No
28/03/2024 | 10:29 | SM410D | URBAN | Unknown | Unknown | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
28/03/2024 | 11:57 | W28 | LONG RURAL | Asset failure | HV | 6.00 | 38.0 | 0.001636 | 0.0000431 | No
28/03/2024 | 12:02 | SM126C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 92.00 | 156.1 | 0.022147 | 0.0001418 | No
28/03/2024 | 12:16 | MG31 | LONG RURAL | Planned |  | 1.00 | 94.0 | 0.000675 | 0.0000072 | No
28/03/2024 | 12:40 | WK21 | SHORT RURAL | Unknown | Unknown | 15.00 | 350.0 | 0.036936 | 0.0001055 | No
28/03/2024 | 12:52 | HH386B | URBAN | Asset failure | LV | 1.00 | 249.0 | 0.000384 | 0.0000015 | No
28/03/2024 | 14:50 | W06 | LONG RURAL | Animal | Animal impact | 1.00 | 20.0 | 0.000144 | 0.0000072 | No
28/03/2024 | 14:54 | HH148C | URBAN | Asset failure | LV | 4.67 | 97.4 | 0.000701 | 0.0000072 | No
28/03/2024 | 16:11 | CBD366S | URBAN | Asset failure | LV | 1.00 | 302.0 | 0.000466 | 0.0000015 | No
28/03/2024 | 16:23 | HH341A | URBAN | Asset failure | LV | 1.00 | 240.0 | 0.000370 | 0.0000015 | No
28/03/2024 | 16:28 | HH386G | URBAN | Asset failure | LV | 1.00 | 305.0 | 0.000470 | 0.0000015 | No
28/03/2024 | 18:46 | GU15 | LONG RURAL | Asset failure | HV | 49.00 | 72.0 | 0.025318 | 0.0003516 | No
28/03/2024 | 19:38 | AP529C | URBAN | Asset failure | LV | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
28/03/2024 | 20:31 | HH148D | URBAN | Asset failure | LV | 8.00 | 136.0 | 0.001677 | 0.0000123 | No
28/03/2024 | 22:58 | CBD103D | URBAN | Asset failure | LV | 1.00 | 296.0 | 0.000456 | 0.0000015 | No
28/03/2024 | 23:05 | GU31 | LONG RURAL | Animal | Animal impact | 177.00 | 215.1 | 0.273217 | 0.0012702 | No
29/03/2024 | 05:34 | CV757A | LONG RURAL | Unknown | Unknown | 373.00 | 303.0 | 0.811062 | 0.0026768 | No
29/03/2024 | 07:04 | LX48 | SHORT RURAL | Unknown | Unknown | 38.00 | 294.0 | 0.078601 | 0.0002673 | No
29/03/2024 | 11:08 | NL451C | URBAN | Asset failure | LV | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
29/03/2024 | 11:14 | NL111C | URBAN | Asset failure | LV | 1.00 | 211.0 | 0.000325 | 0.0000015 | No
29/03/2024 | 12:34 | SM216E | URBAN | Unknown | Unknown | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
29/03/2024 | 12:38 | HH522B | URBAN | Asset failure | LV | 6.67 | 71.0 | 0.000730 | 0.0000103 | No
29/03/2024 | 13:27 | HH102B | URBAN | Asset failure | LV | 28.33 | 57.0 | 0.002490 | 0.0000437 | No
29/03/2024 | 13:38 | SA17 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
29/03/2024 | 14:28 | EL25 | URBAN | Network business | Switching and protection error | 14.00 | 133.0 | 0.002871 | 0.0000216 | No
29/03/2024 | 15:05 | R31 | LONG RURAL | Asset failure | LV | 1.00 | 223.0 | 0.001600 | 0.0000072 | No
29/03/2024 | 16:17 | M91 | LONG RURAL | Unknown | Unknown | 37.00 | 182.0 | 0.048325 | 0.0002655 | No
29/03/2024 | 16:58 | CN83 | LONG RURAL | Unknown | Unknown | 267.00 | 194.0 | 0.371720 | 0.0019161 | No
29/03/2024 | 17:29 | SA42 | URBAN | Asset failure | LV | 1.00 | 165.0 | 0.000254 | 0.0000015 | No
29/03/2024 | 20:35 | PA18 | LONG RURAL | Asset failure | HV | 97.00 | 762.9 | 0.531027 | 0.0006961 | No
29/03/2024 | 21:25 | HH341J | URBAN | Asset failure | LV | 1.00 | 235.0 | 0.000362 | 0.0000015 | No
29/03/2024 | 22:29 | PA04 | URBAN | Third Party | Unauthorised access | 18.00 | 719.0 | 0.019953 | 0.0000278 | No
29/03/2024 | 22:46 | SD55100 | LONG RURAL | Weather |  | 291.00 | 218.8 | 0.457003 | 0.0020883 | No
29/03/2024 | 23:27 | MTB54 | LONG RURAL | Animal | Animal impact | 252.00 | 53.0 | 0.095847 | 0.0018084 | No
30/03/2024 | 06:34 | NA52 | LONG RURAL | Asset failure | LV | 17.00 | 239.0 | 0.029157 | 0.0001220 | No
30/03/2024 | 07:38 | MI15 | LONG RURAL | Unknown | Unknown | 28.00 | 202.0 | 0.040589 | 0.0002009 | No
30/03/2024 | 08:06 | SG12 | SHORT RURAL | Overloads |  | 1.00 | 385.0 | 0.002709 | 0.0000070 | No
30/03/2024 | 08:23 | SG12 | SHORT RURAL | Overloads |  | 1.00 | 188.0 | 0.001323 | 0.0000070 | No
30/03/2024 | 08:25 | SB17 | LONG RURAL | Weather |  | 35.00 | 286.0 | 0.071835 | 0.0002512 | No
30/03/2024 | 12:22 | KI44 | LONG RURAL | Asset failure | HV | 6.00 | 135.7 | 0.005842 | 0.0000431 | No
30/03/2024 | 12:58 | EL08G | URBAN | Overloads |  | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
30/03/2024 | 14:34 | SB21 | LONG RURAL | Asset failure | HV | 1.00 | 182.0 | 0.001306 | 0.0000072 | No
30/03/2024 | 15:28 | MI20 | LONG RURAL | Overloads |  | 1.00 | 187.0 | 0.001342 | 0.0000072 | No
30/03/2024 | 16:07 | MTB62 | SHORT RURAL | Overloads |  | 1.00 | 90.0 | 0.000633 | 0.0000070 | No
30/03/2024 | 16:56 | SB17 | LONG RURAL | Weather |  | 35.00 | 1,145.0 | 0.287591 | 0.0002512 | No
30/03/2024 | 18:07 | ST22 | SHORT RURAL | Asset failure | HV | 3.33 | 11.0 | 0.000258 | 0.0000235 | No
30/03/2024 | 18:46 | WHY08 | URBAN | Asset failure | LV | 26.00 | 236.0 | 0.009460 | 0.0000401 | No
30/03/2024 | 19:13 | NA60 | LONG RURAL | Other |  | 2.00 | 36.0 | 0.000517 | 0.0000144 | No
30/03/2024 | 20:36 | MTB61 | SHORT RURAL | Unknown | Unknown | 129.33 | 116.0 | 0.105551 | 0.0009099 | No
30/03/2024 | 21:22 | PA18 | LONG RURAL | Weather |  | 59.00 | 127.9 | 0.054145 | 0.0004234 | No
30/03/2024 | 21:53 | SA11 | URBAN | Asset failure | LV | 1.00 | 279.0 | 0.000430 | 0.0000015 | No
30/03/2024 | 22:20 | NL210A | URBAN | Animal | Animal impact | 11.00 | 118.0 | 0.002001 | 0.0000170 | No
30/03/2024 | 22:29 | MTB61 | SHORT RURAL | Unknown | Unknown | 1.00 | 40.0 | 0.000281 | 0.0000070 | No
30/03/2024 | 22:34 | MTB61 | SHORT RURAL | Planned |  | 1.00 | 53.0 | 0.000373 | 0.0000070 | No
31/03/2024 | 02:49 | SG01 | SHORT RURAL | Unknown | Unknown | 441.00 | 90.0 | 0.279239 | 0.0031027 | No
31/03/2024 | 03:14 | CV757A | LONG RURAL | Weather |  | 371.00 | 426.2 | 1.134822 | 0.0026624 | No
31/03/2024 | 04:21 | CM25 | LONG RURAL | Weather |  | 1.00 | 358.0 | 0.002569 | 0.0000072 | No
31/03/2024 | 04:23 | CM10 | LONG RURAL | Unknown | Unknown | 23.00 | 465.0 | 0.076751 | 0.0001651 | No
31/03/2024 | 04:25 | CM29 | LONG RURAL | Weather |  | 531.00 | 250.7 | 0.955442 | 0.0038106 | No
31/03/2024 | 05:07 | SD55100 | LONG RURAL | Weather |  | 2.00 | 657.0 | 0.009430 | 0.0000144 | No
31/03/2024 | 05:07 | SD55100 | LONG RURAL | Weather |  | 59.00 | 280.0 | 0.118553 | 0.0004234 | No
31/03/2024 | 06:40 | CN33 | LONG RURAL | Unknown | Unknown | 8.00 | 258.0 | 0.014812 | 0.0000574 | No
31/03/2024 | 07:43 | HH121H | URBAN | Asset failure | LV | 1.00 | 245.0 | 0.000378 | 0.0000015 | No
31/03/2024 | 08:03 | R36 | SHORT RURAL | Weather |  | 43.00 | 80.0 | 0.024202 | 0.0003025 | No
31/03/2024 | 08:03 | SD34102 | SHORT RURAL | Weather |  | 4.00 | 222.0 | 0.006248 | 0.0000281 | No
31/03/2024 | 08:04 | HH428A | URBAN | Asset failure | LV | 22.67 | 251.0 | 0.008772 | 0.0000349 | No
31/03/2024 | 10:16 | HH432F | URBAN | Asset failure | LV | 63.67 | 103.0 | 0.010110 | 0.0000982 | No
31/03/2024 | 13:01 | ME131C | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
31/03/2024 | 16:11 | BT01 | LONG RURAL | Asset failure | LV | 1.00 | 240.0 | 0.001722 | 0.0000072 | No
31/03/2024 | 20:00 | VH21 | SHORT RURAL | Overloads |  | 1.00 | 120.0 | 0.000844 | 0.0000070 | No
31/03/2024 | 22:38 | YK29 | LONG RURAL | Weather |  | 150.00 | 76.0 | 0.081810 | 0.0010764 | No
31/03/2024 | 23:08 | YK29 | LONG RURAL | Weather |  | 76.00 | 34.0 | 0.018544 | 0.0005454 | No
01/04/2024 | 00:45 | GU21 | LONG RURAL | Unknown | Unknown | 16.00 | 149.0 | 0.017108 | 0.0001148 | No
01/04/2024 | 01:34 | NL210E | URBAN | Asset failure | LV | 1.00 | 1,336.0 | 0.002060 | 0.0000015 | No
01/04/2024 | 05:16 | NA52 | LONG RURAL | Unknown | Unknown | 17.00 | 276.0 | 0.033671 | 0.0001220 | No
01/04/2024 | 07:48 | SM374B | URBAN | Asset failure | LV | 93.00 | 276.0 | 0.039574 | 0.0001434 | No
01/04/2024 | 08:11 | CM20 | LONG RURAL | Unknown | Unknown | 1.00 | 140.0 | 0.001005 | 0.0000072 | No
01/04/2024 | 08:55 | EL09 | URBAN | Asset failure | LV | 1.00 | 153.0 | 0.000236 | 0.0000015 | No
01/04/2024 | 10:07 | MT01 | LONG RURAL | Unknown | Unknown | 2.00 | 260.0 | 0.003732 | 0.0000144 | No
01/04/2024 | 10:54 | M51 | SHORT RURAL | Overloads |  | 1.00 | 569.0 | 0.004003 | 0.0000070 | No
01/04/2024 | 11:51 | CV18 | SHORT RURAL | Weather |  | 57.00 | 111.0 | 0.044514 | 0.0004010 | No
01/04/2024 | 12:24 | BT02 | LONG RURAL | Asset failure | HV | 5.33 | 247.7 | 0.009482 | 0.0000383 | No
01/04/2024 | 13:04 | WK43 | SHORT RURAL | Unknown | Unknown | 46.00 | 245.0 | 0.079290 | 0.0003236 | No
01/04/2024 | 14:26 | WHY08 | URBAN | Asset failure | LV | 1.00 | 161.0 | 0.000248 | 0.0000015 | No
01/04/2024 | 15:25 | SA18 | URBAN | Asset failure | LV | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
01/04/2024 | 17:01 | CM10 | LONG RURAL | Weather |  | 206.67 | 140.6 | 0.208559 | 0.0014831 | No
01/04/2024 | 17:03 | CN33 | LONG RURAL | Unknown | Unknown | 8.00 | 295.0 | 0.016936 | 0.0000574 | No
01/04/2024 | 17:11 | KA03 | LONG RURAL | Weather |  | 629.00 | 76.1 | 0.343488 | 0.0045139 | No
01/04/2024 | 18:30 | SG03 | SHORT RURAL | Animal | Animal impact | 2.00 | 106.0 | 0.001492 | 0.0000141 | No
01/04/2024 | 18:48 | EL260C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1,081.00 | 47.0 | 0.078332 | 0.0016666 | No
01/04/2024 | 19:11 | NU24 | LONG RURAL | Weather |  | 399.00 | 224.0 | 0.641392 | 0.0028634 | No
01/04/2024 | 19:35 | MB72 | LONG RURAL | Unknown | Unknown | 260.00 | 224.6 | 0.419112 | 0.0018658 | No
01/04/2024 | 20:03 | GA38 | LONG RURAL | Weather |  | 25.00 | 726.7 | 0.130380 | 0.0001794 | No
01/04/2024 | 21:16 | EL01A | URBAN | Animal | Animal impact | 577.67 | 19.2 | 0.017124 | 0.0008906 | No
01/04/2024 | 23:00 | WK21 | SHORT RURAL | Unknown | Unknown | 15.00 | 190.0 | 0.020051 | 0.0001055 | No
01/04/2024 | 23:36 | WHY12 | URBAN | Overloads |  | 1.00 | 55.0 | 0.000085 | 0.0000015 | No
01/04/2024 | 23:48 | HH177D | URBAN | Vegetation | Grow-in - NSP responsibility | 44.67 | 64.0 | 0.004407 | 0.0000689 | No
02/04/2024 | 00:02 | PL04 | URBAN | Asset failure | HV | 115.00 | 204.1 | 0.036187 | 0.0001773 | No
02/04/2024 | 00:25 | SM172E | URBAN | Asset failure | LV | 85.00 | 80.0 | 0.010484 | 0.0001310 | No
02/04/2024 | 02:19 | MG32 | LONG RURAL | Unknown | Unknown | 1.00 | 170.0 | 0.001220 | 0.0000072 | No
02/04/2024 | 02:57 | SG14 | SHORT RURAL | Unknown | Unknown | 1.00 | 109.0 | 0.000767 | 0.0000070 | No
02/04/2024 | 05:00 | MB72 | LONG RURAL | Weather |  | 260.00 | 355.0 | 0.662375 | 0.0018658 | No
02/04/2024 | 05:10 | PL04 | URBAN | Unknown | Unknown | 18.00 | 436.0 | 0.012100 | 0.0000278 | No
02/04/2024 | 05:40 | VH21 | SHORT RURAL | Unknown | Unknown | 170.00 | 198.0 | 0.236815 | 0.0011960 | No
02/04/2024 | 06:52 | CN33 | LONG RURAL | Weather |  | 8.00 | 679.0 | 0.038982 | 0.0000574 | No
02/04/2024 | 07:00 | MTB21 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 56.00 | 137.0 | 0.053976 | 0.0003940 | No
02/04/2024 | 08:14 | MV53 | SHORT RURAL | Unknown | Unknown | 193.00 | 136.0 | 0.184668 | 0.0013578 | No
02/04/2024 | 08:33 | ST24 | SHORT RURAL | Unknown | Unknown | 152.33 | 180.3 | 0.193274 | 0.0010717 | No
02/04/2024 | 08:44 | MG38 | SHORT RURAL | Planned |  | 2.00 | 156.0 | 0.002195 | 0.0000141 | No
02/04/2024 | 09:06 | SA41 | URBAN | Asset failure | LV | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
02/04/2024 | 09:13 | SA19 | URBAN | Asset failure | LV | 2.00 | 152.0 | 0.000469 | 0.0000031 | No
02/04/2024 | 09:14 | WK52 | SHORT RURAL | Planned |  | 8.00 | 216.0 | 0.012157 | 0.0000563 | No
02/04/2024 | 09:30 | CBD103F | URBAN | Asset failure | LV | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
02/04/2024 | 09:32 | SM172B | URBAN | Overloads |  | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
02/04/2024 | 09:38 | BU09 | LONG RURAL | Asset failure | LV | 1.00 | 236.0 | 0.001694 | 0.0000072 | No
02/04/2024 | 09:48 | MV61 | SHORT RURAL | Planned |  | 620.00 | 216.0 | 0.942193 | 0.0043620 | No
02/04/2024 | 09:48 | MV61 | URBAN | Planned |  | 351.00 | 240.0 | 0.129891 | 0.0005412 | No
02/04/2024 | 10:07 | MG10 | LONG RURAL | Animal | Animal impact | 411.00 | 66.0 | 0.194665 | 0.0029495 | No
02/04/2024 | 10:17 | HH145E | URBAN | Planned |  | 238.00 | 213.7 | 0.078414 | 0.0003669 | No
02/04/2024 | 10:45 | BM44 | SHORT RURAL | Animal | Animal impact | 966.00 | 44.1 | 0.299796 | 0.0067963 | No
02/04/2024 | 10:57 | MB28 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 436.0 | 0.006135 | 0.0000141 | No
02/04/2024 | 11:34 | PL803C | URBAN | Asset failure | LV | 25.33 | 317.0 | 0.012381 | 0.0000391 | No
02/04/2024 | 11:39 | MB24 | SHORT RURAL | Overloads |  | 1.00 | 546.0 | 0.003841 | 0.0000070 | No
02/04/2024 | 12:21 | AP829D | URBAN | Overloads |  | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
02/04/2024 | 12:33 | ST21 | SHORT RURAL | Unknown | Unknown | 3.33 | 130.0 | 0.003049 | 0.0000235 | No
02/04/2024 | 12:46 | HH386A | URBAN | Asset failure | LV | 1.33 | 122.0 | 0.000251 | 0.0000021 | No
02/04/2024 | 13:03 | HH118B | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
02/04/2024 | 13:22 | MT08 | LONG RURAL | Asset failure | LV | 1.00 | 104.0 | 0.000746 | 0.0000072 | No
02/04/2024 | 14:29 | SD35300 | LONG RURAL | Unknown | Unknown | 2.00 | 166.0 | 0.002383 | 0.0000144 | No
02/04/2024 | 16:09 | SG11 | SHORT RURAL | Asset failure | LV | 35.00 | 179.0 | 0.044077 | 0.0002462 | No
02/04/2024 | 17:10 | SA36 | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
02/04/2024 | 18:13 | SM350H | URBAN | Asset failure | LV | 7.00 | 69.0 | 0.000745 | 0.0000108 | No
02/04/2024 | 18:36 | HH121D | URBAN | Asset failure | LV | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
02/04/2024 | 19:50 | HH341E | URBAN | Asset failure | LV | 33.00 | 77.0 | 0.003918 | 0.0000509 | No
02/04/2024 | 21:25 | SA17 | URBAN | Asset failure | LV | 69.00 | 64.0 | 0.006808 | 0.0001064 | No
02/04/2024 | 22:22 | VH21 | SHORT RURAL | Weather |  | 170.00 | 189.7 | 0.226930 | 0.0011960 | No
03/04/2024 | 03:47 | NL210A | URBAN | Asset failure | LV | 1.00 | 57.0 | 0.000088 | 0.0000015 | No
03/04/2024 | 05:14 | EL23 | URBAN | Unknown | Unknown | 36.00 | 242.0 | 0.013432 | 0.0000555 | No
03/04/2024 | 08:05 | HH121H | URBAN | Asset failure | LV | 1.00 | 243.0 | 0.000375 | 0.0000015 | No
03/04/2024 | 08:33 | AP372B | URBAN | Planned |  | 77.00 | 388.0 | 0.046061 | 0.0001187 | No
03/04/2024 | 08:33 | EL260D | URBAN | Planned |  | 8.00 | 400.0 | 0.004934 | 0.0000123 | No
03/04/2024 | 08:36 | KA24 | LONG RURAL | Planned |  | 49.00 | 230.0 | 0.080877 | 0.0003516 | No
03/04/2024 | 08:37 | EL260D | URBAN | Planned |  | 2.00 | 48.0 | 0.000148 | 0.0000031 | No
03/04/2024 | 09:00 | MI19 | LONG RURAL | Third Party | Vehicle impact | 80.00 | 157.2 | 0.090264 | 0.0005741 | No
03/04/2024 | 09:11 | HH102D | URBAN | Asset failure | LV | 1.00 | 111.0 | 0.000171 | 0.0000015 | No
03/04/2024 | 09:24 | SM349F | URBAN | Planned |  | 89.00 | 313.0 | 0.042955 | 0.0001372 | No
03/04/2024 | 09:28 | MTB51 | LONG RURAL | Planned |  | 2.00 | 284.0 | 0.004076 | 0.0000144 | No
03/04/2024 | 09:32 | AP139B | URBAN | Asset failure | LV | 1.00 | 164.0 | 0.000253 | 0.0000015 | No
03/04/2024 | 09:32 | HH102A | URBAN | Unknown | Unknown | 1.00 | 305.0 | 0.000470 | 0.0000015 | No
03/04/2024 | 09:33 | HH145A | URBAN | Planned |  | 29.00 | 320.9 | 0.014348 | 0.0000447 | No
03/04/2024 | 09:46 | G23 | LONG RURAL | Planned |  | 90.00 | 133.0 | 0.085901 | 0.0006459 | No
03/04/2024 | 10:28 | HH177G | URBAN | Overloads |  | 1.00 | 96.0 | 0.000148 | 0.0000015 | No
03/04/2024 | 10:53 | KA20 | LONG RURAL | Planned |  | 3.00 | 17.0 | 0.000366 | 0.0000215 | No
03/04/2024 | 11:11 | EL01Z | URBAN | Planned |  | 1.00 | 34.0 | 0.000052 | 0.0000015 | No
03/04/2024 | 11:11 | SG04 | SHORT RURAL | Unknown | Unknown | 66.00 | 104.0 | 0.048292 | 0.0004643 | No
03/04/2024 | 11:21 | W27 | LONG RURAL | Planned |  | 11.00 | 228.0 | 0.017998 | 0.0000789 | No
03/04/2024 | 11:34 | MG17 | LONG RURAL | Weather |  | 1.00 | 324.0 | 0.002325 | 0.0000072 | No
03/04/2024 | 11:58 | MG17 | LONG RURAL | Weather |  | 21.00 | 284.0 | 0.042800 | 0.0001507 | No
03/04/2024 | 12:46 | NA01 | LONG RURAL | Unknown | Unknown | 42.00 | 46.0 | 0.013865 | 0.0003014 | No
03/04/2024 | 13:08 | HH432B | URBAN | Asset failure | LV | 4.00 | 336.0 | 0.002072 | 0.0000062 | No
03/04/2024 | 13:28 | CM05 | LONG RURAL | Asset failure | LV | 2.00 | 348.0 | 0.004995 | 0.0000144 | No
03/04/2024 | 13:36 | BM43 | SHORT RURAL | Asset failure | LV | 2.00 | 180.0 | 0.002533 | 0.0000141 | No
03/04/2024 | 14:02 | G05 | LONG RURAL | Asset failure | HV | 6.00 | 269.0 | 0.011583 | 0.0000431 | No
03/04/2024 | 16:52 | ST34 | LONG RURAL | Animal | Animal impact | 49.33 | 171.0 | 0.060540 | 0.0003540 | No
03/04/2024 | 17:06 | BM44 | SHORT RURAL | Overloads |  | 9.00 | 28.0 | 0.001773 | 0.0000633 | No
03/04/2024 | 18:27 | AP351C | URBAN | Third Party | Vehicle impact | 1.00 | 925.0 | 0.001426 | 0.0000015 | No
03/04/2024 | 18:48 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 1,329.0 | 0.009350 | 0.0000070 | No
03/04/2024 | 19:20 | VH23 | SHORT RURAL | Asset failure | LV | 12.00 | 185.8 | 0.015689 | 0.0000844 | No
03/04/2024 | 20:44 | SM216C | URBAN | Unknown | Unknown | 1.00 | 90.0 | 0.000139 | 0.0000015 | No
04/04/2024 | 03:36 | SM350B | URBAN | Animal | Animal impact | 1,753.00 | 77.0 | 0.208107 | 0.0027027 | No
04/04/2024 | 03:48 | SM350A | URBAN | Animal | Animal impact | 2.00 | 87.0 | 0.000268 | 0.0000031 | No
04/04/2024 | 03:50 | LX48 | SHORT RURAL | Unknown | Unknown | 38.00 | 450.0 | 0.120307 | 0.0002673 | No
04/04/2024 | 05:07 | HH121E | URBAN | Animal | Animal impact | 10.00 | 321.0 | 0.004949 | 0.0000154 | No
04/04/2024 | 06:41 | VH15 | SHORT RURAL | Asset failure | HV | 2,126.00 | 75.3 | 1.126945 | 0.0149575 | No
04/04/2024 | 06:51 | VH12 | SHORT RURAL | Asset failure | LV | 1.00 | 483.0 | 0.003398 | 0.0000070 | No
04/04/2024 | 07:50 | NL234D | URBAN | Asset failure | LV | 77.00 | 180.2 | 0.021393 | 0.0001187 | No
04/04/2024 | 08:17 | KA15 | LONG RURAL | Planned |  | 157.00 | 226.0 | 0.254631 | 0.0011267 | No
04/04/2024 | 08:38 | GA28 | LONG RURAL | Planned |  | 912.00 | 5.0 | 0.032731 | 0.0065448 | No
04/04/2024 | 09:00 | HH130B | URBAN | Planned |  | 79.00 | 351.0 | 0.042751 | 0.0001218 | No
04/04/2024 | 09:26 | ST34 | LONG RURAL | Planned |  | 7.00 | 354.0 | 0.017783 | 0.0000502 | No
04/04/2024 | 09:26 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 334.0 | 0.002350 | 0.0000070 | No
04/04/2024 | 09:39 | MG06 | SHORT RURAL | Network business | Switching and protection error | 1.00 | 302.0 | 0.002125 | 0.0000070 | No
04/04/2024 | 09:46 | HH130D | URBAN | Planned |  | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
04/04/2024 | 09:57 | WK11 | SHORT RURAL | Planned |  | 25.00 | 296.0 | 0.052063 | 0.0001759 | No
04/04/2024 | 10:18 | SD35200 | LONG RURAL | Planned |  | 17.00 | 40.0 | 0.004880 | 0.0001220 | No
04/04/2024 | 10:50 | NA13 | LONG RURAL | Planned |  | 7.00 | 283.0 | 0.014216 | 0.0000502 | No
04/04/2024 | 10:58 | R11 | LONG RURAL | Planned |  | 1.00 | 265.0 | 0.001902 | 0.0000072 | No
04/04/2024 | 12:58 | HH130B | URBAN | Asset failure | LV | 28.00 | 129.0 | 0.005569 | 0.0000432 | No
04/04/2024 | 13:10 | GA09 | LONG RURAL | Unknown | Unknown | 2.33 | 324.0 | 0.005425 | 0.0000167 | No
04/04/2024 | 13:24 | SM172C | URBAN | Asset failure | LV | 2.67 | 109.0 | 0.000448 | 0.0000041 | No
04/04/2024 | 13:29 | SM172C | URBAN | Asset failure | LV | 87.67 | 105.0 | 0.014192 | 0.0001352 | No
04/04/2024 | 17:15 | LX43 | SHORT RURAL | Asset failure | LV | 4.00 | 75.8 | 0.002132 | 0.0000281 | No
04/04/2024 | 18:44 | PP02 | URBAN | Asset failure | LV | 15.33 | 341.0 | 0.008061 | 0.0000236 | No
04/04/2024 | 18:51 | PP02 | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
04/04/2024 | 20:32 | WK41 | SHORT RURAL | Other |  | 1.00 | 97.0 | 0.000682 | 0.0000070 | No
04/04/2024 | 21:23 | MTB62 | SHORT RURAL | Asset failure | LV | 1.00 | 484.0 | 0.003405 | 0.0000070 | No
05/04/2024 | 05:12 | LX48 | SHORT RURAL | Weather |  | 38.00 | 499.5 | 0.133534 | 0.0002673 | No
05/04/2024 | 07:41 | BT01 | LONG RURAL | Asset failure | LV | 2.00 | 85.5 | 0.001227 | 0.0000144 | No
05/04/2024 | 08:08 | WHY06 | URBAN | Planned |  | 23.00 | 226.0 | 0.008014 | 0.0000355 | No
05/04/2024 | 08:35 | HH522B | URBAN | Planned |  | 101.00 | 247.6 | 0.038548 | 0.0001557 | No
05/04/2024 | 08:53 | GA26 | URBAN | Planned |  | 99.00 | 290.3 | 0.044313 | 0.0001526 | No
05/04/2024 | 08:58 | AP132A | URBAN | Planned |  | 4.00 | 227.5 | 0.001403 | 0.0000062 | No
05/04/2024 | 09:06 | MV62 | SHORT RURAL | Planned |  | 166.00 | 146.4 | 0.170934 | 0.0011679 | No
05/04/2024 | 09:11 | ST21 | SHORT RURAL | Third Party | Dig-in | 1.00 | 98.0 | 0.000689 | 0.0000070 | No
05/04/2024 | 09:12 | AP365A | URBAN | Third Party | Vehicle impact | 340.00 | 837.7 | 0.439125 | 0.0005242 | No
05/04/2024 | 09:12 | NL111P | URBAN | Planned |  | 197.00 | 138.0 | 0.041914 | 0.0003037 | No
05/04/2024 | 09:25 | AP132B | URBAN | Unknown | Unknown | 1.00 | 240.0 | 0.000370 | 0.0000015 | No
05/04/2024 | 09:29 | GU118 | LONG RURAL | Planned |  | 4.00 | 322.0 | 0.009243 | 0.0000287 | No
05/04/2024 | 10:14 | SM411E | URBAN | Overloads |  | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
05/04/2024 | 10:28 | CM22 | LONG RURAL | Planned |  | 1.00 | 150.0 | 0.001076 | 0.0000072 | No
05/04/2024 | 10:40 | AP425C | URBAN | Planned |  | 93.00 | 183.0 | 0.026239 | 0.0001434 | No
05/04/2024 | 13:34 | EL13 | URBAN | Unknown | Unknown | 1.00 | 4,215.0 | 0.006498 | 0.0000015 | No
05/04/2024 | 13:38 | VH45 | SHORT RURAL | Asset failure | LV | 15.33 | 218.0 | 0.023517 | 0.0001079 | No
05/04/2024 | 16:14 | HH432F | URBAN | Overloads |  | 2.00 | 247.0 | 0.000762 | 0.0000031 | No
05/04/2024 | 16:23 | GA800A | SHORT RURAL | Third Party | Vehicle impact | 2.00 | 549.0 | 0.007725 | 0.0000141 | No
05/04/2024 | 16:50 | HH386F | URBAN | Unknown | Unknown | 1,204.00 | 74.0 | 0.137364 | 0.0018563 | No
05/04/2024 | 17:01 | HH118D | URBAN | Network business | Switching and protection error | 105.00 | 95.0 | 0.015379 | 0.0001619 | No
05/04/2024 | 18:21 | CM12 | LONG RURAL | Asset failure | LV | 2.00 | 195.0 | 0.002799 | 0.0000144 | No
05/04/2024 | 19:35 | EL260C | URBAN | Asset failure | LV | 18.00 | 169.4 | 0.004702 | 0.0000278 | No
05/04/2024 | 20:09 | HH177F | URBAN | Asset failure | LV | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
05/04/2024 | 20:23 | HH121E | URBAN | Unknown | Unknown | 548.00 | 7.2 | 0.006062 | 0.0008449 | No
05/04/2024 | 20:45 | AP149B | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
06/04/2024 | 07:13 | SA16 | URBAN | Asset failure | LV | 18.00 | 88.0 | 0.002442 | 0.0000278 | No
06/04/2024 | 07:18 | R15 | LONG RURAL | Unknown | Unknown | 94.00 | 327.4 | 0.220873 | 0.0006746 | No
06/04/2024 | 07:27 | AP372D | URBAN | Unknown | Unknown | 2.00 | 169.0 | 0.000521 | 0.0000031 | No
06/04/2024 | 08:29 | SM410B | URBAN | Asset failure | LV | 2.00 | 258.0 | 0.000796 | 0.0000031 | No
06/04/2024 | 08:30 | AP829L | URBAN | Planned |  | 1.00 | 429.0 | 0.000661 | 0.0000015 | No
06/04/2024 | 08:30 | SM410B | URBAN | Asset failure | LV | 2.00 | 247.0 | 0.000762 | 0.0000031 | No
06/04/2024 | 10:16 | WHY12 | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
06/04/2024 | 12:23 | ME231B | URBAN | Asset failure | LV | 18.00 | 68.1 | 0.001890 | 0.0000278 | No
06/04/2024 | 13:09 | AP355D | URBAN | Planned |  | 21.00 | 84.0 | 0.002720 | 0.0000324 | No
06/04/2024 | 13:19 | AP355D | URBAN | Planned |  | 2.00 | 69.0 | 0.000213 | 0.0000031 | No
06/04/2024 | 13:27 | HH121D | URBAN | Asset failure | LV | 1.00 | 278.0 | 0.000429 | 0.0000015 | No
06/04/2024 | 14:12 | R09 | LONG RURAL | Overloads |  | 1.00 | 110.0 | 0.000789 | 0.0000072 | No
06/04/2024 | 15:14 | HH403A | URBAN | Asset failure | LV | 22.00 | 236.0 | 0.008005 | 0.0000339 | No
06/04/2024 | 16:23 | AP424F | URBAN | Asset failure | LV | 16.00 | 683.0 | 0.016848 | 0.0000247 | No
06/04/2024 | 19:31 | AP214B | URBAN | Overloads |  | 36.00 | 168.0 | 0.009325 | 0.0000555 | No
06/04/2024 | 21:07 | HH177B | URBAN | Overloads |  | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
06/04/2024 | 21:17 | HH341K | URBAN | Third Party | Vehicle impact | 44.00 | 327.0 | 0.022183 | 0.0000678 | No
07/04/2024 | 04:16 | CV757A | LONG RURAL | Asset failure | HV | 544.00 | 189.0 | 0.737676 | 0.0039039 | No
07/04/2024 | 08:07 | M81 | LONG RURAL | Unknown | Unknown | 1.00 | 284.0 | 0.002038 | 0.0000072 | No
07/04/2024 | 08:35 | EL07 | URBAN | Planned |  | 25.00 | 292.8 | 0.011286 | 0.0000385 | No
07/04/2024 | 09:00 | AP365E | URBAN | Planned |  | 18.00 | 233.0 | 0.006466 | 0.0000278 | No
07/04/2024 | 09:52 | SA20 | URBAN | Asset failure | LV | 25.00 | 878.0 | 0.033841 | 0.0000385 | No
07/04/2024 | 09:55 | PL15 | LONG RURAL | Unknown | Unknown | 2.00 | 103.0 | 0.001478 | 0.0000144 | No
07/04/2024 | 10:20 | HH429B | URBAN | Overloads |  | 9.00 | 165.0 | 0.002290 | 0.0000139 | No
07/04/2024 | 12:00 | GU31 | LONG RURAL | Unknown | Unknown | 1.00 | 239.0 | 0.001715 | 0.0000072 | No
07/04/2024 | 13:57 | SA744C | URBAN | Third Party | Vehicle impact | 12.67 | 143.0 | 0.002793 | 0.0000195 | No
07/04/2024 | 15:03 | WHY01 | SHORT RURAL | Asset failure | LV | 41.00 | 112.0 | 0.032307 | 0.0002885 | No
07/04/2024 | 16:26 | PP18 | LONG RURAL | Planned |  | 12.00 | 82.0 | 0.007062 | 0.0000861 | No
07/04/2024 | 19:22 | SM216G | URBAN | Asset failure | LV | 19.67 | 143.0 | 0.004336 | 0.0000303 | No
07/04/2024 | 19:37 | SM216G | URBAN | Asset failure | LV | 2.00 | 141.0 | 0.000435 | 0.0000031 | No
07/04/2024 | 22:10 | HH409C | URBAN | Planned |  | 1.00 | 362.0 | 0.000558 | 0.0000015 | No
07/04/2024 | 22:18 | HH409B | URBAN | Planned |  | 214.00 | 317.8 | 0.104852 | 0.0003299 | No
07/04/2024 | 22:25 | HH409C | URBAN | Planned |  | 1.00 | 343.0 | 0.000529 | 0.0000015 | No
07/04/2024 | 23:05 | EL01Q | URBAN | Overloads |  | 16.00 | 363.0 | 0.008955 | 0.0000247 | No
08/04/2024 | 03:20 | PL11 | LONG RURAL | Asset failure | HV | 1.00 | 404.0 | 0.002899 | 0.0000072 | No
08/04/2024 | 07:36 | KA29 | LONG RURAL | Asset failure | LV | 4.67 | 149.3 | 0.005000 | 0.0000335 | No
08/04/2024 | 08:19 | VH45 | SHORT RURAL | Overloads |  | 1.00 | 200.0 | 0.001407 | 0.0000070 | No
08/04/2024 | 08:32 | BT02 | LONG RURAL | Planned |  | 40.00 | 344.0 | 0.098746 | 0.0002871 | No
08/04/2024 | 08:42 | MG04 | SHORT RURAL | Planned |  | 12.00 | 329.0 | 0.027776 | 0.0000844 | No
08/04/2024 | 08:54 | SD54300 | LONG RURAL | Planned |  | 1.00 | 127.0 | 0.000911 | 0.0000072 | No
08/04/2024 | 08:54 | SG04 | SHORT RURAL | Unknown | Unknown | 66.00 | 174.0 | 0.080796 | 0.0004643 | No
08/04/2024 | 09:03 | NU20 | LONG RURAL | Unknown | Unknown | 86.67 | 96.0 | 0.059707 | 0.0006219 | No
08/04/2024 | 09:38 | SB19 | LONG RURAL | Planned |  | 2.00 | 145.0 | 0.002081 | 0.0000144 | No
08/04/2024 | 09:43 | GA08 | LONG RURAL | Planned |  | 1,279.00 | 27.0 | 0.247820 | 0.0091785 | No
08/04/2024 | 09:46 | MV64 | SHORT RURAL | Third Party | Vehicle impact | 20.00 | 291.0 | 0.040947 | 0.0001407 | No
08/04/2024 | 09:46 | HH409F | URBAN | Planned |  | 63.00 | 153.0 | 0.014861 | 0.0000971 | No
08/04/2024 | 10:15 | GA10 | LONG RURAL | Planned |  | 96.00 | 215.0 | 0.148119 | 0.0006889 | No
08/04/2024 | 10:33 | BM41 | SHORT RURAL | Network business | Switching and protection error | 2.00 | 169.0 | 0.002378 | 0.0000141 | No
08/04/2024 | 11:04 | NL234B | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
08/04/2024 | 11:17 | VH22 | SHORT RURAL | Animal | Animal impact | 45.00 | 114.0 | 0.036092 | 0.0003166 | No
08/04/2024 | 11:52 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 365.0 | 0.002619 | 0.0000072 | No
08/04/2024 | 11:57 | SM126C | URBAN | Planned |  | 63.00 | 64.0 | 0.006216 | 0.0000971 | No
08/04/2024 | 12:34 | YK02 | SHORT RURAL | Asset failure | LV | 2.00 | 200.0 | 0.002814 | 0.0000141 | No
08/04/2024 | 13:31 | CM18 | LONG RURAL | Weather |  | 652.00 | 237.1 | 1.109597 | 0.0046790 | No
08/04/2024 | 14:35 | NL511A | URBAN | Asset failure | LV | 1.00 | 461.0 | 0.000711 | 0.0000015 | No
08/04/2024 | 15:01 | MV14 | SHORT RURAL | Asset failure | HV | 53.00 | 394.6 | 0.147147 | 0.0003729 | No
08/04/2024 | 15:37 | ST24 | SHORT RURAL | Weather |  | 152.33 | 118.1 | 0.126554 | 0.0010717 | No
08/04/2024 | 16:14 | GA13 | LONG RURAL | Overloads |  | 2.00 | 86.0 | 0.001234 | 0.0000144 | No
08/04/2024 | 16:17 | NU15 | LONG RURAL | Animal | Animal impact | 1.00 | 307.0 | 0.002203 | 0.0000072 | No
08/04/2024 | 16:39 | HH107B | URBAN | Asset failure | LV | 1.00 | 298.0 | 0.000459 | 0.0000015 | No
08/04/2024 | 17:45 | GA03 | LONG RURAL | Animal | Animal impact | 1.00 | 183.0 | 0.001313 | 0.0000072 | No
08/04/2024 | 18:12 | HH341E | URBAN | Asset failure | LV | 24.67 | 141.0 | 0.005362 | 0.0000380 | No
08/04/2024 | 18:18 | SM374A | URBAN | Third Party | Unauthorised access | 8.00 | 282.0 | 0.003478 | 0.0000123 | No
08/04/2024 | 18:28 | YK12 | LONG RURAL | Animal | Animal impact | 1.00 | 178.0 | 0.001277 | 0.0000072 | No
08/04/2024 | 18:36 | MB12 | SHORT RURAL | Overloads |  | 3.00 | 175.0 | 0.003694 | 0.0000211 | No
08/04/2024 | 18:48 | NL111Q | URBAN | Asset failure | LV | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
08/04/2024 | 19:46 | CL12 | LONG RURAL | Weather |  | 89.00 | 407.4 | 0.260178 | 0.0006387 | No
09/04/2024 | 06:35 | MTB22 | SHORT RURAL | Asset failure | HV | 16.00 | 314.0 | 0.035346 | 0.0001126 | No
09/04/2024 | 07:17 | LX48 | SHORT RURAL | Unknown | Unknown | 38.00 | 312.0 | 0.083413 | 0.0002673 | No
09/04/2024 | 07:35 | MTB21 | SHORT RURAL | Unknown | Unknown | 1.00 | 442.0 | 0.003110 | 0.0000070 | No
09/04/2024 | 08:00 | WK31 | SHORT RURAL | Planned |  | 38.00 | 331.0 | 0.088492 | 0.0002673 | No
09/04/2024 | 08:02 | ME116D | URBAN | Asset failure | LV | 1.00 | 290.0 | 0.000447 | 0.0000015 | No
09/04/2024 | 08:48 | SD54300 | LONG RURAL | Planned |  | 2.00 | 87.0 | 0.001249 | 0.0000144 | No
09/04/2024 | 08:54 | MI16 | LONG RURAL | Planned |  | 234.00 | 340.0 | 0.570949 | 0.0016793 | No
09/04/2024 | 09:04 | GU19 | LONG RURAL | Planned |  | 5.00 | 334.8 | 0.012013 | 0.0000359 | No
09/04/2024 | 09:13 | CM18 | LONG RURAL | Planned |  | 4.00 | 300.0 | 0.008612 | 0.0000287 | No
09/04/2024 | 09:23 | SD35200 | LONG RURAL | Asset failure | Subtransmission | 11.33 | 138.0 | 0.011224 | 0.0000813 | No
09/04/2024 | 09:30 | HH386F | URBAN | Planned |  | 26.00 | 324.0 | 0.012988 | 0.0000401 | No
09/04/2024 | 09:30 | AP227D | URBAN | Asset failure | LV | 1.00 | 60.0 | 0.000093 | 0.0000015 | No
09/04/2024 | 10:02 | NA36 | LONG RURAL | Planned |  | 2.00 | 184.0 | 0.002641 | 0.0000144 | No
09/04/2024 | 10:08 | CD17 | LONG RURAL | Planned |  | 11.00 | 173.0 | 0.013657 | 0.0000789 | No
09/04/2024 | 10:09 | VH22 | SHORT RURAL | Unknown | Unknown | 1.00 | 129.0 | 0.000908 | 0.0000070 | No
09/04/2024 | 10:28 | YK30 | LONG RURAL | Planned |  | 85.00 | 161.9 | 0.098768 | 0.0006100 | No
09/04/2024 | 10:39 | GA22 | SHORT RURAL | Planned |  | 1.00 | 221.0 | 0.001555 | 0.0000070 | No
09/04/2024 | 11:35 | SA36 | URBAN | Other |  | 1.00 | 1,326.0 | 0.002044 | 0.0000015 | No
09/04/2024 | 12:22 | WK31 | SHORT RURAL | Planned |  | 1.00 | 102.0 | 0.000718 | 0.0000070 | No
09/04/2024 | 15:46 | CM12 | LONG RURAL | Asset failure | HV | 1.00 | 60.0 | 0.000431 | 0.0000072 | No
09/04/2024 | 16:32 | CV753A | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 1.00 | 87.0 | 0.000624 | 0.0000072 | No
09/04/2024 | 16:51 | MI16 | LONG RURAL | Overloads |  | 20.33 | 133.0 | 0.019407 | 0.0001459 | No
09/04/2024 | 16:52 | MB32 | LONG RURAL | Asset failure | HV | 120.00 | 76.0 | 0.065448 | 0.0008612 | No
09/04/2024 | 17:00 | NA34 | LONG RURAL | Unknown | Unknown | 4.00 | 114.0 | 0.003272 | 0.0000287 | No
09/04/2024 | 19:39 | MV64 | SHORT RURAL | Overloads |  | 1.00 | 300.0 | 0.002111 | 0.0000070 | No
09/04/2024 | 19:43 | NL234A | URBAN | Unknown | Unknown | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
09/04/2024 | 21:10 | CN25 | LONG RURAL | Animal | Animal impact | 86.00 | 227.0 | 0.140103 | 0.0006172 | No
09/04/2024 | 21:37 | AP214D | URBAN | Animal | Animal impact | 1,614.00 | 33.0 | 0.082117 | 0.0024884 | No
09/04/2024 | 21:41 | AP425D | URBAN | Animal | Animal impact | 103.00 | 45.0 | 0.007146 | 0.0001588 | No
09/04/2024 | 21:44 | AP214B | URBAN | Animal | Animal impact | 3.00 | 42.0 | 0.000194 | 0.0000046 | No
09/04/2024 | 22:44 | R30 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 1,330.00 | 801.7 | 7.652314 | 0.0095445 | No
09/04/2024 | 22:44 | R30 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 1,039.00 | 1,507.5 | 11.019956 | 0.0073099 | No
09/04/2024 | 22:44 | R35 | LONG RURAL | Unknown | Unknown | 69.00 | 1,096.0 | 0.542703 | 0.0004952 | No
09/04/2024 | 22:45 | MTB71 | SHORT RURAL | Planned |  | 223.00 | 282.2 | 0.442800 | 0.0015689 | No
09/04/2024 | 23:31 | R12 | LONG RURAL | Asset failure | HV | 86.00 | 482.0 | 0.297473 | 0.0006172 | No
09/04/2024 | 23:55 | HH130D | URBAN | Asset failure | LV | 17.00 | 228.0 | 0.005976 | 0.0000262 | No
10/04/2024 | 02:30 | MG22 | LONG RURAL | Asset failure | HV | 2.00 | 44.0 | 0.000632 | 0.0000144 | No
10/04/2024 | 03:57 | MTB22 | SHORT RURAL | Weather |  | 16.00 | 61.0 | 0.006867 | 0.0001126 | No
10/04/2024 | 06:59 | WK65 | SHORT RURAL | Animal | Animal impact | 64.00 | 179.0 | 0.080599 | 0.0004503 | No
10/04/2024 | 07:52 | HH121D | URBAN | Asset failure | LV | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
10/04/2024 | 08:00 | WK31 | SHORT RURAL | Planned |  | 59.00 | 382.0 | 0.158566 | 0.0004151 | No
10/04/2024 | 08:14 | MT14 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 595.00 | 208.0 | 0.870712 | 0.0041861 | No
10/04/2024 | 08:39 | CD03 | SHORT RURAL | Planned |  | 84.00 | 179.0 | 0.105786 | 0.0005910 | No
10/04/2024 | 08:52 | SB01 | LONG RURAL | Planned |  | 32.00 | 25.0 | 0.005741 | 0.0002296 | No
10/04/2024 | 08:52 | CV09 | LONG RURAL | Planned |  | 5.00 | 22.0 | 0.000789 | 0.0000359 | No
10/04/2024 | 09:06 | SD54300 | LONG RURAL | Planned |  | 2.00 | 109.0 | 0.001564 | 0.0000144 | No
10/04/2024 | 09:18 | KI31 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 145.0 | 0.001041 | 0.0000072 | No
10/04/2024 | 09:18 | KI31 | SHORT RURAL | Asset failure | Subtransmission | 1,728.00 | 145.2 | 1.764853 | 0.0121573 | No
10/04/2024 | 09:28 | MI10 | LONG RURAL | Planned |  | 47.00 | 287.0 | 0.096802 | 0.0003373 | No
10/04/2024 | 09:42 | MV51 | SHORT RURAL | Planned |  | 5.00 | 271.0 | 0.009533 | 0.0000352 | No
10/04/2024 | 09:44 | GA09 | LONG RURAL | Planned |  | 1.00 | 42.0 | 0.000301 | 0.0000072 | No
10/04/2024 | 10:46 | PL07 | URBAN | Overloads |  | 1.00 | 1,211.0 | 0.001867 | 0.0000015 | No
10/04/2024 | 10:47 | SG07 | SHORT RURAL | Unknown | Unknown | 2.00 | 225.0 | 0.003166 | 0.0000141 | No
10/04/2024 | 13:05 | SM410C | URBAN | Third Party | Other | 2,775.00 | 29.0 | 0.124073 | 0.0042784 | No
10/04/2024 | 13:48 | HH496C | URBAN | Asset failure | LV | 7.00 | 13.0 | 0.000140 | 0.0000108 | No
10/04/2024 | 14:23 | HH121E | URBAN | Planned |  | 5.00 | 7.0 | 0.000054 | 0.0000077 | No
10/04/2024 | 14:27 | GA40 | SHORT RURAL | Planned |  | 53.00 | 23.0 | 0.008576 | 0.0003729 | No
10/04/2024 | 15:59 | VH45 | SHORT RURAL | Asset failure | LV | 1.00 | 460.0 | 0.003236 | 0.0000070 | No
10/04/2024 | 17:12 | SA17 | URBAN | Overloads |  | 1.00 | 103.0 | 0.000159 | 0.0000015 | No
10/04/2024 | 19:07 | HH496A | URBAN | Asset failure | LV | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
10/04/2024 | 22:36 | AP365D1 | URBAN | Planned |  | 15.00 | 253.0 | 0.005851 | 0.0000231 | No
10/04/2024 | 23:56 | GA23 | SHORT RURAL | Asset failure | HV | 61.67 | 159.0 | 0.068983 | 0.0004339 | No
11/04/2024 | 02:05 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 125.00 | 147.0 | 0.129277 | 0.0008794 | No
11/04/2024 | 06:39 | SD38200 | LONG RURAL | Animal | Animal impact | 3.00 | 205.0 | 0.004413 | 0.0000215 | No
11/04/2024 | 06:49 | R15 | LONG RURAL | Weather |  | 95.00 | 228.2 | 0.155576 | 0.0006818 | No
11/04/2024 | 08:33 | YK04 | SHORT RURAL | Planned |  | 13.00 | 392.0 | 0.035853 | 0.0000915 | No
11/04/2024 | 08:50 | CV25 | LONG RURAL | Planned |  | 1.00 | 122.0 | 0.000876 | 0.0000072 | No
11/04/2024 | 08:53 | CL05 | LONG RURAL | Asset failure | LV | 1.00 | 439.0 | 0.003150 | 0.0000072 | No
11/04/2024 | 09:06 | CL22 | LONG RURAL | Unknown | Unknown | 1.00 | 423.0 | 0.003036 | 0.0000072 | No
11/04/2024 | 09:16 | CM21 | LONG RURAL | Planned |  | 65.00 | 312.0 | 0.145536 | 0.0004665 | No
11/04/2024 | 09:24 | NL234A | URBAN | Planned |  | 54.00 | 257.0 | 0.021396 | 0.0000833 | No
11/04/2024 | 09:55 | SM216A | URBAN | Asset failure | LV | 1.00 | 57.0 | 0.000088 | 0.0000015 | No
11/04/2024 | 09:56 | LX41 | SHORT RURAL | Planned |  | 71.00 | 271.0 | 0.135370 | 0.0004995 | No
11/04/2024 | 09:58 | CD15 | LONG RURAL | Planned |  | 8.00 | 216.0 | 0.012401 | 0.0000574 | No
11/04/2024 | 10:23 | ST12 | SHORT RURAL | Third Party | Vehicle impact | 5.00 | 127.0 | 0.004468 | 0.0000352 | No
11/04/2024 | 10:36 | MG46 | SHORT RURAL | Asset failure | LV | 90.00 | 301.0 | 0.190591 | 0.0006332 | No
11/04/2024 | 11:13 | SM126B | URBAN | Asset failure | LV | 4.00 | 35.0 | 0.000216 | 0.0000062 | No
11/04/2024 | 11:39 | MB63 | LONG RURAL | Asset failure | LV | 1.00 | 591.0 | 0.004241 | 0.0000072 | No
11/04/2024 | 12:20 | MB13 | SHORT RURAL | Asset failure | LV | 7.00 | 70.0 | 0.003447 | 0.0000492 | No
11/04/2024 | 12:30 | NL234A | URBAN | Third Party | Vehicle impact | 6.67 | 57.0 | 0.000586 | 0.0000103 | No
11/04/2024 | 12:42 | M21 | LONG RURAL | Asset failure | LV | 1.00 | 382.0 | 0.002741 | 0.0000072 | No
11/04/2024 | 13:00 | PA23 | LONG RURAL | Weather |  | 89.00 | 55.0 | 0.035128 | 0.0006387 | No
11/04/2024 | 13:30 | SM411E | URBAN | Overloads |  | 1.00 | 229.0 | 0.000353 | 0.0000015 | No
11/04/2024 | 15:42 | BT03 | LONG RURAL | Third Party | Vehicle impact | 177.00 | 85.4 | 0.108506 | 0.0012702 | No
11/04/2024 | 16:24 | HH121F | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
11/04/2024 | 16:51 | VH10 | SHORT RURAL | Third Party | Vehicle impact | 86.00 | 264.0 | 0.159734 | 0.0006051 | No
11/04/2024 | 17:34 | SM411E | URBAN | Overloads |  | 1.00 | 177.0 | 0.000273 | 0.0000015 | No
11/04/2024 | 20:10 | SA36 | URBAN | Overloads |  | 2.00 | 477.0 | 0.001471 | 0.0000031 | No
11/04/2024 | 20:14 | MG11 | SHORT RURAL | Asset failure | HV | 8.00 | 131.0 | 0.007373 | 0.0000563 | No
11/04/2024 | 20:26 | GA800A | SHORT RURAL | Asset failure | LV | 1.00 | 191.0 | 0.001344 | 0.0000070 | No
11/04/2024 | 21:21 | HH341K | URBAN | Planned |  | 56.00 | 19.0 | 0.001640 | 0.0000863 | No
11/04/2024 | 21:47 | SM349F | URBAN | Asset failure | LV | 80.00 | 111.7 | 0.013772 | 0.0001233 | No
11/04/2024 | 22:03 | HH102D | URBAN | Planned |  | 51.00 | 273.3 | 0.021492 | 0.0000786 | No
11/04/2024 | 22:42 | HH341K | URBAN | Planned |  | 56.00 | 160.0 | 0.013814 | 0.0000863 | No
11/04/2024 | 22:54 | PL07 | URBAN | Overloads |  | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
11/04/2024 | 23:18 | HH341K | URBAN | Planned |  | 2.00 | 107.0 | 0.000330 | 0.0000031 | No
12/04/2024 | 08:24 | EL16 | URBAN | Planned |  | 4.00 | 344.0 | 0.002121 | 0.0000062 | No
12/04/2024 | 08:31 | BM15 | SHORT RURAL | Asset failure | LV | 2.00 | 432.0 | 0.006079 | 0.0000141 | No
12/04/2024 | 08:38 | SM349H | URBAN | Planned |  | 122.00 | 404.0 | 0.075990 | 0.0001881 | No
12/04/2024 | 08:51 | MG11 | SHORT RURAL | Overloads |  | 1.00 | 147.0 | 0.001034 | 0.0000070 | No
12/04/2024 | 08:55 | SM126E | URBAN | Asset failure | LV | 1.00 | 2,526.0 | 0.003894 | 0.0000015 | No
12/04/2024 | 08:55 | VH45 | SHORT RURAL | Planned |  | 3.00 | 182.3 | 0.003848 | 0.0000211 | No
12/04/2024 | 08:56 | AP139D | URBAN | Planned |  | 71.00 | 262.0 | 0.028680 | 0.0001095 | No
12/04/2024 | 09:29 | NL234B | URBAN | Planned |  | 10.00 | 245.0 | 0.003777 | 0.0000154 | No
12/04/2024 | 10:49 | MB65 | LONG RURAL | Overloads |  | 1.33 | 584.0 | 0.005588 | 0.0000096 | No
12/04/2024 | 10:58 | WK21 | SHORT RURAL | Animal | Animal impact | 16.00 | 316.0 | 0.035571 | 0.0001126 | No
12/04/2024 | 11:02 | AP139B | URBAN | Planned |  | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
12/04/2024 | 11:36 | HH107A | URBAN | Planned |  | 1.00 | 103.0 | 0.000159 | 0.0000015 | No
12/04/2024 | 12:04 | GU13 | LONG RURAL | Planned |  | 3.00 | 252.0 | 0.005425 | 0.0000215 | No
12/04/2024 | 13:41 | AP424D | URBAN | Asset failure | LV | 4.33 | 328.0 | 0.002191 | 0.0000067 | No
12/04/2024 | 13:55 | VH11 | URBAN | Asset failure | LV | 2.00 | 85.0 | 0.000262 | 0.0000031 | No
12/04/2024 | 14:00 | WK72 | SHORT RURAL | Unknown | Unknown | 1.00 | 275.0 | 0.001935 | 0.0000070 | No
12/04/2024 | 14:18 | GA53 | SHORT RURAL | Asset failure | LV | 1.00 | 211.0 | 0.001484 | 0.0000070 | No
12/04/2024 | 14:29 | SD52300 | LONG RURAL | Planned |  | 8.00 | 2.0 | 0.000115 | 0.0000574 | No
12/04/2024 | 15:00 | SM126B | URBAN | Asset failure | LV | 1.00 | 1,138.0 | 0.001755 | 0.0000015 | No
12/04/2024 | 16:53 | GA41 | LONG RURAL | Asset failure | HV | 50.00 | 603.1 | 0.216388 | 0.0003588 | No
12/04/2024 | 17:39 | SG14 | SHORT RURAL | Asset failure | LV | 1.00 | 306.0 | 0.002153 | 0.0000070 | No
12/04/2024 | 17:47 | KA04 | LONG RURAL | Animal | Animal impact | 98.00 | 79.0 | 0.055559 | 0.0007033 | No
12/04/2024 | 17:57 | SD31100 | LONG RURAL | Animal | Animal impact | 12.00 | 11.0 | 0.000947 | 0.0000861 | No
12/04/2024 | 20:49 | HH121G | URBAN | Third Party | Vehicle impact | 163.00 | 439.6 | 0.110474 | 0.0002513 | No
12/04/2024 | 21:38 | HH177E | URBAN | Overloads |  | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
12/04/2024 | 21:44 | LX51 | SHORT RURAL | Planned |  | 1,020.00 | 4.0 | 0.028705 | 0.0071762 | No
13/04/2024 | 06:29 | MI15 | LONG RURAL | Unknown | Unknown | 26.00 | 233.0 | 0.043474 | 0.0001866 | No
13/04/2024 | 06:29 | CBD367Q | CBD | Animal | Animal impact | 1.00 | 216.0 | 0.031207 | 0.0001445 | No
13/04/2024 | 06:38 | KI41 | LONG RURAL | Animal | Animal impact | 95.00 | 105.0 | 0.071584 | 0.0006818 | No
13/04/2024 | 07:06 | ME427D | URBAN | Animal | Animal impact | 2.67 | 147.0 | 0.000604 | 0.0000041 | No
13/04/2024 | 08:15 | HH341K | URBAN | Planned |  | 193.00 | 126.3 | 0.037576 | 0.0002976 | No
13/04/2024 | 09:36 | HH428F | URBAN | Third Party | Vehicle impact | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
13/04/2024 | 11:47 | SA14 | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
13/04/2024 | 11:53 | SA35 | URBAN | Unknown | Unknown | 1.00 | 123.0 | 0.000190 | 0.0000015 | No
13/04/2024 | 12:12 | SA35 | URBAN | Unknown | Unknown | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
13/04/2024 | 14:13 | HH148B | URBAN | Asset failure | LV | 1.00 | 118.0 | 0.000182 | 0.0000015 | No
13/04/2024 | 14:48 | HH148B | URBAN | Other |  | 33.00 | 52.0 | 0.002646 | 0.0000509 | No
13/04/2024 | 16:05 | AP424F | URBAN | Asset failure | LV | 16.00 | 129.0 | 0.003182 | 0.0000247 | No
13/04/2024 | 18:01 | EL17 | URBAN | Planned |  | 3.00 | 102.0 | 0.000472 | 0.0000046 | No
13/04/2024 | 21:17 | ST21 | SHORT RURAL | Asset failure | LV | 20.00 | 156.0 | 0.021951 | 0.0001407 | No
14/04/2024 | 05:32 | MTB63 | SHORT RURAL | Asset failure | HV | 154.00 | 173.0 | 0.187454 | 0.0010835 | No
14/04/2024 | 06:09 | WK32 | SHORT RURAL | Overloads |  | 1.00 | 402.0 | 0.002828 | 0.0000070 | No
14/04/2024 | 06:11 | MTB62 | SHORT RURAL | Asset failure | LV | 1.00 | 409.0 | 0.002878 | 0.0000070 | No
14/04/2024 | 06:19 | MI28 | LONG RURAL | Unknown | Unknown | 51.00 | 277.0 | 0.101380 | 0.0003660 | No
14/04/2024 | 06:34 | WHY14 | URBAN | Weather |  | 97.33 | 128.4 | 0.019268 | 0.0001501 | No
14/04/2024 | 08:24 | ME347F | URBAN | Planned |  | 58.00 | 351.0 | 0.031387 | 0.0000894 | No
14/04/2024 | 08:30 | SG07 | SHORT RURAL | Asset failure | LV | 1.00 | 273.0 | 0.001921 | 0.0000070 | No
14/04/2024 | 08:48 | SA14 | URBAN | Planned |  | 135.00 | 259.5 | 0.054005 | 0.0002081 | No
14/04/2024 | 08:54 | AP214C | URBAN | Planned |  | 96.00 | 365.8 | 0.054134 | 0.0001480 | No
14/04/2024 | 09:01 | NL760C | URBAN | Planned |  | 290.00 | 305.0 | 0.136374 | 0.0004471 | No
14/04/2024 | 09:05 | EL07 | URBAN | Planned |  | 26.00 | 195.0 | 0.007817 | 0.0000401 | No
14/04/2024 | 09:05 | SM402E | URBAN | Planned |  | 4.00 | 204.0 | 0.001258 | 0.0000062 | No
14/04/2024 | 09:11 | PL803C | URBAN | Planned |  | 159.00 | 239.0 | 0.058588 | 0.0002451 | No
14/04/2024 | 09:25 | MTB13 | SHORT RURAL | Planned |  | 13.00 | 294.0 | 0.026890 | 0.0000915 | No
14/04/2024 | 10:29 | AP214C | URBAN | Network business | Switching and protection error | 3.00 | 36.0 | 0.000167 | 0.0000046 | No
14/04/2024 | 11:07 | BU13 | LONG RURAL | Asset failure | LV | 1.00 | 419.0 | 0.003007 | 0.0000072 | No
14/04/2024 | 11:47 | HH496C | URBAN | Asset failure | LV | 1.00 | 315.0 | 0.000486 | 0.0000015 | No
14/04/2024 | 14:57 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 197.0 | 0.001386 | 0.0000070 | No
14/04/2024 | 16:41 | VH16 | SHORT RURAL | Asset failure | LV | 1.00 | 159.0 | 0.001119 | 0.0000070 | No
14/04/2024 | 17:41 | MI14 | LONG RURAL | Asset failure | LV | 1.00 | 403.0 | 0.002892 | 0.0000072 | No
14/04/2024 | 17:49 | HH386F | URBAN | Overloads |  | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
14/04/2024 | 17:53 | GU15 | LONG RURAL | Asset failure | LV | 1.00 | 475.0 | 0.003409 | 0.0000072 | No
14/04/2024 | 20:50 | HH121H | URBAN | Planned |  | 34.00 | 458.1 | 0.024013 | 0.0000524 | No
14/04/2024 | 22:16 | HH341G | URBAN | Planned |  | 1.00 | 376.0 | 0.000580 | 0.0000015 | No
15/04/2024 | 06:56 | W33 | LONG RURAL | Weather |  | 33.00 | 365.0 | 0.086439 | 0.0002368 | No
15/04/2024 | 09:06 | PL10 | LONG RURAL | Planned |  | 2.00 | 220.0 | 0.003158 | 0.0000144 | No
15/04/2024 | 09:09 | EL13 | URBAN | Asset failure | LV | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
15/04/2024 | 09:12 | NL210C | URBAN | Planned |  | 153.00 | 193.0 | 0.045537 | 0.0002359 | No
15/04/2024 | 09:22 | ST11 | SHORT RURAL | Planned |  | 116.00 | 329.8 | 0.269185 | 0.0008161 | No
15/04/2024 | 09:30 | NL760C | URBAN | Network business | Switching and protection error | 3.00 | 87.0 | 0.000402 | 0.0000046 | No
15/04/2024 | 09:50 | NU08 | LONG RURAL | Planned |  | 1.00 | 122.0 | 0.000876 | 0.0000072 | No
15/04/2024 | 10:25 | SB15 | LONG RURAL | Planned |  | 1.00 | 218.0 | 0.001564 | 0.0000072 | No
15/04/2024 | 10:35 | SD41300 | SHORT RURAL | Planned |  | 1.00 | 213.0 | 0.001499 | 0.0000070 | No
15/04/2024 | 11:02 | YK24 | LONG RURAL | Planned |  | 68.00 | 165.0 | 0.080518 | 0.0004880 | No
15/04/2024 | 12:07 | SA36 | URBAN | Asset failure | LV | 8.00 | 82.0 | 0.001011 | 0.0000123 | No
15/04/2024 | 12:52 | MB44 | LONG RURAL | Asset failure | LV | 1.00 | 308.0 | 0.002210 | 0.0000072 | No
15/04/2024 | 13:44 | MG05 | LONG RURAL | Third Party | Vehicle impact | 3.00 | 169.0 | 0.003638 | 0.0000215 | No
15/04/2024 | 13:59 | NL210C | URBAN | Asset failure | LV | 8.00 | 69.0 | 0.000851 | 0.0000123 | No
15/04/2024 | 14:44 | VH23 | SHORT RURAL | Asset failure | LV | 41.00 | 90.0 | 0.025961 | 0.0002885 | No
15/04/2024 | 14:45 | KI44 | LONG RURAL | Asset failure | LV | 1.00 | 117.0 | 0.000840 | 0.0000072 | No
15/04/2024 | 15:32 | EL14 | URBAN | Overloads |  | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
15/04/2024 | 15:34 | VH33 | SHORT RURAL | Unknown | Unknown | 4.00 | 3,600.0 | 0.101311 | 0.0000281 | No
15/04/2024 | 15:51 | GA43 | SHORT RURAL | Overloads |  | 1.00 | 340.0 | 0.002392 | 0.0000070 | No
15/04/2024 | 16:04 | AP125D | URBAN | Asset failure | LV | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
15/04/2024 | 17:01 | HH121D | URBAN | Asset failure | LV | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
15/04/2024 | 17:16 | MB44 | LONG RURAL | Asset failure | HV | 9.00 | 42.0 | 0.002713 | 0.0000646 | No
15/04/2024 | 19:08 | HH429C | URBAN | Asset failure | LV | 1.00 | 59.0 | 0.000091 | 0.0000015 | No
15/04/2024 | 19:46 | SM179A | URBAN | Asset failure | LV | 12.00 | 52.0 | 0.000962 | 0.0000185 | No
15/04/2024 | 22:50 | G31 | LONG RURAL | Unknown | Unknown | 54.00 | 248.0 | 0.096105 | 0.0003875 | No
15/04/2024 | 23:00 | LC01 | LONG RURAL | Asset failure | HV | 125.00 | 721.0 | 0.646767 | 0.0008970 | No
15/04/2024 | 23:00 | LC01 | SHORT RURAL | Asset failure | HV | 230.00 | 755.5 | 1.222592 | 0.0016182 | No
16/04/2024 | 01:12 | HH145A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 719.00 | 148.2 | 0.164237 | 0.0011085 | No
16/04/2024 | 01:17 | GA15 | SHORT RURAL | Weather |  | 14.00 | 107.0 | 0.010539 | 0.0000985 | No
16/04/2024 | 05:37 | SM411A | URBAN | Asset failure | LV | 1.00 | 156.0 | 0.000241 | 0.0000015 | No
16/04/2024 | 07:11 | HH341K | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
16/04/2024 | 08:05 | NU02 | LONG RURAL | Planned |  | 90.00 | 446.0 | 0.288058 | 0.0006459 | No
16/04/2024 | 08:27 | MB24 | SHORT RURAL | Asset failure | LV | 1.00 | 172.0 | 0.001210 | 0.0000070 | No
16/04/2024 | 08:33 | MV64 | SHORT RURAL | Planned |  | 677.00 | 310.6 | 1.479331 | 0.0047630 | No
16/04/2024 | 08:58 | R25 | LONG RURAL | Planned |  | 26.00 | 333.0 | 0.062133 | 0.0001866 | No
16/04/2024 | 09:00 | NL451C | URBAN | Planned |  | 191.00 | 72.8 | 0.021444 | 0.0002945 | No
16/04/2024 | 09:06 | HH341J | URBAN | Planned |  | 291.00 | 234.9 | 0.105383 | 0.0004487 | No
16/04/2024 | 09:07 | PP12 | LONG RURAL | Asset failure | HV | 21.00 | 256.3 | 0.038630 | 0.0001507 | No
16/04/2024 | 09:30 | EL13 | URBAN | Planned |  | 102.00 | 151.0 | 0.023746 | 0.0001573 | No
16/04/2024 | 09:45 | CV16 | LONG RURAL | Planned |  | 12.00 | 147.0 | 0.012659 | 0.0000861 | No
16/04/2024 | 09:57 | HH496C | URBAN | Asset failure | LV | 1.00 | 368.0 | 0.000567 | 0.0000015 | No
16/04/2024 | 10:22 | MI08 | LONG RURAL | Planned |  | 8.00 | 274.0 | 0.015731 | 0.0000574 | No
16/04/2024 | 12:24 | AP355H | URBAN | Asset failure | LV | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
16/04/2024 | 13:56 | BM34 | SHORT RURAL | Animal | Animal impact | 14.33 | 126.0 | 0.012706 | 0.0001008 | No
16/04/2024 | 15:08 | SG07 | SHORT RURAL | Asset failure | LV | 1.00 | 427.0 | 0.003004 | 0.0000070 | No
16/04/2024 | 17:05 | WHY12 | URBAN | Unknown | Unknown | 1.00 | 23.0 | 0.000035 | 0.0000015 | No
16/04/2024 | 17:26 | MG41 | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
16/04/2024 | 18:38 | MG52 | URBAN | Asset failure | LV | 117.00 | 53.0 | 0.009560 | 0.0001804 | No
16/04/2024 | 20:14 | MB123 | LONG RURAL | Planned |  | 1,239.00 | 579.9 | 5.156473 | 0.0088915 | No
16/04/2024 | 21:06 | VH22 | SHORT RURAL | Unknown | Unknown | 66.00 | 10.8 | 0.005009 | 0.0004643 | No
16/04/2024 | 21:09 | MV64 | SHORT RURAL | Asset failure | LV | 68.00 | 45.0 | 0.021529 | 0.0004784 | No
16/04/2024 | 21:55 | AP139B | URBAN | Planned |  | 8.00 | 219.0 | 0.002701 | 0.0000123 | No
17/04/2024 | 01:05 | NU33 | LONG RURAL | Animal | Animal impact | 503.00 | 146.0 | 0.527015 | 0.0036097 | No
17/04/2024 | 10:20 | EL10 | URBAN | Asset failure | LV | 1.00 | 2,251.0 | 0.003470 | 0.0000015 | No
18/04/2024 | 01:46 | PP03 | URBAN | Asset failure | LV | 18.00 | 176.0 | 0.004884 | 0.0000278 | No
18/04/2024 | 05:42 | SM126A | URBAN | Network business | Switching and protection error | 29.67 | 185.0 | 0.008462 | 0.0000457 | No
18/04/2024 | 08:00 | MT09 | LONG RURAL | Planned |  | 25.00 | 275.0 | 0.049337 | 0.0001794 | No
18/04/2024 | 08:24 | HH341D | URBAN | Asset failure | LV | 6.00 | 222.0 | 0.002054 | 0.0000093 | No
18/04/2024 | 08:48 | AP425A | URBAN | Planned |  | 1,526.00 | 20.0 | 0.047005 | 0.0023527 | No
18/04/2024 | 08:58 | CD17 | LONG RURAL | Planned |  | 2.00 | 46.0 | 0.000660 | 0.0000144 | No
18/04/2024 | 09:06 | CM10 | LONG RURAL | Planned |  | 70.00 | 364.4 | 0.183068 | 0.0005023 | No
18/04/2024 | 09:20 | SM349D | URBAN | Planned |  | 240.00 | 70.9 | 0.026244 | 0.0003700 | No
18/04/2024 | 09:30 | SD40102 | LONG RURAL | Asset failure | Subtransmission | 150.00 | 85.9 | 0.092424 | 0.0010764 | No
18/04/2024 | 09:37 | MTB11 | LONG RURAL | Planned |  | 1.00 | 58.0 | 0.000416 | 0.0000072 | No
18/04/2024 | 09:37 | MTB11 | SHORT RURAL | Planned |  | 414.00 | 59.9 | 0.174354 | 0.0029127 | No
18/04/2024 | 09:44 | NU19 | LONG RURAL | Planned |  | 1,130.00 | 4.0 | 0.032437 | 0.0081093 | No
18/04/2024 | 09:44 | R33 | LONG RURAL | Planned |  | 105.00 | 1.0 | 0.000754 | 0.0007535 | No
18/04/2024 | 09:49 | LM63 | LONG RURAL | Planned |  | 9.00 | 247.0 | 0.015953 | 0.0000646 | No
18/04/2024 | 10:10 | GA36 | LONG RURAL | Planned |  | 93.00 | 170.0 | 0.113458 | 0.0006674 | No
18/04/2024 | 10:14 | MG42 | SHORT RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 2.00 | 20.0 | 0.000281 | 0.0000141 | No
18/04/2024 | 10:15 | R25 | LONG RURAL | Planned |  | 1.00 | 274.0 | 0.001966 | 0.0000072 | No
18/04/2024 | 11:15 | SG13 | SHORT RURAL | Third Party | Vehicle impact | 3.00 | 301.7 | 0.006367 | 0.0000211 | No
18/04/2024 | 12:13 | AP139C | URBAN | Asset failure | LV | 6.00 | 154.0 | 0.001425 | 0.0000093 | No
18/04/2024 | 12:48 | BT02 | LONG RURAL | Unknown | Unknown | 2.00 | 243.0 | 0.003488 | 0.0000144 | No
18/04/2024 | 13:27 | CD17 | LONG RURAL | Planned |  | 1.00 | 30.0 | 0.000215 | 0.0000072 | No
18/04/2024 | 13:46 | AP149E | URBAN | Asset failure | LV | 1.00 | 1,555.0 | 0.002397 | 0.0000015 | No
18/04/2024 | 15:18 | R25 | LONG RURAL | Planned |  | 105.00 | 2.0 | 0.001507 | 0.0007535 | No
18/04/2024 | 15:27 | HH121E | URBAN | Overloads |  | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
18/04/2024 | 15:39 | AP425A | URBAN | Asset failure | LV | 40.00 | 198.0 | 0.012211 | 0.0000617 | No
18/04/2024 | 16:43 | SA744C | URBAN | Asset failure | LV | 12.00 | 73.0 | 0.001351 | 0.0000185 | No
18/04/2024 | 16:44 | SM410D | URBAN | Overloads |  | 1.00 | 625.0 | 0.000964 | 0.0000015 | No
18/04/2024 | 17:23 | SG04 | SHORT RURAL | Unknown | Unknown | 45.67 | 241.0 | 0.077430 | 0.0003213 | No
18/04/2024 | 18:34 | SG04 | SHORT RURAL | Unknown | Unknown | 2.00 | 205.0 | 0.002885 | 0.0000141 | No
18/04/2024 | 21:44 | CN52 | LONG RURAL | Unknown | Unknown | 86.00 | 408.1 | 0.251875 | 0.0006172 | No
19/04/2024 | 00:01 | SM350F | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
19/04/2024 | 01:03 | EL02 | URBAN | Weather |  | 768.00 | 102.7 | 0.121598 | 0.0011841 | No
19/04/2024 | 01:58 | MB02 | LONG RURAL | Unknown | Unknown | 105.00 | 624.6 | 0.470645 | 0.0007535 | No
19/04/2024 | 02:02 | HH121F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 487.00 | 122.0 | 0.091602 | 0.0007508 | No
19/04/2024 | 02:57 | HH341K | URBAN | Planned |  | 928.00 | 8.0 | 0.011446 | 0.0014307 | No
19/04/2024 | 03:11 | HH130B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
19/04/2024 | 04:14 | AP355H | URBAN | Unknown | Unknown | 102.00 | 235.0 | 0.036956 | 0.0001573 | No
19/04/2024 | 06:09 | SM216B | URBAN | Weather |  | 619.00 | 140.1 | 0.133738 | 0.0009543 | No
19/04/2024 | 07:24 | HH428D | URBAN | Overloads |  | 23.67 | 132.0 | 0.004816 | 0.0000365 | No
19/04/2024 | 07:55 | NU14 | LONG RURAL | Overloads |  | 2.00 | 175.0 | 0.002512 | 0.0000144 | No
19/04/2024 | 08:00 | MT18 | LONG RURAL | Planned |  | 13.00 | 300.8 | 0.028059 | 0.0000933 | No
19/04/2024 | 08:39 | PL07 | URBAN | Planned |  | 51.00 | 232.0 | 0.018242 | 0.0000786 | No
19/04/2024 | 08:39 | KI13 | LONG RURAL | Planned |  | 1.00 | 160.0 | 0.001148 | 0.0000072 | No
19/04/2024 | 08:43 | G42 | LONG RURAL | Unknown | Unknown | 17.00 | 1,350.8 | 0.164790 | 0.0001220 | No
19/04/2024 | 08:45 | HH121D | URBAN | Planned |  | 95.00 | 326.0 | 0.047748 | 0.0001465 | No
19/04/2024 | 08:49 | SM216C | URBAN | Planned |  | 64.00 | 351.0 | 0.034634 | 0.0000987 | No
19/04/2024 | 08:50 | AP829C | URBAN | Planned |  | 130.00 | 60.8 | 0.012180 | 0.0002004 | No
19/04/2024 | 08:55 | AP125B | URBAN | Planned |  | 205.00 | 304.0 | 0.096096 | 0.0003161 | No
19/04/2024 | 09:08 | SB22 | LONG RURAL | Planned |  | 8.00 | 95.0 | 0.005454 | 0.0000574 | No
19/04/2024 | 09:09 | HH118D | URBAN | Overloads |  | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
19/04/2024 | 09:12 | LX24 | SHORT RURAL | Planned |  | 2.00 | 69.0 | 0.000971 | 0.0000141 | No
19/04/2024 | 09:18 | GU21 | LONG RURAL | Planned |  | 28.00 | 267.0 | 0.053650 | 0.0002009 | No
19/04/2024 | 09:27 | SM410C | URBAN | Asset failure | LV | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
19/04/2024 | 09:53 | ME427E | URBAN | Asset failure | LV | 1.00 | 284.0 | 0.000438 | 0.0000015 | No
19/04/2024 | 10:04 | CD23 | LONG RURAL | Planned |  | 3.00 | 11.0 | 0.000237 | 0.0000215 | No
19/04/2024 | 10:23 | ST12 | SHORT RURAL | Planned |  | 1.00 | 114.0 | 0.000802 | 0.0000070 | No
19/04/2024 | 10:24 | SD40102 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 423.0 | 0.003036 | 0.0000072 | No
19/04/2024 | 10:42 | NL234C | URBAN | Unknown | Unknown | 1.00 | 122.0 | 0.000188 | 0.0000015 | No
19/04/2024 | 10:55 | LX21 | SHORT RURAL | Asset failure | LV | 4.00 | 68.0 | 0.001914 | 0.0000281 | No
19/04/2024 | 11:01 | SA42 | URBAN | Planned |  | 267.00 | 11.0 | 0.004528 | 0.0004116 | No
19/04/2024 | 11:25 | CD23 | LONG RURAL | Planned |  | 1.00 | 32.0 | 0.000230 | 0.0000072 | No
19/04/2024 | 11:33 | AP149D | URBAN | Asset failure | LV | 1.00 | 594.0 | 0.000916 | 0.0000015 | No
19/04/2024 | 11:43 | NL115C | URBAN | Asset failure | LV | 22.00 | 97.0 | 0.003290 | 0.0000339 | No
19/04/2024 | 11:52 | BS0198 | URBAN | Planned |  | 1.00 | 51.0 | 0.000079 | 0.0000015 | No
19/04/2024 | 12:58 | MI14 | LONG RURAL | Asset failure | LV | 1.00 | 366.0 | 0.002627 | 0.0000072 | No
19/04/2024 | 13:46 | SM172F | URBAN | Asset failure | LV | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
19/04/2024 | 15:18 | ME116A | URBAN | Asset failure | LV | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
19/04/2024 | 16:09 | HH145B | URBAN | Asset failure | LV | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
19/04/2024 | 17:08 | NU14 | LONG RURAL | Overloads |  | 2.00 | 137.0 | 0.001966 | 0.0000144 | No
19/04/2024 | 17:54 | NL111P | URBAN | Asset failure | LV | 19.00 | 1,426.6 | 0.041791 | 0.0000293 | No
19/04/2024 | 18:46 | HH130B | URBAN | Vegetation | Grow-in - NSP responsibility | 91.00 | 59.0 | 0.008278 | 0.0001403 | No
19/04/2024 | 21:27 | LC01 | LONG RURAL | Asset failure | HV | 125.00 | 11.0 | 0.009867 | 0.0008970 | No
19/04/2024 | 21:27 | LC01 | SHORT RURAL | Asset failure | HV | 230.00 | 237.1 | 0.383680 | 0.0016182 | No
19/04/2024 | 23:16 | GU118 | LONG RURAL | Asset failure | LV | 6.00 | 106.7 | 0.004593 | 0.0000431 | No
20/04/2024 | 05:33 | AP227D | URBAN | Weather |  | 3.00 | 817.0 | 0.003779 | 0.0000046 | No
20/04/2024 | 08:14 | AP425D | URBAN | Asset failure | LV | 58.00 | 392.0 | 0.035053 | 0.0000894 | No
20/04/2024 | 08:45 | SM349D | URBAN | Planned |  | 4.00 | 169.0 | 0.001042 | 0.0000062 | No
20/04/2024 | 09:19 | SD52300 | LONG RURAL | Animal | Animal impact | 1.00 | 52.0 | 0.000373 | 0.0000072 | No
20/04/2024 | 09:20 | HH496C | URBAN | Asset failure | LV | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
20/04/2024 | 09:34 | GA40 | SHORT RURAL | Unknown | Unknown | 53.00 | 310.7 | 0.115846 | 0.0003729 | No
20/04/2024 | 10:36 | SD33200 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 658.0 | 0.004722 | 0.0000072 | No
20/04/2024 | 11:02 | MB14 | SHORT RURAL | Asset failure | LV | 4.00 | 152.0 | 0.004278 | 0.0000281 | No
20/04/2024 | 11:56 | PL12 | LONG RURAL | Third Party | Vehicle impact | 79.00 | 320.0 | 0.181418 | 0.0005669 | No
20/04/2024 | 17:24 | HH130B | URBAN | Asset failure | LV | 30.33 | 100.0 | 0.004677 | 0.0000468 | No
20/04/2024 | 19:10 | SM349E | URBAN | Asset failure | LV | 1.00 | 281.0 | 0.000433 | 0.0000015 | No
21/04/2024 | 01:47 | HH148C | URBAN | Animal | Animal impact | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
21/04/2024 | 08:02 | AP355F | URBAN | Overloads |  | 1.00 | 174.0 | 0.000268 | 0.0000015 | No
21/04/2024 | 08:02 | SM349G | URBAN | Planned |  | 1.00 | 733.0 | 0.001130 | 0.0000015 | No
21/04/2024 | 08:22 | AP139D | URBAN | Planned |  | 17.00 | 374.0 | 0.009802 | 0.0000262 | No
21/04/2024 | 09:15 | PP04 | SHORT RURAL | Asset failure | HV | 2,061.00 | 37.8 | 0.547713 | 0.0145001 | No
21/04/2024 | 10:36 | MG38 | SHORT RURAL | Third Party | Vehicle impact | 267.00 | 365.0 | 0.685644 | 0.0018785 | No
21/04/2024 | 11:42 | NU21 | LONG RURAL | Asset failure | LV | 1.00 | 95.0 | 0.000682 | 0.0000072 | No
21/04/2024 | 17:47 | W04 | LONG RURAL | Asset failure | LV | 6.00 | 324.0 | 0.013951 | 0.0000431 | No
21/04/2024 | 17:48 | CBD412H | URBAN | Overloads |  | 5.33 | 163.0 | 0.001340 | 0.0000082 | No
21/04/2024 | 19:17 | GA745A | SHORT RURAL | Third Party | Vehicle impact | 9.00 | 244.0 | 0.015450 | 0.0000633 | No
21/04/2024 | 20:46 | NL210D | URBAN | Asset failure | HV | 7.00 | 234.0 | 0.002525 | 0.0000108 | No
21/04/2024 | 22:10 | HH121G | URBAN | Planned |  | 71.00 | 316.6 | 0.034652 | 0.0001095 | No
21/04/2024 | 22:10 | GU34 | LONG RURAL | Unknown | Unknown | 93.00 | 452.0 | 0.301664 | 0.0006674 | No
21/04/2024 | 23:24 | CBD353S | CBD | Planned |  | 1.00 | 346.0 | 0.049989 | 0.0001445 | No
22/04/2024 | 03:21 | M43 | LONG RURAL | Unknown | Unknown | 35.00 | 323.0 | 0.081128 | 0.0002512 | No
22/04/2024 | 08:04 | KI16 | LONG RURAL | Planned |  | 90.00 | 284.0 | 0.183427 | 0.0006459 | No
22/04/2024 | 08:05 | MI10 | LONG RURAL | Unknown | Unknown | 47.00 | 198.0 | 0.066783 | 0.0003373 | No
22/04/2024 | 08:12 | SD34300 | SHORT RURAL | Asset failure | Subtransmission | 1.00 | 279.0 | 0.001963 | 0.0000070 | No
22/04/2024 | 08:33 | LM33 | LONG RURAL | Overloads |  | 1.00 | 660.0 | 0.004736 | 0.0000072 | No
22/04/2024 | 08:43 | EL01Q | URBAN | Unknown | Unknown | 1.00 | 459.0 | 0.000708 | 0.0000015 | No
22/04/2024 | 08:53 | SA14 | URBAN | Planned |  | 52.00 | 29.0 | 0.002325 | 0.0000802 | No
22/04/2024 | 09:05 | SA31 | URBAN | Planned |  | 145.00 | 9.0 | 0.002012 | 0.0002236 | No
22/04/2024 | 09:11 | HH341J | URBAN | Planned |  | 261.00 | 186.1 | 0.074901 | 0.0004024 | No
22/04/2024 | 09:32 | HH341J | URBAN | Planned |  | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
22/04/2024 | 09:41 | HK02 | LONG RURAL | Planned |  | 24.00 | 255.0 | 0.043919 | 0.0001722 | No
22/04/2024 | 09:56 | NU14 | LONG RURAL | Asset failure | LV | 2.00 | 392.0 | 0.005626 | 0.0000144 | No
22/04/2024 | 10:00 | SD34102 | LONG RURAL | Planned |  | 5.00 | 128.0 | 0.004593 | 0.0000359 | No
22/04/2024 | 10:21 | HH121F | URBAN | Unknown | Unknown | 115.00 | 130.0 | 0.023049 | 0.0001773 | No
22/04/2024 | 10:22 | SA520D | URBAN | Animal | Animal impact | 21.00 | 695.0 | 0.022502 | 0.0000324 | No
22/04/2024 | 10:24 | SM172A | URBAN | Third Party | Vehicle impact | 96.00 | 53.0 | 0.007844 | 0.0001480 | No
22/04/2024 | 10:28 | NA01 | LONG RURAL | Asset failure | LV | 1.00 | 300.0 | 0.002153 | 0.0000072 | No
22/04/2024 | 10:39 | SM350G | URBAN | Asset failure | LV | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
22/04/2024 | 11:07 | SD44400 | SHORT RURAL | Asset failure | Subtransmission | 938.00 | 4.9 | 0.032659 | 0.0065993 | No
22/04/2024 | 11:10 | CV32 | LONG RURAL | Planned |  | 2.00 | 66.0 | 0.000947 | 0.0000144 | No
22/04/2024 | 11:20 | CL25 | LONG RURAL | Asset failure | LV | 1.00 | 272.0 | 0.001952 | 0.0000072 | No
22/04/2024 | 12:02 | KA03 | LONG RURAL | Third Party | Other | 1.00 | 156.0 | 0.001120 | 0.0000072 | No
22/04/2024 | 12:44 | HH121F | URBAN | Unknown | Unknown | 116.00 | 231.0 | 0.041321 | 0.0001788 | No
22/04/2024 | 13:00 | HH121E | URBAN | Weather |  | 4.00 | 156.0 | 0.000962 | 0.0000062 | No
22/04/2024 | 13:34 | CV30 | LONG RURAL | Planned |  | 2.00 | 55.0 | 0.000789 | 0.0000144 | No
22/04/2024 | 13:42 | SM349H | URBAN | Asset failure | LV | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
22/04/2024 | 14:34 | LX34 | SHORT RURAL | Unknown | Unknown | 1.00 | 120.0 | 0.000844 | 0.0000070 | No
22/04/2024 | 14:58 | MG46 | SHORT RURAL | Asset failure | LV | 1.00 | 1,429.0 | 0.010054 | 0.0000070 | No
22/04/2024 | 16:15 | PA03 | URBAN | Asset failure | LV | 1.00 | 184.0 | 0.000284 | 0.0000015 | No
22/04/2024 | 17:10 | LX43 | SHORT RURAL | Asset failure | LV | 23.00 | 88.0 | 0.014240 | 0.0001618 | No
22/04/2024 | 17:42 | SG10 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 2,748.0 | 0.019334 | 0.0000070 | No
22/04/2024 | 17:57 | HH386G | URBAN | Asset failure | LV | 50.00 | 14.0 | 0.001079 | 0.0000771 | No
22/04/2024 | 19:45 | SM179B | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | No
22/04/2024 | 21:43 | HH428B | URBAN | Overloads |  | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
22/04/2024 | 22:58 | SG13 | SHORT RURAL | Weather |  | 135.00 | 150.2 | 0.142638 | 0.0009498 | No
23/04/2024 | 00:06 | GU37 | LONG RURAL | Unknown | Unknown | 676.00 | 295.1 | 1.431635 | 0.0048512 | No
23/04/2024 | 07:05 | R21 | LONG RURAL | Asset failure | LV | 1.00 | 193.0 | 0.001385 | 0.0000072 | No
23/04/2024 | 08:20 | MI16 | LONG RURAL | Planned |  | 74.00 | 319.4 | 0.169613 | 0.0005310 | No
23/04/2024 | 08:36 | KA02 | SHORT RURAL | Overloads |  | 43.00 | 152.0 | 0.045984 | 0.0003025 | No
23/04/2024 | 08:54 | LX21 | SHORT RURAL | Planned |  | 92.00 | 327.4 | 0.211909 | 0.0006473 | No
23/04/2024 | 09:11 | CV25 | LONG RURAL | Planned |  | 1.00 | 285.0 | 0.002045 | 0.0000072 | No
23/04/2024 | 09:28 | KA02 | SHORT RURAL | Overloads |  | 1.00 | 101.0 | 0.000711 | 0.0000070 | No
23/04/2024 | 09:31 | HH496C | URBAN | Planned |  | 53.00 | 287.0 | 0.023452 | 0.0000817 | No
23/04/2024 | 10:01 | W24 | LONG RURAL | Planned |  | 2.00 | 73.0 | 0.001048 | 0.0000144 | No
23/04/2024 | 10:12 | CM21 | LONG RURAL | Planned |  | 2.00 | 150.0 | 0.002153 | 0.0000144 | No
23/04/2024 | 10:31 | YK17 | LONG RURAL | Planned |  | 61.00 | 100.0 | 0.043776 | 0.0004378 | No
23/04/2024 | 10:31 | MI08 | LONG RURAL | Planned |  | 8.00 | 286.3 | 0.016434 | 0.0000574 | No
23/04/2024 | 10:59 | YK03 | LONG RURAL | Asset failure | LV | 2.00 | 58.0 | 0.000832 | 0.0000144 | No
23/04/2024 | 11:13 | HH341G | URBAN | Asset failure | LV | 1.00 | 477.0 | 0.000735 | 0.0000015 | No
23/04/2024 | 11:44 | ST15 | SHORT RURAL | Weather |  | 16.00 | 32.0 | 0.003602 | 0.0001126 | No
23/04/2024 | 11:57 | G03 | LONG RURAL | Asset failure | LV | 1.00 | 519.0 | 0.003725 | 0.0000072 | No
23/04/2024 | 12:30 | SA13 | URBAN | Vegetation | Grow-in - NSP responsibility | 48.00 | 106.0 | 0.007844 | 0.0000740 | No
23/04/2024 | 13:00 | W24 | LONG RURAL | Planned |  | 3.00 | 131.0 | 0.002820 | 0.0000215 | No
23/04/2024 | 13:38 | SG01 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 13.00 | 133.0 | 0.012164 | 0.0000915 | No
23/04/2024 | 14:05 | HH341A | URBAN | Vegetation | Grow-in - NSP responsibility | 4.00 | 215.0 | 0.001326 | 0.0000062 | No
23/04/2024 | 14:48 | R16 | LONG RURAL | Asset failure | HV | 79.00 | 118.0 | 0.066898 | 0.0005669 | No
23/04/2024 | 15:31 | NL234E | URBAN | Unknown | Unknown | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
23/04/2024 | 15:37 | YK03 | LONG RURAL | Asset failure | LV | 2.00 | 94.0 | 0.001349 | 0.0000144 | No
23/04/2024 | 15:39 | NU13 | LONG RURAL | Unknown | Unknown | 2.00 | 376.0 | 0.005397 | 0.0000144 | No
23/04/2024 | 15:53 | HH432C | URBAN | Weather |  | 13.00 | 441.0 | 0.008839 | 0.0000200 | No
23/04/2024 | 16:25 | MG22 | LONG RURAL | Third Party | Vehicle impact | 17.00 | 692.5 | 0.084487 | 0.0001220 | No
23/04/2024 | 16:25 | AP351C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 85.00 | 264.0 | 0.034597 | 0.0001310 | No
23/04/2024 | 16:40 | MG21 | LONG RURAL | Unknown | Unknown | 64.00 | 139.0 | 0.063855 | 0.0004593 | No
23/04/2024 | 16:44 | AP355H | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 361.00 | 113.3 | 0.063078 | 0.0005566 | No
23/04/2024 | 17:03 | HH409C | URBAN | Network business | Switching and protection error | 1.00 | 363.0 | 0.000560 | 0.0000015 | No
23/04/2024 | 17:35 | EL14 | URBAN | Overloads |  | 1.00 | 120.0 | 0.000185 | 0.0000015 | No
23/04/2024 | 17:54 | SA17 | URBAN | Asset failure | LV | 1.00 | 378.0 | 0.000583 | 0.0000015 | No
23/04/2024 | 18:15 | MG41 | URBAN | Asset failure | LV | 50.00 | 185.0 | 0.014261 | 0.0000771 | No
23/04/2024 | 18:50 | HH522C | URBAN | Asset failure | LV | 1.00 | 234.0 | 0.000361 | 0.0000015 | No
23/04/2024 | 19:30 | MI08 | LONG RURAL | Unknown | Unknown | 1.00 | 873.0 | 0.006265 | 0.0000072 | No
23/04/2024 | 20:20 | MG21 | LONG RURAL | Asset failure | HV | 64.00 | 22.3 | 0.010248 | 0.0004593 | No
23/04/2024 | 21:07 | SM216C | URBAN | Planned |  | 11.00 | 323.0 | 0.005478 | 0.0000170 | No
23/04/2024 | 21:54 | CN52 | LONG RURAL | Unknown | Unknown | 86.00 | 327.1 | 0.201892 | 0.0006172 | No
23/04/2024 | 23:19 | AP344B | URBAN | Weather |  | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
24/04/2024 | 00:32 | VH18 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 4.00 | 167.0 | 0.004700 | 0.0000281 | No
24/04/2024 | 00:41 | GU43 | LONG RURAL | Asset failure | LV | 1.00 | 63.0 | 0.000452 | 0.0000072 | No
24/04/2024 | 01:05 | GU43 | LONG RURAL | Asset failure | HV | 37.00 | 39.0 | 0.010355 | 0.0002655 | No
24/04/2024 | 04:58 | HH145D | URBAN | Asset failure | LV | 1.00 | 299.0 | 0.000461 | 0.0000015 | No
24/04/2024 | 08:27 | CD01 | SHORT RURAL | Planned |  | 73.00 | 246.2 | 0.126442 | 0.0005136 | No
24/04/2024 | 08:28 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 190.0 | 0.001337 | 0.0000070 | No
24/04/2024 | 08:30 | SA32 | URBAN | Asset failure | LV | 1.00 | 302.0 | 0.000466 | 0.0000015 | No
24/04/2024 | 08:42 | WK31 | SHORT RURAL | Planned |  | 1.00 | 203.0 | 0.001428 | 0.0000070 | No
24/04/2024 | 08:46 | BT02 | LONG RURAL | Planned |  | 161.00 | 381.0 | 0.440203 | 0.0011554 | No
24/04/2024 | 08:47 | HH145D | URBAN | Planned |  | 105.00 | 323.4 | 0.052359 | 0.0001619 | No
24/04/2024 | 08:58 | SM126B | URBAN | Planned |  | 64.00 | 303.0 | 0.029898 | 0.0000987 | No
24/04/2024 | 09:17 | MI10 | LONG RURAL | Planned |  | 47.00 | 354.0 | 0.119400 | 0.0003373 | No
24/04/2024 | 09:24 | KI53 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 202.00 | 186.7 | 0.270662 | 0.0014496 | No
24/04/2024 | 09:27 | AP424A | URBAN | Planned |  | 239.00 | 130.5 | 0.048077 | 0.0003685 | No
24/04/2024 | 09:37 | GA05 | SHORT RURAL | Planned |  | 472.00 | 49.9 | 0.165630 | 0.0033208 | No
24/04/2024 | 10:13 | ST15 | SHORT RURAL | Other |  | 7.00 | 74.0 | 0.003644 | 0.0000492 | No
24/04/2024 | 12:28 | HH432B | URBAN | Asset failure | LV | 1.67 | 132.0 | 0.000339 | 0.0000026 | No
24/04/2024 | 12:42 | NU28 | LONG RURAL | Third Party | Vehicle impact | 47.00 | 283.0 | 0.095452 | 0.0003373 | No
24/04/2024 | 13:30 | HH429B | URBAN | Asset failure | LV | 126.00 | 90.0 | 0.017483 | 0.0001943 | No
24/04/2024 | 14:25 | NL234C | URBAN | Asset failure | LV | 24.00 | 245.0 | 0.009066 | 0.0000370 | No
24/04/2024 | 15:22 | NL760C | URBAN | Asset failure | LV | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
24/04/2024 | 17:20 | R33 | LONG RURAL | Asset failure | LV | 2.00 | 187.0 | 0.002684 | 0.0000144 | No
24/04/2024 | 19:20 | MTB22 | SHORT RURAL | Asset failure | LV | 4.67 | 188.0 | 0.006172 | 0.0000328 | No
24/04/2024 | 20:15 | MI03 | LONG RURAL | Asset failure | HV | 3.00 | 8.0 | 0.000172 | 0.0000215 | No
24/04/2024 | 20:29 | NL111Q | URBAN | Asset failure | LV | 41.00 | 59.0 | 0.003730 | 0.0000632 | No
24/04/2024 | 20:54 | HH148D | URBAN | Asset failure | LV | 1.00 | 127.0 | 0.000196 | 0.0000015 | No
24/04/2024 | 20:57 | NL111Q | URBAN | Asset failure | LV | 67.00 | 185.0 | 0.019110 | 0.0001033 | No
24/04/2024 | 21:07 | NL111Q | URBAN | Asset failure | LV | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
24/04/2024 | 21:23 | HH130B | URBAN | Asset failure | LV | 20.00 | 154.0 | 0.004749 | 0.0000308 | No
25/04/2024 | 02:49 | HH177E | URBAN | Asset failure | LV | 84.00 | 60.0 | 0.007770 | 0.0001295 | No
25/04/2024 | 10:55 | SM410C | URBAN | Asset failure | LV | 1.00 | 372.0 | 0.000574 | 0.0000015 | No
25/04/2024 | 15:38 | EL07 | URBAN | Overloads |  | 1.00 | 81.0 | 0.000125 | 0.0000015 | No
25/04/2024 | 17:37 | NL451A | URBAN | Asset failure | LV | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
25/04/2024 | 17:45 | VH23 | SHORT RURAL | Asset failure | LV | 18.67 | 232.0 | 0.030468 | 0.0001313 | No
25/04/2024 | 18:57 | ME231D | URBAN | Asset failure | LV | 21.33 | 151.0 | 0.004966 | 0.0000329 | No
25/04/2024 | 19:55 | AP424A | URBAN | Asset failure | LV | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
25/04/2024 | 22:04 | SD38200 | LONG RURAL | Unknown | Unknown | 511.00 | 9.2 | 0.033607 | 0.0036671 | No
25/04/2024 | 22:09 | HH130A | URBAN | Asset failure | LV | 34.00 | 86.3 | 0.004522 | 0.0000524 | No
26/04/2024 | 03:03 | PA02 | URBAN | Asset failure | LV | 1.00 | 330.0 | 0.000509 | 0.0000015 | No
26/04/2024 | 08:45 | HH177D | URBAN | Asset failure | LV | 1.00 | 168.0 | 0.000259 | 0.0000015 | No
26/04/2024 | 09:01 | CV22 | LONG RURAL | Planned |  | 4.00 | 276.0 | 0.007923 | 0.0000287 | No
26/04/2024 | 09:02 | HH130A | URBAN | Asset failure | LV | 2.00 | 92.0 | 0.000284 | 0.0000031 | No
26/04/2024 | 09:03 | MG19 | LONG RURAL | Planned |  | 5.00 | 217.0 | 0.007786 | 0.0000359 | No
26/04/2024 | 09:22 | G30 | LONG RURAL | Planned |  | 1.00 | 212.0 | 0.001521 | 0.0000072 | No
26/04/2024 | 09:23 | AP132A | URBAN | Third Party | Vehicle impact | 89.00 | 552.3 | 0.075786 | 0.0001372 | No
26/04/2024 | 09:30 | CM10 | LONG RURAL | Planned |  | 1.00 | 86.0 | 0.000617 | 0.0000072 | No
26/04/2024 | 09:49 | MTB52 | LONG RURAL | Asset failure | LV | 2.00 | 285.0 | 0.004091 | 0.0000144 | No
26/04/2024 | 10:25 | GA27 | LONG RURAL | Planned |  | 17.00 | 163.0 | 0.019886 | 0.0001220 | No
26/04/2024 | 11:25 | HH386G | URBAN | Asset failure | LV | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
26/04/2024 | 11:34 | HH130B | URBAN | Asset failure | LV | 23.00 | 69.0 | 0.002447 | 0.0000355 | No
26/04/2024 | 11:38 | EL01N | URBAN | Overloads |  | 360.67 | 12.1 | 0.006708 | 0.0005561 | No
26/04/2024 | 12:10 | VH21 | SHORT RURAL | Asset failure | LV | 10.00 | 61.7 | 0.004341 | 0.0000704 | No
26/04/2024 | 12:22 | PL803A | URBAN | Third Party | Vehicle impact | 1.00 | 157.0 | 0.000242 | 0.0000015 | No
26/04/2024 | 13:48 | W27 | LONG RURAL | Planned |  | 2.00 | 35.0 | 0.000502 | 0.0000144 | No
26/04/2024 | 14:36 | EL11 | URBAN | Asset failure | LV | 9.00 | 463.1 | 0.006426 | 0.0000139 | No
26/04/2024 | 14:40 | LX43 | SHORT RURAL | Asset failure | LV | 23.00 | 59.0 | 0.009547 | 0.0001618 | No
26/04/2024 | 14:59 | EL01N | URBAN | Asset failure | LV | 1.00 | 435.0 | 0.000671 | 0.0000015 | No
26/04/2024 | 15:00 | NL21 | URBAN | Overloads |  | 1.00 | 158.0 | 0.000244 | 0.0000015 | No
26/04/2024 | 15:41 | HH121A | URBAN | Network business | Switching and protection error | 11.00 | 88.0 | 0.001492 | 0.0000170 | No
26/04/2024 | 17:52 | KI53 | LONG RURAL | Third Party | Vehicle impact | 184.00 | 136.0 | 0.179580 | 0.0013204 | No
26/04/2024 | 18:36 | VH11 | URBAN | Asset failure | LV | 19.00 | 151.0 | 0.004423 | 0.0000293 | No
26/04/2024 | 18:53 | VH12 | SHORT RURAL | Asset failure | LV | 9.67 | 134.0 | 0.009113 | 0.0000680 | No
27/04/2024 | 00:33 | MTB11 | LONG RURAL | Asset failure | HV | 2.00 | 42.0 | 0.000603 | 0.0000144 | No
27/04/2024 | 00:33 | MTB11 | SHORT RURAL | Asset failure | HV | 279.67 | 42.0 | 0.082639 | 0.0019676 | No
27/04/2024 | 09:51 | SA32 | URBAN | Asset failure | LV | 2.00 | 117.0 | 0.000361 | 0.0000031 | No
27/04/2024 | 10:18 | MI10 | LONG RURAL | Unknown | Unknown | 47.00 | 169.0 | 0.057002 | 0.0003373 | No
27/04/2024 | 10:52 | CD18 | LONG RURAL | Overloads |  | 2.00 | 26.0 | 0.000373 | 0.0000144 | No
27/04/2024 | 11:56 | PA04 | URBAN | Asset failure | HV | 4.00 | 2,815.3 | 0.017362 | 0.0000062 | No
27/04/2024 | 12:17 | ST11 | SHORT RURAL | Overloads |  | 1.00 | 130.0 | 0.000915 | 0.0000070 | No
27/04/2024 | 14:00 | PA10 | LONG RURAL | Asset failure | LV | 1.00 | 320.0 | 0.002296 | 0.0000072 | No
27/04/2024 | 14:44 | GA800A | SHORT RURAL | Asset failure | LV | 42.00 | 164.0 | 0.048460 | 0.0002955 | No
27/04/2024 | 17:47 | SG11 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 170.0 | 0.001196 | 0.0000070 | No
27/04/2024 | 19:46 | GU15 | LONG RURAL | Unknown | Unknown | 511.00 | 144.7 | 0.530647 | 0.0036671 | No
27/04/2024 | 23:14 | NL115D | URBAN | Asset failure | LV | 20.00 | 321.0 | 0.009898 | 0.0000308 | No
28/04/2024 | 00:20 | ST41 | LONG RURAL | Animal | Animal impact | 2.00 | 98.0 | 0.001407 | 0.0000144 | No
28/04/2024 | 08:01 | SA18 | URBAN | Asset failure | LV | 21.00 | 133.0 | 0.004306 | 0.0000324 | No
28/04/2024 | 10:41 | CBD366E | URBAN | Animal | Animal impact | 516.67 | 27.5 | 0.021877 | 0.0007966 | No
28/04/2024 | 11:21 | MTB13 | SHORT RURAL | Asset failure | LV | 1.00 | 420.0 | 0.002955 | 0.0000070 | No
28/04/2024 | 12:08 | HH409C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,271.00 | 57.2 | 0.200371 | 0.0035013 | No
28/04/2024 | 13:21 | HH429C | URBAN | Asset failure | LV | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
28/04/2024 | 15:03 | HH145E | URBAN | Asset failure | LV | 6.00 | 54.0 | 0.000500 | 0.0000093 | No
28/04/2024 | 15:28 | HH177D | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
28/04/2024 | 15:55 | AP365A | URBAN | Asset failure | LV | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
28/04/2024 | 17:34 | MG06 | SHORT RURAL | Unknown | Unknown | 46.00 | 118.0 | 0.038189 | 0.0003236 | No
28/04/2024 | 17:41 | SA520D | URBAN | Overloads |  | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
28/04/2024 | 18:51 | MG19 | LONG RURAL | Asset failure | LV | 1.00 | 210.0 | 0.001507 | 0.0000072 | No
28/04/2024 | 19:10 | AP226D | URBAN | Asset failure | LV | 1.00 | 179.0 | 0.000276 | 0.0000015 | No
28/04/2024 | 19:21 | HH121C | URBAN | Asset failure | LV | 1.00 | 157.0 | 0.000242 | 0.0000015 | No
28/04/2024 | 21:19 | HH121F | URBAN | Overloads |  | 1.00 | 61.0 | 0.000094 | 0.0000015 | No
29/04/2024 | 05:41 | EL10 | URBAN | Asset failure | LV | 1.00 | 197.0 | 0.000304 | 0.0000015 | No
29/04/2024 | 09:07 | HH432B | URBAN | Asset failure | LV | 124.00 | 191.0 | 0.036515 | 0.0001912 | No
29/04/2024 | 09:13 | NU31 | LONG RURAL | Planned |  | 14.00 | 137.0 | 0.013764 | 0.0001005 | No
29/04/2024 | 09:19 | SM410D | URBAN | Planned |  | 76.00 | 294.0 | 0.034449 | 0.0001172 | No
29/04/2024 | 09:26 | ST16 | SHORT RURAL | Planned |  | 231.00 | 235.5 | 0.382766 | 0.0016252 | No
29/04/2024 | 09:32 | SB23 | LONG RURAL | Planned |  | 2.00 | 74.0 | 0.001062 | 0.0000144 | No
29/04/2024 | 09:51 | SA18 | URBAN | Planned |  | 44.00 | 263.0 | 0.017841 | 0.0000678 | No
29/04/2024 | 10:24 | HH130A | URBAN | Network business | Switching and protection error | 1.00 | 45.0 | 0.000069 | 0.0000015 | No
29/04/2024 | 10:31 | MTB10 | URBAN | Asset failure | LV | 1.00 | 137.0 | 0.000211 | 0.0000015 | No
29/04/2024 | 10:32 | SM350H | URBAN | Third Party | Vehicle impact | 15.00 | 430.0 | 0.009944 | 0.0000231 | No
29/04/2024 | 10:38 | SM411E | URBAN | Asset failure | LV | 1.00 | 226.0 | 0.000348 | 0.0000015 | No
29/04/2024 | 10:41 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 92.0 | 0.000660 | 0.0000072 | No
29/04/2024 | 10:50 | CM16 | LONG RURAL | Planned |  | 17.00 | 191.2 | 0.023323 | 0.0001220 | No
29/04/2024 | 10:56 | SA17 | URBAN | Asset failure | LV | 36.00 | 109.0 | 0.006050 | 0.0000555 | No
29/04/2024 | 11:03 | NL115F | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
29/04/2024 | 11:06 | SM179A | URBAN | Unknown | Unknown | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
29/04/2024 | 11:16 | SM350H | URBAN | Third Party | Vehicle impact | 82.00 | 89.0 | 0.011252 | 0.0001264 | No
29/04/2024 | 11:24 | SM411D | URBAN | Asset failure | LV | 31.00 | 58.0 | 0.002772 | 0.0000478 | No
29/04/2024 | 11:51 | WHY14 | URBAN | Asset failure | HV | 1.00 | 16.0 | 0.000025 | 0.0000015 | No
29/04/2024 | 11:53 | HH130C | URBAN | Asset failure | LV | 1.00 | 315.0 | 0.000486 | 0.0000015 | No
29/04/2024 | 12:49 | GU42 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 712.00 | 35.7 | 0.182164 | 0.0051095 | No
29/04/2024 | 13:49 | HH121E | URBAN | Asset failure | LV | 2.00 | 86.0 | 0.000265 | 0.0000031 | No
29/04/2024 | 13:56 | CN25 | LONG RURAL | Planned |  | 1.00 | 3,186.0 | 0.022864 | 0.0000072 | No
29/04/2024 | 14:03 | HH121E | URBAN | Asset failure | LV | 3.00 | 79.0 | 0.000365 | 0.0000046 | No
29/04/2024 | 14:46 | SB17 | LONG RURAL | Asset failure | HV | 1.00 | 180.0 | 0.001292 | 0.0000072 | No
29/04/2024 | 14:58 | BT01 | LONG RURAL | Planned |  | 1.00 | 25.0 | 0.000179 | 0.0000072 | No
29/04/2024 | 15:18 | KI53 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 112.00 | 1,344.6 | 1.080719 | 0.0008037 | No
29/04/2024 | 16:23 | NL115D | URBAN | Asset failure | LV | 20.00 | 757.1 | 0.023345 | 0.0000308 | No
29/04/2024 | 16:35 | HK01 | LONG RURAL | Asset failure | LV | 1.00 | 1,210.0 | 0.008683 | 0.0000072 | No
29/04/2024 | 17:13 | NL210B | URBAN | Asset failure | LV | 4.00 | 208.0 | 0.001283 | 0.0000062 | No
29/04/2024 | 17:43 | CBD412M | URBAN | Asset failure | LV | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
29/04/2024 | 17:56 | CN24 | LONG RURAL | Asset failure | HV | 107.00 | 75.7 | 0.058135 | 0.0007679 | No
29/04/2024 | 20:54 | ST11 | SHORT RURAL | Unknown | Unknown | 1.00 | 774.0 | 0.005445 | 0.0000070 | No
29/04/2024 | 21:48 | MI14 | LONG RURAL | Asset failure | LV | 22.67 | 825.0 | 0.134197 | 0.0001627 | No
30/04/2024 | 02:45 | EL02 | URBAN | Asset failure | LV | 73.00 | 47.9 | 0.005390 | 0.0001125 | No
30/04/2024 | 03:17 | ME116D | URBAN | Asset failure | LV | 130.00 | 418.0 | 0.083779 | 0.0002004 | No
30/04/2024 | 04:58 | CM15 | LONG RURAL | Asset failure | HV | 25.00 | 625.0 | 0.112130 | 0.0001794 | No
30/04/2024 | 06:54 | EL15 | URBAN | Asset failure | LV | 1.00 | 347.0 | 0.000535 | 0.0000015 | No
30/04/2024 | 08:28 | EL260A | URBAN | Planned |  | 182.00 | 330.2 | 0.092650 | 0.0002806 | No
30/04/2024 | 08:34 | HH121E | URBAN | Unknown | Unknown | 100.33 | 4.0 | 0.000619 | 0.0001547 | No
30/04/2024 | 08:35 | EL01Z | URBAN | Third Party | Vehicle impact | 13.00 | 127.0 | 0.002545 | 0.0000200 | No
30/04/2024 | 08:59 | AP227A | URBAN | Planned |  | 43.00 | 400.0 | 0.026518 | 0.0000663 | No
30/04/2024 | 09:03 | MG11 | SHORT RURAL | Planned |  | 1.00 | 378.0 | 0.002659 | 0.0000070 | No
30/04/2024 | 09:15 | PL04 | URBAN | Planned |  | 19.00 | 198.0 | 0.005800 | 0.0000293 | No
30/04/2024 | 09:16 | EL01R | URBAN | Planned |  | 1,002.00 | 22.0 | 0.034016 | 0.0015448 | No
30/04/2024 | 09:19 | WHY01 | SHORT RURAL | Asset failure | LV | 1.00 | 84.0 | 0.000591 | 0.0000070 | No
30/04/2024 | 09:27 | NA30 | LONG RURAL | Planned |  | 65.00 | 287.0 | 0.133874 | 0.0004665 | No
30/04/2024 | 09:31 | NL451C | URBAN | Planned |  | 35.00 | 169.0 | 0.009119 | 0.0000540 | No
30/04/2024 | 09:34 | CV15 | LONG RURAL | Planned |  | 30.00 | 153.0 | 0.032939 | 0.0002153 | No
30/04/2024 | 09:45 | HH177C | URBAN | Vegetation | Grow-in - NSP responsibility | 16.33 | 90.0 | 0.002266 | 0.0000252 | No
30/04/2024 | 09:55 | NL451C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 406.00 | 70.0 | 0.043817 | 0.0006260 | No
30/04/2024 | 11:50 | PP12 | LONG RURAL | Planned |  | 75.00 | 61.0 | 0.032832 | 0.0005382 | No
30/04/2024 | 12:56 | HH522A | URBAN | Asset failure | LV | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
30/04/2024 | 13:58 | NU13 | LONG RURAL | Planned |  | 1.00 | 78.0 | 0.000560 | 0.0000072 | No
30/04/2024 | 15:41 | HH403A | URBAN | Third Party | Vehicle impact | 71.00 | 256.8 | 0.028109 | 0.0001095 | No
30/04/2024 | 15:59 | HH386E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 956.00 | 63.0 | 0.092857 | 0.0014739 | No
30/04/2024 | 17:20 | NL111Q | URBAN | Asset failure | LV | 15.00 | 69.0 | 0.001596 | 0.0000231 | No
30/04/2024 | 18:57 | CN52 | LONG RURAL | Planned |  | 17.00 | 164.0 | 0.020008 | 0.0001220 | No
30/04/2024 | 21:33 | G02 | LONG RURAL | Planned |  | 292.00 | 407.6 | 0.854069 | 0.0020955 | No
01/05/2024 | 06:05 | G31 | LONG RURAL | Unknown | Unknown | 54.00 | 356.0 | 0.137958 | 0.0003875 | No
01/05/2024 | 08:22 | MI16 | LONG RURAL | Asset failure | LV | 1.00 | 110.0 | 0.000789 | 0.0000072 | No
01/05/2024 | 08:55 | SG14 | SHORT RURAL | Planned |  | 1.00 | 127.0 | 0.000894 | 0.0000070 | No
01/05/2024 | 08:55 | EL18 | URBAN | Asset failure | LV | 2.00 | 789.0 | 0.002433 | 0.0000031 | No
01/05/2024 | 09:01 | SD54102 | LONG RURAL | Planned |  | 1.00 | 155.0 | 0.001112 | 0.0000072 | No
01/05/2024 | 09:08 | SG14 | SHORT RURAL | Planned |  | 23.00 | 121.0 | 0.019580 | 0.0001618 | No
01/05/2024 | 09:09 | MT08 | LONG RURAL | Planned |  | 733.00 | 240.0 | 1.262460 | 0.0052602 | No
01/05/2024 | 09:15 | WK11 | SHORT RURAL | Planned |  | 102.00 | 410.3 | 0.294414 | 0.0007176 | No
01/05/2024 | 09:21 | MB62 | LONG RURAL | Planned |  | 50.00 | 237.0 | 0.085040 | 0.0003588 | No
01/05/2024 | 09:23 | MTB22 | SHORT RURAL | Planned |  | 156.00 | 295.0 | 0.323773 | 0.0010975 | No
01/05/2024 | 09:55 | BT23 | LONG RURAL | Asset failure | HV | 1.00 | 5.0 | 0.000036 | 0.0000072 | No
01/05/2024 | 10:36 | HH496G | URBAN | Planned |  | 260.00 | 36.7 | 0.014696 | 0.0004009 | No
01/05/2024 | 10:40 | NL111P | URBAN | Unknown | Unknown | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
01/05/2024 | 11:20 | HH386G | URBAN | Asset failure | LV | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
01/05/2024 | 11:33 | KI41 | LONG RURAL | Planned |  | 2.00 | 11,699.0 | 0.167912 | 0.0000144 | No
01/05/2024 | 11:41 | R36 | SHORT RURAL | Planned |  | 2.00 | 57.0 | 0.000802 | 0.0000141 | No
01/05/2024 | 12:48 | R36 | SHORT RURAL | Planned |  | 2.00 | 10.0 | 0.000141 | 0.0000141 | No
01/05/2024 | 13:22 | PP03 | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
01/05/2024 | 14:11 | BT02 | LONG RURAL | Asset failure | HV | 13.33 | 112.0 | 0.010717 | 0.0000957 | No
01/05/2024 | 14:20 | SA520D | URBAN | Asset failure | LV | 1.00 | 165.0 | 0.000254 | 0.0000015 | No
01/05/2024 | 15:03 | NA01 | LONG RURAL | Third Party | Vehicle impact | 22.00 | 114.0 | 0.017998 | 0.0001579 | No
01/05/2024 | 16:09 | CM16 | LONG RURAL | Weather |  | 85.00 | 170.0 | 0.103698 | 0.0006100 | No
01/05/2024 | 17:41 | MI28 | LONG RURAL | Unknown | Unknown | 6.00 | 315.0 | 0.013563 | 0.0000431 | No
01/05/2024 | 17:53 | ME200E | URBAN | Overloads |  | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
01/05/2024 | 18:21 | GA27 | LONG RURAL | Overloads |  | 13.67 | 230.0 | 0.022558 | 0.0000981 | No
01/05/2024 | 19:21 | ME427D | URBAN | Asset failure | LV | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
01/05/2024 | 21:19 | SM179A | URBAN | Third Party | Vehicle impact | 97.00 | 366.0 | 0.054737 | 0.0001496 | No
01/05/2024 | 21:31 | SM179A | URBAN | Planned |  | 69.00 | 20.9 | 0.002219 | 0.0001064 | No
01/05/2024 | 21:47 | AP424F | URBAN | Planned |  | 950.00 | 125.2 | 0.183353 | 0.0014647 | No
01/05/2024 | 21:54 | AP214C | URBAN | Planned |  | 1.00 | 112.0 | 0.000173 | 0.0000015 | No
01/05/2024 | 22:27 | AP424A | URBAN | Planned |  | 1.00 | 439.0 | 0.000677 | 0.0000015 | No
02/05/2024 | 00:26 | AP365A | URBAN | Asset failure | LV | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
02/05/2024 | 04:44 | HH429C | URBAN | Asset failure | LV | 10.67 | 223.0 | 0.003667 | 0.0000164 | No
02/05/2024 | 07:51 | SA14 | URBAN | Asset failure | LV | 1.00 | 145.0 | 0.000224 | 0.0000015 | No
02/05/2024 | 08:47 | KA27 | LONG RURAL | Asset failure | LV | 9.00 | 114.0 | 0.007363 | 0.0000646 | No
02/05/2024 | 08:56 | NU13 | LONG RURAL | Planned |  | 2.00 | 370.0 | 0.005310 | 0.0000144 | No
02/05/2024 | 09:22 | ST22 | SHORT RURAL | Planned |  | 1.00 | 346.0 | 0.002434 | 0.0000070 | No
02/05/2024 | 09:22 | MV63 | SHORT RURAL | Planned |  | 6.00 | 264.0 | 0.011144 | 0.0000422 | No
02/05/2024 | 09:28 | CV09 | LONG RURAL | Planned |  | 4.00 | 228.0 | 0.006545 | 0.0000287 | No
02/05/2024 | 09:30 | CM25 | LONG RURAL | Planned |  | 4.00 | 280.0 | 0.008037 | 0.0000287 | No
02/05/2024 | 09:41 | MI30 | LONG RURAL | Planned |  | 18.00 | 312.8 | 0.040410 | 0.0001292 | No
02/05/2024 | 10:24 | SA11 | URBAN | Asset failure | LV | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
02/05/2024 | 11:23 | ME116D | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
02/05/2024 | 11:53 | MTB53 | LONG RURAL | Weather |  | 125.00 | 1,779.6 | 1.596339 | 0.0008970 | No
02/05/2024 | 11:54 | EL01N | URBAN | Planned |  | 84.00 | 5.0 | 0.000648 | 0.0001295 | No
02/05/2024 | 12:00 | HH496G | URBAN | Third Party | Vehicle impact | 8.00 | 115.0 | 0.001418 | 0.0000123 | No
02/05/2024 | 12:06 | HH341K | URBAN | Asset failure | LV | 33.00 | 75.0 | 0.003816 | 0.0000509 | No
02/05/2024 | 12:10 | EL01P | URBAN | Planned |  | 411.00 | 15.0 | 0.009505 | 0.0006337 | No
02/05/2024 | 12:32 | EL01P | URBAN | Planned |  | 411.00 | 8.3 | 0.005257 | 0.0006337 | No
02/05/2024 | 12:56 | EL01R | URBAN | Planned |  | 106.00 | 4.0 | 0.000654 | 0.0001634 | No
02/05/2024 | 13:22 | EL01R | URBAN | Planned |  | 359.00 | 4.0 | 0.002214 | 0.0005535 | No
02/05/2024 | 14:42 | AP372D | URBAN | Overloads |  | 1.00 | 249.0 | 0.000384 | 0.0000015 | No
02/05/2024 | 15:17 | SA12 | URBAN | Overloads |  | 1.00 | 103.0 | 0.000159 | 0.0000015 | No
02/05/2024 | 17:04 | HH121H | URBAN | Asset failure | LV | 1.00 | 232.0 | 0.000358 | 0.0000015 | No
02/05/2024 | 17:23 | CM18 | LONG RURAL | Weather |  | 12.00 | 108.0 | 0.009301 | 0.0000861 | No
02/05/2024 | 17:54 | GA36 | LONG RURAL | Asset failure | HV | 1.00 | 19.0 | 0.000136 | 0.0000072 | No
02/05/2024 | 19:24 | NA04 | LONG RURAL | Asset failure | LV | 1.00 | 221.0 | 0.001586 | 0.0000072 | No
02/05/2024 | 19:46 | HH177B | URBAN | Asset failure | LV | 9.00 | 418.0 | 0.005800 | 0.0000139 | No
02/05/2024 | 20:43 | EL19 | URBAN | Animal | Animal impact | 481.00 | 27.3 | 0.020209 | 0.0007416 | No
02/05/2024 | 21:05 | G02 | LONG RURAL | Planned |  | 11.00 | 446.0 | 0.035207 | 0.0000789 | No
03/05/2024 | 02:18 | HH121C | URBAN | Asset failure | HV | 1,828.00 | 77.8 | 0.219308 | 0.0028183 | No
03/05/2024 | 08:04 | CN02 | LONG RURAL | Asset failure | HV | 80.00 | 841.4 | 0.483075 | 0.0005741 | No
03/05/2024 | 09:02 | EL23 | URBAN | Planned |  | 42.00 | 352.0 | 0.022793 | 0.0000648 | No
03/05/2024 | 09:12 | EL23 | URBAN | Planned |  | 51.00 | 9,169.4 | 0.720983 | 0.0000786 | No
03/05/2024 | 10:29 | LM13 | LONG RURAL | Unknown | Unknown | 82.00 | 609.0 | 0.358400 | 0.0005885 | No
03/05/2024 | 12:04 | CBD103A | URBAN | Asset failure | LV | 1.00 | 5,558.0 | 0.008569 | 0.0000015 | No
03/05/2024 | 21:54 | HH107B | URBAN | Animal | Animal impact | 181.00 | 235.0 | 0.065578 | 0.0002791 | No
04/05/2024 | 00:02 | CBD412H | URBAN | Asset failure | LV | 21.00 | 91.0 | 0.002946 | 0.0000324 | No
04/05/2024 | 03:28 | HH107B | URBAN | Asset failure | LV | 31.67 | 343.0 | 0.016746 | 0.0000488 | No
04/05/2024 | 08:28 | LC01 | SHORT RURAL | Planned |  | 152.00 | 673.4 | 0.720153 | 0.0010694 | No
04/05/2024 | 08:28 | LC01 | SHORT RURAL | Asset failure | LV | 1.00 | 1,933.0 | 0.013600 | 0.0000070 | No
04/05/2024 | 08:35 | MG11 | SHORT RURAL | Third Party | Unauthorised access | 1.00 | 212.0 | 0.001492 | 0.0000070 | No
04/05/2024 | 10:02 | NA52 | LONG RURAL | Planned |  | 2,216.00 | 291.0 | 4.627699 | 0.0159027 | No
04/05/2024 | 12:06 | MT06 | LONG RURAL | Asset failure | LV | 5.67 | 113.0 | 0.004595 | 0.0000407 | No
04/05/2024 | 13:06 | G16 | LONG RURAL | Third Party | Vehicle impact | 22.00 | 167.0 | 0.026366 | 0.0001579 | No
04/05/2024 | 16:25 | LC01 | LONG RURAL | Asset failure | HV | 127.00 | 32.0 | 0.029165 | 0.0009114 | No
04/05/2024 | 16:25 | LC01 | SHORT RURAL | Asset failure | HV | 79.00 | 32.0 | 0.017786 | 0.0005558 | No
04/05/2024 | 17:16 | SA14 | URBAN | Asset failure | LV | 1.00 | 292.0 | 0.000450 | 0.0000015 | No
04/05/2024 | 17:47 | MT06 | LONG RURAL | Asset failure | LV | 5.67 | 113.0 | 0.004595 | 0.0000407 | No
04/05/2024 | 18:52 | YK17 | LONG RURAL | Overloads |  | 1.00 | 77.0 | 0.000553 | 0.0000072 | No
04/05/2024 | 19:17 | LM64 | LONG RURAL | Third Party | Vehicle impact | 369.00 | 272.1 | 0.720654 | 0.0026481 | No
04/05/2024 | 23:48 | HH118C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 29.00 | 148.0 | 0.006617 | 0.0000447 | No
05/05/2024 | 08:22 | WHY03 | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
05/05/2024 | 08:29 | MI08 | LONG RURAL | Planned |  | 881.00 | 303.5 | 1.918958 | 0.0063223 | No
05/05/2024 | 08:57 | PP09 | LONG RURAL | Planned |  | 8.00 | 276.8 | 0.015888 | 0.0000574 | No
05/05/2024 | 09:00 | PL03 | URBAN | Planned |  | 28.00 | 259.0 | 0.011181 | 0.0000432 | No
05/05/2024 | 09:06 | SA31 | URBAN | Planned |  | 270.00 | 55.1 | 0.022926 | 0.0004163 | No
05/05/2024 | 09:27 | HH341F | URBAN | Planned |  | 121.00 | 395.0 | 0.073688 | 0.0001866 | No
05/05/2024 | 09:40 | EL16 | URBAN | Unknown | Unknown | 9.00 | 177.0 | 0.002456 | 0.0000139 | No
05/05/2024 | 10:14 | LC01 | SHORT RURAL | Planned |  | 55.00 | 298.0 | 0.115312 | 0.0003870 | No
05/05/2024 | 13:21 | MI10 | LONG RURAL | Unknown | Unknown | 1.00 | 252.0 | 0.001808 | 0.0000072 | No
05/05/2024 | 13:22 | SA711C | URBAN | Asset failure | LV | 65.00 | 51.0 | 0.005111 | 0.0001002 | No
05/05/2024 | 13:58 | CM18 | LONG RURAL | Unknown | Unknown | 47.00 | 92.0 | 0.031030 | 0.0003373 | No
05/05/2024 | 14:26 | SA744D | URBAN | Asset failure | HV | 611.00 | 526.3 | 0.495794 | 0.0009420 | No
05/05/2024 | 14:33 | SM126C | URBAN | Asset failure | LV | 2.00 | 302.0 | 0.000931 | 0.0000031 | No
05/05/2024 | 16:35 | LX51 | SHORT RURAL | Asset failure | LV | 1.00 | 86.0 | 0.000605 | 0.0000070 | No
05/05/2024 | 17:18 | NL234A | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
05/05/2024 | 18:16 | HH429C | URBAN | Unknown | Unknown | 1.00 | 40.0 | 0.000062 | 0.0000015 | No
05/05/2024 | 20:05 | NL115C | URBAN | Asset failure | LV | 4.00 | 128.0 | 0.000789 | 0.0000062 | No
05/05/2024 | 20:41 | MV11 | SHORT RURAL | Third Party | Vehicle impact | 138.00 | 254.8 | 0.247368 | 0.0009709 | No
05/05/2024 | 21:16 | HH121E | URBAN | Asset failure | LV | 1.00 | 66.0 | 0.000102 | 0.0000015 | No
05/05/2024 | 22:29 | HH341B | URBAN | Planned |  | 27.00 | 387.0 | 0.016110 | 0.0000416 | No
06/05/2024 | 03:22 | SA744D | URBAN | Asset failure | LV | 1.00 | 4.0 | 0.000006 | 0.0000015 | No
06/05/2024 | 08:51 | KA30 | SHORT RURAL | Planned |  | 1.00 | 6.0 | 0.000042 | 0.0000070 | No
06/05/2024 | 09:08 | SB01 | LONG RURAL | Planned |  | 3.00 | 198.0 | 0.004263 | 0.0000215 | No
06/05/2024 | 09:26 | CM24 | LONG RURAL | Planned |  | 2.00 | 261.0 | 0.003746 | 0.0000144 | No
06/05/2024 | 09:30 | MV41 | SHORT RURAL | Planned |  | 52.00 | 375.0 | 0.137192 | 0.0003658 | No
06/05/2024 | 09:36 | EL15 | SHORT RURAL | Planned |  | 308.00 | 237.0 | 0.513563 | 0.0021669 | No
06/05/2024 | 09:36 | EL15 | URBAN | Planned |  | 1,833.00 | 174.3 | 0.492703 | 0.0028260 | No
06/05/2024 | 09:53 | KI55 | LONG RURAL | Planned |  | 12.00 | 278.0 | 0.023940 | 0.0000861 | No
06/05/2024 | 09:57 | MI33 | LONG RURAL | Planned |  | 45.00 | 279.0 | 0.090099 | 0.0003229 | No
06/05/2024 | 10:26 | GA23 | SHORT RURAL | Planned |  | 8.00 | 250.3 | 0.014085 | 0.0000563 | No
06/05/2024 | 10:31 | HH145B | URBAN | Planned |  | 238.00 | 59.8 | 0.021935 | 0.0003669 | No
06/05/2024 | 10:31 | LX42 | SHORT RURAL | Planned |  | 6.00 | 56.0 | 0.002364 | 0.0000422 | No
06/05/2024 | 10:36 | SG04 | SHORT RURAL | Planned |  | 1.00 | 200.0 | 0.001407 | 0.0000070 | No
06/05/2024 | 10:44 | YK12 | LONG RURAL | Asset failure | LV | 2.00 | 256.0 | 0.003674 | 0.0000144 | No
06/05/2024 | 12:20 | HH145B | URBAN | Unknown | Unknown | 1.00 | 227.0 | 0.000350 | 0.0000015 | No
06/05/2024 | 12:30 | GA09 | LONG RURAL | Asset failure | HV | 4.00 | 98.0 | 0.002813 | 0.0000287 | No
06/05/2024 | 13:09 | HH386D | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
06/05/2024 | 13:29 | LX53 | SHORT RURAL | Planned |  | 2.00 | 19.0 | 0.000267 | 0.0000141 | No
06/05/2024 | 14:16 | VH43 | SHORT RURAL | Asset failure | Zone substation | 1.00 | 16.0 | 0.000113 | 0.0000070 | No
06/05/2024 | 15:01 | MB24 | SHORT RURAL | Overloads |  | 1.00 | 123.0 | 0.000865 | 0.0000070 | No
06/05/2024 | 16:15 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 194.0 | 0.001365 | 0.0000070 | No
06/05/2024 | 17:52 | EL10 | URBAN | Asset failure | LV | 33.00 | 38.0 | 0.001933 | 0.0000509 | No
06/05/2024 | 18:22 | VH45 | SHORT RURAL | Unknown | Unknown | 5.67 | 131.0 | 0.005223 | 0.0000399 | No
06/05/2024 | 18:59 | HH145A | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
06/05/2024 | 19:37 | EL07 | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
06/05/2024 | 19:47 | CN02 | LONG RURAL | Planned |  | 1.00 | 1,220.0 | 0.008755 | 0.0000072 | No
06/05/2024 | 20:04 | SG02 | SHORT RURAL | Animal | Animal impact | 6.00 | 176.0 | 0.007429 | 0.0000422 | No
06/05/2024 | 20:34 | SG14 | SHORT RURAL | Unknown | Unknown | 1.00 | 194.0 | 0.001365 | 0.0000070 | No
07/05/2024 | 05:52 | CV29 | LONG RURAL | Unknown | Unknown | 36.00 | 250.3 | 0.064659 | 0.0002583 | No
07/05/2024 | 06:27 | CV24 | LONG RURAL | Unknown | Unknown | 2.00 | 702.0 | 0.010076 | 0.0000144 | No
07/05/2024 | 07:03 | KA28 | LONG RURAL | Unknown | Unknown | 7.00 | 303.0 | 0.015221 | 0.0000502 | No
07/05/2024 | 08:39 | NA52 | LONG RURAL | Planned |  | 147.00 | 251.0 | 0.264764 | 0.0010549 | No
07/05/2024 | 08:52 | PA24 | LONG RURAL | Planned |  | 2.00 | 76.0 | 0.001091 | 0.0000144 | No
07/05/2024 | 08:57 | MB31 | LONG RURAL | Planned |  | 229.00 | 310.5 | 0.510345 | 0.0016434 | No
07/05/2024 | 09:01 | GA50 | URBAN | Planned |  | 426.00 | 321.2 | 0.210991 | 0.0006568 | No
07/05/2024 | 09:01 | MI16 | LONG RURAL | Planned |  | 76.00 | 298.1 | 0.162580 | 0.0005454 | No
07/05/2024 | 09:09 | NL210B | URBAN | Planned |  | 6.00 | 340.0 | 0.003145 | 0.0000093 | No
07/05/2024 | 09:42 | MI30 | LONG RURAL | Planned |  | 2.00 | 214.0 | 0.003071 | 0.0000144 | No
07/05/2024 | 09:42 | KI16 | LONG RURAL | Unknown | Unknown | 1.00 | 337.0 | 0.002418 | 0.0000072 | No
07/05/2024 | 09:42 | GU13 | LONG RURAL | Planned |  | 60.00 | 262.0 | 0.112812 | 0.0004306 | No
07/05/2024 | 09:49 | NA01 | LONG RURAL | Planned |  | 90.00 | 232.1 | 0.149928 | 0.0006459 | No
07/05/2024 | 10:25 | R16 | LONG RURAL | Planned |  | 2.00 | 197.0 | 0.002827 | 0.0000144 | No
07/05/2024 | 10:33 | AP829A | URBAN | Asset failure | HV | 279.00 | 140.1 | 0.060244 | 0.0004301 | No
07/05/2024 | 10:55 | AP227B | URBAN | Asset failure | LV | 68.00 | 90.0 | 0.009436 | 0.0001048 | No
07/05/2024 | 11:23 | HH432E | URBAN | Asset failure | LV | 1.00 | 184.0 | 0.000284 | 0.0000015 | No
07/05/2024 | 12:18 | GA52 | LONG RURAL | Weather |  | 3.00 | 14.0 | 0.000301 | 0.0000215 | No
07/05/2024 | 12:23 | EL13 | URBAN | Asset failure | LV | 1.00 | 159.0 | 0.000245 | 0.0000015 | No
07/05/2024 | 12:47 | MG33 | LONG RURAL | Unknown | Unknown | 1.00 | 213.0 | 0.001529 | 0.0000072 | No
07/05/2024 | 13:44 | AP125B | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
07/05/2024 | 14:14 | SM349F | URBAN | Asset failure | LV | 147.00 | 59.1 | 0.013387 | 0.0002266 | No
07/05/2024 | 14:46 | PA14 | LONG RURAL | Asset failure | LV | 1.00 | 348.0 | 0.002497 | 0.0000072 | No
07/05/2024 | 15:13 | YK25 | LONG RURAL | Asset failure | LV | 2.00 | 1,261.0 | 0.018099 | 0.0000144 | No
07/05/2024 | 15:30 | HH341F | URBAN | Asset failure | LV | 1.00 | 78.0 | 0.000120 | 0.0000015 | No
07/05/2024 | 15:52 | GA50 | URBAN | Asset failure | LV | 122.00 | 129.8 | 0.024412 | 0.0001881 | No
07/05/2024 | 16:12 | HH409E | URBAN | Asset failure | LV | 1.00 | 91.0 | 0.000140 | 0.0000015 | No
07/05/2024 | 19:52 | KA28 | LONG RURAL | Asset failure | HV | 7.00 | 103.0 | 0.005174 | 0.0000502 | No
07/05/2024 | 23:46 | HH403A | URBAN | Asset failure | HV | 1,540.00 | 113.1 | 0.268592 | 0.0023743 | No
08/05/2024 | 06:05 | SM350B | URBAN | Third Party | Vehicle impact | 1,754.00 | 174.6 | 0.472231 | 0.0027042 | No
08/05/2024 | 08:09 | CN42 | LONG RURAL | Planned |  | 246.00 | 325.0 | 0.573826 | 0.0017654 | No
08/05/2024 | 08:15 | AP425F | URBAN | Planned |  | 2.00 | 256.0 | 0.000789 | 0.0000031 | No
08/05/2024 | 08:16 | VH10 | SHORT RURAL | Planned |  | 7.00 | 187.0 | 0.009209 | 0.0000492 | No
08/05/2024 | 08:54 | GA50 | URBAN | Planned |  | 349.00 | 223.7 | 0.120371 | 0.0005381 | No
08/05/2024 | 09:06 | NA52 | LONG RURAL | Planned |  | 115.00 | 336.0 | 0.277293 | 0.0008253 | No
08/05/2024 | 09:12 | PA03 | URBAN | Overloads |  | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
08/05/2024 | 09:18 | SM349D | URBAN | Planned |  | 63.00 | 326.0 | 0.031665 | 0.0000971 | No
08/05/2024 | 09:31 | R14 | LONG RURAL | Planned |  | 8.00 | 350.8 | 0.020137 | 0.0000574 | No
08/05/2024 | 09:31 | BT37 | LONG RURAL | Planned |  | 14.00 | 113.0 | 0.011353 | 0.0001005 | No
08/05/2024 | 09:41 | SB19 | LONG RURAL | Planned |  | 13.00 | 218.0 | 0.020338 | 0.0000933 | No
08/05/2024 | 09:49 | GA02 | URBAN | Planned |  | 2.00 | 105.0 | 0.000324 | 0.0000031 | No
08/05/2024 | 09:50 | HH118D | URBAN | Asset failure | LV | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
08/05/2024 | 10:04 | MG12 | LONG RURAL | Planned |  | 307.00 | 294.0 | 0.647721 | 0.0022031 | No
08/05/2024 | 10:14 | BU10 | LONG RURAL | Planned |  | 47.00 | 93.0 | 0.031368 | 0.0003373 | No
08/05/2024 | 10:33 | KI11 | LONG RURAL | Planned |  | 456.00 | 132.0 | 0.431958 | 0.0032724 | No
08/05/2024 | 10:33 | NL111P | URBAN | Other |  | 1.00 | 60.0 | 0.000093 | 0.0000015 | No
08/05/2024 | 12:27 | R02 | LONG RURAL | Asset failure | LV | 2.00 | 259.0 | 0.003717 | 0.0000144 | No
08/05/2024 | 12:38 | SM216A | URBAN | Asset failure | LV | 35.00 | 254.0 | 0.013706 | 0.0000540 | No
08/05/2024 | 13:29 | SM216E | URBAN | Asset failure | LV | 2.00 | 1,671.0 | 0.005153 | 0.0000031 | No
08/05/2024 | 14:33 | MI11 | LONG RURAL | Unknown | Unknown | 43.00 | 162.0 | 0.049990 | 0.0003086 | No
08/05/2024 | 15:13 | HH148D | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
08/05/2024 | 15:40 | YK03 | LONG RURAL | Weather |  | 97.00 | 50.3 | 0.035013 | 0.0006961 | No
08/05/2024 | 16:32 | CD23 | LONG RURAL | Asset failure | LV | 2.00 | 53.0 | 0.000761 | 0.0000144 | No
08/05/2024 | 16:54 | MV32 | SHORT RURAL | Third Party | Vehicle impact | 9.00 | 103.0 | 0.006522 | 0.0000633 | No
08/05/2024 | 17:26 | SM374B | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
08/05/2024 | 17:43 | CM18 | LONG RURAL | Weather |  | 8.00 | 45.0 | 0.002583 | 0.0000574 | No
08/05/2024 | 19:38 | VH23 | SHORT RURAL | Asset failure | LV | 1.00 | 127.0 | 0.000894 | 0.0000070 | No
08/05/2024 | 20:28 | AP829G | URBAN | Overloads |  | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
09/05/2024 | 06:43 | ST22 | SHORT RURAL | Overloads |  | 4.00 | 230.0 | 0.006473 | 0.0000281 | No
09/05/2024 | 08:01 | AP425E | URBAN | Planned |  | 2.00 | 163.0 | 0.000503 | 0.0000031 | No
09/05/2024 | 08:09 | NA51 | LONG RURAL | Planned |  | 419.00 | 123.0 | 0.369846 | 0.0030069 | No
09/05/2024 | 08:12 | GA800A | URBAN | Animal | Animal impact | 2.00 | 55.0 | 0.000170 | 0.0000031 | No
09/05/2024 | 08:16 | PL08 | URBAN | Planned |  | 206.00 | 404.0 | 0.128320 | 0.0003176 | No
09/05/2024 | 08:33 | AP424A | URBAN | Planned |  | 113.00 | 343.0 | 0.059757 | 0.0001742 | No
09/05/2024 | 08:38 | MTB81 | SHORT RURAL | Planned |  | 60.00 | 295.0 | 0.124528 | 0.0004221 | No
09/05/2024 | 08:53 | MI24 | LONG RURAL | Planned |  | 120.00 | 188.8 | 0.162616 | 0.0008612 | No
09/05/2024 | 08:58 | SM349D | URBAN | Planned |  | 4.00 | 307.0 | 0.001893 | 0.0000062 | No
09/05/2024 | 09:05 | HH428F | URBAN | Unknown | Unknown | 4.67 | 183.0 | 0.001317 | 0.0000072 | No
09/05/2024 | 09:06 | NU28 | LONG RURAL | Planned |  | 74.00 | 292.0 | 0.155066 | 0.0005310 | No
09/05/2024 | 09:07 | BT03 | LONG RURAL | Planned |  | 7.00 | 257.0 | 0.012910 | 0.0000502 | No
09/05/2024 | 09:08 | HH130D | URBAN | Planned |  | 22.00 | 239.0 | 0.008107 | 0.0000339 | No
09/05/2024 | 09:10 | SM349F | URBAN | Planned |  | 76.00 | 299.8 | 0.035126 | 0.0001172 | No
09/05/2024 | 09:21 | MTB51 | LONG RURAL | Planned |  | 59.00 | 305.0 | 0.129124 | 0.0004234 | No
09/05/2024 | 09:30 | GA800A | SHORT RURAL | Planned |  | 26.00 | 343.7 | 0.062869 | 0.0001829 | No
09/05/2024 | 09:43 | SA41 | URBAN | Asset failure | LV | 1.00 | 110.0 | 0.000170 | 0.0000015 | No
09/05/2024 | 09:48 | ST21 | SHORT RURAL | Animal | Animal impact | 30.00 | 243.7 | 0.051429 | 0.0002111 | No
09/05/2024 | 10:12 | HH148D | URBAN | Unknown | Unknown | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
09/05/2024 | 10:14 | SD33100 | LONG RURAL | Planned |  | 4.00 | 171.3 | 0.004916 | 0.0000287 | No
09/05/2024 | 10:21 | GA800C | URBAN | Asset failure | HV | 2.00 | 56.0 | 0.000173 | 0.0000031 | No
09/05/2024 | 10:28 | NL111C | URBAN | Planned |  | 501.00 | 208.0 | 0.160663 | 0.0007724 | No
09/05/2024 | 10:36 | EL01A | URBAN | Asset failure | LV | 1.00 | 44.0 | 0.000068 | 0.0000015 | No
09/05/2024 | 11:25 | BT22 | LONG RURAL | Network business | Switching and protection error | 2.00 | 84.0 | 0.001206 | 0.0000144 | No
09/05/2024 | 11:27 | HH121D | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
09/05/2024 | 12:27 | KA06 | LONG RURAL | Asset failure | LV | 1.00 | 67.0 | 0.000481 | 0.0000072 | No
09/05/2024 | 12:31 | HH429C | URBAN | Planned |  | 189.00 | 3.0 | 0.000874 | 0.0002914 | No
09/05/2024 | 14:25 | NL234E | URBAN | Planned |  | 1.00 | 1.0 | 0.000002 | 0.0000015 | No
09/05/2024 | 15:08 | LX43 | SHORT RURAL | Unknown | Unknown | 17.00 | 115.0 | 0.013754 | 0.0001196 | No
09/05/2024 | 17:34 | PA06 | LONG RURAL | Asset failure | LV | 1.00 | 111.0 | 0.000797 | 0.0000072 | No
09/05/2024 | 19:18 | PL08 | URBAN | Third Party | Vehicle impact | 2.00 | 72.0 | 0.000222 | 0.0000031 | No
09/05/2024 | 19:45 | SA14 | URBAN | Overloads |  | 1.00 | 511.0 | 0.000788 | 0.0000015 | No
09/05/2024 | 20:52 | EL16 | URBAN | Unknown | Unknown | 281.00 | 12.6 | 0.005462 | 0.0004332 | No
10/05/2024 | 04:19 | CN52 | LONG RURAL | Weather |  | 17.00 | 307.0 | 0.037453 | 0.0001220 | No
10/05/2024 | 07:56 | EL02 | URBAN | Unknown | Unknown | 1.00 | 66.0 | 0.000102 | 0.0000015 | No
10/05/2024 | 08:38 | G02 | LONG RURAL | Third Party | Vehicle impact | 60.00 | 167.0 | 0.071907 | 0.0004306 | No
10/05/2024 | 09:08 | MI01 | LONG RURAL | Asset failure | LV | 53.00 | 1,433.0 | 0.545035 | 0.0003803 | No
10/05/2024 | 09:20 | CV25 | LONG RURAL | Asset failure | HV | 12.00 | 211.3 | 0.018199 | 0.0000861 | No
10/05/2024 | 09:22 | VH12 | SHORT RURAL | Planned |  | 367.00 | 165.0 | 0.426020 | 0.0025820 | No
10/05/2024 | 09:25 | CN52 | LONG RURAL | Weather |  | 86.00 | 44.0 | 0.027155 | 0.0006172 | No
10/05/2024 | 09:26 | HH341K | URBAN | Planned |  | 81.00 | 341.0 | 0.042585 | 0.0001249 | No
10/05/2024 | 09:33 | CN53 | LONG RURAL | Other |  | 2.00 | 190.0 | 0.002727 | 0.0000144 | No
10/05/2024 | 09:43 | MTB52 | LONG RURAL | Asset failure | LV | 2.00 | 136.0 | 0.001952 | 0.0000144 | No
10/05/2024 | 09:44 | HH130C | URBAN | Planned |  | 80.00 | 222.0 | 0.027383 | 0.0001233 | No
10/05/2024 | 09:48 | CN52 | LONG RURAL | Weather |  | 17.00 | 137.0 | 0.016714 | 0.0001220 | No
10/05/2024 | 10:20 | GU15 | LONG RURAL | Planned |  | 49.00 | 191.0 | 0.067163 | 0.0003516 | No
10/05/2024 | 10:47 | MB25 | LONG RURAL | Planned |  | 2.00 | 198.0 | 0.002842 | 0.0000144 | No
10/05/2024 | 11:09 | CBD27L | CBD | Unknown | Unknown | 7.00 | 76.0 | 0.076862 | 0.0010113 | No
10/05/2024 | 11:19 | SA14 | URBAN | Asset failure | LV | 24.33 | 159.0 | 0.005965 | 0.0000375 | No
10/05/2024 | 11:30 | SD33200 | LONG RURAL | Planned |  | 1.00 | 22.0 | 0.000158 | 0.0000072 | No
10/05/2024 | 13:09 | AP529A | URBAN | Asset failure | LV | 1.00 | 177.0 | 0.000273 | 0.0000015 | No
10/05/2024 | 14:25 | HH386B | URBAN | Asset failure | LV | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
10/05/2024 | 14:52 | HH118C | URBAN | Asset failure | LV | 1.00 | 122.0 | 0.000188 | 0.0000015 | No
10/05/2024 | 15:42 | AP424C | URBAN | Asset failure | LV | 1.00 | 179.0 | 0.000276 | 0.0000015 | No
10/05/2024 | 16:39 | PL04 | URBAN | Asset failure | HV | 3.00 | 9.0 | 0.000042 | 0.0000046 | No
10/05/2024 | 17:37 | CBD367G | CBD | Asset failure | LV | 1.00 | 226.0 | 0.032652 | 0.0001445 | No
10/05/2024 | 17:42 | HH118C | URBAN | Asset failure | LV | 1.00 | 438.0 | 0.000675 | 0.0000015 | No
10/05/2024 | 19:51 | EL20 | URBAN | Overloads |  | 3.00 | 79.0 | 0.000365 | 0.0000046 | No
10/05/2024 | 21:50 | SM411C | URBAN | Animal | Animal impact | 6.00 | 79.0 | 0.000731 | 0.0000093 | No
11/05/2024 | 01:44 | MV13 | SHORT RURAL | Unknown | Unknown | 487.00 | 12.5 | 0.042952 | 0.0034263 | No
11/05/2024 | 05:07 | CV24 | LONG RURAL | Unknown | Unknown | 82.00 | 328.0 | 0.193015 | 0.0005885 | No
11/05/2024 | 05:48 | MV42 | SHORT RURAL | Third Party | Vehicle impact | 18.67 | 360.0 | 0.047279 | 0.0001313 | No
11/05/2024 | 06:31 | MTB54 | LONG RURAL | Third Party | Vehicle impact | 252.00 | 280.3 | 0.506864 | 0.0018084 | No
11/05/2024 | 06:43 | CN52 | LONG RURAL | Unknown | Unknown | 17.00 | 348.0 | 0.042455 | 0.0001220 | No
11/05/2024 | 08:57 | W26 | LONG RURAL | Unknown | Unknown | 91.00 | 344.0 | 0.224648 | 0.0006530 | No
11/05/2024 | 09:21 | NL115D | URBAN | Animal | Animal nesting/burrowing, etc and other | 35.00 | 48.0 | 0.002590 | 0.0000540 | No
11/05/2024 | 09:27 | EL07 | URBAN | Other |  | 3.00 | 37.0 | 0.000171 | 0.0000046 | No
11/05/2024 | 09:49 | MV63 | SHORT RURAL | Planned |  | 230.00 | 142.0 | 0.229779 | 0.0016182 | No
11/05/2024 | 11:06 | SM172C | URBAN | Asset failure | LV | 53.00 | 77.0 | 0.006292 | 0.0000817 | No
11/05/2024 | 11:29 | CM03 | LONG RURAL | Unknown | Unknown | 7.00 | 219.0 | 0.011001 | 0.0000502 | No
11/05/2024 | 13:39 | NL111C | URBAN | Asset failure | LV | 1.00 | 192.0 | 0.000296 | 0.0000015 | No
11/05/2024 | 15:17 | SA14 | URBAN | Network business | Switching and protection error | 7.33 | 131.0 | 0.001481 | 0.0000113 | No
11/05/2024 | 15:34 | YK14 | LONG RURAL | Asset failure | HV | 472.00 | 205.9 | 0.697331 | 0.0033872 | No
11/05/2024 | 16:19 | EL25 | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
11/05/2024 | 17:44 | SA14 | URBAN | Asset failure | LV | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
11/05/2024 | 17:45 | CBD27L | CBD | Asset failure | LV | 21.00 | 388.0 | 1.177201 | 0.0030340 | No
11/05/2024 | 19:33 | SA40 | URBAN | Third Party | Vehicle impact | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
11/05/2024 | 20:58 | EL18 | URBAN | Asset failure | LV | 1.00 | 299.0 | 0.000461 | 0.0000015 | No
12/05/2024 | 01:28 | EL14 | URBAN | Unknown | Unknown | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
12/05/2024 | 05:00 | CBD412A | CBD | Planned |  | 4.00 | 271.8 | 0.157047 | 0.0005779 | No
12/05/2024 | 06:47 | SD35200 | LONG RURAL | Unknown | Unknown | 45.00 | 244.0 | 0.078796 | 0.0003229 | No
12/05/2024 | 07:07 | CN52 | LONG RURAL | Weather |  | 17.00 | 81.0 | 0.009882 | 0.0001220 | No
12/05/2024 | 07:59 | SM350D | URBAN | Unknown | Unknown | 125.00 | 96.0 | 0.018501 | 0.0001927 | No
12/05/2024 | 08:05 | SM350E | URBAN | Unknown | Unknown | 23.00 | 166.0 | 0.005886 | 0.0000355 | No
12/05/2024 | 08:33 | CN52 | LONG RURAL | Weather |  | 86.00 | 52.7 | 0.032509 | 0.0006172 | No
12/05/2024 | 09:14 | VH16 | SHORT RURAL | Asset failure | HV | 3.00 | 129.0 | 0.002723 | 0.0000211 | No
12/05/2024 | 10:35 | NL111Q | URBAN | Asset failure | LV | 1.00 | 242.0 | 0.000373 | 0.0000015 | No
12/05/2024 | 12:01 | CBD366T | CBD | Asset failure | LV | 1.00 | 374.0 | 0.054035 | 0.0001445 | No
12/05/2024 | 16:21 | MV15 | SHORT RURAL | Animal | Animal impact | 1,170.00 | 134.0 | 1.102898 | 0.0082315 | No
12/05/2024 | 18:28 | HH148D | URBAN | Asset failure | LV | 1.00 | 249.0 | 0.000384 | 0.0000015 | No
12/05/2024 | 18:40 | NA12 | LONG RURAL | Asset failure | LV | 1.00 | 229.0 | 0.001643 | 0.0000072 | No
12/05/2024 | 22:16 | GA26 | SHORT RURAL | Planned |  | 1.00 | 281.0 | 0.001977 | 0.0000070 | No
12/05/2024 | 22:16 | GA26 | URBAN | Planned |  | 176.00 | 284.0 | 0.077058 | 0.0002713 | No
12/05/2024 | 22:23 | MTB11 | SHORT RURAL | Asset failure | LV | 1.00 | 268.0 | 0.001886 | 0.0000070 | No
13/05/2024 | 05:38 | MT15 | LONG RURAL | Unknown | Unknown | 45.00 | 16.0 | 0.005167 | 0.0003229 | No
13/05/2024 | 05:53 | MG27 | LONG RURAL | Unknown | Unknown | 92.00 | 172.0 | 0.113558 | 0.0006602 | No
13/05/2024 | 08:02 | HH145B | URBAN | Asset failure | LV | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
13/05/2024 | 08:11 | AP425C | URBAN | Third Party | Unauthorised access | 3.00 | 99.0 | 0.000458 | 0.0000046 | No
13/05/2024 | 08:58 | GA25 | SHORT RURAL | Planned |  | 228.00 | 184.5 | 0.295997 | 0.0016041 | No
13/05/2024 | 09:04 | MG27 | LONG RURAL | Asset failure | HV | 12.00 | 198.0 | 0.017051 | 0.0000861 | No
13/05/2024 | 09:09 | GA17 | LONG RURAL | Planned |  | 115.00 | 122.0 | 0.100684 | 0.0008253 | No
13/05/2024 | 09:17 | PP16 | SHORT RURAL | Planned |  | 90.00 | 242.0 | 0.153233 | 0.0006332 | No
13/05/2024 | 09:21 | SG13 | SHORT RURAL | Planned |  | 24.00 | 228.3 | 0.038540 | 0.0001689 | No
13/05/2024 | 09:32 | CBD366T | CBD | Asset failure | LV | 4.33 | 283.0 | 0.177177 | 0.0006261 | No
13/05/2024 | 09:46 | KI13 | LONG RURAL | Planned |  | 1.00 | 255.0 | 0.001830 | 0.0000072 | No
13/05/2024 | 10:04 | NU13 | LONG RURAL | Animal | Animal impact | 62.00 | 112.9 | 0.050234 | 0.0004449 | No
13/05/2024 | 10:24 | WK65 | SHORT RURAL | Asset failure | LV | 1.00 | 410.0 | 0.002885 | 0.0000070 | No
13/05/2024 | 10:31 | G10 | LONG RURAL | Planned |  | 64.00 | 242.0 | 0.111147 | 0.0004593 | No
13/05/2024 | 10:35 | LM63 | LONG RURAL | Planned |  | 16.00 | 235.0 | 0.026983 | 0.0001148 | No
13/05/2024 | 11:18 | PL06 | URBAN | Planned |  | 1.00 | 84.0 | 0.000130 | 0.0000015 | No
13/05/2024 | 11:45 | HH107D | URBAN | Third Party | Other | 31.00 | 44.0 | 0.002103 | 0.0000478 | No
13/05/2024 | 12:03 | GA46 | LONG RURAL | Planned |  | 89.00 | 102.0 | 0.065147 | 0.0006387 | No
13/05/2024 | 12:04 | SA34 | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
13/05/2024 | 12:31 | CN42 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 1,758.0 | 0.012616 | 0.0000072 | No
13/05/2024 | 13:51 | EL01M | URBAN | Animal | Animal impact | 92.00 | 134.0 | 0.019007 | 0.0001418 | No
13/05/2024 | 15:06 | GA25 | SHORT RURAL | Asset failure | LV | 60.00 | 195.0 | 0.082315 | 0.0004221 | No
13/05/2024 | 16:26 | KI31 | LONG RURAL | Planned |  | 1.00 | 3.0 | 0.000022 | 0.0000072 | No
13/05/2024 | 16:26 | KI31 | SHORT RURAL | Planned |  | 1,732.00 | 3.0 | 0.036556 | 0.0121855 | No
13/05/2024 | 16:37 | NL234E | URBAN | Asset failure | LV | 1.00 | 279.0 | 0.000430 | 0.0000015 | No
13/05/2024 | 17:07 | KI22 | LONG RURAL | Asset failure | LV | 1.00 | 463.0 | 0.003323 | 0.0000072 | No
13/05/2024 | 18:21 | ST35 | LONG RURAL | Unknown | Unknown | 9.00 | 208.0 | 0.013434 | 0.0000646 | No
13/05/2024 | 20:06 | SM374A | URBAN | Unknown | Unknown | 3,071.00 | 46.8 | 0.221421 | 0.0047347 | No
13/05/2024 | 23:44 | MI14 | LONG RURAL | Asset failure | HV | 167.00 | 129.9 | 0.155712 | 0.0011984 | No
14/05/2024 | 00:03 | W01 | LONG RURAL | Animal | Animal impact | 43.00 | 137.0 | 0.042276 | 0.0003086 | No
14/05/2024 | 07:04 | AP132B | URBAN | Unknown | Unknown | 69.00 | 212.6 | 0.022618 | 0.0001064 | No
14/05/2024 | 07:13 | WK43 | SHORT RURAL | Weather |  | 41.33 | 205.2 | 0.059670 | 0.0002908 | No
14/05/2024 | 08:05 | CD03 | SHORT RURAL | Planned |  | 6.00 | 276.7 | 0.011679 | 0.0000422 | No
14/05/2024 | 08:23 | SD48104 | SHORT RURAL | Planned |  | 1.00 | 572.0 | 0.004024 | 0.0000070 | No
14/05/2024 | 08:24 | CL09 | LONG RURAL | Unknown | Unknown | 1.00 | 44.0 | 0.000316 | 0.0000072 | No
14/05/2024 | 08:27 | AP425B | URBAN | Animal | Animal impact | 41.33 | 180.0 | 0.011471 | 0.0000637 | No
14/05/2024 | 08:53 | G02 | LONG RURAL | Planned |  | 20.00 | 459.0 | 0.065879 | 0.0001435 | No
14/05/2024 | 08:59 | MV52 | SHORT RURAL | Planned |  | 12.00 | 379.3 | 0.032019 | 0.0000844 | No
14/05/2024 | 09:00 | GA47 | LONG RURAL | Planned |  | 59.00 | 140.0 | 0.059276 | 0.0004234 | No
14/05/2024 | 09:02 | HH496C | URBAN | Asset failure | LV | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
14/05/2024 | 09:04 | LX21 | SHORT RURAL | Planned |  | 92.00 | 211.0 | 0.136573 | 0.0006473 | No
14/05/2024 | 09:11 | GA07 | LONG RURAL | Overloads |  | 1.00 | 184.0 | 0.001320 | 0.0000072 | No
14/05/2024 | 09:23 | HH496G | URBAN | Planned |  | 260.00 | 76.6 | 0.030687 | 0.0004009 | No
14/05/2024 | 09:33 | MI30 | LONG RURAL | Planned |  | 28.00 | 308.0 | 0.061889 | 0.0002009 | No
14/05/2024 | 09:49 | GA25 | SHORT RURAL | Planned |  | 110.00 | 183.0 | 0.141624 | 0.0007739 | No
14/05/2024 | 10:07 | G06 | LONG RURAL | Planned |  | 66.00 | 192.0 | 0.090938 | 0.0004736 | No
14/05/2024 | 10:13 | MV63 | SHORT RURAL | Asset failure | LV | 1.00 | 317.0 | 0.002230 | 0.0000070 | No
14/05/2024 | 10:14 | SM172D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 830.00 | 31.0 | 0.039669 | 0.0012797 | No
14/05/2024 | 10:17 | SG07 | SHORT RURAL | Planned |  | 24.00 | 256.5 | 0.043318 | 0.0001689 | No
14/05/2024 | 11:27 | HH386D | URBAN | Asset failure | LV | 25.00 | 53.0 | 0.002043 | 0.0000385 | No
14/05/2024 | 11:52 | HH496G | URBAN | Planned |  | 211.00 | 8.0 | 0.002602 | 0.0003253 | No
14/05/2024 | 12:29 | SM179A | URBAN | Overloads |  | 22.33 | 104.0 | 0.003581 | 0.0000344 | No
14/05/2024 | 14:10 | AP125B | URBAN | Asset failure | HV | 500.00 | 9.0 | 0.006916 | 0.0007709 | No
14/05/2024 | 14:12 | AP125B | URBAN | Asset failure | HV | 421.00 | 3.0 | 0.001947 | 0.0006491 | No
14/05/2024 | 15:24 | CM09 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 2.00 | 139.0 | 0.001995 | 0.0000144 | No
14/05/2024 | 15:52 | LM61 | LONG RURAL | Overloads |  | 2.33 | 145.0 | 0.002428 | 0.0000167 | No
14/05/2024 | 16:53 | SG10 | SHORT RURAL | Asset failure | LV | 1.00 | 241.0 | 0.001696 | 0.0000070 | No
14/05/2024 | 17:05 | VH45 | SHORT RURAL | Asset failure | LV | 2.00 | 322.0 | 0.004531 | 0.0000141 | No
14/05/2024 | 17:40 | SA33 | URBAN | Asset failure | LV | 21.00 | 145.0 | 0.004693 | 0.0000324 | No
14/05/2024 | 18:42 | EL01R | URBAN | Asset failure | LV | 16.00 | 1,582.0 | 0.039025 | 0.0000247 | No
14/05/2024 | 18:56 | MB62 | LONG RURAL | Asset failure | LV | 1.00 | 305.0 | 0.002189 | 0.0000072 | No
14/05/2024 | 18:56 | MB62 | LONG RURAL | Asset failure | LV | 12.00 | 308.0 | 0.026524 | 0.0000861 | No
15/05/2024 | 00:18 | EL01B | URBAN | Overloads |  | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
15/05/2024 | 08:12 | GA09 | LONG RURAL | Planned |  | 10.00 | 348.0 | 0.024974 | 0.0000718 | No
15/05/2024 | 08:43 | SM350D | URBAN | Overloads |  | 1.00 | 261.0 | 0.000402 | 0.0000015 | No
15/05/2024 | 08:47 | SA18 | URBAN | Asset failure | LV | 1.00 | 99.0 | 0.000153 | 0.0000015 | No
15/05/2024 | 08:52 | GA50 | URBAN | Planned |  | 8.00 | 185.0 | 0.002282 | 0.0000123 | No
15/05/2024 | 08:52 | SD34102 | LONG RURAL | Unknown | Unknown | 1.00 | 364.0 | 0.002612 | 0.0000072 | No
15/05/2024 | 09:06 | GA24 | LONG RURAL | Planned |  | 99.00 | 79.0 | 0.056126 | 0.0007105 | No
15/05/2024 | 09:07 | KI11 | LONG RURAL | Planned |  | 183.00 | 369.0 | 0.484596 | 0.0013133 | No
15/05/2024 | 09:07 | VH15 | SHORT RURAL | Planned |  | 4.00 | 285.0 | 0.008020 | 0.0000281 | No
15/05/2024 | 09:10 | GA05 | SHORT RURAL | Planned |  | 27.00 | 140.2 | 0.026636 | 0.0001900 | No
15/05/2024 | 09:12 | MB16 | SHORT RURAL | Planned |  | 38.00 | 302.4 | 0.080845 | 0.0002673 | No
15/05/2024 | 09:17 | CM11 | LONG RURAL | Planned |  | 63.00 | 258.0 | 0.116644 | 0.0004521 | No
15/05/2024 | 09:32 | HH409A | URBAN | Planned |  | 39.00 | 240.0 | 0.014431 | 0.0000601 | No
15/05/2024 | 09:50 | EL01A | URBAN | Overloads |  | 1.00 | 104.0 | 0.000160 | 0.0000015 | No
15/05/2024 | 10:06 | SD34102 | LONG RURAL | Planned |  | 2.00 | 275.0 | 0.003947 | 0.0000144 | No
15/05/2024 | 10:10 | NL760A | URBAN | Planned |  | 10.00 | 228.0 | 0.003515 | 0.0000154 | No
15/05/2024 | 10:26 | SD33200 | LONG RURAL | Planned |  | 2.00 | 27.0 | 0.000388 | 0.0000144 | No
15/05/2024 | 11:08 | SD34400 | LONG RURAL | Planned |  | 1.00 | 36.0 | 0.000258 | 0.0000072 | No
15/05/2024 | 11:38 | EL19 | URBAN | Planned |  | 16.00 | 69.0 | 0.001702 | 0.0000247 | No
15/05/2024 | 12:52 | HH177D | URBAN | Asset failure | LV | 19.00 | 102.0 | 0.002988 | 0.0000293 | No
15/05/2024 | 12:53 | WHY13 | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
15/05/2024 | 13:15 | CBD366E | URBAN | Other |  | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
15/05/2024 | 13:21 | CV24 | LONG RURAL | Weather |  | 7.00 | 46.0 | 0.002311 | 0.0000502 | No
15/05/2024 | 15:11 | AP149C | URBAN | Asset failure | LV | 145.00 | 210.9 | 0.047155 | 0.0002236 | No
15/05/2024 | 15:11 | R03 | LONG RURAL | Asset failure | HV | 1.00 | 18.0 | 0.000129 | 0.0000072 | No
15/05/2024 | 16:25 | NL115E | URBAN | Asset failure | LV | 1.00 | 175.0 | 0.000270 | 0.0000015 | No
15/05/2024 | 17:01 | HH409A | URBAN | Asset failure | LV | 15.00 | 139.0 | 0.003215 | 0.0000231 | No
15/05/2024 | 19:54 | HH177G | URBAN | Asset failure | LV | 1.00 | 94.0 | 0.000145 | 0.0000015 | No
15/05/2024 | 20:29 | BM21 | SHORT RURAL | Asset failure | LV | 13.00 | 42.0 | 0.003841 | 0.0000915 | No
15/05/2024 | 21:06 | MT14 | SHORT RURAL | Asset failure | HV | 2.00 | 30.0 | 0.000422 | 0.0000141 | No
15/05/2024 | 21:21 | AP529A | URBAN | Asset failure | LV | 1.00 | 82.0 | 0.000126 | 0.0000015 | No
16/05/2024 | 03:10 | HH177G | URBAN | Third Party | Vehicle impact | 36.00 | 357.0 | 0.019815 | 0.0000555 | No
16/05/2024 | 06:45 | HH177G | URBAN | Third Party | Vehicle impact | 48.00 | 187.0 | 0.013839 | 0.0000740 | No
16/05/2024 | 07:03 | WHY14 | URBAN | Asset failure | HV | 105.00 | 312.0 | 0.050508 | 0.0001619 | No
16/05/2024 | 07:10 | SB17 | LONG RURAL | Asset failure | HV | 80.00 | 47.2 | 0.027076 | 0.0005741 | No
16/05/2024 | 07:11 | GU51 | URBAN | Overloads |  | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
16/05/2024 | 07:17 | MG04 | SHORT RURAL | Unknown | Unknown | 60.67 | 100.0 | 0.042682 | 0.0004268 | No
16/05/2024 | 08:07 | PL08 | URBAN | Planned |  | 205.00 | 445.5 | 0.140810 | 0.0003161 | No
16/05/2024 | 08:16 | AP139B | URBAN | Planned |  | 144.00 | 428.0 | 0.095021 | 0.0002220 | No
16/05/2024 | 08:40 | GA09 | LONG RURAL | Planned |  | 65.00 | 146.0 | 0.068103 | 0.0004665 | No
16/05/2024 | 08:44 | EL260D | URBAN | Unknown | Unknown | 1.00 | 115.0 | 0.000177 | 0.0000015 | No
16/05/2024 | 08:54 | GA15 | SHORT RURAL | Planned |  | 242.00 | 193.9 | 0.330070 | 0.0017026 | No
16/05/2024 | 09:19 | MV53 | SHORT RURAL | Third Party | Other | 1.00 | 211.0 | 0.001484 | 0.0000070 | No
16/05/2024 | 09:36 | AP139D | URBAN | Planned |  | 2.00 | 332.0 | 0.001024 | 0.0000031 | No
16/05/2024 | 09:37 | EL10 | URBAN | Planned |  | 136.00 | 189.6 | 0.039751 | 0.0002097 | No
16/05/2024 | 09:37 | AP139B | URBAN | Planned |  | 105.00 | 150.0 | 0.024283 | 0.0001619 | No
16/05/2024 | 09:41 | KI13 | LONG RURAL | Planned |  | 95.00 | 282.0 | 0.192254 | 0.0006818 | No
16/05/2024 | 09:47 | MV51 | SHORT RURAL | Planned |  | 37.00 | 317.6 | 0.082667 | 0.0002603 | No
16/05/2024 | 09:52 | CM16 | LONG RURAL | Third Party | Vehicle impact | 651.00 | 157.4 | 0.735244 | 0.0046718 | No
16/05/2024 | 10:21 | LX21 | SHORT RURAL | Planned |  | 1.00 | 104.0 | 0.000732 | 0.0000070 | No
16/05/2024 | 10:28 | VH12 | SHORT RURAL | Asset failure | LV | 7.67 | 211.0 | 0.011381 | 0.0000539 | No
16/05/2024 | 10:36 | SB01 | LONG RURAL | Asset failure | HV | 981.00 | 50.4 | 0.354597 | 0.0070400 | No
16/05/2024 | 10:39 | CM01 | LONG RURAL | Unknown | Unknown | 1.00 | 291.0 | 0.002088 | 0.0000072 | No
16/05/2024 | 11:57 | AP149H | URBAN | Asset failure | LV | 84.00 | 142.2 | 0.018418 | 0.0001295 | No
16/05/2024 | 12:21 | PP03 | URBAN | Asset failure | LV | 1.00 | 578.0 | 0.000891 | 0.0000015 | No
16/05/2024 | 12:24 | AP139B | URBAN | Planned |  | 1.00 | 161.0 | 0.000248 | 0.0000015 | No
16/05/2024 | 12:28 | AP139D | URBAN | Planned |  | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
16/05/2024 | 13:47 | HH409E | URBAN | Asset failure | LV | 1.00 | 269.0 | 0.000415 | 0.0000015 | No
16/05/2024 | 14:00 | CD17 | LONG RURAL | Asset failure | HV | 5.00 | 212.0 | 0.007607 | 0.0000359 | No
16/05/2024 | 15:19 | PP05 | LONG RURAL | Third Party | Vehicle impact | 7.00 | 188.0 | 0.009444 | 0.0000502 | No
16/05/2024 | 16:06 | SA14 | URBAN | Overloads |  | 1.00 | 324.0 | 0.000500 | 0.0000015 | No
16/05/2024 | 16:10 | LX41 | SHORT RURAL | Asset failure | LV | 7.00 | 52.0 | 0.002561 | 0.0000492 | No
16/05/2024 | 16:19 | MV51 | SHORT RURAL | Planned |  | 12.00 | 21.0 | 0.001773 | 0.0000844 | No
16/05/2024 | 16:41 | EL16 | URBAN | Unknown | Unknown | 9.00 | 489.0 | 0.006785 | 0.0000139 | No
16/05/2024 | 17:47 | HH145D | URBAN | Asset failure | LV | 21.67 | 218.0 | 0.007282 | 0.0000334 | No
16/05/2024 | 21:50 | PL08 | URBAN | Planned |  | 2.00 | 12.0 | 0.000037 | 0.0000031 | No
16/05/2024 | 23:13 | EL260A | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
17/05/2024 | 03:24 | CL12 | LONG RURAL | Planned |  | 1.00 | 21.0 | 0.000151 | 0.0000072 | No
17/05/2024 | 03:49 | MI20 | LONG RURAL | Unknown | Unknown | 33.67 | 182.0 | 0.043972 | 0.0002416 | No
17/05/2024 | 04:58 | MB83 | LONG RURAL | Asset failure | HV | 382.00 | 157.2 | 0.430867 | 0.0027414 | No
17/05/2024 | 07:02 | NL210A | URBAN | Overloads |  | 1.00 | 219.0 | 0.000338 | 0.0000015 | No
17/05/2024 | 08:00 | AP149C | URBAN | Planned |  | 53.00 | 459.0 | 0.037506 | 0.0000817 | No
17/05/2024 | 08:25 | VH21 | SHORT RURAL | Asset failure | HV | 219.00 | 57.4 | 0.088471 | 0.0015408 | No
17/05/2024 | 08:38 | NL21 | URBAN | Asset failure | LV | 1.00 | 163.0 | 0.000251 | 0.0000015 | No
17/05/2024 | 08:41 | MTB81 | LONG RURAL | Planned |  | 36.00 | 213.0 | 0.055028 | 0.0002583 | No
17/05/2024 | 08:41 | MTB81 | SHORT RURAL | Planned |  | 4.00 | 226.0 | 0.006360 | 0.0000281 | No
17/05/2024 | 08:47 | EL03 | URBAN | Planned |  | 46.00 | 413.0 | 0.029290 | 0.0000709 | No
17/05/2024 | 08:47 | HH130B | URBAN | Overloads |  | 1.00 | 37.0 | 0.000057 | 0.0000015 | No
17/05/2024 | 08:53 | YK20 | LONG RURAL | Planned |  | 90.00 | 239.0 | 0.154363 | 0.0006459 | No
17/05/2024 | 09:03 | GA15 | SHORT RURAL | Planned |  | 40.00 | 168.0 | 0.047278 | 0.0002814 | No
17/05/2024 | 09:06 | SB19 | LONG RURAL | Third Party | Vehicle impact | 50.00 | 267.0 | 0.095790 | 0.0003588 | No
17/05/2024 | 09:07 | MG26 | LONG RURAL | Unknown | Unknown | 11.00 | 229.0 | 0.018077 | 0.0000789 | No
17/05/2024 | 09:09 | GA08 | LONG RURAL | Planned |  | 63.00 | 167.3 | 0.075653 | 0.0004521 | No
17/05/2024 | 09:10 | VH35 | SHORT RURAL | Planned |  | 3.00 | 263.0 | 0.005551 | 0.0000211 | No
17/05/2024 | 09:12 | MB02 | LONG RURAL | Unknown | Unknown | 105.00 | 323.0 | 0.243357 | 0.0007535 | No
17/05/2024 | 09:27 | GA26 | URBAN | Planned |  | 149.00 | 177.8 | 0.040846 | 0.0002297 | No
17/05/2024 | 10:16 | EL01N | URBAN | Overloads |  | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
17/05/2024 | 10:20 | HH403D | URBAN | Unknown | Unknown | 2.00 | 74.0 | 0.000228 | 0.0000031 | No
17/05/2024 | 10:23 | NL234B | URBAN | Planned |  | 10.00 | 103.0 | 0.001588 | 0.0000154 | No
17/05/2024 | 10:31 | R32 | LONG RURAL | Planned |  | 79.00 | 91.6 | 0.051949 | 0.0005669 | No
17/05/2024 | 10:44 | CM11 | LONG RURAL | Asset failure | HV | 7.00 | 100.7 | 0.005059 | 0.0000502 | No
17/05/2024 | 10:50 | MV33 | SHORT RURAL | Planned |  | 19.00 | 17.0 | 0.002272 | 0.0001337 | No
17/05/2024 | 11:39 | NL111C | URBAN | Planned |  | 98.00 | 35.0 | 0.005288 | 0.0001511 | No
17/05/2024 | 11:41 | ME200F | URBAN | Asset failure | LV | 1.00 | 196.0 | 0.000302 | 0.0000015 | No
17/05/2024 | 12:14 | HH107C | URBAN | Third Party | Vehicle impact | 1.00 | 35.0 | 0.000054 | 0.0000015 | No
17/05/2024 | 12:48 | EL12 | URBAN | Planned |  | 3.00 | 15.0 | 0.000069 | 0.0000046 | No
17/05/2024 | 13:13 | G22 | LONG RURAL | Asset failure | HV | 3.00 | 351.0 | 0.007557 | 0.0000215 | No
17/05/2024 | 14:17 | GA35 | LONG RURAL | Third Party | Vehicle impact | 72.00 | 438.9 | 0.226786 | 0.0005167 | No
17/05/2024 | 14:18 | MI16 | LONG RURAL | Asset failure | HV | 18.33 | 162.0 | 0.021314 | 0.0001316 | No
17/05/2024 | 14:47 | AP424C | URBAN | Asset failure | LV | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
17/05/2024 | 16:26 | SG12 | SHORT RURAL | Animal | Animal impact | 1.00 | 81.0 | 0.000570 | 0.0000070 | No
17/05/2024 | 19:04 | ME116B | URBAN | Asset failure | LV | 1.00 | 319.0 | 0.000492 | 0.0000015 | No
17/05/2024 | 20:30 | VH72 | SHORT RURAL | Asset failure | HV | 38.00 | 117.0 | 0.031280 | 0.0002673 | No
17/05/2024 | 20:35 | HH118D | URBAN | Asset failure | LV | 81.00 | 44.0 | 0.005495 | 0.0001249 | No
17/05/2024 | 20:41 | SM179C | URBAN | Weather |  | 1,357.00 | 206.4 | 0.431895 | 0.0020922 | No
17/05/2024 | 20:56 | SM179C | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
17/05/2024 | 21:06 | SM179C | URBAN | Asset failure | LV | 1.00 | 108.0 | 0.000167 | 0.0000015 | No
17/05/2024 | 21:14 | PL07 | URBAN | Asset failure | LV | 2.67 | 48.6 | 0.000200 | 0.0000041 | No
17/05/2024 | 21:52 | SG10 | SHORT RURAL | Weather |  | 776.00 | 177.8 | 0.970729 | 0.0054595 | No
18/05/2024 | 01:17 | ME116B | URBAN | Asset failure | LV | 1.00 | 630.0 | 0.000971 | 0.0000015 | No
18/05/2024 | 07:13 | PA08 | LONG RURAL | Asset failure | LV | 1.00 | 157.0 | 0.001127 | 0.0000072 | No
18/05/2024 | 07:34 | SM411E | URBAN | Asset failure | LV | 1.00 | 368.0 | 0.000567 | 0.0000015 | No
18/05/2024 | 07:52 | NU13 | LONG RURAL | Animal | Animal impact | 8.00 | 198.0 | 0.011367 | 0.0000574 | No
18/05/2024 | 08:36 | HH409D | URBAN | Asset failure | LV | 38.00 | 29.0 | 0.001699 | 0.0000586 | No
18/05/2024 | 10:37 | MTB82 | SHORT RURAL | Planned |  | 627.00 | 21.0 | 0.092664 | 0.0044113 | No
18/05/2024 | 11:53 | G40 | LONG RURAL | Planned |  | 1,118.00 | 3.0 | 0.024069 | 0.0080231 | No
18/05/2024 | 12:10 | ME427F | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
18/05/2024 | 12:14 | SA14 | URBAN | Unknown | Unknown | 17.00 | 99.0 | 0.002595 | 0.0000262 | No
18/05/2024 | 12:19 | HH148A | URBAN | Asset failure | LV | 39.00 | 716.0 | 0.043052 | 0.0000601 | No
18/05/2024 | 17:22 | G22 | LONG RURAL | Animal | Animal impact | 2.00 | 281.0 | 0.004033 | 0.0000144 | No
18/05/2024 | 18:10 | G40 | LONG RURAL | Asset failure | LV | 27.00 | 53.0 | 0.010269 | 0.0001938 | No
18/05/2024 | 19:06 | HH386F | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 3.00 | 291.0 | 0.001346 | 0.0000046 | No
18/05/2024 | 20:37 | HH409E | URBAN | Asset failure | LV | 122.00 | 106.0 | 0.019938 | 0.0001881 | No
18/05/2024 | 20:50 | G22 | LONG RURAL | Animal | Animal impact | 1.00 | 72.0 | 0.000517 | 0.0000072 | No
18/05/2024 | 23:18 | MV64 | SHORT RURAL | Asset failure | LV | 70.00 | 187.0 | 0.092095 | 0.0004925 | No
19/05/2024 | 04:13 | HH121D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 626.00 | 86.0 | 0.083002 | 0.0009651 | No
19/05/2024 | 06:26 | NA52 | LONG RURAL | Weather |  | 492.00 | 161.2 | 0.569054 | 0.0035308 | No
19/05/2024 | 07:58 | SM126E | URBAN | Asset failure | LV | 1.00 | 364.0 | 0.000561 | 0.0000015 | No
19/05/2024 | 08:01 | YK20 | LONG RURAL | Planned |  | 1,411.00 | 341.0 | 3.452805 | 0.0101258 | No
19/05/2024 | 08:41 | SD44400 | SHORT RURAL | Asset failure | Subtransmission | 9.00 | 197.0 | 0.012474 | 0.0000633 | No
19/05/2024 | 08:51 | SM349H | URBAN | Planned |  | 166.00 | 264.5 | 0.067695 | 0.0002559 | No
19/05/2024 | 09:10 | GA28 | LONG RURAL | Planned |  | 1.00 | 194.0 | 0.001392 | 0.0000072 | No
19/05/2024 | 09:10 | GA28 | LONG RURAL | Planned |  | 16.00 | 185.0 | 0.021242 | 0.0001148 | No
19/05/2024 | 09:35 | EL25 | URBAN | Planned |  | 669.00 | 26.0 | 0.026817 | 0.0010314 | No
19/05/2024 | 09:55 | VH21 | SHORT RURAL | Overloads |  | 1.00 | 241.0 | 0.001696 | 0.0000070 | No
19/05/2024 | 10:15 | MV14 | SHORT RURAL | Planned |  | 26.00 | 12.0 | 0.002195 | 0.0001829 | No
19/05/2024 | 10:31 | MV14 | SHORT RURAL | Planned |  | 26.00 | 156.0 | 0.028536 | 0.0001829 | No
19/05/2024 | 11:27 | VH33 | SHORT RURAL | Animal | Animal impact | 12.67 | 235.0 | 0.020942 | 0.0000891 | No
19/05/2024 | 12:04 | HH145A | URBAN | Asset failure | LV | 1.00 | 207.0 | 0.000319 | 0.0000015 | No
19/05/2024 | 14:02 | SM349H | URBAN | Planned |  | 38.00 | 66.0 | 0.003867 | 0.0000586 | No
19/05/2024 | 14:30 | HH118D | URBAN | Asset failure | LV | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
19/05/2024 | 14:43 | HH102B | URBAN | Overloads |  | 1.00 | 421.0 | 0.000649 | 0.0000015 | No
19/05/2024 | 14:44 | ME427F | URBAN | Animal | Animal impact | 4.67 | 208.0 | 0.001497 | 0.0000072 | No
19/05/2024 | 16:50 | HH121A | URBAN | Third Party | Other | 1,148.00 | 32.0 | 0.056638 | 0.0017699 | No
19/05/2024 | 16:52 | EL260A | URBAN | Weather |  | 1,123.00 | 140.3 | 0.242880 | 0.0017314 | No
19/05/2024 | 18:44 | HH409F | URBAN | Asset failure | LV | 63.00 | 123.0 | 0.011947 | 0.0000971 | No
19/05/2024 | 21:08 | AP424C | URBAN | Unknown | Unknown | 642.00 | 137.0 | 0.135645 | 0.0009898 | No
19/05/2024 | 22:20 | HH496H | URBAN | Planned |  | 4.00 | 213.0 | 0.001314 | 0.0000062 | No
20/05/2024 | 00:22 | MB02 | LONG RURAL | Weather |  | 105.00 | 416.5 | 0.313821 | 0.0007535 | No
20/05/2024 | 04:22 | CN83 | LONG RURAL | Weather |  | 147.00 | 658.3 | 0.694403 | 0.0010549 | No
20/05/2024 | 05:27 | GA45 | SHORT RURAL | Weather |  | 58.00 | 390.0 | 0.159143 | 0.0004081 | No
20/05/2024 | 07:05 | VH17 | SHORT RURAL | Asset failure | HV | 309.00 | 21.2 | 0.046104 | 0.0021740 | No
20/05/2024 | 07:09 | MG17 | LONG RURAL | Network business | Switching and protection error | 1.00 | 124.0 | 0.000890 | 0.0000072 | No
20/05/2024 | 07:25 | LX21 | SHORT RURAL | Animal | Animal impact | 210.00 | 195.9 | 0.289468 | 0.0014775 | No
20/05/2024 | 07:26 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 90.0 | 0.000633 | 0.0000070 | No
20/05/2024 | 08:30 | KA04 | LONG RURAL | Planned |  | 10.00 | 228.0 | 0.016362 | 0.0000718 | No
20/05/2024 | 08:45 | LC01 | SHORT RURAL | Planned |  | 17.00 | 179.0 | 0.021409 | 0.0001196 | No
20/05/2024 | 09:01 | VH23 | SHORT RURAL | Planned |  | 5.00 | 373.0 | 0.013121 | 0.0000352 | No
20/05/2024 | 09:06 | MI10 | LONG RURAL | Planned |  | 47.00 | 354.0 | 0.119400 | 0.0003373 | No
20/05/2024 | 09:07 | BT10 | LONG RURAL | Planned |  | 34.00 | 424.0 | 0.103454 | 0.0002440 | No
20/05/2024 | 09:12 | R12 | LONG RURAL | Planned |  | 100.00 | 327.0 | 0.234666 | 0.0007176 | No
20/05/2024 | 09:21 | BM42 | SHORT RURAL | Unknown | Unknown | 95.00 | 66.0 | 0.044113 | 0.0006684 | No
20/05/2024 | 09:42 | SD38200 | LONG RURAL | Planned |  | 2.00 | 276.0 | 0.003961 | 0.0000144 | No
20/05/2024 | 09:44 | CD01 | SHORT RURAL | Planned |  | 32.00 | 407.0 | 0.091630 | 0.0002251 | No
20/05/2024 | 09:51 | CL01 | LONG RURAL | Weather |  | 1.00 | 564.0 | 0.004047 | 0.0000072 | No
20/05/2024 | 09:54 | MI20 | LONG RURAL | Planned |  | 2.00 | 229.0 | 0.003287 | 0.0000144 | No
20/05/2024 | 10:37 | SG09 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 38.0 | 0.000267 | 0.0000070 | No
20/05/2024 | 10:59 | AP425C | URBAN | Asset failure | LV | 74.00 | 86.4 | 0.009855 | 0.0001141 | No
20/05/2024 | 11:01 | YK04 | SHORT RURAL | Asset failure | LV | 1.00 | 118.0 | 0.000830 | 0.0000070 | No
20/05/2024 | 11:45 | M51 | SHORT RURAL | Animal | Animal impact | 2.67 | 1,674.0 | 0.031406 | 0.0000188 | No
20/05/2024 | 12:36 | EL03 | URBAN | Unknown | Unknown | 1.00 | 144.0 | 0.000222 | 0.0000015 | No
20/05/2024 | 12:50 | AP829D | URBAN | Asset failure | LV | 1.00 | 76.0 | 0.000117 | 0.0000015 | No
20/05/2024 | 13:51 | CL20 | LONG RURAL | Asset failure | LV | 1.00 | 334.0 | 0.002397 | 0.0000072 | No
20/05/2024 | 14:42 | ST21 | SHORT RURAL | Asset failure | LV | 2.00 | 235.0 | 0.003307 | 0.0000141 | No
20/05/2024 | 14:48 | SM216E | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
20/05/2024 | 15:01 | HH177C | URBAN | Asset failure | LV | 1.00 | 519.0 | 0.000800 | 0.0000015 | No
20/05/2024 | 15:37 | SA32 | URBAN | Asset failure | LV | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
20/05/2024 | 16:18 | LX21 | SHORT RURAL | Asset failure | LV | 1.00 | 187.0 | 0.001316 | 0.0000070 | No
20/05/2024 | 16:31 | MV13 | SHORT RURAL | Third Party | Vehicle impact | 51.00 | 364.0 | 0.130607 | 0.0003588 | No
20/05/2024 | 18:32 | SM374C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 642.00 | 44.0 | 0.043551 | 0.0009898 | No
20/05/2024 | 18:44 | NL544A | URBAN | Asset failure | LV | 26.33 | 179.0 | 0.007267 | 0.0000406 | No
20/05/2024 | 19:00 | NL511B | URBAN | Asset failure | LV | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
20/05/2024 | 19:31 | GU42 | LONG RURAL | Asset failure | LV | 1.00 | 202.0 | 0.001450 | 0.0000072 | No
20/05/2024 | 19:44 | GA20 | LONG RURAL | Asset failure | LV | 3.00 | 350.0 | 0.007535 | 0.0000215 | No
20/05/2024 | 20:35 | SA14 | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
20/05/2024 | 21:12 | HH341E | URBAN | Asset failure | LV | 1.00 | 353.0 | 0.000544 | 0.0000015 | No
20/05/2024 | 21:19 | HH121C | URBAN | Asset failure | LV | 15.00 | 272.0 | 0.006290 | 0.0000231 | No
20/05/2024 | 21:49 | BM21 | SHORT RURAL | Overloads |  | 1.00 | 273.0 | 0.001921 | 0.0000070 | No
21/05/2024 | 00:44 | NL21 | URBAN | Unknown | Unknown | 21.00 | 227.0 | 0.007350 | 0.0000324 | No
21/05/2024 | 02:23 | LM43 | LONG RURAL | Unknown | Unknown | 88.00 | 642.0 | 0.405434 | 0.0006315 | No
21/05/2024 | 07:04 | LC01 | LONG RURAL | Planned |  | 127.00 | 347.0 | 0.316254 | 0.0009114 | No
21/05/2024 | 07:04 | LC01 | SHORT RURAL | Planned |  | 237.00 | 347.0 | 0.578592 | 0.0016674 | No
21/05/2024 | 08:08 | AP125A | URBAN | Asset failure | LV | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
21/05/2024 | 08:31 | BM42 | SHORT RURAL | Planned |  | 109.00 | 233.0 | 0.178680 | 0.0007669 | No
21/05/2024 | 08:44 | VH45 | SHORT RURAL | Planned |  | 47.00 | 415.1 | 0.137262 | 0.0003307 | No
21/05/2024 | 08:47 | CD03 | SHORT RURAL | Planned |  | 312.00 | 417.0 | 0.915416 | 0.0021951 | No
21/05/2024 | 09:00 | CV33 | LONG RURAL | Planned |  | 8.00 | 231.0 | 0.013262 | 0.0000574 | No
21/05/2024 | 09:23 | HH429C | URBAN | Planned |  | 120.00 | 338.5 | 0.062623 | 0.0001850 | No
21/05/2024 | 09:31 | EL11 | URBAN | Planned |  | 418.00 | 29.6 | 0.019105 | 0.0006445 | No
21/05/2024 | 09:33 | NU19 | LONG RURAL | Planned |  | 107.00 | 263.9 | 0.202674 | 0.0007679 | No
21/05/2024 | 09:34 | VH16 | SHORT RURAL | Asset failure | LV | 1.00 | 302.0 | 0.002125 | 0.0000070 | No
21/05/2024 | 09:45 | HH121H | URBAN | Overloads |  | 7.00 | 104.0 | 0.001122 | 0.0000108 | No
21/05/2024 | 09:54 | MV62 | SHORT RURAL | Planned |  | 149.00 | 378.3 | 0.396584 | 0.0010483 | No
21/05/2024 | 13:11 | SM216E | URBAN | Asset failure | LV | 54.00 | 82.0 | 0.006827 | 0.0000833 | No
21/05/2024 | 13:44 | CV04 | SHORT RURAL | Third Party | Vehicle impact | 4.00 | 147.3 | 0.004144 | 0.0000281 | No
21/05/2024 | 13:48 | CV04 | SHORT RURAL | Unknown | Unknown | 11.00 | 27.5 | 0.002132 | 0.0000774 | No
21/05/2024 | 16:19 | ST21 | SHORT RURAL | Third Party | Vehicle impact | 2.00 | 91.0 | 0.001280 | 0.0000141 | No
21/05/2024 | 18:01 | MB13 | SHORT RURAL | Asset failure | LV | 1.00 | 228.0 | 0.001604 | 0.0000070 | No
21/05/2024 | 18:27 | GU42 | LONG RURAL | Asset failure | LV | 1.00 | 1,023.0 | 0.007341 | 0.0000072 | No
21/05/2024 | 20:48 | HH107A | URBAN | Planned |  | 68.00 | 360.0 | 0.037742 | 0.0001048 | No
21/05/2024 | 20:52 | KI41 | LONG RURAL | Third Party | Vehicle impact | 310.00 | 146.1 | 0.325030 | 0.0022247 | No
21/05/2024 | 22:28 | LM52 | LONG RURAL | Asset failure | HV | 2.00 | 60.0 | 0.000861 | 0.0000144 | No
21/05/2024 | 23:18 | EL01Q | URBAN | Overloads |  | 1.00 | 63.0 | 0.000097 | 0.0000015 | No
22/05/2024 | 00:05 | AP226E | URBAN | Overloads |  | 1.00 | 42.0 | 0.000065 | 0.0000015 | No
22/05/2024 | 01:08 | HH121C | URBAN | Asset failure | LV | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
22/05/2024 | 03:04 | AP214B | URBAN | Asset failure | LV | 24.33 | 122.0 | 0.004577 | 0.0000375 | No
22/05/2024 | 05:17 | HH496C | URBAN | Asset failure | HV | 914.00 | 167.8 | 0.236470 | 0.0014092 | No
22/05/2024 | 07:26 | HH522B | URBAN | Overloads |  | 14.00 | 35.9 | 0.000776 | 0.0000216 | No
22/05/2024 | 08:17 | GA800A | SHORT RURAL | Planned |  | 22.00 | 336.0 | 0.052006 | 0.0001548 | No
22/05/2024 | 08:30 | CN24 | LONG RURAL | Overloads |  | 6.67 | 901.0 | 0.043106 | 0.0000478 | No
22/05/2024 | 08:38 | EL01A | URBAN | Overloads |  | 1.00 | 228.0 | 0.000352 | 0.0000015 | No
22/05/2024 | 08:44 | R08 | LONG RURAL | Other |  | 1.00 | 515.0 | 0.003696 | 0.0000072 | No
22/05/2024 | 08:50 | YK03 | LONG RURAL | Planned |  | 280.00 | 248.0 | 0.498324 | 0.0020094 | No
22/05/2024 | 08:50 | SG09 | SHORT RURAL | Planned |  | 31.00 | 285.9 | 0.062363 | 0.0002181 | No
22/05/2024 | 08:57 | AP372B | URBAN | Asset failure | LV | 44.00 | 570.0 | 0.038667 | 0.0000678 | No
22/05/2024 | 09:21 | GU13 | LONG RURAL | Planned |  | 60.00 | 327.0 | 0.140800 | 0.0004306 | No
22/05/2024 | 09:33 | ME427F | URBAN | Third Party | Unauthorised access | 1.00 | 62.0 | 0.000096 | 0.0000015 | No
22/05/2024 | 09:41 | MI03 | LONG RURAL | Planned |  | 1.00 | 67.0 | 0.000481 | 0.0000072 | No
22/05/2024 | 09:50 | SB22 | LONG RURAL | Planned |  | 45.00 | 346.0 | 0.111735 | 0.0003229 | No
22/05/2024 | 09:55 | CV25 | LONG RURAL | Planned |  | 1.00 | 12,876.0 | 0.092402 | 0.0000072 | No
22/05/2024 | 10:17 | VH15 | SHORT RURAL | Asset failure | LV | 63.00 | 20.0 | 0.008865 | 0.0004432 | No
22/05/2024 | 10:26 | PL11 | LONG RURAL | Planned |  | 5.00 | 94.0 | 0.003373 | 0.0000359 | No
22/05/2024 | 10:27 | ST15 | SHORT RURAL | Other |  | 2.00 | 229.0 | 0.003222 | 0.0000141 | No
22/05/2024 | 10:40 | EL17 | URBAN | Planned |  | 6.00 | 204.0 | 0.001887 | 0.0000093 | No
22/05/2024 | 10:49 | HH522B | URBAN | Asset failure | LV | 1.00 | 383.0 | 0.000590 | 0.0000015 | No
22/05/2024 | 11:11 | BM52 | URBAN | Asset failure | LV | 13.00 | 215.0 | 0.004309 | 0.0000200 | No
22/05/2024 | 11:46 | NL111P | URBAN | Asset failure | LV | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
22/05/2024 | 12:21 | WHY07 | URBAN | Overloads |  | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
22/05/2024 | 12:24 | PA06 | LONG RURAL | Asset failure | HV | 49.00 | 169.5 | 0.059614 | 0.0003516 | No
22/05/2024 | 12:24 | HH432D | URBAN | Overloads |  | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
22/05/2024 | 12:38 | MB123 | LONG RURAL | Third Party | Vehicle impact | 168.00 | 95.1 | 0.114663 | 0.0012056 | No
22/05/2024 | 14:22 | HH145E | URBAN | Asset failure | LV | 9.00 | 119.0 | 0.001651 | 0.0000139 | No
22/05/2024 | 14:40 | MG52 | URBAN | Weather |  | 13.00 | 84.0 | 0.001684 | 0.0000200 | No
22/05/2024 | 17:31 | SA744D | URBAN | Overloads |  | 1.00 | 362.0 | 0.000558 | 0.0000015 | No
22/05/2024 | 17:43 | AP529E | URBAN | Overloads |  | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
22/05/2024 | 17:48 | HH148A | URBAN | Unknown | Unknown | 19.33 | 60.0 | 0.001788 | 0.0000298 | No
22/05/2024 | 17:48 | EL13 | URBAN | Asset failure | LV | 1.00 | 91.0 | 0.000140 | 0.0000015 | No
22/05/2024 | 17:56 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 245.0 | 0.001758 | 0.0000072 | No
22/05/2024 | 18:53 | GA03 | LONG RURAL | Asset failure | HV | 1.00 | 343.0 | 0.002461 | 0.0000072 | No
22/05/2024 | 19:17 | ME231E | URBAN | Asset failure | LV | 24.00 | 105.0 | 0.003885 | 0.0000370 | No
22/05/2024 | 21:24 | PP08 | LONG RURAL | Weather |  | 974.00 | 147.0 | 1.027493 | 0.0069897 | No
23/05/2024 | 07:07 | CBD412H | URBAN | Planned |  | 2.00 | 245.0 | 0.000755 | 0.0000031 | No
23/05/2024 | 07:57 | R21 | LONG RURAL | Asset failure | LV | 1.00 | 429.0 | 0.003079 | 0.0000072 | No
23/05/2024 | 08:01 | MI31 | LONG RURAL | Planned |  | 40.00 | 462.0 | 0.132619 | 0.0002871 | No
23/05/2024 | 08:27 | AP139B | URBAN | Asset failure | LV | 1.00 | 484.0 | 0.000746 | 0.0000015 | No
23/05/2024 | 08:51 | NU21 | LONG RURAL | Planned |  | 213.00 | 283.8 | 0.433816 | 0.0015286 | No
23/05/2024 | 08:54 | LX21 | SHORT RURAL | Planned |  | 5.00 | 366.0 | 0.012875 | 0.0000352 | No
23/05/2024 | 09:00 | SD58101 | LONG RURAL | Planned |  | 3.00 | 155.0 | 0.003337 | 0.0000215 | No
23/05/2024 | 09:03 | W18 | LONG RURAL | Asset failure | HV | 5.00 | 450.0 | 0.016147 | 0.0000359 | No
23/05/2024 | 09:07 | YK25 | LONG RURAL | Planned |  | 392.00 | 3.0 | 0.008439 | 0.0028131 | No
23/05/2024 | 09:08 | NL115B | URBAN | Planned |  | 75.00 | 204.4 | 0.023635 | 0.0001156 | No
23/05/2024 | 09:24 | PL28 | LONG RURAL | Planned |  | 94.00 | 280.0 | 0.188881 | 0.0006746 | No
23/05/2024 | 09:28 | SD52300 | LONG RURAL | Unknown | Unknown | 1.00 | 273.0 | 0.001959 | 0.0000072 | No
23/05/2024 | 09:32 | MI16 | LONG RURAL | Planned |  | 27.00 | 400.2 | 0.077547 | 0.0001938 | No
23/05/2024 | 09:33 | MV41 | SHORT RURAL | Planned |  | 39.00 | 307.2 | 0.084285 | 0.0002744 | No
23/05/2024 | 09:33 | NU13 | LONG RURAL | Planned |  | 2.00 | 55.0 | 0.000789 | 0.0000144 | No
23/05/2024 | 09:46 | R18 | LONG RURAL | Planned |  | 1.00 | 135.0 | 0.000969 | 0.0000072 | No
23/05/2024 | 09:52 | SA14 | URBAN | Unknown | Unknown | 2.00 | 136.0 | 0.000419 | 0.0000031 | No
23/05/2024 | 09:56 | SA14 | URBAN | Asset failure | LV | 1.00 | 182.0 | 0.000281 | 0.0000015 | No
23/05/2024 | 10:08 | MG44 | URBAN | Overloads |  | 1.00 | 220.0 | 0.000339 | 0.0000015 | No
23/05/2024 | 10:46 | CV32 | LONG RURAL | Planned |  | 2.00 | 159.0 | 0.002282 | 0.0000144 | No
23/05/2024 | 10:50 | G36 | LONG RURAL | Planned |  | 68.00 | 218.0 | 0.106382 | 0.0004880 | No
23/05/2024 | 11:00 | BT18 | LONG RURAL | Planned |  | 1.00 | 212.0 | 0.001521 | 0.0000072 | No
23/05/2024 | 11:23 | PL07 | URBAN | Unknown | Unknown | 1.00 | 180.0 | 0.000278 | 0.0000015 | No
23/05/2024 | 12:39 | AP226B | URBAN | Asset failure | LV | 34.00 | 115.6 | 0.006059 | 0.0000524 | No
23/05/2024 | 13:10 | HH102B | URBAN | Asset failure | LV | 1.00 | 333.0 | 0.000513 | 0.0000015 | No
23/05/2024 | 13:48 | HH145D | URBAN | Third Party | Vehicle impact | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
23/05/2024 | 13:52 | MB02 | LONG RURAL | Planned |  | 2.00 | 63.0 | 0.000904 | 0.0000144 | No
23/05/2024 | 14:04 | SM350H | URBAN | Network business | Switching and protection error | 7.00 | 252.0 | 0.002720 | 0.0000108 | No
23/05/2024 | 14:14 | SG02 | SHORT RURAL | Asset failure | LV | 6.00 | 89.0 | 0.003757 | 0.0000422 | No
23/05/2024 | 14:40 | MV15 | SHORT RURAL | Animal | Animal impact | 1,169.00 | 69.0 | 0.567490 | 0.0082245 | No
23/05/2024 | 15:11 | AP146C | URBAN | Asset failure | LV | 1.00 | 483.0 | 0.000745 | 0.0000015 | No
23/05/2024 | 15:15 | BT29 | LONG RURAL | Asset failure | HV | 1.00 | 94.0 | 0.000675 | 0.0000072 | No
23/05/2024 | 16:18 | HH177C | URBAN | Asset failure | LV | 1.00 | 195.0 | 0.000301 | 0.0000015 | No
23/05/2024 | 17:29 | SM349H | URBAN | Overloads |  | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
23/05/2024 | 18:05 | AP227B | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
23/05/2024 | 18:26 | WK61 | SHORT RURAL | Asset failure | LV | 1.00 | 75.0 | 0.000528 | 0.0000070 | No
23/05/2024 | 18:34 | SM216A | URBAN | Asset failure | LV | 1.00 | 240.0 | 0.000370 | 0.0000015 | No
23/05/2024 | 18:43 | HH102A | URBAN | Asset failure | LV | 1.00 | 343.0 | 0.000529 | 0.0000015 | No
23/05/2024 | 18:45 | MV33 | SHORT RURAL | Unknown | Unknown | 41.00 | 193.0 | 0.055672 | 0.0002885 | No
23/05/2024 | 18:46 | NL210E | URBAN | Animal | Animal impact | 26.00 | 113.0 | 0.004530 | 0.0000401 | No
23/05/2024 | 19:09 | M21 | LONG RURAL | Third Party | Vehicle impact | 7.00 | 271.6 | 0.013642 | 0.0000502 | No
23/05/2024 | 21:06 | HH432C | URBAN | Planned |  | 64.00 | 350.0 | 0.034535 | 0.0000987 | No
23/05/2024 | 21:15 | HH107A | URBAN | Third Party | Vehicle impact | 579.00 | 133.6 | 0.119233 | 0.0008927 | No
23/05/2024 | 21:52 | CBD412Q | CBD | Planned |  | 21.00 | 31.1 | 0.094488 | 0.0030340 | No
23/05/2024 | 22:22 | SM411D | URBAN | Planned |  | 14.00 | 262.0 | 0.005655 | 0.0000216 | No
23/05/2024 | 22:27 | AP355H | URBAN | Unknown | Unknown | 2.00 | 216.0 | 0.000666 | 0.0000031 | No
23/05/2024 | 23:25 | HH130F | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
23/05/2024 | 23:41 | CN21 | LONG RURAL | Asset failure | HV | 1.00 | 753.0 | 0.005404 | 0.0000072 | No
24/05/2024 | 00:02 | HH409F | URBAN | Asset failure | LV | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
24/05/2024 | 02:45 | HH148A | URBAN | Overloads |  | 1.00 | 477.0 | 0.000735 | 0.0000015 | No
24/05/2024 | 07:00 | BT02 | LONG RURAL | Asset failure | HV | 11.33 | 230.0 | 0.018706 | 0.0000813 | No
24/05/2024 | 07:34 | HH341J | URBAN | Asset failure | LV | 3.00 | 275.0 | 0.001272 | 0.0000046 | No
24/05/2024 | 07:49 | MI08 | LONG RURAL | Planned |  | 136.00 | 432.9 | 0.422485 | 0.0009760 | No
24/05/2024 | 08:32 | W28 | LONG RURAL | Planned |  | 81.00 | 398.0 | 0.231351 | 0.0005813 | No
24/05/2024 | 08:39 | HH102A | URBAN | Planned |  | 346.00 | 406.0 | 0.216579 | 0.0005334 | No
24/05/2024 | 08:39 | HH102A | URBAN | Asset failure | LV | 30.00 | 1,046.0 | 0.048380 | 0.0000463 | No
24/05/2024 | 08:45 | PP03 | URBAN | Planned |  | 15.00 | 305.0 | 0.007054 | 0.0000231 | No
24/05/2024 | 08:49 | ST12 | SHORT RURAL | Asset failure | LV | 6.00 | 415.0 | 0.017518 | 0.0000422 | No
24/05/2024 | 08:51 | HH145B | URBAN | Planned |  | 239.00 | 294.0 | 0.108333 | 0.0003685 | No
24/05/2024 | 09:00 | MG28 | LONG RURAL | Planned |  | 196.00 | 156.0 | 0.219423 | 0.0014066 | No
24/05/2024 | 09:01 | LM21 | LONG RURAL | Asset failure | LV | 1.00 | 358.0 | 0.002569 | 0.0000072 | No
24/05/2024 | 09:08 | CV18 | SHORT RURAL | Planned |  | 1.00 | 18.0 | 0.000127 | 0.0000070 | No
24/05/2024 | 09:19 | SD47200 | URBAN | Planned |  | 2.00 | 699.0 | 0.002155 | 0.0000031 | No
24/05/2024 | 09:36 | AP149F | URBAN | Planned |  | 60.00 | 304.0 | 0.028122 | 0.0000925 | No
24/05/2024 | 10:00 | CBD353C | CBD | Asset failure | LV | 2.00 | 321.0 | 0.092754 | 0.0002890 | No
24/05/2024 | 10:07 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 469.0 | 0.003300 | 0.0000070 | No
24/05/2024 | 10:26 | PP04 | SHORT RURAL | Planned |  | 43.00 | 113.0 | 0.034185 | 0.0003025 | No
24/05/2024 | 10:59 | EL18 | URBAN | Planned |  | 17.00 | 161.0 | 0.004220 | 0.0000262 | No
24/05/2024 | 12:07 | CL13 | LONG RURAL | Planned |  | 2.00 | 35.0 | 0.000502 | 0.0000144 | No
24/05/2024 | 12:25 | EL15 | URBAN | Overloads |  | 1.00 | 361.0 | 0.000557 | 0.0000015 | No
24/05/2024 | 12:31 | HH177D | URBAN | Overloads |  | 1.00 | 894.0 | 0.001378 | 0.0000015 | No
24/05/2024 | 14:54 | SA14 | URBAN | Unknown | Unknown | 15.00 | 258.0 | 0.005967 | 0.0000231 | No
24/05/2024 | 16:34 | EL14 | URBAN | Overloads |  | 1.00 | 184.0 | 0.000284 | 0.0000015 | No
24/05/2024 | 17:58 | SA33 | URBAN | Overloads |  | 1.00 | 517.0 | 0.000797 | 0.0000015 | No
24/05/2024 | 19:15 | AP355C | URBAN | Planned |  | 47.00 | 567.0 | 0.041086 | 0.0000725 | No
24/05/2024 | 20:20 | AP355C | URBAN | Third Party | Vehicle impact | 61.00 | 119.5 | 0.011236 | 0.0000940 | No
24/05/2024 | 21:04 | HH341D | URBAN | Asset failure | LV | 1.00 | 568.0 | 0.000876 | 0.0000015 | No
25/05/2024 | 07:02 | ME200E | URBAN | Overloads |  | 11.00 | 227.0 | 0.003850 | 0.0000170 | No
25/05/2024 | 08:46 | MI08 | LONG RURAL | Planned |  | 11.00 | 412.0 | 0.032523 | 0.0000789 | No
25/05/2024 | 08:48 | MI08 | LONG RURAL | Planned |  | 32.00 | 13,226.8 | 3.037425 | 0.0002296 | No
25/05/2024 | 09:43 | SM350F | URBAN | Unknown | Unknown | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
25/05/2024 | 10:42 | NA15 | LONG RURAL | Planned |  | 668.00 | 269.0 | 1.289529 | 0.0047938 | No
25/05/2024 | 11:57 | CL09 | LONG RURAL | Asset failure | HV | 1.00 | 24.0 | 0.000172 | 0.0000072 | No
25/05/2024 | 11:59 | NL111P | URBAN | Asset failure | LV | 116.00 | 72.0 | 0.012877 | 0.0001788 | No
25/05/2024 | 14:50 | WK41 | SHORT RURAL | Asset failure | LV | 1.00 | 305.0 | 0.002146 | 0.0000070 | No
25/05/2024 | 14:52 | HH145B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 65.00 | 75.0 | 0.007516 | 0.0001002 | No
25/05/2024 | 17:18 | MI14 | LONG RURAL | Asset failure | LV | 22.67 | 280.0 | 0.045546 | 0.0001627 | No
25/05/2024 | 18:10 | NL234C | URBAN | Asset failure | LV | 1.00 | 247.0 | 0.000381 | 0.0000015 | No
25/05/2024 | 20:48 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 310.0 | 0.002181 | 0.0000070 | No
25/05/2024 | 22:25 | AP529E | URBAN | Asset failure | LV | 18.00 | 82.0 | 0.002276 | 0.0000278 | No
25/05/2024 | 22:36 | EL01R | URBAN | Overloads |  | 1.00 | 284.0 | 0.000438 | 0.0000015 | No
25/05/2024 | 22:44 | SM374B | URBAN | Overloads |  | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
26/05/2024 | 07:28 | PA15 | LONG RURAL | Planned |  | 1.00 | 219.0 | 0.001572 | 0.0000072 | No
26/05/2024 | 07:38 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 225.0 | 0.001583 | 0.0000070 | No
26/05/2024 | 08:19 | BM14 | URBAN | Planned |  | 9.00 | 404.0 | 0.005606 | 0.0000139 | No
26/05/2024 | 08:34 | NU02 | LONG RURAL | Asset failure | LV | 1.00 | 211.0 | 0.001514 | 0.0000072 | No
26/05/2024 | 08:35 | HH341D | URBAN | Planned |  | 212.00 | 429.0 | 0.140219 | 0.0003269 | No
26/05/2024 | 08:45 | AP365F | URBAN | Asset failure | LV | 24.33 | 137.0 | 0.005140 | 0.0000375 | No
26/05/2024 | 09:20 | EL13 | URBAN | Asset failure | LV | 1.00 | 639.0 | 0.000985 | 0.0000015 | No
26/05/2024 | 09:25 | MG06 | SHORT RURAL | Planned |  | 371.00 | 320.0 | 0.835253 | 0.0026102 | No
26/05/2024 | 09:57 | HH121E | URBAN | Planned |  | 1,260.00 | 42.5 | 0.082507 | 0.0019426 | No
26/05/2024 | 10:22 | PA15 | LONG RURAL | Asset failure | HV | 1.00 | 22.0 | 0.000158 | 0.0000072 | No
26/05/2024 | 11:49 | HH386B | URBAN | Unknown | Unknown | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
26/05/2024 | 12:11 | HH121D | URBAN | Asset failure | LV | 28.00 | 1,004.0 | 0.043342 | 0.0000432 | No
26/05/2024 | 12:57 | NU20 | LONG RURAL | Asset failure | LV | 2.00 | 104.0 | 0.001493 | 0.0000144 | No
26/05/2024 | 13:19 | SG05 | SHORT RURAL | Third Party | Fire | 6.00 | 371.0 | 0.015661 | 0.0000422 | No
26/05/2024 | 15:32 | AP425B | URBAN | Asset failure | LV | 62.00 | 139.0 | 0.013287 | 0.0000956 | No
26/05/2024 | 15:38 | SG03 | SHORT RURAL | Asset failure | LV | 18.00 | 164.0 | 0.020769 | 0.0001266 | No
26/05/2024 | 18:36 | SM349D | URBAN | Overloads |  | 1.00 | 288.0 | 0.000444 | 0.0000015 | No
26/05/2024 | 19:12 | EL02 | URBAN | Overloads |  | 14.00 | 12.0 | 0.000259 | 0.0000216 | No
26/05/2024 | 19:14 | SA744D | URBAN | Asset failure | LV | 71.00 | 319.2 | 0.034942 | 0.0001095 | No
26/05/2024 | 21:36 | NL234A | URBAN | Asset failure | LV | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
27/05/2024 | 00:47 | GU34 | LONG RURAL | Unknown | Unknown | 93.00 | 254.9 | 0.170144 | 0.0006674 | No
27/05/2024 | 03:29 | AP344E | URBAN | Asset failure | LV | 1.00 | 152.0 | 0.000234 | 0.0000015 | No
27/05/2024 | 05:00 | NL115E | URBAN | Asset failure | LV | 1.00 | 440.0 | 0.000678 | 0.0000015 | No
27/05/2024 | 07:43 | NU04 | SHORT RURAL | Third Party | Vehicle impact | 12.00 | 54.0 | 0.004559 | 0.0000844 | No
27/05/2024 | 08:15 | M43 | LONG RURAL | Unknown | Unknown | 35.00 | 208.0 | 0.052244 | 0.0002512 | No
27/05/2024 | 08:42 | KA24 | LONG RURAL | Planned |  | 5.00 | 43.0 | 0.001543 | 0.0000359 | No
27/05/2024 | 08:43 | MG10 | LONG RURAL | Planned |  | 16.00 | 161.3 | 0.018522 | 0.0001148 | No
27/05/2024 | 08:58 | SG13 | SHORT RURAL | Planned |  | 8.00 | 65.0 | 0.003658 | 0.0000563 | No
27/05/2024 | 09:11 | AP372F | URBAN | Asset failure | LV | 52.00 | 115.0 | 0.009220 | 0.0000802 | No
27/05/2024 | 09:21 | MG46 | SHORT RURAL | Planned |  | 14.00 | 198.0 | 0.019502 | 0.0000985 | No
27/05/2024 | 09:43 | AP529A | URBAN | Asset failure | LV | 1.00 | 344.0 | 0.000530 | 0.0000015 | No
27/05/2024 | 09:55 | MB23 | SHORT RURAL | Unknown | Unknown | 26.00 | 367.9 | 0.067302 | 0.0001829 | No
27/05/2024 | 10:02 | BT08 | LONG RURAL | Planned |  | 5.00 | 75.0 | 0.002691 | 0.0000359 | No
27/05/2024 | 10:04 | HH429C | URBAN | Planned |  | 229.00 | 235.0 | 0.082969 | 0.0003531 | No
27/05/2024 | 10:20 | CM25 | LONG RURAL | Planned |  | 4.00 | 280.0 | 0.008037 | 0.0000287 | No
27/05/2024 | 11:09 | HH429B | URBAN | Planned |  | 6.00 | 220.0 | 0.002035 | 0.0000093 | No
27/05/2024 | 11:45 | LC01 | SHORT RURAL | Asset failure | HV | 1.00 | 56.0 | 0.000394 | 0.0000070 | No
27/05/2024 | 12:26 | M21 | LONG RURAL | Unknown | Unknown | 18.00 | 531.0 | 0.068591 | 0.0001292 | No
27/05/2024 | 12:36 | EL01R | URBAN | Asset failure | LV | 1.00 | 1,566.0 | 0.002414 | 0.0000015 | No
27/05/2024 | 13:06 | NU22 | LONG RURAL | Third Party | Dig-in | 3.00 | 103.0 | 0.002217 | 0.0000215 | No
27/05/2024 | 13:57 | MG48 | LONG RURAL | Asset failure | LV | 7.00 | 55.7 | 0.002799 | 0.0000502 | No
27/05/2024 | 14:25 | M81 | LONG RURAL | Asset failure | LV | 1.00 | 1,883.0 | 0.013513 | 0.0000072 | No
27/05/2024 | 15:03 | MI14 | LONG RURAL | Asset failure | HV | 737.00 | 97.0 | 0.513029 | 0.0052890 | No
27/05/2024 | 15:41 | AP226E | URBAN | Third Party | Other | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
27/05/2024 | 16:39 | G03 | LONG RURAL | Asset failure | LV | 1.00 | 383.0 | 0.002749 | 0.0000072 | No
27/05/2024 | 16:57 | HH341E | URBAN | Asset failure | LV | 1.00 | 239.0 | 0.000368 | 0.0000015 | No
27/05/2024 | 17:35 | EL18 | URBAN | Asset failure | LV | 13.00 | 469.0 | 0.009400 | 0.0000200 | No
27/05/2024 | 17:45 | AP372F | URBAN | Asset failure | LV | 17.33 | 111.0 | 0.002966 | 0.0000267 | No
27/05/2024 | 18:46 | HH429B | URBAN | Overloads |  | 1.00 | 194.0 | 0.000299 | 0.0000015 | No
27/05/2024 | 20:09 | LM56 | LONG RURAL | Unknown | Unknown | 54.00 | 253.0 | 0.098043 | 0.0003875 | No
27/05/2024 | 20:52 | AP214C | URBAN | Overloads |  | 8.67 | 154.0 | 0.002058 | 0.0000134 | No
27/05/2024 | 21:32 | HH341B | URBAN | Planned |  | 36.00 | 350.0 | 0.019426 | 0.0000555 | No
27/05/2024 | 21:34 | SA42 | URBAN | Asset failure | LV | 12.00 | 97.0 | 0.001795 | 0.0000185 | No
28/05/2024 | 00:45 | CBD412S | URBAN | Planned |  | 3.00 | 202.3 | 0.000936 | 0.0000046 | No
28/05/2024 | 01:12 | VH16 | SHORT RURAL | Asset failure | LV | 1.00 | 145.0 | 0.001020 | 0.0000070 | No
28/05/2024 | 02:42 | HH130E | URBAN | Asset failure | LV | 1.00 | 190.0 | 0.000293 | 0.0000015 | No
28/05/2024 | 07:36 | ST42 | LONG RURAL | Unknown | Unknown | 441.33 | 14.4 | 0.045596 | 0.0031672 | No
28/05/2024 | 08:04 | MV12 | SHORT RURAL | Asset failure | LV | 1.00 | 235.0 | 0.001653 | 0.0000070 | No
28/05/2024 | 08:12 | MV12 | SHORT RURAL | Asset failure | LV | 3.00 | 225.0 | 0.004749 | 0.0000211 | No
28/05/2024 | 08:46 | MV12 | SHORT RURAL | Asset failure | LV | 1.00 | 190.0 | 0.001337 | 0.0000070 | No
28/05/2024 | 08:49 | MV12 | SHORT RURAL | Asset failure | LV | 6.00 | 182.0 | 0.007683 | 0.0000422 | No
28/05/2024 | 09:04 | MV52 | SHORT RURAL | Planned |  | 12.00 | 314.4 | 0.026545 | 0.0000844 | No
28/05/2024 | 09:12 | MV12 | SHORT RURAL | Asset failure | LV | 1.00 | 162.0 | 0.001140 | 0.0000070 | No
28/05/2024 | 09:21 | CM09 | LONG RURAL | Planned |  | 10.00 | 306.0 | 0.021960 | 0.0000718 | No
28/05/2024 | 09:25 | PP04 | SHORT RURAL | Planned |  | 35.00 | 176.0 | 0.043339 | 0.0002462 | No
28/05/2024 | 09:26 | SM137B | URBAN | Overloads |  | 1.00 | 498.0 | 0.000768 | 0.0000015 | No
28/05/2024 | 09:34 | CD17 | LONG RURAL | Planned |  | 13.00 | 144.0 | 0.013434 | 0.0000933 | No
28/05/2024 | 09:41 | MI02 | SHORT RURAL | Asset failure | HV | 1.00 | 85.0 | 0.000598 | 0.0000070 | No
28/05/2024 | 10:04 | MV12 | SHORT RURAL | Asset failure | LV | 1.00 | 105.0 | 0.000739 | 0.0000070 | No
28/05/2024 | 10:10 | NL234C | URBAN | Asset failure | LV | 9.00 | 149.0 | 0.002067 | 0.0000139 | No
28/05/2024 | 10:11 | CV22 | LONG RURAL | Planned |  | 2.00 | 174.0 | 0.002497 | 0.0000144 | No
28/05/2024 | 10:12 | EL20 | URBAN | Asset failure | LV | 1.00 | 328.0 | 0.000506 | 0.0000015 | No
28/05/2024 | 10:44 | MV12 | SHORT RURAL | Asset failure | LV | 1.00 | 59.0 | 0.000415 | 0.0000070 | No
28/05/2024 | 11:18 | EL01R | URBAN | Asset failure | LV | 15.00 | 112.0 | 0.002590 | 0.0000231 | No
28/05/2024 | 11:21 | SM137B | URBAN | Asset failure | LV | 4.00 | 141.0 | 0.000870 | 0.0000062 | No
28/05/2024 | 12:04 | MB22 | SHORT RURAL | Asset failure | LV | 12.33 | 336.0 | 0.029155 | 0.0000868 | No
28/05/2024 | 12:07 | SM410D | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
28/05/2024 | 12:13 | LM56 | LONG RURAL | Asset failure | HV | 54.00 | 266.0 | 0.103081 | 0.0003875 | No
28/05/2024 | 12:59 | PA06 | LONG RURAL | Asset failure | LV | 14.00 | 104.0 | 0.010449 | 0.0001005 | No
28/05/2024 | 13:11 | CBD103F | URBAN | Overloads |  | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
28/05/2024 | 13:38 | BM13 | SHORT RURAL | Asset failure | LV | 9.00 | 106.0 | 0.006712 | 0.0000633 | No
28/05/2024 | 14:54 | MT01 | LONG RURAL | Unknown | Unknown | 2.00 | 114.0 | 0.001636 | 0.0000144 | No
28/05/2024 | 16:22 | MG46 | SHORT RURAL | Asset failure | LV | 1.00 | 141.0 | 0.000992 | 0.0000070 | No
28/05/2024 | 21:47 | CBD353P | CBD | Planned |  | 18.00 | 35.4 | 0.092177 | 0.0026006 | No
28/05/2024 | 22:02 | SM172E | URBAN | Network business | Switching and protection error | 5.00 | 167.0 | 0.001287 | 0.0000077 | No
28/05/2024 | 22:16 | HH118B | URBAN | Planned |  | 120.00 | 495.8 | 0.091720 | 0.0001850 | No
28/05/2024 | 22:34 | SA711C | URBAN | Asset failure | LV | 42.00 | 437.0 | 0.028297 | 0.0000648 | No
28/05/2024 | 22:41 | SM350B | URBAN | Planned |  | 60.00 | 327.0 | 0.030249 | 0.0000925 | No
29/05/2024 | 00:07 | EL17 | URBAN | Unknown | Unknown | 12.00 | 204.0 | 0.003774 | 0.0000185 | No
29/05/2024 | 02:47 | SG02 | SHORT RURAL | Third Party | Fire | 2.00 | 689.0 | 0.009695 | 0.0000141 | No
29/05/2024 | 08:17 | PP18 | LONG RURAL | Planned |  | 32.00 | 66.0 | 0.015156 | 0.0002296 | No
29/05/2024 | 08:24 | BM44 | SHORT RURAL | Planned |  | 13.00 | 343.0 | 0.031371 | 0.0000915 | No
29/05/2024 | 08:49 | CV21 | LONG RURAL | Planned |  | 57.00 | 158.0 | 0.064630 | 0.0004091 | No
29/05/2024 | 08:56 | MI10 | LONG RURAL | Planned |  | 47.00 | 342.0 | 0.115352 | 0.0003373 | No
29/05/2024 | 09:08 | MI02 | SHORT RURAL | Planned |  | 15.00 | 123.0 | 0.012980 | 0.0001055 | No
29/05/2024 | 09:18 | EL01R | URBAN | Other |  | 4.00 | 69.0 | 0.000426 | 0.0000062 | No
29/05/2024 | 09:29 | VH45 | SHORT RURAL | Planned |  | 9.00 | 324.0 | 0.020515 | 0.0000633 | No
29/05/2024 | 09:29 | HH121C | URBAN | Asset failure | LV | 7.00 | 94.0 | 0.001014 | 0.0000108 | No
29/05/2024 | 09:32 | EL11 | URBAN | Planned |  | 416.00 | 340.0 | 0.218096 | 0.0006414 | No
29/05/2024 | 10:13 | CM15 | LONG RURAL | Planned |  | 59.00 | 240.0 | 0.101617 | 0.0004234 | No
29/05/2024 | 10:26 | SA744C | URBAN | Unknown | Unknown | 5.00 | 291.0 | 0.002243 | 0.0000077 | No
29/05/2024 | 11:44 | MT07 | LONG RURAL | Asset failure | LV | 1.00 | 78.0 | 0.000560 | 0.0000072 | No
29/05/2024 | 11:52 | SM216C | URBAN | Unknown | Unknown | 510.00 | 87.0 | 0.068408 | 0.0007863 | No
29/05/2024 | 12:04 | SM410D | URBAN | Unknown | Unknown | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
29/05/2024 | 13:46 | HH102B | URBAN | Asset failure | LV | 1.00 | 69.0 | 0.000106 | 0.0000015 | No
29/05/2024 | 13:52 | PA07 | LONG RURAL | Asset failure | LV | 8.00 | 58.0 | 0.003330 | 0.0000574 | No
29/05/2024 | 13:58 | SD33100 | LONG RURAL | Unknown | Unknown | 5.00 | 348.0 | 0.012487 | 0.0000359 | No
29/05/2024 | 14:31 | HH130F | URBAN | Asset failure | LV | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
29/05/2024 | 19:26 | ST42 | LONG RURAL | Unknown | Unknown | 2.00 | 148.0 | 0.002124 | 0.0000144 | No
29/05/2024 | 21:04 | MI32 | LONG RURAL | Asset failure | LV | 1.00 | 234.0 | 0.001679 | 0.0000072 | No
29/05/2024 | 21:29 | AP365D1 | URBAN | Planned |  | 4.00 | 369.3 | 0.002277 | 0.0000062 | No
29/05/2024 | 21:56 | CBD353Q | CBD | Planned |  | 1.00 | 215.0 | 0.031063 | 0.0001445 | No
29/05/2024 | 22:15 | MG36 | LONG RURAL | Planned |  | 15.00 | 39.0 | 0.004198 | 0.0001076 | No
29/05/2024 | 22:15 | SM349C | URBAN | Asset failure | LV | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
29/05/2024 | 22:55 | GA49 | LONG RURAL | Planned |  | 2.00 | 65.0 | 0.000933 | 0.0000144 | No
30/05/2024 | 02:01 | NL111D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 266.00 | 99.0 | 0.040601 | 0.0004101 | No
30/05/2024 | 02:01 | ME200G | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 109.0 | 0.000168 | 0.0000015 | No
30/05/2024 | 04:59 | SM216B | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 2,450.00 | 47.1 | 0.178025 | 0.0037773 | No
30/05/2024 | 05:06 | VH72 | SHORT RURAL | Asset failure | HV | 12.00 | 341.3 | 0.028810 | 0.0000844 | No
30/05/2024 | 06:53 | MV31 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 176.0 | 0.001238 | 0.0000070 | No
30/05/2024 | 07:12 | NL210E | URBAN | Asset failure | HV | 2,894.00 | 107.7 | 0.480736 | 0.0044618 | No
30/05/2024 | 07:12 | NU13 | LONG RURAL | Overloads |  | 1.00 | 125.0 | 0.000897 | 0.0000072 | No
30/05/2024 | 07:23 | PA04 | URBAN | Planned |  | 5.00 | 207.0 | 0.001596 | 0.0000077 | No
30/05/2024 | 07:41 | EL25 | URBAN | Asset failure | LV | 18.00 | 268.0 | 0.007437 | 0.0000278 | No
30/05/2024 | 07:48 | HH522B | URBAN | Animal | Animal impact | 134.00 | 78.8 | 0.016278 | 0.0002066 | No
30/05/2024 | 07:49 | NL115B | URBAN | Asset failure | LV | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
30/05/2024 | 08:38 | NA34 | LONG RURAL | Weather |  | 148.00 | 143.9 | 0.152885 | 0.0010621 | No
30/05/2024 | 08:44 | GA05 | SHORT RURAL | Third Party | Fire | 1.00 | 350.0 | 0.002462 | 0.0000070 | No
30/05/2024 | 08:47 | SM126C | URBAN | Weather |  | 1,040.00 | 210.0 | 0.336719 | 0.0016034 | No
30/05/2024 | 08:53 | SM126E | URBAN | Unknown | Unknown | 41.00 | 369.0 | 0.023325 | 0.0000632 | No
30/05/2024 | 09:06 | CN43 | LONG RURAL | Third Party | Other | 24.00 | 141.0 | 0.024285 | 0.0001722 | No
30/05/2024 | 09:07 | HH522B | URBAN | Planned |  | 261.00 | 232.4 | 0.093503 | 0.0004024 | No
30/05/2024 | 09:33 | AP125D | URBAN | Weather |  | 32.00 | 219.0 | 0.010805 | 0.0000493 | No
30/05/2024 | 09:42 | KI55 | LONG RURAL | Planned |  | 8.00 | 288.0 | 0.016534 | 0.0000574 | No
30/05/2024 | 10:01 | EL01B | URBAN | Overloads |  | 1.00 | 388.0 | 0.000598 | 0.0000015 | No
30/05/2024 | 10:03 | R18 | LONG RURAL | Asset failure | LV | 56.00 | 44.0 | 0.017682 | 0.0004019 | No
30/05/2024 | 10:14 | KA33 | LONG RURAL | Planned |  | 68.00 | 122.0 | 0.059535 | 0.0004880 | No
30/05/2024 | 10:22 | SM137B | URBAN | Network business | Switching and protection error | 1.00 | 52.0 | 0.000080 | 0.0000015 | No
30/05/2024 | 10:32 | SM349C | URBAN | Planned |  | 254.00 | 305.3 | 0.119538 | 0.0003916 | No
30/05/2024 | 10:34 | HH341D | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 5.00 | 109.0 | 0.000840 | 0.0000077 | No
30/05/2024 | 10:38 | MTB72 | LONG RURAL | Asset failure | HV | 173.00 | 221.1 | 0.274466 | 0.0012415 | No
30/05/2024 | 10:44 | WHY05 | URBAN | Weather |  | 511.00 | 115.6 | 0.091065 | 0.0007878 | No
30/05/2024 | 10:48 | HH386B | URBAN | Third Party | Other | 23.00 | 255.0 | 0.009042 | 0.0000355 | No
30/05/2024 | 11:01 | ST42 | LONG RURAL | Asset failure | LV | 1.00 | 179.0 | 0.001285 | 0.0000072 | No
30/05/2024 | 11:34 | LM12 | LONG RURAL | Asset failure | LV | 3.00 | 59.0 | 0.001270 | 0.0000215 | No
30/05/2024 | 11:35 | GA22 | SHORT RURAL | Unknown | Unknown | 1.00 | 696.0 | 0.004897 | 0.0000070 | No
30/05/2024 | 11:39 | AP149C | URBAN | Asset failure | LV | 21.00 | 81.0 | 0.002623 | 0.0000324 | No
30/05/2024 | 12:09 | PP09 | LONG RURAL | Weather |  | 955.00 | 48.6 | 0.332766 | 0.0068534 | No
30/05/2024 | 12:14 | WHY03 | URBAN | Asset failure | LV | 1.00 | 192.0 | 0.000296 | 0.0000015 | No
30/05/2024 | 12:19 | GU31 | LONG RURAL | Unknown | Unknown | 1.00 | 263.0 | 0.001887 | 0.0000072 | No
30/05/2024 | 12:44 | AP132D | URBAN | Asset failure | LV | 1.00 | 302.0 | 0.000466 | 0.0000015 | No
30/05/2024 | 13:09 | EL01L | URBAN | Other |  | 2.00 | 213.0 | 0.000657 | 0.0000031 | No
30/05/2024 | 13:40 | NL210E | URBAN | Asset failure | LV | 27.33 | 111.0 | 0.004678 | 0.0000421 | No
30/05/2024 | 13:55 | SA520E | URBAN | Overloads |  | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
30/05/2024 | 14:10 | HH177C | URBAN | Overloads |  | 1.00 | 470.0 | 0.000725 | 0.0000015 | No
30/05/2024 | 14:11 | R26 | LONG RURAL | Asset failure | LV | 10.00 | 60.5 | 0.004342 | 0.0000718 | No
30/05/2024 | 15:34 | HH177D | URBAN | Asset failure | LV | 25.00 | 393.0 | 0.015148 | 0.0000385 | No
30/05/2024 | 15:54 | HH130A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
30/05/2024 | 16:30 | PL07 | URBAN | Asset failure | HV | 6.00 | 154.0 | 0.001425 | 0.0000093 | No
30/05/2024 | 16:39 | HH177A | URBAN | Vegetation | Grow-in - NSP responsibility | 23.00 | 35.0 | 0.001241 | 0.0000355 | No
30/05/2024 | 16:55 | HH428D | URBAN | Overloads |  | 1.00 | 284.0 | 0.000438 | 0.0000015 | No
30/05/2024 | 17:18 | EL25 | URBAN | Overloads |  | 1.00 | 178.0 | 0.000274 | 0.0000015 | No
30/05/2024 | 17:41 | AP355F | URBAN | Overloads |  | 1.00 | 312.0 | 0.000481 | 0.0000015 | No
30/05/2024 | 17:46 | SA32 | URBAN | Asset failure | LV | 1.00 | 337.0 | 0.000520 | 0.0000015 | No
30/05/2024 | 18:14 | CV29 | LONG RURAL | Asset failure | LV | 2.00 | 393.0 | 0.005641 | 0.0000144 | No
30/05/2024 | 18:32 | PP09 | LONG RURAL | Asset failure | LV | 1.00 | 309.0 | 0.002217 | 0.0000072 | No
30/05/2024 | 20:27 | NU13 | LONG RURAL | Vegetation | Grow-in - NSP responsibility | 1.00 | 91.0 | 0.000653 | 0.0000072 | No
30/05/2024 | 21:11 | AP351C | URBAN | Planned |  | 133.00 | 288.0 | 0.059055 | 0.0002051 | No
30/05/2024 | 21:22 | SM126C | URBAN | Planned |  | 120.00 | 349.9 | 0.064729 | 0.0001850 | No
30/05/2024 | 21:31 | MI02 | SHORT RURAL | Asset failure | LV | 1.00 | 142.0 | 0.000999 | 0.0000070 | No
30/05/2024 | 21:56 | HH118B | URBAN | Planned |  | 120.00 | 444.0 | 0.082149 | 0.0001850 | No
30/05/2024 | 22:55 | AP226E | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 188.0 | 0.000290 | 0.0000015 | No
30/05/2024 | 23:02 | MV64 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 16.00 | 167.0 | 0.018799 | 0.0001126 | No
30/05/2024 | 23:49 | YK17 | LONG RURAL | Asset failure | HV | 509.00 | 240.1 | 0.876861 | 0.0036528 | No
31/05/2024 | 00:51 | EL01A | URBAN | Unknown | Unknown | 22.00 | 32.0 | 0.001085 | 0.0000339 | No
31/05/2024 | 01:20 | MV64 | SHORT RURAL | Asset failure | LV | 22.00 | 111.0 | 0.017181 | 0.0001548 | No
31/05/2024 | 02:50 | GU31 | LONG RURAL | Asset failure | HV | 2.00 | 59.0 | 0.000847 | 0.0000144 | No
31/05/2024 | 02:57 | SM126C | URBAN | Planned |  | 1.00 | 97.0 | 0.000150 | 0.0000015 | No
31/05/2024 | 03:44 | NL760C | URBAN | Asset failure | LV | 107.00 | 50.0 | 0.008248 | 0.0001650 | No
31/05/2024 | 05:07 | AP372F | URBAN | Asset failure | LV | 1.00 | 231.0 | 0.000356 | 0.0000015 | No
31/05/2024 | 06:48 | EL02 | URBAN | Asset failure | LV | 1.00 | 169.0 | 0.000261 | 0.0000015 | No
31/05/2024 | 07:02 | SA42 | URBAN | Overloads |  | 1.00 | 58.0 | 0.000089 | 0.0000015 | No
31/05/2024 | 07:35 | SD38100 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 334.0 | 0.002397 | 0.0000072 | No
31/05/2024 | 08:28 | AP149E | URBAN | Planned |  | 102.00 | 387.0 | 0.060859 | 0.0001573 | No
31/05/2024 | 08:33 | HH177B | URBAN | Overloads |  | 1.00 | 272.0 | 0.000419 | 0.0000015 | No
31/05/2024 | 08:43 | PL803A | URBAN | Asset failure | LV | 1.00 | 644.0 | 0.000993 | 0.0000015 | No
31/05/2024 | 08:46 | CL13 | LONG RURAL | Planned |  | 19.00 | 215.0 | 0.029315 | 0.0001364 | No
31/05/2024 | 08:52 | HH386A | URBAN | Asset failure | LV | 1.00 | 147.0 | 0.000227 | 0.0000015 | No
31/05/2024 | 09:09 | M43 | LONG RURAL | Planned |  | 1.00 | 123.0 | 0.000883 | 0.0000072 | No
31/05/2024 | 09:18 | CM02 | LONG RURAL | Planned |  | 1.00 | 216.0 | 0.001550 | 0.0000072 | No
31/05/2024 | 09:24 | HH102B | URBAN | Planned |  | 142.00 | 233.3 | 0.051075 | 0.0002189 | No
31/05/2024 | 09:24 | HH130C | URBAN | Planned |  | 23.00 | 189.0 | 0.006702 | 0.0000355 | No
31/05/2024 | 09:33 | MB01 | LONG RURAL | Planned |  | 19.00 | 114.0 | 0.015544 | 0.0001364 | No
31/05/2024 | 09:43 | WHY02 | URBAN | Planned |  | 3.00 | 313.0 | 0.001448 | 0.0000046 | No
31/05/2024 | 09:50 | SB20 | LONG RURAL | Planned |  | 11.00 | 205.0 | 0.016183 | 0.0000789 | No
31/05/2024 | 09:56 | HH496A | URBAN | Planned |  | 281.00 | 159.1 | 0.068918 | 0.0004332 | No
31/05/2024 | 10:11 | PA23 | LONG RURAL | Planned |  | 1.00 | 6.0 | 0.000043 | 0.0000072 | No
31/05/2024 | 10:15 | EL01A | URBAN | Asset failure | LV | 1.00 | 303.0 | 0.000467 | 0.0000015 | No
31/05/2024 | 10:19 | YK02 | SHORT RURAL | Planned |  | 119.00 | 170.0 | 0.142328 | 0.0008372 | No
31/05/2024 | 10:21 | HH130B | URBAN | Asset failure | LV | 1.00 | 211.0 | 0.000325 | 0.0000015 | No
31/05/2024 | 10:24 | VH33 | SHORT RURAL | Planned |  | 5.00 | 235.0 | 0.008267 | 0.0000352 | No
31/05/2024 | 10:45 | SD31400 | LONG RURAL | Planned |  | 1.00 | 360.0 | 0.002583 | 0.0000072 | No
31/05/2024 | 11:22 | MB72 | LONG RURAL | Weather |  | 260.00 | 346.2 | 0.645984 | 0.0018658 | No
31/05/2024 | 11:31 | EL17 | URBAN | Animal | Animal impact | 6.00 | 324.0 | 0.002997 | 0.0000093 | No
31/05/2024 | 11:37 | BM53 | SHORT RURAL | Asset failure | LV | 1.00 | 293.0 | 0.002061 | 0.0000070 | No
31/05/2024 | 12:11 | SB23 | LONG RURAL | Planned |  | 1.00 | 134.0 | 0.000962 | 0.0000072 | No
31/05/2024 | 12:17 | EL17 | URBAN | Other |  | 1.00 | 176.0 | 0.000271 | 0.0000015 | No
31/05/2024 | 12:18 | SA520E | URBAN | Asset failure | LV | 72.00 | 213.0 | 0.023644 | 0.0001110 | No
31/05/2024 | 12:18 | PA15 | LONG RURAL | Weather |  | 1.00 | 116.0 | 0.000832 | 0.0000072 | No
31/05/2024 | 12:38 | KA22 | LONG RURAL | Overloads |  | 1.00 | 116.0 | 0.000832 | 0.0000072 | No
31/05/2024 | 13:30 | AP424E | URBAN | Unknown | Unknown | 843.00 | 95.0 | 0.123471 | 0.0012997 | No
31/05/2024 | 13:47 | HH386B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1,613.00 | 97.6 | 0.242683 | 0.0024868 | No
31/05/2024 | 13:56 | NL511A | URBAN | Asset failure | LV | 1.00 | 521.0 | 0.000803 | 0.0000015 | No
31/05/2024 | 14:36 | SM349H | URBAN | Asset failure | LV | 39.00 | 410.0 | 0.024653 | 0.0000601 | No
31/05/2024 | 15:18 | AP149E | URBAN | Unknown | Unknown | 6.00 | 362.5 | 0.003353 | 0.0000093 | No
31/05/2024 | 15:33 | AP149B | URBAN | Asset failure | LV | 1.00 | 452.0 | 0.000697 | 0.0000015 | No
31/05/2024 | 16:07 | HH177B | URBAN | Overloads |  | 1.00 | 270.0 | 0.000416 | 0.0000015 | No
31/05/2024 | 16:27 | YK02 | SHORT RURAL | Asset failure | LV | 32.00 | 124.0 | 0.027917 | 0.0002251 | No
31/05/2024 | 17:24 | SA20 | URBAN | Overloads |  | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
31/05/2024 | 17:41 | SM349H | URBAN | Asset failure | LV | 1.00 | 228.0 | 0.000352 | 0.0000015 | No
31/05/2024 | 20:11 | MTB32 | LONG RURAL | Asset failure | HV | 34.00 | 270.0 | 0.065867 | 0.0002440 | No
31/05/2024 | 21:17 | PP16 | SHORT RURAL | Unknown | Unknown | 74.00 | 301.7 | 0.157067 | 0.0005206 | No
31/05/2024 | 23:04 | AP829A | URBAN | Unknown | Unknown | 2.00 | 133.0 | 0.000410 | 0.0000031 | No
31/05/2024 | 23:05 | SA744D | URBAN | Overloads |  | 1.00 | 81.0 | 0.000125 | 0.0000015 | No
31/05/2024 | 23:26 | MV34 | SHORT RURAL | Planned |  | 1,944.00 | 352.0 | 4.814731 | 0.0136770 | No
31/05/2024 | 23:38 | SG13 | SHORT RURAL | Unknown | Unknown | 1.00 | 102.0 | 0.000718 | 0.0000070 | No
01/06/2024 | 01:20 | AP149E | URBAN | Third Party | Vehicle impact | 52.00 | 108.0 | 0.008658 | 0.0000802 | No
01/06/2024 | 01:27 | AP149E | URBAN | Third Party | Vehicle impact | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
01/06/2024 | 06:20 | SD37301 | SHORT RURAL | Unknown | Unknown | 92.00 | 183.0 | 0.118435 | 0.0006473 | No
01/06/2024 | 08:35 | AP139D | URBAN | Asset failure | HV | 2,087.00 | 6.2 | 0.019969 | 0.0032176 | No
01/06/2024 | 08:40 | HH177C | URBAN | Overloads |  | 1.00 | 244.0 | 0.000376 | 0.0000015 | No
01/06/2024 | 09:50 | EL15 | URBAN | Animal | Animal impact | 18.00 | 570.0 | 0.015818 | 0.0000278 | No
01/06/2024 | 10:17 | PA06 | LONG RURAL | Planned |  | 26.00 | 214.0 | 0.039929 | 0.0001866 | No
01/06/2024 | 10:22 | CL03 | LONG RURAL | Animal | Animal impact | 1.00 | 116.0 | 0.000832 | 0.0000072 | No
01/06/2024 | 10:57 | NL210C | URBAN | Unknown | Unknown | 1.00 | 275.0 | 0.000424 | 0.0000015 | No
01/06/2024 | 11:03 | EL14 | URBAN | Network business | Switching and protection error | 978.00 | 43.7 | 0.065831 | 0.0015078 | No
01/06/2024 | 11:22 | EL260C | URBAN | Asset failure | LV | 1.00 | 597.0 | 0.000920 | 0.0000015 | No
01/06/2024 | 11:41 | MV31 | SHORT RURAL | Asset failure | LV | 2.00 | 194.0 | 0.002730 | 0.0000141 | No
01/06/2024 | 11:54 | AP146A | URBAN | Unknown | Unknown | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
01/06/2024 | 11:57 | HH403A | URBAN | Asset failure | LV | 10.00 | 199.0 | 0.003068 | 0.0000154 | No
01/06/2024 | 12:03 | PA06 | LONG RURAL | Asset failure | LV | 1.00 | 80.0 | 0.000574 | 0.0000072 | No
01/06/2024 | 12:03 | PA06 | LONG RURAL | Asset failure | LV | 36.00 | 75.0 | 0.019376 | 0.0002583 | No
01/06/2024 | 12:13 | AP149A | URBAN | Asset failure | LV | 56.00 | 308.0 | 0.026592 | 0.0000863 | No
01/06/2024 | 14:08 | YK23 | LONG RURAL | Animal | Animal impact | 54.67 | 116.0 | 0.045508 | 0.0003923 | No
01/06/2024 | 15:04 | YK23 | LONG RURAL | Unknown | Unknown | 1.00 | 128.0 | 0.000919 | 0.0000072 | No
01/06/2024 | 15:21 | MV34 | SHORT RURAL | Asset failure | HV | 289.00 | 386.5 | 0.785885 | 0.0020333 | No
01/06/2024 | 15:46 | HH409C | URBAN | Asset failure | LV | 13.00 | 65.0 | 0.001303 | 0.0000200 | No
01/06/2024 | 16:46 | MTB52 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 182.0 | 0.001306 | 0.0000072 | No
01/06/2024 | 16:48 | NU04 | SHORT RURAL | Unknown | Unknown | 25.00 | 83.0 | 0.014599 | 0.0001759 | No
01/06/2024 | 17:47 | SA38 | URBAN | Unknown | Unknown | 43.00 | 339.3 | 0.022494 | 0.0000663 | No
01/06/2024 | 19:11 | ME231A | URBAN | Unknown | Unknown | 1.00 | 247.0 | 0.000381 | 0.0000015 | No
02/06/2024 | 00:28 | EL03 | URBAN | Asset failure | LV | 1.00 | 150.0 | 0.000231 | 0.0000015 | No
02/06/2024 | 07:03 | HH403D | URBAN | Third Party | Vehicle impact | 270.00 | 288.1 | 0.119933 | 0.0004163 | No
02/06/2024 | 07:17 | VH44 | SHORT RURAL | Asset failure | HV | 19.00 | 72.1 | 0.009632 | 0.0001337 | No
02/06/2024 | 08:22 | VH22 | SHORT RURAL | Asset failure | LV | 11.33 | 42.0 | 0.003349 | 0.0000797 | No
02/06/2024 | 09:00 | GU42 | LONG RURAL | Planned |  | 4.00 | 194.0 | 0.005569 | 0.0000287 | No
02/06/2024 | 09:22 | HH341B | URBAN | Planned |  | 11.00 | 253.0 | 0.004291 | 0.0000170 | No
02/06/2024 | 10:27 | HH148D | URBAN | Asset failure | LV | 2.00 | 322.0 | 0.000993 | 0.0000031 | No
02/06/2024 | 11:49 | AP344F | URBAN | Asset failure | LV | 34.00 | 100.0 | 0.005242 | 0.0000524 | No
02/06/2024 | 11:50 | KA10 | LONG RURAL | Third Party | Vehicle impact | 36.00 | 81.6 | 0.021091 | 0.0002583 | No
02/06/2024 | 12:23 | SM349H | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
02/06/2024 | 12:51 | M51 | SHORT RURAL | Animal | Animal impact | 1.33 | 253.0 | 0.002373 | 0.0000094 | No
02/06/2024 | 13:13 | EL25 | URBAN | Planned |  | 5.00 | 159.0 | 0.001226 | 0.0000077 | No
02/06/2024 | 13:41 | SA31 | URBAN | Asset failure | LV | 11.00 | 81.0 | 0.001374 | 0.0000170 | No
02/06/2024 | 14:20 | HH121A | URBAN | Third Party | Vehicle impact | 49.00 | 279.1 | 0.021087 | 0.0000755 | No
02/06/2024 | 14:38 | HH121H | URBAN | Weather |  | 22.00 | 286.0 | 0.009701 | 0.0000339 | No
02/06/2024 | 14:50 | EL10 | URBAN | Asset failure | LV | 1.00 | 171.0 | 0.000264 | 0.0000015 | No
02/06/2024 | 14:55 | CV15 | LONG RURAL | Animal | Animal impact | 59.00 | 185.2 | 0.078416 | 0.0004234 | No
02/06/2024 | 15:03 | SD34201 | SHORT RURAL | Asset failure | Subtransmission | 12.00 | 541.0 | 0.045674 | 0.0000844 | No
02/06/2024 | 15:32 | AP149A | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 265.0 | 0.000409 | 0.0000015 | No
02/06/2024 | 17:22 | GA15 | SHORT RURAL | Overloads |  | 1.00 | 213.0 | 0.001499 | 0.0000070 | No
02/06/2024 | 17:44 | HH341K | URBAN | Asset failure | LV | 9.67 | 136.0 | 0.002027 | 0.0000149 | No
02/06/2024 | 18:27 | M11 | LONG RURAL | Unknown | Unknown | 1.00 | 198.0 | 0.001421 | 0.0000072 | No
02/06/2024 | 19:27 | NL544B | URBAN | Asset failure | LV | 32.00 | 156.0 | 0.007696 | 0.0000493 | No
02/06/2024 | 21:05 | HH341C | URBAN | Planned |  | 405.00 | 324.6 | 0.202656 | 0.0006244 | No
02/06/2024 | 21:19 | MG17 | LONG RURAL | Planned |  | 1,432.00 | 458.9 | 4.715896 | 0.0102765 | No
02/06/2024 | 21:45 | EL18 | URBAN | Asset failure | LV | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
03/06/2024 | 07:11 | VH22 | SHORT RURAL | Unknown | Unknown | 66.00 | 93.2 | 0.043282 | 0.0004643 | No
03/06/2024 | 08:30 | PP09 | LONG RURAL | Animal | Animal impact | 71.00 | 15.1 | 0.007674 | 0.0005095 | No
03/06/2024 | 09:46 | NL115B | URBAN | Third Party | Vehicle impact | 1,777.00 | 91.6 | 0.251055 | 0.0027397 | No
03/06/2024 | 14:03 | CN03 | LONG RURAL | Asset failure | HV | 2.00 | 282.0 | 0.004047 | 0.0000144 | No
03/06/2024 | 14:54 | NL760B | URBAN | Asset failure | LV | 1.00 | 1,092.0 | 0.001684 | 0.0000015 | No
03/06/2024 | 17:42 | HH130D | URBAN | Asset failure | HV | 3,209.00 | 215.3 | 1.065195 | 0.0049475 | No
03/06/2024 | 18:04 | ST36 | LONG RURAL | Asset failure | HV | 10.00 | 137.0 | 0.009832 | 0.0000718 | No
03/06/2024 | 20:55 | VH12 | SHORT RURAL | Asset failure | LV | 19.00 | 376.0 | 0.050261 | 0.0001337 | No
04/06/2024 | 01:41 | CV15 | LONG RURAL | Asset failure | LV | 1.00 | 624.0 | 0.004478 | 0.0000072 | No
04/06/2024 | 01:41 | CV15 | LONG RURAL | Asset failure | HV | 2.00 | 615.0 | 0.008827 | 0.0000144 | No
04/06/2024 | 03:16 | KA07 | LONG RURAL | Asset failure | HV | 70.00 | 269.7 | 0.135496 | 0.0005023 | No
04/06/2024 | 05:58 | CM21 | LONG RURAL | Asset failure | HV | 59.00 | 622.0 | 0.263357 | 0.0004234 | No
04/06/2024 | 06:36 | HH386G | URBAN | Third Party | Vehicle impact | 3.00 | 500.0 | 0.002313 | 0.0000046 | No
04/06/2024 | 07:24 | SG10 | SHORT RURAL | Asset failure | LV | 1.00 | 253.0 | 0.001780 | 0.0000070 | No
04/06/2024 | 08:25 | GU42 | LONG RURAL | Asset failure | LV | 1.00 | 196.0 | 0.001407 | 0.0000072 | No
04/06/2024 | 08:45 | AP149F | URBAN | Planned |  | 130.00 | 290.0 | 0.058124 | 0.0002004 | No
04/06/2024 | 08:47 | KI31 | SHORT RURAL | Planned |  | 2.00 | 165.0 | 0.002322 | 0.0000141 | No
04/06/2024 | 08:48 | SD34400 | LONG RURAL | Planned |  | 1.00 | 103.0 | 0.000739 | 0.0000072 | No
04/06/2024 | 08:52 | EL01N | URBAN | Asset failure | LV | 1.00 | 274.0 | 0.000422 | 0.0000015 | No
04/06/2024 | 09:16 | MG32 | LONG RURAL | Planned |  | 33.00 | 375.8 | 0.089001 | 0.0002368 | No
04/06/2024 | 09:26 | GA800A | SHORT RURAL | Planned |  | 2.00 | 616.0 | 0.008668 | 0.0000141 | No
04/06/2024 | 09:29 | SB22 | LONG RURAL | Planned |  | 21.00 | 182.0 | 0.027428 | 0.0001507 | No
04/06/2024 | 09:40 | HH121D | URBAN | Planned |  | 204.00 | 226.3 | 0.071167 | 0.0003145 | No
04/06/2024 | 09:58 | MV14 | SHORT RURAL | Planned |  | 3.00 | 259.0 | 0.005467 | 0.0000211 | No
04/06/2024 | 10:26 | GU118 | LONG RURAL | Planned |  | 4.00 | 236.0 | 0.006774 | 0.0000287 | No
04/06/2024 | 10:45 | SD37102 | LONG RURAL | Planned |  | 15.00 | 250.0 | 0.026911 | 0.0001076 | No
04/06/2024 | 10:56 | SM126C | URBAN | Third Party | Vehicle impact | 1.00 | 236.0 | 0.000364 | 0.0000015 | No
04/06/2024 | 11:05 | LM33 | LONG RURAL | Planned |  | 3.00 | 49.0 | 0.001055 | 0.0000215 | No
04/06/2024 | 11:06 | YK17 | LONG RURAL | Planned |  | 4.00 | 348.0 | 0.009989 | 0.0000287 | No
04/06/2024 | 11:08 | KI42 | LONG RURAL | Unknown | Unknown | 1.00 | 197.0 | 0.001414 | 0.0000072 | No
04/06/2024 | 11:56 | KA30 | SHORT RURAL | Planned |  | 30.00 | 11.0 | 0.002322 | 0.0002111 | No
04/06/2024 | 12:04 | SM350B | URBAN | Asset failure | LV | 133.00 | 91.8 | 0.018826 | 0.0002051 | No
04/06/2024 | 13:55 | GU42 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 1.00 | 64.0 | 0.000459 | 0.0000072 | No
04/06/2024 | 14:03 | ME231C | URBAN | Asset failure | LV | 1.00 | 418.0 | 0.000644 | 0.0000015 | No
04/06/2024 | 14:28 | SM350A | URBAN | Asset failure | LV | 6.00 | 530.0 | 0.004903 | 0.0000093 | No
04/06/2024 | 15:02 | HH177F | URBAN | Overloads |  | 1.00 | 159.0 | 0.000245 | 0.0000015 | No
04/06/2024 | 15:08 | HH145B | URBAN | Asset failure | LV | 83.00 | 96.9 | 0.012397 | 0.0001280 | No
04/06/2024 | 15:57 | MG32 | LONG RURAL | Asset failure | LV | 5.00 | 17.0 | 0.000610 | 0.0000359 | No
04/06/2024 | 16:28 | HH341D | URBAN | Overloads |  | 1.00 | 291.0 | 0.000449 | 0.0000015 | No
04/06/2024 | 16:32 | CV30 | LONG RURAL | Asset failure | HV | 1.00 | 131.0 | 0.000940 | 0.0000072 | No
04/06/2024 | 16:33 | W04 | LONG RURAL | Asset failure | HV | 2.00 | 31.0 | 0.000445 | 0.0000144 | No
04/06/2024 | 16:36 | SD49200 | LONG RURAL | Unknown | Unknown | 27.00 | 120.0 | 0.023251 | 0.0001938 | No
04/06/2024 | 17:16 | HH102B | URBAN | Third Party | Vehicle impact | 1.00 | 483.0 | 0.000745 | 0.0000015 | No
04/06/2024 | 17:35 | AP132A | URBAN | Planned |  | 190.00 | 41.5 | 0.012152 | 0.0002929 | No
04/06/2024 | 18:21 | GA01 | URBAN | Asset failure | LV | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
04/06/2024 | 18:37 | MI14 | LONG RURAL | Other |  | 1.00 | 24.0 | 0.000172 | 0.0000072 | No
04/06/2024 | 19:43 | G17 | LONG RURAL | Asset failure | LV | 1.00 | 477.0 | 0.003423 | 0.0000072 | No
04/06/2024 | 19:49 | SM216B | URBAN | Unknown | Unknown | 5.00 | 413.0 | 0.003184 | 0.0000077 | No
04/06/2024 | 20:02 | MV64 | SHORT RURAL | Overloads |  | 19.67 | 161.0 | 0.022277 | 0.0001384 | No
04/06/2024 | 20:17 | HH177D | URBAN | Overloads |  | 1.00 | 233.0 | 0.000359 | 0.0000015 | No
04/06/2024 | 20:18 | SM374B | URBAN | Asset failure | LV | 15.33 | 99.0 | 0.002340 | 0.0000236 | No
04/06/2024 | 21:29 | EL20 | URBAN | Animal | Animal impact | 1,295.00 | 16.5 | 0.032853 | 0.0019966 | No
04/06/2024 | 21:59 | AP365D1 | URBAN | Planned |  | 4.00 | 275.0 | 0.001696 | 0.0000062 | No
04/06/2024 | 23:29 | HH145E | URBAN | Planned |  | 267.00 | 91.7 | 0.037731 | 0.0004116 | No
05/06/2024 | 02:04 | HH145E | URBAN | Planned |  | 26.00 | 3.0 | 0.000120 | 0.0000401 | No
05/06/2024 | 03:02 | NL511A | URBAN | Asset failure | LV | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
05/06/2024 | 04:17 | CV16 | LONG RURAL | Asset failure | HV | 53.00 | 654.5 | 0.248925 | 0.0003803 | No
05/06/2024 | 08:44 | NU21 | LONG RURAL | Planned |  | 24.00 | 357.0 | 0.061487 | 0.0001722 | No
05/06/2024 | 08:46 | EL23 | URBAN | Planned |  | 55.00 | 368.1 | 0.031213 | 0.0000848 | No
05/06/2024 | 08:57 | CN02 | LONG RURAL | Planned |  | 80.00 | 209.0 | 0.119988 | 0.0005741 | No
05/06/2024 | 09:03 | SD54300 | LONG RURAL | Planned |  | 1.00 | 144.0 | 0.001033 | 0.0000072 | No
05/06/2024 | 09:12 | YK22 | SHORT RURAL | Planned |  | 82.00 | 256.0 | 0.147689 | 0.0005769 | No
05/06/2024 | 09:17 | HH102A | URBAN | Asset failure | LV | 1.00 | 128.0 | 0.000197 | 0.0000015 | No
05/06/2024 | 09:20 | SD41300 | SHORT RURAL | Planned |  | 1.00 | 100.0 | 0.000704 | 0.0000070 | No
05/06/2024 | 09:25 | HH102A | URBAN | Planned |  | 347.00 | 362.2 | 0.193786 | 0.0005350 | No
05/06/2024 | 09:37 | NL111C | URBAN | Asset failure | LV | 1.00 | 100.0 | 0.000154 | 0.0000015 | No
05/06/2024 | 09:46 | SM350E | URBAN | Planned |  | 53.00 | 70.0 | 0.005720 | 0.0000817 | No
05/06/2024 | 09:58 | SM350E | URBAN | Planned |  | 1.00 | 54.0 | 0.000083 | 0.0000015 | No
05/06/2024 | 10:00 | VH33 | SHORT RURAL | Overloads |  | 1.00 | 226.0 | 0.001590 | 0.0000070 | No
05/06/2024 | 10:30 | PL12 | LONG RURAL | Planned |  | 144.00 | 142.0 | 0.146742 | 0.0010334 | No
05/06/2024 | 10:30 | AP214B | URBAN | Overloads |  | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
05/06/2024 | 10:59 | W27 | LONG RURAL | Planned |  | 1.00 | 335.0 | 0.002404 | 0.0000072 | No
05/06/2024 | 11:36 | PL33 | LONG RURAL | Planned |  | 1.00 | 66.0 | 0.000474 | 0.0000072 | No
05/06/2024 | 12:01 | MG21 | LONG RURAL | Asset failure | LV | 1.00 | 154.0 | 0.001105 | 0.0000072 | No
05/06/2024 | 12:06 | SD40102 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 65.0 | 0.000466 | 0.0000072 | No
05/06/2024 | 13:19 | BM42 | SHORT RURAL | Asset failure | LV | 2.00 | 119.0 | 0.001674 | 0.0000141 | No
05/06/2024 | 14:02 | HH177D | URBAN | Asset failure | LV | 39.00 | 97.9 | 0.005888 | 0.0000601 | No
05/06/2024 | 14:35 | WHY04 | URBAN | Network business | Switching and protection error | 17.00 | 100.0 | 0.002621 | 0.0000262 | No
05/06/2024 | 14:41 | KA06 | LONG RURAL | Overloads |  | 3.00 | 92.0 | 0.001981 | 0.0000215 | No
05/06/2024 | 15:48 | HH496G | URBAN | Planned |  | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
05/06/2024 | 16:54 | HH102A | URBAN | Unknown | Unknown | 1.00 | 159.0 | 0.000245 | 0.0000015 | No
05/06/2024 | 17:22 | HH341F | URBAN | Overloads |  | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
05/06/2024 | 18:49 | VH17 | SHORT RURAL | Unknown | Unknown | 4.00 | 131.0 | 0.003687 | 0.0000281 | No
05/06/2024 | 20:34 | AP149D | URBAN | Overloads |  | 1.00 | 157.0 | 0.000242 | 0.0000015 | No
05/06/2024 | 20:37 | AP355E | URBAN | Overloads |  | 1.00 | 203.0 | 0.000313 | 0.0000015 | No
05/06/2024 | 20:39 | NL511A | URBAN | Planned |  | 199.00 | 492.0 | 0.150953 | 0.0003068 | No
05/06/2024 | 20:57 | SM350H | URBAN | Network business | Switching and protection error | 1.00 | 62.0 | 0.000096 | 0.0000015 | No
05/06/2024 | 22:59 | NL111C | URBAN | Asset failure | HV | 14.00 | 148.3 | 0.003201 | 0.0000216 | No
05/06/2024 | 23:29 | CBD366J | CBD | Planned |  | 13.00 | 136.0 | 0.255436 | 0.0018782 | No
05/06/2024 | 23:29 | CBD366J | URBAN | Planned |  | 59.00 | 113.9 | 0.010364 | 0.0000910 | No
06/06/2024 | 07:18 | SM179A | URBAN | Asset failure | LV | 1.00 | 254.0 | 0.000392 | 0.0000015 | No
06/06/2024 | 08:06 | KA04 | LONG RURAL | Planned |  | 14.00 | 326.0 | 0.032753 | 0.0001005 | No
06/06/2024 | 08:24 | PL04 | URBAN | Planned |  | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
06/06/2024 | 08:41 | SD59100 | LONG RURAL | Unknown | Unknown | 3.00 | 256.0 | 0.005511 | 0.0000215 | No
06/06/2024 | 08:55 | HH121G | URBAN | Planned |  | 16.00 | 217.6 | 0.005368 | 0.0000247 | No
06/06/2024 | 09:06 | NU25 | LONG RURAL | Planned |  | 17.00 | 397.0 | 0.048433 | 0.0001220 | No
06/06/2024 | 09:11 | YK11 | LONG RURAL | Planned |  | 2.00 | 133.0 | 0.001909 | 0.0000144 | No
06/06/2024 | 09:14 | SD34201 | SHORT RURAL | Asset failure | Subtransmission | 5.67 | 31.0 | 0.001236 | 0.0000399 | No
06/06/2024 | 09:21 | GA745C | SHORT RURAL | Planned |  | 1.00 | 310.0 | 0.002181 | 0.0000070 | No
06/06/2024 | 09:29 | MTB54 | LONG RURAL | Planned |  | 15.00 | 253.0 | 0.027234 | 0.0001076 | No
06/06/2024 | 09:38 | KI52 | LONG RURAL | Unknown | Unknown | 27.00 | 260.7 | 0.050507 | 0.0001938 | No
06/06/2024 | 09:39 | W06 | LONG RURAL | Planned |  | 1.00 | 343.0 | 0.002461 | 0.0000072 | No
06/06/2024 | 09:57 | HH121E | URBAN | Planned |  | 42.00 | 69.4 | 0.004491 | 0.0000648 | No
06/06/2024 | 10:57 | MV64 | SHORT RURAL | Asset failure | LV | 1.00 | 599.0 | 0.004214 | 0.0000070 | No
06/06/2024 | 11:08 | MV64 | SHORT RURAL | Asset failure | LV | 52.00 | 592.0 | 0.216581 | 0.0003658 | No
06/06/2024 | 11:38 | SD38100 | LONG RURAL | Overloads |  | 1.00 | 156.0 | 0.001120 | 0.0000072 | No
06/06/2024 | 12:31 | AP425A | URBAN | Planned |  | 129.00 | 92.2 | 0.018331 | 0.0001989 | No
06/06/2024 | 13:43 | SD40600 | LONG RURAL | Third Party | Vehicle impact | 1,722.00 | 812.2 | 10.037138 | 0.0123576 | No
06/06/2024 | 13:47 | NL111C | URBAN | Third Party | Vehicle impact | 29.00 | 672.0 | 0.030046 | 0.0000447 | No
06/06/2024 | 14:14 | HH496G | URBAN | Animal | Animal impact | 13.00 | 552.0 | 0.011064 | 0.0000200 | No
06/06/2024 | 15:34 | HH496G | URBAN | Animal | Animal impact | 7.00 | 36.0 | 0.000389 | 0.0000108 | No
06/06/2024 | 15:48 | SB01 | LONG RURAL | Overloads |  | 1.00 | 189.0 | 0.001356 | 0.0000072 | No
06/06/2024 | 16:09 | SM411D | URBAN | Asset failure | LV | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
06/06/2024 | 16:18 | WHY10 | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
06/06/2024 | 17:15 | HH121A | URBAN | Asset failure | LV | 19.33 | 130.0 | 0.003875 | 0.0000298 | No
06/06/2024 | 21:16 | MG13 | SHORT RURAL | Asset failure | HV | 5.00 | 174.0 | 0.006121 | 0.0000352 | No
06/06/2024 | 21:38 | NL511A | URBAN | Planned |  | 5.00 | 225.0 | 0.001734 | 0.0000077 | No
06/06/2024 | 22:23 | AP149H | URBAN | Asset failure | LV | 66.00 | 153.0 | 0.015569 | 0.0001018 | No
06/06/2024 | 23:55 | HH121C | URBAN | Unknown | Unknown | 16.00 | 80.0 | 0.001973 | 0.0000247 | No
07/06/2024 | 00:24 | EL15 | URBAN | Asset failure | HV | 1.00 | 95.0 | 0.000146 | 0.0000015 | No
07/06/2024 | 08:50 | CV17 | LONG RURAL | Weather |  | 26.00 | 53.0 | 0.009889 | 0.0001866 | No
07/06/2024 | 10:11 | SA20 | URBAN | Asset failure | HV | 614.00 | 7.4 | 0.006995 | 0.0009466 | No
07/06/2024 | 12:29 | PL26 | URBAN | Asset failure | HV | 2.00 | 165.0 | 0.000509 | 0.0000031 | No
07/06/2024 | 15:23 | ST12 | SHORT RURAL | Unknown | Unknown | 46.00 | 225.0 | 0.072817 | 0.0003236 | No
07/06/2024 | 18:13 | HH409A | URBAN | Asset failure | LV | 1.00 | 496.0 | 0.000765 | 0.0000015 | No
07/06/2024 | 18:30 | G09 | LONG RURAL | Weather |  | 48.00 | 32.0 | 0.011023 | 0.0003445 | No
07/06/2024 | 19:20 | NU06 | LONG RURAL | Third Party | Vehicle impact | 12.67 | 149.0 | 0.013544 | 0.0000909 | No
07/06/2024 | 20:30 | G17 | LONG RURAL | Asset failure | LV | 1.00 | 841.0 | 0.006035 | 0.0000072 | No
08/06/2024 | 08:16 | NL111Q | URBAN | Asset failure | LV | 1.00 | 247.0 | 0.000381 | 0.0000015 | No
08/06/2024 | 08:28 | BS0314 | LONG RURAL | Planned |  | 1.00 | 108.0 | 0.000775 | 0.0000072 | No
08/06/2024 | 09:17 | HH107B | URBAN | Overloads |  | 1.00 | 114.0 | 0.000176 | 0.0000015 | No
08/06/2024 | 09:26 | KA01 | SHORT RURAL | Asset failure | LV | 1.00 | 80.0 | 0.000563 | 0.0000070 | No
08/06/2024 | 11:37 | EL260D | URBAN | Asset failure | LV | 1.00 | 224.0 | 0.000345 | 0.0000015 | No
08/06/2024 | 11:55 | EL01Z | URBAN | Overloads |  | 1.00 | 576.0 | 0.000888 | 0.0000015 | No
08/06/2024 | 12:35 | MTB63 | SHORT RURAL | Asset failure | LV | 2.00 | 117.0 | 0.001646 | 0.0000141 | No
08/06/2024 | 14:06 | SM411E | URBAN | Overloads |  | 1.00 | 204.0 | 0.000315 | 0.0000015 | No
08/06/2024 | 14:26 | GA45 | SHORT RURAL | Third Party | Vehicle impact | 83.00 | 332.0 | 0.193856 | 0.0005839 | No
08/06/2024 | 17:06 | YK14 | LONG RURAL | Asset failure | LV | 2.00 | 251.0 | 0.003603 | 0.0000144 | No
08/06/2024 | 18:25 | PP04 | SHORT RURAL | Asset failure | LV | 1.00 | 83.0 | 0.000584 | 0.0000070 | No
08/06/2024 | 18:59 | BM34 | SHORT RURAL | Unknown | Unknown | 10.00 | 103.0 | 0.007247 | 0.0000704 | No
08/06/2024 | 19:46 | AP529A | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
08/06/2024 | 19:55 | HH341K | URBAN | Asset failure | LV | 1.00 | 132.0 | 0.000204 | 0.0000015 | No
08/06/2024 | 20:20 | SM349E | URBAN | Overloads |  | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
08/06/2024 | 22:22 | AP425B | URBAN | Asset failure | LV | 1.00 | 209.0 | 0.000322 | 0.0000015 | No
08/06/2024 | 22:45 | GU42 | LONG RURAL | Asset failure | LV | 1.00 | 114.0 | 0.000818 | 0.0000072 | No
09/06/2024 | 07:20 | SG12 | SHORT RURAL | Unknown | Unknown | 1.00 | 2,940.0 | 0.020684 | 0.0000070 | No
09/06/2024 | 07:25 | NL115A | URBAN | Asset failure | LV | 1.00 | 289.0 | 0.000446 | 0.0000015 | No
09/06/2024 | 08:42 | HH145E | URBAN | Planned |  | 238.00 | 304.2 | 0.111631 | 0.0003669 | No
09/06/2024 | 11:53 | KA25 | LONG RURAL | Asset failure | LV | 1.00 | 332.0 | 0.002383 | 0.0000072 | No
09/06/2024 | 12:33 | HH121C | URBAN | Asset failure | LV | 1.00 | 80.0 | 0.000123 | 0.0000015 | No
09/06/2024 | 14:52 | WK91 | SHORT RURAL | Asset failure | HV | 48.00 | 293.6 | 0.099158 | 0.0003377 | No
09/06/2024 | 18:54 | AP149C | URBAN | Asset failure | LV | 31.33 | 173.0 | 0.008357 | 0.0000483 | No
09/06/2024 | 20:47 | BM53 | SHORT RURAL | Asset failure | LV | 1.00 | 110.0 | 0.000774 | 0.0000070 | No
09/06/2024 | 21:39 | CD15 | LONG RURAL | Animal | Animal impact | 860.00 | 226.5 | 1.397949 | 0.0061716 | No
10/06/2024 | 04:10 | NL210D | URBAN | Overloads |  | 6.00 | 16.0 | 0.000148 | 0.0000093 | No
10/06/2024 | 07:32 | NU14 | LONG RURAL | Asset failure | HV | 1.00 | 532.0 | 0.003818 | 0.0000072 | No
10/06/2024 | 09:05 | HH429C | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
10/06/2024 | 10:00 | EL10 | URBAN | Asset failure | LV | 1.00 | 336.0 | 0.000518 | 0.0000015 | No
10/06/2024 | 10:54 | MI32 | LONG RURAL | Asset failure | LV | 2.00 | 183.0 | 0.002627 | 0.0000144 | No
10/06/2024 | 12:15 | SG13 | SHORT RURAL | Overloads |  | 1.00 | 64.0 | 0.000450 | 0.0000070 | No
10/06/2024 | 12:18 | PL803A | URBAN | Third Party | Vehicle impact | 1.00 | 70.0 | 0.000108 | 0.0000015 | No
10/06/2024 | 15:09 | R21 | LONG RURAL | Asset failure | HV | 4.00 | 305.0 | 0.008755 | 0.0000287 | No
10/06/2024 | 15:10 | SA11 | URBAN | Overloads |  | 1.00 | 390.0 | 0.000601 | 0.0000015 | No
10/06/2024 | 16:00 | EL20 | URBAN | Asset failure | LV | 5.67 | 77.8 | 0.000680 | 0.0000087 | No
10/06/2024 | 17:13 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 136.0 | 0.000957 | 0.0000070 | No
10/06/2024 | 18:06 | SA20 | URBAN | Asset failure | LV | 5.00 | 84.0 | 0.000648 | 0.0000077 | No
10/06/2024 | 22:50 | AP214B | URBAN | Asset failure | LV | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
10/06/2024 | 22:50 | HH432B | URBAN | Asset failure | LV | 147.00 | 132.0 | 0.029916 | 0.0002266 | No
11/06/2024 | 00:36 | MB12 | SHORT RURAL | Asset failure | LV | 6.00 | 201.0 | 0.008485 | 0.0000422 | No
11/06/2024 | 05:47 | AP529D | URBAN | Asset failure | LV | 31.67 | 156.0 | 0.007616 | 0.0000488 | No
11/06/2024 | 05:57 | NL111C | URBAN | Asset failure | LV | 1.00 | 333.0 | 0.000513 | 0.0000015 | No
11/06/2024 | 06:07 | MV62 | SHORT RURAL | Asset failure | LV | 1.00 | 226.0 | 0.001590 | 0.0000070 | No
11/06/2024 | 08:16 | HH121E | URBAN | Planned |  | 35.00 | 200.0 | 0.010792 | 0.0000540 | No
11/06/2024 | 08:32 | YK27 | LONG RURAL | Planned |  | 1.00 | 97.0 | 0.000696 | 0.0000072 | No
11/06/2024 | 08:33 | AP214A | URBAN | Planned |  | 62.00 | 73.0 | 0.006978 | 0.0000956 | No
11/06/2024 | 08:44 | MI01 | LONG RURAL | Asset failure | LV | 1.00 | 458.0 | 0.003287 | 0.0000072 | No
11/06/2024 | 08:51 | CM01 | LONG RURAL | Asset failure | LV | 1.00 | 306.0 | 0.002196 | 0.0000072 | No
11/06/2024 | 09:12 | R33 | LONG RURAL | Planned |  | 1.00 | 140.0 | 0.001005 | 0.0000072 | No
11/06/2024 | 09:13 | KI55 | LONG RURAL | Planned |  | 9.00 | 190.0 | 0.012272 | 0.0000646 | No
11/06/2024 | 09:23 | HH409C | URBAN | Asset failure | LV | 1.00 | 706.0 | 0.001088 | 0.0000015 | No
11/06/2024 | 09:28 | HK01 | LONG RURAL | Planned |  | 1.00 | 148.0 | 0.001062 | 0.0000072 | No
11/06/2024 | 09:29 | G23 | LONG RURAL | Planned |  | 104.00 | 332.0 | 0.247784 | 0.0007463 | No
11/06/2024 | 09:34 | PA19 | LONG RURAL | Planned |  | 2.00 | 97.0 | 0.001392 | 0.0000144 | No
11/06/2024 | 10:24 | VH72 | SHORT RURAL | Planned |  | 123.00 | 244.0 | 0.211149 | 0.0008654 | No
11/06/2024 | 10:37 | CM18 | LONG RURAL | Planned |  | 2.00 | 110.0 | 0.001579 | 0.0000144 | No
11/06/2024 | 11:24 | HH130D | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 1,262.00 | 98.4 | 0.191551 | 0.0019457 | No
11/06/2024 | 11:31 | SA520D | URBAN | Asset failure | LV | 5.00 | 98.0 | 0.000755 | 0.0000077 | No
11/06/2024 | 11:42 | YK16 | LONG RURAL | Planned |  | 2.00 | 81.0 | 0.001163 | 0.0000144 | No
11/06/2024 | 12:08 | WHY12 | URBAN | Unknown | Unknown | 2.00 | 78.0 | 0.000241 | 0.0000031 | No
11/06/2024 | 12:29 | SG14 | SHORT RURAL | Asset failure | LV | 1.00 | 111.0 | 0.000781 | 0.0000070 | No
11/06/2024 | 12:43 | NL210A | URBAN | Unknown | Unknown | 1.00 | 384.0 | 0.000592 | 0.0000015 | No
11/06/2024 | 13:31 | VH15 | SHORT RURAL | Other |  | 1.00 | 99.0 | 0.000697 | 0.0000070 | No
11/06/2024 | 13:46 | HH341G | URBAN | Unknown | Unknown | 10.33 | 228.0 | 0.003632 | 0.0000159 | No
11/06/2024 | 15:31 | HH403B | URBAN | Asset failure | LV | 1.00 | 287.0 | 0.000442 | 0.0000015 | No
11/06/2024 | 17:06 | HH177E | URBAN | Asset failure | LV | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
11/06/2024 | 17:18 | AP344E | URBAN | Asset failure | LV | 1.00 | 221.0 | 0.000341 | 0.0000015 | No
11/06/2024 | 19:39 | PA03 | URBAN | Asset failure | LV | 1.00 | 158.0 | 0.000244 | 0.0000015 | No
11/06/2024 | 20:40 | HH428F | URBAN | Asset failure | LV | 1.00 | 75.0 | 0.000116 | 0.0000015 | No
11/06/2024 | 20:56 | SM411D | URBAN | Planned |  | 73.00 | 432.5 | 0.048682 | 0.0001125 | No
11/06/2024 | 23:19 | CBD367K | CBD | Planned |  | 30.00 | 261.0 | 1.131258 | 0.0043343 | No
12/06/2024 | 00:24 | HH107C | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 896.00 | 84.0 | 0.116039 | 0.0013814 | No
12/06/2024 | 00:32 | M11 | LONG RURAL | Weather |  | 778.00 | 60.0 | 0.334991 | 0.0055832 | No
12/06/2024 | 07:33 | AP829B | URBAN | Asset failure | HV | 138.00 | 12.3 | 0.002623 | 0.0002128 | No
12/06/2024 | 09:15 | NL115E | URBAN | Asset failure | HV | 148.67 | 76.5 | 0.017523 | 0.0002292 | No
12/06/2024 | 10:31 | MV32 | SHORT RURAL | Animal | Animal impact | 2.00 | 90.0 | 0.001266 | 0.0000141 | No
12/06/2024 | 12:56 | PA23 | LONG RURAL | Asset failure | HV | 1.00 | 153.0 | 0.001098 | 0.0000072 | No
12/06/2024 | 18:02 | HK01 | LONG RURAL | Asset failure | HV | 1.00 | 1,123.0 | 0.008059 | 0.0000072 | No
13/06/2024 | 00:58 | SA33 | URBAN | Asset failure | LV | 1.00 | 121.0 | 0.000187 | 0.0000015 | No
13/06/2024 | 08:32 | MB12 | SHORT RURAL | Planned |  | 2.00 | 110.0 | 0.001548 | 0.0000141 | No
13/06/2024 | 08:38 | HH341H | URBAN | Planned |  | 168.00 | 270.4 | 0.070043 | 0.0002590 | No
13/06/2024 | 08:43 | MTB12 | SHORT RURAL | Unknown | Unknown | 1.00 | 28.0 | 0.000197 | 0.0000070 | No
13/06/2024 | 08:52 | MB81 | LONG RURAL | Planned |  | 9.00 | 347.0 | 0.022412 | 0.0000646 | No
13/06/2024 | 09:03 | R09 | LONG RURAL | Planned |  | 82.00 | 255.7 | 0.150459 | 0.0005885 | No
13/06/2024 | 09:15 | MV52 | SHORT RURAL | Planned |  | 12.00 | 372.0 | 0.031406 | 0.0000844 | No
13/06/2024 | 09:17 | KI41 | LONG RURAL | Planned |  | 5.00 | 309.0 | 0.011087 | 0.0000359 | No
13/06/2024 | 09:30 | EL260A | URBAN | Overloads |  | 1.00 | 267.0 | 0.000412 | 0.0000015 | No
13/06/2024 | 09:32 | NA29 | LONG RURAL | Planned |  | 52.00 | 254.0 | 0.094785 | 0.0003732 | No
13/06/2024 | 09:37 | ST21 | SHORT RURAL | Planned |  | 27.00 | 287.0 | 0.054518 | 0.0001900 | No
13/06/2024 | 09:48 | CM21 | LONG RURAL | Planned |  | 65.00 | 263.0 | 0.122679 | 0.0004665 | No
13/06/2024 | 09:48 | SD38200 | LONG RURAL | Planned |  | 2.00 | 49.0 | 0.000703 | 0.0000144 | No
13/06/2024 | 09:56 | AP226D | URBAN | Planned |  | 75.00 | 53.0 | 0.006128 | 0.0001156 | No
13/06/2024 | 10:35 | G32 | LONG RURAL | Planned |  | 34.00 | 251.0 | 0.061243 | 0.0002440 | No
13/06/2024 | 10:52 | CN76 | LONG RURAL | Planned |  | 2.00 | 83.0 | 0.001191 | 0.0000144 | No
13/06/2024 | 11:36 | GA22 | SHORT RURAL | Asset failure | LV | 22.00 | 128.9 | 0.019953 | 0.0001548 | No
13/06/2024 | 12:52 | NL760C | URBAN | Asset failure | LV | 40.00 | 75.0 | 0.004625 | 0.0000617 | No
13/06/2024 | 13:00 | BT15 | LONG RURAL | Third Party | Vehicle impact | 2.00 | 33.0 | 0.000474 | 0.0000144 | No
13/06/2024 | 13:27 | CV17 | LONG RURAL | Asset failure | HV | 14.00 | 66.0 | 0.006631 | 0.0001005 | No
13/06/2024 | 15:21 | VH34 | SHORT RURAL | Overloads |  | 2.00 | 417.0 | 0.005868 | 0.0000141 | No
13/06/2024 | 15:33 | CN75 | LONG RURAL | Asset failure | HV | 1.00 | 1,597.0 | 0.011461 | 0.0000072 | No
13/06/2024 | 16:17 | MTB62 | SHORT RURAL | Other |  | 1.00 | 130.0 | 0.000915 | 0.0000070 | No
13/06/2024 | 18:22 | NU20 | LONG RURAL | Asset failure | LV | 1.00 | 5,069.0 | 0.036377 | 0.0000072 | No
13/06/2024 | 18:38 | SA18 | URBAN | Overloads |  | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
13/06/2024 | 20:47 | MTB32 | LONG RURAL | Unknown | Unknown | 18.00 | 298.0 | 0.038494 | 0.0001292 | No
13/06/2024 | 21:10 | GA22 | SHORT RURAL | Overloads |  | 2.00 | 242.0 | 0.003405 | 0.0000141 | No
13/06/2024 | 21:30 | SM126A | URBAN | Overloads |  | 1.00 | 297.0 | 0.000458 | 0.0000015 | No
13/06/2024 | 23:13 | AP149D | URBAN | Planned |  | 141.00 | 298.3 | 0.064849 | 0.0002174 | No
14/06/2024 | 09:16 | NL210A | URBAN | Weather |  | 45.00 | 103.0 | 0.007146 | 0.0000694 | No
14/06/2024 | 10:31 | MI24 | LONG RURAL | Weather |  | 166.00 | 320.5 | 0.381745 | 0.0011913 | No
14/06/2024 | 10:48 | NL760A | URBAN | Unknown | Unknown | 432.00 | 90.0 | 0.059943 | 0.0006660 | No
14/06/2024 | 10:50 | VH18 | SHORT RURAL | Weather |  | 86.33 | 97.8 | 0.059431 | 0.0006074 | No
14/06/2024 | 11:19 | CD03 | LONG RURAL | Third Party | Vehicle impact | 861.00 | 508.0 | 3.138840 | 0.0061788 | No
14/06/2024 | 11:19 | CD03 | SHORT RURAL | Third Party | Vehicle impact | 1,397.00 | 508.0 | 4.992919 | 0.0098286 | No
14/06/2024 | 12:10 | SG01 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 23.00 | 123.0 | 0.019903 | 0.0001618 | No
14/06/2024 | 19:34 | SG04 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 216.00 | 118.0 | 0.179321 | 0.0015197 | No
14/06/2024 | 19:43 | CN02 | LONG RURAL | Asset failure | HV | 1.00 | 242.0 | 0.001737 | 0.0000072 | No
15/06/2024 | 03:35 | VH23 | SHORT RURAL | Asset failure | HV | 28.00 | 499.9 | 0.098483 | 0.0001970 | No
15/06/2024 | 07:06 | CV29 | LONG RURAL | Asset failure | LV | 1.00 | 485.0 | 0.003481 | 0.0000072 | No
15/06/2024 | 07:12 | MG24 | SHORT RURAL | Unknown | Unknown | 309.00 | 130.8 | 0.284382 | 0.0021740 | No
15/06/2024 | 07:15 | G42 | LONG RURAL | Unknown | Unknown | 17.00 | 1,037.5 | 0.126576 | 0.0001220 | No
15/06/2024 | 08:09 | HH130B | URBAN | Asset failure | LV | 27.33 | 142.0 | 0.005984 | 0.0000421 | No
15/06/2024 | 08:24 | NL511A | URBAN | Asset failure | LV | 3.00 | 496.0 | 0.002294 | 0.0000046 | No
15/06/2024 | 08:40 | HH177E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 19.00 | 269.0 | 0.007880 | 0.0000293 | No
15/06/2024 | 08:51 | NA22 | LONG RURAL | Planned |  | 126.00 | 96.0 | 0.086805 | 0.0009042 | No
15/06/2024 | 09:33 | MV42 | SHORT RURAL | Asset failure | LV | 1.00 | 586.0 | 0.004123 | 0.0000070 | No
15/06/2024 | 10:01 | NA01 | LONG RURAL | Planned |  | 1.00 | 73.0 | 0.000524 | 0.0000072 | No
15/06/2024 | 10:30 | HH403D | URBAN | Asset failure | LV | 95.00 | 77.0 | 0.011278 | 0.0001465 | No
15/06/2024 | 11:03 | SG07 | SHORT RURAL | Other |  | 1.00 | 448.0 | 0.003152 | 0.0000070 | No
15/06/2024 | 11:18 | HH341C | URBAN | Vegetation | Grow-in - NSP responsibility | 8.33 | 75.0 | 0.000964 | 0.0000128 | No
15/06/2024 | 11:33 | ST21 | SHORT RURAL | Animal | Animal impact | 10.00 | 300.0 | 0.021106 | 0.0000704 | No
15/06/2024 | 11:49 | NL210B | URBAN | Unknown | Unknown | 3.00 | 250.0 | 0.001156 | 0.0000046 | No
15/06/2024 | 13:27 | BU05 | LONG RURAL | Asset failure | HV | 1.00 | 60.0 | 0.000431 | 0.0000072 | No
15/06/2024 | 13:33 | SM411E | URBAN | Asset failure | HV | 277.33 | 60.5 | 0.025881 | 0.0004276 | No
15/06/2024 | 14:02 | EL14 | URBAN | Unknown | Unknown | 22.67 | 66.0 | 0.002306 | 0.0000349 | No
15/06/2024 | 15:12 | SG02 | SHORT RURAL | Other |  | 1.00 | 196.0 | 0.001379 | 0.0000070 | No
15/06/2024 | 15:44 | CN24 | LONG RURAL | Asset failure | HV | 107.00 | 203.9 | 0.156544 | 0.0007679 | No
15/06/2024 | 16:06 | NL234C | URBAN | Asset failure | LV | 1.00 | 239.0 | 0.000368 | 0.0000015 | No
15/06/2024 | 17:13 | HH121E | URBAN | Asset failure | LV | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
15/06/2024 | 19:41 | HH121A | URBAN | Asset failure | LV | 23.00 | 34.0 | 0.001206 | 0.0000355 | No
15/06/2024 | 19:50 | BM52 | URBAN | Overloads |  | 2.00 | 142.0 | 0.000438 | 0.0000031 | No
15/06/2024 | 21:39 | NU25 | LONG RURAL | Asset failure | LV | 5.67 | 152.0 | 0.006181 | 0.0000407 | No
15/06/2024 | 22:45 | LM43 | LONG RURAL | Planned |  | 2,722.00 | 570.0 | 11.134362 | 0.0195340 | No
16/06/2024 | 00:21 | HH130F | URBAN | Vegetation | Grow-in - NSP responsibility | 16.67 | 54.0 | 0.001388 | 0.0000257 | No
16/06/2024 | 03:58 | HH130B | URBAN | Third Party | Vehicle impact | 17.00 | 705.0 | 0.018478 | 0.0000262 | No
16/06/2024 | 08:13 | PP04 | SHORT RURAL | Planned |  | 32.00 | 470.7 | 0.105976 | 0.0002251 | No
16/06/2024 | 08:23 | AP355E | URBAN | Planned |  | 73.00 | 273.0 | 0.030730 | 0.0001125 | No
16/06/2024 | 08:29 | AP829A | URBAN | Planned |  | 4.00 | 352.0 | 0.002171 | 0.0000062 | No
16/06/2024 | 08:33 | AP425C | URBAN | Asset failure | LV | 1.00 | 271.0 | 0.000418 | 0.0000015 | No
16/06/2024 | 08:37 | EL07 | URBAN | Planned |  | 18.00 | 315.8 | 0.008763 | 0.0000278 | No
16/06/2024 | 08:39 | ME427A | URBAN | Network business | Switching and protection error | 17.00 | 407.0 | 0.010667 | 0.0000262 | No
16/06/2024 | 08:49 | GU42 | LONG RURAL | Planned |  | 5.00 | 451.2 | 0.016190 | 0.0000359 | No
16/06/2024 | 08:56 | PP04 | SHORT RURAL | Planned |  | 1.00 | 179.0 | 0.001259 | 0.0000070 | No
16/06/2024 | 09:26 | SM179D | URBAN | Overloads |  | 1.00 | 200.0 | 0.000308 | 0.0000015 | No
16/06/2024 | 09:36 | CN81 | LONG RURAL | Planned |  | 31.00 | 296.3 | 0.065922 | 0.0002225 | No
16/06/2024 | 11:01 | NL760C | URBAN | Asset failure | LV | 37.00 | 58.8 | 0.003352 | 0.0000570 | No
16/06/2024 | 11:06 | SA711C | URBAN | Asset failure | LV | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
16/06/2024 | 12:35 | CBD367G | CBD | Planned |  | 1.00 | 343.0 | 0.049556 | 0.0001445 | No
16/06/2024 | 12:42 | PL06 | URBAN | Asset failure | LV | 15.67 | 166.0 | 0.004010 | 0.0000242 | No
16/06/2024 | 12:47 | HH148B | URBAN | Asset failure | LV | 47.00 | 77.0 | 0.005580 | 0.0000725 | No
16/06/2024 | 12:57 | HH341H | URBAN | Asset failure | LV | 1.00 | 67.0 | 0.000103 | 0.0000015 | No
16/06/2024 | 12:58 | PP03 | URBAN | Asset failure | LV | 1.00 | 378.0 | 0.000583 | 0.0000015 | No
16/06/2024 | 13:32 | EL14 | URBAN | Asset failure | LV | 15.00 | 506.0 | 0.011702 | 0.0000231 | No
16/06/2024 | 13:46 | SM349D | URBAN | Asset failure | LV | 1.00 | 149.0 | 0.000230 | 0.0000015 | No
16/06/2024 | 14:29 | AP146E | URBAN | Asset failure | LV | 143.00 | 55.0 | 0.012126 | 0.0002205 | No
16/06/2024 | 14:51 | SM350A | URBAN | Asset failure | LV | 1.00 | 205.0 | 0.000316 | 0.0000015 | No
16/06/2024 | 16:26 | SM216G | URBAN | Asset failure | LV | 32.00 | 50.0 | 0.002467 | 0.0000493 | No
16/06/2024 | 17:03 | SM216G | URBAN | Asset failure | LV | 2.00 | 14.0 | 0.000043 | 0.0000031 | No
16/06/2024 | 17:20 | SM216B | URBAN | Asset failure | LV | 11.33 | 113.0 | 0.001974 | 0.0000175 | No
16/06/2024 | 17:58 | NL451E | URBAN | Asset failure | LV | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
16/06/2024 | 18:49 | G24 | LONG RURAL | Overloads |  | 2.00 | 218.0 | 0.003129 | 0.0000144 | No
16/06/2024 | 18:54 | AP139B | URBAN | Unknown | Unknown | 24.33 | 183.0 | 0.006865 | 0.0000375 | No
16/06/2024 | 20:14 | VH45 | SHORT RURAL | Overloads |  | 1.00 | 323.0 | 0.002272 | 0.0000070 | No
16/06/2024 | 21:21 | HH341D | URBAN | Planned |  | 46.00 | 298.0 | 0.021134 | 0.0000709 | No
16/06/2024 | 21:29 | CBD353R | CBD | Planned |  | 8.00 | 4.0 | 0.004623 | 0.0011558 | No
16/06/2024 | 22:08 | AP424C | URBAN | Asset failure | LV | 1.00 | 201.0 | 0.000310 | 0.0000015 | No
16/06/2024 | 22:20 | PA02 | URBAN | Overloads |  | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
16/06/2024 | 22:30 | EL01P | URBAN | Asset failure | LV | 1.00 | 187.0 | 0.000288 | 0.0000015 | No
16/06/2024 | 23:11 | HH341C | URBAN | Asset failure | LV | 32.33 | 187.0 | 0.009322 | 0.0000498 | No
16/06/2024 | 23:18 | GU17 | LONG RURAL | Planned |  | 730.00 | 364.8 | 1.911186 | 0.0052387 | No
17/06/2024 | 05:33 | NU13 | LONG RURAL | Asset failure | LV | 1.00 | 654.0 | 0.004693 | 0.0000072 | No
17/06/2024 | 06:26 | EL01P | URBAN | Asset failure | LV | 20.00 | 158.0 | 0.004872 | 0.0000308 | No
17/06/2024 | 07:53 | BM34 | SHORT RURAL | Asset failure | LV | 3.00 | 133.0 | 0.002807 | 0.0000211 | No
17/06/2024 | 08:14 | WHY11 | URBAN | 7 - STPIS Exclusion (3.3)(a) |  | 3.00 | 3,094.0 | 0.014311 | 0.0000046 | No
17/06/2024 | 08:36 | KA08 | LONG RURAL | Planned |  | 2.00 | 23.0 | 0.000330 | 0.0000144 | No
17/06/2024 | 08:38 | MTB22 | SHORT RURAL | Asset failure | LV | 3.00 | 536.0 | 0.011313 | 0.0000211 | No
17/06/2024 | 08:50 | MB11 | SHORT RURAL | Asset failure | LV | 1.00 | 325.0 | 0.002287 | 0.0000070 | No
17/06/2024 | 09:10 | CM22 | LONG RURAL | Planned |  | 52.00 | 71.0 | 0.026495 | 0.0003732 | No
17/06/2024 | 09:12 | PL02 | URBAN | Unknown | Unknown | 2.00 | 268.0 | 0.000826 | 0.0000031 | No
17/06/2024 | 09:14 | HH118C | URBAN | Overloads |  | 19.67 | 222.0 | 0.006731 | 0.0000303 | No
17/06/2024 | 09:16 | BS0315 | LONG RURAL | Planned |  | 1.00 | 242.0 | 0.001737 | 0.0000072 | No
17/06/2024 | 09:23 | MG05 | LONG RURAL | Planned |  | 1.00 | 38.0 | 0.000273 | 0.0000072 | No
17/06/2024 | 09:26 | CM16 | LONG RURAL | Planned |  | 85.00 | 294.0 | 0.179336 | 0.0006100 | No
17/06/2024 | 09:31 | EL01P | URBAN | Asset failure | LV | 1.00 | 94.0 | 0.000145 | 0.0000015 | No
17/06/2024 | 09:56 | CV18 | SHORT RURAL | Planned |  | 2.00 | 155.0 | 0.002181 | 0.0000141 | No
17/06/2024 | 09:58 | VH11 | URBAN | Asset failure | LV | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
17/06/2024 | 10:04 | MT25 | LONG RURAL | Planned |  | 57.00 | 186.0 | 0.076083 | 0.0004091 | No
17/06/2024 | 10:06 | HK02 | LONG RURAL | Planned |  | 1.00 | 82.0 | 0.000588 | 0.0000072 | No
17/06/2024 | 10:28 | G11 | LONG RURAL | Planned |  | 109.00 | 38.8 | 0.030385 | 0.0007822 | No
17/06/2024 | 10:43 | HH409F | URBAN | Overloads |  | 34.67 | 291.0 | 0.015553 | 0.0000534 | No
17/06/2024 | 11:38 | HH102B | URBAN | Planned |  | 79.00 | 17.0 | 0.002071 | 0.0001218 | No
17/06/2024 | 11:50 | GU41 | LONG RURAL | Other |  | 8.00 | 57.0 | 0.003272 | 0.0000574 | No
17/06/2024 | 11:51 | ME231A | URBAN | Overloads |  | 1.00 | 398.0 | 0.000614 | 0.0000015 | No
17/06/2024 | 11:54 | MT11 | LONG RURAL | Planned |  | 1.00 | 59.0 | 0.000423 | 0.0000072 | No
17/06/2024 | 11:55 | MTB32 | LONG RURAL | Asset failure | LV | 1.00 | 192.0 | 0.001378 | 0.0000072 | No
17/06/2024 | 12:58 | SM350B | URBAN | Asset failure | LV | 1.00 | 218.0 | 0.000336 | 0.0000015 | No
17/06/2024 | 13:19 | EL10 | URBAN | Asset failure | LV | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
17/06/2024 | 13:40 | SA711C | URBAN | Asset failure | LV | 1.00 | 468.0 | 0.000722 | 0.0000015 | No
17/06/2024 | 13:44 | R09 | LONG RURAL | Asset failure | HV | 402.00 | 23.0 | 0.066352 | 0.0028849 | No
17/06/2024 | 13:48 | ME427D | URBAN | Asset failure | LV | 1.00 | 198.0 | 0.000305 | 0.0000015 | No
17/06/2024 | 14:03 | HH130E | URBAN | Asset failure | LV | 32.00 | 38.0 | 0.001875 | 0.0000493 | No
17/06/2024 | 14:30 | MB25 | LONG RURAL | Asset failure | HV | 2.00 | 21.0 | 0.000301 | 0.0000144 | No
17/06/2024 | 15:39 | SD44200 | SHORT RURAL | Animal | Animal impact | 10.00 | 11.0 | 0.000774 | 0.0000704 | No
17/06/2024 | 16:08 | G28 | LONG RURAL | Asset failure | HV | 2.00 | 133.0 | 0.001909 | 0.0000144 | No
17/06/2024 | 16:21 | MG21 | LONG RURAL | Weather |  | 25.00 | 45.0 | 0.008073 | 0.0001794 | No
17/06/2024 | 17:47 | GA26 | URBAN | Asset failure | LV | 1.00 | 468.0 | 0.000722 | 0.0000015 | No
17/06/2024 | 18:18 | AP146E | URBAN | Overloads |  | 47.67 | 39.0 | 0.002866 | 0.0000735 | No
17/06/2024 | 19:31 | SM172A | URBAN | Unknown | Unknown | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
17/06/2024 | 19:39 | AP372F | URBAN | Overloads |  | 1.00 | 240.0 | 0.000370 | 0.0000015 | No
17/06/2024 | 20:59 | SM349D | URBAN | Planned |  | 89.00 | 445.2 | 0.061083 | 0.0001372 | No
17/06/2024 | 22:06 | ME347G | URBAN | Planned |  | 1.00 | 197.0 | 0.000304 | 0.0000015 | No
17/06/2024 | 22:15 | CBD366E | URBAN | Planned |  | 69.00 | 181.3 | 0.019289 | 0.0001064 | No
17/06/2024 | 22:21 | CBD366E | CBD | Planned |  | 17.00 | 220.0 | 0.540345 | 0.0024561 | No
17/06/2024 | 22:21 | CBD366E | URBAN | Planned |  | 91.00 | 220.0 | 0.030866 | 0.0001403 | No
17/06/2024 | 22:53 | AP529E | URBAN | Overloads |  | 1.00 | 139.0 | 0.000214 | 0.0000015 | No
18/06/2024 | 02:09 | EL11 | URBAN | Unknown | Unknown | 1.00 | 542.0 | 0.000836 | 0.0000015 | No
18/06/2024 | 03:16 | CBD412S | URBAN | Third Party | Unauthorised access | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
18/06/2024 | 04:21 | WHY02 | URBAN | Weather |  | 630.00 | 155.1 | 0.150663 | 0.0009713 | No
18/06/2024 | 07:04 | EL10 | URBAN | Planned |  | 166.00 | 29.6 | 0.007568 | 0.0002559 | No
18/06/2024 | 07:57 | HH409F | URBAN | Unknown | Unknown | 119.33 | 114.0 | 0.020974 | 0.0001840 | No
18/06/2024 | 08:09 | KA05 | LONG RURAL | Planned |  | 2.00 | 213.0 | 0.003057 | 0.0000144 | No
18/06/2024 | 08:17 | SM349D | URBAN | Asset failure | LV | 1.00 | 249.0 | 0.000384 | 0.0000015 | No
18/06/2024 | 08:31 | NU21 | LONG RURAL | Asset failure | LV | 1.00 | 245.0 | 0.001758 | 0.0000072 | No
18/06/2024 | 08:35 | HH107B | URBAN | Unknown | Unknown | 1.00 | 105.0 | 0.000162 | 0.0000015 | No
18/06/2024 | 08:44 | CD01 | SHORT RURAL | Planned |  | 32.00 | 478.0 | 0.107615 | 0.0002251 | No
18/06/2024 | 08:52 | BS0314 | LONG RURAL | Planned |  | 1.00 | 241.0 | 0.001729 | 0.0000072 | No
18/06/2024 | 09:03 | VH22 | SHORT RURAL | Planned |  | 51.00 | 201.0 | 0.072121 | 0.0003588 | No
18/06/2024 | 09:12 | NL760B | URBAN | Planned |  | 4.00 | 35.0 | 0.000216 | 0.0000062 | No
18/06/2024 | 09:25 | SD54300 | LONG RURAL | Planned |  | 1.00 | 126.0 | 0.000904 | 0.0000072 | No
18/06/2024 | 09:27 | SG04 | SHORT RURAL | Planned |  | 15.00 | 252.7 | 0.026672 | 0.0001055 | No
18/06/2024 | 09:35 | MTB11 | SHORT RURAL | Planned |  | 105.00 | 141.0 | 0.104196 | 0.0007387 | No
18/06/2024 | 09:48 | SD54300 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 923.00 | 13.0 | 0.086109 | 0.0066238 | No
18/06/2024 | 10:44 | NU13 | LONG RURAL | Animal | Animal impact | 2.00 | 75.0 | 0.001076 | 0.0000144 | No
18/06/2024 | 11:02 | YK21 | LONG RURAL | Planned |  | 4.00 | 87.0 | 0.002497 | 0.0000287 | No
18/06/2024 | 11:09 | GA53 | SHORT RURAL | Planned |  | 46.00 | 192.0 | 0.062137 | 0.0003236 | No
18/06/2024 | 11:09 | YK07 | LONG RURAL | Asset failure | LV | 1.00 | 94.0 | 0.000675 | 0.0000072 | No
18/06/2024 | 11:11 | PL33 | LONG RURAL | Planned |  | 3.00 | 17.0 | 0.000366 | 0.0000215 | No
18/06/2024 | 11:34 | HH107B | URBAN | Asset failure | LV | 1.00 | 125.0 | 0.000193 | 0.0000015 | No
18/06/2024 | 12:00 | MG05 | LONG RURAL | Asset failure | LV | 5.00 | 101.6 | 0.003646 | 0.0000359 | No
18/06/2024 | 12:04 | NL210A | URBAN | Asset failure | LV | 1.00 | 64.0 | 0.000099 | 0.0000015 | No
18/06/2024 | 12:26 | BT15 | LONG RURAL | Planned |  | 6.00 | 141.2 | 0.006078 | 0.0000431 | No
18/06/2024 | 12:32 | AP146C | URBAN | Unknown | Unknown | 1.00 | 673.0 | 0.001038 | 0.0000015 | No
18/06/2024 | 12:39 | HH177B | URBAN | Asset failure | LV | 1.00 | 411.0 | 0.000634 | 0.0000015 | No
18/06/2024 | 13:02 | MG13 | SHORT RURAL | Unknown | Unknown | 8.00 | 152.0 | 0.008555 | 0.0000563 | No
18/06/2024 | 13:07 | HH121C | URBAN | Asset failure | LV | 74.00 | 54.0 | 0.006161 | 0.0001141 | No
18/06/2024 | 13:45 | GA50 | URBAN | Asset failure | LV | 1.00 | 225.0 | 0.000347 | 0.0000015 | No
18/06/2024 | 14:16 | SM350H | URBAN | Asset failure | LV | 4.00 | 480.0 | 0.002960 | 0.0000062 | No
18/06/2024 | 14:20 | BM56 | SHORT RURAL | Asset failure | LV | 9.00 | 65.0 | 0.004116 | 0.0000633 | No
18/06/2024 | 15:25 | KI51 | LONG RURAL | Asset failure | LV | 1.00 | 70.0 | 0.000502 | 0.0000072 | No
18/06/2024 | 16:18 | SA14 | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
18/06/2024 | 16:18 | BM56 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 16.00 | 63.0 | 0.007092 | 0.0001126 | No
18/06/2024 | 16:35 | ME131C | URBAN | Asset failure | LV | 1.00 | 336.0 | 0.000518 | 0.0000015 | No
18/06/2024 | 17:23 | MB71 | LONG RURAL | Planned |  | 75.00 | 192.0 | 0.103339 | 0.0005382 | No
18/06/2024 | 17:43 | AP529D | URBAN | Overloads |  | 27.67 | 231.0 | 0.009853 | 0.0000427 | No
18/06/2024 | 17:45 | CN24 | LONG RURAL | Planned |  | 1.00 | 277.0 | 0.001988 | 0.0000072 | No
18/06/2024 | 17:53 | MV62 | SHORT RURAL | Unknown | Unknown | 1.00 | 411.0 | 0.002892 | 0.0000070 | No
18/06/2024 | 18:53 | CV753A | LONG RURAL | Asset failure | LV | 2.00 | 219.0 | 0.003143 | 0.0000144 | No
18/06/2024 | 18:56 | SM179B | URBAN | Asset failure | LV | 1.00 | 271.0 | 0.000418 | 0.0000015 | No
18/06/2024 | 20:33 | PP03 | URBAN | Overloads |  | 16.00 | 228.0 | 0.005624 | 0.0000247 | No
18/06/2024 | 20:46 | ME200A | URBAN | Asset failure | LV | 1.00 | 230.0 | 0.000355 | 0.0000015 | No
19/06/2024 | 00:08 | HH145C | URBAN | Asset failure | LV | 2.00 | 215.0 | 0.000663 | 0.0000031 | No
19/06/2024 | 00:32 | HH145D | URBAN | Overloads |  | 22.67 | 175.0 | 0.006116 | 0.0000349 | No
19/06/2024 | 02:49 | NL544B | URBAN | Unknown | Unknown | 4.00 | 506.0 | 0.003121 | 0.0000062 | No
19/06/2024 | 08:31 | HH121B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 69.00 | 102.0 | 0.010851 | 0.0001064 | No
19/06/2024 | 08:31 | MTB17 | SHORT RURAL | Unknown | Unknown | 1.00 | 364.0 | 0.002561 | 0.0000070 | No
19/06/2024 | 08:34 | MG05 | LONG RURAL | Planned |  | 2.00 | 226.0 | 0.003244 | 0.0000144 | No
19/06/2024 | 08:49 | VH16 | SHORT RURAL | Planned |  | 44.00 | 349.0 | 0.108037 | 0.0003096 | No
19/06/2024 | 08:58 | VH11 | URBAN | Network business | Switching and protection error | 3.00 | 83.0 | 0.000384 | 0.0000046 | No
19/06/2024 | 09:15 | W06 | LONG RURAL | Planned |  | 1.00 | 451.0 | 0.003237 | 0.0000072 | No
19/06/2024 | 09:20 | HH145E | URBAN | Planned |  | 118.00 | 231.7 | 0.042155 | 0.0001819 | No
19/06/2024 | 09:45 | HH148D | URBAN | Asset failure | LV | 1.00 | 286.0 | 0.000441 | 0.0000015 | No
19/06/2024 | 09:48 | SA38 | URBAN | Unknown | Unknown | 2.00 | 517.0 | 0.001594 | 0.0000031 | No
19/06/2024 | 10:01 | SM411D | URBAN | Asset failure | LV | 1.00 | 309.0 | 0.000476 | 0.0000015 | No
19/06/2024 | 10:24 | NL111B | URBAN | Asset failure | LV | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
19/06/2024 | 10:36 | HH428D | URBAN | Asset failure | LV | 1.00 | 250.0 | 0.000385 | 0.0000015 | No
19/06/2024 | 10:48 | CL28 | LONG RURAL | Planned |  | 72.00 | 232.0 | 0.119873 | 0.0005167 | No
19/06/2024 | 11:06 | WK31 | SHORT RURAL | Planned |  | 1.00 | 279.0 | 0.001963 | 0.0000070 | No
19/06/2024 | 12:20 | AP146B | URBAN | Vegetation | Blow-in/Fall-in - NSP responsibility | 40.00 | 350.1 | 0.021591 | 0.0000617 | No
19/06/2024 | 12:28 | SA14 | URBAN | Unknown | Unknown | 1.00 | 72.0 | 0.000111 | 0.0000015 | No
19/06/2024 | 12:35 | VH31 | SHORT RURAL | Unknown | Unknown | 1.00 | 120.0 | 0.000844 | 0.0000070 | No
19/06/2024 | 12:41 | W04 | LONG RURAL | Overloads |  | 2.00 | 275.0 | 0.003947 | 0.0000144 | No
19/06/2024 | 12:42 | VH11 | URBAN | Planned |  | 3.00 | 158.0 | 0.000731 | 0.0000046 | No
19/06/2024 | 12:59 | AP146B | URBAN | Asset failure | LV | 1.00 | 130.0 | 0.000200 | 0.0000015 | No
19/06/2024 | 13:13 | G05 | LONG RURAL | Asset failure | LV | 1.00 | 88.0 | 0.000632 | 0.0000072 | No
19/06/2024 | 14:00 | AP146B | URBAN | Third Party | Other | 1.00 | 65.0 | 0.000100 | 0.0000015 | No
19/06/2024 | 14:26 | SM410D | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 271.00 | 85.0 | 0.035514 | 0.0004178 | No
19/06/2024 | 14:46 | MV32 | SHORT RURAL | Unknown | Unknown | 1,946.00 | 235.9 | 3.229058 | 0.0136911 | No
19/06/2024 | 16:24 | LM43 | LONG RURAL | Asset failure | HV | 2.00 | 48.0 | 0.000689 | 0.0000144 | No
19/06/2024 | 17:57 | GA08 | LONG RURAL | Asset failure | LV | 10.67 | 171.0 | 0.013090 | 0.0000765 | No
19/06/2024 | 19:30 | SM126E | URBAN | Asset failure | LV | 24.33 | 78.0 | 0.002926 | 0.0000375 | No
19/06/2024 | 20:13 | MT01 | LONG RURAL | 7 - STPIS Exclusion (3.3)(a) |  | 10.00 | 24.0 | 0.001722 | 0.0000718 | No
19/06/2024 | 20:56 | HH341D | URBAN | Asset failure | LV | 2.00 | 225.0 | 0.000694 | 0.0000031 | No
19/06/2024 | 21:21 | EL09 | URBAN | Overloads |  | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
19/06/2024 | 21:49 | AP365D1 | URBAN | Planned |  | 4.00 | 237.0 | 0.001462 | 0.0000062 | No
19/06/2024 | 22:53 | AP829C | URBAN | Planned |  | 1.00 | 6.0 | 0.000009 | 0.0000015 | No
20/06/2024 | 06:13 | AP829D | URBAN | Network business | Switching and protection error | 1.00 | 6.0 | 0.000009 | 0.0000015 | No
20/06/2024 | 07:41 | HH428B | URBAN | Overloads |  | 2.00 | 519.0 | 0.001600 | 0.0000031 | No
20/06/2024 | 07:44 | NL760B | URBAN | Asset failure | LV | 1.00 | 120.0 | 0.000185 | 0.0000015 | No
20/06/2024 | 07:53 | HH496G | URBAN | Asset failure | LV | 1.00 | 473.0 | 0.000729 | 0.0000015 | No
20/06/2024 | 07:53 | HH409C | URBAN | Overloads |  | 39.00 | 80.6 | 0.004844 | 0.0000601 | No
20/06/2024 | 08:23 | HH341K | URBAN | Third Party | Other | 1.00 | 206.0 | 0.000318 | 0.0000015 | No
20/06/2024 | 08:40 | SD31100 | LONG RURAL | Planned |  | 2.00 | 305.0 | 0.004378 | 0.0000144 | No
20/06/2024 | 08:56 | MG44 | SHORT RURAL | Planned |  | 110.00 | 273.6 | 0.211740 | 0.0007739 | No
20/06/2024 | 08:56 | MG44 | URBAN | Planned |  | 133.00 | 326.2 | 0.066887 | 0.0002051 | No
20/06/2024 | 08:56 | BM54 | SHORT RURAL | Planned |  | 62.00 | 335.0 | 0.146127 | 0.0004362 | No
20/06/2024 | 09:00 | HH107D | URBAN | Planned |  | 80.00 | 282.0 | 0.034782 | 0.0001233 | No
20/06/2024 | 09:06 | HH121F | URBAN | Planned |  | 156.00 | 211.9 | 0.050966 | 0.0002405 | No
20/06/2024 | 09:08 | GU21 | LONG RURAL | Planned |  | 214.00 | 344.5 | 0.529068 | 0.0015357 | No
20/06/2024 | 09:10 | KA01 | SHORT RURAL | Weather |  | 75.00 | 84.0 | 0.044324 | 0.0005277 | No
20/06/2024 | 09:13 | MG04 | SHORT RURAL | Planned |  | 277.00 | 308.0 | 0.600240 | 0.0019488 | No
20/06/2024 | 09:32 | HH148B | URBAN | Planned |  | 118.00 | 225.6 | 0.041035 | 0.0001819 | No
20/06/2024 | 09:54 | G17 | LONG RURAL | Asset failure | LV | 8.00 | 244.0 | 0.014008 | 0.0000574 | No
20/06/2024 | 10:02 | ME347C | URBAN | Asset failure | LV | 44.67 | 193.0 | 0.013291 | 0.0000689 | No
20/06/2024 | 10:04 | MG48 | LONG RURAL | Asset failure | HV | 12.00 | 63.0 | 0.005425 | 0.0000861 | No
20/06/2024 | 10:04 | NA57 | LONG RURAL | Unknown | Unknown | 4.00 | 240.0 | 0.006889 | 0.0000287 | No
20/06/2024 | 10:13 | HH118D | URBAN | Asset failure | LV | 26.00 | 166.0 | 0.006654 | 0.0000401 | No
20/06/2024 | 10:32 | BM52 | URBAN | Asset failure | LV | 1.00 | 337.0 | 0.000520 | 0.0000015 | No
20/06/2024 | 10:46 | KI42 | LONG RURAL | Planned |  | 2.00 | 140.0 | 0.002009 | 0.0000144 | No
20/06/2024 | 11:03 | R17 | LONG RURAL | Planned |  | 70.00 | 210.0 | 0.105492 | 0.0005023 | No
20/06/2024 | 12:47 | PP03 | URBAN | Asset failure | LV | 1.00 | 345.0 | 0.000532 | 0.0000015 | No
20/06/2024 | 13:22 | HH121F | URBAN | Asset failure | LV | 21.67 | 37.0 | 0.001236 | 0.0000334 | No
20/06/2024 | 13:43 | MI06 | LONG RURAL | Planned |  | 2.00 | 43.0 | 0.000617 | 0.0000144 | No
20/06/2024 | 14:01 | GA50 | URBAN | Overloads |  | 1.00 | 699.0 | 0.001078 | 0.0000015 | No
20/06/2024 | 14:38 | WHY01 | SHORT RURAL | Overloads |  | 1.00 | 44.0 | 0.000310 | 0.0000070 | No
20/06/2024 | 14:40 | KA05 | LONG RURAL | Overloads |  | 1.00 | 29.0 | 0.000208 | 0.0000072 | No
20/06/2024 | 15:29 | AP425C | URBAN | Asset failure | LV | 1.00 | 541.0 | 0.000834 | 0.0000015 | No
20/06/2024 | 15:49 | ST42 | LONG RURAL | Weather |  | 11.67 | 64.0 | 0.005358 | 0.0000837 | No
20/06/2024 | 16:04 | HH428F | URBAN | Unknown | Unknown | 1.00 | 96.0 | 0.000148 | 0.0000015 | No
20/06/2024 | 16:37 | G29 | LONG RURAL | Asset failure | LV | 2.00 | 1,149.0 | 0.016491 | 0.0000144 | No
20/06/2024 | 17:25 | SM411E | URBAN | Asset failure | HV | 77.00 | 422.5 | 0.050161 | 0.0001187 | No
20/06/2024 | 17:48 | HH177G | URBAN | Overloads |  | 1.00 | 707.0 | 0.001090 | 0.0000015 | No
20/06/2024 | 18:08 | HH121F | URBAN | Asset failure | LV | 21.67 | 273.0 | 0.009119 | 0.0000334 | No
20/06/2024 | 18:20 | AP146B | URBAN | Overloads |  | 1.00 | 310.0 | 0.000478 | 0.0000015 | No
20/06/2024 | 18:30 | MTB12 | SHORT RURAL | Asset failure | LV | 1.00 | 225.0 | 0.001583 | 0.0000070 | No
20/06/2024 | 18:49 | EL01Q | URBAN | Asset failure | HV | 34.00 | 86.9 | 0.004557 | 0.0000524 | No
20/06/2024 | 19:15 | AP214D | URBAN | Overloads |  | 3.00 | 288.0 | 0.001332 | 0.0000046 | No
20/06/2024 | 19:26 | EL01Y | URBAN | Asset failure | HV | 36.00 | 536.0 | 0.029750 | 0.0000555 | No
20/06/2024 | 19:26 | EL01Y | URBAN | Asset failure | HV | 53.00 | 58.1 | 0.004750 | 0.0000817 | No
20/06/2024 | 19:31 | MTB52 | LONG RURAL | Overloads |  | 1.00 | 164.0 | 0.001177 | 0.0000072 | No
20/06/2024 | 21:58 | CD03 | LONG RURAL | Planned |  | 861.00 | 241.0 | 1.489096 | 0.0061788 | No
20/06/2024 | 21:58 | CD03 | SHORT RURAL | Planned |  | 1,400.00 | 241.0 | 2.373775 | 0.0098497 | No
20/06/2024 | 23:06 | SD44400 | SHORT RURAL | Planned |  | 64.00 | 298.8 | 0.134554 | 0.0004503 | No
21/06/2024 | 03:06 | CM26 | LONG RURAL | Unknown | Unknown | 2.00 | 111.0 | 0.001593 | 0.0000144 | No
21/06/2024 | 04:23 | SA744D | URBAN | Asset failure | LV | 19.00 | 7.0 | 0.000205 | 0.0000293 | No
21/06/2024 | 04:37 | SA744D | URBAN | Overloads |  | 19.00 | 587.0 | 0.017195 | 0.0000293 | No
21/06/2024 | 08:25 | HH145E | URBAN | Asset failure | LV | 1.00 | 222.0 | 0.000342 | 0.0000015 | No
21/06/2024 | 08:29 | MB13 | SHORT RURAL | Unknown | Unknown | 11.00 | 96.0 | 0.007429 | 0.0000774 | No
21/06/2024 | 08:34 | PP10 | URBAN | Asset failure | LV | 1.00 | 566.0 | 0.000873 | 0.0000015 | No
21/06/2024 | 08:45 | LX24 | SHORT RURAL | Asset failure | LV | 2.00 | 145.0 | 0.002040 | 0.0000141 | No
21/06/2024 | 08:52 | AP227C | URBAN | Planned |  | 1.00 | 360.0 | 0.000555 | 0.0000015 | No
21/06/2024 | 09:06 | SG13 | SHORT RURAL | Planned |  | 52.00 | 243.0 | 0.088900 | 0.0003658 | No
21/06/2024 | 09:08 | NL111A | URBAN | Planned |  | 65.00 | 310.0 | 0.031066 | 0.0001002 | No
21/06/2024 | 09:33 | BT02 | LONG RURAL | Planned |  | 510.00 | 32.7 | 0.119672 | 0.0036599 | No
21/06/2024 | 09:34 | SB17 | LONG RURAL | Planned |  | 99.00 | 197.0 | 0.139960 | 0.0007105 | No
21/06/2024 | 09:42 | HH121F | URBAN | Planned |  | 117.00 | 275.2 | 0.049643 | 0.0001804 | No
21/06/2024 | 09:43 | EL01L | URBAN | Asset failure | LV | 1.00 | 863.0 | 0.001331 | 0.0000015 | No
21/06/2024 | 09:53 | CL05 | LONG RURAL | Planned |  | 67.00 | 228.0 | 0.109626 | 0.0004808 | No
21/06/2024 | 10:01 | NA27 | LONG RURAL | Planned |  | 2.00 | 93.0 | 0.001335 | 0.0000144 | No
21/06/2024 | 10:26 | WK42 | SHORT RURAL | Planned |  | 5.00 | 81.0 | 0.002849 | 0.0000352 | No
21/06/2024 | 10:38 | SM137B | URBAN | Third Party | Other | 38.00 | 71.0 | 0.004160 | 0.0000586 | No
21/06/2024 | 10:40 | NU16 | LONG RURAL | Other |  | 20.00 | 174.0 | 0.024974 | 0.0001435 | No
21/06/2024 | 10:47 | HH148A | URBAN | Third Party | Vehicle impact | 633.00 | 49.2 | 0.047981 | 0.0009759 | No
21/06/2024 | 10:48 | ST42 | LONG RURAL | Asset failure | LV | 13.00 | 391.0 | 0.036477 | 0.0000933 | No
21/06/2024 | 11:04 | MB13 | SHORT RURAL | Unknown | Unknown | 1.00 | 76.0 | 0.000535 | 0.0000070 | No
21/06/2024 | 12:01 | MV11 | SHORT RURAL | Asset failure | LV | 7.00 | 216.0 | 0.010638 | 0.0000492 | No
21/06/2024 | 12:27 | R18 | LONG RURAL | Asset failure | LV | 2.00 | 420.0 | 0.006028 | 0.0000144 | No
21/06/2024 | 13:08 | W04 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 15.00 | 469.0 | 0.050485 | 0.0001076 | No
21/06/2024 | 13:38 | NU06 | LONG RURAL | Unknown | Unknown | 1.00 | 86.0 | 0.000617 | 0.0000072 | No
21/06/2024 | 13:57 | SD32400 | LONG RURAL | Asset failure | Subtransmission | 2.00 | 221.0 | 0.003172 | 0.0000144 | No
21/06/2024 | 14:20 | MB12 | SHORT RURAL | Asset failure | LV | 1.00 | 167.0 | 0.001175 | 0.0000070 | No
21/06/2024 | 14:31 | CL05 | LONG RURAL | Asset failure | LV | 9.00 | 259.4 | 0.016757 | 0.0000646 | No
21/06/2024 | 14:53 | EL01R | URBAN | Asset failure | LV | 14.00 | 237.0 | 0.005116 | 0.0000216 | No
21/06/2024 | 15:13 | HH432C | URBAN | Asset failure | LV | 1.00 | 129.0 | 0.000199 | 0.0000015 | No
21/06/2024 | 15:45 | NL111Q | URBAN | Asset failure | LV | 44.00 | 114.0 | 0.007733 | 0.0000678 | No
21/06/2024 | 16:10 | MTB62 | SHORT RURAL | Asset failure | LV | 1.00 | 48.0 | 0.000338 | 0.0000070 | No
21/06/2024 | 17:34 | CD19 | LONG RURAL | Asset failure | HV | 1.00 | 90.0 | 0.000646 | 0.0000072 | No
21/06/2024 | 17:52 | VH18 | SHORT RURAL | Asset failure | LV | 2.00 | 302.0 | 0.004249 | 0.0000141 | No
21/06/2024 | 17:53 | SA36 | URBAN | Unknown | Unknown | 2.00 | 261.0 | 0.000805 | 0.0000031 | No
21/06/2024 | 18:27 | SM216B | URBAN | Overloads |  | 32.67 | 157.0 | 0.007907 | 0.0000504 | No
21/06/2024 | 18:47 | HH386F | URBAN | Asset failure | LV | 18.67 | 326.0 | 0.009382 | 0.0000288 | No
21/06/2024 | 19:10 | SM126D | URBAN | Unknown | Unknown | 2.00 | 84.0 | 0.000259 | 0.0000031 | No
21/06/2024 | 19:41 | HH177G | URBAN | Asset failure | LV | 1.00 | 317.0 | 0.000489 | 0.0000015 | No
21/06/2024 | 19:54 | EL01L | URBAN | Asset failure | LV | 1.00 | 197.0 | 0.000304 | 0.0000015 | No
21/06/2024 | 20:48 | AP226E | URBAN | Overloads |  | 4.00 | 352.0 | 0.002171 | 0.0000062 | No
21/06/2024 | 22:14 | ME347C | URBAN | Overloads |  | 1.00 | 248.0 | 0.000382 | 0.0000015 | No
21/06/2024 | 23:12 | CBD353E | CBD | Asset failure | HV | 155.00 | 69.1 | 1.548219 | 0.0223940 | No
22/06/2024 | 01:58 | SM411F | URBAN | Overloads |  | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
22/06/2024 | 06:59 | CBD353E | CBD | Asset failure | HV | 1.00 | 448.0 | 0.064726 | 0.0001445 | No
22/06/2024 | 07:33 | HH341C | URBAN | Asset failure | LV | 75.00 | 277.0 | 0.032030 | 0.0001156 | No
22/06/2024 | 07:52 | SA744D | URBAN | Asset failure | LV | 12.33 | 599.0 | 0.011390 | 0.0000190 | No
22/06/2024 | 07:53 | SM126D | URBAN | Asset failure | LV | 1.00 | 173.0 | 0.000267 | 0.0000015 | No
22/06/2024 | 08:06 | EL20 | URBAN | Animal | Animal impact | 1,367.00 | 55.7 | 0.117471 | 0.0021076 | No
22/06/2024 | 08:27 | SA12 | URBAN | Planned |  | 1.00 | 202.0 | 0.000311 | 0.0000015 | No
22/06/2024 | 09:36 | NA35 | SHORT RURAL | Planned |  | 24.00 | 219.0 | 0.036979 | 0.0001689 | No
22/06/2024 | 09:54 | AP149H | URBAN | Asset failure | LV | 1.00 | 284.0 | 0.000438 | 0.0000015 | No
22/06/2024 | 11:04 | EL17 | URBAN | Animal | Animal impact | 1,041.00 | 69.6 | 0.111756 | 0.0016050 | No
22/06/2024 | 11:16 | EL17 | URBAN | Unknown | Unknown | 38.00 | 133.5 | 0.007820 | 0.0000586 | No
22/06/2024 | 12:31 | WHY10 | URBAN | Overloads |  | 1.00 | 50.0 | 0.000077 | 0.0000015 | No
22/06/2024 | 12:37 | M13 | LONG RURAL | Asset failure | LV | 1.00 | 211.0 | 0.001514 | 0.0000072 | No
22/06/2024 | 12:49 | SM411E | URBAN | Asset failure | LV | 78.00 | 65.6 | 0.007889 | 0.0001203 | No
22/06/2024 | 14:08 | AP424C | URBAN | Asset failure | LV | 1.00 | 181.0 | 0.000279 | 0.0000015 | No
22/06/2024 | 14:33 | MTB21 | SHORT RURAL | Overloads |  | 1.00 | 95.0 | 0.000668 | 0.0000070 | No
22/06/2024 | 14:59 | SA31 | URBAN | Asset failure | LV | 14.00 | 1,249.0 | 0.026959 | 0.0000216 | No
22/06/2024 | 17:34 | HH341J | URBAN | Unknown | Unknown | 1.00 | 315.0 | 0.000486 | 0.0000015 | No
22/06/2024 | 19:20 | VH22 | SHORT RURAL | Third Party | Vehicle impact | 1.00 | 119.0 | 0.000837 | 0.0000070 | No
22/06/2024 | 19:56 | NU02 | LONG RURAL | Overloads |  | 1.00 | 271.0 | 0.001945 | 0.0000072 | No
22/06/2024 | 20:14 | EL16 | URBAN | Third Party | Vehicle impact | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
22/06/2024 | 22:28 | SM402D | URBAN | Asset failure | LV | 18.67 | 154.0 | 0.004432 | 0.0000288 | No
23/06/2024 | 04:00 | HH429B | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
23/06/2024 | 05:41 | HH148A | URBAN | Asset failure | LV | 1.00 | 141.0 | 0.000217 | 0.0000015 | No
23/06/2024 | 07:33 | SM349F | URBAN | Asset failure | LV | 1.00 | 340.0 | 0.000524 | 0.0000015 | No
23/06/2024 | 08:20 | CV07 | SHORT RURAL | Planned |  | 18.00 | 453.0 | 0.057367 | 0.0001266 | No
23/06/2024 | 08:25 | HH177D | URBAN | Vegetation | Grow-in - NSP responsibility | 75.00 | 120.0 | 0.013876 | 0.0001156 | No
23/06/2024 | 08:42 | HH177A | URBAN | Planned |  | 23.00 | 139.3 | 0.004940 | 0.0000355 | No
23/06/2024 | 08:46 | EL23 | URBAN | Planned |  | 61.00 | 400.0 | 0.037619 | 0.0000940 | No
23/06/2024 | 08:48 | SD47200 | URBAN | Planned |  | 2.00 | 362.0 | 0.001116 | 0.0000031 | No
23/06/2024 | 09:18 | HH177G | URBAN | Asset failure | LV | 1.00 | 140.0 | 0.000216 | 0.0000015 | No
23/06/2024 | 09:31 | SD32400 | LONG RURAL | Overloads |  | 2.00 | 152.0 | 0.002182 | 0.0000144 | No
23/06/2024 | 11:41 | HH107C | URBAN | Asset failure | LV | 3.33 | 648.0 | 0.003330 | 0.0000051 | No
23/06/2024 | 12:33 | AP424F | URBAN | Asset failure | LV | 1.00 | 321.0 | 0.000495 | 0.0000015 | No
23/06/2024 | 15:28 | GA08 | LONG RURAL | Asset failure | HV | 32.00 | 30.0 | 0.006889 | 0.0002296 | No
23/06/2024 | 15:48 | AP529A | URBAN | Overloads |  | 3.00 | 248.0 | 0.001147 | 0.0000046 | No
23/06/2024 | 16:44 | HH121C | URBAN | Overloads |  | 13.67 | 256.0 | 0.005394 | 0.0000211 | No
23/06/2024 | 17:18 | MT22 | LONG RURAL | Asset failure | LV | 11.00 | 115.0 | 0.009078 | 0.0000789 | No
23/06/2024 | 18:01 | GA43 | SHORT RURAL | Overloads |  | 1.00 | 558.0 | 0.003926 | 0.0000070 | No
23/06/2024 | 18:17 | EL09 | URBAN | Overloads |  | 106.00 | 136.2 | 0.022254 | 0.0001634 | No
23/06/2024 | 18:58 | AP149F | URBAN | Asset failure | LV | 1.00 | 321.0 | 0.000495 | 0.0000015 | No
23/06/2024 | 20:20 | NU21 | LONG RURAL | Planned |  | 115.00 | 352.0 | 0.290498 | 0.0008253 | No
23/06/2024 | 20:58 | SM402B | URBAN | Unknown | Unknown | 1.00 | 37.0 | 0.000057 | 0.0000015 | No
23/06/2024 | 23:44 | KA14 | LONG RURAL | Asset failure | HV | 79.00 | 474.1 | 0.268804 | 0.0005669 | No
24/06/2024 | 00:14 | SA14 | URBAN | Overloads |  | 1.00 | 260.0 | 0.000401 | 0.0000015 | No
24/06/2024 | 04:13 | CBD367U | CBD | Planned |  | 8.00 | 4.0 | 0.004623 | 0.0011558 | No
24/06/2024 | 05:58 | ME231A | URBAN | Asset failure | LV | 1.00 | 185.0 | 0.000285 | 0.0000015 | No
24/06/2024 | 06:00 | PL803C | URBAN | Asset failure | LV | 1.00 | 313.0 | 0.000483 | 0.0000015 | No
24/06/2024 | 06:24 | ME231A | URBAN | Asset failure | LV | 31.67 | 158.0 | 0.007714 | 0.0000488 | No
24/06/2024 | 06:36 | AP355H | URBAN | Weather |  | 2,132.00 | 34.3 | 0.112813 | 0.0032870 | No
24/06/2024 | 07:34 | ME131A | URBAN | Asset failure | LV | 1.00 | 263.0 | 0.000405 | 0.0000015 | No
24/06/2024 | 07:43 | MI14 | LONG RURAL | Overloads |  | 20.33 | 249.0 | 0.036334 | 0.0001459 | No
24/06/2024 | 08:44 | AP425A | URBAN | Planned |  | 63.00 | 50.0 | 0.004857 | 0.0000971 | No
24/06/2024 | 08:48 | EL02 | URBAN | Asset failure | LV | 68.00 | 74.0 | 0.007758 | 0.0001048 | No
24/06/2024 | 08:56 | MG10 | LONG RURAL | Planned |  | 5.00 | 262.0 | 0.009401 | 0.0000359 | No
24/06/2024 | 09:08 | BM15 | SHORT RURAL | Planned |  | 5.00 | 142.0 | 0.004995 | 0.0000352 | No
24/06/2024 | 09:11 | HH118D | URBAN | Overloads |  | 1.00 | 170.0 | 0.000262 | 0.0000015 | No
24/06/2024 | 09:12 | CV16 | LONG RURAL | Planned |  | 53.00 | 293.1 | 0.111470 | 0.0003803 | No
24/06/2024 | 09:15 | ME116D | URBAN | Planned |  | 259.00 | 385.0 | 0.153736 | 0.0003993 | No
24/06/2024 | 10:04 | MI08 | LONG RURAL | Planned |  | 24.00 | 260.0 | 0.044780 | 0.0001722 | No
24/06/2024 | 10:16 | WHY01 | SHORT RURAL | Asset failure | LV | 2.00 | 169.0 | 0.002378 | 0.0000141 | No
24/06/2024 | 10:47 | EL09 | URBAN | Overloads |  | 1.00 | 247.0 | 0.000381 | 0.0000015 | No
24/06/2024 | 13:20 | SM179D | URBAN | Asset failure | LV | 1.00 | 246.0 | 0.000379 | 0.0000015 | No
24/06/2024 | 13:23 | AP125A | URBAN | Network business | Switching and protection error | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
24/06/2024 | 13:32 | SA14 | URBAN | Asset failure | LV | 33.00 | 225.0 | 0.011448 | 0.0000509 | No
24/06/2024 | 14:35 | NA13 | LONG RURAL | Planned |  | 2.00 | 66.0 | 0.000947 | 0.0000144 | No
24/06/2024 | 14:57 | M23 | LONG RURAL | Unknown | Unknown | 1.00 | 400.0 | 0.002871 | 0.0000072 | No
24/06/2024 | 15:19 | WHY06 | URBAN | Overloads |  | 1.00 | 89.0 | 0.000137 | 0.0000015 | No
24/06/2024 | 15:34 | MI10 | LONG RURAL | Weather |  | 47.00 | 982.1 | 0.331252 | 0.0003373 | No
24/06/2024 | 15:58 | NL111P | URBAN | Weather |  | 68.67 | 215.0 | 0.022760 | 0.0001059 | No
24/06/2024 | 16:10 | HH121B | URBAN | Asset failure | LV | 16.00 | 46.0 | 0.001135 | 0.0000247 | No
24/06/2024 | 17:26 | AP125D | URBAN | Asset failure | LV | 20.00 | 187.0 | 0.005766 | 0.0000308 | No
24/06/2024 | 17:27 | ME116C | URBAN | Asset failure | LV | 2.00 | 95.0 | 0.000293 | 0.0000031 | No
24/06/2024 | 18:12 | SM349F | URBAN | Asset failure | LV | 1.00 | 167.0 | 0.000257 | 0.0000015 | No
24/06/2024 | 18:50 | NL234C | URBAN | Asset failure | LV | 29.67 | 140.0 | 0.006403 | 0.0000457 | No
24/06/2024 | 20:16 | LM33 | LONG RURAL | Unknown | Unknown | 2.00 | 410.0 | 0.005885 | 0.0000144 | No
24/06/2024 | 20:44 | ME347C | URBAN | Asset failure | LV | 44.67 | 145.0 | 0.009985 | 0.0000689 | No
24/06/2024 | 20:49 | HH341J | URBAN | Asset failure | LV | 1.00 | 49.0 | 0.000076 | 0.0000015 | No
24/06/2024 | 22:23 | CBD366G | CBD | Planned |  | 1.00 | 270.0 | 0.039009 | 0.0001445 | No
24/06/2024 | 22:35 | VH12 | SHORT RURAL | Planned |  | 140.00 | 336.3 | 0.331224 | 0.0009850 | No
24/06/2024 | 23:24 | AP139D | URBAN | Asset failure | LV | 42.00 | 103.0 | 0.006670 | 0.0000648 | No
24/06/2024 | 23:39 | AP372F | URBAN | Planned |  | 1.00 | 293.0 | 0.000452 | 0.0000015 | No
25/06/2024 | 03:28 | R10 | LONG RURAL | Asset failure | HV | 70.00 | 424.0 | 0.212993 | 0.0005023 | No
25/06/2024 | 03:58 | SM374E | URBAN | Vegetation | Blow-in/Fall-in - Other responsible party | 496.00 | 113.1 | 0.086455 | 0.0007647 | No
25/06/2024 | 05:13 | NL234E | URBAN | Asset failure | HV | 2,635.00 | 109.7 | 0.445834 | 0.0040625 | No
25/06/2024 | 06:52 | EL260C | URBAN | Third Party | Vehicle impact | 48.00 | 535.0 | 0.039592 | 0.0000740 | No
25/06/2024 | 07:14 | HH429B | URBAN | Asset failure | LV | 1.00 | 327.0 | 0.000504 | 0.0000015 | No
25/06/2024 | 08:28 | CV02 | LONG RURAL | Planned |  | 2.00 | 390.0 | 0.005598 | 0.0000144 | No
25/06/2024 | 08:42 | NL511A | URBAN | Asset failure | LV | 1.00 | 135.0 | 0.000208 | 0.0000015 | No
25/06/2024 | 08:49 | MG04 | SHORT RURAL | Planned |  | 1.00 | 86.0 | 0.000605 | 0.0000070 | No
25/06/2024 | 09:01 | SD48100 | SHORT RURAL | Planned |  | 13.00 | 383.0 | 0.035030 | 0.0000915 | No
25/06/2024 | 09:12 | SD33100 | LONG RURAL | Planned |  | 14.00 | 291.0 | 0.029236 | 0.0001005 | No
25/06/2024 | 09:14 | HH121C | URBAN | Planned |  | 178.00 | 150.2 | 0.041208 | 0.0002744 | No
25/06/2024 | 09:19 | NU14 | LONG RURAL | Planned |  | 1.00 | 131.0 | 0.000940 | 0.0000072 | No
25/06/2024 | 09:20 | ST42 | LONG RURAL | Planned |  | 12.00 | 253.0 | 0.021787 | 0.0000861 | No
25/06/2024 | 09:24 | PA13 | LONG RURAL | Planned |  | 56.00 | 283.0 | 0.113730 | 0.0004019 | No
25/06/2024 | 09:24 | SM216C | URBAN | Planned |  | 78.00 | 129.0 | 0.015513 | 0.0001203 | No
25/06/2024 | 09:33 | AP214C | URBAN | Planned |  | 65.00 | 178.0 | 0.017838 | 0.0001002 | No
25/06/2024 | 10:01 | CD18 | LONG RURAL | Planned |  | 2.00 | 62.0 | 0.000890 | 0.0000144 | No
25/06/2024 | 10:03 | MI08 | LONG RURAL | Planned |  | 3.00 | 211.0 | 0.004543 | 0.0000215 | No
25/06/2024 | 10:05 | SG02 | SHORT RURAL | Asset failure | LV | 1.00 | 152.0 | 0.001069 | 0.0000070 | No
25/06/2024 | 10:34 | LM32 | LONG RURAL | Planned |  | 14.00 | 149.0 | 0.014970 | 0.0001005 | No
25/06/2024 | 10:40 | NA13 | LONG RURAL | Overloads |  | 1.00 | 286.0 | 0.002052 | 0.0000072 | No
25/06/2024 | 11:04 | NL760B | URBAN | Asset failure | LV | 1.00 | 72.0 | 0.000111 | 0.0000015 | No
25/06/2024 | 11:45 | MV13 | SHORT RURAL | Asset failure | LV | 2.00 | 488.0 | 0.006867 | 0.0000141 | No
25/06/2024 | 12:30 | SM374A | URBAN | Unknown | Unknown | 32.67 | 101.0 | 0.005087 | 0.0000504 | No
25/06/2024 | 12:34 | SA18 | URBAN | Asset failure | LV | 1.00 | 116.0 | 0.000179 | 0.0000015 | No
25/06/2024 | 12:50 | GA30 | LONG RURAL | Overloads |  | 1.00 | 182.0 | 0.001306 | 0.0000072 | No
25/06/2024 | 14:30 | M13 | LONG RURAL | Asset failure | LV | 41.00 | 108.0 | 0.031777 | 0.0002942 | No
25/06/2024 | 14:50 | NL451D | URBAN | Asset failure | LV | 1.00 | 88.0 | 0.000136 | 0.0000015 | No
25/06/2024 | 15:13 | HH522C | URBAN | Asset failure | LV | 2.00 | 101.0 | 0.000311 | 0.0000031 | No
25/06/2024 | 16:16 | GA01 | URBAN | Overloads |  | 20.00 | 157.0 | 0.004841 | 0.0000308 | No
25/06/2024 | 16:20 | BT13 | LONG RURAL | Unknown | Unknown | 74.00 | 315.0 | 0.167280 | 0.0005310 | No
25/06/2024 | 16:31 | SA744D | URBAN | Asset failure | LV | 2.00 | 29.0 | 0.000089 | 0.0000031 | No
25/06/2024 | 17:16 | SM349H | URBAN | Asset failure | LV | 1.00 | 336.0 | 0.000518 | 0.0000015 | No
25/06/2024 | 17:18 | ST34 | LONG RURAL | Overloads |  | 3.00 | 529.0 | 0.011389 | 0.0000215 | No
25/06/2024 | 17:31 | SM216C | URBAN | Asset failure | LV | 1.00 | 133.0 | 0.000205 | 0.0000015 | No
25/06/2024 | 17:45 | MTB32 | LONG RURAL | Unknown | Unknown | 47.00 | 383.0 | 0.129181 | 0.0003373 | No
25/06/2024 | 18:03 | NU15 | LONG RURAL | Asset failure | HV | 1.00 | 174.0 | 0.001249 | 0.0000072 | No
25/06/2024 | 18:07 | CBD103C | URBAN | Overloads |  | 4.00 | 158.0 | 0.000974 | 0.0000062 | No
25/06/2024 | 19:00 | HH429C | URBAN | Asset failure | LV | 25.67 | 116.0 | 0.004590 | 0.0000396 | No
25/06/2024 | 20:23 | NL111Q | URBAN | Asset failure | LV | 1.00 | 183.0 | 0.000282 | 0.0000015 | No
25/06/2024 | 20:39 | MTB32 | LONG RURAL | Planned |  | 186.00 | 9.0 | 0.012013 | 0.0013348 | No
25/06/2024 | 20:39 | MTB32 | LONG RURAL | Asset failure | HV | 476.00 | 9.0 | 0.030743 | 0.0034159 | No
25/06/2024 | 21:53 | NU02 | LONG RURAL | Asset failure | LV | 1.00 | 229.0 | 0.001643 | 0.0000072 | No
25/06/2024 | 22:03 | EL01Q | URBAN | Asset failure | HV | 8.00 | 96.0 | 0.001184 | 0.0000123 | No
25/06/2024 | 23:17 | SM179C | URBAN | Asset failure | LV | 105.00 | 48.0 | 0.007770 | 0.0001619 | No
25/06/2024 | 23:56 | AP146B | URBAN | Planned |  | 2.00 | 230.0 | 0.000709 | 0.0000031 | No
26/06/2024 | 06:29 | HH121F | URBAN | Asset failure | LV | 1.00 | 255.0 | 0.000393 | 0.0000015 | No
26/06/2024 | 07:18 | AP424B | URBAN | Asset failure | LV | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
26/06/2024 | 07:50 | EL01Q | URBAN | Asset failure | LV | 8.00 | 353.0 | 0.004354 | 0.0000123 | No
26/06/2024 | 08:36 | SM350F | URBAN | Overloads |  | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
26/06/2024 | 08:41 | BS0189 | SHORT RURAL | Planned |  | 1.00 | 139.0 | 0.000978 | 0.0000070 | No
26/06/2024 | 08:51 | SM410C | URBAN | Overloads |  | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
26/06/2024 | 08:55 | MI13 | LONG RURAL | Planned |  | 419.00 | 241.0 | 0.724752 | 0.0030069 | No
26/06/2024 | 08:57 | HH496C | URBAN | Planned |  | 87.00 | 360.3 | 0.048334 | 0.0001341 | No
26/06/2024 | 09:14 | KI56 | LONG RURAL | Planned |  | 77.00 | 342.5 | 0.189247 | 0.0005526 | No
26/06/2024 | 09:16 | NL234E | URBAN | Network business | Switching and protection error | 2.00 | 52.0 | 0.000160 | 0.0000031 | No
26/06/2024 | 09:21 | KI11 | LONG RURAL | Third Party | Vehicle impact | 1.00 | 108.0 | 0.000775 | 0.0000072 | No
26/06/2024 | 09:45 | KA31 | LONG RURAL | Planned |  | 2.00 | 46.0 | 0.000660 | 0.0000144 | No
26/06/2024 | 10:13 | HH432F | URBAN | Asset failure | LV | 1.00 | 134.0 | 0.000207 | 0.0000015 | No
26/06/2024 | 10:40 | NL760B | URBAN | Overloads |  | 1.00 | 73.0 | 0.000113 | 0.0000015 | No
26/06/2024 | 10:42 | AP529E | URBAN | Asset failure | LV | 1.33 | 264.0 | 0.000543 | 0.0000021 | No
26/06/2024 | 10:54 | GU13 | LONG RURAL | Asset failure | LV | 1.00 | 171.0 | 0.001227 | 0.0000072 | No
26/06/2024 | 11:01 | W25 | LONG RURAL | Planned |  | 1.00 | 224.0 | 0.001607 | 0.0000072 | No
26/06/2024 | 11:26 | WK42 | SHORT RURAL | Weather |  | 37.00 | 69.4 | 0.018074 | 0.0002603 | No
26/06/2024 | 13:36 | SA744D | URBAN | Asset failure | LV | 1.00 | 424.0 | 0.000654 | 0.0000015 | No
26/06/2024 | 13:37 | NL234B | URBAN | Unknown | Unknown | 1.00 | 210.0 | 0.000324 | 0.0000015 | No
26/06/2024 | 13:40 | CV08 | LONG RURAL | Asset failure | LV | 1.00 | 291.0 | 0.002088 | 0.0000072 | No
26/06/2024 | 15:33 | EL01Q | URBAN | Asset failure | LV | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
26/06/2024 | 15:37 | AP529E | URBAN | Asset failure | LV | 1.00 | 580.0 | 0.000894 | 0.0000015 | No
26/06/2024 | 15:48 | SA744D | URBAN | Asset failure | LV | 1.00 | 272.0 | 0.000419 | 0.0000015 | No
26/06/2024 | 15:51 | MV13 | SHORT RURAL | Unknown | Unknown | 4.33 | 67.0 | 0.002043 | 0.0000305 | No
26/06/2024 | 16:53 | AP529E | URBAN | Asset failure | LV | 1.33 | 399.0 | 0.000820 | 0.0000021 | No
26/06/2024 | 17:10 | EL260B | URBAN | Asset failure | HV | 2,643.00 | 24.7 | 0.100464 | 0.0040749 | No
26/06/2024 | 17:41 | AP529E | URBAN | Asset failure | LV | 1.00 | 301.0 | 0.000464 | 0.0000015 | No
26/06/2024 | 17:53 | SM179C | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
26/06/2024 | 18:24 | HH130D | URBAN | Asset failure | LV | 28.00 | 31.0 | 0.001338 | 0.0000432 | No
26/06/2024 | 19:21 | CN25 | LONG RURAL | Asset failure | HV | 1.00 | 50.0 | 0.000359 | 0.0000072 | No
26/06/2024 | 21:32 | ST34 | LONG RURAL | Weather |  | 490.00 | 6.0 | 0.021098 | 0.0035164 | No
26/06/2024 | 21:32 | ST34 | SHORT RURAL | Weather |  | 1,103.00 | 272.8 | 2.117148 | 0.0077601 | No
26/06/2024 | 21:44 | MB12 | SHORT RURAL | Planned |  | 5.00 | 381.0 | 0.013403 | 0.0000352 | No
26/06/2024 | 21:49 | ST11 | SHORT RURAL | Asset failure | LV | 4.00 | 277.0 | 0.007795 | 0.0000281 | No
27/06/2024 | 02:24 | GA02 | SHORT RURAL | Weather |  | 56.00 | 29.0 | 0.011426 | 0.0003940 | No
27/06/2024 | 02:57 | SA744D | URBAN | Asset failure | LV | 58.00 | 122.0 | 0.010909 | 0.0000894 | No
27/06/2024 | 08:02 | PP08 | LONG RURAL | Planned |  | 101.00 | 326.0 | 0.236288 | 0.0007248 | No
27/06/2024 | 08:04 | MI08 | LONG RURAL | Planned |  | 288.00 | 486.8 | 1.006057 | 0.0020668 | No
27/06/2024 | 08:19 | LX63 | LONG RURAL | Asset failure | LV | 1.00 | 430.0 | 0.003086 | 0.0000072 | No
27/06/2024 | 08:28 | ME131D | URBAN | Asset failure | LV | 1.00 | 614.0 | 0.000947 | 0.0000015 | No
27/06/2024 | 08:55 | KI31 | SHORT RURAL | Planned |  | 5.00 | 371.2 | 0.013058 | 0.0000352 | No
27/06/2024 | 08:56 | GA53 | URBAN | Planned |  | 689.00 | 20.0 | 0.021245 | 0.0010623 | No
27/06/2024 | 09:04 | SM410D | URBAN | Planned |  | 137.00 | 316.0 | 0.066746 | 0.0002112 | No
27/06/2024 | 09:07 | VH15 | SHORT RURAL | Planned |  | 13.00 | 325.4 | 0.029760 | 0.0000915 | No
27/06/2024 | 09:12 | MTB12 | SHORT RURAL | Planned |  | 3.00 | 273.0 | 0.005762 | 0.0000211 | No
27/06/2024 | 09:13 | AP425A | URBAN | Asset failure | LV | 1.00 | 94.0 | 0.000145 | 0.0000015 | No
27/06/2024 | 09:16 | YK02 | SHORT RURAL | Planned |  | 119.00 | 314.4 | 0.263233 | 0.0008372 | No
27/06/2024 | 09:16 | SM410D | URBAN | Other |  | 3.00 | 201.0 | 0.000930 | 0.0000046 | No
27/06/2024 | 09:33 | BU05 | LONG RURAL | Asset failure | LV | 1.00 | 471.0 | 0.003380 | 0.0000072 | No
27/06/2024 | 09:36 | EL23 | URBAN | Planned |  | 24.00 | 361.0 | 0.013358 | 0.0000370 | No
27/06/2024 | 09:45 | HH496F | URBAN | Asset failure | LV | 1.00 | 538.0 | 0.000829 | 0.0000015 | No
27/06/2024 | 09:56 | HH177F | URBAN | Planned |  | 29.00 | 126.0 | 0.005634 | 0.0000447 | No
27/06/2024 | 10:09 | SA711C | URBAN | Asset failure | LV | 43.00 | 68.0 | 0.004508 | 0.0000663 | No
27/06/2024 | 10:17 | GA22 | SHORT RURAL | Planned |  | 125.00 | 194.0 | 0.170611 | 0.0008794 | No
27/06/2024 | 10:57 | KI31 | SHORT RURAL | Planned |  | 1.00 | 266.0 | 0.001871 | 0.0000070 | No
27/06/2024 | 11:34 | HH145A | URBAN | Asset failure | LV | 1.00 | 151.0 | 0.000233 | 0.0000015 | No
27/06/2024 | 11:44 | NL115F | URBAN | Asset failure | LV | 1.00 | 193.0 | 0.000298 | 0.0000015 | No
27/06/2024 | 11:56 | ST51 | SHORT RURAL | Asset failure | LV | 3.00 | 198.0 | 0.004179 | 0.0000211 | No
27/06/2024 | 11:59 | CBD412B | URBAN | Unknown | Unknown | 1.00 | 91.0 | 0.000140 | 0.0000015 | No
27/06/2024 | 12:17 | MI29 | SHORT RURAL | Third Party | Vehicle impact | 8.00 | 32.0 | 0.001801 | 0.0000563 | No
27/06/2024 | 12:23 | HH496C | URBAN | Asset failure | LV | 11.00 | 462.0 | 0.007835 | 0.0000170 | No
27/06/2024 | 13:10 | SM402D | URBAN | Third Party | Vehicle impact | 1.00 | 107.0 | 0.000165 | 0.0000015 | No
27/06/2024 | 14:03 | PL25 | LONG RURAL | Weather |  | 70.00 | 57.0 | 0.028634 | 0.0005023 | No
27/06/2024 | 14:53 | MG07 | SHORT RURAL | Asset failure | LV | 34.00 | 83.1 | 0.019889 | 0.0002392 | No
27/06/2024 | 14:58 | EL25 | URBAN | Asset failure | LV | 14.00 | 779.0 | 0.016814 | 0.0000216 | No
27/06/2024 | 14:58 | EL25 | URBAN | Planned |  | 676.00 | 23.0 | 0.023971 | 0.0010422 | No
27/06/2024 | 15:07 | PP02 | URBAN | Asset failure | LV | 24.67 | 107.0 | 0.004069 | 0.0000380 | No
27/06/2024 | 15:33 | MG17 | LONG RURAL | Asset failure | LV | 7.00 | 326.0 | 0.016376 | 0.0000502 | No
27/06/2024 | 15:39 | G42 | LONG RURAL | Asset failure | HV | 17.00 | 62.0 | 0.007564 | 0.0001220 | No
27/06/2024 | 17:01 | HH102A | URBAN | Asset failure | LV | 61.00 | 63.0 | 0.005925 | 0.0000940 | No
27/06/2024 | 17:24 | ME231C | URBAN | Asset failure | LV | 11.00 | 293.0 | 0.004969 | 0.0000170 | No
27/06/2024 | 17:47 | CN42 | LONG RURAL | Other |  | 7.00 | 32.0 | 0.001607 | 0.0000502 | No
28/06/2024 | 01:04 | AP355A | URBAN | Asset failure | LV | 1.00 | 166.0 | 0.000256 | 0.0000015 | No
28/06/2024 | 06:16 | MV33 | SHORT RURAL | Asset failure | LV | 1.00 | 249.0 | 0.001752 | 0.0000070 | No
28/06/2024 | 06:46 | EL01N | URBAN | Asset failure | LV | 1.00 | 189.0 | 0.000291 | 0.0000015 | No
28/06/2024 | 06:46 | CD01 | SHORT RURAL | Asset failure | LV | 11.33 | 158.0 | 0.012598 | 0.0000797 | No
28/06/2024 | 07:03 | SM126A | URBAN | Unknown | Unknown | 44.67 | 137.0 | 0.009435 | 0.0000689 | No
28/06/2024 | 07:42 | SD37301 | SHORT RURAL | Weather |  | 92.00 | 132.4 | 0.085720 | 0.0006473 | No
28/06/2024 | 08:24 | MTB61 | SHORT RURAL | Planned |  | 103.00 | 175.0 | 0.126850 | 0.0007247 | No
28/06/2024 | 08:34 | HH409C | URBAN | Asset failure | LV | 39.00 | 27.0 | 0.001623 | 0.0000601 | No
28/06/2024 | 08:40 | NL111C | URBAN | Planned |  | 504.00 | 183.4 | 0.142489 | 0.0007770 | No
28/06/2024 | 08:58 | PL06 | URBAN | Planned |  | 47.00 | 291.0 | 0.021087 | 0.0000725 | No
28/06/2024 | 09:02 | NA12 | LONG RURAL | Planned |  | 6.00 | 96.0 | 0.004134 | 0.0000431 | No
28/06/2024 | 09:10 | HH341K | URBAN | Planned |  | 36.00 | 288.9 | 0.016037 | 0.0000555 | No
28/06/2024 | 09:11 | NU04 | SHORT RURAL | Planned |  | 5.00 | 309.8 | 0.010898 | 0.0000352 | No
28/06/2024 | 09:30 | MV31 | SHORT RURAL | Planned |  | 3.00 | 171.0 | 0.003609 | 0.0000211 | No
28/06/2024 | 09:32 | GA22 | SHORT RURAL | Planned |  | 26.00 | 198.3 | 0.036275 | 0.0001829 | No
28/06/2024 | 09:36 | SD34400 | LONG RURAL | Asset failure | Subtransmission | 1.00 | 261.0 | 0.001873 | 0.0000072 | No
28/06/2024 | 09:46 | MV34 | SHORT RURAL | Asset failure | LV | 1.00 | 276.0 | 0.001942 | 0.0000070 | No
28/06/2024 | 09:47 | NL21 | URBAN | Planned |  | 14.00 | 114.0 | 0.002461 | 0.0000216 | No
28/06/2024 | 09:57 | PP03 | URBAN | Planned |  | 476.00 | 59.7 | 0.043838 | 0.0007339 | No
28/06/2024 | 10:33 | MT14 | SHORT RURAL | Asset failure | HV | 75.00 | 526.9 | 0.278036 | 0.0005277 | No
28/06/2024 | 10:44 | NL210C | URBAN | Asset failure | LV | 1.00 | 385.0 | 0.000594 | 0.0000015 | No
28/06/2024 | 11:09 | NL111Q | URBAN | Asset failure | LV | 1.00 | 1,263.0 | 0.001947 | 0.0000015 | No
28/06/2024 | 11:52 | BM21 | SHORT RURAL | Third Party | Unauthorised access | 2.00 | 201.0 | 0.002828 | 0.0000141 | No
28/06/2024 | 12:17 | HH118E | URBAN | Third Party | Vehicle impact | 70.00 | 608.0 | 0.065617 | 0.0001079 | No
28/06/2024 | 13:04 | SM137B | URBAN | Asset failure | HV | 12.33 | 287.0 | 0.005457 | 0.0000190 | No
28/06/2024 | 13:25 | EL260C | URBAN | Asset failure | LV | 10.00 | 109.0 | 0.001681 | 0.0000154 | No
28/06/2024 | 14:12 | EL10 | URBAN | Asset failure | LV | 1.00 | 148.0 | 0.000228 | 0.0000015 | No
28/06/2024 | 14:36 | SA31 | URBAN | Unknown | Unknown | 47.00 | 233.0 | 0.016884 | 0.0000725 | No
28/06/2024 | 14:56 | AP344F | URBAN | Asset failure | LV | 33.00 | 310.0 | 0.015772 | 0.0000509 | No
28/06/2024 | 16:08 | SG03 | SHORT RURAL | Asset failure | LV | 1.00 | 106.0 | 0.000746 | 0.0000070 | No
28/06/2024 | 16:41 | HH102D | URBAN | Third Party | Vehicle impact | 39.00 | 88.0 | 0.005291 | 0.0000601 | No
28/06/2024 | 17:11 | MV13 | SHORT RURAL | Overloads |  | 4.33 | 192.0 | 0.005854 | 0.0000305 | No
28/06/2024 | 19:04 | VH21 | SHORT RURAL | Asset failure | LV | 1.00 | 83.0 | 0.000584 | 0.0000070 | No
28/06/2024 | 20:31 | MG05 | LONG RURAL | Weather |  | 137.00 | 126.6 | 0.124438 | 0.0009832 | No
28/06/2024 | 20:36 | MG05 | LONG RURAL | Weather |  | 1.00 | 170.0 | 0.001220 | 0.0000072 | No
28/06/2024 | 21:25 | PP10 | URBAN | Asset failure | LV | 30.00 | 68.0 | 0.003145 | 0.0000463 | No
28/06/2024 | 21:38 | EL25 | URBAN | Unknown | Unknown | 1.00 | 102.0 | 0.000157 | 0.0000015 | No
29/06/2024 | 03:32 | CBD103C | URBAN | Animal | Animal impact | 39.33 | 159.0 | 0.009642 | 0.0000606 | No
29/06/2024 | 03:52 | NL21 | URBAN | Overloads |  | 1.00 | 199.0 | 0.000307 | 0.0000015 | No
29/06/2024 | 04:31 | CM18 | LONG RURAL | Asset failure | HV | 651.00 | 188.0 | 0.878311 | 0.0046718 | No
29/06/2024 | 05:27 | YK02 | LONG RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 2,406.00 | 4.0 | 0.069065 | 0.0172662 | No
29/06/2024 | 05:27 | YK02 | SHORT RURAL | 5 - STPIS Exclusion (3.3)(a) |  | 824.00 | 4.0 | 0.023189 | 0.0057972 | No
29/06/2024 | 07:06 | NL760C | URBAN | Overloads |  | 1.00 | 618.0 | 0.000953 | 0.0000015 | No
29/06/2024 | 07:17 | MV13 | SHORT RURAL | Asset failure | LV | 13.00 | 488.0 | 0.044633 | 0.0000915 | No
29/06/2024 | 07:24 | MG22 | LONG RURAL | Weather |  | 1,044.00 | 53.8 | 0.403159 | 0.0074921 | No
29/06/2024 | 07:33 | ME427E | URBAN | Asset failure | LV | 1.00 | 277.0 | 0.000427 | 0.0000015 | No
29/06/2024 | 08:03 | HH145A | URBAN | Vegetation | Grow-in - NSP responsibility | 1.00 | 467.0 | 0.000720 | 0.0000015 | No
29/06/2024 | 08:39 | SM216E | URBAN | Asset failure | LV | 2.33 | 440.0 | 0.001583 | 0.0000036 | No
29/06/2024 | 09:08 | CD01 | SHORT RURAL | Planned |  | 58.00 | 330.0 | 0.134659 | 0.0004081 | No
29/06/2024 | 09:31 | SG03 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 558.0 | 0.003926 | 0.0000070 | No
29/06/2024 | 09:32 | HH403D | URBAN | Asset failure | LV | 8.00 | 288.0 | 0.003552 | 0.0000123 | No
29/06/2024 | 10:07 | NL544B | URBAN | Asset failure | LV | 97.00 | 95.0 | 0.014207 | 0.0001496 | No
29/06/2024 | 10:15 | SM216C | URBAN | Vegetation | Grow-in - NSP responsibility | 2.00 | 113.0 | 0.000348 | 0.0000031 | No
29/06/2024 | 10:40 | MG17 | LONG RURAL | Unknown | Unknown | 2.00 | 178.0 | 0.002555 | 0.0000144 | No
29/06/2024 | 11:32 | AP149C | URBAN | Asset failure | LV | 1.00 | 101.0 | 0.000156 | 0.0000015 | No
29/06/2024 | 11:43 | NL210E | URBAN | Asset failure | LV | 8.00 | 260.0 | 0.003207 | 0.0000123 | No
29/06/2024 | 11:43 | NL210E | URBAN | Asset failure | LV | 14.00 | 398.0 | 0.008591 | 0.0000216 | No
29/06/2024 | 11:51 | SG05 | SHORT RURAL | Asset failure | LV | 1.00 | 788.0 | 0.005544 | 0.0000070 | No
29/06/2024 | 12:09 | AP146E | URBAN | Asset failure | LV | 2.00 | 240.5 | 0.000742 | 0.0000031 | No
29/06/2024 | 13:34 | MI20 | LONG RURAL | Asset failure | LV | 93.00 | 148.0 | 0.098775 | 0.0006674 | No
29/06/2024 | 13:40 | GU31 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 129.67 | 136.0 | 0.126552 | 0.0009305 | No
29/06/2024 | 13:46 | SG02 | SHORT RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 19.00 | 305.0 | 0.040771 | 0.0001337 | No
29/06/2024 | 14:13 | CL25 | LONG RURAL | Vegetation | Blow-in/Fall-in - Other responsible party | 1.00 | 197.0 | 0.001414 | 0.0000072 | No
29/06/2024 | 14:22 | SA11 | URBAN | Asset failure | LV | 1.00 | 342.0 | 0.000527 | 0.0000015 | No
29/06/2024 | 15:41 | HH409D | URBAN | Asset failure | LV | 1.00 | 124.0 | 0.000191 | 0.0000015 | No
29/06/2024 | 16:04 | SG12 | SHORT RURAL | Asset failure | LV | 1.00 | 429.0 | 0.003018 | 0.0000070 | No
29/06/2024 | 16:42 | NL210E | URBAN | Asset failure | LV | 8.00 | 101.0 | 0.001246 | 0.0000123 | No
29/06/2024 | 16:47 | HH145B | URBAN | Unknown | Unknown | 1.00 | 249.0 | 0.000384 | 0.0000015 | No
29/06/2024 | 17:25 | LX63 | LONG RURAL | Asset failure | HV | 2.00 | 11.0 | 0.000158 | 0.0000144 | No
29/06/2024 | 17:26 | AP132D | URBAN | Overloads |  | 1.00 | 83.0 | 0.000128 | 0.0000015 | No
29/06/2024 | 17:41 | MG27 | LONG RURAL | Asset failure | LV | 3.00 | 149.0 | 0.003208 | 0.0000215 | No
29/06/2024 | 18:25 | SM374A | URBAN | Asset failure | LV | 1.00 | 808.0 | 0.001246 | 0.0000015 | No
29/06/2024 | 19:46 | PA06 | LONG RURAL | Asset failure | HV | 40.00 | 166.5 | 0.047794 | 0.0002871 | No
29/06/2024 | 19:51 | NL451E | URBAN | Asset failure | LV | 13.00 | 316.5 | 0.006344 | 0.0000200 | No
29/06/2024 | 20:08 | SM374B | URBAN | Unknown | Unknown | 1.00 | 106.0 | 0.000163 | 0.0000015 | No
29/06/2024 | 20:11 | SM216A | URBAN | Third Party | Unauthorised access | 28.00 | 4.0 | 0.000173 | 0.0000432 | No
29/06/2024 | 22:33 | AP365F | URBAN | Overloads |  | 1.00 | 460.0 | 0.000709 | 0.0000015 | No
29/06/2024 | 23:48 | MT25 | LONG RURAL | Asset failure | HV | 69.00 | 646.5 | 0.320136 | 0.0004952 | No
30/06/2024 | 06:07 | HH145B | URBAN | Asset failure | LV | 1.00 | 432.0 | 0.000666 | 0.0000015 | No
30/06/2024 | 06:38 | MV32 | SHORT RURAL | Animal | Animal impact | 111.00 | 166.0 | 0.129636 | 0.0007809 | No
30/06/2024 | 08:17 | GA50 | URBAN | Asset failure | LV | 3.33 | 86.0 | 0.000442 | 0.0000051 | No
30/06/2024 | 08:21 | EL07 | URBAN | Planned |  | 18.00 | 392.7 | 0.010897 | 0.0000278 | No
30/06/2024 | 08:26 | HH386E | URBAN | Planned |  | 255.00 | 368.3 | 0.144781 | 0.0003931 | No
30/06/2024 | 08:33 | AP529E | URBAN | Overloads |  | 1.00 | 142.0 | 0.000219 | 0.0000015 | No
30/06/2024 | 08:35 | AP424E | URBAN | Asset failure | LV | 33.33 | 268.0 | 0.013773 | 0.0000514 | No
30/06/2024 | 08:46 | AP365F | URBAN | Asset failure | LV | 1.00 | 71.0 | 0.000109 | 0.0000015 | No
30/06/2024 | 08:57 | R12 | LONG RURAL | Planned |  | 233.00 | 239.0 | 0.399628 | 0.0016721 | No
30/06/2024 | 09:22 | HH496C | URBAN | Asset failure | LV | 1.00 | 319.0 | 0.000492 | 0.0000015 | No
30/06/2024 | 09:40 | NL210E | URBAN | Asset failure | LV | 1.00 | 208.0 | 0.000321 | 0.0000015 | No
30/06/2024 | 09:57 | AP132C | URBAN | Planned |  | 1.00 | 143.0 | 0.000220 | 0.0000015 | No
30/06/2024 | 10:03 | PA13 | LONG RURAL | Planned |  | 25.00 | 213.0 | 0.038214 | 0.0001794 | No
30/06/2024 | 10:05 | SG13 | SHORT RURAL | Asset failure | LV | 1.00 | 561.0 | 0.003947 | 0.0000070 | No
30/06/2024 | 10:14 | AP529D | URBAN | Unknown | Unknown | 1.00 | 60.0 | 0.000093 | 0.0000015 | No
30/06/2024 | 10:21 | SM126E | URBAN | Asset failure | LV | 1.00 | 294.0 | 0.000453 | 0.0000015 | No
30/06/2024 | 11:14 | ST44 | LONG RURAL | Animal | Animal nesting/burrowing, etc and other | 39.00 | 294.0 | 0.082284 | 0.0002799 | No
30/06/2024 | 11:23 | SA12 | URBAN | Asset failure | LV | 1.00 | 549.0 | 0.000846 | 0.0000015 | No
30/06/2024 | 12:18 | WHY04 | URBAN | Planned |  | 17.00 | 173.0 | 0.004534 | 0.0000262 | No
30/06/2024 | 12:18 | EL01L | URBAN | Asset failure | LV | 14.00 | 754.0 | 0.016275 | 0.0000216 | No
30/06/2024 | 12:21 | EL17 | URBAN | Asset failure | LV | 1.00 | 465.0 | 0.000717 | 0.0000015 | No
30/06/2024 | 14:26 | EL01Q | URBAN | Unknown | Unknown | 14.00 | 276.0 | 0.005957 | 0.0000216 | No
30/06/2024 | 14:40 | EL01Q | URBAN | Asset failure | HV | 106.00 | 230.0 | 0.037588 | 0.0001634 | No
30/06/2024 | 15:51 | NL210A | URBAN | Asset failure | LV | 13.00 | 30.0 | 0.000601 | 0.0000200 | No
30/06/2024 | 17:12 | MG41 | URBAN | Asset failure | LV | 1.00 | 154.0 | 0.000237 | 0.0000015 | No
30/06/2024 | 17:18 | ME347C | URBAN | Overloads |  | 44.67 | 147.0 | 0.010123 | 0.0000689 | No
30/06/2024 | 17:40 | SG03 | SHORT RURAL | Asset failure | LV | 1.00 | 355.0 | 0.002498 | 0.0000070 | No
30/06/2024 | 17:48 | AP425A | URBAN | Overloads |  | 1.00 | 186.0 | 0.000287 | 0.0000015 | No
30/06/2024 | 17:59 | ME116D | URBAN | Unknown | Unknown | 1.00 | 155.0 | 0.000239 | 0.0000015 | No
30/06/2024 | 18:37 | NL210A | URBAN | Asset failure | LV | 1.00 | 494.0 | 0.000762 | 0.0000015 | No
30/06/2024 | 18:39 | SA40 | URBAN | Asset failure | LV | 1.00 | 138.0 | 0.000213 | 0.0000015 | No
30/06/2024 | 18:58 | HH121C | URBAN | Asset failure | LV | 1.00 | 500.0 | 0.000771 | 0.0000015 | No
30/06/2024 | 19:12 | AP529E | URBAN | Asset failure | LV | 1.00 | 79.0 | 0.000122 | 0.0000015 | No
30/06/2024 | 19:42 | EL01Q | URBAN | Asset failure | LV | 1.00 | 172.0 | 0.000265 | 0.0000015 | No
30/06/2024 | 20:02 | HH121B | URBAN | Overloads |  | 47.00 | 341.0 | 0.024710 | 0.0000725 | No
30/06/2024 | 20:58 | CBD367G | CBD | Planned |  | 3.00 | 137.0 | 0.059380 | 0.0004334 | No
30/06/2024 | 21:00 | SM216D | URBAN | Asset failure | LV | 1.00 | 237.0 | 0.000365 | 0.0000015 | No
Contents
Instructions
CONFIDENTIAL
NON-CONFIDENTIAL
NON-AMENDED
AMENDED
FOR AMENDED SUBMISSIONS ONLY
Protected (SOCI)
NON-Protected

## Amendments
This sheet may be used to identify amendments made to data resubmitted to the AER. It may also be used to provide additional information not captured in this workbook.
NSP data amendments
Worksheet | Table | Comments
Contents
Instructions