## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | TasNetworks
DNSP - Australian company number: |  | 167 357 299
Reporting year: |  | 2013-14
Business address | Address |  | 1-7 Maria Street
| Suburb |  | Lenah Valley
|  | State | Tas | Postcode | 7008
Postal address | Address |  | PO Box 606
| Suburb |  | Moonah
|  | State | Tas | Postcode | 7009
Contact name/s | Chantal Hopwood / Michael Sward
Contact phone/s | 0400 827 037 / 03 6271 6343
Contact email address/s | chantal.hopwood@tasnetworks.com.au / michael.sward@tasnetworks.com.au

## Contents
Electricity Distribution Network Service Provider Annual Reporting Template
Table of contents
Cover sheet
1. Service Target Performance Incentive Scheme | 2. Customer service
1a. STPIS - Reliability | 3. Network performance
1b. STPIS - Customer service | 3a. Feeder reliability
1c. STPIS - Daily performance | 3b. Planned outages
1d. STPIS - GSL

## 1a. STPIS Reliability
TasNetworks
STPIS Data Reporting
2013-14
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI (System Average Interruption Duration Index)
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Total | 6.8383 | 39.1638 | 154.1817 | 551.873 | 807.1624 | 385.011
Total (after removing excluded events and MED) | 6.8289 | 27.6605 | 101.8928 | 289.2917 | 532.9978 | 239.3885
Table 2: SAIFI (System Average Interruption Frequency Index)
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Total | 0.13408 | 0.41763 | 1.4586 | 3.6649 | 5.3731 | 2.78
Total (after removing excluded events and MED) | 0.13382 | 0.31521 | 1.2058 | 2.9957 | 4.65 | 2.3421
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Total | 0 | 0.57642 | 2.2049 | 5.0484 | 6.4806 | 3.6928
Total (after removing excluded events and MED) | 0 | 0.52115 | 2.0459 | 4.637 | 5.9132 | 3.392
Table 4: Customer numbers
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Customer numbers at the start of period | 1883.5218 | 4655.1918 | 187544.9531 | 42228.5176 | 43304.8157 | 279617
Customer numbers at the end of period | 1875.5719 | 4677.2772 | 189019.3502 | 42655.8358 | 43657.9648 | 281886
Average customer numbers | 1879.5469 | 4666.2345 | 188282.1517 | 42442.1767 | 43481.3902 | 280751.5
Table 5: Average customer numbers (kVA)
Supply reliablity category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Customer numbers at the start of period | 124500 | 134800 | 1851043 | 762009 | 931839 | 3804191
Customer numbers at the end of period | 123530 | 134800 | 1853733 | 760417 | 935202 | 3807682
Average customer numbers | 124015 | 134800 | 1852388 | 761213 | 933520.5 | 3805936.5
Contents
Contents

## 1b. STPIS Customer Service
TasNetworks
STPIS Data Reporting - AER Definitions
2013-14
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
| Total - after removing excluded events | Total
Number of calls | 56943 | 81609
Number of calls answered in 30 seconds | 45541 | 62411
Percentage of calls answered within 30 seconds | 79.98% | 76.48%
Table 2: New connections
Note: This is for newly energised properties only
Total
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date | #DIV/0!
Table 3: Streetlight repair
Total
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business
Faulty streetlights not repaired within 5 business days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 business days of fault report or agreed date | #DIV/0!
Contents

## 1c. STPIS Daily Performance
TasNetworks |  |  | 2013-07-01 | 2013-07-01
STPIS Data Reporting |  |  | 2014-07-01 | 2014-07-01
2013-14 |  |  | 2015-07-01 | 2015-07-01
Daily Performance Data |  |  | 2016-07-01 | 2016-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1 Daily Performance Data (unplanned)
*Customer service information must be reported as per the definitions in the STPIS, that is excluding: • calls to payment lines and automated interactive services • calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned).
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | Critical infrastructure SAIDI all events total | Critical infrastructure SAIDI all events after removing excluded events | High density commercial SAIDI all events total | High density commercial SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | HIgh density rural SAIDI all events total | High density rural SAIDI all events after removing excluded events | Low density rural SAIDI all events total | Low density rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | Critical infrastructure SAIFI all events total | Critical infrastructure SAIFI all events after removing excluded events | High density commercial SAIFI all events total | High density commercial SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | HIgh density rural SAIFI all events total | High density rural SAIFI all events after removing excluded events | Low density rural SAIFI all events total | Low density rural SAIFI all events after removing excluded events | Network MAIFI all events total | Network MAIFI all events after removing excluded events | Critical infrastructure MAIFI all events total | Critical infrastructure MAIFI all events after removing excluded events | High density commercial MAIFI all events total | High density commercial MAIFI all events after removing excluded events | Urban MAIFI all events total | Urban MAIFI all events after removing excluded events | HIgh density rural MAIFI all events total | High density rural MAIFI all events after removing excluded events | Low density rural MAIFI all events total | Low density rural MAIFI all events after removing excluded events | Total number of calls (after removing excluded events) | Total number of calls answered in 30 seconds (after removing excluded events) | MED - YES/NO
2013-07-01 | 1.4264 | 1.4261 | 0 | 0 | 0.20586 | 0.20586 | 1.9923 | 1.9922 | 0.16837 | 0.16837 | 1.6953 | 1.6941 | 0.028226 | 0.028215 | 0 | 0 | 0.0055638 | 0.0055638 | 0.048125 | 0.048112 | 0.00035995 | 0.00035995 | 0.018484 | 0.018467 | 0.013452 | 0.013452 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081909 | 0.0081909 | 0.048166 | 0.048166 | 424.8 | 332 | NO
2013-07-02 | 0.84965 | 0.84908 | 0 | 0 | 0 | 0 | 0.32002 | 0.31985 | 0.96172 | 0.96172 | 2.0448 | 2.0428 | 0.011715 | 0.011706 | 0 | 0 | 0 | 0 | 0.0090915 | 0.0090786 | 0.010412 | 0.010412 | 0.02123 | 0.021222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.4 | 227 | NO
2013-07-03 | 0.16223 | 0.16138 | 0 | 0 | 0 | 0 | 0.0025437 | 0.0015245 | 0.12492 | 0.12481 | 0.55449 | 0.55315 | 0.0010886 | 0.0010781 | 0 | 0 | 0 | 0 | 6.4781e-05 | 5.1825e-05 | 0.0013662 | 0.0013557 | 0.0031954 | 0.0031869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 188 | NO
2013-07-04 | 0.80022 | 0.79779 | 0 | 0 | 0 | 0 | 0.55875 | 0.55769 | 1.9978 | 1.9978 | 0.52467 | 0.51687 | 0.011408 | 0.011388 | 0 | 0 | 0 | 0 | 0.011876 | 0.011867 | 0.01505 | 0.01505 | 0.010671 | 0.010609 | 0.015253 | 0.015253 | 0 | 0 | 0 | 0 | 0.0015898 | 0.0015898 | 0.034784 | 0.034784 | 0.030667 | 0.030667 | 278.4 | 243 | NO
2013-07-05 | 2.9002 | 2.8987 | 0 | 0 | 0 | 0 | 1.1261 | 1.1261 | 1.0326 | 1.026 | 8.7476 | 8.747 | 0.019136 | 0.018989 | 0 | 0 | 0 | 0 | 0.011453 | 0.011453 | 0.014541 | 0.013874 | 0.043431 | 0.043378 | 0.021574 | 0.021574 | 0 | 0 | 0 | 0 | 0.003923 | 0.003923 | 0.019943 | 0.019943 | 0.06391 | 0.06391 | 485.2 | 390 | NO
2013-07-06 | 0.5235 | 0.52332 | 0 | 0 | 0 | 0 | 0.4555 | 0.4555 | 1.0278 | 1.0278 | 0.39232 | 0.39161 | 0.0051336 | 0.0051228 | 0 | 0 | 0 | 0 | 0.0049137 | 0.0049137 | 0.0093285 | 0.0093285 | 0.0035725 | 0.0035286 | 0.02297 | 0.02297 | 0 | 0 | 0 | 0 | 0.0046939 | 0.0046939 | 0.0090855 | 0.0090855 | 0.076925 | 0.076925 | 246.6 | 169 | NO
2013-07-07 | 0.51724 | 0.51707 | 0 | 0 | 0 | 0 | 0.066134 | 0.065789 | 1.3154 | 1.3154 | 0.90493 | 0.90493 | 0.004977 | 0.0049707 | 0 | 0 | 0 | 0 | 0.0010327 | 0.0010198 | 0.01486 | 0.01486 | 0.0061241 | 0.0061241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.4 | 104 | NO
2013-07-08 | 2.192 | 2.192 | 0 | 0 | 0.0060534 | 0.0060534 | 0.016474 | 0.016474 | 1.7519 | 1.7518 | 7.4748 | 7.4747 | 0.021612 | 0.021608 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 7.5578e-05 | 7.5578e-05 | 0.054998 | 0.054987 | 0.043106 | 0.043097 | 0.0017512 | 0.0017512 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078033 | 0.0078033 | 0.00077663 | 0.00077663 | 323.4 | 227 | NO
2013-07-09 | 0.075946 | 0.075831 | 0 | 0 | 0 | 0 | 0.014117 | 0.013923 | 0.31771 | 0.31771 | 0.022554 | 0.022469 | 0.00081714 | 0.00081084 | 0 | 0 | 0 | 0 | 0.00025427 | 0.00024563 | 0.0032002 | 0.0032002 | 0.00021746 | 0.00020889 | 0.0069602 | 0.0069602 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087794 | 0.0087794 | 0.021218 | 0.021218 | 206.6 | 192 | NO
2013-07-10 | 0.044345 | 0.043321 | 0 | 0 | 0 | 0 | 0.033301 | 0.033016 | 0.073873 | 0.073873 | 0.054478 | 0.050868 | 0.00048635 | 0.00047531 | 0 | 0 | 0 | 0 | 0.00044375 | 0.00042648 | 0.00098921 | 0.00098921 | 0.00029565 | 0.00028494 | 0.0010255 | 0.0010255 | 0 | 0 | 0 | 0 | 0.0020665 | 0.0020665 | 9.8527e-05 | 9.8527e-05 | 0 | 0 | 238.4 | 223 | NO
2013-07-11 | 0.14219 | 0.14207 | 0.0014192 | 0.0014192 | 0.70104 | 0.70104 | 0.055141 | 0.055141 | 0.084597 | 0.084597 | 0.2999 | 0.2994 | 0.0023448 | 0.0023427 | 6.4508e-05 | 6.4508e-05 | 0.035237 | 0.035237 | 0.00098791 | 0.00098791 | 0.00031529 | 0.00031529 | 0.0022453 | 0.0022367 | 0.0039967 | 0.0039967 | 0 | 0 | 0.035237 | 0.035237 | 0.0006748 | 0.0006748 | 0.004414 | 0.004414 | 0.0062677 | 0.0062677 | 225.4 | 202 | NO
2013-07-12 | 0.0031913 | 0.0030043 | 0 | 0 | 0.0052819 | 0 | 0.0016023 | 0.0016023 | 0.0081554 | 0.0081554 | 0.0024188 | 0.0024188 | 5.8067e-05 | 5.5965e-05 | 0 | 0 | 5.9347e-05 | 0 | 3.0231e-05 | 3.0231e-05 | 0.00011955 | 0.00011955 | 7.07e-05 | 7.07e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.6 | 168 | NO
2013-07-13 | 0.10841 | 0.1082 | 0 | 0 | 0 | 0 | 0.0070007 | 0.0070007 | 0.00031529 | 0.00031529 | 0.42782 | 0.42696 | 0.0008668 | 0.0008647 | 0 | 0 | 0 | 0 | 0.00017491 | 0.00017491 | 1.051e-05 | 1.051e-05 | 0.0031783 | 0.0031697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 61 | NO
2013-07-14 | 0.50403 | 0.50396 | 0 | 0 | 0 | 0 | 0.014502 | 0.014502 | 0.56743 | 0.56709 | 1.5634 | 1.5634 | 0.0065119 | 0.0065098 | 0 | 0 | 0 | 0 | 0.00028288 | 0.00028288 | 0.01516 | 0.01515 | 0.013626 | 0.013626 | 0.0039762 | 0.0039762 | 0 | 0 | 0 | 0 | 0.004133 | 0.004133 | 0.0083039 | 0.0083039 | 0.0012383 | 0.0012383 | 122 | 113 | NO
2013-07-15 | 1.4434 | 1.4433 | 0 | 0 | 0 | 0 | 2.7478 | 2.7478 | 0.4295 | 0.4295 | 0.081775 | 0.081775 | 0.012527 | 0.012523 | 0 | 0 | 0 | 0 | 0.023997 | 0.023988 | 0.0032908 | 0.0032908 | 0.00077235 | 0.00077235 | 0.011671 | 0.011671 | 0 | 0 | 0 | 0 | 0.020358 | 0.020358 | 0.0033302 | 0.0033302 | 0.0044712 | 0.0044712 | 373 | 334 | NO
2013-07-16 | 1.7223 | 0.67799 | 0 | 0 | 0 | 0 | 1.2456 | 0.23314 | 0.15184 | 0.14645 | 4.4263 | 2.1821 | 0.031081 | 0.014241 | 0 | 0 | 0 | 0 | 0.032909 | 0.0048624 | 0.0022687 | 0.0021374 | 0.059565 | 0.046667 | 0.0024039 | 0.0024039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098005 | 0.0098005 | 360.6 | 261 | NO
2013-07-17 | 0.2605 | 0.2603 | 0 | 0 | 0 | 0 | 0.046164 | 0.045784 | 0.33762 | 0.33762 | 0.69516 | 0.69507 | 0.0030849 | 0.0030765 | 0 | 0 | 0 | 0 | 0.00045617 | 0.00044321 | 0.0053178 | 0.0053178 | 0.0073357 | 0.0073271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.8 | 212 | NO
2013-07-18 | 0.073432 | 0.073017 | 0 | 0 | 0.00059347 | 0.00059347 | 0.022261 | 0.022261 | 0.021647 | 0.019571 | 0.23747 | 0.23747 | 0.0006214 | 0.00059302 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00043511 | 0.00043511 | 0.00025617 | 0.00011429 | 0.0014526 | 0.0014526 | 0.00054415 | 0.00054415 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011876 | 0.0011876 | 0.0012501 | 0.0012501 | 272.8 | 226 | NO
2013-07-19 | 0.90249 | 0.90234 | 0 | 0 | 0.0042136 | 0.0042136 | 0.0031656 | 0.0031009 | 0.57097 | 0.5704 | 3.2069 | 3.2069 | 0.0094852 | 0.0094789 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 4.3187e-05 | 3.455e-05 | 0.0046794 | 0.0046689 | 0.034761 | 0.034761 | 0.014423 | 0.014423 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030307 | 0.030307 | 0.034089 | 0.034089 | 316.8 | 260 | NO
2013-07-20 | 0.63465 | 0.63436 | 0 | 0 | 0 | 0 | 0.0061132 | 0.0058972 | 0.40799 | 0.40718 | 2.2426 | 2.2425 | 0.0047176 | 0.0047113 | 0 | 0 | 0 | 0 | 0.00017059 | 0.00016627 | 0.012458 | 0.012447 | 0.0087368 | 0.0087282 | 0.0022115 | 0.0022115 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0059169 | 0.0059169 | 0.0041917 | 0.0041917 | 102.8 | 92 | NO
2013-07-21 | 5.7679 | 5.7679 | 0 | 0 | 0 | 0 | 6.3422 | 6.3422 | 3.8106 | 3.8106 | 7.8234 | 7.8234 | 0.030081 | 0.030077 | 0 | 0 | 0 | 0 | 0.034595 | 0.034587 | 0.02511 | 0.02511 | 0.033517 | 0.033517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282.4 | 223 | NO
2013-07-22 | 1.0632 | 1.0603 | 0 | 0 | 0.004095 | 0.004095 | 0.049864 | 0.044608 | 3.7232 | 3.7229 | 1.1992 | 1.1981 | 0.0067069 | 0.0066859 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.0004837 | 0.00045779 | 0.024334 | 0.024313 | 0.0065333 | 0.0065162 | 0.0098223 | 0.0098223 | 0 | 0 | 0 | 0 | 3.401e-05 | 3.401e-05 | 0.031585 | 0.031585 | 0.014223 | 0.014223 | 333.2 | 294 | NO
2013-07-23 | 1.3084 | 1.3079 | 0 | 0 | 0.0088427 | 0.0088427 | 0.15228 | 0.1522 | 3.2889 | 3.2889 | 2.3489 | 2.3473 | 0.01111 | 0.011104 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00094527 | 0.00093663 | 0.032614 | 0.032614 | 0.016818 | 0.016809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353.2 | 288 | NO
2013-07-24 | 0.32018 | 0.32014 | 0 | 0 | 0 | 0 | 0.0016282 | 0.001585 | 1.383 | 1.3829 | 0.17444 | 0.17444 | 0.0029175 | 0.0029133 | 0 | 0 | 0 | 0 | 3.8869e-05 | 3.455e-05 | 0.01242 | 0.012409 | 0.0016904 | 0.0016904 | 0.0035342 | 0.0035342 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014741 | 0.014741 | 0.0023888 | 0.0023888 | 201.2 | 189 | NO
2013-07-25 | 0.051698 | 0.05145 | 0 | 0 | 0 | 0 | 0.0093118 | 0.0088022 | 0.060352 | 0.060352 | 0.14308 | 0.14308 | 0.00037258 | 0.00036837 | 0 | 0 | 0 | 0 | 0.00013766 | 0.00012902 | 0.0007488 | 0.0007488 | 0.00063523 | 0.00063523 | 0.0012664 | 0.0012664 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062361 | 0.0062361 | 7.8199e-05 | 7.8199e-05 | 170 | 166 | NO
2013-07-26 | 0.081696 | 0.081675 | 0 | 0 | 0 | 0 | 0.078566 | 0.078523 | 0.08696 | 0.08696 | 0.10626 | 0.10626 | 0.0041727 | 0.0041706 | 0 | 0 | 0 | 0 | 0.0016665 | 0.0016622 | 0.0045112 | 0.0045112 | 0.010027 | 0.010027 | 0.0054733 | 0.0054733 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012355 | 0.012355 | 0.01224 | 0.01224 | 154 | 147 | NO
2013-07-27 | 0.052701 | 0.052659 | 0 | 0 | 0 | 0 | 0.030604 | 0.030561 | 0 | 0 | 0.15413 | 0.15405 | 0.00063401 | 0.00062981 | 0 | 0 | 0 | 0 | 0.0006991 | 0.00069478 | 0 | 0 | 0.0011976 | 0.001189 | 0.0014853 | 0.0014853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0060556 | 0.0060556 | 91.4 | 85 | NO
2013-07-28 | 0.16708 | 0.16684 | 0 | 0 | 0 | 0 | 0.024093 | 0.023605 | 0.084499 | 0.084499 | 0.56445 | 0.56445 | 0.0015615 | 0.0015573 | 0 | 0 | 0 | 0 | 0.00075308 | 0.00074444 | 0.0028757 | 0.0028757 | 0.002527 | 0.002527 | 0.0051564 | 0.0051564 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017819 | 0.017819 | 0.0064926 | 0.0064926 | 87.4 | 73 | NO
2013-07-29 | 0.1846 | 0.18409 | 0 | 0 | 0.51187 | 0.51187 | 0.053659 | 0.052623 | 0.49833 | 0.49833 | 0.16585 | 0.16585 | 0.0048753 | 0.0048732 | 0 | 0 | 0.0055638 | 0.0055638 | 0.0003984 | 0.00039409 | 0.016204 | 0.016204 | 0.005069 | 0.005069 | 0.0033217 | 0.0033217 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081068 | 0.0081068 | 0.0069318 | 0.0069318 | 260.6 | 213 | NO
2013-07-30 | 0.16442 | 0.16419 | 0 | 0 | 0 | 0 | 0.0010235 | 0.00059167 | 0.1155 | 0.1155 | 0.57411 | 0.57404 | 0.00065555 | 0.00064715 | 0 | 0 | 0 | 0 | 2.1594e-05 | 8.6375e-06 | 0.00098396 | 0.00098396 | 0.0018275 | 0.0018189 | 0.0048658 | 0.0048658 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098041 | 0.0098041 | 0.011843 | 0.011843 | 190.4 | 170 | NO
2013-07-31 | 0.010445 | 0.010342 | 0 | 0 | 0 | 0 | 0.0020816 | 0.00187 | 0.03285 | 0.03285 | 0.011668 | 0.011668 | 0.00020731 | 0.0002031 | 0 | 0 | 0 | 0 | 3.8869e-05 | 3.0231e-05 | 0.00081318 | 0.00081318 | 0.00010498 | 0.00010498 | 0.0055655 | 0.0055655 | 0 | 0 | 0 | 0 | 0.0080302 | 0.0080302 | 0.0041789 | 0.0041789 | 0.0033486 | 0.0033486 | 165.8 | 145 | NO
2013-08-01 | 0.026595 | 0.026541 | 0 | 0 | 0 | 0 | 0.012881 | 0.012768 | 0.037769 | 0.037769 | 0.052072 | 0.052072 | 0.00027641 | 0.00027431 | 0 | 0 | 0 | 0 | 0.00033416 | 0.00032984 | 0.00039411 | 0.00039411 | 0.00014247 | 0.00014247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.6 | 35 | NO
2013-08-02 | 0.29012 | 0.28985 | 0 | 0 | 0 | 0 | 0.20186 | 0.20132 | 0.10345 | 0.10345 | 0.6979 | 0.69786 | 0.0038566 | 0.0038482 | 0 | 0 | 0 | 0 | 0.005122 | 0.0051091 | 0.0011311 | 0.0011311 | 0.0046373 | 0.0046287 | 0.0012759 | 0.0012759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052018 | 0.0052018 | 52.4 | 47 | NO
2013-08-03 | 1.1057 | 1.1056 | 0 | 0 | 0 | 0 | 0.60978 | 0.60953 | 0.99176 | 0.99176 | 2.4893 | 2.4893 | 0.0052846 | 0.0052825 | 0 | 0 | 0 | 0 | 0.0053158 | 0.0053115 | 0.0044271 | 0.0044271 | 0.0073871 | 0.0073871 | 0.004705 | 0.004705 | 0 | 0 | 0 | 0 | 0.00012146 | 0.00012146 | 0.012701 | 0.012701 | 0.0085847 | 0.0085847 | 5.8 | 5 | NO
2013-08-04 | 1.0422 | 1.0421 | 0 | 0 | 0 | 0 | 2.0644 | 2.0643 | 0.028047 | 0.028047 | 0.12953 | 0.12944 | 0.0029919 | 0.0029877 | 0 | 0 | 0 | 0 | 0.0049417 | 0.0049374 | 6.5685e-05 | 6.5685e-05 | 0.0023385 | 0.0023299 | 0.0037662 | 0.0037662 | 0 | 0 | 0 | 0 | 0.0057736 | 0.0057736 | 0.00019705 | 0.00019705 | 0.0037375 | 0.0037375 | 8 | 8 | NO
2013-08-05 | 0.30847 | 0.28707 | 0 | 0 | 0 | 0 | 0.040583 | 0.035159 | 0.36524 | 0.36493 | 0.87926 | 0.80303 | 0.0028358 | 0.0015681 | 0 | 0 | 0 | 0 | 0.00053283 | 0.00030555 | 0.0030451 | 0.0030136 | 0.0080212 | 0.0033293 | 0.015837 | 0.015837 | 0 | 0 | 0 | 0 | 0.011181 | 0.011181 | 0.028582 | 0.028582 | 0.019072 | 0.019072 | 42 | 31 | NO
2013-08-06 | 0.81865 | 0.81862 | 0 | 0 | 0 | 0 | 0.16592 | 0.16586 | 2.1692 | 2.1692 | 1.2396 | 1.2396 | 0.0059636 | 0.0059615 | 0 | 0 | 0 | 0 | 0.0010916 | 0.0010872 | 0.0165 | 0.0165 | 0.0086929 | 0.0086929 | 0.0026075 | 0.0026075 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074986 | 0.0074986 | 0.0045162 | 0.0045162 | 45.8 | 43 | NO
2013-08-07 | 0.10194 | 0.10165 | 0 | 0 | 0.0077151 | 0 | 0.13009 | 0.13009 | 0.080146 | 0.080146 | 0.090991 | 0.090948 | 0.0029325 | 0.0029283 | 0 | 0 | 5.9347e-05 | 0 | 0.0053412 | 0.0053412 | 0.00099709 | 0.00099709 | 0.00053561 | 0.00052704 | 0.0096234 | 0.0096234 | 0 | 0 | 0 | 0 | 0.015407 | 0.015407 | 0 | 0 | 0.0086629 | 0.0086629 | 42 | 41 | NO
2013-08-08 | 0.032934 | 0.032698 | 0 | 0 | 0 | 0 | 0.01718 | 0.016761 | 0.069973 | 0.06992 | 0.043122 | 0.043036 | 0.00030558 | 0.00029717 | 0 | 0 | 0 | 0 | 0.00021378 | 0.00020514 | 0.00070151 | 0.000691 | 0.00024959 | 0.00024102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 52 | NO
2013-08-09 | 1.191 | 1.1908 | 0 | 0 | 0 | 0 | 0.39931 | 0.39931 | 1.4667 | 1.4667 | 2.8673 | 2.8666 | 0.014573 | 0.014556 | 0 | 0 | 0 | 0 | 0.0095358 | 0.0095358 | 0.027147 | 0.027147 | 0.018354 | 0.018287 | 0.016101 | 0.016101 | 0 | 0 | 0 | 0 | 0.0089242 | 0.0089242 | 0.042029 | 0.042029 | 0.013665 | 0.013665 | 36.8 | 37 | NO
2013-08-10 | 3.1519 | 3.1514 | 0 | 0 | 0.35608 | 0.35608 | 3.6748 | 3.6748 | 0.60296 | 0.60228 | 5.0152 | 5.0136 | 0.035597 | 0.035582 | 0 | 0 | 0.0055638 | 0.0055638 | 0.030067 | 0.030054 | 0.02659 | 0.02658 | 0.06298 | 0.062954 | 0.011077 | 0.011077 | 0 | 0 | 0 | 0 | 1.8895e-05 | 1.8895e-05 | 0.016249 | 0.016249 | 0.031872 | 0.031872 | 11 | 8 | NO
2013-08-11 | 0.016714 | 0.016266 | 0 | 0 | 0 | 0 | 0.006016 | 0.0053423 | 0.04148 | 0.04148 | 0.022382 | 0.021893 | 0.00019916 | 0.00019286 | 0 | 0 | 0 | 0 | 0.00012524 | 0.00011661 | 0.00032842 | 0.00032842 | 0.00029565 | 0.00028709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | NO
2013-08-12 | 1.6479 | 1.6455 | 0 | 0 | 0.0049258 | 0.0049258 | 0.014936 | 0.010039 | 4.5032 | 4.5029 | 3.0163 | 3.0163 | 0.0029827 | 0.0029701 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00014684 | 0.00012956 | 0.0074329 | 0.0074119 | 0.0057996 | 0.0057996 | 0.010778 | 0.010778 | 0 | 0 | 0 | 0 | 0.0037638 | 0.0037638 | 0.016949 | 0.016949 | 0.022653 | 0.022653 | 48 | 45 | NO
2013-08-13 | 3.9935 | 3.9555 | 0 | 0 | 0 | 0 | 3.7308 | 3.6532 | 2.2878 | 2.287 | 7.0127 | 7.0126 | 0.037694 | 0.037285 | 0 | 0 | 0 | 0 | 0.035067 | 0.034236 | 0.019477 | 0.019466 | 0.068213 | 0.068204 | 0.042262 | 0.042262 | 0 | 0 | 0 | 0 | 0.013914 | 0.013914 | 0.11153 | 0.11153 | 0.053744 | 0.053744 | 39.6 | 39 | NO
2013-08-14 | 1.6508 | 1.6478 | 0 | 0 | 0 | 0 | 0.20663 | 0.20491 | 1.4441 | 1.439 | 5.1427 | 5.1381 | 0.011468 | 0.011399 | 0 | 0 | 0 | 0 | 0.0015305 | 0.0015132 | 0.022988 | 0.022978 | 0.024973 | 0.024733 | 0.020881 | 0.020881 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021656 | 0.021656 | 0.067473 | 0.067473 | 39 | 31 | NO
2013-08-15 | 0.77155 | 0.77069 | 0.72572 | 0.72572 | 2.003 | 2.003 | 0.19978 | 0.19913 | 0.19143 | 0.1887 | 2.2074 | 2.2074 | 0.0052008 | 0.0051924 | 0.012095 | 0.012095 | 0.033383 | 0.033383 | 0.0017124 | 0.0016994 | 0.0034892 | 0.0034787 | 0.0085333 | 0.0085333 | 0.0035671 | 0.0035671 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01024 | 0.01024 | 0.0061927 | 0.0061927 | 31.6 | 32 | NO
2013-08-16 | 0.13141 | 0.13095 | 0 | 0 | 0 | 0 | 0.0095056 | 0.0093112 | 0.48944 | 0.48933 | 0.11778 | 0.11639 | 0.0059993 | 0.005993 | 0 | 0 | 0 | 0 | 0.00077576 | 0.00077144 | 0.02323 | 0.02322 | 0.0039774 | 0.0039688 | 0.012215 | 0.012215 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03614 | 0.03614 | 0.020331 | 0.020331 | 32 | 31 | NO
2013-08-17 | 0.84468 | 0.84467 | 0 | 0 | 0 | 0 | 0.0015202 | 0.0014986 | 1.8833 | 1.8833 | 1.9051 | 1.9051 | 0.0053028 | 0.0053007 | 0 | 0 | 0 | 0 | 2.1594e-05 | 1.7275e-05 | 0.012656 | 0.012656 | 0.011256 | 0.011256 | 0.0078963 | 0.0078963 | 0 | 0 | 0 | 0 | 0.011509 | 0.011509 | 0.010021 | 0.010021 | 0.0011848 | 0.0011848 | 6 | 4 | NO
2013-08-18 | 6.9808 | 6.9807 | 0 | 0 | 0 | 0 | 3.8007 | 3.8006 | 15.6224 | 15.6224 | 8.1799 | 8.1799 | 0.042126 | 0.042124 | 0 | 0 | 0 | 0 | 0.021266 | 0.021262 | 0.088806 | 0.088806 | 0.057133 | 0.057133 | 0.080611 | 0.080611 | 0 | 0 | 0 | 0 | 0.042381 | 0.042381 | 0.13038 | 0.13038 | 0.13824 | 0.13824 | 8.8 | 7 | NO
2013-08-19 | 4.6758 | 4.6741 | 0 | 0 | 5.0742 | 5.0742 | 0.85637 | 0.85633 | 3.639 | 3.6387 | 13.6637 | 13.6571 | 0.029216 | 0.029201 | 0 | 0 | 0.011128 | 0.011128 | 0.0094985 | 0.0094942 | 0.043805 | 0.043784 | 0.062939 | 0.062904 | 0.019207 | 0.019207 | 0 | 0 | 0 | 0 | 8.0977e-06 | 8.0977e-06 | 0.018028 | 0.018028 | 0.063588 | 0.063588 | 54.6 | 47 | NO
2013-08-20 | 0.85139 | 0.85113 | 0 | 0 | 0 | 0 | 0.088485 | 0.088398 | 0.051065 | 0.050959 | 3.2539 | 3.2531 | 0.0024869 | 0.0024788 | 0 | 0 | 0 | 0 | 0.00075848 | 0.00075416 | 0.000959 | 0.00094849 | 0.007852 | 0.0078359 | 0.006477 | 0.006477 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039608 | 0.0039608 | 0.023177 | 0.023177 | 29 | 29 | NO
2013-08-21 | 0.36421 | 0.36398 | 0 | 0 | 0 | 0 | 0.4217 | 0.42126 | 0.031219 | 0.031219 | 0.62264 | 0.62256 | 0.00091121 | 0.0009007 | 0 | 0 | 0 | 0 | 0.00061272 | 0.00059545 | 0.00038097 | 0.00038097 | 0.0021885 | 0.0021799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | NO
2013-08-22 | 0.35768 | 0.35762 | 0 | 0 | 0 | 0 | 0.080385 | 0.080342 | 1.1386 | 1.1385 | 0.3703 | 0.37022 | 0.0057339 | 0.0057276 | 0 | 0 | 0 | 0 | 0.0010727 | 0.0010684 | 0.013953 | 0.013942 | 0.0098712 | 0.0098627 | 0.00087889 | 0.00087889 | 0 | 0 | 0 | 0 | 0.00062082 | 0.00062082 | 0.0028836 | 0.0028836 | 0 | 0 | 24 | 22 | NO
2013-08-23 | 0.20396 | 0.20377 | 0 | 0 | 0 | 0 | 0.081858 | 0.081473 | 0.33949 | 0.33949 | 0.39229 | 0.39229 | 0.0025886 | 0.0025865 | 0 | 0 | 0 | 0 | 0.0002872 | 0.00028288 | 0.0065488 | 0.0065488 | 0.0046437 | 0.0046437 | 0.0033823 | 0.0033823 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026142 | 0.0026142 | 0.011658 | 0.011658 | 20.8 | 21 | NO
2013-08-24 | 2.1173 | 0.18034 | 0 | 0 | 0 | 0 | 0.0043555 | 0.0043555 | 9.6846 | 0 | 0.72662 | 0.72662 | 0.0023111 | 0.0012601 | 0 | 0 | 0 | 0 | 0.00030933 | 0.00030933 | 0.0052548 | 0 | 0.0045237 | 0.0045237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | NO
2013-08-25 | 0.030678 | 0.030678 | 0 | 0 | 0 | 0 | 0.0021135 | 0.0021135 | 0.14107 | 0.14107 | 0.0058435 | 0.0058435 | 0.00036601 | 0.00036601 | 0 | 0 | 0 | 0 | 0.00013334 | 0.00013334 | 0.0014595 | 0.0014595 | 3.7492e-05 | 3.7492e-05 | 0.012849 | 0.012849 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029844 | 0.029844 | 0.028049 | 0.028049 | 2.8 | 3 | NO
2013-08-26 | 0.13247 | 0.13191 | 0 | 0 | 0 | 0 | 0.004647 | 0.0039517 | 0.30582 | 0.30472 | 0.28149 | 0.28149 | 0.0017318 | 0.0017234 | 0 | 0 | 0 | 0 | 0.00015547 | 0.00014252 | 0.003564 | 0.0035535 | 0.0038457 | 0.0038457 | 0.0008802 | 0.0008802 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039608 | 0.0039608 | 0.00035886 | 0.00035886 | 26 | 23 | NO
2013-08-27 | 0.37196 | 0.3716 | 0 | 0 | 3.5586 | 3.5586 | 0.35017 | 0.34944 | 0.043018 | 0.043018 | 0.27269 | 0.27269 | 0.0031367 | 0.0031283 | 0 | 0 | 0.011128 | 0.011128 | 0.0034566 | 0.0034393 | 0.00086835 | 0.00086835 | 0.0036143 | 0.0036143 | 0.009487 | 0.009487 | 0 | 0 | 0 | 0 | 0.0022835 | 0.0022835 | 0.036631 | 0.036631 | 0.0042774 | 0.0042774 | 30 | 23 | NO
2013-08-28 | 0.1466 | 0.14654 | 0 | 0 | 0 | 0 | 0.058789 | 0.058659 | 0.52542 | 0.52542 | 0.052607 | 0.052607 | 0.0008266 | 0.0008203 | 0 | 0 | 0 | 0 | 0.00056144 | 0.00054848 | 0.0013137 | 0.0013137 | 0.0011848 | 0.0011848 | 0.00093538 | 0.00093538 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026142 | 0.0026142 | 0.0016818 | 0.0016818 | 25 | 23 | NO
2013-08-29 | 0.31223 | 0.31223 | 0 | 0 | 0 | 0 | 0.00051825 | 0.00051825 | 0.010784 | 0.010784 | 1.2631 | 1.2631 | 0.00095482 | 0.00095482 | 0 | 0 | 0 | 0 | 8.6375e-06 | 8.6375e-06 | 0.00013006 | 0.00013006 | 0.0037696 | 0.0037696 | 0.0034667 | 0.0034667 | 0 | 0 | 0 | 0 | 0.0026992 | 0.0026992 | 0.010764 | 0.010764 | 0 | 0 | 25 | 22 | NO
2013-08-30 | 0.9446 | 0.94375 | 0 | 0 | 0 | 0 | 0.70424 | 0.70424 | 1.0564 | 1.0563 | 1.5923 | 1.5889 | 0.010117 | 0.010032 | 0 | 0 | 0 | 0 | 0.0044996 | 0.0044996 | 0.014519 | 0.014508 | 0.020478 | 0.020141 | 0.027035 | 0.027035 | 0 | 0 | 0 | 0 | 0.0022835 | 0.0022835 | 0.07146 | 0.07146 | 0.04742 | 0.04742 | 24 | 22 | NO
2013-08-31 | 0.0026637 | 0.0026637 | 0 | 0 | 0 | 0 | 0.0011488 | 0.0011488 | 0 | 0 | 0.0085804 | 0.0085804 | 3.6785e-05 | 3.6785e-05 | 0 | 0 | 0 | 0 | 1.2956e-05 | 1.2956e-05 | 0 | 0 | 0.00012426 | 0.00012426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | NO
2013-09-01 | 0.044876 | 0.044876 | 0 | 0 | 0 | 0 | 0.017885 | 0.017885 | 0.02731 | 0.02731 | 0.1252 | 0.1252 | 0.00065214 | 0.00065214 | 0 | 0 | 0 | 0 | 0.00030825 | 0.00030825 | 0.0003166 | 0.0003166 | 0.0017889 | 0.0017889 | 0.00048871 | 0.00048871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019925 | 0.0019925 | 26 | 26 | NO
2013-09-02 | 0.024175 | 0.024175 | 0 | 0 | 0 | 0 | 0.023034 | 0.023034 | 0.060687 | 0.060687 | 0.0033679 | 0.0033679 | 0.00025644 | 0.00025644 | 0 | 0 | 0 | 0 | 0.00030447 | 0.00030447 | 0.00049789 | 0.00049789 | 3.535e-05 | 3.535e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.2 | 97 | NO
2013-09-03 | 0.56593 | 0.24619 | 0 | 0 | 0 | 0 | 0.0017059 | 0.0017059 | 0.025433 | 0.025381 | 2.2832 | 0.97963 | 0.0037113 | 0.00221 | 0 | 0 | 0 | 0 | 2.5912e-05 | 2.5912e-05 | 0.00023121 | 0.0002207 | 0.014891 | 0.0087786 | 0.00069313 | 0.00069313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028259 | 0.0028259 | 125.6 | 111 | NO
2013-09-04 | 0.087334 | 0.087061 | 0 | 0 | 0 | 0 | 0.029985 | 0.029467 | 0.29321 | 0.29321 | 0.057471 | 0.057385 | 0.00059013 | 0.00058382 | 0 | 0 | 0 | 0 | 0.0003455 | 0.00033686 | 0.0016933 | 0.0016933 | 0.00033957 | 0.00033101 | 0.00076118 | 0.00076118 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038058 | 0.0038058 | 0 | 0 | 115 | 104 | NO
2013-09-05 | 0.15435 | 0.15435 | 0 | 0 | 0 | 0 | 0.1466 | 0.1466 | 0.012634 | 0.012634 | 0.32806 | 0.32806 | 0.0035505 | 0.0035505 | 0 | 0 | 0 | 0 | 0.0047603 | 0.0047603 | 0.00032711 | 0.00032711 | 0.0047626 | 0.0047626 | 0.0031737 | 0.0031737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012939 | 0.012939 | 102.8 | 92 | NO
2013-09-06 | 0.78519 | 0.78517 | 0 | 0 | 0 | 0 | 0.10538 | 0.10538 | 2.4839 | 2.4838 | 0.9667 | 0.9667 | 0.005262 | 0.0052599 | 0 | 0 | 0 | 0 | 0.00059707 | 0.00059707 | 0.014155 | 0.014145 | 0.0087261 | 0.0087261 | 0.0098115 | 0.0098115 | 0 | 0 | 0 | 0 | 0.015058 | 0.015058 | 0 | 0 | 0.010121 | 0.010121 | 113.8 | 103 | NO
2013-09-07 | 2.4842 | 2.4842 | 0 | 0 | 0 | 0 | 0.025054 | 0.025054 | 12.3336 | 12.3335 | 0.021279 | 0.021279 | 0.0029767 | 0.0029746 | 0 | 0 | 0 | 0 | 0.00051015 | 0.00051015 | 0.0017459 | 0.0017354 | 0.0096998 | 0.0096998 | 0.006446 | 0.006446 | 0 | 0 | 0 | 0 | 0.0080302 | 0.0080302 | 0.012556 | 0.012556 | 0.00010712 | 0.00010712 | 74.4 | 64 | NO
2013-09-08 | 0.14677 | 0.14677 | 0 | 0 | 0 | 0 | 0.15753 | 0.15753 | 0.0029374 | 0.0029374 | 0.2834 | 0.2834 | 0.0021293 | 0.0021293 | 0 | 0 | 0 | 0 | 0.002994 | 0.002994 | 5.3861e-05 | 5.3861e-05 | 0.0026962 | 0.0026962 | 0.0030797 | 0.0030797 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021847 | 0.0021847 | 0.010774 | 0.010774 | 66.6 | 63 | NO
2013-09-09 | 0.12284 | 0.12203 | 0 | 0 | 0 | 0 | 0.074455 | 0.073306 | 0.0032566 | 0.0020375 | 0.3504 | 0.3504 | 0.0014971 | 0.0014845 | 0 | 0 | 0 | 0 | 0.00088426 | 0.00086699 | 5.1234e-05 | 3.0215e-05 | 0.0043074 | 0.0043074 | 0.016094 | 0.016094 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032514 | 0.032514 | 0.0391 | 0.0391 | 178.6 | 166 | NO
2013-09-10 | 0.25599 | 0.25428 | 0 | 0 | 0 | 0 | 0.011035 | 0.0082925 | 1.1037 | 1.1036 | 0.12178 | 0.12032 | 0.0054087 | 0.0052649 | 0 | 0 | 0 | 0 | 0.0015359 | 0.0012616 | 0.01992 | 0.019909 | 0.0027605 | 0.0027273 | 0.0047712 | 0.0047712 | 0 | 0 | 0 | 0 | 0.0082315 | 0.0082315 | 0.0037913 | 0.0037913 | 2.678e-05 | 2.678e-05 | 147.6 | 130 | NO
2013-09-11 | 0.12305 | 0.12244 | 0 | 0 | 0 | 0 | 0.020302 | 0.019827 | 0.45926 | 0.45926 | 0.086876 | 0.085334 | 0.0014485 | 0.0014401 | 0 | 0 | 0 | 0 | 0.00023753 | 0.00022457 | 0.0062886 | 0.0062886 | 0.00030637 | 0.0002978 | 0.014368 | 0.014368 | 0 | 0 | 0 | 0 | 0.002696 | 0.002696 | 0.02157 | 0.02157 | 0.035638 | 0.035638 | 115.8 | 109 | NO
2013-09-12 | 0.15346 | 0.14354 | 0 | 0 | 0 | 0 | 0.019003 | 0.019003 | 0.045715 | 0.045715 | 0.55069 | 0.51022 | 0.0016075 | 0.0016009 | 0 | 0 | 0 | 0 | 0.00012524 | 0.00012524 | 0.00095768 | 0.00095768 | 0.0055242 | 0.0054975 | 0.0016918 | 0.0016918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0068975 | 0.0068975 | 122.6 | 105 | NO
2013-09-13 | 0.11276 | 0.1122 | 0 | 0 | 0 | 0 | 0.0040828 | 0.0038496 | 0.01859 | 0.01859 | 0.43647 | 0.43462 | 0.0011306 | 0.0011243 | 0 | 0 | 0 | 0 | 0.00019596 | 0.00018733 | 0.00039936 | 0.00039936 | 0.0038949 | 0.0038864 | 0.0027184 | 0.0027184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011083 | 0.011083 | 88 | 88 | NO
2013-09-14 | 0.41334 | 0.41324 | 0 | 0 | 0 | 0 | 0.84377 | 0.84357 | 0.0027653 | 0.0027653 | 0.0086233 | 0.0086233 | 0.0077292 | 0.0077271 | 0 | 0 | 0 | 0 | 0.015734 | 0.01573 | 4.3352e-05 | 4.3352e-05 | 0.00025495 | 0.00025495 | 0.0012664 | 0.0012664 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062361 | 0.0062361 | 7.8199e-05 | 7.8199e-05 | 49.6 | 45 | NO
2013-09-15 | 0.091048 | 0.09084 | 0 | 0 | 0 | 0 | 0.0010322 | 0.00098467 | 0 | 0 | 0.36915 | 0.3684 | 0.00029848 | 0.00029428 | 0 | 0 | 0 | 0 | 2.1594e-05 | 1.7275e-05 | 0 | 0 | 0.0011741 | 0.0011655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 41 | NO
2013-09-16 | 0.11729 | 0.11133 | 0 | 0 | 0 | 0 | 0.091755 | 0.079609 | 0.28284 | 0.28273 | 0.065478 | 0.065392 | 0.00092592 | 0.00072466 | 0 | 0 | 0 | 0 | 0.00074498 | 0.0003401 | 0.0011587 | 0.0011482 | 0.0013519 | 0.0013433 | 0.033543 | 0.033543 | 0 | 0 | 0 | 0 | 0.014142 | 0.014142 | 0.054886 | 0.054886 | 0.063935 | 0.063935 | 160.8 | 130 | NO
2013-09-17 | 0.17904 | 0.17898 | 0 | 0 | 0 | 0 | 0.030866 | 0.030779 | 0.15248 | 0.15248 | 0.54437 | 0.54429 | 0.001685 | 0.0016766 | 0 | 0 | 0 | 0 | 0.00054632 | 0.00053337 | 0.0019416 | 0.0019416 | 0.0042024 | 0.0041938 | 0.010542 | 0.010542 | 0 | 0 | 0 | 0 | 0.012928 | 0.012928 | 0.00088806 | 0.00088806 | 0.016604 | 0.016604 | 133 | 124 | NO
2013-09-18 | 0.048017 | 0.047846 | 0 | 0 | 0 | 0 | 0.07164 | 0.071291 | 0.050942 | 0.050942 | 0.012066 | 0.012066 | 0.00052234 | 0.00051604 | 0 | 0 | 0 | 0 | 0.00071799 | 0.00070504 | 0.00068969 | 0.00068969 | 0.00014247 | 0.00014247 | 0.022906 | 0.022906 | 0 | 0 | 0 | 0 | 0.0036137 | 0.0036137 | 0.042531 | 0.042531 | 0.051535 | 0.051535 | 147.6 | 130 | NO
2013-09-19 | 1.8945 | 1.8944 | 0 | 0 | 0 | 0 | 0.053673 | 0.053544 | 0.20791 | 0.20791 | 7.4478 | 7.4478 | 0.012588 | 0.012582 | 0 | 0 | 0 | 0 | 0.0065067 | 0.0064938 | 0.020674 | 0.020674 | 0.021553 | 0.021553 | 0.00013794 | 0.00013794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056239 | 0.00056239 | 176.4 | 141 | NO
2013-09-20 | 1.1689 | 1.1689 | 0 | 0 | 0.39317 | 0.39317 | 0.48438 | 0.48436 | 1.2131 | 1.2131 | 2.7584 | 2.7584 | 0.017857 | 0.017855 | 0 | 0 | 0.0074184 | 0.0074184 | 0.0074633 | 0.007459 | 0.011832 | 0.011832 | 0.047275 | 0.047275 | 0.011003 | 0.011003 | 0 | 0 | 0 | 0 | 0.0027289 | 0.0027289 | 0 | 0 | 0.039442 | 0.039442 | 178.2 | 141 | NO
2013-09-21 | 0.13862 | 0.13857 | 0 | 0 | 0 | 0 | 0.076397 | 0.07628 | 0.1681 | 0.1681 | 0.2765 | 0.2765 | 0.00086076 | 0.00085866 | 0 | 0 | 0 | 0 | 0.00022026 | 0.00021594 | 0.0013478 | 0.0013478 | 0.0019732 | 0.0019732 | 0.0055011 | 0.0055011 | 0 | 0 | 0 | 0 | 0.00813 | 0.00813 | 0.0051221 | 0.0051221 | 0.0021189 | 0.0021189 | 64.8 | 60 | NO
2013-09-22 | 0.72634 | 0.72631 | 0 | 0 | 2.5593 | 2.5593 | 0.99785 | 0.9978 | 0.10628 | 0.10628 | 0.52499 | 0.52499 | 0.0059972 | 0.0059951 | 0 | 0 | 0.025964 | 0.025964 | 0.0088518 | 0.0088475 | 0.00013137 | 0.00013137 | 0.0030294 | 0.0030294 | 0.010313 | 0.010313 | 0 | 0 | 0 | 0 | 0.018201 | 0.018201 | 0.0034222 | 0.0034222 | 0.0031408 | 0.0031408 | 63.8 | 59 | NO
2013-09-23 | 0.23511 | 0.23508 | 0 | 0 | 0 | 0 | 0.21222 | 0.21218 | 0.062867 | 0.062867 | 0.48616 | 0.48611 | 0.004437 | 0.0044328 | 0 | 0 | 0 | 0 | 0.005271 | 0.0052667 | 0.0019653 | 0.0019653 | 0.0060277 | 0.0060192 | 0.0067389 | 0.0067389 | 0 | 0 | 0 | 0 | 0.0070282 | 0.0070282 | 0.0072056 | 0.0072056 | 0.0076528 | 0.0076528 | 232.6 | 191 | NO
2013-09-24 | 0.51627 | 0.020278 | 0 | 0 | 0 | 0 | 0.38322 | 0.0030048 | 0.26387 | 0.069836 | 1.1292 | 0.019764 | 0.018002 | 0.00036338 | 0 | 0 | 0 | 0 | 0.014167 | 4.3727e-05 | 0.0084431 | 0.0015134 | 0.038398 | 0.00016068 | 0.0079589 | 0.0079589 | 0 | 0 | 0 | 0 | 0.0089393 | 0.0089393 | 0.0090684 | 0.0090684 | 0.0073153 | 0.0073153 | 168.4 | 145 | NO
2013-09-25 | 0.67085 | 0.67079 | 0 | 0 | 0.0061721 | 0.0061721 | 0.22475 | 0.22475 | 2.0033 | 2.003 | 0.65465 | 0.65465 | 0.010183 | 0.010178 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.0021799 | 0.0021799 | 0.033722 | 0.033701 | 0.0096816 | 0.0096816 | 0.016891 | 0.016891 | 0 | 0 | 0 | 0 | 0.0049828 | 0.0049828 | 0.029871 | 0.029871 | 0.034621 | 0.034621 | 273 | 239 | NO
2013-09-26 | 2.3382 | 2.3348 | 0 | 0 | 0 | 0 | 1.6973 | 1.6905 | 2.8939 | 2.8939 | 3.8052 | 3.8047 | 0.015107 | 0.01497 | 0 | 0 | 0 | 0 | 0.0094624 | 0.0091838 | 0.022063 | 0.022063 | 0.024825 | 0.024817 | 0.019024 | 0.019024 | 0 | 0 | 0 | 0 | 0.0045768 | 0.0045768 | 0.034191 | 0.034191 | 0.040597 | 0.040597 | 294 | 258 | NO
2013-09-27 | 0.44968 | 0.44966 | 0.0014837 | 0.0014837 | 0.0014837 | 0.0014837 | 0.061135 | 0.061135 | 1.5028 | 1.5027 | 0.48617 | 0.48617 | 0.011536 | 0.011534 | 6.4508e-05 | 6.4508e-05 | 5.9347e-05 | 5.9347e-05 | 0.0027807 | 0.0027807 | 0.032088 | 0.032078 | 0.015332 | 0.015332 | 0.0272 | 0.0272 | 0 | 0 | 0 | 0 | 0.022342 | 0.022342 | 0.059902 | 0.059902 | 0.017716 | 0.017716 | 163.6 | 148 | NO
2013-09-28 | 1.3832 | 1.3771 | 0 | 0 | 0 | 0 | 0.037115 | 0.037072 | 3.8224 | 3.8223 | 2.4489 | 2.424 | 0.0075075 | 0.007497 | 0 | 0 | 0 | 0 | 0.00025373 | 0.00024941 | 0.019803 | 0.019782 | 0.013957 | 0.01394 | 0.00046349 | 0.00046349 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023174 | 0.0023174 | 0 | 0 | 170.2 | 118 | NO
2013-09-29 | 0.17575 | 0.1754 | 0.0038705 | 0 | 0 | 0 | 0.087707 | 0.08725 | 0.089326 | 0.089326 | 0.46913 | 0.46913 | 0.0011994 | 0.001191 | 6.4508e-05 | 0 | 0 | 0 | 0.00057385 | 0.0005609 | 0.00076194 | 0.00076194 | 0.0031215 | 0.0031215 | 0.0070997 | 0.0070997 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056331 | 0.0056331 | 0.024352 | 0.024352 | 66.8 | 58 | NO
2013-09-30 | 0.25972 | 0.25941 | 0 | 0 | 0 | 0 | 0.15994 | 0.15956 | 0.40067 | 0.40017 | 0.41479 | 0.4147 | 0.0014472 | 0.0014367 | 0 | 0 | 0 | 0 | 0.00055226 | 0.00054362 | 0.0023318 | 0.0023108 | 0.002903 | 0.0028944 | 0.011913 | 0.011913 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014803 | 0.014803 | 0.036499 | 0.036499 | 208.8 | 172 | NO
2013-10-01 | 4.5037 | 4.0069 | 0 | 0 | 0 | 0 | 1.5825 | 1.359 | 2.3429 | 2.3429 | 13.3106 | 11.7288 | 0.036135 | 0.017539 | 0 | 0 | 0 | 0 | 0.030966 | 0.0093215 | 0.018568 | 0.018568 | 0.070737 | 0.037867 | 0.043813 | 0.043813 | 0 | 0 | 0 | 0 | 0.013223 | 0.013223 | 0.061348 | 0.061348 | 0.10236 | 0.10236 | 624.2 | 434 | NO
2013-10-02 | 42.1838 | 0 | 0 | 0 | 2.0901 | 0 | 15.4881 | 0 | 90.1417 | 0 | 67.4437 | 0 | 0.10691 | 0 | 0 | 0 | 0.042656 | 0 | 0.06386 | 0 | 0.2012 | 0 | 0.13891 | 0 | 0.14867 | 0 | 0 | 0 | 0.042656 | 0 | 0.10584 | 0 | 0.19049 | 0 | 0.23461 | 0 | 0 | 0 | YES
2013-10-03 | 3.6444 | 3.6379 | 0 | 0 | 0 | 0 | 0.16674 | 0.15911 | 3.2259 | 3.2257 | 11.8968 | 11.8856 | 0.016193 | 0.01617 | 0 | 0 | 0 | 0 | 0.0086197 | 0.0085981 | 0.028905 | 0.028884 | 0.025346 | 0.025312 | 0.0060306 | 0.0060306 | 0 | 0 | 0 | 0 | 0.0046432 | 0.0046432 | 0.0051155 | 0.0051155 | 0.011202 | 0.011202 | 1069.2 | 831 | NO
2013-10-04 | 0.66633 | 0.66624 | 0 | 0 | 0 | 0 | 0.038842 | 0.038778 | 0.43643 | 0.4361 | 2.2837 | 2.2837 | 0.0065592 | 0.0065508 | 0 | 0 | 0 | 0 | 0.00066725 | 0.00065861 | 0.0041421 | 0.0041211 | 0.02204 | 0.02204 | 0.0020232 | 0.0020232 | 0 | 0 | 0 | 0 | 0.0031225 | 0.0031225 | 0 | 0 | 0.0020524 | 0.0020524 | 305.8 | 269 | NO
2013-10-05 | 1.1205 | 1.1205 | 0 | 0 | 0.00059347 | 0 | 0.15235 | 0.15235 | 0.046461 | 0.046461 | 4.228 | 4.228 | 0.0090774 | 0.0090753 | 0 | 0 | 5.9347e-05 | 0 | 0.00084378 | 0.00084378 | 0.00059248 | 0.00059248 | 0.034842 | 0.034842 | 0.011128 | 0.011128 | 0 | 0 | 0 | 0 | 3.401e-05 | 3.401e-05 | 0.00037834 | 0.00037834 | 0.044994 | 0.044994 | 194.6 | 155 | NO
2013-10-06 | 0.65619 | 0.65619 | 0 | 0 | 0.20586 | 0.20586 | 1.2169 | 1.2169 | 0.11173 | 0.11173 | 0.1398 | 0.1398 | 0.0085456 | 0.0085456 | 0 | 0 | 0.0055638 | 0.0055638 | 0.016292 | 0.016292 | 0.00041381 | 0.00041381 | 0.0013701 | 0.0013701 | 0.00065687 | 0.00065687 | 0 | 0 | 0.0055638 | 0.0055638 | 0.00094473 | 0.00094473 | 0 | 0 | 0 | 0 | 82.4 | 73 | NO
2013-10-07 | 0.51667 | 0.51662 | 0 | 0 | 0 | 0 | 0.0090284 | 0.0089852 | 0.15885 | 0.15885 | 1.959 | 1.9589 | 0.006101 | 0.0060968 | 0 | 0 | 0 | 0 | 0.00021486 | 0.00021054 | 0.0041289 | 0.0041289 | 0.02108 | 0.021072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.4 | 209 | NO
2013-10-08 | 0.38195 | 0.38192 | 0 | 0 | 0 | 0 | 0.062836 | 0.062792 | 0.19148 | 0.19148 | 1.2764 | 1.2763 | 0.0024493 | 0.002443 | 0 | 0 | 0 | 0 | 0.00050745 | 0.00049882 | 0.0010575 | 0.0010575 | 0.0081166 | 0.008108 | 0.01467 | 0.01467 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011266 | 0.011266 | 0.050623 | 0.050623 | 179 | 166 | NO
2013-10-09 | 0.55229 | 0.4695 | 0 | 0 | 0 | 0 | 0.012182 | 0.012139 | 1.9552 | 1.9552 | 0.63315 | 0.29572 | 0.013577 | 0.013312 | 0 | 0 | 0 | 0 | 0.00014198 | 0.00013766 | 0.054301 | 0.054301 | 0.010794 | 0.0097223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.2 | 185 | NO
2013-10-10 | 0.10356 | 0.10319 | 0 | 0 | 0 | 0 | 0.0098532 | 0.0091018 | 0.17756 | 0.17756 | 0.25789 | 0.25785 | 0.00090858 | 0.00090017 | 0 | 0 | 0 | 0 | 0.00037681 | 0.00036385 | 0.00084865 | 0.00084865 | 0.0022645 | 0.002256 | 0.0010315 | 0.0010315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002299 | 0.0002299 | 0.0040181 | 0.0040181 | 149.2 | 135 | NO
2013-10-11 | 0.22945 | 0.22943 | 0 | 0 | 0.0058754 | 0.0058754 | 0.088228 | 0.088184 | 0.4395 | 0.4395 | 0.40117 | 0.40117 | 0.0014908 | 0.0014866 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00066941 | 0.00066077 | 0.0038754 | 0.0038754 | 0.0015811 | 0.0015811 | 0.0022155 | 0.0022155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0090325 | 0.0090325 | 189.6 | 184 | NO
2013-10-12 | 1.0121 | 1.012 | 0.34472 | 0.34472 | 0 | 0 | 0.018454 | 0.018454 | 0.39837 | 0.39827 | 3.7189 | 3.7188 | 0.0020339 | 0.0020297 | 0.0060477 | 0.0060477 | 0 | 0 | 0.00013388 | 0.00013388 | 0.0013255 | 0.001315 | 0.0061423 | 0.0061338 | 0.004349 | 0.004349 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062361 | 0.0062361 | 0.012646 | 0.012646 | 75.4 | 61 | NO
2013-10-13 | 0.88795 | 0.88705 | 0 | 0 | 0 | 0 | 0.0065515 | 0.0047722 | 1.9767 | 1.9765 | 1.9953 | 1.9953 | 0.014071 | 0.014065 | 0 | 0 | 0 | 0 | 3.8869e-05 | 3.455e-05 | 0.040756 | 0.040735 | 0.024056 | 0.024056 | 0.0049021 | 0.0049021 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017007 | 0.017007 | 0.0061177 | 0.0061177 | 122.8 | 99 | NO
2013-10-14 | 0.63536 | 0.63527 | 0.0012902 | 0.0012902 | 0 | 0 | 0.080357 | 0.080227 | 0.061476 | 0.06137 | 2.3806 | 2.3806 | 0.0027617 | 0.0027575 | 6.4508e-05 | 6.4508e-05 | 0 | 0 | 0.00041676 | 0.00041244 | 0.0014832 | 0.0014726 | 0.0092146 | 0.0092146 | 0.011529 | 0.011529 | 0 | 0 | 0 | 0 | 0.02124 | 0.02124 | 0.0059537 | 0.0059537 | 0 | 0 | 236.4 | 199 | NO
2013-10-15 | 0.18988 | 0.1468 | 0 | 0 | 0.24481 | 0 | 0.074663 | 0.0043382 | 0.37997 | 0.37997 | 0.28079 | 0.28007 | 0.0099424 | 0.0032943 | 0 | 0 | 0.040801 | 0 | 0.010994 | 0.00031311 | 0.0079754 | 0.0079754 | 0.0063234 | 0.0063062 | 0.008817 | 0.008817 | 0 | 0 | 0 | 0 | 0.0019245 | 0.0019245 | 0.020921 | 0.020921 | 0.015069 | 0.015069 | 198.6 | 162 | NO
2013-10-16 | 3.5034 | 3.5033 | 0.66524 | 0.66524 | 0 | 0 | 0.41004 | 0.40997 | 3.5365 | 3.5365 | 10.4974 | 10.4972 | 0.028707 | 0.028698 | 0.0060477 | 0.0060477 | 0 | 0 | 0.010619 | 0.01061 | 0.03267 | 0.03267 | 0.068522 | 0.068505 | 0.036053 | 0.036053 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043863 | 0.043863 | 0.11122 | 0.11122 | 638.8 | 543 | NO
2013-10-17 | 0.25657 | 0.25652 | 0 | 0 | 0.015668 | 0.015668 | 0.13068 | 0.13064 | 0.10322 | 0.10317 | 0.70029 | 0.70021 | 0.0013842 | 0.0013778 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00051339 | 0.00050907 | 0.0015764 | 0.0015659 | 0.0033304 | 0.0033218 | 0.0069252 | 0.0069252 | 0 | 0 | 0 | 0 | 0.0087438 | 0.0087438 | 0 | 0 | 0.010884 | 0.010884 | 294.2 | 255 | NO
2013-10-18 | 0.049006 | 0.048964 | 0 | 0 | 0 | 0 | 0.032542 | 0.032499 | 0.032422 | 0.032317 | 0.10879 | 0.10879 | 0.00037967 | 0.00037547 | 0 | 0 | 0 | 0 | 0.00014684 | 0.00014252 | 0.00053599 | 0.00052548 | 0.00081948 | 0.00081948 | 0.010369 | 0.010369 | 0 | 0 | 0 | 0 | 0.013113 | 0.013113 | 0.0051733 | 0.0051733 | 0.012036 | 0.012036 | 195.4 | 179 | NO
2013-10-19 | 0.2998 | 0.29682 | 0 | 0 | 0 | 0 | 0.014397 | 0.0082726 | 0.26708 | 0.26708 | 0.97592 | 0.97592 | 0.002859 | 0.0028548 | 0 | 0 | 0 | 0 | 0.00020082 | 0.00019218 | 0.00087886 | 0.00087886 | 0.010541 | 0.010541 | 0.0025247 | 0.0025247 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015396 | 0.0015396 | 0.0090378 | 0.0090378 | 97 | 89 | NO
2013-10-20 | 2.2207 | 2.2207 | 0 | 0 | 0 | 0 | 0.0029886 | 0.0029886 | 1.1235 | 1.1235 | 8.1316 | 8.1316 | 0.016657 | 0.016657 | 0 | 0 | 0 | 0 | 2.5912e-05 | 2.5912e-05 | 0.0083787 | 0.0083787 | 0.061026 | 0.061026 | 0.01232 | 0.01232 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078375 | 0.0078375 | 0.043838 | 0.043838 | 80.8 | 66 | NO
2013-10-21 | 0.0791 | 0.079079 | 0.16227 | 0.16227 | 0 | 0 | 0.02253 | 0.022487 | 0.10072 | 0.10072 | 0.1741 | 0.1741 | 0.00074594 | 0.00074384 | 0.0061122 | 0.0061122 | 0 | 0 | 0.00059815 | 0.00059383 | 0.0007002 | 0.0007002 | 0.00047133 | 0.00047133 | 0.0044373 | 0.0044373 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019742 | 0.019742 | 0.0019925 | 0.0019925 | 197.2 | 139 | NO
2013-10-22 | 0.041495 | 0.041127 | 0 | 0 | 0 | 0 | 0.0032391 | 0.0024833 | 0.072934 | 0.072934 | 0.10327 | 0.10327 | 0.00019601 | 0.00019181 | 0 | 0 | 0 | 0 | 4.3187e-05 | 3.455e-05 | 0.0004703 | 0.0004703 | 0.00032993 | 0.00032993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.8 | 142 | NO
2013-10-23 | 0.048249 | 0.048196 | 0 | 0 | 0.00059347 | 0 | 0.065202 | 0.065202 | 0.044902 | 0.044902 | 0.030627 | 0.030498 | 0.0013038 | 0.0012995 | 0 | 0 | 5.9347e-05 | 0 | 0.00056144 | 0.00056144 | 0.00061218 | 0.00061218 | 0.0036935 | 0.003685 | 0.0095782 | 0.0095782 | 0 | 0 | 0 | 0 | 0.01494 | 0.01494 | 0.00042695 | 0.00042695 | 0.009056 | 0.009056 | 189.6 | 178 | NO
2013-10-24 | 0.60612 | 0.6061 | 0 | 0 | 0 | 0 | 0.31266 | 0.31266 | 1.2286 | 1.2285 | 0.8489 | 0.8489 | 0.010909 | 0.010907 | 0 | 0 | 0 | 0 | 0.0050762 | 0.0050762 | 0.022355 | 0.022345 | 0.016173 | 0.016173 | 0.0063222 | 0.0063222 | 0 | 0 | 0 | 0 | 0.0064808 | 0.0064808 | 0.011919 | 0.011919 | 0.0031965 | 0.0031965 | 226 | 184 | NO
2013-10-25 | 0.66233 | 0.66222 | 0 | 0 | 0.0040356 | 0.0040356 | 0.20408 | 0.20404 | 0.50688 | 0.50641 | 1.8814 | 1.8814 | 0.0054034 | 0.0053971 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.0064528 | 0.0064484 | 0.0028376 | 0.0028166 | 0.0069029 | 0.0069029 | 0.0063837 | 0.0063837 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062558 | 0.0062558 | 0.020925 | 0.020925 | 269.6 | 238 | NO
2013-10-26 | 1.6022 | 1.602 | 0 | 0 | 0 | 0 | 0.87635 | 0.87631 | 1.8529 | 1.8529 | 3.2821 | 3.2817 | 0.0091665 | 0.0091602 | 0 | 0 | 0 | 0 | 0.0058541 | 0.0058454 | 0.010768 | 0.010768 | 0.016974 | 0.016966 | 0.012785 | 0.012785 | 0 | 0 | 0 | 0 | 0.0023451 | 0.0023451 | 0.022052 | 0.022052 | 0.029491 | 0.029491 | 183.2 | 128 | NO
2013-10-27 | 0.42843 | 0.42843 | 0 | 0 | 0 | 0 | 0.55907 | 0.55907 | 0.18354 | 0.18354 | 0.48768 | 0.48768 | 0.0071788 | 0.0071788 | 0 | 0 | 0 | 0 | 0.0032105 | 0.0032105 | 0.0064555 | 0.0064555 | 0.017633 | 0.017633 | 0.0016774 | 0.0016774 | 0 | 0 | 0 | 0 | 0.00066293 | 0.00066293 | 0 | 0 | 0.0055232 | 0.0055232 | 101 | 85 | NO
2013-10-28 | 0.15045 | 0.14498 | 0 | 0 | 0 | 0 | 0.15971 | 0.15954 | 0.155 | 0.12817 | 0.1701 | 0.17001 | 0.0010733 | 0.00067027 | 0 | 0 | 0 | 0 | 0.00084378 | 0.00083946 | 0.002701 | 0.00070677 | 0.00049919 | 0.00049062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.2 | 148 | NO
2013-10-29 | 0.37821 | 0.37819 | 0 | 0 | 0 | 0 | 0.68346 | 0.68343 | 0.1861 | 0.1861 | 0.033998 | 0.033998 | 0.0053388 | 0.0053367 | 0 | 0 | 0 | 0 | 0.010454 | 0.010449 | 0.0010733 | 0.0010733 | 0.00014783 | 0.00014783 | 0.00201 | 0.00201 | 0 | 0 | 0.046365 | 0.046365 | 0.00075578 | 0.00075578 | 0 | 0 | 0 | 0 | 158.6 | 150 | NO
2013-10-30 | 0.0098317 | 0.0098107 | 0 | 0 | 0 | 0 | 0.0036925 | 0.0036493 | 0.029326 | 0.029326 | 0.0088439 | 0.0088439 | 0.00018603 | 0.00018392 | 0 | 0 | 0 | 0 | 7.5578e-05 | 7.1259e-05 | 0.00063189 | 0.00063189 | 9.3196e-05 | 9.3196e-05 | 0.0011077 | 0.0011077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045162 | 0.0045162 | 182.4 | 156 | NO
2013-10-31 | 0.6533 | 0.64939 | 0 | 0 | 0.39317 | 0.39317 | 0.0030274 | 0.0029843 | 2.329 | 2.329 | 0.70155 | 0.68569 | 0.0055913 | 0.0055829 | 0 | 0 | 0.0074184 | 0.0074184 | 2.5912e-05 | 2.1594e-05 | 0.018082 | 0.018082 | 0.0069286 | 0.0069029 | 0.0066357 | 0.0066357 | 0 | 0 | 0.035245 | 0.035245 | 0.0088264 | 0.0088264 | 0.0054571 | 0.0054571 | 0 | 0 | 164.6 | 133 | NO
2013-11-01 | 0.092787 | 0.092787 | 0 | 0 | 0 | 0 | 0.001179 | 0.001179 | 0.24639 | 0.24639 | 0.17504 | 0.17504 | 0.00070994 | 0.00070994 | 0 | 0 | 0 | 0 | 1.7275e-05 | 1.7275e-05 | 0.0024645 | 0.0024645 | 0.00085054 | 0.00085054 | 0.0020153 | 0.0020153 | 0 | 0 | 0 | 0 | 0.0012497 | 0.0012497 | 0 | 0 | 0.0057363 | 0.0057363 | 22 | 20 | NO
2013-11-02 | 0.033758 | 0.033035 | 0 | 0 | 0 | 0 | 0.00059599 | 0.00038869 | 0.057077 | 0.054072 | 0.089907 | 0.089821 | 0.0012026 | 0.0011942 | 0 | 0 | 0 | 0 | 1.2956e-05 | 8.6375e-06 | 0.00062926 | 0.00060824 | 0.0043641 | 0.0043556 | 0.001124 | 0.001124 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004414 | 0.004414 | 0.00098337 | 0.00098337 | 6 | 6 | NO
2013-11-03 | 9.1745 | 0 | 0 | 0 | 0 | 0 | 4.4403 | 0 | 16.5133 | 0 | 15.1278 | 0 | 0.03312 | 0 | 0 | 0 | 0 | 0 | 0.010985 | 0 | 0.077331 | 0 | 0.050174 | 0 | 0.025336 | 0 | 0 | 0 | 0 | 0 | 0.013055 | 0 | 0.064468 | 0 | 0.024821 | 0 | 0 | 0 | YES
2013-11-04 | 0.20708 | 0.20658 | 0 | 0 | 1.046 | 1.046 | 0.0054287 | 0.004431 | 0.13395 | 0.13389 | 0.57322 | 0.57322 | 0.0018453 | 0.0018411 | 0 | 0 | 0.014837 | 0.014837 | 7.1259e-05 | 6.6941e-05 | 0.0010982 | 0.0010877 | 0.0043438 | 0.0043438 | 0.012392 | 0.012392 | 0 | 0 | 0 | 0 | 0.0046939 | 0.0046939 | 0.011412 | 0.011412 | 0.031901 | 0.031901 | 21.8 | 21 | NO
2013-11-05 | 0.53798 | 0.53794 | 0 | 0 | 0 | 0 | 0.030804 | 0.030804 | 0.25979 | 0.25963 | 1.9203 | 1.9203 | 0.017846 | 0.017842 | 0 | 0 | 0 | 0 | 0.00029152 | 0.00029152 | 0.012127 | 0.012106 | 0.062292 | 0.062292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | NO
2013-11-06 | 0.20965 | 0.20435 | 0 | 0 | 0 | 0 | 0.16623 | 0.16619 | 0.089699 | 0.06332 | 0.45174 | 0.45174 | 0.0064158 | 0.0058861 | 0 | 0 | 0 | 0 | 0.0087476 | 0.0087433 | 0.0029663 | 0.00032842 | 0.0063801 | 0.0063801 | 0.0057027 | 0.0057027 | 0 | 0 | 0 | 0 | 0.00026992 | 0.00026992 | 0.011043 | 0.011043 | 0.013709 | 0.013709 | 22 | 19 | NO
2013-11-07 | 1.2494 | 1.2451 | 0 | 0 | 0 | 0 | 1.5116 | 1.5116 | 0.14196 | 0.12044 | 1.9786 | 1.9786 | 0.0068291 | 0.006796 | 0 | 0 | 0 | 0 | 0.0097701 | 0.0097701 | 0.0012362 | 0.0010707 | 0.0074471 | 0.0074471 | 0.043583 | 0.043583 | 0 | 0 | 0 | 0 | 0.073948 | 0.073948 | 0.0073146 | 0.0073146 | 0.024988 | 0.024988 | 22.6 | 21 | NO
2013-11-08 | 0.1409 | 0.1409 | 0 | 0 | 0 | 0 | 0.074639 | 0.074639 | 0.28997 | 0.28997 | 0.18988 | 0.18988 | 0.0015907 | 0.0015907 | 0 | 0 | 0 | 0 | 0.00036224 | 0.00036224 | 0.0022779 | 0.0022779 | 0.0039089 | 0.0039089 | 0.019308 | 0.019308 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053126 | 0.053126 | 0.035398 | 0.035398 | 23 | 21 | NO
2013-11-09 | 2.6615 | 2.637 | 0 | 0 | 0 | 0 | 0.052417 | 0.0021491 | 3.2786 | 3.2786 | 8.0732 | 8.0732 | 0.0068049 | 0.0066015 | 0 | 0 | 0 | 0 | 0.00043565 | 1.7815e-05 | 0.0069402 | 0.0069402 | 0.02122 | 0.02122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | NO
2013-11-10 | 0.29032 | 0.29028 | 0 | 0 | 0 | 0 | 0.0078515 | 0.0078515 | 0.20033 | 0.20012 | 1.0047 | 1.0047 | 0.015765 | 0.015761 | 0 | 0 | 0 | 0 | 0.00018355 | 0.00018355 | 0.011139 | 0.011118 | 0.054827 | 0.054827 | 0.0091087 | 0.0091087 | 0 | 0 | 0 | 0 | 0.01049 | 0.01049 | 0.012957 | 0.012957 | 0.0057546 | 0.0057546 | 4 | 3 | NO
2013-11-11 | 0.1627 | 0.16077 | 0 | 0 | 0 | 0 | 0.0013215 | 0.0012999 | 0.016018 | 0.0064174 | 0.64763 | 0.64763 | 0.00059144 | 0.00057279 | 0 | 0 | 0 | 0 | 2.1594e-05 | 1.7275e-05 | 0.00017603 | 9.3272e-05 | 0.0022249 | 0.0022249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 26 | NO
2013-11-12 | 0.1733 | 0.17326 | 0 | 0 | 0 | 0 | 0.013945 | 0.013902 | 0.23815 | 0.23815 | 0.48466 | 0.48458 | 0.0079644 | 0.0079602 | 0 | 0 | 0 | 0 | 0.00027856 | 0.00027424 | 0.022581 | 0.022581 | 0.013505 | 0.013496 | 0.0023101 | 0.0023101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0094181 | 0.0094181 | 23 | 22 | NO
2013-11-13 | 0.24777 | 0.24702 | 0 | 0 | 0 | 0 | 0.031883 | 0.031862 | 0.3227 | 0.31914 | 0.68373 | 0.68365 | 0.017593 | 0.017586 | 0 | 0 | 0 | 0 | 0.00041676 | 0.00041244 | 0.013387 | 0.013376 | 0.059983 | 0.059974 | 0.0036963 | 0.0036963 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0042406 | 0.0042406 | 0.011612 | 0.011612 | 25 | 24 | NO
2013-11-14 | 0.65534 | 0.37198 | 0 | 0 | 0 | 0 | 0.030613 | 0.030484 | 0.76951 | 0.23262 | 1.9836 | 1.2664 | 0.018057 | 0.01639 | 0 | 0 | 0 | 0 | 0.00040812 | 0.00039085 | 0.014847 | 0.011708 | 0.060701 | 0.056499 | 0.0013807 | 0.0013807 | 0 | 0 | 0 | 0 | 0.0020055 | 0.0020055 | 0.0011692 | 0.0011692 | 0.00069629 | 0.00069629 | 19 | 16 | NO
2013-11-15 | 0.34762 | 0.3228 | 0 | 0 | 0 | 0 | 0.024319 | 0.024319 | 0.31113 | 0.23614 | 1.1153 | 1.0752 | 0.016103 | 0.016011 | 0 | 0 | 0 | 0 | 0.00019218 | 0.00019218 | 0.011675 | 0.011402 | 0.055751 | 0.055596 | 0.0081704 | 0.0081704 | 0 | 0 | 0 | 0 | 0.010923 | 0.010923 | 0.002563 | 0.002563 | 0.0095467 | 0.0095467 | 47 | 43 | NO
2013-11-16 | 0.0055277 | 0.0054856 | 0 | 0 | 0 | 0 | 0.010542 | 0.010456 | 0 | 0 | 0.0016175 | 0.0016175 | 0.00014714 | 0.00014293 | 0 | 0 | 0 | 0 | 0.00029152 | 0.00028288 | 0 | 0 | 2.1424e-05 | 2.1424e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 3 | NO
2013-11-17 | 0.01576 | 0.01576 | 0 | 0 | 0 | 0 | 0.020395 | 0.020395 | 0 | 0 | 0.023781 | 0.023781 | 0.00018051 | 0.00018051 | 0 | 0 | 0 | 0 | 0.00022457 | 0.00022457 | 0 | 0 | 0.0002903 | 0.0002903 | 0.0026107 | 0.0026107 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011876 | 0.0011876 | 0.0096752 | 0.0096752 | 5 | 5 | NO
2013-11-18 | 0.97637 | 0.97604 | 0.0019352 | 0 | 0 | 0 | 0.060741 | 0.060236 | 0.45897 | 0.45886 | 3.4856 | 3.4856 | 0.019159 | 0.019149 | 6.4508e-05 | 0 | 0 | 0 | 0.0009091 | 0.00089614 | 0.013754 | 0.013744 | 0.065083 | 0.065083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 21 | NO
2013-11-19 | 0.2631 | 0.26287 | 0 | 0 | 0 | 0 | 0.29838 | 0.2979 | 0.13422 | 0.13422 | 0.37113 | 0.37113 | 0.0020211 | 0.0020147 | 0 | 0 | 0 | 0 | 0.0018398 | 0.0018268 | 0.0013176 | 0.0013176 | 0.0035147 | 0.0035147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 24 | NO
2013-11-20 | 0.035302 | 0.035281 | 0 | 0 | 0 | 0 | 0.006625 | 0.006625 | 0.080411 | 0.080306 | 0.065209 | 0.065209 | 0.0004937 | 0.0004916 | 0 | 0 | 0 | 0 | 2.5912e-05 | 2.5912e-05 | 0.00046111 | 0.0004506 | 0.0015854 | 0.0015854 | 0.005674 | 0.005674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023133 | 0.023133 | 28 | 24 | NO
2013-11-21 | 2.4165 | 2.4161 | 0 | 0 | 0 | 0 | 0.024429 | 0.024114 | 1.7604 | 1.7592 | 8.368 | 8.368 | 0.038085 | 0.038079 | 0 | 0 | 0 | 0 | 0.0002872 | 0.00027856 | 0.029387 | 0.029377 | 0.13074 | 0.13074 | 0.019802 | 0.019802 | 0 | 0 | 0 | 0 | 0.0063675 | 0.0063675 | 0.0012703 | 0.0012703 | 0.067061 | 0.067061 | 25.8 | 24 | NO
2013-11-22 | 5.6507 | 5.6503 | 0 | 0 | 0 | 0 | 0.1312 | 0.13049 | 2.8666 | 2.8666 | 20.4399 | 20.4399 | 0.028257 | 0.028234 | 0 | 0 | 0 | 0 | 0.00076172 | 0.00071475 | 0.016174 | 0.016174 | 0.1005 | 0.1005 | 0.065929 | 0.065929 | 0 | 0 | 0 | 0 | 0.076428 | 0.076428 | 0.0013334 | 0.0013334 | 0.11605 | 0.11605 | 23 | 21 | NO
2013-11-23 | 2.1581 | 2.1577 | 0 | 0 | 0 | 0 | 0.80982 | 0.809 | 5.0613 | 5.0613 | 3.0646 | 3.0646 | 0.016911 | 0.016909 | 0 | 0 | 0 | 0 | 0.011029 | 0.011025 | 0.032963 | 0.032963 | 0.020181 | 0.020181 | 0.048779 | 0.048779 | 0 | 0 | 0 | 0 | 0.0073111 | 0.0073111 | 0.079185 | 0.079185 | 0.11979 | 0.11979 | 15 | 8 | NO
2013-11-24 | 0.47348 | 0.4734 | 0 | 0 | 0 | 0 | 0.022673 | 0.022609 | 1.598 | 1.5979 | 0.5823 | 0.58222 | 0.012049 | 0.01204 | 0 | 0 | 0 | 0 | 0.00040812 | 0.00039948 | 0.032057 | 0.032046 | 0.022172 | 0.022163 | 0.0184 | 0.0184 | 0 | 0 | 0 | 0 | 0.0069624 | 0.0069624 | 0.028171 | 0.028171 | 0.038232 | 0.038232 | 4.8 | 5 | NO
2013-11-25 | 0.61034 | 0.60981 | 0 | 0 | 0 | 0 | 0.094011 | 0.093009 | 1.0469 | 1.0468 | 1.4481 | 1.448 | 0.0052442 | 0.0052337 | 0 | 0 | 0 | 0 | 0.00051231 | 0.00049936 | 0.00415 | 0.0041394 | 0.01698 | 0.016971 | 0.03341 | 0.03341 | 0 | 0 | 0 | 0 | 0.065054 | 0.065054 | 0 | 0 | 0.0071236 | 0.0071236 | 33.8 | 32 | NO
2013-11-26 | 0.13304 | 0.10466 | 0 | 0 | 0 | 0 | 0.16608 | 0.16606 | 0.0085653 | 0.0085653 | 0.20586 | 0.090173 | 0.00061824 | 0.00041908 | 0 | 0 | 0 | 0 | 0.00053876 | 0.00053445 | 0.00010904 | 0.00010904 | 0.0013626 | 0.00055917 | 0.0062445 | 0.0062445 | 0 | 0 | 0 | 0 | 0.010125 | 0.010125 | 0 | 0 | 0.0053668 | 0.0053668 | 26 | 23 | NO
2013-11-27 | 0.057364 | 0.057343 | 0 | 0 | 0 | 0 | 0.00079033 | 0.00079033 | 0.23223 | 0.23223 | 0.042934 | 0.042848 | 0.00059407 | 0.00059197 | 0 | 0 | 0 | 0 | 8.6375e-06 | 8.6375e-06 | 0.002249 | 0.002249 | 0.00057096 | 0.00056239 | 0.032241 | 0.032241 | 0 | 0 | 0 | 0 | 0.062627 | 0.062627 | 0.0035062 | 0.0035062 | 0.0043138 | 0.0043138 | 21 | 21 | NO
2013-11-28 | 0.58441 | 0.52153 | 0 | 0 | 0 | 0 | 1.0361 | 0.90695 | 0.13019 | 0.13019 | 0.22053 | 0.22045 | 0.0040734 | 0.0038637 | 0 | 0 | 0 | 0 | 0.0067254 | 0.0062989 | 0.0012454 | 0.0012454 | 0.0022463 | 0.0022378 | 0.021982 | 0.021982 | 0 | 0 | 0 | 0 | 0.0051533 | 0.0051533 | 0 | 0 | 0.079395 | 0.079395 | 25 | 24 | NO
2013-11-29 | 0.62912 | 0.6291 | 0 | 0 | 0 | 0 | 0.66298 | 0.66298 | 1.1832 | 1.1831 | 0.28459 | 0.28459 | 0.012526 | 0.012524 | 0 | 0 | 0 | 0 | 0.0093512 | 0.0093512 | 0.033712 | 0.033701 | 0.0050229 | 0.0050229 | 0.013409 | 0.013409 | 0 | 0 | 0 | 0 | 0.0068549 | 0.0068549 | 0.0048554 | 0.0048554 | 0.037107 | 0.037107 | 23 | 22 | NO
2013-11-30 | 0.28781 | 0.020468 | 0 | 0 | 0 | 0 | 0.55361 | 0.0043187 | 0.022364 | 0.022364 | 0.05664 | 0.05664 | 0.00036522 | 0.00023385 | 0 | 0 | 0 | 0 | 0.00039085 | 0.00012092 | 0.00028376 | 0.00028376 | 0.00048205 | 0.00048205 | 0.0014546 | 0.0014546 | 0 | 0 | 0 | 0 | 0.00071259 | 0.00071259 | 0 | 0 | 0.0045162 | 0.0045162 | 16 | 14 | NO
2013-12-01 | 0.23101 | 0.20128 | 0 | 0 | 0 | 0 | 0.00048802 | 0.00022458 | 0.63653 | 0.63653 | 0.42179 | 0.30111 | 0.0036464 | 0.003443 | 0 | 0 | 0 | 0 | 8.6375e-06 | 4.3187e-06 | 0.014347 | 0.014347 | 0.0031504 | 0.0023299 | 0.01232 | 0.01232 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078375 | 0.0078375 | 0.043838 | 0.043838 | 61.8 | 56 | NO
2013-12-02 | 0.49588 | 0.49549 | 0 | 0 | 0.77522 | 0.77522 | 0.085837 | 0.085164 | 0.038125 | 0.038125 | 1.7083 | 1.7081 | 0.012441 | 0.012398 | 0 | 0 | 0.035237 | 0.035237 | 0.004498 | 0.0044267 | 0.00039936 | 0.00039936 | 0.036384 | 0.036348 | 0.029602 | 0.029602 | 0 | 0 | 0.035237 | 0.035237 | 0.0006748 | 0.0006748 | 0.015675 | 0.015675 | 0.10148 | 0.10148 | 246 | 211 | NO
2013-12-03 | 0.16998 | 0.16793 | 0 | 0 | 0.0022552 | 0.0022552 | 0.020818 | 0.01664 | 0.17149 | 0.17149 | 0.51153 | 0.51145 | 0.0075033 | 0.0072978 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00055604 | 0.0001382 | 0.0018011 | 0.0018011 | 0.02801 | 0.028002 | 0.0067765 | 0.0067765 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016194 | 0.016194 | 0.014423 | 0.014423 | 200 | 179 | NO
2013-12-04 | 1.5993 | 1.5992 | 0 | 0 | 1.3464 | 1.3464 | 0.56112 | 0.56097 | 0.053953 | 0.053953 | 5.1683 | 5.1683 | 0.016324 | 0.016316 | 0 | 0 | 0.011128 | 0.011128 | 0.0048996 | 0.0048823 | 0.0014884 | 0.0014884 | 0.05401 | 0.05401 | 0.012055 | 0.012055 | 0 | 0 | 0 | 0 | 0.0046939 | 0.0046939 | 0.0063307 | 0.0063307 | 0.034672 | 0.034672 | 231.8 | 209 | NO
2013-12-05 | 2.0292 | 2.0288 | 0 | 0 | 0 | 0 | 0.41143 | 0.41143 | 0.27426 | 0.27426 | 7.2329 | 7.2313 | 0.015548 | 0.015545 | 0 | 0 | 0 | 0 | 0.003733 | 0.003733 | 0.0045204 | 0.0045204 | 0.052296 | 0.052285 | 0.036503 | 0.036503 | 0 | 0 | 0 | 0 | 0.011932 | 0.011932 | 0.063178 | 0.063178 | 0.07363 | 0.07363 | 330.8 | 278 | NO
2013-12-06 | 0.13115 | 0.13102 | 0 | 0 | 0.0013056 | 0 | 0.10916 | 0.10898 | 0.17038 | 0.17038 | 0.17897 | 0.17897 | 0.0009254 | 0.00092119 | 0 | 0 | 5.9347e-05 | 0 | 0.00051015 | 0.00050583 | 0.0021518 | 0.0021518 | 0.0009973 | 0.0009973 | 0.0039346 | 0.0039346 | 0 | 0 | 0 | 0 | 0.0080302 | 0.0080302 | 0 | 0 | 0.00010712 | 0.00010712 | 183 | 160 | NO
2013-12-07 | 0.59742 | 0.024578 | 0 | 0 | 0 | 0 | 0.00086807 | 0.00078169 | 2.8802 | 0.016324 | 0.085383 | 0.08534 | 0.0013324 | 0.0002751 | 0 | 0 | 0 | 0 | 2.5912e-05 | 1.7275e-05 | 0.0056594 | 0.00040462 | 0.00076592 | 0.00075735 | 0.00083396 | 0.00083396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012703 | 0.0012703 | 0.0023642 | 0.0023642 | 67.8 | 61 | NO
2013-12-08 | 0.10713 | 0.10713 | 0 | 0 | 0.008546 | 0.008546 | 0.011169 | 0.011169 | 0.28746 | 0.28746 | 0.17896 | 0.17896 | 0.0073603 | 0.0073603 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00017869 | 0.00017869 | 0.016914 | 0.016914 | 0.015853 | 0.015853 | 0.040622 | 0.040622 | 0 | 0 | 0 | 0 | 0.006328 | 0.006328 | 0.044756 | 0.044756 | 0.11656 | 0.11656 | 68 | 59 | NO
2013-12-09 | 0.24109 | 0.24101 | 0 | 0 | 0 | 0 | 0.3615 | 0.3615 | 0.11946 | 0.11915 | 0.16819 | 0.1681 | 0.00251 | 0.0025058 | 0 | 0 | 0 | 0 | 0.0041233 | 0.0041233 | 0.00048738 | 0.00047687 | 0.001654 | 0.0016454 | 0.0057718 | 0.0057718 | 0 | 0 | 0 | 0 | 0.0030166 | 0.0030166 | 0.015588 | 0.015588 | 0.0048344 | 0.0048344 | 191 | 141 | NO
2013-12-10 | 2.7445 | 2.7444 | 0 | 0 | 0 | 0 | 0.73749 | 0.73736 | 0.13051 | 0.13051 | 9.6193 | 9.6193 | 0.012077 | 0.012072 | 0 | 0 | 0 | 0 | 0.0033368 | 0.0033325 | 0.002718 | 0.002718 | 0.040399 | 0.04039 | 0.0013602 | 0.0013602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055457 | 0.0055457 | 219.2 | 182 | NO
2013-12-11 | 0.21618 | 0.21615 | 0 | 0 | 0 | 0 | 0.002872 | 0.0028072 | 0.18319 | 0.18319 | 0.72628 | 0.72628 | 0.0013692 | 0.001365 | 0 | 0 | 0 | 0 | 4.3187e-05 | 3.455e-05 | 0.0012651 | 0.0012651 | 0.0044648 | 0.0044648 | 0.0016616 | 0.0016616 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0081068 | 0.0081068 | 0.0001639 | 0.0001639 | 206 | 155 | NO
2013-12-12 | 0.012023 | 0.011981 | 0 | 0 | 0 | 0 | 0.0038313 | 0.0037881 | 0.0087439 | 0.0087439 | 0.034284 | 0.034199 | 0.00021309 | 0.00020678 | 0 | 0 | 0 | 0 | 0.00020892 | 0.00020028 | 0.00015239 | 0.00015239 | 0.00032993 | 0.00032136 | 0.0035121 | 0.0035121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014319 | 0.014319 | 141.4 | 111 | NO
2013-12-13 | 0.043678 | 0.043678 | 0 | 0 | 0 | 0 | 0.0026301 | 0.0026301 | 0.045216 | 0.045216 | 0.13598 | 0.13598 | 0.00034105 | 0.00034105 | 0 | 0 | 0 | 0 | 2.5912e-05 | 2.5912e-05 | 0.0005662 | 0.0005662 | 0.00087732 | 0.00087732 | 0.0023219 | 0.0023219 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011692 | 0.0011692 | 0.0085129 | 0.0085129 | 143.4 | 126 | NO
2013-12-14 | 0.14999 | 0.14991 | 0 | 0 | 0 | 0 | 0.0043619 | 0.0042108 | 0.39684 | 0.39684 | 0.27924 | 0.27924 | 0.0017552 | 0.0017509 | 0 | 0 | 0 | 0 | 0.00017923 | 0.00017059 | 0.0031502 | 0.0031502 | 0.0042313 | 0.0042313 | 0.0013736 | 0.0013736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056003 | 0.0056003 | 82.2 | 78 | NO
2013-12-15 | 0.084565 | 0.084544 | 0 | 0 | 0 | 0 | 0.028852 | 0.028852 | 0.10248 | 0.10248 | 0.20395 | 0.20386 | 0.00072308 | 0.00072098 | 0 | 0 | 0 | 0 | 0.00014792 | 0.00014792 | 0.0012927 | 0.0012927 | 0.0016004 | 0.0015918 | 0.0089289 | 0.0089289 | 0 | 0 | 0 | 0 | 0.0039187 | 0.0039187 | 0.012073 | 0.012073 | 0.018783 | 0.018783 | 53.8 | 52 | NO
2013-12-16 | 0.23316 | 0.23295 | 0 | 0 | 0 | 0 | 0.072417 | 0.072123 | 0.049646 | 0.049383 | 0.76642 | 0.76634 | 0.0016374 | 0.001629 | 0 | 0 | 0 | 0 | 0.00074175 | 0.00073743 | 0.0004033 | 0.00038228 | 0.0048751 | 0.0048665 | 0.011816 | 0.011816 | 0 | 0 | 0 | 0 | 0.015786 | 0.015786 | 0.010146 | 0.010146 | 0.0085751 | 0.0085751 | 200 | 172 | NO
2013-12-17 | 0.26808 | 0.25684 | 0 | 0 | 0 | 0 | 0.19585 | 0.17277 | 0.64311 | 0.64311 | 0.1799 | 0.1799 | 0.0031517 | 0.0029483 | 0 | 0 | 0 | 0 | 0.0021761 | 0.0017583 | 0.0085916 | 0.0085916 | 0.0015254 | 0.0015254 | 0.035331 | 0.035331 | 0 | 0 | 0 | 0 | 0.017661 | 0.017661 | 0.061537 | 0.061537 | 0.058819 | 0.058819 | 230.2 | 179 | NO
2013-12-18 | 0.090168 | 0.090168 | 0 | 0 | 0 | 0 | 0.00044483 | 0.00044483 | 0.1443 | 0.1443 | 0.24906 | 0.24906 | 0.00064531 | 0.00064531 | 0 | 0 | 0 | 0 | 8.6375e-06 | 8.6375e-06 | 0.0014608 | 0.0014608 | 0.0014226 | 0.0014226 | 0.001092 | 0.001092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004452 | 0.004452 | 142 | 134 | NO
2013-12-19 | 1.0547 | 1.0547 | 0 | 0 | 0 | 0 | 0.40719 | 0.40708 | 2.7216 | 2.7216 | 1.2729 | 1.2729 | 0.017355 | 0.017353 | 0 | 0 | 0 | 0 | 0.007824 | 0.0078196 | 0.040724 | 0.040724 | 0.022024 | 0.022024 | 0.0088223 | 0.0088223 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027338 | 0.027338 | 0.013676 | 0.013676 | 224 | 201 | NO
2013-12-20 | 0.10751 | 0.10749 | 0 | 0 | 0 | 0 | 0.0031397 | 0.0030965 | 0.18507 | 0.18507 | 0.28118 | 0.28118 | 0.00069654 | 0.00069444 | 0 | 0 | 0 | 0 | 3.0231e-05 | 2.5912e-05 | 0.001809 | 0.001809 | 0.0013047 | 0.0013047 | 0.010659 | 0.010659 | 0 | 0 | 0 | 0 | 0.0032979 | 0.0032979 | 0.0098448 | 0.0098448 | 0.028883 | 0.028883 | 159.4 | 151 | NO
2013-12-21 | 0.81929 | 0.81909 | 0 | 0 | 0.0037982 | 0.0037982 | 0.87535 | 0.8752 | 0.0056752 | 0.0051392 | 1.5981 | 1.598 | 0.0067326 | 0.0067221 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.012346 | 0.012337 | 0.00016158 | 0.00014057 | 0.0028109 | 0.0028023 | 0.028662 | 0.028662 | 0 | 0 | 0 | 0 | 0.034051 | 0.034051 | 0.040948 | 0.040948 | 0.015899 | 0.015899 | 92.8 | 86 | NO
2013-12-22 | 0.18306 | 0.18303 | 0 | 0 | 0.68991 | 0.68991 | 0.21799 | 0.21793 | 0.16878 | 0.16878 | 0.076534 | 0.076534 | 0.0019425 | 0.0019383 | 0 | 0 | 0.0074184 | 0.0074184 | 0.0023699 | 0.0023613 | 0.0014897 | 0.0014897 | 0.00093088 | 0.00093088 | 0.0014173 | 0.0014173 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011876 | 0.0011876 | 0.0048097 | 0.0048097 | 116.2 | 104 | NO
2013-12-23 | 0.28248 | 0.28233 | 0 | 0 | 0 | 0 | 0.081469 | 0.081425 | 0.29188 | 0.29188 | 0.75201 | 0.75147 | 0.0021191 | 0.0020907 | 0 | 0 | 0 | 0 | 0.0011855 | 0.0011812 | 0.0018116 | 0.0018116 | 0.0048097 | 0.0047026 | 0.006585 | 0.006585 | 0 | 0 | 0 | 0 | 0.0070234 | 0.0070234 | 0.0012703 | 0.0012703 | 0.011874 | 0.011874 | 168.6 | 133 | NO
2013-12-24 | 1.6873 | 1.6873 | 0 | 0 | 0 | 0 | 0.94811 | 0.94811 | 6.0616 | 6.0616 | 0.055071 | 0.055071 | 0.013963 | 0.013963 | 0 | 0 | 0 | 0 | 0.0087838 | 0.0087838 | 0.047462 | 0.047462 | 0.00079591 | 0.00079591 | 0.00045928 | 0.00045928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018725 | 0.0018725 | 173.8 | 149 | NO
2013-12-25 | 0.54737 | 0.54732 | 0 | 0 | 0 | 0 | 0.041192 | 0.041149 | 1.8329 | 1.8329 | 0.65529 | 0.6552 | 0.0091226 | 0.0091184 | 0 | 0 | 0 | 0 | 0.00086159 | 0.00085727 | 0.032698 | 0.032698 | 0.0088204 | 0.0088118 | 0.027251 | 0.027251 | 0 | 0 | 0 | 0 | 0.013632 | 0.013632 | 0.066324 | 0.066324 | 0.029971 | 0.029971 | 65.8 | 61 | NO
2013-12-26 | 0.73016 | 0.72994 | 0 | 0 | 0 | 0 | 1.218 | 1.2177 | 0.65915 | 0.65878 | 0.022538 | 0.022538 | 0.011475 | 0.011469 | 0 | 0 | 0 | 0 | 0.019205 | 0.019196 | 0.010432 | 0.010422 | 0.00016925 | 0.00016925 | 0.025089 | 0.025089 | 0 | 0 | 0 | 0 | 0.01421 | 0.01421 | 0.060834 | 0.060834 | 0.024486 | 0.024486 | 122.6 | 97 | NO
2013-12-27 | 0.578 | 0.57798 | 0 | 0 | 0 | 0 | 0.0065861 | 0.0065861 | 2.469 | 2.4689 | 0.33012 | 0.33012 | 0.0029504 | 0.0029483 | 0 | 0 | 0 | 0 | 0.00010797 | 0.00010797 | 0.011522 | 0.011512 | 0.0024188 | 0.0024188 | 0.010271 | 0.010271 | 0 | 0 | 0 | 0 | 0.0022868 | 0.0022868 | 0.016333 | 0.016333 | 0.024019 | 0.024019 | 144 | 107 | NO
2013-12-28 | 0.28743 | 0.28295 | 0 | 0 | 0 | 0 | 0.061289 | 0.061267 | 0.52659 | 0.52659 | 0.62082 | 0.60261 | 0.0061853 | 0.006157 | 0 | 0 | 0 | 0 | 0.0031273 | 0.003123 | 0.0069048 | 0.0069048 | 0.013382 | 0.013274 | 0.023356 | 0.023356 | 0 | 0 | 0 | 0 | 0.020293 | 0.020293 | 0.031684 | 0.031684 | 0.029119 | 0.029119 | 177.2 | 137 | NO
2013-12-29 | 0.92476 | 0.92472 | 0 | 0 | 0.10571 | 0.10571 | 0.30492 | 0.30483 | 0.81013 | 0.81013 | 2.4893 | 2.4893 | 0.0097161 | 0.0097119 | 0 | 0 | 0.0055638 | 0.0055638 | 0.0076355 | 0.0076269 | 0.0055136 | 0.0055136 | 0.019162 | 0.019162 | 0.0022586 | 0.0022586 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036823 | 0.0036823 | 0.0062055 | 0.0062055 | 110.2 | 93 | NO
2013-12-30 | 0.61806 | 0.61804 | 0 | 0 | 0 | 0 | 0.015929 | 0.015929 | 2.4512 | 2.4512 | 0.48941 | 0.48933 | 0.010952 | 0.010947 | 0 | 0 | 0 | 0 | 0.0001436 | 0.0001436 | 0.033847 | 0.033847 | 0.016764 | 0.016747 | 0.0017215 | 0.0017215 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012703 | 0.0012703 | 0.0059827 | 0.0059827 | 174.2 | 154 | NO
2013-12-31 | 0.058823 | 0.058823 | 0 | 0 | 0 | 0 | 0.024424 | 0.024424 | 0.086738 | 0.086738 | 0.12063 | 0.12063 | 0.0012228 | 0.0012228 | 0 | 0 | 0 | 0 | 0.0002046 | 0.0002046 | 0.0039332 | 0.0039332 | 0.0013722 | 0.0013722 | 0.0096723 | 0.0096723 | 0 | 0 | 0 | 0 | 0.0070709 | 0.0070709 | 0.0060482 | 0.0060482 | 0.020471 | 0.020471 | 100 | 94 | NO
2014-01-01 | 1.5314 | 1.5314 | 0 | 0 | 0 | 0 | 0.11614 | 0.11614 | 2.3964 | 2.3964 | 4.0591 | 4.0591 | 0.014293 | 0.014291 | 0 | 0 | 0 | 0 | 0.0058983 | 0.0058983 | 0.012442 | 0.012442 | 0.036424 | 0.036416 | 0.0035878 | 0.0035878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014627 | 0.014627 | 130.4 | 113 | NO
2014-01-02 | 6.4833 | 6.4832 | 0 | 0 | 0.85683 | 0.85683 | 4.6377 | 4.6375 | 7.7212 | 7.7211 | 10.8098 | 10.8097 | 0.043745 | 0.04373 | 0 | 0 | 0.0055638 | 0.0055638 | 0.03253 | 0.032513 | 0.049936 | 0.049926 | 0.072276 | 0.072259 | 0.026453 | 0.026453 | 0 | 0 | 0 | 0 | 0.0039894 | 0.0039894 | 0.074777 | 0.074777 | 0.038957 | 0.038957 | 798.2 | 609 | NO
2014-01-03 | 0.13824 | 0.13821 | 0 | 0 | 0 | 0 | 0.019574 | 0.019574 | 0.32979 | 0.32969 | 0.25582 | 0.25582 | 0.0012013 | 0.0011992 | 0 | 0 | 0 | 0 | 0.00018733 | 0.00018733 | 0.00088543 | 0.00087492 | 0.0038039 | 0.0038039 | 0.01163 | 0.01163 | 0 | 0 | 0 | 0 | 0.01616 | 0.01616 | 0.0095873 | 0.0095873 | 0.0075306 | 0.0075306 | 227.8 | 188 | NO
2014-01-04 | 0.24548 | 0.2452 | 0 | 0 | 0 | 0 | 0.10575 | 0.10523 | 0.063258 | 0.063143 | 0.73939 | 0.73939 | 0.0015478 | 0.0015205 | 0 | 0 | 0 | 0 | 0.00063917 | 0.00058735 | 0.00057408 | 0.00056357 | 0.0045741 | 0.0045741 | 0.0040939 | 0.0040939 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015738 | 0.015738 | 0.0038574 | 0.0038574 | 152.4 | 126 | NO
2014-01-05 | 0.31278 | 0.31224 | 0 | 0 | 0 | 0 | 0.059064 | 0.058861 | 0.60245 | 0.60245 | 0.66674 | 0.66493 | 0.0064481 | 0.006431 | 0 | 0 | 0 | 0 | 0.00036224 | 0.0003536 | 0.0049474 | 0.0049474 | 0.021536 | 0.021483 | 0.014174 | 0.014174 | 0 | 0 | 0 | 0 | 0.0063621 | 0.0063621 | 0.01387 | 0.01387 | 0.033855 | 0.033855 | 171 | 135 | NO
2014-01-06 | 8.1849 | 0 | 0 | 0 | 7.3442 | 0 | 0.27055 | 0 | 10.0109 | 0 | 23.6091 | 0 | 0.045486 | 0 | 0 | 0 | 0.011128 | 0 | 0.005908 | 0 | 0.091581 | 0 | 0.097438 | 0 | 0.059153 | 0 | 0 | 0 | 0.012611 | 0 | 0.011678 | 0 | 0.04256 | 0 | 0.18147 | 0 | 0 | 0 | YES
2014-01-07 | 0.36983 | 0.3698 | 0 | 0 | 0.79006 | 0.79006 | 0.0090305 | 0.0089657 | 0.058959 | 0.058959 | 1.3277 | 1.3277 | 0.0020119 | 0.0020098 | 0 | 0 | 0.011128 | 0.011128 | 0.00012092 | 0.00011661 | 0.00065553 | 0.00065553 | 0.005821 | 0.005821 | 0.00077038 | 0.00077038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0031408 | 0.0031408 | 290.4 | 170 | NO
2014-01-08 | 0.13441 | 0.13437 | 0 | 0 | 0 | 0 | 0.19982 | 0.19973 | 0.088352 | 0.088352 | 0.079431 | 0.079431 | 0.0023266 | 0.0023224 | 0 | 0 | 0 | 0 | 0.0042685 | 0.0042599 | 0.00054387 | 0.00054387 | 0.00057203 | 0.00057203 | 0.0061115 | 0.0061115 | 0 | 0 | 0 | 0 | 0.00018355 | 0.00018355 | 0.011282 | 0.011282 | 0.015353 | 0.015353 | 188.8 | 119 | NO
2014-01-09 | 0.24932 | 0.12847 | 0 | 0 | 0 | 0 | 0.15037 | 0.12119 | 0.56949 | 0.14311 | 0.25371 | 0.1666 | 0.0044262 | 0.0019964 | 0 | 0 | 0 | 0 | 0.0015639 | 0.00095984 | 0.010139 | 0.0016487 | 0.0066747 | 0.0048901 | 0.0024496 | 0.0024496 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098041 | 0.0098041 | 0.0019925 | 0.0019925 | 191.2 | 167 | NO
2014-01-10 | 0.05131 | 0.05086 | 0 | 0 | 0 | 0 | 0.0055987 | 0.0048948 | 0.091713 | 0.091713 | 0.12329 | 0.12286 | 0.00071415 | 0.00070784 | 0 | 0 | 0 | 0 | 0.00035792 | 0.00034928 | 0.00062269 | 0.00062269 | 0.0016936 | 0.001685 | 0.0041133 | 0.0041133 | 0 | 0 | 0 | 0 | 0.0025545 | 0.0025545 | 0.0049329 | 0.0049329 | 0.0076785 | 0.0076785 | 145.6 | 125 | NO
2014-01-11 | 0.068248 | 0.068248 | 0 | 0 | 0 | 0 | 0.061356 | 0.061356 | 0.053369 | 0.053369 | 0.11298 | 0.11298 | 0.00091226 | 0.00091226 | 0 | 0 | 0 | 0 | 0.00086807 | 0.00086807 | 0.0014332 | 0.0014332 | 0.00082805 | 0.00082805 | 0.00081504 | 0.00081504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033229 | 0.0033229 | 86.6 | 76 | NO
2014-01-12 | 0.42004 | 0.42004 | 0 | 0 | 0 | 0 | 0.060265 | 0.060265 | 0.031366 | 0.031366 | 1.5673 | 1.5673 | 0.010645 | 0.010645 | 0 | 0 | 0 | 0 | 0.0033065 | 0.0033065 | 0.0016789 | 0.0016789 | 0.035468 | 0.035468 | 0.00488 | 0.00488 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00096951 | 0.00096951 | 0.019105 | 0.019105 | 90.6 | 72 | NO
2014-01-13 | 1.0115 | 1.0115 | 0 | 0 | 0 | 0 | 0.40526 | 0.40526 | 1.124 | 1.124 | 2.4034 | 2.4034 | 0.013854 | 0.013854 | 0 | 0 | 0 | 0 | 0.0055701 | 0.0055701 | 0.015109 | 0.015109 | 0.03311 | 0.03311 | 0.010621 | 0.010621 | 0 | 0 | 0 | 0 | 0.002696 | 0.002696 | 0.017297 | 0.017297 | 0.023848 | 0.023848 | 203.6 | 160 | NO
2014-01-14 | 1.094 | 1.094 | 0 | 0 | 0 | 0 | 0.44902 | 0.44902 | 1.2781 | 1.2781 | 2.527 | 2.5269 | 0.021931 | 0.021929 | 0 | 0 | 0 | 0 | 0.0078482 | 0.0078482 | 0.057638 | 0.057638 | 0.026839 | 0.026831 | 0.0048522 | 0.0048522 | 0 | 0 | 0 | 0 | 0.0025545 | 0.0025545 | 0.0069245 | 0.0069245 | 0.0090668 | 0.0090668 | 315.8 | 233 | NO
2014-01-15 | 1.5485 | 1.4799 | 0 | 0 | 0 | 0 | 0.040644 | 0.040601 | 2.3643 | 2.3642 | 4.3048 | 4.0251 | 0.010133 | 0.0093023 | 0 | 0 | 0 | 0 | 0.00047452 | 0.0004702 | 0.018665 | 0.018654 | 0.025151 | 0.021781 | 0.007095 | 0.007095 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028179 | 0.028179 | 0.0059484 | 0.0059484 | 208 | 161 | NO
2014-01-16 | 0.76172 | 0.75513 | 0 | 0 | 0 | 0 | 0.97737 | 0.97737 | 1.1257 | 1.1256 | 0.24819 | 0.22141 | 0.0093422 | 0.0093139 | 0 | 0 | 0 | 0 | 0.0065737 | 0.0065737 | 0.023226 | 0.023216 | 0.0061048 | 0.0059977 | 0.0017034 | 0.0017034 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055635 | 0.0055635 | 0.0024081 | 0.0024081 | 189.4 | 163 | NO
2014-01-17 | 0.91445 | 0.91405 | 0 | 0 | 0 | 0 | 0.027541 | 0.026707 | 0.42751 | 0.42751 | 3.3249 | 3.3249 | 0.0045516 | 0.0045453 | 0 | 0 | 0 | 0 | 0.0001965 | 0.00018355 | 0.0024527 | 0.0024527 | 0.016167 | 0.016167 | 0.0035655 | 0.0035655 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041972 | 0.0041972 | 0.011114 | 0.011114 | 165.6 | 146 | NO
2014-01-18 | 0.15053 | 0.15053 | 0 | 0 | 0 | 0 | 0.0075017 | 0.0075017 | 0.066863 | 0.066863 | 0.54431 | 0.54431 | 0.0013017 | 0.0013017 | 0 | 0 | 0 | 0 | 2.5912e-05 | 2.5912e-05 | 0.0015791 | 0.0015791 | 0.0039678 | 0.0039678 | 0.0076709 | 0.0076709 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014272 | 0.014272 | 0.019636 | 0.019636 | 86.6 | 77 | NO
2014-01-19 | 0.59051 | 0.59051 | 0 | 0 | 0 | 0 | 0.061311 | 0.061311 | 0.11374 | 0.11374 | 2.1931 | 2.1931 | 0.0044486 | 0.0044486 | 0 | 0 | 0 | 0 | 0.00035252 | 0.00035252 | 0.00038097 | 0.00038097 | 0.017127 | 0.017127 | 0.015921 | 0.015921 | 0 | 0 | 0 | 0 | 0.010515 | 0.010515 | 0.03893 | 0.03893 | 0.012301 | 0.012301 | 87.6 | 75 | NO
2014-01-20 | 0.35173 | 0.35171 | 0 | 0 | 0 | 0 | 0.071836 | 0.071836 | 0.81971 | 0.81971 | 0.62302 | 0.62298 | 0.015552 | 0.01555 | 0 | 0 | 0 | 0 | 0.00087077 | 0.00087077 | 0.0054256 | 0.0054256 | 0.057252 | 0.057244 | 0.0046267 | 0.0046267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018863 | 0.018863 | 247.4 | 173 | NO
2014-01-21 | 0.52629 | 0.52621 | 0 | 0 | 0 | 0 | 0.88401 | 0.88384 | 0.27779 | 0.27779 | 0.16501 | 0.16501 | 0.0061267 | 0.0061225 | 0 | 0 | 0 | 0 | 0.0072139 | 0.0072053 | 0.0098553 | 0.0098553 | 0.0026277 | 0.0026277 | 0.014898 | 0.014898 | 0 | 0 | 0 | 0 | 0.020537 | 0.020537 | 0.015875 | 0.015875 | 0.00704 | 0.00704 | 251 | 176 | NO
2014-01-22 | 0.61021 | 0.31949 | 0 | 0 | 0 | 0 | 0.21973 | 0.21969 | 2.4751 | 1.0317 | 0.033497 | 0.025313 | 0.0064943 | 0.0062765 | 0 | 0 | 0 | 0 | 0.011528 | 0.011524 | 0.004058 | 0.0030727 | 0.00029351 | 0.00021746 | 0.011577 | 0.011577 | 0 | 0 | 0 | 0 | 0.0030166 | 0.0030166 | 0.025566 | 0.025566 | 0.020367 | 0.020367 | 179.6 | 150 | NO
2014-01-23 | 0.27923 | 0.27894 | 0 | 0 | 0.0027893 | 0.0027893 | 0.25391 | 0.25335 | 0.025695 | 0.025695 | 0.61321 | 0.61317 | 0.0050957 | 0.0050894 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.0062892 | 0.0062805 | 0.00026274 | 0.00026274 | 0.0080727 | 0.0080641 | 0.027891 | 0.027891 | 0 | 0 | 0 | 0 | 0.01411 | 0.01411 | 0.07544 | 0.07544 | 0.024197 | 0.024197 | 179.6 | 155 | NO
2014-01-24 | 0.58238 | 0.58233 | 0 | 0 | 0 | 0 | 0.026885 | 0.026885 | 2.0305 | 2.0305 | 0.66527 | 0.6651 | 0.0061832 | 0.006179 | 0 | 0 | 0 | 0 | 0.00045725 | 0.00045725 | 0.022948 | 0.022948 | 0.0055896 | 0.0055725 | 0.015344 | 0.015344 | 0 | 0 | 0 | 0 | 0.0046939 | 0.0046939 | 0.013853 | 0.013853 | 0.041949 | 0.041949 | 189.8 | 155 | NO
2014-01-25 | 0.14298 | 0.13815 | 0 | 0 | 0.0035015 | 0.0035015 | 0.15775 | 0.1577 | 0.084715 | 0.060666 | 0.20034 | 0.20034 | 0.0045361 | 0.0045043 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.008055 | 0.0080507 | 0.0014884 | 0.00134 | 0.0012876 | 0.0012876 | 0.00032528 | 0.00032528 | 0 | 0 | 0 | 0 | 0.00018355 | 0.00018355 | 0 | 0 | 0.00096195 | 0.00096195 | 114.4 | 98 | NO
2014-01-26 | 0.27158 | 0.27158 | 0 | 0 | 0 | 0 | 0.00076874 | 0.00076874 | 0.0010404 | 0.0010404 | 1.1049 | 1.1049 | 0.0011014 | 0.0011014 | 0 | 0 | 0 | 0 | 1.7275e-05 | 1.7275e-05 | 1.051e-05 | 1.051e-05 | 0.0044477 | 0.0044477 | 0.012406 | 0.012406 | 0 | 0 | 0 | 0 | 0.00966 | 0.00966 | 0.027718 | 0.027718 | 0.0088075 | 0.0088075 | 79.6 | 73 | NO
2014-01-27 | 0.057997 | 0.057997 | 0 | 0 | 0 | 0 | 0.064866 | 0.064866 | 0.080958 | 0.080958 | 0.041722 | 0.041722 | 0.00060537 | 0.00060537 | 0 | 0 | 0 | 0 | 0.00075524 | 0.00075524 | 0.00070414 | 0.00070414 | 0.00039528 | 0.00039528 | 0.0047686 | 0.0047686 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055398 | 0.0055398 | 0.014924 | 0.014924 | 64.8 | 65 | NO
2014-01-28 | 2.5756 | 1.6344 | 0 | 0 | 0.0037389 | 0.0037389 | 2.1991 | 2.1991 | 0.67189 | 0.67189 | 5.5888 | 1.7513 | 0.023244 | 0.019787 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.028579 | 0.028579 | 0.0077679 | 0.0077679 | 0.031714 | 0.01762 | 0.008034 | 0.008034 | 0 | 0 | 0 | 0 | 0.006328 | 0.006328 | 0.013241 | 0.013241 | 0.009401 | 0.009401 | 427.2 | 320 | NO
2014-01-29 | 0.072654 | 0.072276 | 0 | 0 | 0 | 0 | 0.010441 | 0.0096632 | 0.15939 | 0.15939 | 0.14553 | 0.14553 | 0.00073885 | 0.00073674 | 0 | 0 | 0 | 0 | 0.00047668 | 0.00047236 | 0.0014451 | 0.0014451 | 0.00088804 | 0.00088804 | 0.012667 | 0.012667 | 0 | 0 | 0 | 0 | 0.00017815 | 0.00017815 | 0.031568 | 0.031568 | 0.025546 | 0.025546 | 207.8 | 167 | NO
2014-01-30 | 0.15103 | 0.15076 | 0 | 0 | 0.0063501 | 0.0063501 | 0.042443 | 0.041907 | 0.15244 | 0.15244 | 0.40632 | 0.40628 | 0.0025673 | 0.0025631 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.0022101 | 0.0022058 | 0.0033565 | 0.0033565 | 0.0033358 | 0.0033272 | 0.011096 | 0.011096 | 0 | 0 | 0 | 0 | 0.010393 | 0.010393 | 0.019196 | 0.019196 | 0.0089618 | 0.0089618 | 183.8 | 136 | NO
2014-01-31 | 0.41423 | 0.41419 | 0 | 0 | 0 | 0 | 0.0080323 | 0.0079891 | 0.16077 | 0.16077 | 1.5418 | 1.5417 | 0.0013831 | 0.0013789 | 0 | 0 | 0 | 0 | 0.00037033 | 0.00036601 | 0.0024697 | 0.0024697 | 0.0028901 | 0.0028816 | 0.0050926 | 0.0050926 | 0 | 0 | 0 | 0 | 0.0038399 | 0.0038399 | 0.0079281 | 0.0079281 | 0.0066779 | 0.0066779 | 156.2 | 115 | NO
2014-02-01 | 0.07972 | 0.07972 | 0 | 0 | 0 | 0 | 0.015956 | 0.015956 | 0.2801 | 0.2801 | 0.064953 | 0.064953 | 0.00072203 | 0.00072203 | 0 | 0 | 0 | 0 | 0.00011769 | 0.00011769 | 0.0026996 | 0.0026996 | 0.00050883 | 0.00050883 | 0.0030216 | 0.0030216 | 0 | 0 | 0 | 0 | 0.0035117 | 0.0035117 | 0.00026274 | 0.00026274 | 0.0051365 | 0.0051365 | 74.6 | 65 | NO
2014-02-02 | 0.016385 | 0.016364 | 0 | 0 | 0 | 0 | 0.015878 | 0.015878 | 0.014536 | 0.014483 | 0.023442 | 0.0234 | 0.0013965 | 0.0013923 | 0 | 0 | 0 | 0 | 0.00021324 | 0.00021324 | 0.00017472 | 0.00016421 | 0.0051279 | 0.0051193 | 0.0103 | 0.0103 | 0 | 0 | 0 | 0 | 0.0084 | 0.0084 | 0.014916 | 0.014916 | 0.013163 | 0.013163 | 37 | 36 | NO
2014-02-03 | 0.56308 | 0.55394 | 0 | 0 | 0.24481 | 0.24481 | 0.13904 | 0.13895 | 0.66255 | 0.66255 | 1.4442 | 1.4071 | 0.0098987 | 0.0098924 | 0 | 0 | 0.0055638 | 0.0055638 | 0.0027743 | 0.0027656 | 0.012567 | 0.012567 | 0.023801 | 0.023793 | 0.0072778 | 0.0072778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029672 | 0.029672 | 234 | 164 | NO
2014-02-04 | 0.47983 | 0.46149 | 0 | 0 | 0.016691 | 0.016691 | 0.17085 | 0.16915 | 0.84438 | 0.75768 | 0.9263 | 0.9256 | 0.019139 | 0.018863 | 0 | 0 | 0.0055638 | 0.0055638 | 0.013656 | 0.013652 | 0.029709 | 0.028395 | 0.025902 | 0.025859 | 0.0069854 | 0.0069854 | 0 | 0 | 0 | 0 | 0.0039171 | 0.0039171 | 0.01395 | 0.01395 | 0.0093313 | 0.0093313 | 176.4 | 135 | NO
2014-02-05 | 0.17636 | 0.17634 | 0 | 0 | 0 | 0 | 0.058081 | 0.058076 | 0.14925 | 0.14915 | 0.48207 | 0.48207 | 0.0018442 | 0.00184 | 0 | 0 | 0 | 0 | 0.00043026 | 0.00042594 | 0.0017722 | 0.0017617 | 0.00522 | 0.00522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.8 | 120 | NO
2014-02-06 | 1.193 | 1.187 | 0 | 0 | 0.0034421 | 0.0034421 | 0.21376 | 0.21376 | 2.6294 | 2.5997 | 2.2951 | 2.2949 | 0.011266 | 0.01123 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.013126 | 0.013126 | 0.010297 | 0.010138 | 0.011479 | 0.011462 | 0.0022115 | 0.0022115 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0059169 | 0.0059169 | 0.0041917 | 0.0041917 | 175.4 | 135 | NO
2014-02-07 | 0.16781 | 0.16781 | 0 | 0 | 0 | 0 | 0.021749 | 0.021749 | 0.13246 | 0.13246 | 0.533 | 0.533 | 0.0013781 | 0.0013781 | 0 | 0 | 0 | 0 | 9.6632e-05 | 9.6632e-05 | 0.0013715 | 0.0013715 | 0.0043084 | 0.0043084 | 0.0068427 | 0.0068427 | 0 | 0 | 0 | 0 | 0.01043 | 0.01043 | 0 | 0 | 0.0072018 | 0.0072018 | 159.2 | 114 | NO
2014-02-08 | 0.38667 | 0.25114 | 0.27989 | 0.27989 | 0 | 0 | 0.11937 | 0.11937 | 0.54719 | 0.54719 | 0.8562 | 0.30366 | 0.02522 | 0.021832 | 0.0061767 | 0.0061767 | 0 | 0 | 0.010625 | 0.010625 | 0.062014 | 0.062014 | 0.030351 | 0.016537 | 0.0061341 | 0.0061341 | 0 | 0 | 0 | 0 | 0.00018355 | 0.00018355 | 0.023225 | 0.023225 | 0.0057064 | 0.0057064 | 82.2 | 72 | NO
2014-02-09 | 77.8086 | 0 | 0 | 0 | 0 | 0 | 29.2081 | 0 | 130.3256 | 0 | 152.9954 | 0 | 0.15564 | 0 | 0 | 0 | 0 | 0 | 0.080156 | 0 | 0.25929 | 0 | 0.26406 | 0 | 0.067646 | 0 | 0 | 0 | 0 | 0 | 0.028423 | 0 | 0.11387 | 0 | 0.12654 | 0 | 0 | 0 | YES
2014-02-10 | 2.857 | 2.8565 | 0 | 0 | 0 | 0 | 1.597 | 1.5963 | 2.3719 | 2.3716 | 6.5448 | 6.5445 | 0.0068362 | 0.0068151 | 0 | 0 | 0 | 0 | 0.0029168 | 0.0028995 | 0.019109 | 0.019077 | 0.0065012 | 0.0064755 | 0.049887 | 0.049887 | 0 | 0 | 0.21328 | 0.21328 | 0.070853 | 0.070853 | 0.016943 | 0.016943 | 0.018183 | 0.018183 | 2006.8 | 638 | NO
2014-02-11 | 0.31434 | 0.31434 | 0 | 0 | 0 | 0 | 0.03612 | 0.03612 | 0.29919 | 0.29919 | 0.96594 | 0.96594 | 0.00092303 | 0.00092303 | 0 | 0 | 0 | 0 | 0.00033416 | 0.00033416 | 0.0012322 | 0.0012322 | 0.0020953 | 0.0020953 | 0.059055 | 0.059055 | 0 | 0 | 0 | 0 | 0.0652 | 0.0652 | 0.11355 | 0.11355 | 0.018799 | 0.018799 | 475.8 | 349 | NO
2014-02-12 | 0.28254 | 0.28252 | 0 | 0 | 0 | 0 | 0.41804 | 0.41804 | 0.19828 | 0.19828 | 0.1607 | 0.16062 | 0.017264 | 0.017261 | 0 | 0 | 0 | 0 | 0.013807 | 0.013807 | 0.018562 | 0.018562 | 0.02785 | 0.027842 | 0.030873 | 0.030873 | 0 | 0 | 0 | 0 | 0.029644 | 0.029644 | 0.068249 | 0.068249 | 0.011395 | 0.011395 | 324.4 | 240 | NO
2014-02-13 | 0.2604 | 0.25802 | 0 | 0 | 0 | 0 | 0.019046 | 0.01883 | 0.098068 | 0.086718 | 0.94388 | 0.94388 | 0.0058569 | 0.0058243 | 0 | 0 | 0 | 0 | 0.00021486 | 0.00020622 | 0.00057934 | 0.00043746 | 0.02298 | 0.02298 | 0.042221 | 0.042221 | 0 | 0 | 0 | 0 | 0.045402 | 0.045402 | 0.040891 | 0.040891 | 0.048697 | 0.048697 | 233.2 | 165 | NO
2014-02-14 | 0.81092 | 0.8083 | 0 | 0 | 0 | 0 | 0.21582 | 0.21051 | 0.38557 | 0.38541 | 2.5634 | 2.5634 | 0.0073322 | 0.0073149 | 0 | 0 | 0 | 0 | 0.0050362 | 0.0050049 | 0.0021873 | 0.0021768 | 0.018116 | 0.018116 | 0.042827 | 0.042827 | 0 | 0 | 0.10386 | 0.10386 | 0.061727 | 0.061727 | 0.0089305 | 0.0089305 | 0.029841 | 0.029841 | 153.4 | 125 | NO
2014-02-15 | 2.7466 | 2.7465 | 0 | 0 | 0 | 0 | 0.023969 | 0.023947 | 0.16899 | 0.16899 | 11.0122 | 11.0122 | 0.013498 | 0.013495 | 0 | 0 | 0 | 0 | 0.00017923 | 0.00017491 | 0.0012073 | 0.0012073 | 0.053689 | 0.053689 | 0.022969 | 0.022969 | 0 | 0 | 0 | 0 | 0.0071718 | 0.0071718 | 0.050085 | 0.050085 | 0.038572 | 0.038572 | 224.6 | 208 | NO
2014-02-16 | 1.9187 | 1.9186 | 0 | 0 | 0 | 0 | 1.1124 | 1.1123 | 2.8025 | 2.8024 | 3.3299 | 3.3298 | 0.01923 | 0.019224 | 0 | 0 | 0 | 0 | 0.01525 | 0.015245 | 0.012673 | 0.012663 | 0.037808 | 0.0378 | 0.028482 | 0.028482 | 0 | 0 | 0 | 0 | 0.020619 | 0.020619 | 0.031676 | 0.031676 | 0.049377 | 0.049377 | 188.6 | 134 | NO
2014-02-17 | 0.36151 | 0.36149 | 0 | 0 | 0 | 0 | 0.0019515 | 0.0019515 | 0.47863 | 0.47863 | 1.0797 | 1.0796 | 0.012632 | 0.01263 | 0 | 0 | 0 | 0 | 0.00022242 | 0.00022242 | 0.016257 | 0.016257 | 0.037804 | 0.037796 | 0.02279 | 0.02279 | 0 | 0 | 0 | 0 | 0.014816 | 0.014816 | 0.032229 | 0.032229 | 0.037235 | 0.037235 | 191 | 98 | NO
2014-02-18 | 0.075902 | 0.075776 | 0 | 0 | 0 | 0 | 0.0020692 | 0.0018533 | 0.15707 | 0.15707 | 0.17727 | 0.17718 | 0.00078877 | 0.00076775 | 0 | 0 | 0 | 0 | 5.5604e-05 | 1.6735e-05 | 0.0016224 | 0.0016224 | 0.0017825 | 0.0017739 | 0.019696 | 0.019696 | 0 | 0 | 0 | 0 | 0.023485 | 0.023485 | 0.024988 | 0.024988 | 0.013324 | 0.013324 | 153.4 | 109 | NO
2014-02-19 | 0.40085 | 0.33693 | 0 | 0 | 1.8027 | 0 | 0.003658 | 0.0035716 | 0.30897 | 0.30884 | 1.1147 | 1.1147 | 0.0016711 | 0.001402 | 0 | 0 | 0.0074184 | 0 | 7.1259e-05 | 6.6941e-05 | 0.0017722 | 0.0017512 | 0.0041552 | 0.0041552 | 0.0037121 | 0.0037121 | 0 | 0 | 0 | 0 | 0.0037638 | 0.0037638 | 0.0019916 | 0.0019916 | 0.0060416 | 0.0060416 | 148.4 | 112 | NO
2014-02-20 | 0.51197 | 0.51197 | 0 | 0 | 0 | 0 | 0.010802 | 0.010802 | 0.039515 | 0.039515 | 2.0336 | 2.0336 | 0.001608 | 0.001608 | 0 | 0 | 0 | 0 | 0.00019596 | 0.00019596 | 0.0003455 | 0.0003455 | 0.0058852 | 0.0058852 | 0.026821 | 0.026821 | 0 | 0 | 0 | 0 | 0.012916 | 0.012916 | 0.042323 | 0.042323 | 0.049209 | 0.049209 | 197.4 | 150 | NO
2014-02-21 | 0.337 | 0.33603 | 0 | 0 | 0 | 0 | 0.027716 | 0.027716 | 0.2955 | 0.29066 | 1.078 | 1.078 | 0.0015894 | 0.0015873 | 0 | 0 | 0 | 0 | 0.00023267 | 0.00023267 | 0.0019246 | 0.0019141 | 0.0044488 | 0.0044488 | 0.005956 | 0.005956 | 0 | 0 | 0 | 0 | 0.0080302 | 0.0080302 | 0 | 0 | 0.008348 | 0.008348 | 177.6 | 144 | NO
2014-02-22 | 0.028133 | 0.028091 | 0 | 0 | 0 | 0 | 0.0011704 | 0.001084 | 0.03584 | 0.03584 | 0.08315 | 0.08315 | 0.00078535 | 0.00078115 | 0 | 0 | 0 | 0 | 2.1594e-05 | 1.2956e-05 | 0.00034944 | 0.00034944 | 0.0028741 | 0.0028741 | 0.00079823 | 0.00079823 | 0 | 0 | 0 | 0 | 0.00057385 | 0.00057385 | 0.0025945 | 0.0025945 | 0 | 0 | 52.6 | 47 | NO
2014-02-23 | 0.84078 | 0.8406 | 0 | 0 | 0 | 0 | 0.0045617 | 0.0045617 | 0.020093 | 0.020093 | 3.4024 | 3.4017 | 0.0028329 | 0.0028243 | 0 | 0 | 0 | 0 | 8.3136e-05 | 8.3136e-05 | 0.00033893 | 0.00033893 | 0.011108 | 0.011073 | 0.027797 | 0.027797 | 0 | 0 | 0 | 0 | 0.0042135 | 0.0042135 | 0.040036 | 0.040036 | 0.07232 | 0.07232 | 74.8 | 71 | NO
2014-02-24 | 2.8543 | 2.8541 | 0 | 0 | 0 | 0 | 2.8738 | 2.8735 | 0.29142 | 0.29142 | 5.6967 | 5.6967 | 0.016689 | 0.016673 | 0 | 0 | 0 | 0 | 0.017458 | 0.017423 | 0.0053257 | 0.0053257 | 0.029058 | 0.029058 | 0.0082416 | 0.0082416 | 0 | 0 | 0 | 0 | 3.401e-05 | 3.401e-05 | 0.0036455 | 0.0036455 | 0.030561 | 0.030561 | 189.4 | 132 | NO
2014-02-25 | 0.89426 | 0.89386 | 0.0090312 | 0.0090312 | 0 | 0 | 0.76669 | 0.76667 | 0.18904 | 0.18707 | 1.9692 | 1.9692 | 0.0061853 | 0.0061811 | 6.4508e-05 | 6.4508e-05 | 0 | 0 | 0.0038934 | 0.003889 | 0.0063819 | 0.0063714 | 0.012279 | 0.012279 | 0.0029535 | 0.0029535 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048817 | 0.0048817 | 0.0080609 | 0.0080609 | 182.6 | 147 | NO
2014-02-26 | 0.74918 | 0.74912 | 0 | 0 | 0 | 0 | 0.018378 | 0.018357 | 0.039441 | 0.039441 | 2.9857 | 2.9856 | 0.0022155 | 0.0022092 | 0 | 0 | 0 | 0 | 0.00030069 | 0.00029637 | 0.00073698 | 0.00073698 | 0.0078349 | 0.0078177 | 0.0015221 | 0.0015221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062055 | 0.0062055 | 156.8 | 116 | NO
2014-02-27 | 0.040251 | 0.040188 | 0 | 0 | 0 | 0 | 0.0022819 | 0.0021524 | 0.11023 | 0.11023 | 0.06969 | 0.06969 | 0.00037652 | 0.00037021 | 0 | 0 | 0 | 0 | 7.2879e-05 | 5.9923e-05 | 0.0014109 | 0.0014109 | 0.00023995 | 0.00023995 | 0.0023768 | 0.0023768 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092471 | 0.0092471 | 0.0021499 | 0.0021499 | 129.4 | 113 | NO
2014-02-28 | 0.35776 | 0.35677 | 0 | 0 | 0.0039169 | 0.0039169 | 0.0015288 | 0.0015072 | 0.29999 | 0.29508 | 1.2104 | 1.2104 | 0.016259 | 0.016246 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 5.2905e-05 | 4.8586e-05 | 0.011794 | 0.01174 | 0.056557 | 0.056557 | 0.0051583 | 0.0051583 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012284 | 0.012284 | 0.011013 | 0.011013 | 107.2 | 96 | NO
2014-03-01 | 0.12978 | 0.12976 | 0 | 0 | 0 | 0 | 0.0027991 | 0.0027559 | 0.29996 | 0.29996 | 0.27897 | 0.27897 | 0.0011267 | 0.0011246 | 0 | 0 | 0 | 0 | 0.00018409 | 0.00017977 | 0.0017012 | 0.0017012 | 0.0028409 | 0.0028409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.6 | 58 | NO
2014-03-02 | 0.037615 | 0.037594 | 0 | 0 | 0 | 0 | 0.0091341 | 0.0091341 | 0.12049 | 0.12039 | 0.036978 | 0.036978 | 0.0010305 | 0.0010284 | 0 | 0 | 0 | 0 | 0.0011418 | 0.0011418 | 0.0018182 | 0.0018076 | 0.00045312 | 0.00045312 | 0.0036469 | 0.0036469 | 0 | 0 | 0 | 0 | 0.003164 | 0.003164 | 0.0038504 | 0.0038504 | 0.0054503 | 0.0054503 | 47.8 | 44 | NO
2014-03-03 | 0.18682 | 0.18527 | 0 | 0 | 0 | 0 | 0.01097 | 0.0081624 | 0.070414 | 0.069489 | 0.68249 | 0.68249 | 0.00089176 | 0.00087705 | 0 | 0 | 0 | 0 | 0.00034982 | 0.00032822 | 0.00080135 | 0.00078033 | 0.0022881 | 0.0022881 | 0.012818 | 0.012818 | 0 | 0 | 0 | 0 | 0.013257 | 0.013257 | 0.0075866 | 0.0075866 | 0.019766 | 0.019766 | 166.8 | 142 | NO
2014-03-04 | 0.23122 | 0.23117 | 0 | 0 | 0.094584 | 0.094584 | 0.044685 | 0.044577 | 0.46363 | 0.46363 | 0.4623 | 0.4623 | 0.0085414 | 0.0085372 | 0 | 0 | 0.0055638 | 0.0055638 | 0.0025902 | 0.0025815 | 0.012663 | 0.012663 | 0.018554 | 0.018554 | 0.010721 | 0.010721 | 0 | 0 | 0 | 0 | 0.0094975 | 0.0094975 | 0.023093 | 0.023093 | 0.006032 | 0.006032 | 136.8 | 117 | NO
2014-03-05 | 3.9092 | 3.9085 | 0.0029674 | 0 | 0 | 0 | 0.015774 | 0.015645 | 1.988 | 1.9879 | 14.2847 | 14.2829 | 0.017011 | 0.016999 | 6.4508e-05 | 0 | 0 | 0 | 0.00032175 | 0.00030879 | 0.013103 | 0.013092 | 0.058023 | 0.058015 | 0.033544 | 0.033544 | 0 | 0 | 0 | 0 | 0.014381 | 0.014381 | 0.043613 | 0.043613 | 0.072657 | 0.072657 | 428.2 | 354 | NO
2014-03-06 | 0.36555 | 0.36555 | 0 | 0 | 0.0024926 | 0.0024926 | 0.0066401 | 0.0066401 | 0.50953 | 0.50953 | 1.0613 | 1.0613 | 0.0032 | 0.0032 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 7.1259e-05 | 7.1259e-05 | 0.0036232 | 0.0036232 | 0.0099419 | 0.0099419 | 0.0015865 | 0.0015865 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064056 | 0.0064056 | 0.0012448 | 0.0012448 | 160.4 | 148 | NO
2014-03-07 | 0.22692 | 0.22686 | 0 | 0 | 0 | 0 | 0.12288 | 0.12279 | 0.026135 | 0.026135 | 0.66002 | 0.65993 | 0.0052442 | 0.00524 | 0 | 0 | 0 | 0 | 0.0075513 | 0.007547 | 0.00020625 | 0.00020625 | 0.006228 | 0.0062195 | 0.0069428 | 0.0069428 | 0 | 0 | 0 | 0 | 0.0038399 | 0.0038399 | 0.017418 | 0.017418 | 0.006483 | 0.006483 | 135.4 | 119 | NO
2014-03-08 | 4.3307 | 4.3303 | 0 | 0 | 0 | 0 | 0.34372 | 0.34372 | 11.6231 | 11.6212 | 7.4965 | 7.4964 | 0.0041359 | 0.0041317 | 0 | 0 | 0 | 0 | 0.0016606 | 0.0016606 | 0.0090106 | 0.0090001 | 0.0062195 | 0.0062109 | 0.003725 | 0.003725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015187 | 0.015187 | 84.6 | 75 | NO
2014-03-09 | 0.1537 | 0.1535 | 0 | 0 | 0 | 0 | 0.25203 | 0.25186 | 0.093714 | 0.093714 | 0.050109 | 0.049629 | 0.0043776 | 0.0043734 | 0 | 0 | 0 | 0 | 0.0078758 | 0.0078715 | 0.0019311 | 0.0019311 | 0.00064487 | 0.0006363 | 0.015812 | 0.015812 | 0 | 0 | 0 | 0 | 0.0022835 | 0.0022835 | 0.040135 | 0.040135 | 0.027208 | 0.027208 | 115.2 | 102 | NO
2014-03-10 | 0.13212 | 0.1315 | 0 | 0 | 0 | 0 | 0.045312 | 0.045312 | 0.28432 | 0.28123 | 0.21689 | 0.21689 | 0.0029302 | 0.0029215 | 0 | 0 | 0 | 0 | 0.0026344 | 0.0026344 | 0.0020678 | 0.0020244 | 0.0050326 | 0.0050326 | 0.01874 | 0.01874 | 0 | 0 | 0 | 0 | 0.005372 | 0.005372 | 0.042163 | 0.042163 | 0.031361 | 0.031361 | 85.6 | 80 | NO
2014-03-11 | 1.6236 | 1.5192 | 0 | 0 | 0.012463 | 0.012463 | 0.20542 | 0.20533 | 1.3147 | 1.3147 | 5.1378 | 4.7124 | 0.016714 | 0.015042 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.0025999 | 0.0025912 | 0.014469 | 0.014469 | 0.051175 | 0.044375 | 0.064934 | 0.064934 | 0 | 0 | 0 | 0 | 0.0042135 | 0.0042135 | 0.092137 | 0.092137 | 0.18124 | 0.18124 | 658.4 | 376 | NO
2014-03-12 | 0.22272 | 0.21967 | 0 | 0 | 0 | 0 | 0.0064646 | 0.0064646 | 0.4268 | 0.4268 | 0.54719 | 0.53472 | 0.0014942 | 0.00149 | 0 | 0 | 0 | 0 | 0.00018733 | 0.00018733 | 0.0035273 | 0.0035273 | 0.0028441 | 0.0028269 | 0.0091586 | 0.0091586 | 0 | 0 | 0 | 0 | 0.0034275 | 0.0034275 | 0.0047004 | 0.0047004 | 0.026705 | 0.026705 | 304.4 | 241 | NO
2014-03-13 | 0.6793 | 0.40653 | 0 | 0 | 0 | 0 | 0.0010926 | 0.0010063 | 1.2748 | 1.2748 | 1.7279 | 0.61595 | 0.0036722 | 0.0019696 | 0 | 0 | 0 | 0 | 3.0231e-05 | 1.7275e-05 | 0.006265 | 0.006265 | 0.0098027 | 0.0028869 | 0.0014927 | 0.0014927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0060856 | 0.0060856 | 136.8 | 119 | NO
2014-03-14 | 0.097101 | 0.09658 | 0 | 0 | 0 | 0 | 0.00063486 | 0.00063486 | 0.39849 | 0.39838 | 0.069685 | 0.067645 | 0.00050894 | 0.00049843 | 0 | 0 | 0 | 0 | 1.2956e-05 | 1.2956e-05 | 0.0019942 | 0.0019837 | 0.00042313 | 0.00038885 | 0.013527 | 0.013527 | 0 | 0 | 0 | 0 | 0.010456 | 0.010456 | 0.0083446 | 0.0083446 | 0.027599 | 0.027599 | 153.8 | 145 | NO
2014-03-15 | 0.49265 | 0.49259 | 0 | 0 | 0 | 0 | 0.00081625 | 0.00077306 | 0.15454 | 0.15454 | 1.8809 | 1.8807 | 0.0024005 | 0.0023942 | 0 | 0 | 0 | 0 | 1.2956e-05 | 8.6375e-06 | 0.0030412 | 0.0030412 | 0.007281 | 0.0072639 | 0.010085 | 0.010085 | 0 | 0 | 0 | 0 | 0.0070369 | 0.0070369 | 0.015088 | 0.015088 | 0.01485 | 0.01485 | 144.8 | 128 | NO
2014-03-16 | 0.059722 | 0.059029 | 0 | 0 | 0 | 0 | 0.01011 | 0.0099374 | 0.23599 | 0.23294 | 0.030991 | 0.030991 | 0.00030137 | 0.00028876 | 0 | 0 | 0 | 0 | 0.00015116 | 0.00013388 | 0.00097082 | 0.0009498 | 0.00013712 | 0.00013712 | 0.0025623 | 0.0025623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010446 | 0.010446 | 72.6 | 68 | NO
2014-03-17 | 0.32204 | 0.322 | 0 | 0 | 0 | 0 | 0.5257 | 0.52566 | 0.055264 | 0.055159 | 0.22473 | 0.22473 | 0.0025006 | 0.0024964 | 0 | 0 | 0 | 0 | 0.0038458 | 0.0038415 | 0.00053336 | 0.00052285 | 0.0021285 | 0.0021285 | 0.0044959 | 0.0044959 | 0 | 0 | 0 | 0 | 0.0025545 | 0.0025545 | 0.01304 | 0.01304 | 0.0026277 | 0.0026277 | 244 | 208 | NO
2014-03-18 | 0.26312 | 0.26294 | 0 | 0 | 0 | 0 | 0.012665 | 0.012665 | 0.25836 | 0.25741 | 0.83695 | 0.83695 | 0.0031115 | 0.0031094 | 0 | 0 | 0 | 0 | 0.00039085 | 0.00039085 | 0.0033407 | 0.0033302 | 0.0091857 | 0.0091857 | 0.0051596 | 0.0051596 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00096951 | 0.00096951 | 0.020245 | 0.020245 | 214.2 | 185 | NO
2014-03-19 | 0.20686 | 0.20567 | 0 | 0 | 0 | 0 | 0.016624 | 0.014249 | 0.62172 | 0.62172 | 0.30342 | 0.30329 | 0.0010628 | 0.0010541 | 0 | 0 | 0 | 0 | 0.00024563 | 0.00024131 | 0.0010904 | 0.0010904 | 0.0029565 | 0.0029298 | 0.019308 | 0.019308 | 0 | 0 | 0 | 0 | 0.0034949 | 0.0034949 | 0.027492 | 0.027492 | 0.049366 | 0.049366 | 166.4 | 150 | NO
2014-03-20 | 0.23716 | 0.22846 | 0 | 0 | 0 | 0 | 0.0032347 | 0.0031916 | 0.090146 | 0.090146 | 0.88697 | 0.85158 | 0.0019751 | 0.0019446 | 0 | 0 | 0 | 0 | 2.5912e-05 | 2.1594e-05 | 0.0012782 | 0.0012782 | 0.0069586 | 0.0068429 | 0.0035894 | 0.0035894 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013394 | 0.013394 | 0.0037118 | 0.0037118 | 147.6 | 136 | NO
2014-03-21 | 2.6636 | 2.6624 | 0 | 0 | 0 | 0 | 1.0691 | 1.0668 | 6.2682 | 6.2682 | 3.6269 | 3.6263 | 0.022022 | 0.022016 | 0 | 0 | 0 | 0 | 0.017594 | 0.017585 | 0.043071 | 0.043071 | 0.019752 | 0.019744 | 0.012152 | 0.012152 | 0 | 0 | 0 | 0 | 0.016322 | 0.016322 | 0.017427 | 0.017427 | 0.0029469 | 0.0029469 | 241.8 | 207 | NO
2014-03-22 | 0.55213 | 0.55107 | 0 | 0 | 0 | 0 | 0.12624 | 0.1262 | 0.50484 | 0.50473 | 1.5889 | 1.5847 | 0.0072907 | 0.0072839 | 0 | 0 | 0 | 0 | 0.0013788 | 0.0013744 | 0.015224 | 0.015214 | 0.014574 | 0.014563 | 0.0014701 | 0.0014701 | 0 | 0 | 0 | 0 | 8.7995e-05 | 8.7995e-05 | 0.0044035 | 0.0044035 | 0.0022281 | 0.0022281 | 96.2 | 88 | NO
2014-03-23 | 0.20098 | 0.20096 | 0 | 0 | 0 | 0 | 0.080781 | 0.080738 | 0.057131 | 0.057131 | 0.6125 | 0.6125 | 0.008961 | 0.0089589 | 0 | 0 | 0 | 0 | 0.0037994 | 0.0037951 | 0.0022963 | 0.0022963 | 0.027122 | 0.027122 | 0.011515 | 0.011515 | 0 | 0 | 0 | 0 | 0.011349 | 0.011349 | 0.0093863 | 0.0093863 | 0.016774 | 0.016774 | 45.6 | 45 | NO
2014-03-24 | 0.77971 | 0.77971 | 0 | 0 | 4.0546 | 4.0546 | 0.12847 | 0.12847 | 0.091885 | 0.091885 | 2.2635 | 2.2635 | 0.0072989 | 0.0072989 | 0 | 0 | 0.035297 | 0.035297 | 0.0012406 | 0.0012406 | 0.0011587 | 0.0011587 | 0.021254 | 0.021254 | 0.0055505 | 0.0055505 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011197 | 0.011197 | 0.013499 | 0.013499 | 302.4 | 253 | NO
2014-03-25 | 0.63774 | 0.63772 | 0 | 0 | 0 | 0 | 0.0013107 | 0.0013107 | 0.016809 | 0.016809 | 2.5837 | 2.5837 | 0.010412 | 0.01041 | 0 | 0 | 0 | 0 | 0.00027856 | 0.00027856 | 0.00030346 | 0.00030346 | 0.04165 | 0.041641 | 0.022558 | 0.022558 | 0 | 0 | 0 | 0 | 0.0033794 | 0.0033794 | 0.10145 | 0.10145 | 0.0025409 | 0.0025409 | 201.2 | 170 | NO
2014-03-26 | 0.45344 | 0.45344 | 0 | 0 | 0 | 0 | 0.025271 | 0.025271 | 0.074678 | 0.074678 | 1.7376 | 1.7376 | 0.002056 | 0.002056 | 0 | 0 | 0 | 0 | 0.0006111 | 0.0006111 | 0.0014201 | 0.0014201 | 0.0060117 | 0.0060117 | 0.0056228 | 0.0056228 | 0 | 0 | 0 | 0 | 0.0070282 | 0.0070282 | 0.00015107 | 0.00015107 | 0.0088547 | 0.0088547 | 144.4 | 119 | NO
2014-03-27 | 1.2803 | 1.2803 | 0 | 0 | 0 | 0 | 0.42897 | 0.42888 | 0.74671 | 0.7467 | 3.7598 | 3.7598 | 0.02365 | 0.023641 | 0 | 0 | 0 | 0 | 0.015322 | 0.015309 | 0.019092 | 0.019081 | 0.050448 | 0.050448 | 0.0068782 | 0.0068782 | 0 | 0 | 0 | 0 | 0.01049 | 0.01049 | 0.0037532 | 0.0037532 | 0.004166 | 0.004166 | 207.6 | 145 | NO
2014-03-28 | 1.4302 | 1.43 | 0 | 0 | 0.11128 | 0.11128 | 1.086 | 1.0855 | 0.74417 | 0.74417 | 3.0531 | 3.0531 | 0.02747 | 0.027463 | 0 | 0 | 0.0055638 | 0.0055638 | 0.017152 | 0.017144 | 0.016692 | 0.016692 | 0.063543 | 0.063535 | 0.015953 | 0.015953 | 0 | 0 | 0 | 0 | 0.010041 | 0.010041 | 0.020453 | 0.020453 | 0.028441 | 0.028441 | 242 | 158 | NO
2014-03-29 | 0.027925 | 0.027925 | 0 | 0 | 0 | 0 | 0.016182 | 0.016182 | 0.0074145 | 0.0074145 | 0.075692 | 0.075692 | 0.00043169 | 0.00043169 | 0 | 0 | 0 | 0 | 0.00033254 | 0.00033254 | 0.00019443 | 0.00019443 | 0.0009416 | 0.0009416 | 0.010818 | 0.010818 | 0 | 0 | 0 | 0 | 0.0059091 | 0.0059091 | 0.022945 | 0.022945 | 0.01367 | 0.01367 | 83.6 | 82 | NO
2014-03-30 | 0.10469 | 0.10469 | 0 | 0 | 0 | 0 | 0.0024595 | 0.0024595 | 0.036284 | 0.036284 | 0.39235 | 0.39235 | 0.00089938 | 0.00089938 | 0 | 0 | 0 | 0 | 5.8303e-05 | 5.8303e-05 | 0.00057802 | 0.00057802 | 0.0030797 | 0.0030797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 58 | NO
2014-03-31 | 0.035672 | 0.035305 | 0 | 0 | 0 | 0 | 0.00031527 | 0.00022889 | 0.017781 | 0.016152 | 0.13031 | 0.13031 | 0.00029796 | 0.00028955 | 0 | 0 | 0 | 0 | 1.2956e-05 | 4.3187e-06 | 0.00018917 | 0.00016815 | 0.0010348 | 0.0010348 | 0.0025615 | 0.0025615 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019916 | 0.0019916 | 0.0088193 | 0.0088193 | 198.6 | 150 | NO
2014-04-01 | 0.30161 | 0.30159 | 0 | 0 | 0 | 0 | 0.056435 | 0.056392 | 0.64986 | 0.64986 | 0.58775 | 0.58775 | 0.0061147 | 0.0061126 | 0 | 0 | 0 | 0 | 0.0011985 | 0.0011941 | 0.012635 | 0.012635 | 0.012248 | 0.012248 | 0.012587 | 0.012587 | 0 | 0 | 0 | 0 | 0.014056 | 0.014056 | 0.0030031 | 0.0030031 | 0.020974 | 0.020974 | 134.4 | 112 | NO
2014-04-02 | 0.084964 | 0.084943 | 0 | 0 | 0 | 0 | 0.013505 | 0.013462 | 0.027325 | 0.027325 | 0.29732 | 0.29732 | 0.0010964 | 0.0010922 | 0 | 0 | 0 | 0 | 0.00014684 | 0.0001382 | 0.00026274 | 0.00026274 | 0.0039646 | 0.0039646 | 0.019887 | 0.019887 | 0 | 0 | 0.035237 | 0.035237 | 0.030673 | 0.030673 | 0 | 0 | 0.015123 | 0.015123 | 157.8 | 138 | NO
2014-04-03 | 0.050517 | 0.049796 | 0 | 0 | 0 | 0 | 0.0023321 | 0.00093717 | 0.070607 | 0.070607 | 0.14375 | 0.14358 | 0.00034131 | 0.0003329 | 0 | 0 | 0 | 0 | 2.5912e-05 | 1.2956e-05 | 0.00060693 | 0.00060693 | 0.00084519 | 0.00083662 | 0.0066052 | 0.0066052 | 0 | 0 | 0 | 0 | 0.0091628 | 0.0091628 | 0.0037821 | 0.0037821 | 0.0056635 | 0.0056635 | 130.2 | 117 | NO
2014-04-04 | 0.68565 | 0.68565 | 0 | 0 | 0 | 0 | 0.0053682 | 0.0053682 | 0.96863 | 0.96863 | 1.9949 | 1.9949 | 0.021611 | 0.021611 | 0 | 0 | 0 | 0 | 4.3187e-06 | 4.3187e-06 | 0.012664 | 0.012664 | 0.077772 | 0.077772 | 0.0076709 | 0.0076709 | 0 | 0 | 0 | 0 | 0.0028396 | 0.0028396 | 0.010307 | 0.010307 | 0.017235 | 0.017235 | 183 | 127 | NO
2014-04-05 | 1.0513 | 1.0513 | 0 | 0 | 0 | 0 | 0.00060031 | 0.00060031 | 0.42022 | 0.42022 | 3.9424 | 3.9424 | 0.020522 | 0.020522 | 0 | 0 | 0 | 0 | 8.6375e-06 | 8.6375e-06 | 0.0079347 | 0.0079347 | 0.07718 | 0.07718 | 0.015746 | 0.015746 | 0 | 0 | 0 | 0 | 0.0064808 | 0.0064808 | 0.02658 | 0.02658 | 0.029662 | 0.029662 | 80 | 64 | NO
2014-04-06 | 0.35144 | 0.35144 | 0 | 0 | 0 | 0 | 0.39611 | 0.39611 | 0.38573 | 0.38573 | 0.33227 | 0.33227 | 0.0050424 | 0.0050424 | 0 | 0 | 0 | 0 | 0.0075465 | 0.0075465 | 0.0038925 | 0.0038925 | 0.0024092 | 0.0024092 | 0.0028479 | 0.0028479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011611 | 0.011611 | 56.2 | 56 | NO
2014-04-07 | 0.29141 | 0.28543 | 0 | 0 | 0 | 0 | 0.066864 | 0.066756 | 0.64005 | 0.61531 | 0.5335 | 0.52948 | 0.0019811 | 0.0019375 | 0 | 0 | 0 | 0 | 0.00019758 | 0.00019326 | 0.0059747 | 0.0058 | 0.002813 | 0.0027862 | 0.013024 | 0.013024 | 0 | 0 | 0 | 0 | 0.0075179 | 0.0075179 | 0.04597 | 0.04597 | 0.00069736 | 0.00069736 | 174.4 | 141 | NO
2014-04-08 | 0.052059 | 0.052059 | 0 | 0 | 0 | 0 | 0.00097172 | 0.00097172 | 0.12957 | 0.12957 | 0.10466 | 0.10466 | 0.0012919 | 0.0012919 | 0 | 0 | 0 | 0 | 1.7275e-05 | 1.7275e-05 | 0.0013623 | 0.0013623 | 0.004122 | 0.004122 | 0.0065503 | 0.0065503 | 0 | 0 | 0 | 0 | 0.0032979 | 0.0032979 | 0.0016907 | 0.0016907 | 0.018783 | 0.018783 | 100.8 | 86 | NO
2014-04-09 | 0.23843 | 0.16866 | 0 | 0 | 0 | 0 | 0.20314 | 0.20314 | 0.16884 | 0.16868 | 0.43132 | 0.14698 | 0.0043766 | 0.0035442 | 0 | 0 | 0 | 0 | 0.0057412 | 0.0057412 | 0.0025407 | 0.0025302 | 0.0043791 | 0.00099409 | 0.0052783 | 0.0052783 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01024 | 0.01024 | 0.01317 | 0.01317 | 163 | 148 | NO
2014-04-10 | 0.43246 | 0.43246 | 0 | 0 | 0 | 0 | 0.033925 | 0.033925 | 1.4822 | 1.4822 | 0.4872 | 0.4872 | 0.0046251 | 0.0046251 | 0 | 0 | 0 | 0 | 0.0030841 | 0.0030841 | 0.011663 | 0.011663 | 0.0032265 | 0.0032265 | 0.0055752 | 0.0055752 | 0 | 0 | 0 | 0 | 0.0069624 | 0.0069624 | 0.0001156 | 0.0001156 | 0.0088204 | 0.0088204 | 194.2 | 157 | NO
2014-04-11 | 0.30715 | 0.30713 | 0 | 0 | 0 | 0 | 0.0077025 | 0.0076593 | 0.048917 | 0.048917 | 1.1971 | 1.1971 | 0.0049155 | 0.0049134 | 0 | 0 | 0 | 0 | 7.9897e-05 | 7.5578e-05 | 0.00047818 | 0.00047818 | 0.019492 | 0.019492 | 0.0050721 | 0.0050721 | 0 | 0 | 0 | 0 | 0.0019316 | 0.0019316 | 0.01604 | 0.01604 | 0.0037664 | 0.0037664 | 166.2 | 136 | NO
2014-04-12 | 1.4625 | 1.4625 | 0 | 0 | 0 | 0 | 0.18124 | 0.18124 | 0.064883 | 0.064883 | 5.5501 | 5.5501 | 0.018697 | 0.018697 | 0 | 0 | 0 | 0 | 0.0084799 | 0.0084799 | 0.0016237 | 0.0016237 | 0.058077 | 0.058077 | 0.0086872 | 0.0086872 | 0 | 0 | 0 | 0 | 0.0050627 | 0.0050627 | 0.0026142 | 0.0026142 | 0.02324 | 0.02324 | 75.8 | 70 | NO
2014-04-13 | 0.015163 | 0.015058 | 0 | 0 | 0.0035015 | 0.0035015 | 0.0010926 | 0.00087671 | 0.00094586 | 0.00094586 | 0.058373 | 0.058373 | 0.0013581 | 0.001356 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 1.7275e-05 | 1.2956e-05 | 2.1019e-05 | 2.1019e-05 | 0.0054771 | 0.0054771 | 0.0025531 | 0.0025531 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062335 | 0.0062335 | 0.0053261 | 0.0053261 | 49.4 | 47 | NO
2014-04-14 | 0.24965 | 0.24964 | 0 | 0 | 0 | 0 | 0.0017232 | 0.0017016 | 0.48315 | 0.48315 | 0.62041 | 0.62041 | 0.0025568 | 0.0025547 | 0 | 0 | 0 | 0 | 4.3187e-05 | 3.8869e-05 | 0.0051707 | 0.0051707 | 0.006122 | 0.006122 | 0.0095905 | 0.0095905 | 0 | 0 | 0 | 0 | 0.013412 | 0.013412 | 0.0049802 | 0.0049802 | 0.0084251 | 0.0084251 | 180.2 | 152 | NO
2014-04-15 | 0.078634 | 0.078544 | 0 | 0 | 0 | 0 | 0.026379 | 0.026293 | 0.17217 | 0.17195 | 0.12785 | 0.12783 | 0.00082056 | 0.00081005 | 0 | 0 | 0 | 0 | 0.00025481 | 0.00024185 | 0.0014779 | 0.0014674 | 0.0016347 | 0.0016261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.4 | 114 | NO
2014-04-16 | 0.54837 | 0.54835 | 0 | 0 | 0 | 0 | 0.088627 | 0.088627 | 0.96738 | 0.96731 | 1.271 | 1.271 | 0.0069218 | 0.0069197 | 0 | 0 | 0 | 0 | 0.0011769 | 0.0011769 | 0.012919 | 0.012908 | 0.01535 | 0.01535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.8 | 92 | NO
2014-04-17 | 0.75871 | 0.75842 | 0 | 0 | 0 | 0 | 0.41996 | 0.4199 | 1.961 | 1.961 | 0.66089 | 0.65982 | 0.0085729 | 0.0085445 | 0 | 0 | 0 | 0 | 0.0037719 | 0.0037676 | 0.024847 | 0.024847 | 0.0072061 | 0.0070989 | 0.014997 | 0.014997 | 0 | 0 | 0 | 0 | 0.0079265 | 0.0079265 | 0.029793 | 0.029793 | 0.021119 | 0.021119 | 146.6 | 103 | NO
2014-04-18 | 0.42603 | 0.42603 | 0 | 0 | 0 | 0 | 0.16941 | 0.16941 | 0.68494 | 0.68494 | 0.84223 | 0.84223 | 0.0053903 | 0.0053903 | 0 | 0 | 0 | 0 | 0.003259 | 0.003259 | 0.0056804 | 0.0056804 | 0.010877 | 0.010877 | 0.0085361 | 0.0085361 | 0 | 0 | 0 | 0 | 0.0026992 | 0.0026992 | 0.018971 | 0.018971 | 0.013976 | 0.013976 | 77.6 | 67 | NO
2014-04-19 | 0.070827 | 0.070659 | 0 | 0 | 0 | 0 | 0.015436 | 0.01509 | 0.086007 | 0.086007 | 0.188 | 0.188 | 0.0010347 | 0.0010326 | 0 | 0 | 0 | 0 | 0.00023807 | 0.00023375 | 0.0012099 | 0.0012099 | 0.0027594 | 0.0027594 | 0.0012664 | 0.0012664 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062361 | 0.0062361 | 7.8199e-05 | 7.8199e-05 | 86 | 73 | NO
2014-04-20 | 0.058625 | 0.058604 | 0 | 0 | 0 | 0 | 0.00072123 | 0.00067804 | 0.12866 | 0.12866 | 0.13267 | 0.13267 | 0.0013345 | 0.0013324 | 0 | 0 | 0 | 0 | 1.7275e-05 | 1.2956e-05 | 0.0026734 | 0.0026734 | 0.0032265 | 0.0032265 | 0.024607 | 0.024607 | 0 | 0 | 0 | 0 | 0.015341 | 0.015341 | 0.015198 | 0.015198 | 0.057486 | 0.057486 | 48.8 | 48 | NO
2014-04-21 | 2.8449 | 2.8449 | 0 | 0 | 0 | 0 | 0.12521 | 0.12521 | 7.7551 | 7.7551 | 5.0264 | 5.0264 | 0.017491 | 0.017491 | 0 | 0 | 0 | 0 | 0.0048537 | 0.0048537 | 0.047504 | 0.047504 | 0.022941 | 0.022941 | 0.0214 | 0.0214 | 0 | 0 | 0 | 0 | 0.0072301 | 0.0072301 | 0.051003 | 0.051003 | 0.031311 | 0.031311 | 161.8 | 101 | NO
2014-04-22 | 1.1135 | 1.1057 | 0 | 0 | 0 | 0 | 0.0085727 | 0.0084647 | 0.95188 | 0.95188 | 3.7464 | 3.715 | 0.0083756 | 0.0083606 | 0 | 0 | 0 | 0 | 0.00010203 | 8.9074e-05 | 0.0073738 | 0.0073738 | 0.027932 | 0.027897 | 0.0071772 | 0.0071772 | 0 | 0 | 0 | 0 | 8.0977e-06 | 8.0977e-06 | 0.0033814 | 0.0033814 | 0.026488 | 0.026488 | 223 | 188 | NO
2014-04-23 | 0.26929 | 0.26927 | 0 | 0 | 0 | 0 | 0.013107 | 0.013107 | 0.14937 | 0.14927 | 0.95009 | 0.95009 | 0.0015347 | 0.0015326 | 0 | 0 | 0 | 0 | 0.00014306 | 0.00014306 | 0.0029939 | 0.0029834 | 0.0035318 | 0.0035318 | 0.00013794 | 0.00013794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056239 | 0.00056239 | 164.8 | 113 | NO
2014-04-24 | 2.5962 | 2.5956 | 0 | 0 | 0 | 0 | 3.835 | 3.8348 | 0.75424 | 0.75403 | 2.3599 | 2.3579 | 0.02089 | 0.020869 | 0 | 0 | 0 | 0 | 0.021629 | 0.02162 | 0.014045 | 0.014024 | 0.030797 | 0.030745 | 0.0089 | 0.0089 | 0 | 0 | 0 | 0 | 0.012745 | 0.012745 | 0.00026274 | 0.00026274 | 0.010782 | 0.010782 | 146.8 | 89 | NO
2014-04-25 | 0.024335 | 0.024293 | 0 | 0 | 0 | 0 | 0.0018052 | 0.0017405 | 0.022924 | 0.022924 | 0.07694 | 0.076897 | 0.00024436 | 0.00023805 | 0 | 0 | 0 | 0 | 3.0231e-05 | 2.1594e-05 | 0.00032974 | 0.00032974 | 0.00066737 | 0.0006588 | 0.016532 | 0.016532 | 0 | 0 | 0 | 0 | 0.0033945 | 0.0033945 | 0.037804 | 0.037804 | 0.029839 | 0.029839 | 56.8 | 49 | NO
2014-04-26 | 2.4419 | 2.4415 | 0.012708 | 0.012708 | 0 | 0 | 0.85605 | 0.8556 | 4.378 | 4.378 | 4.6854 | 4.6844 | 0.023139 | 0.023126 | 6.4508e-05 | 6.4508e-05 | 0 | 0 | 0.015563 | 0.015542 | 0.038888 | 0.038888 | 0.031735 | 0.031726 | 0.027618 | 0.027618 | 0 | 0 | 0 | 0 | 0.024474 | 0.024474 | 0.042799 | 0.042799 | 0.029135 | 0.029135 | 241 | 192 | NO
2014-04-27 | 0.86705 | 0.86703 | 0 | 0 | 0 | 0 | 0.043598 | 0.043598 | 2.9193 | 2.9193 | 1.0679 | 1.0679 | 0.012904 | 0.012901 | 0 | 0 | 0 | 0 | 0.00098899 | 0.00098899 | 0.042851 | 0.042851 | 0.015703 | 0.015694 | 0.0046554 | 0.0046554 | 0 | 0 | 0 | 0 | 0.0064808 | 0.0064808 | 0.0075051 | 0.0075051 | 0 | 0 | 72.6 | 74 | NO
2014-04-28 | 0.15252 | 0.15246 | 0 | 0 | 0 | 0 | 0.12767 | 0.12758 | 0.22762 | 0.22751 | 0.1829 | 0.1829 | 0.0031606 | 0.0031564 | 0 | 0 | 0 | 0 | 0.0009566 | 0.00095228 | 0.0096596 | 0.0096491 | 0.0031108 | 0.0031108 | 0.0024827 | 0.0024827 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0089922 | 0.0089922 | 0.0027894 | 0.0027894 | 219.4 | 163 | NO
2014-04-29 | 0.87952 | 0.87944 | 0 | 0 | 0 | 0 | 0.70764 | 0.70756 | 1.3869 | 1.3867 | 1.0507 | 1.0507 | 0.021795 | 0.021786 | 0 | 0 | 0 | 0 | 0.018808 | 0.018799 | 0.034294 | 0.034273 | 0.023573 | 0.023573 | 0.0061039 | 0.0061039 | 0 | 0 | 0 | 0 | 0.0067426 | 0.0067426 | 0.013314 | 0.013314 | 0.00064916 | 0.00064916 | 278.2 | 146 | NO
2014-04-30 | 0.19552 | 0.19548 | 0 | 0 | 0 | 0 | 0.091842 | 0.091798 | 0.46492 | 0.46482 | 0.23577 | 0.23577 | 0.004436 | 0.0044318 | 0 | 0 | 0 | 0 | 0.0017761 | 0.0017718 | 0.013401 | 0.01339 | 0.0036336 | 0.0036336 | 0.00074988 | 0.00074988 | 0 | 0 | 0 | 0 | 3.401e-05 | 3.401e-05 | 0.0013189 | 0.0013189 | 0.0019143 | 0.0019143 | 173.2 | 131 | NO
2014-05-01 | 0.13862 | 0.13862 | 0 | 0 | 0 | 0 | 0.003252 | 0.003252 | 0.032678 | 0.032678 | 0.53205 | 0.53205 | 0.00060195 | 0.00060195 | 0 | 0 | 0 | 0 | 3.9948e-05 | 3.9948e-05 | 5.2548e-05 | 5.2548e-05 | 0.002332 | 0.002332 | 0.005798 | 0.005798 | 0 | 0 | 0 | 0 | 0.0070369 | 0.0070369 | 0 | 0 | 0.0096752 | 0.0096752 | 163.8 | 126 | NO
2014-05-02 | 0.085568 | 0.085547 | 0 | 0 | 0 | 0 | 0.14491 | 0.14491 | 0.024535 | 0.024535 | 0.041308 | 0.041222 | 0.0043952 | 0.0043931 | 0 | 0 | 0 | 0 | 0.0083222 | 0.0083222 | 0.0012296 | 0.0012296 | 0.00040278 | 0.00039421 | 0.001742 | 0.001742 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038018 | 0.0038018 | 0.0040021 | 0.0040021 | 144 | 100 | NO
2014-05-03 | 0.079307 | 0.079105 | 0 | 0 | 0.0056973 | 0 | 0.0082099 | 0.0082099 | 0.14993 | 0.14993 | 0.18396 | 0.18396 | 0.0010155 | 0.0010134 | 0 | 0 | 5.9347e-05 | 0 | 0.00011661 | 0.00011661 | 0.00084602 | 0.00084602 | 0.0032104 | 0.0032104 | 0.00082582 | 0.00082582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033668 | 0.0033668 | 80.6 | 74 | NO
2014-05-04 | 0.045094 | 0.044757 | 0.00064508 | 0 | 0 | 0 | 0.045514 | 0.044952 | 0.029374 | 0.029374 | 0.069495 | 0.069324 | 0.00048976 | 0.00048135 | 6.4508e-05 | 0 | 0 | 0 | 0.00065051 | 0.00064619 | 0.00038097 | 0.00038097 | 0.00038671 | 0.00036957 | 0.013746 | 0.013746 | 0 | 0 | 0 | 0 | 0.00027802 | 0.00027802 | 0.035948 | 0.035948 | 0.026176 | 0.026176 | 96.6 | 89 | NO
2014-05-05 | 0.41883 | 0.41869 | 0 | 0 | 0 | 0 | 0.043213 | 0.043213 | 0.16733 | 0.16733 | 1.4853 | 1.4848 | 0.0041215 | 0.0041173 | 0 | 0 | 0 | 0 | 0.00073635 | 0.00073635 | 0.0056082 | 0.0056082 | 0.010769 | 0.010752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.2 | 155 | NO
2014-05-06 | 2.3092 | 2.3092 | 0.0036125 | 0.0036125 | 0 | 0 | 0.040738 | 0.040738 | 4.6182 | 4.6182 | 5.5675 | 5.5675 | 0.019957 | 0.019957 | 6.4508e-05 | 6.4508e-05 | 0 | 0 | 0.0045671 | 0.0045671 | 0.054952 | 0.054952 | 0.027484 | 0.027484 | 0.011756 | 0.011756 | 0 | 0 | 0 | 0 | 0.0042135 | 0.0042135 | 0.029498 | 0.029498 | 0.015517 | 0.015517 | 238.6 | 183 | NO
2014-05-07 | 0.033665 | 0.033665 | 0 | 0 | 0 | 0 | 0.012308 | 0.012308 | 0.11352 | 0.11352 | 0.020264 | 0.020264 | 0.00024199 | 0.00024199 | 0 | 0 | 0 | 0 | 0.00013388 | 0.00013388 | 0.00065553 | 0.00065553 | 0.00018639 | 0.00018639 | 0.0049528 | 0.0049528 | 0 | 0 | 0 | 0 | 0.0047728 | 0.0047728 | 0.0067524 | 0.0067524 | 0.0052157 | 0.0052157 | 168.6 | 155 | NO
2014-05-08 | 0.17152 | 0.17149 | 0 | 0 | 0 | 0 | 0.0054071 | 0.0054071 | 0.62316 | 0.62306 | 0.1804 | 0.1804 | 0.0049975 | 0.0049954 | 0 | 0 | 0 | 0 | 0.00013388 | 0.00013388 | 0.0019929 | 0.0019824 | 0.018484 | 0.018484 | 0.0036498 | 0.0036498 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067209 | 0.0067209 | 0.0093999 | 0.0093999 | 148 | 132 | NO
2014-05-09 | 0.092781 | 0.09276 | 0 | 0 | 0 | 0 | 0.019823 | 0.01978 | 0.17067 | 0.17067 | 0.19976 | 0.19976 | 0.0013069 | 0.0013048 | 0 | 0 | 0 | 0 | 0.00013388 | 0.00012956 | 0.0031318 | 0.0031318 | 0.0025088 | 0.0025088 | 0.0072579 | 0.0072579 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015357 | 0.015357 | 0.017068 | 0.017068 | 162.2 | 101 | NO
2014-05-10 | 0.093721 | 0.093711 | 0 | 0 | 0 | 0 | 0.021672 | 0.02165 | 0.097483 | 0.097483 | 0.25961 | 0.25961 | 0.0017165 | 0.0017144 | 0 | 0 | 0 | 0 | 0.0001965 | 0.00019218 | 0.0022609 | 0.0022609 | 0.0047648 | 0.0047648 | 0.0059867 | 0.0059867 | 0 | 0 | 0 | 0 | 0.0073764 | 0.0073764 | 0.0055635 | 0.0055635 | 0.005234 | 0.005234 | 70 | 66 | NO
2014-05-11 | 0.025157 | 0.025157 | 0 | 0 | 0 | 0 | 0.0015882 | 0.0015882 | 0.037181 | 0.037181 | 0.069093 | 0.069093 | 0.00017552 | 0.00017552 | 0 | 0 | 0 | 0 | 2.2134e-05 | 2.2134e-05 | 0.00047424 | 0.00047424 | 0.00028494 | 0.00028494 | 0.0077873 | 0.0077873 | 0 | 0 | 0 | 0 | 0.0070369 | 0.0070369 | 0.0047411 | 0.0047411 | 0.013919 | 0.013919 | 57.6 | 52 | NO
2014-05-12 | 0.46423 | 0.46416 | 0 | 0 | 0 | 0 | 0.090525 | 0.090417 | 0.36844 | 0.36833 | 1.4126 | 1.4126 | 0.018036 | 0.018031 | 0 | 0 | 0 | 0 | 0.0048775 | 0.0048732 | 0.0034169 | 0.0034064 | 0.061066 | 0.061066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.4 | 134 | NO
2014-05-13 | 0.56849 | 0.56847 | 0 | 0 | 0 | 0 | 0.76059 | 0.76055 | 0.3913 | 0.3913 | 0.48939 | 0.48939 | 0.010411 | 0.010409 | 0 | 0 | 0 | 0 | 0.014111 | 0.014107 | 0.0074697 | 0.0074697 | 0.0083544 | 0.0083544 | 0.0045045 | 0.0045045 | 0 | 0 | 0 | 0 | 0.0078229 | 0.0078229 | 0.0028901 | 0.0028901 | 0.00048526 | 0.00048526 | 201.8 | 147 | NO
2014-05-14 | 0.048552 | 0.048552 | 0 | 0 | 0 | 0 | 0.0031311 | 0.0031311 | 0.034361 | 0.034361 | 0.16371 | 0.16371 | 0.00037967 | 0.00037967 | 0 | 0 | 0 | 0 | 6.6941e-05 | 6.6941e-05 | 0.00061218 | 0.00061218 | 0.00091589 | 0.00091589 | 0.0074594 | 0.0074594 | 0 | 0 | 0 | 0 | 0.0023213 | 0.0023213 | 0.0048777 | 0.0048777 | 0.021828 | 0.021828 | 113 | 100 | NO
2014-05-15 | 0.02561 | 0.025419 | 0 | 0 | 0.0048665 | 0.0048665 | 0.033464 | 0.033114 | 0.00096688 | 0.00086178 | 0.036519 | 0.036519 | 0.00023989 | 0.00023568 | 0 | 0 | 0.00011869 | 0.00011869 | 0.0004038 | 0.00039948 | 2.1019e-05 | 1.051e-05 | 0.00014247 | 0.00014247 | 0.0034943 | 0.0034943 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0083748 | 0.0083748 | 0.0074171 | 0.0074171 | 145 | 125 | NO
2014-05-16 | 0.12099 | 0.12095 | 0 | 0 | 0 | 0 | 0.0064609 | 0.0064177 | 0.19608 | 0.19608 | 0.32057 | 0.32049 | 0.0014238 | 0.0014196 | 0 | 0 | 0 | 0 | 7.9897e-05 | 7.5578e-05 | 0.0025275 | 0.0025275 | 0.0035854 | 0.0035768 | 0.0065737 | 0.0065737 | 0 | 0 | 0 | 0 | 0.0043187 | 0.0043187 | 0.01652 | 0.01652 | 0.0047605 | 0.0047605 | 150.6 | 136 | NO
2014-05-17 | 0.79529 | 0.79526 | 0 | 0 | 0 | 0 | 0.042508 | 0.042444 | 2.3996 | 2.3996 | 1.2014 | 1.2014 | 0.0041272 | 0.004123 | 0 | 0 | 0 | 0 | 0.0010246 | 0.001016 | 0.01209 | 0.01209 | 0.0049351 | 0.0049351 | 0.01893 | 0.01893 | 0 | 0 | 0 | 0 | 0.029018 | 0.029018 | 0.010196 | 0.010196 | 0.011285 | 0.011285 | 93 | 77 | NO
2014-05-18 | 0.38049 | 0.38026 | 0.0019352 | 0.0019352 | 0 | 0 | 0.43254 | 0.4325 | 0.40278 | 0.40278 | 0.36427 | 0.36341 | 0.0092445 | 0.0092403 | 6.4508e-05 | 6.4508e-05 | 0 | 0 | 0.017272 | 0.017267 | 0.0015488 | 0.0015488 | 0.0021456 | 0.0021371 | 0.010171 | 0.010171 | 0 | 0 | 0 | 0 | 0.015506 | 0.015506 | 0.011755 | 0.011755 | 0.0011141 | 0.0011141 | 84.6 | 79 | NO
2014-05-19 | 0.53376 | 0.53356 | 0 | 0 | 0.0050445 | 0.0050445 | 0.0054028 | 0.0050054 | 2.5861 | 2.5861 | 0.055916 | 0.055916 | 0.0030568 | 0.0030526 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00014684 | 0.0001382 | 0.013779 | 0.013779 | 0.0009266 | 0.0009266 | 0.011988 | 0.011988 | 0 | 0 | 0 | 0 | 0.01626 | 0.01626 | 0.0030294 | 0.0030294 | 0.014139 | 0.014139 | 208 | 181 | NO
2014-05-20 | 0.13446 | 0.13437 | 0 | 0 | 0 | 0 | 0.00032391 | 0.00019434 | 0.06111 | 0.061005 | 0.49773 | 0.49769 | 0.0012972 | 0.0012867 | 0 | 0 | 0 | 0 | 2.1594e-05 | 8.6375e-06 | 0.0011705 | 0.00116 | 0.0042913 | 0.0042827 | 0.0030043 | 0.0030043 | 0 | 0 | 0 | 0 | 0.0040828 | 0.0040828 | 0.0011876 | 0.0011876 | 0.0031783 | 0.0031783 | 138 | 109 | NO
2014-05-21 | 0.99948 | 0.99944 | 0 | 0 | 0 | 0 | 0.018016 | 0.017972 | 2.5007 | 2.5007 | 2 | 1.9999 | 0.0082169 | 0.0082127 | 0 | 0 | 0 | 0 | 0.00018787 | 0.00018355 | 0.029951 | 0.029951 | 0.0087047 | 0.0086961 | 0.0080679 | 0.0080679 | 0 | 0 | 0 | 0 | 0.0081219 | 0.0081219 | 0.010992 | 0.010992 | 0.0078134 | 0.0078134 | 169.8 | 112 | NO
2014-05-22 | 0.75445 | 0.74364 | 0 | 0 | 0 | 0 | 0.36891 | 0.36886 | 0.77345 | 0.77214 | 1.7132 | 1.6702 | 0.00555 | 0.0054933 | 0 | 0 | 0 | 0 | 0.0048705 | 0.0048662 | 0.0050341 | 0.0049027 | 0.0088579 | 0.0087422 | 0.011755 | 0.011755 | 0 | 0 | 0 | 0 | 0.012975 | 0.012975 | 0.013585 | 0.013585 | 0.011102 | 0.011102 | 250.8 | 202 | NO
2014-05-23 | 0.56767 | 0.56738 | 0 | 0 | 0 | 0 | 1.0615 | 1.0609 | 0.094093 | 0.094093 | 0.13127 | 0.13127 | 0.0040321 | 0.0040279 | 0 | 0 | 0 | 0 | 0.0076987 | 0.0076901 | 0.00042695 | 0.00042695 | 0.00081412 | 0.00081412 | 0.00033579 | 0.00033579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001369 | 0.001369 | 329.2 | 208 | NO
2014-05-24 | 1.5296 | 1.5293 | 0 | 0 | 0 | 0 | 3.0079 | 3.0074 | 0.18327 | 0.18316 | 0.11812 | 0.11803 | 0.0059657 | 0.0059594 | 0 | 0 | 0 | 0 | 0.011458 | 0.011454 | 0.0007869 | 0.00077639 | 0.00094374 | 0.00093517 | 0.0035035 | 0.0035035 | 0 | 0 | 0 | 0 | 0.0070282 | 0.0070282 | 0 | 0 | 0.00033743 | 0.00033743 | 277 | 201 | NO
2014-05-25 | 0.055744 | 0.055541 | 0 | 0 | 0 | 0 | 0.0085943 | 0.008197 | 0.030134 | 0.030081 | 0.18564 | 0.18564 | 0.0002638 | 0.00025539 | 0 | 0 | 0 | 0 | 0.00012956 | 0.00011661 | 0.00034944 | 0.00033893 | 0.00053346 | 0.00053346 | 0.0047873 | 0.0047873 | 0 | 0 | 0 | 0 | 0.0024158 | 0.0024158 | 0.0035233 | 0.0035233 | 0.011851 | 0.011851 | 74.8 | 67 | NO
2014-05-26 | 0.012037 | 0.011911 | 0 | 0 | 0 | 0 | 0.0034815 | 0.0032655 | 0.00090382 | 0.00090382 | 0.041428 | 0.041342 | 6.4636e-05 | 5.833e-05 | 0 | 0 | 0 | 0 | 3.9409e-05 | 3.0771e-05 | 1.051e-05 | 1.051e-05 | 0.00017675 | 0.00016818 | 0.013989 | 0.013989 | 0 | 0 | 0 | 0 | 0.0054276 | 0.0054276 | 0.01044 | 0.01044 | 0.037752 | 0.037752 | 205 | 182 | NO
2014-05-27 | 0.086489 | 0.086417 | 0 | 0 | 0 | 0 | 0.10216 | 0.10206 | 0.033026 | 0.032921 | 0.12296 | 0.12296 | 0.0010733 | 0.001067 | 0 | 0 | 0 | 0 | 0.0011779 | 0.0011693 | 0.00046242 | 0.00045191 | 0.0016615 | 0.0016615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192.8 | 158 | NO
2014-05-28 | 0.020647 | 0.020626 | 0 | 0 | 0 | 0 | 0.028841 | 0.028841 | 0.0021676 | 0.0020625 | 0.025182 | 0.025182 | 0.00026774 | 0.00026564 | 0 | 0 | 0 | 0 | 0.0002872 | 0.0002872 | 5.3861e-05 | 4.3352e-05 | 0.00047776 | 0.00047776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.8 | 109 | NO
2014-05-29 | 0.0095669 | 0.009424 | 0 | 0 | 0 | 0 | 0.0019305 | 0.0018873 | 0.028152 | 0.027543 | 0.012217 | 0.012217 | 0.00015765 | 0.00015134 | 0 | 0 | 0 | 0 | 3.0231e-05 | 2.5912e-05 | 0.00054256 | 0.00052154 | 0.00014033 | 0.00014033 | 0.0016159 | 0.0016159 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026142 | 0.0026142 | 0.0044562 | 0.0044562 | 125.8 | 113 | NO
2014-05-30 | 0.35513 | 0.35476 | 0 | 0 | 0 | 0 | 0.0036385 | 0.0028784 | 0.036983 | 0.036983 | 1.4105 | 1.4105 | 0.0017885 | 0.0017843 | 0 | 0 | 0 | 0 | 5.2365e-05 | 4.3727e-05 | 0.00049001 | 0.00049001 | 0.0067883 | 0.0067883 | 0.0035371 | 0.0035371 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0063307 | 0.0063307 | 0.0092585 | 0.0092585 | 179.4 | 150 | NO
2014-05-31 | 0.081178 | 0.080747 | 0 | 0 | 0.007181 | 0.007181 | 0.11269 | 0.11183 | 0.089502 | 0.089502 | 0.033325 | 0.033283 | 0.00067001 | 0.0006616 | 0 | 0 | 5.9347e-05 | 5.9347e-05 | 0.00074175 | 0.00072879 | 0.0011101 | 0.0011101 | 0.000346 | 0.00033743 | 0.0008802 | 0.0008802 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039608 | 0.0039608 | 0.00035886 | 0.00035886 | 93.2 | 75 | NO
2014-06-01 | 0.46288 | 0.46283 | 0.0039995 | 0.0039995 | 0 | 0 | 0.24117 | 0.24113 | 0.00071465 | 0.00060955 | 1.4075 | 1.4075 | 0.0020237 | 0.0020195 | 6.4508e-05 | 6.4508e-05 | 0 | 0 | 0.00083136 | 0.00082704 | 2.1019e-05 | 1.051e-05 | 0.0065751 | 0.0065751 | 0.014554 | 0.014554 | 0 | 0 | 0 | 0 | 0.010582 | 0.010582 | 0.0049907 | 0.0049907 | 0.034269 | 0.034269 | 72.6 | 71 | NO
2014-06-02 | 0.30622 | 0.30618 | 0 | 0 | 0 | 0 | 0.55764 | 0.5576 | 0.035953 | 0.035848 | 0.1126 | 0.1126 | 0.0023737 | 0.0023695 | 0 | 0 | 0 | 0 | 0.0041552 | 0.0041509 | 0.000758 | 0.00074749 | 0.00081412 | 0.00081412 | 0.0056664 | 0.0056664 | 0 | 0 | 0 | 0 | 0.0090424 | 0.0090424 | 0 | 0 | 0.005159 | 0.005159 | 240.4 | 183 | NO
2014-06-03 | 1.366 | 1.366 | 0 | 0 | 0 | 0 | 0.78512 | 0.78508 | 1.0218 | 1.0217 | 3.178 | 3.178 | 0.024465 | 0.024461 | 0 | 0 | 0 | 0 | 0.014559 | 0.014555 | 0.039316 | 0.039306 | 0.038795 | 0.038795 | 0.0093725 | 0.0093725 | 0 | 0 | 0 | 0 | 0.0024158 | 0.0024158 | 0.0079071 | 0.0079071 | 0.02697 | 0.02697 | 312.8 | 241 | NO
2014-06-04 | 0.35628 | 0.35604 | 0 | 0 | 0 | 0 | 0.14782 | 0.14778 | 0.58574 | 0.58464 | 0.6816 | 0.6816 | 0.0068091 | 0.0068049 | 0 | 0 | 0 | 0 | 0.0074401 | 0.0074358 | 0.0067865 | 0.006776 | 0.0074631 | 0.0074631 | 0.0012481 | 0.0012481 | 0 | 0 | 0 | 0 | 0.0025643 | 0.0025643 | 0 | 0 | 0 | 0 | 189.6 | 168 | NO
2014-06-05 | 0.068734 | 0.068587 | 0 | 0 | 0 | 0 | 0.020169 | 0.019867 | 0.061615 | 0.061615 | 0.18996 | 0.18996 | 0.0011422 | 0.0011274 | 0 | 0 | 0 | 0 | 0.00032984 | 0.00029961 | 0.00060561 | 0.00060561 | 0.0035082 | 0.0035082 | 0.0028947 | 0.0028947 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036074 | 0.0036074 | 0.00886 | 0.00886 | 152.4 | 130 | NO
2014-06-06 | 0.10498 | 0.098762 | 0 | 0 | 0 | 0 | 0.042373 | 0.04233 | 0.29406 | 0.26305 | 0.10415 | 0.10415 | 0.0015605 | 0.0015321 | 0 | 0 | 0 | 0 | 0.00045779 | 0.00045347 | 0.004167 | 0.0040357 | 0.0020557 | 0.0020557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.8 | 141 | NO
2014-06-07 | 0.5469 | 0.54674 | 0 | 0 | 0 | 0 | 0.058826 | 0.058489 | 0.108 | 0.108 | 2.0249 | 2.0249 | 0.0025623 | 0.0025581 | 0 | 0 | 0 | 0 | 0.00070288 | 0.00069424 | 0.0015607 | 0.0015607 | 0.0077792 | 0.0077792 | 0.0043758 | 0.0043758 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012887 | 0.0012887 | 0.016789 | 0.016789 | 66.8 | 67 | NO
2014-06-08 | 0.56603 | 0.56601 | 0 | 0 | 1.1851 | 1.1851 | 1.0503 | 1.0503 | 0.00052548 | 0.00052548 | 0.051932 | 0.051847 | 0.0069733 | 0.0069691 | 0 | 0 | 0.0055638 | 0.0055638 | 0.013493 | 0.013493 | 0.00026274 | 0.00026274 | 0.00063844 | 0.0006213 | 0.013133 | 0.013133 | 0 | 0 | 0.011128 | 0.011128 | 0.024915 | 0.024915 | 0.0030609 | 0.0030609 | 0 | 0 | 152.8 | 125 | NO
2014-06-09 | 0.039104 | 0.039104 | 0 | 0 | 0 | 0 | 0.045838 | 0.045838 | 0.033294 | 0.033294 | 0.041322 | 0.041322 | 0.00051341 | 0.00051341 | 0 | 0 | 0 | 0 | 0.00059761 | 0.00059761 | 0.00080923 | 0.00080923 | 0.00024745 | 0.00024745 | 0.00098215 | 0.00098215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040042 | 0.0040042 | 127.4 | 100 | NO
2014-06-10 | 0.10281 | 0.10265 | 0 | 0 | 0 | 0 | 0.01233 | 0.012222 | 0.006001 | 0.005528 | 0.38981 | 0.38972 | 0.00081504 | 0.00080453 | 0 | 0 | 0 | 0 | 0.0002181 | 0.00020514 | 5.1234e-05 | 4.0724e-05 | 0.0028484 | 0.0028398 | 0.0050101 | 0.0050101 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015385 | 0.015385 | 0.0078809 | 0.0078809 | 200 | 184 | NO
2014-06-11 | 0.021863 | 0.021853 | 0 | 0 | 0 | 0 | 0.015921 | 0.015899 | 0.0013978 | 0.0013978 | 0.056405 | 0.056405 | 0.00032108 | 0.00031898 | 0 | 0 | 0 | 0 | 0.00034982 | 0.0003455 | 1.051e-05 | 1.051e-05 | 0.00060631 | 0.00060631 | 0.0036207 | 0.0036207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014761 | 0.014761 | 160.2 | 153 | NO
2014-06-12 | 0.86567 | 0.86566 | 0 | 0 | 0 | 0 | 0.65577 | 0.65576 | 1.4776 | 1.4776 | 1.0232 | 1.0232 | 0.007653 | 0.0076509 | 0 | 0 | 0 | 0 | 0.0056241 | 0.0056198 | 0.013259 | 0.013259 | 0.0092296 | 0.0092296 | 0.0013828 | 0.0013828 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048817 | 0.0048817 | 0.0016572 | 0.0016572 | 145.8 | 124 | NO
2014-06-13 | 0.05783 | 0.05783 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087116 | 0.087116 | 0.16474 | 0.16474 | 0.00059486 | 0.00059486 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009209 | 0.0009209 | 0.0016743 | 0.0016743 | 0.0079817 | 0.0079817 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019192 | 0.019192 | 0.016892 | 0.016892 | 131.4 | 112 | NO
2014-06-14 | 0.23696 | 0.23694 | 0 | 0 | 0.23955 | 0.23955 | 0.43691 | 0.43687 | 0.01428 | 0.01428 | 0.052867 | 0.052867 | 0.0010055 | 0.0010034 | 0 | 0 | 0.0056231 | 0.0056231 | 0.0015159 | 0.0015116 | 0.00017472 | 0.00017472 | 0.00013712 | 0.00013712 | 0.0027751 | 0.0027751 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048331 | 0.0048331 | 0.0073732 | 0.0073732 | 65.4 | 65 | NO
2014-06-15 | 0.12632 | 0.1262 | 0 | 0 | 0 | 0 | 0.018052 | 0.017802 | 0.03627 | 0.03627 | 0.44962 | 0.44962 | 0.0022665 | 0.0022602 | 0 | 0 | 0 | 0 | 0.00048478 | 0.00047182 | 0.0010982 | 0.0010982 | 0.0073828 | 0.0073828 | 0.00066291 | 0.00066291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027027 | 0.0027027 | 72.4 | 73 | NO
2014-06-16 | 0.087027 | 0.087006 | 0 | 0 | 0 | 0 | 0.01072 | 0.01072 | 0.27046 | 0.27046 | 0.11299 | 0.11291 | 0.00099345 | 0.00099135 | 0 | 0 | 0 | 0 | 0.00020892 | 0.00020892 | 0.0023896 | 0.0023896 | 0.0016872 | 0.0016786 | 0.0031753 | 0.0031753 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038123 | 0.0038123 | 0.009837 | 0.009837 | 181.2 | 112 | NO
2014-06-17 | 0.065639 | 0.065292 | 0 | 0 | 0 | 0 | 0.0082186 | 0.0077478 | 0.23136 | 0.23136 | 0.062642 | 0.062163 | 0.00094537 | 0.00093906 | 0 | 0 | 0 | 0 | 0.0001382 | 0.00012956 | 0.0036508 | 0.0036508 | 0.00060309 | 0.00059452 | 0.001798 | 0.001798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073303 | 0.0073303 | 161.4 | 134 | NO
2014-06-18 | 0.052759 | 0.052749 | 0 | 0 | 0 | 0 | 0.042538 | 0.042516 | 0.10618 | 0.10618 | 0.044107 | 0.044107 | 0.00054809 | 0.00054599 | 0 | 0 | 0 | 0 | 0.00033686 | 0.00033254 | 0.0015922 | 0.0015922 | 0.0002678 | 0.0002678 | 0.0038965 | 0.0038965 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00042695 | 0.00042695 | 0.015538 | 0.015538 | 134.4 | 117 | NO
2014-06-19 | 0.093266 | 0.093266 | 0 | 0 | 0 | 0 | 0.016001 | 0.016001 | 0.14064 | 0.14064 | 0.23381 | 0.23381 | 0.0039205 | 0.0039205 | 0 | 0 | 0 | 0 | 0.00012092 | 0.00012092 | 0.0021164 | 0.0021164 | 0.014018 | 0.014018 | 0.0013474 | 0.0013474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054932 | 0.0054932 | 146.2 | 115 | NO
2014-06-20 | 0.35334 | 0.35333 | 0 | 0 | 0.00029674 | 0 | 0.24303 | 0.24303 | 0.75357 | 0.75357 | 0.34382 | 0.34382 | 0.0066257 | 0.0066236 | 0 | 0 | 5.9347e-05 | 0 | 0.0034588 | 0.0034588 | 0.017223 | 0.017223 | 0.0060973 | 0.0060973 | 0.0049517 | 0.0049517 | 0 | 0 | 0 | 0 | 0.0020784 | 0.0020784 | 0.016785 | 0.016785 | 0.002377 | 0.002377 | 162.6 | 130 | NO
2014-06-21 | 0.46842 | 0.46842 | 0.0072894 | 0.0072894 | 0.0056973 | 0.0056973 | 0.00084215 | 0.00084215 | 0.75624 | 0.75624 | 1.2896 | 1.2896 | 0.0067626 | 0.0067626 | 6.4508e-05 | 6.4508e-05 | 5.9347e-05 | 5.9347e-05 | 1.2956e-05 | 1.2956e-05 | 0.013393 | 0.013393 | 0.016607 | 0.016607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 60 | NO
2014-06-22 | 0.0083125 | 0.0082915 | 0 | 0 | 0 | 0 | 0.0060419 | 0.0059987 | 0.013925 | 0.013925 | 0.010546 | 0.010546 | 0.00013059 | 0.00012848 | 0 | 0 | 0 | 0 | 0.00012524 | 0.00012092 | 0.00026274 | 0.00026274 | 6.9629e-05 | 6.9629e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 82 | NO
2014-06-23 | 1.8099 | 1.8099 | 0 | 0 | 0 | 0 | 1.6067 | 1.6067 | 2.1991 | 2.1991 | 2.3973 | 2.3973 | 0.019303 | 0.019303 | 0 | 0 | 0 | 0 | 0.021629 | 0.021629 | 0.021108 | 0.021108 | 0.018566 | 0.018566 | 0.02092 | 0.02092 | 0 | 0 | 0 | 0 | 0.015401 | 0.015401 | 0.029872 | 0.029872 | 0.030372 | 0.030372 | 394.6 | 294 | NO
2014-06-24 | 0.72991 | 0.72984 | 0 | 0 | 0 | 0 | 0.0022242 | 0.0022242 | 2.5932 | 2.5932 | 0.85683 | 0.85652 | 0.0072954 | 0.0072933 | 0 | 0 | 0 | 0 | 3.0231e-05 | 3.0231e-05 | 0.028315 | 0.028315 | 0.0065944 | 0.0065858 | 0.0077264 | 0.0077264 | 0 | 0 | 0 | 0 | 0.01049 | 0.01049 | 0.0079938 | 0.0079938 | 0.004166 | 0.004166 | 198.4 | 162 | NO
2014-06-25 | 0.44705 | 0.44703 | 0 | 0 | 0 | 0 | 0.012963 | 0.012963 | 1.3136 | 1.3136 | 0.72573 | 0.72565 | 0.00559 | 0.0055857 | 0 | 0 | 0 | 0 | 0.0029125 | 0.0029125 | 0.012408 | 0.012408 | 0.0068933 | 0.0068761 | 0.0039346 | 0.0039346 | 0 | 0 | 0 | 0 | 0.0080302 | 0.0080302 | 0 | 0 | 0.00010712 | 0.00010712 | 161.6 | 141 | NO
2014-06-26 | 1.7344 | 1.5368 | 0 | 0 | 0 | 0 | 0.22617 | 0.009687 | 2.599 | 2.599 | 4.503 | 4.1269 | 0.021626 | 0.012112 | 0 | 0 | 0 | 0 | 0.011017 | 0.00018787 | 0.019833 | 0.019833 | 0.050135 | 0.032835 | 0.030283 | 0.030283 | 0 | 0 | 0 | 0 | 0.0073764 | 0.0073764 | 0.056787 | 0.056787 | 0.062521 | 0.062521 | 202.4 | 167 | NO
2014-06-27 | 0.50752 | 0.50711 | 0 | 0 | 0 | 0 | 0.92476 | 0.92461 | 0.10851 | 0.10851 | 0.14567 | 0.14427 | 0.0045308 | 0.0045266 | 0 | 0 | 0 | 0 | 0.0080269 | 0.0080226 | 0.0015423 | 0.0015423 | 0.0012865 | 0.001278 | 0.0061845 | 0.0061845 | 0 | 0 | 0 | 0 | 0.0078931 | 0.0078931 | 0.010659 | 0.010659 | 0.00086018 | 0.00086018 | 203.4 | 147 | NO
2014-06-28 | 0.86049 | 0.86032 | 0 | 0 | 0 | 0 | 0.44722 | 0.44711 | 1.5482 | 1.5482 | 1.3583 | 1.3579 | 0.010086 | 0.010077 | 0 | 0 | 0 | 0 | 0.0090408 | 0.0090278 | 0.014181 | 0.014181 | 0.011615 | 0.011607 | 0.014649 | 0.014649 | 0 | 0 | 0 | 0 | 0.01606 | 0.01606 | 0.013585 | 0.013585 | 0.016776 | 0.016776 | 119.4 | 107 | NO
2014-06-29 | 1.3623 | 1.3621 | 4.0519 | 4.0519 | 0 | 0 | 0.081981 | 0.081955 | 2.3751 | 2.3751 | 2.9163 | 2.9157 | 0.0093078 | 0.0093015 | 0.072572 | 0.072572 | 0 | 0 | 0.001159 | 0.0011547 | 0.01284 | 0.01284 | 0.015537 | 0.01552 | 0.00166 | 0.00166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067679 | 0.0067679 | 249.6 | 172 | NO
2014-06-30 | 0.35798 | 0.35796 | 0.55638 | 0.55638 | 0 | 0 | 0.045867 | 0.045824 | 0.032178 | 0.032178 | 1.2683 | 1.2683 | 0.0021204 | 0.0021183 | 0.024191 | 0.024191 | 0 | 0 | 0.00044483 | 0.00044051 | 0.00010378 | 0.00010378 | 0.0044637 | 0.0044637 | 0.00166 | 0.00166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067679 | 0.0067679 | 242.4 | 193 | NO
Contents
Contents

## 1d. STPIS GSL
Table | TasNetworks
STPIS Data Reporting
2013-14
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
| Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
| Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Customer Service
TasNetworks
Customer Service | The information is required to assess the outturn level of service provided to the DNSP's customers, and will inform the AER’s review of future regulatory proposals. The information may be used in performance reports.
2013-14
Table 1 Quality of supply
Over voltage events - due to high voltage injection |  | 1
Customers receiving over-voltage - due to high voltage injection |  | 2
Over voltage events - due to lightning |  | 73
Customers receiving over-voltage - due to lightning |  | 73
Over voltage events - due to voltage regulation or other cause |  | 79
Customers receiving over-voltage - due to voltage regulation or other cause |  | 79
Voltage variations - steady state (zone sub) |  | 3
Voltage variations - one minute (zone sub) |  | -
Voltage variations - 10 seconds (zone sub) Min<0.7 |  | -
Voltage variations - 10 seconds (zone sub) Min<0.8 |  | -
Voltage variations - 10 seconds (zone sub) Min<0.9 |  | -
Voltage variations - steady state (feeder) |  | -
Voltage variations - % zone subs monitored |  | 0.0909
Voltage variations - % feeders monitored |  | 0
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number |  | 431
Complaints by category (%)
Low voltage supply |  | 36
Voltage dips |  | 42
Voltage swell |  | 101
Voltage spike (impulsive transient) |  | 0
Waveform distortion |  | 2
TV or radio interference |  | 19
Noise from appliances |  | 0
Other |  | 231
Complaints by Likely Cause (%)
Network equipment faulty |  | 12
Network interference by NSP equipment |  | 0
Network interference by another customer |  | 0
Network limitation |  | 189
Customer internal problem |  | 1
No problem identified |  | 217
Environmental |  | 0
Other |  | 12
Table 3 Customer service
Timely provision of services
Connections made |  | 0
Connections not made on agreed date |  | 0
Timely repair of faulty streetlights
Streetlights - average monthly number "out" |  | 267
Streetlights - not repaired by "fix by" date |  | 383
Streetlights - average number of days to repair |  | 9.8
Total streetlights |  | 47135
Call Centre Performance (number, unless stated)
Calls to call centre fault line |  | 81609
Calls to fault line answered within 30 seconds |  | 62411
Calls to fault line - average waiting time before call answered |  | 27 secs
Calls abandoned - percentage |  | 6%
Call centre - number of overload events |  | 616
Customer complaints (number)
Complaint - reliability of supply |  | 259
Complaint - technical quality of supply |  | 431
Complaint - administrative process or customer service |  | 0
Complaint - connection or augmentation |  | 267
Complaint - other |  | 2575
Total complaints |  | 3532
Contents

## 3a. Feeder Reliability
TasNetworks
Annual Feeder Reliability
2013-14
Table 1 Annual Feeder Reliability Data
Feeder ID / name | Description of the feeder service area | Feeder classification | Number of Customers(1) | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply (including excluded events and MEDs) | Planned customer minutes off-supply (after removing excluded events and MED) | Planned interruptions (SAIFI) (including excluded events and MEDs) | Planned interruptions (SAIFI) (after removing excluded events and MEDs) | Total number of momentary feeder outages | Momentary interruptions due to feeder outages (MAIFI) (including excluded events and MEDs) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events and MEDs) | Low Reliability Feeder (SAIDI)
10002 | West Hobart Zone Substation | Urban | 40 | 5.71 | 0.25 | 13.1998 | 9.0573 | 0 | 7 | 193.2564 | 193.2564 | 6.022 | 6.022 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
12017 | Enterprise Rd-Mt Nelson-Taroona | Urban | 963 | 6.51 | 2.73 | 3.3426 | 19.8741 | 0.0057241 | 14 | 596.1499 | 593.7752 | 6.0026 | 5.9996 | 2 | 0.38197 | 0.38197 | 0.060037 | 0.060037 | 0 | 0 | 0 | Yes
12018 | Upper Sandy Bay | Urban | 903 | 0.02 | 4.87 | 2.8344 | 4.6836 | 0.3591 | 6 | 200.4491 | 200.4348 | 1.0057 | 1.0043 | 2 | 76.6964 | 76.6964 | 0.22321 | 0.22321 | 0 | 0 | 0 | Yes
12019 | Lower Sandy Bay | Urban | 1119 | 2.2 | 3.55 | 4.0712 | 6.8141 | 0.22859 | 13 | 138.476 | 51.5434 | 0.20731 | 0.15194 | 2 | 19.9336 | 19.9336 | 0.066445 | 0.066445 | 0 | 0 | 0 | No
12030 | Lower Sandy Bay-Taroona (North)-Station Supply | Short Rural | 925 | 6.18 | 5.24 | 3.3559 | 17.8294 | 0.0017629 | 9 | 738.5423 | 463.3539 | 4.0312 | 3.0301 | 1 | 0.064473 | 0.064473 | 0.0010745 | 0.0010745 | 0 | 0 | 0 | No
12031 | Taroona | Short Rural | 993 | 10.19 | 4.07 | 3.9242 | 22.3551 | 0.0024069 | 18 | 934.2227 | 871.2179 | 7.098 | 7.0615 | 1 | 0.82811 | 0.82811 | 0.0029575 | 0.0029575 | 0 | 0 | 0 | Yes
12032 | Open | Short Rural | 993 | 0 | 0 | 2.1325 | 22.3551 | 0.0024069 | 5 | 0.49687 | 0.49687 | 0.004732 | 0.004732 | 1 | 0.056785 | 0.056785 | 0.00094641 | 0.00094641 | 0 | 0 | 0 | No
12033 | Sandy Bay | Urban | 339 | 0.68 | 2.39 | 1.1432 | 2.1233 | 0 | 7 | 279.2516 | 279.2135 | 3.0152 | 3.0114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
12035 | Sandy Bay | Urban | 826 | 1.27 | 4.32 | 3.3091 | 4.0138 | 0 | 12 | 192.2524 | 192.0579 | 2.0955 | 2.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
12036 | Sandy Bay-University Campus | Urban | 2 | 0.29 | 3.51 | 4.9938 | 4.0138 | 0 | 1 | 187.0002 | 187.0002 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
12037 | Casino-Battery Point | Urban | 204 | 0 | 2.74 | 2.8471 | 2.6507 | 1.0851 | 2 | 135.0364 | 135.0364 | 1.0783 | 1.0783 | 2 | 34.4531 | 34.4531 | 0.125 | 0.125 | 0 | 0 | 0 | No
12038 | Tolmans Hill-Mt Nelson-Taroona-Sandy Bay | Short Rural | 707 | 25.56 | 4.73 | 2.9146 | 5.2208 | 0.033061 | 16 | 313.7287 | 248.9941 | 1.5 | 1.2704 | 3 | 3.8814 | 3.8814 | 0.017643 | 0.017643 | 0 | 0 | 0 | No
12039 | Open | Short Rural | 707 | 0 | 0 | 4.1248 | 5.2208 | 0.033061 | 5 | 0.19635 | 0.12797 | 0.0031365 | 0.0018819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
13043 | Lynton Avenue South Hobart | Urban | 448 | 0 | 1.47 | 1.9319 | 0.37054 | 0.0022073 | 4 | 39.9447 | 39.918 | 0.258 | 0.25533 | 1 | 0.16 | 0.16 | 0.0026667 | 0.0026667 | 0 | 0 | 0 | No
13044 | West Hobart Substation | Urban | 448 | 0 | 0.06 | 3.7036 | 0.37054 | 0.0022073 | 1 | 0.32267 | 0.32267 | 0.0026667 | 0.0026667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
13045 | South Hobart-Cascades | Urban | 1440 | 10.82 | 4 | 4.6462 | 16.3366 | 1.3402 | 37 | 678.6743 | 587.3118 | 4.4911 | 4.3741 | 7 | 58.7632 | 58.7632 | 0.20165 | 0.20165 | 2 | 2.0564 | 2.0564 | Yes
13047 | City (South-East)(Macquarie St)-Salamanca | Urban | 194 | 0 | 1.93 | 1.8116 | 0.0043324 | 0 | 2 | 0.14171 | 0.14171 | 0.0045714 | 0.0045714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
13048 | City (North)(Melville St) | Urban | 320 | 0 | 1.83 | 3.1754 | 0.52907 | 0 | 5 | 9.5233 | 9.5233 | 0.22578 | 0.22578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
13049 | OPEN | Urban | 1081 | 0.54 | 3.73 | 2.6072 | 1.105 | 0.55025 | 11 | 73.6763 | 73.6763 | 0.81271 | 0.81271 | 5 | 160.2991 | 160.2991 | 0.46729 | 0.46729 | 0 | 0 | 0 | No
13050 | Sandy Bay | Urban | 290 | 0.04 | 2.87 | 1.4105 | 0.018646 | 0.000591 | 3 | 0.62031 | 0.62031 | 0.0073846 | 0.0073846 | 1 | 24.3077 | 24.3077 | 0.15385 | 0.15385 | 0 | 0 | 0 | No
13051 | Sandy Bay Zone | Short Rural | 1187 | 0.52 | 4.72 | 0 | 0.018268 | 0.0002967 | 4 | 207.3116 | 207.3116 | 1.087 | 1.087 | 1 | 25.5682 | 25.5682 | 0.085227 | 0.085227 | 0 | 0 | 0 | No
13052 | Battery Point | Urban | 726 | 0.13 | 5.87 | 3.8641 | 0.014957 | 0.81649 | 9 | 0.26449 | 0.20801 | 0.0061989 | 0.0020663 | 1 | 34.0938 | 34.0938 | 0.12914 | 0.12914 | 0 | 0 | 0 | No
13053 | Battery Point (Hampton Road) | Urban | 751 | 0 | 3.73 | 3.5899 | 0.34608 | 0 | 10 | 22.549 | 22.549 | 0.34926 | 0.34926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
13054 | St Davids Park | Urban | 210 | 0 | 2.08 | 3.5632 | 0.0088493 | 0.73863 | 1 | 0.038564 | 0.038564 | 0.00082051 | 0.00082051 | 2 | 78.6051 | 78.6051 | 0.41026 | 0.41026 | 0 | 0 | 0 | No
13055 | South Hobart | Urban | 982 | 2.51 | 2.12 | 3.5899 | 0.057416 | 2.7281 | 13 | 2.2596 | 2.2235 | 0.013419 | 0.0092903 | 1 | 71.4 | 71.4 | 0.2 | 0.2 | 0 | 0 | 0 | No
13056 | South Hobart - Sandy Bay Zone | Short Rural | 1172 | 3.33 | 6.19 | 1.5844 | 2.287 | 0.17267 | 4 | 178.9724 | 178.9724 | 2.0091 | 2.0091 | 2 | 25.4167 | 25.4167 | 0.071138 | 0.071138 | 0 | 0 | 0 | No
13057 | Huon Road-Mount Wellington-Nieka | Short Rural | 852 | 38.87 | 0.93 | 3.0685 | 7.2212 | 0.15411 | 26 | 1836.3559 | 1836.3454 | 4.893 | 4.8919 | 5 | 4.3017 | 4.3017 | 0.070159 | 0.070159 | 0 | 0 | 0 | Yes
14061 | Domain-Tasman Bridge | Urban | 418 | 3.13 | 4.55 | 4.5927 | 0.61593 | 0.0079497 | 3 | 129.4665 | 129.4665 | 1.4258 | 1.4258 | 1 | 0.049664 | 0.049664 | 0.00082773 | 0.00082773 | 0 | 0 | 0 | No
14063 | Argyle St North Hobart | Urban | 144 | 0 | 2.45 | 2.9548 | 7.6429 | 0.0097449 | 2 | 260.8581 | 0 | 0.1885 | 0 | 1 | 0.145 | 0.145 | 0.001 | 0.001 | 0 | 0 | 0 | No
14064 | Collins Street | Urban | 50 | 0 | 0.77 | 2.5336 | 0 | 0.0040806 | 0 | 0 | 0 | 0 | 0 | 1 | 0.06 | 0.06 | 0.0013333 | 0.0013333 | 0 | 0 | 0 | No
14065 | Collins Street | Urban | 217 | 0 | 1.86 | 3.7237 | 0.028745 | 0 | 2 | 0.12973 | 0.12108 | 0.0017297 | 0.00086486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
14067 | West Hobart Zone Substation | Urban | 138 | 0 | 2.51 | 3.5163 | 0 | 0.00097428 | 0 | 0 | 0 | 0 | 0 | 1 | 1.5319 | 1.5319 | 0.12766 | 0.12766 | 0 | 0 | 0 | No
14068 | Town Hall | Urban | 164 | 0 | 1.6 | 4.8666 | 0.0092728 | 0.81769 | 2 | 0.027586 | 0.027586 | 0.0011034 | 0.0011034 | 4 | 87.8373 | 87.8373 | 0.4149 | 0.4149 | 0 | 0 | 0 | No
14069 | Trafalgar Place | Urban | 116 | 0 | 0.98 | 3.4896 | 0.042009 | 0 | 3 | 14.5175 | 14.4341 | 0.13322 | 0.13183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
14070 | Mawson Place - West Hobart Zone | Urban | 144 | 0 | 1.75 | 4.5794 | 1.0106 | 0.03595 | 3 | 49.711 | 49.711 | 1.0442 | 1.0442 | 2 | 25.3044 | 25.3044 | 0.13043 | 0.13043 | 0 | 0 | 0 | No
16091 | Albert Rpad-Charles St Moonah | Urban | 1157 | 2.65 | 2.6 | 3.3358 | 6.6718 | 0.58737 | 25 | 283.2574 | 95.4097 | 2.0939 | 1.0986 | 4 | 48.4417 | 48.4417 | 0.24074 | 0.24074 | 0 | 0 | 0 | No
16092 | Moonah-Gormanston Rd | Urban | 530 | 0 | 2.19 | 2.186 | 0.046145 | 0.00879 | 5 | 2.0724 | 1.6777 | 0.007619 | 0.0045714 | 2 | 0.44952 | 0.44952 | 0.0030476 | 0.0030476 | 0 | 0 | 0 | No
16093 | Moonah-Birdwood Dr | Urban | 332 | 0 | 3.48 | 2.7476 | 0.0050915 | 0 | 2 | 0.18863 | 0.18863 | 0.0033684 | 0.0033684 | 1 | 41.0526 | 41.0526 | 0.10526 | 0.10526 | 1 | 1 | 1 | No
16094 | Lutana | Urban | 884 | 3.35 | 2.11 | 4.0177 | 0.1659 | 0.2115 | 18 | 8.3019 | 6.4487 | 0.035067 | 0.027935 | 3 | 17.4606 | 17.4606 | 0.049183 | 0.049183 | 0 | 0 | 0 | No
16095 | Selfs Point-Lenox Avenue | Urban | 353 | 1.53 | 2.72 | 1.972 | 1.5257 | 0.072294 | 6 | 128.3569 | 19.3567 | 1.0675 | 0.06753 | 2 | 6.8291 | 6.8291 | 0.076161 | 0.076161 | 0 | 0 | 0 | No
16096 | North Hobart | Urban | 1102 | 1.73 | 8.37 | 3.8773 | 1.0284 | 0.82569 | 16 | 14.903 | 14.903 | 0.17911 | 0.17911 | 5 | 69.6311 | 69.6311 | 0.20499 | 0.20499 | 0 | 0 | 0 | No
16097 | Cross st New Town | Urban | 230 | 0 | 1.25 | 1.2701 | 0.00084808 | 0.0052248 | 2 | 0.47556 | 0.47556 | 0.0088889 | 0.0088889 | 1 | 74.4443 | 74.4443 | 0.55556 | 0.55556 | 0 | 0 | 0 | No
16098 | Augusta Rd Lenah Valley-Creek Road Lenah Valley | Urban | 1014 | 4.97 | 4.46 | 3.9509 | 3.214 | 1.1767 | 6 | 110.071 | 110.0496 | 1.0044 | 1.0018 | 7 | 22.2888 | 22.2888 | 0.143 | 0.143 | 0 | 0 | 0 | No
17100 | Eady St nr Cooper St-Derwent Pk (East) | Urban | 63 | 0 | 4.69 | 2.5404 | 0.67766 | 0 | 4 | 45.7279 | 35.0511 | 1.0891 | 1.0009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
17101 | East Derwent Hwy Bowen Bridge | Short Rural | 331 | 10.11 | 6.53 | 2.1926 | 0.47715 | 0.21527 | 6 | 41.93 | 41.9073 | 1.0853 | 1.083 | 8 | 76.4073 | 76.4073 | 0.31363 | 0.31363 | 0 | 0 | 0 | No
17102 | Derwent Park (HEC Garage) | Urban | 1 | 0 | 0.88 | 0.46789 | 0.060129 | 0 | 1 | 39.0195 | 39.0195 | 1.0005 | 1.0005 | 0 | 0 | 0 | 0 | 0 | 1 | 1.0005 | 1.0005 | No
17103 | Dowsing Point-Grove Road | Urban | 620 | 2.07 | 4.78 | 2.6539 | 6.5059 | 0.033296 | 18 | 153.8719 | 44.7705 | 1.2148 | 1.1454 | 11 | 0.47405 | 0.47405 | 0.0079009 | 0.0079009 | 0 | 0 | 0 | No
17104 | Derwent Park (Sunderland Street) | Urban | 167 | 0 | 1.86 | 2.1124 | 0.32275 | 0 | 2 | 40.2363 | 40.2363 | 1.0019 | 1.0019 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
17105 | Goodwood | Urban | 860 | 2.72 | 3.95 | 4.5259 | 1.738 | 0.02383 | 13 | 58.9679 | 58.935 | 2.0809 | 2.0792 | 7 | 0.24234 | 0.24234 | 0.0040389 | 0.0040389 | 0 | 0 | 0 | No
17106 | Brooker Hwy Lutana | Urban | 585 | 2.58 | 3.76 | 3.4896 | 6.6802 | 0.03801 | 8 | 123.4795 | 36.3048 | 1.0758 | 1.003 | 6 | 67.833 | 67.833 | 0.17549 | 0.17549 | 0 | 0 | 0 | No
17107 | Main Rd Moonah | Urban | 297 | 0 | 3.16 | 2.7141 | 1.7439 | 0.0065296 | 7 | 68.5034 | 68.4834 | 1.2137 | 1.211 | 1 | 0.08 | 0.08 | 0.0013333 | 0.0013333 | 1 | 1.0833 | 1.0833 | No
17108 | Derwent Park (Howard Road) | Urban | 25 | 0 | 1.45 | 0.90911 | 0.095655 | 0 | 2 | 40.998 | 40.0079 | 1.0992 | 1.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
17109 | Moonah (Lampton Ave)-Moonah (HEC Depot) | Urban | 39 | 0 | 1.42 | 1.1967 | 0.22371 | 0 | 1 | 39 | 39 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
18131 | A-City (West), B-North Hobart-City (West/South) | Urban | 615 | 0 | 4.67 | 3.4094 | 0.096117 | 0.43663 | 5 | 2.084 | 2.0703 | 0.044686 | 0.044229 | 4 | 32.5543 | 32.5543 | 0.3 | 0.3 | 0 | 0 | 0 | No
18133 | A-RHH, B-North Hobart (Brisbane Street) | Urban | 132 | 0 | 3.84 | 2.7596 | 0.0015358 | 0.2932 | 1 | 0.002579 | 0 | 0.0005158 | 0 | 2 | 12.1857 | 12.1857 | 0.064475 | 0.064475 | 0 | 0 | 0 | No
18134 | A-North Hobart, B-Domain | Urban | 1719 | 6.82 | 3.65 | 4.0151 | 8.7113 | 1.9941 | 25 | 324.1296 | 225.936 | 4.0766 | 3.091 | 13 | 125.1945 | 125.1945 | 0.47964 | 0.47964 | 0 | 0 | 0 | Yes
18135 | A-New Town Substation, B-Augusta Rd | Short Rural | 592 | 0.56 | 2.69 | 0 | 0.25004 | 0.0039842 | 5 | 7.2951 | 7.2951 | 0.1542 | 0.1542 | 3 | 0.32464 | 0.32464 | 0.0069565 | 0.0069565 | 0 | 0 | 0 | No
18136 | A-New Town-Mt Stuart, B-Stn Supp No1 (Transend) | Urban | 474 | 0.47 | 3.42 | 2.2903 | 0.0012092 | 0.0073788 | 1 | 0.047568 | 0.047568 | 0.0014414 | 0.0014414 | 2 | 0.36036 | 0.36036 | 0.0028829 | 0.0028829 | 0 | 0 | 0 | No
18141 | A-Stn Supp No2 (Transend), B-North Hobart | Short Rural | 429 | 0 | 3.15 | 0 | 0.017263 | 0.34393 | 4 | 0.23747 | 0.23747 | 0.0033684 | 0.0033684 | 1 | 15.3947 | 15.3947 | 0.078947 | 0.078947 | 2 | 2 | 2 | No
18142 | A-City (West), B-City (West) | Short Rural | 510 | 0 | 5.2 | 0.59765 | 0.14507 | 0 | 2 | 45.8377 | 45.8377 | 0.76267 | 0.76267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
18143 | A-North Hobart, B-Mount Stuart-City(North) | Urban | 1467 | 1.64 | 5.59 | 2.896 | 0.1433 | 0.65141 | 12 | 3.0574 | 3.0489 | 0.041277 | 0.040426 | 2 | 29.8723 | 29.8723 | 0.085106 | 0.085106 | 0 | 0 | 0 | No
18144 | A-North Hobart, B-Lenah Valley-New Town | Urban | 1215 | 2.46 | 7.8 | 3.3452 | 3.8632 | 0.81359 | 15 | 56.7402 | 28.2625 | 0.22555 | 0.15202 | 4 | 15.6262 | 15.6262 | 0.075182 | 0.075182 | 0 | 0 | 0 | No
18145 | Noth Hobart Substation | Urban | 147 | 0 | 3.87 | 1.3196 | 0.0092635 | 0 | 2 | 0.2271 | 0.21677 | 0.0020645 | 0.0010323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
18146 | A-Mount Stuart, B-New Town, Ogilvie High School | Urban | 1364 | 2.61 | 7.23 | 4.1515 | 0.34758 | 0.14268 | 16 | 4.0587 | 2.9901 | 0.022263 | 0.020567 | 6 | 0.72642 | 0.72642 | 0.018023 | 0.018023 | 0 | 0 | 0 | No
20534 | Glenorchy (East) | Short Rural | 295 | 1.51 | 2.11 | 1.0788 | 0 | 0.0014851 | 0 | 0 | 0 | 0 | 0 | 1 | 0.192 | 0.192 | 0.0032 | 0.0032 | 0 | 0 | 0 | No
20535 | West Moonah | Urban | 1706 | 4.65 | 5.79 | 4.3209 | 14.4404 | 0.35717 | 25 | 503.7331 | 38.5834 | 1.1963 | 0.19007 | 7 | 40.2168 | 40.2168 | 0.20346 | 0.20346 | 2 | 2 | 0 | No
20536 | Glenorchy (Central) | Urban | 893 | 2.32 | 2.67 | 2.4941 | 0.0071732 | 0.0098796 | 11 | 0.67154 | 0.58295 | 0.019491 | 0.010631 | 2 | 0.89369 | 0.89369 | 0.071539 | 0.071539 | 0 | 0 | 0 | No
20537 | Merton-Glenorchy (Central) | Urban | 822 | 2.85 | 4.84 | 2.3758 | 0.10673 | 0.00072381 | 6 | 6.8068 | 0.79925 | 1.0075 | 0.0060207 | 1 | 2.0884 | 2.0884 | 0.056444 | 0.056444 | 0 | 0 | 0 | No
20539 | Glenorchy (Central) | Short Rural | 128 | 0.11 | 3.92 | 0.5429 | 4.7734 | 0.012917 | 5 | 1090.5082 | 789.9669 | 3.17 | 2.0033 | 2 | 48.95 | 48.95 | 0.12833 | 0.12833 | 1 | 1.0417 | 1.0417 | Yes
20540 | Northgate-Nichols St | Urban | 192 | 0 | 3.43 | 2.7161 | 0.87367 | 0.0057453 | 5 | 49.4644 | 43.4644 | 3.0027 | 2.0027 | 1 | 0.08 | 0.08 | 0.0013333 | 0.0013333 | 2 | 2 | 2 | No
20541 | Rosetta-Berriedale | Urban | 740 | 3 | 7.51 | 5.2631 | 0.44077 | 0.4813 | 9 | 28.4021 | 2.0917 | 1.0989 | 0.029152 | 5 | 18.3478 | 18.3478 | 0.096373 | 0.096373 | 0 | 0 | 0 | No
20544 | Glenorchy (North)-Montrose | Urban | 832 | 3.12 | 3.86 | 2.7919 | 0.0093352 | 0.0040884 | 9 | 0.41359 | 0.27673 | 0.0090566 | 0.0050314 | 3 | 0.18113 | 0.18113 | 0.0030189 | 0.0030189 | 0 | 0 | 0 | No
20545 | Glenorchy (West) | Urban | 293 | 0 | 1.9 | 0.77855 | 0.00046757 | 0 | 1 | 0.092444 | 0.092444 | 0.0035556 | 0.0035556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
20547 | Stn Service No2 (Transend)-Merton-West Moonah | Urban | 933 | 3.8 | 0.76 | 2.3531 | 0.075008 | 1.3394 | 7 | 3.7815 | 3.7274 | 0.090507 | 0.088427 | 6 | 101.368 | 69.7685 | 0.43329 | 0.35527 | 0 | 0 | 0 | No
20548 | Lenah Valley | Short Rural | 1589 | 13.73 | 5 | 5.435 | 7.1538 | 0.55622 | 16 | 116.2871 | 3.548 | 0.16771 | 0.096304 | 9 | 11.2323 | 11.2323 | 0.13896 | 0.13896 | 0 | 0 | 0 | No
20549 | Berridale (West)-Glenlusk-Collinsvale | Short Rural | 1205 | 2.3 | 8.54 | 3.0478 | 0.048889 | 0.018167 | 11 | 36.0846 | 36.0632 | 0.10122 | 0.098293 | 11 | 1.9268 | 1.9268 | 0.070732 | 0.070732 | 0 | 0 | 0 | No
20551 | Glenorchy (West) | Urban | 212 | 2.29 | 0.64 | 1.4999 | 0.02179 | 0 | 4 | 48.1637 | 48.0702 | 0.13099 | 0.12164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
20552 | Montrose | Urban | 1023 | 5.51 | 2.94 | 3.1431 | 2.2359 | 0.04106 | 11 | 107.0147 | 107.0015 | 1.016 | 1.0147 | 4 | 2.9376 | 2.9376 | 0.036885 | 0.036885 | 0 | 0 | 0 | No
20553 | Future | Short Rural | 923 | 47.33 | 2.59 | 2.6692 | 0.20958 | 0.04066 | 22 | 18.8807 | 18.7773 | 0.105 | 0.1006 | 6 | 2.9206 | 2.9206 | 0.10651 | 0.10651 | 0 | 0 | 0 | No
20554 | Glenorchy (Central) | Urban | 401 | 0.47 | 2.88 | 2.9016 | 2.212 | 0 | 2 | 115.1117 | 115.1117 | 1.0013 | 1.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
21081 | Claremont | Urban | 811 | 2.73 | 4.14 | 2.6339 | 0.01369 | 0 | 8 | 0.83407 | 0.80996 | 0.012857 | 0.0096424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
21083 | Cadburys | Urban | 342 | 0 | 4.04 | 3.5031 | 0.65267 | 0.017473 | 2 | 1.4731 | 1.4683 | 0.01861 | 0.018127 | 2 | 0.058006 | 0.058006 | 0.00096677 | 0.00096677 | 0 | 0 | 0 | No
21084 | Cadburys | Urban | 101 | 0 | 2.53 | 2.8278 | 0.0033874 | 0 | 2 | 0.13333 | 0 | 0.026667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
21085 | Claremont | Urban | 981 | 2.09 | 3.42 | 3.0083 | 5.0217 | 0.0011438 | 9 | 163.7295 | 7.3972 | 0.16365 | 0.10196 | 1 | 0.089469 | 0.089469 | 0.0014911 | 0.0014911 | 0 | 0 | 0 | No
21086 | Claremont (East) | Urban | 713 | 2.37 | 2.67 | 2.7141 | 0.31454 | 0.55177 | 14 | 16.9829 | 16.6898 | 0.060164 | 0.05659 | 4 | 88.6016 | 88.6016 | 0.33001 | 0.33001 | 0 | 0 | 0 | No
21087 | Rosetta | Urban | 355 | 0.88 | 1.71 | 1.8184 | 0.083523 | 0.0022051 | 6 | 10.592 | 0.58667 | 0.021333 | 0.014222 | 1 | 0.21333 | 0.21333 | 0.0035556 | 0.0035556 | 0 | 0 | 0 | No
21088 | Berridale | Urban | 339 | 1.07 | 1.25 | 1.0629 | 0.051323 | 0.0051749 | 2 | 300.1927 | 300.1927 | 1.0034 | 1.0034 | 3 | 0.61935 | 0.61935 | 0.010323 | 0.010323 | 0 | 0 | 0 | Yes
21089 | Claremont West-Austins Ferry | Short Rural | 1081 | 13.43 | 5.28 | 3.0149 | 2.4303 | 0.12244 | 12 | 156.0277 | 156.0235 | 0.49811 | 0.49727 | 1 | 17.0693 | 17.0693 | 0.052521 | 0.052521 | 0 | 0 | 0 | No
22323 | Shorline-Howrah-Tranmere | Urban | 487 | 1.41 | 3.2 | 1.972 | 2.743 | 0.046411 | 12 | 170.3268 | 123.7915 | 3.096 | 2.0844 | 3 | 48.6764 | 48.6764 | 0.11491 | 0.11491 | 0 | 0 | 0 | No
22324 | Mornington | Short Rural | 283 | 9.78 | 3.82 | 2.1926 | 0.72877 | 0.63139 | 7 | 65.2795 | 20.4084 | 2.0184 | 1.0205 | 6 | 32.923 | 32.923 | 0.088308 | 0.088308 | 0 | 0 | 0 | No
22325 | Ninabah St Howrah | Short Rural | 808 | 0 | 5.59 | 1.2769 | 0.56824 | 0.015502 | 9 | 55.8204 | 7.7665 | 1.1905 | 0.18909 | 3 | 37.36 | 37.36 | 0.18327 | 0.18327 | 0 | 0 | 0 | No
22326 | Rokeby | Urban | 343 | 0 | 2.77 | 0.88243 | 0.52881 | 0.12667 | 7 | 47.4539 | 1.4539 | 1.0209 | 0.02087 | 11 | 53.3478 | 52.513 | 0.36087 | 0.34696 | 0 | 0 | 0 | No
22328 | Clarence St Bellerive | Short Rural | 780 | 2.82 | 4.61 | 1.444 | 0.89462 | 0.28646 | 6 | 56.8011 | 56.8011 | 2.0352 | 2.0352 | 6 | 41.0291 | 41.0291 | 0.12412 | 0.12412 | 0 | 0 | 0 | No
22329 | Howrah-Rokeby-Bellerive Zone | Short Rural | 982 | 4.89 | 6.47 | 3.0083 | 0.38402 | 0.10779 | 8 | 14.8635 | 0.26062 | 0.31167 | 0.006717 | 6 | 88.8491 | 88.8491 | 1.0558 | 1.0558 | 0 | 0 | 0 | No
22330 | Rokeby | Short Rural | 70 | 0.79 | 0.19 | 0.20717 | 0.047728 | 0.064762 | 3 | 69.1333 | 22.1333 | 1.0533 | 0.053333 | 2 | 346.6 | 346.6 | 1.0267 | 1.0267 | 0 | 0 | 0 | No
22331 | Howrah-Tranmere | Urban | 901 | 0 | 6.65 | 3.2891 | 3.8259 | 0.0027622 | 11 | 179.9144 | 36.7267 | 3.1967 | 2.1173 | 2 | 0.14545 | 0.14545 | 0.0024242 | 0.0024242 | 0 | 0 | 0 | No
25308 | Geilston Bay Zone Substation | Urban | 901 | 2.21 | 0.2 | 14.2521 | 0 | 0 | 2 | 1.5455 | 1.5455 | 0.030303 | 0.030303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
26161 | Risdon-Otago Bay | Short Rural | 622 | 13.2 | 6.03 | 2.2396 | 0.083737 | 0.55378 | 13 | 5.3456 | 5.211 | 0.054104 | 0.040636 | 12 | 11.8745 | 11.8745 | 0.10391 | 0.10391 | 1 | 1.0871 | 1.0871 | No
26162 | Lindisfarne (West)-Geilston Bay | Urban | 712 | 1.17 | 2.4 | 3.3827 | 1.1686 | 0 | 7 | 60.5684 | 60.526 | 0.29311 | 0.28971 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
26163 | Lindisfarne-Rose Bay-Montagu Bay | Urban | 613 | 3.34 | 1.42 | 4.3119 | 1.7956 | 0.00066731 | 10 | 117.1593 | 117.1498 | 0.44952 | 0.44761 | 2 | 6.933 | 6.933 | 0.073684 | 0.073684 | 0 | 0 | 0 | No
26164 | Risdon Brook | Urban | 1133 | 8.38 | 4.57 | 4.2517 | 0.053483 | 0.58887 | 10 | 2.7496 | 2.7496 | 0.041275 | 0.041275 | 5 | 60.5258 | 60.5258 | 0.261 | 0.261 | 0 | 0 | 0 | No
26165 | Flagstaff Gully-Warrane (North) - Kennedy Drive | Urban | 405 | 4.32 | 4.1 | 3.3827 | 3.2207 | 0.053678 | 12 | 204.4962 | 204.4723 | 3.066 | 3.0636 | 4 | 16.9244 | 16.9244 | 0.048467 | 0.048467 | 0 | 0 | 0 | No
26166 | Lindisfarne (East)-Rosny Park | Urban | 1114 | 4.7 | 4.25 | 3.9242 | 0.43246 | 0 | 10 | 14.3792 | 14.2611 | 0.045009 | 0.042105 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
26167 | Risdon Vale | Short Rural | 749 | 9.11 | 4.4 | 3.6567 | 0.016274 | 0.0066037 | 6 | 0.44812 | 0.44812 | 0.0070943 | 0.0070943 | 3 | 0.21283 | 0.21283 | 0.0035471 | 0.0035471 | 0 | 0 | 0 | No
26169 | Lindisfarne (Central)-Montagu Bay-Rosny Matric | Urban | 905 | 2.61 | 5.16 | 4.2116 | 0.73316 | 0.0015415 | 5 | 61.7386 | 61.7268 | 1.1499 | 1.1487 | 1 | 2.0649 | 2.0649 | 0.073746 | 0.073746 | 1 | 1 | 1 | No
27171 | Mornington (West)-Bellerive (East)-Station Service | Urban | 1346 | 4.07 | 3.57 | 4.3119 | 1.0003 | 1.2684 | 13 | 38.487 | 38.4767 | 1.0499 | 1.0489 | 22 | 122.7742 | 122.7742 | 0.50669 | 0.50669 | 2 | 1.9974 | 1.9974 | No
27172 | Warrane-Rosny Park | Urban | 756 | 0 | 4.16 | 3.4896 | 0.28921 | 2.3017 | 18 | 4.188 | 3.6867 | 0.060979 | 0.052028 | 15 | 98.5035 | 98.5035 | 0.27692 | 0.27692 | 1 | 1.0699 | 1.0699 | No
27173 | Cambridge | Short Rural | 155 | 8.58 | 1.58 | 0.28739 | 0.1148 | 0.0022184 | 6 | 71.7039 | 2.137 | 0.09352 | 0.028719 | 2 | 0.67747 | 0.67747 | 0.011782 | 0.011782 | 0 | 0 | 0 | No
27174 | Open | Short Rural | 155 | 0 | 0 | 3.7237 | 0.1148 | 0.0022184 | 1 | 0.05891 | 0 | 0.005891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
27175 | Warrane-Bellerive (West) | Urban | 1313 | 2.68 | 3.15 | 4.0712 | 0.9121 | 0.052492 | 10 | 49.8367 | 49.7061 | 1.0495 | 1.0473 | 8 | 13.7007 | 13.7007 | 0.075646 | 0.075646 | 0 | 0 | 0 | No
27176 | Warrane-Rosny | Urban | 235 | 0.33 | 5.21 | 3.1152 | 0.021739 | 0.043343 | 2 | 6.823 | 6.823 | 0.14389 | 0.14389 | 2 | 55.9405 | 55.9405 | 0.17234 | 0.17234 | 0 | 0 | 0 | No
27178 | Howrah (North) | Urban | 592 | 3.76 | 2.54 | 2.4133 | 0.0071097 | 0.023553 | 6 | 0.2273 | 0.17186 | 0.0066528 | 0.005544 | 3 | 0.60651 | 0.60651 | 0.0033264 | 0.0033264 | 0 | 0 | 0 | No
28221 | Tranmere-Droughty Point | Short Rural | 850 | 10.85 | 3.34 | 3.3994 | 6.123 | 0.3186 | 18 | 244.6725 | 244.6512 | 2.1542 | 2.1517 | 3 | 12.8807 | 12.8807 | 0.066358 | 0.066358 | 1 | 1.0168 | 1.0168 | No
28222 | Howrah-Rokeby | Urban | 716 | 0 | 4.23 | 2.184 | 0.82903 | 0.80749 | 14 | 120.2533 | 120.138 | 0.39527 | 0.38667 | 24 | 91.4021 | 91.2989 | 0.58108 | 0.57935 | 0 | 0 | 0 | No
28223 | Sandford-Cremorne | Short Rural | 951 | 66.86 | 1.83 | 2.6573 | 14.9842 | 0.25226 | 46 | 1377.257 | 277.3291 | 5.5005 | 4.0371 | 19 | 14.0733 | 14.0733 | 0.075419 | 0.075419 | 2 | 1.9865 | 0 | No
28224 | Lauderdale-Acton | Short Rural | 1308 | 28.21 | 3.21 | 4.3139 | 10.8784 | 0.66092 | 36 | 265.6321 | 54.2116 | 2.2009 | 1.147 | 29 | 31.4814 | 31.4814 | 0.1477 | 0.1477 | 0 | 0 | 0 | No
28225 | Rokeby Village | Urban | 643 | 0 | 4.33 | 1.8491 | 0.0026072 | 0.48225 | 2 | 0.236 | 0.236 | 0.004 | 0.004 | 5 | 94.235 | 94.235 | 0.3185 | 0.3185 | 0 | 0 | 0 | No
28227 | Clarendon Vale-Pass Road | Urban | 554 | 0.57 | 5.41 | 2.2562 | 0.014422 | 0.71241 | 14 | 0.90451 | 0.83357 | 0.017736 | 0.012668 | 28 | 62.0966 | 62.0966 | 0.19129 | 0.19129 | 0 | 0 | 0 | No
28228 | Sandford-South Arm-Opossum Bay | Short Rural | 1248 | 79.87 | 3.78 | 3.2891 | 11.1621 | 0.61921 | 49 | 667.2687 | 349.6583 | 4.0398 | 3.1337 | 22 | 12.5337 | 12.5337 | 0.074233 | 0.074233 | 1 | 1.0043 | 1.0043 | No
28229 | Howrah (South) | Urban | 10 | 0.96 | 2.47 | 3.249 | 0.00036111 | 0 | 1 | 0.095352 | 0 | 0.01907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
28230 | Howrah (North) | Short Rural | 77 | 2.63 | 0.66 | 0.23064 | 0 | 0.083854 | 0 | 0 | 0 | 0 | 0 | 3 | 303.9267 | 302.5149 | 0.97353 | 0.95 | 0 | 0 | 0 | No
29481 | Mount Rumney | Short Rural | 364 | 14.79 | 6.45 | 1.3216 | 0.22195 | 0.21374 | 10 | 36.3407 | 20.9648 | 1.2174 | 0.2153 | 6 | 26.0994 | 26.0994 | 0.14953 | 0.14953 | 0 | 0 | 0 | No
29482 | Backhouse Lane | Short Rural | 76 | 6.28 | 0.7 | 0.81124 | 0.99476 | 0 | 7 | 643.9509 | 628.6317 | 3.0624 | 2.1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
29483 | Seven Mile Beach | Short Rural | 670 | 23.96 | 1.53 | 2.6008 | 0.17373 | 0.50227 | 9 | 50.2112 | 34.3308 | 1.2981 | 0.30439 | 7 | 34.1544 | 34.1544 | 0.099558 | 0.099558 | 0 | 0 | 0 | No
29485 | Hobart Airport | Short Rural | 1 | 4.16 | 6.18 | 1.8728 | 0.74167 | 0 | 1 | 39.0055 | 0 | 1.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
29486 | Cranston Parade | Short Rural | 4 | 0.86 | 2.72 | 0.79379 | 0.102 | 0.36751 | 1 | 32.9642 | 0 | 0.89092 | 0 | 1 | 5.1492 | 5.1492 | 0.018325 | 0.018325 | 0 | 0 | 0 | No
29488 | Cambridge-Richmond Golf Course-Brighton | Short Rural | 379 | 39.26 | 2.73 | 3.2566 | 0.64007 | 0.04365 | 13 | 99.5537 | 99.5537 | 0.92279 | 0.92279 | 8 | 0.91107 | 0.91107 | 0.016178 | 0.016178 | 0 | 0 | 0 | No
29489 | Pittwater Road | Short Rural | 195 | 12.82 | 3.72 | 1.7284 | 0.050668 | 0 | 5 | 12.744 | 6.7856 | 0.24791 | 0.12081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
29490 | Acton Park | Short Rural | 316 | 13.34 | 2.86 | 1.2872 | 0.061381 | 0.012261 | 5 | 6.4017 | 6.4017 | 0.058197 | 0.058197 | 4 | 2.5747 | 2.5747 | 0.043128 | 0.043128 | 0 | 0 | 0 | No
30603 | Huonville (North)-Ranelagh-Judbury-Lonnavale | Short Rural | 1025 | 88.53 | 1.41 | 3.8651 | 19.2213 | 1.0188 | 28 | 1027.8512 | 39.1847 | 1.6006 | 0.13335 | 12 | 38.3764 | 38.3764 | 0.19393 | 0.19393 | 0 | 0 | 0 | No
30604 | Huonville (Central)-South Franklin-Glen Huon | Short Rural | 848 | 72.48 | 1.78 | 2.7616 | 2.6867 | 0.74122 | 31 | 236.9284 | 236.9041 | 5.5434 | 5.5416 | 22 | 69.7991 | 69.7991 | 0.30059 | 0.30059 | 1 | 1.0379 | 1.0379 | No
30605 | Huonville (South)-Franklin | Short Rural | 691 | 33.39 | 0.88 | 2.4977 | 4.05 | 0.56374 | 19 | 278.6888 | 174.3559 | 2.6502 | 1.5152 | 12 | 45.2193 | 45.2193 | 0.24737 | 0.24737 | 0 | 0 | 0 | No
30606 | Cradoc-Cygnet-Glaziers Bay | Short Rural | 983 | 70.95 | 0.67 | 2.918 | 3.7692 | 0.12461 | 30 | 211.0227 | 210.9756 | 1.5294 | 1.5272 | 15 | 7.4357 | 7.4357 | 0.042568 | 0.042568 | 0 | 0 | 0 | No
30607 | Pelverata-Cygnet-Gardners Bay-Verona Sands | Short Rural | 1423 | 138.28 | 0.79 | 2.4668 | 20.54 | 0.54069 | 46 | 1125.7576 | 159.3735 | 2.5213 | 1.8643 | 34 | 47.4489 | 47.4489 | 0.22867 | 0.22867 | 0 | 0 | 0 | No
30608 | Grove-Crabtree-Lower Longley-Mountain River | Short Rural | 1244 | 130.22 | 0.19 | 3.7937 | 11.208 | 0.86457 | 54 | 448.6678 | 133.2403 | 1.9612 | 1.476 | 29 | 38.2637 | 38.2637 | 0.14876 | 0.14876 | 0 | 0 | 0 | No
31002 | Wattle Grove-Petcheys Bay-Lymington | Short Rural | 389 | 57.26 | 1.56 | 0.76812 | 7.213 | 0.47015 | 24 | 1271.4348 | 29.4158 | 1.7969 | 0.94123 | 7 | 171.703 | 171.703 | 0.61161 | 0.61161 | 0 | 0 | 0 | No
31007 | Geeveston-Police Point-Surveyors Bay | Short Rural | 1041 | 94.95 | 1.98 | 2.04 | 14.1818 | 0.57681 | 38 | 1174.5738 | 42.704 | 1.2241 | 0.52145 | 20 | 27.501 | 27.501 | 0.12085 | 0.12085 | 0 | 0 | 0 | No
31008 | Dover-Southport-Lune River | Short Rural | 1103 | 94.93 | 11.37 | 2.4672 | 6.5739 | 2.0678 | 37 | 505.63 | 496.2622 | 4.8083 | 4.8019 | 14 | 45.445 | 45.445 | 0.16701 | 0.16701 | 0 | 0 | 0 | No
31010 | Port Huon-Castle Forbes Bay | Short Rural | 443 | 28.52 | 0.07 | 1.1301 | 0.4605 | 0.28434 | 16 | 72.3959 | 38.5422 | 0.31248 | 0.22275 | 3 | 23.7644 | 23.7644 | 0.099594 | 0.099594 | 0 | 0 | 0 | No
32374 | Summerleas Rd Kingston - Kingston Zone | Short Rural | 1078 | 3.17 | 7.93 | #N/A | 0.62796 | 0.43688 | 6 | 884.3626 | 181.2297 | 3.0775 | 1.0775 | 2 | 33.233 | 33.233 | 0.13676 | 0.13676 | 0 | 0 | 0 | No
32377 | Kingston | Short Rural | 306 | 0.27 | 2.51 | #N/A | 0.00033142 | 0.14229 | 0 | 0 | 0 | 0 | 0 | 5 | 129.3055 | 129.3055 | 0.72222 | 0.72222 | 0 | 0 | 0 | No
32379 | Whitewater Cresent | Short Rural | 1393 | 11.22 | 5.4 | #N/A | 13.5112 | 0.74967 | 12 | 338.7798 | 136.0943 | 2.3352 | 1.0246 | 5 | 50.9792 | 50.9792 | 0.15142 | 0.15142 | 0 | 0 | 0 | No
33271 | Snug-Conningham-Oyster Cove-Bruny Is | Short Rural | 1500 | 153.86 | 2.68 | 2.4875 | 31.6943 | 1.3868 | 49 | 2633.4953 | 606.9797 | 5.3753 | 3.9379 | 18 | 107.8972 | 107.8972 | 0.42162 | 0.42162 | 6 | 6.0431 | 5.0359 | Yes
33272 | Nierinna-West Margate-Kaoota-Sandfly-Longley | Short Rural | 1399 | 114.02 | 0.59 | 4.4296 | 19.1092 | 0.5519 | 39 | 930.7113 | 51.717 | 0.61158 | 0.22368 | 16 | 17.2328 | 14.2606 | 0.10235 | 0.075333 | 3 | 3.0194 | 3.0194 | No
33274 | Margate,Kingston Term,Huntingfield,Blackmans Bay | Urban | 802 | 12.29 | 2.59 | 6.2964 | 13.5234 | 0.07075 | 10 | 528.0535 | 5.7133 | 1.3824 | 0.053316 | 8 | 1.6365 | 1.6365 | 0.014316 | 0.014316 | 4 | 4 | 4 | No
33275 | Tinderbox-Dennes Point-Killora | Short Rural | 1167 | 60.89 | 6.83 | 3.4704 | 0.21566 | 1.6726e-05 | 38 | 654.3465 | 46.775 | 1.6531 | 0.36198 | 1 | 0.03947 | 0.03947 | 0.00065784 | 0.00065784 | 1 | 1 | 1 | No
33276 | Lower Snug-Nicolls Rivulet-Kettering-Gordon | Short Rural | 1542 | 148.27 | 0.39 | 3.9312 | 19.2884 | 3.0543 | 81 | 1074.1982 | 439.0598 | 6.5621 | 5.2442 | 26 | 97.6424 | 96.3964 | 0.30021 | 0.29559 | 5 | 5.0225 | 5.0225 | No
33277 | Hazell Bros Industrial | Urban | 1 | 0.09 | 0.2 | 0.35739 | 0 | 0.069591 | 0 | 0 | 0 | 0 | 0 | 1 | 23735.0202 | 23735.0202 | 101 | 101 | 0 | 0 | 0 | Yes
34251 | Channel Hwy Margate | Urban | 67 | 9.75 | 0.48 | 3.5698 | 8.9018 | 0 | 7 | 392.173 | 45.1732 | 1.274 | 0.27399 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | No
34252 | Sirius Drive-Margate - Blackmans Bay | Short Rural | 1639 | 7.63 | 6.28 | 1.079 | 4.1625 | 0.1598 | 8 | 570.3503 | 498.13 | 1.9234 | 1.73 | 1 | 21.5064 | 21.5064 | 0.047371 | 0.047371 | 4 | 4 | 4 | No
34253 | North West Blackmans Bay | Urban | 601 | 1.86 | 5.13 | 5.0399 | 8.1018 | 0.012413 | 18 | 418.0429 | 29.0844 | 2.0448 | 1.0498 | 6 | 0.79668 | 0.79668 | 0.013278 | 0.013278 | 4 | 4 | 4 | No
34256 | Channel Hwy-Redwood Rd | Urban | 469 | 1.56 | 5.42 | 3.9629 | 4.4525 | 0.00054965 | 16 | 396.5815 | 390.5971 | 3.2929 | 3.2864 | 1 | 0.021534 | 0.021534 | 0.0021534 | 0.0021534 | 2 | 2 | 2 | Yes
34257 | Summerleas Zone-Huon Hwy-Kingston | Urban | 5 | 0 | 3.39 | 3.249 | 5.8554 | 4.9409 | 1 | 0.89 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.0625 | 1.0625 | No
34258 | Legana Ave-Maronoa Rd-Channel Hwy | Urban | 255 | 0.59 | 3.99 | 2.9902 | 1.1171 | 0 | 2 | 88.2612 | 0.26101 | 1.0013 | 0.0013051 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
34259 | Chanel Hwy-Beach Rd-Kingston (North) | Urban | 1515 | 7.26 | 7.87 | 5.1602 | 1.5888 | 1.4879 | 17 | 53.7455 | 53.6664 | 0.47722 | 0.47482 | 9 | 48.2099 | 48.2099 | 0.2444 | 0.2444 | 2 | 2.0629 | 2.0629 | No
34260 | Redwood Road | Urban | 661 | 0.09 | 5.34 | 2.2943 | 0.0043103 | 0.97983 | 3 | 0.69494 | 0.67736 | 0.16835 | 0.16659 | 10 | 42.0528 | 42.0528 | 0.14593 | 0.14593 | 1 | 1 | 1 | No
34261 | Leslie Vale-Longley-Bonnet Hill | Short Rural | 435 | 43.81 | 0.38 | 4.5626 | 5.4154 | 0.38171 | 24 | 178.8353 | 44.3721 | 0.89954 | 0.26107 | 3 | 5.4501 | 5.4501 | 0.020886 | 0.020886 | 2 | 2 | 2 | No
34262 | 0 | Short Rural | 435 | 0 | 0 | 5.1362 | 5.4154 | 0.38171 | 6 | 0.15863 | 0.13748 | 0.006345 | 0.0031725 | 1 | 0.06345 | 0.06345 | 0.0010575 | 0.0010575 | 0 | 0 | 0 | No
35010 | New Norfolk Township (South) | Short Rural | 897 | 80.31 | 0.27 | 2.5336 | 0.87233 | 0.10511 | 26 | 93.9208 | 91.4782 | 0.50647 | 0.50005 | 23 | 48.9581 | 48.9581 | 0.22765 | 0.22765 | 0 | 0 | 0 | No
35011 | Lachlan Park-Molesworth-Lachlan | Short Rural | 1052 | 102.6 | 2.07 | 2.5454 | 0.55062 | 1.4963 | 25 | 39.7012 | 20.5612 | 1.3771 | 1.3576 | 29 | 74.2425 | 74.2425 | 0.26207 | 0.26207 | 0 | 0 | 0 | No
35012 | New Norfolk Township (South) | Urban | 464 | 1.95 | 2.19 | 2.5536 | 0.0080863 | 0.011128 | 4 | 0.25764 | 0.20968 | 0.0054818 | 0.0027409 | 5 | 0.41113 | 0.41113 | 0.0068522 | 0.0068522 | 0 | 0 | 0 | No
37001 | Gretna | Short Rural | 116 | 35.49 | 0 | 0.2541 | 0.16177 | 0.065222 | 5 | 94.7072 | 94.7072 | 2.2876 | 2.2876 | 1 | 86.8856 | 86.8856 | 0.21721 | 0.21721 | 0 | 0 | 0 | No
37002 | Bushy Park-Plenty | Short Rural | 181 | 30.51 | 0 | 0.76872 | 0.5714 | 0.12275 | 10 | 116.8168 | 116.8024 | 2.2004 | 2.199 | 5 | 26.9303 | 26.9303 | 0.11161 | 0.11161 | 0 | 0 | 0 | No
38002 | National Park-Maydena | Short Rural | 270 | 45.93 | 0.66 | 0.72861 | 0.92622 | 1.5606 | 11 | 246.8361 | 11.7082 | 1.239 | 0.077338 | 5 | 321.5695 | 321.5695 | 1.0404 | 1.0404 | 0 | 0 | 0 | No
39565 | ANM Backup-New Norfolk Township (North)-Magra | Short Rural | 1594 | 48.36 | 0.99 | 5.0098 | 1.1242 | 0.1422 | 27 | 23.3201 | 23.247 | 0.14611 | 0.14333 | 28 | 7.5427 | 7.5427 | 0.11785 | 0.11785 | 0 | 0 | 0 | No
39568 | Dromedary | Short Rural | 223 | 32.46 | 1.04 | 0.91452 | 0.52435 | 0.049489 | 7 | 70.4842 | 70.4842 | 0.5108 | 0.5108 | 6 | 5.5088 | 5.5088 | 0.053441 | 0.053441 | 0 | 0 | 0 | No
39570 | Metropolitan Water Board (Lawitta) | Urban | 22 | 11.88 | 0.8 | 5.2786 | 0 | 0.044167 | 0 | 0 | 0 | 0 | 0 | 1 | 0.1335 | 0.1335 | 0.0024272 | 0.0024272 | 2 | 3.5379 | 3.5379 | No
39571 | Black Hills-Hayes-Glenora-Westerway Zone Sub | Short Rural | 770 | 157.41 | 1.87 | 3.5217 | 2.907 | 1.1804 | 33 | 184.8752 | 179.3826 | 3.2038 | 3.1634 | 12 | 28.8331 | 28.8331 | 0.11648 | 0.11648 | 4 | 0.32788 | 0.32788 | No
40001 | Richmond | Short Rural | 208 | 2.25 | 0.44 | 0.6538 | 3.469 | 0.0010839 | 7 | 651.7656 | 33.9892 | 1.4497 | 0.44108 | 1 | 0.51892 | 0.51892 | 0.0086486 | 0.0086486 | 0 | 0 | 0 | No
40002 | Campania-Colebrook-Rhyndaston | Long Rural | 933 | 222.04 | 0 | 1.7984 | 9.4981 | 0.27643 | 51 | 689.4305 | 537.6095 | 4.0069 | 3.5998 | 16 | 28.9966 | 28.9966 | 0.10474 | 0.10474 | 0 | 0 | 0 | No
40003 | Tea Tree | Short Rural | 235 | 49.64 | 0.15 | 0.97609 | 0.57858 | 0.034082 | 12 | 126.9839 | 126.9839 | 1.338 | 1.338 | 5 | 11.6595 | 11.6595 | 0.05751 | 0.05751 | 0 | 0 | 0 | No
41511 | Midway Point | Short Rural | 1310 | 16.65 | 1.77 | 3.5735 | 3.5587 | 0.047452 | 21 | 107.6015 | 37.3051 | 0.25485 | 0.19808 | 16 | 6.0618 | 6.0618 | 0.039616 | 0.039616 | 1 | 0.99805 | 0.99805 | No
41512 | Penna-Richmond-Richmond Zone Sub-Grasstree Hill | Short Rural | 380 | 68.37 | 2.31 | 4.5642 | 5.6992 | 0.17466 | 25 | 398.3931 | 398.3931 | 2.829 | 2.829 | 9 | 5.9676 | 5.9676 | 0.055708 | 0.055708 | 1 | 1.0183 | 1.0183 | No
41513 | Sorell | Urban | 1191 | 12.4 | 3.86 | 4.9071 | 5.3232 | 0.29221 | 17 | 217.8438 | 217.822 | 3.0496 | 3.049 | 17 | 8.809 | 8.809 | 0.063629 | 0.063629 | 0 | 0 | 0 | No
41514 | Nugent-Lewisham-Connellys Marsh-Port Arthur | Short Rural | 1853 | 60.27 | 2.59 | 5.3347 | 1.094 | 0.29147 | 48 | 23.6223 | 15.3509 | 0.2054 | 0.1954 | 13 | 10.3411 | 10.3315 | 0.072411 | 0.07049 | 0 | 0 | 0 | No
41515 | Forcett-Copping-Nubeena-Highcroft-Saltwater River | Long Rural | 2890 | 331.74 | 12.92 | 4.7844 | 22.4511 | 1.7976 | 91 | 1482.6906 | 461.1821 | 9.2425 | 5.8896 | 58 | 73.1663 | 73.1663 | 0.33003 | 0.33003 | 2 | 2.0061 | 1.0031 | No
41516 | Orielton-Runnymede-Levendale-Buckland-Oatlands | Long Rural | 2120 | 526.35 | 2.04 | 4.0849 | 7.6991 | 2.083 | 124 | 343.609 | 145.0934 | 3.9772 | 1.62 | 64 | 68.1378 | 68.1378 | 0.35658 | 0.35658 | 0 | 0 | 0 | No
41517 | Pawleena-Dodges Ferry-Carlton-Primrose Sands | Short Rural | 772 | 118.44 | 5.93 | 4.2906 | 14.4088 | 0.77644 | 50 | 927.8905 | 589.855 | 11.0355 | 9.4115 | 31 | 84.2608 | 84.2608 | 0.24478 | 0.24478 | 1 | 0.99283 | 0.99283 | Yes
41518 | ? | Short Rural | 1940 | 111.21 | 3.53 | 4.1334 | 4.1497 | 0.40069 | 72 | 222.9139 | 82.6754 | 1.1518 | 0.32463 | 37 | 23.7956 | 23.7956 | 0.13124 | 0.13124 | 0 | 0 | 0 | No
43505 | Chip Mill | Short Rural | 2 | 9.52 | 0.74 | 0 | 0.058263 | 0 | 5 | 557.0002 | 517.0002 | 5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
43506 | Triabunna Township | Short Rural | 1681 | 81.67 | 1.22 | 2.7745 | 5.4348 | 0.30327 | 54 | 559.9365 | 543.9773 | 5.513 | 5.4967 | 11 | 8.5045 | 8.5045 | 0.043319 | 0.043319 | 1 | 1.0129 | 0 | No
43507 | Swansea | Long Rural | 1393 | 204.03 | 0.46 | 2.5831 | 2.6098 | 0.28236 | 90 | 185.1462 | 183.394 | 2.2644 | 2.2571 | 28 | 13.8305 | 13.8091 | 0.12442 | 0.12316 | 0 | 0 | 0 | No
45001 | Gretna-Gretna Zone Substation | Short Rural | 53 | 28.42 | 0.04 | 1.7167 | 4.294 | 0.42666 | 22 | 1020.7874 | 1020.7257 | 8.8404 | 8.8343 | 4 | 147.7902 | 147.7902 | 0.89697 | 0.89697 | 0 | 0 | 0 | Yes
45002 | Hollow Tree-Bothwell-Jericho | Long Rural | 687 | 289.74 | 0.7 | 1.3959 | 7.8529 | 0.42183 | 71 | 1405.4345 | 1142.8089 | 7.429 | 6.7167 | 20 | 47.5379 | 47.5379 | 0.26154 | 0.26154 | 0 | 0 | 0 | Yes
45003 | Hamilton Zone Sub-Ouse-Strickland-Lawrenny | Short Rural | 601 | 183.26 | 0.24 | 3.626 | 4.1536 | 0.19598 | 46 | 536.1226 | 529.7517 | 5.5955 | 5.5853 | 3 | 10.4404 | 10.4404 | 0.055694 | 0.055694 | 0 | 0 | 0 | No
48180 | Gagebrook (West)-Old Beach-Austins Ferry-Granton | Short Rural | 1040 | 3.51 | 9.02 | 3.6842 | 0.042151 | 0.21979 | 18 | 1.6917 | 1.6605 | 0.018762 | 0.015635 | 23 | 7.5779 | 7.5779 | 0.04899 | 0.04899 | 1 | 1.0001 | 1.0001 | No
48181 | Gagebrook (Lamprill Circle-Highway Side) | Short Rural | 288 | 0 | 6.25 | 0.97268 | 0.0039721 | 0.040306 | 3 | 0.35334 | 0.31851 | 0.007465 | 0.0049767 | 22 | 3.2846 | 3.2846 | 0.054743 | 0.054743 | 0 | 0 | 0 | No
48182 | Gagebrook-Old Beach-Austins Ferry | Short Rural | 1218 | 19.34 | 11.44 | 5.3447 | 0.58217 | 0.074484 | 15 | 50.0304 | 50.0071 | 2.0887 | 2.0864 | 19 | 4.8757 | 4.8757 | 0.076206 | 0.076206 | 1 | 1 | 1 | No
48183 | Bridgewater--Gagebrook | Short Rural | 795 | 47 | 2.82 | 2.5891 | 0.68777 | 0.86132 | 20 | 39.8536 | 39.8364 | 0.2999 | 0.29783 | 33 | 42.0012 | 42.0012 | 0.1927 | 0.1927 | 1 | 1.0022 | 1.0022 | No
48184 | Bridgewater (East) | Urban | 1120 | 0 | 7.9 | 3.8446 | 0.089863 | 1.9958 | 10 | 1.3686 | 1.3102 | 0.044551 | 0.041677 | 32 | 57.6551 | 57.6551 | 0.18347 | 0.18347 | 1 | 1.0301 | 1.0301 | No
48185 | Granton-Dromedary-Broadmarsh-Elderslie--Pelham | Short Rural | 1116 | 176.47 | 5.23 | 2.906 | 1.439 | 0.38694 | 35 | 123.3063 | 38.8757 | 0.57853 | 0.21608 | 31 | 28.163 | 28.163 | 0.16106 | 0.16106 | 3 | 3.0324 | 3.0324 | No
48187 | Bridgewater (West) | Urban | 557 | 1.79 | 3.09 | 2.0075 | 5.2968 | 0.17073 | 10 | 516.7466 | 0.8665 | 1.0636 | 0.0094039 | 26 | 16.2217 | 16.2217 | 0.083963 | 0.083963 | 1 | 1 | 0 | No
48188 | Brighton (West) | Short Rural | 1303 | 31 | 4.04 | 4.0833 | 1.1273 | 0.14006 | 29 | 109.8181 | 98.0777 | 2.1132 | 2.098 | 15 | 27.1733 | 27.1733 | 0.17293 | 0.17293 | 13 | 13.0376 | 13.0376 | No
48190 | Brighton (East)-Dysart-Kempton-Melton Mowbray | Short Rural | 1562 | 158.15 | 2.96 | 4.8815 | 7.9566 | 0.29013 | 35 | 367.8228 | 367.6606 | 2.7795 | 2.7769 | 28 | 11.0313 | 11.0313 | 0.066732 | 0.066732 | 2 | 1.9919 | 0.99594 | No
48191 | Bridgewater (North) | Short Rural | 91 | 6.24 | 5.41 | 3.3352 | 0.071003 | 0.11602 | 2 | 32.6479 | 32.6479 | 0.94869 | 0.94869 | 2 | 0.13856 | 0.13856 | 0.0036723 | 0.0036723 | 1 | 0.97362 | 0.97362 | No
49202 | Tods Corner-Liawenee | Short Rural | 723 | 110 | 0.63 | 0.70274 | 7.6313 | 0.017782 | 28 | 3425.7252 | 3035.1678 | 17.0546 | 14.7887 | 6 | 8.7714 | 8.7714 | 0.10073 | 0.10073 | 0 | 0 | 0 | Yes
49303 | Bronte Park | Short Rural | 267 | 97.94 | 0.71 | #N/A | 65.8691 | 0.21569 | 24 | 4686.0322 | 3115.6789 | 12.4103 | 10.3747 | 4 | 20.2483 | 20.2483 | 0.26728 | 0.26728 | 0 | 0 | 0 | Yes
49304 | Tarraleah Stn-Liapootah Dam | Short Rural | 267 | 2.85 | 0.25 | #N/A | 0.42458 | 1.6522 | 15 | 13280.9898 | 12635.9898 | 59 | 49 | 9 | 7914.0012 | 7914.0012 | 20 | 20 | 1 | 1 | 1 | Yes
49307 | Tarraleah | Short Rural | 12 | 6.94 | 0.35 | #N/A | 2.3935 | 0 | 16 | 3754.0291 | 3361.0289 | 15.0481 | 12.0481 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | Yes
49411 | Wayatinah | Short Rural | 62 | 10.8 | 0.35 | 0.56436 | 2.4617 | 1.222 | 5 | 628 | 457 | 5 | 4 | 1 | 319.9998 | 319.9998 | 1 | 1 | 5 | 5 | 5 | Yes
49412 | Wayatinah-Catagunya-Repulse-Cluny | Short Rural | 24 | 50.4 | 0.36 | #N/A | 0.74152 | 0.050209 | 8 | 766.2018 | 559.396 | 6.1675 | 4.9581 | 2 | 290.812 | 290.812 | 1.2348 | 1.2348 | 0 | 0 | 0 | Yes
49520 | Butlers Gorge Village-Derwent Pumps | Short Rural | 24 | 6.38 | 0.13 | #N/A | 0.0067991 | 0 | 1 | 0.75435 | 0.75435 | 0.0058027 | 0.0058027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
49621 | Lake St Clair-Derwent Bridge | Short Rural | 40 | 11.89 | 2.2 | #N/A | 5.0628 | 0.046391 | 14 | 2948.067 | 2888.0439 | 25.5646 | 21.2944 | 3 | 57.9358 | 57.9358 | 2.4241 | 2.4241 | 15 | 9.8393 | 9.8393 | Yes
49801 | Gordon Area-Strathgordon | Short Rural | 26 | 19.93 | 0 | 0.3273 | 3.1215 | 0.49874 | 8 | 1350.317 | 1350.317 | 6.0333 | 6.0333 | 2 | 225 | 225 | 2 | 2 | 0 | 0 | 0 | Yes
51001 | Poatina | Short Rural | 8 | 26.98 | 0.2 | 1.0004 | 0.91259 | 0 | 11 | 285.2365 | 240.1804 | 4.5906 | 4.2569 | 0 | 0 | 0 | 0 | 0 | 6 | 3.187 | 2.6559 | No
51002 | Bracknell-Liffey-Bishopsbourne-Oaks-Cluan | Long Rural | 812 | 202.49 | 0.34 | 3.0007 | 6.2584 | 0.54365 | 92 | 447.0356 | 182.1353 | 2.3826 | 1.1489 | 25 | 59.8512 | 59.8512 | 0.24385 | 0.24385 | 2 | 2.0161 | 2.0161 | No
51003 | Delmont-Cressy-Epping Forest-Blessington | Long Rural | 1309 | 383.13 | 4.02 | 7.5725 | 38.2844 | 6.7502 | 216 | 844.6796 | 801.8279 | 15.4382 | 15.2835 | 76 | 145.4463 | 145.4463 | 0.557 | 0.557 | 2 | 2.0361 | 2.0361 | Yes
53001 | Bell Bay Industrial | Short Rural | 965 | 27.02 | 7.19 | 6.0567 | 4.3367 | 1.3774 | 27 | 165.8874 | 155.4938 | 2.22 | 2.1792 | 2 | 59.3187 | 59.3187 | 0.17619 | 0.17619 | 0 | 0 | 0 | No
53002 | Long Reach | Short Rural | 1 | 7.42 | 1.98 | 0.33693 | 0 | 1.266 | 0 | 0 | 0 | 0 | 0 | 1 | 540 | 540 | 1 | 1 | 0 | 0 | 0 | No
53003 | George Town (North) | Short Rural | 2042 | 49.23 | 5.85 | 5.5754 | 13.9227 | 0.29103 | 76 | 436.4492 | 428.2288 | 2.067 | 2.0431 | 16 | 24.2467 | 24.2467 | 0.12763 | 0.12763 | 0 | 0 | 0 | No
53004 | Bell Bay Power Station Standby - Beaconsfield Gold | Short Rural | 616 | 66.13 | 13.69 | 3.8907 | 3.9358 | 0.61422 | 37 | 1654.0735 | 1652.4371 | 8.2276 | 8.2154 | 2 | 66.6451 | 66.6451 | 0.21325 | 0.21325 | 0 | 0 | 0 | Yes
53006 | East Tamar Hwy (Sth of GT Sub) | Short Rural | 2 | 0.48 | 0.25 | 0 | 0.044874 | 0 | 1 | 429 | 429 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
53007 | Bell Bay Power Station Main Feeder | Short Rural | 5 | 5.48 | 1.19 | 0.20055 | 0.48892 | 0 | 3 | 693.5045 | 555.7967 | 2.8484 | 1.9242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
53008 | Hillwood-The Glen-Pipers River-Weymouth | Long Rural | 1216 | 201.63 | 1.43 | 2.3264 | 25.6691 | 0.82046 | 118 | 1385.2745 | 1326.5198 | 7.2152 | 7.0599 | 13 | 31.6727 | 31.6727 | 0.11245 | 0.11245 | 3 | 3.0786 | 3.0786 | Yes
53009 | George Town (South)-Greens Beach-Beauty Point | Short Rural | 1596 | 101.4 | 3.29 | 7.2199 | 9.743 | 1.5772 | 73 | 260.5993 | 258.9747 | 3.0994 | 3.0895 | 17 | 57.426 | 44.6393 | 0.22015 | 0.15286 | 0 | 0 | 0 | No
53010 | Bell Bay | Urban | 57 | 7.59 | 2.43 | 4.0913 | 0.4781 | 1.9249e-09 | 7 | 317.0297 | 317.0297 | 3.0822 | 3.0822 | 1 | 47.6877 | 47.6877 | 0.13358 | 0.13358 | 1 | 0.99943 | 0.99943 | Yes
54003 | Ringarooma Rd-Scottsdale | Long Rural | 1960 | 284.02 | 1.68 | 4.5313 | 33.0171 | 1.1093 | 171 | 1474.4411 | 919.405 | 6.2099 | 5.0483 | 23 | 110.6309 | 110.6309 | 0.41842 | 0.41842 | 1 | 1.0139 | 1.0139 | Yes
54004 | Tongah | Short Rural | 147 | 30.29 | 0.22 | 0.82909 | 0.56823 | 0.27728 | 22 | 89.4409 | 89.4328 | 0.84949 | 0.84787 | 4 | 46.7365 | 46.7365 | 0.18074 | 0.18074 | 0 | 0 | 0 | No
54005 | Scottsdale-Springfield-Golconda-Lillydale | Long Rural | 1492 | 312.07 | 2.12 | 3.9176 | 29.6156 | 1.0969 | 176 | 996.9539 | 754.265 | 5.9735 | 5.6124 | 28 | 44.9653 | 44.9653 | 0.18005 | 0.18005 | 2 | 2.0005 | 2.0005 | No
54006 | Derby Terminal-Mt Horror-North Scottsdale | Short Rural | 165 | 72.22 | 6.7 | 0.73523 | 2.0645 | 0.019746 | 37 | 564.8848 | 517.9843 | 4.0111 | 3.8515 | 5 | 7.4894 | 7.4894 | 0.078053 | 0.078053 | 4 | 4.0402 | 4.0402 | No
54007 | North Scottsdale-Forester-Bridport-Waterhouse | Urban | 1045 | 10.39 | 1.87 | 4.1446 | 0.80711 | 1.2237 | 19 | 15.1176 | 10.6397 | 0.27945 | 0.23535 | 4 | 38.9773 | 38.9773 | 0.13091 | 0.13091 | 0 | 0 | 0 | No
55001 | Derby-Branxholm-Legerwood-Ringarooma | Short Rural | 847 | 152.45 | 0.34 | 4.0949 | 5.5446 | 1.3433 | 100 | 403.5334 | 397.7903 | 5.0521 | 5.0502 | 23 | 116.0848 | 116.0848 | 0.5522 | 0.5522 | 1 | 1.009 | 1.009 | No
55002 | Herrick-Gladstone-Weldborough | Short Rural | 618 | 174.89 | 13.65 | 1.1363 | 3.1118 | 0.12855 | 62 | 768.5472 | 768.4564 | 4.567 | 4.5629 | 19 | 67.5536 | 67.5536 | 0.20174 | 0.20174 | 4 | 4.3137 | 4.3137 | Yes
55003 | Winnaleah-Telita | Short Rural | 280 | 72.7 | 1.28 | 0.70695 | 4.1888 | 0.26145 | 57 | 993.7443 | 636.7346 | 5.9806 | 4.9796 | 29 | 57.0868 | 57.0868 | 0.41964 | 0.41964 | 19 | 19 | 15 | Yes
56001 | Royal George | Short Rural | 96 | 53.54 | 0.19 | 0.46528 | 0.18676 | 0.001 | 14 | 246.4031 | 246.4031 | 3.7534 | 3.7534 | 2 | 0.40193 | 0.40193 | 0.0066988 | 0.0066988 | 2 | 2.0105 | 2.0105 | No
56002 | Rossarden-Storeys Creek | Short Rural | 62 | 31.82 | 0.22 | 0 | 0.073147 | 0.12465 | 8 | 935.2103 | 806.2103 | 17.9601 | 16.9601 | 2 | 392.3481 | 392.3481 | 0.87737 | 0.87737 | 6 | 6 | 6 | Yes
56003 | Fingal-Mangana-Mathinna-Upper Esk | Short Rural | 486 | 163.16 | 0.37 | 2.7436 | 6.0939 | 4.4775 | 40 | 667.0854 | 606.621 | 5.8845 | 5.6153 | 17 | 521.3417 | 521.3417 | 1.5425 | 1.5425 | 1 | 1.0386 | 1.0386 | Yes
56004 | Conara-Campbell Town-Ross-Oatlands | Long Rural | 1758 | 502.89 | 3.28 | 6.4658 | 21.8478 | 4.4876 | 163 | 617.3081 | 518.4478 | 6.3866 | 6.0752 | 58 | 232.1463 | 232.1463 | 0.74434 | 0.74434 | 6 | 6.2339 | 6.2339 | No
57003 | Dianas Beach | Short Rural | 518 | 34.83 | 6.95 | 1.083 | 0.065985 | 1.6916 | 14 | 10.9035 | 10.9035 | 0.092111 | 0.092111 | 3 | 84.9029 | 84.9029 | 0.22627 | 0.22627 | 5 | 5.001 | 5.001 | No
57004 | Chain of Lagoons-Bicheno-Coles Bay | Long Rural | 1951 | 214.58 | 4.66 | 4.5325 | 2.1271 | 2.6745 | 63 | 51.3826 | 51.2391 | 1.526 | 1.5246 | 26 | 62.0531 | 62.0531 | 0.21099 | 0.21099 | 3 | 2.3142 | 2.3142 | No
57005 | St Marys-German Town-Mt Nicholas | Short Rural | 284 | 50.41 | 0.36 | 2.1259 | 0.79588 | 4.0441 | 12 | 96.814 | 96.8033 | 1.0479 | 1.0468 | 17 | 597.1068 | 597.1068 | 1.5681 | 1.5681 | 5 | 5.0017 | 5.0017 | Yes
57006 | Binalong Bay. and Weldborough | Long Rural | 3318 | 216.33 | 19.38 | 7.0996 | 31.4577 | 7.3546 | 126 | 1422.7032 | 784.1159 | 13.0651 | 11.1921 | 50 | 126.6759 | 126.6759 | 0.4314 | 0.4314 | 5 | 5.0295 | 4.0236 | Yes
61021 | Riverside-Newnham-Alanvale | Short Rural | 1438 | 105.51 | 5.3 | 5.9496 | 1.3998 | 1.5204 | 33 | 77.2191 | 77.203 | 0.69709 | 0.69664 | 18 | 69.1084 | 69.1084 | 0.28319 | 0.28319 | 6 | 6.0003 | 6.0003 | No
61022 | Prospect Vale | Short Rural | 7 | 6.56 | 0.91 | 0 | 0.048117 | 0 | 1 | 184.0002 | 184.0002 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
61023 | Glengarry-Birralee-Beaconsfield-Beauty Point | Long Rural | 1660 | 321.77 | 0.8 | 5.2172 | 8.6343 | 0.89864 | 171 | 662.7515 | 565.2336 | 8.5641 | 8.3445 | 58 | 52.2522 | 52.09 | 0.27639 | 0.27538 | 8 | 8.0377 | 8.0377 | No
61024 | City (North) | Urban | 322 | 0 | 6.9 | 7.9018 | 0.24676 | 0.41998 | 3 | 12.5636 | 1.0197 | 0.083515 | 0.03601 | 3 | 30.8789 | 30.8789 | 0.11876 | 0.11876 | 0 | 0 | 0 | No
61025 | Trevallyn-City (South) | Urban | 1707 | 12.75 | 4.78 | 5.7246 | 3.1109 | 1.4747 | 32 | 142.364 | 137.5053 | 4.1373 | 4.1203 | 4 | 30.8293 | 30.8293 | 0.17606 | 0.17606 | 12 | 12.0286 | 11.0262 | No
61026 | City (Central) | Urban | 184 | 1.45 | 5 | 4.8105 | 0.86796 | 2.7349 | 2 | 62.0042 | 61.9998 | 1.0004 | 1 | 3 | 29.7094 | 29.7094 | 0.10518 | 0.10518 | 0 | 0 | 0 | No
61027 | Trevallyn-West Launceston | Urban | 2269 | 12.43 | 3.89 | 7.3122 | 7.4673 | 0.4499 | 52 | 365.7682 | 364.8157 | 3.8252 | 3.8204 | 8 | 51.5309 | 51.5309 | 0.18464 | 0.18464 | 13 | 13 | 13 | Yes
61028 | Rosevears-Exeter-Deviot | Short Rural | 1554 | 69.53 | 2.77 | 4.9059 | 9.0686 | 9.4116 | 58 | 660.0476 | 486.9781 | 9.276 | 8.6105 | 26 | 197.663 | 197.663 | 1.1594 | 1.1594 | 5 | 5.0129 | 5.0129 | Yes
61029 | Alanvale-Rocherlea | Urban | 1947 | 13.53 | 12.63 | 11.099 | 2.058 | 2.0208 | 23 | 94.1363 | 94.0326 | 2.0437 | 2.0429 | 11 | 21.3289 | 21.3289 | 0.086223 | 0.086223 | 0 | 0 | 0 | No
61037 | West Riverside-Summerhill-Prospect | Short Rural | 821 | 22.93 | 1.78 | 3.2758 | 0.10086 | 0.25781 | 20 | 78.3191 | 75.9122 | 1.039 | 1.027 | 7 | 18.3906 | 18.3906 | 0.070125 | 0.070125 | 3 | 3.0449 | 3.0449 | No
61039 | City (Central / North) | Urban | 617 | 0 | 7.78 | 6.9793 | 1.1001 | 0 | 14 | 103.9352 | 51.9625 | 0.44955 | 0.37039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
61040 | City (Central)-Launceston General Hospital | Urban | 1137 | 0 | 8.82 | 8.0354 | 0.91751 | 0.0016452 | 23 | 42.2778 | 38.9178 | 0.19027 | 0.15221 | 1 | 0.72993 | 0.72993 | 0.048662 | 0.048662 | 0 | 0 | 0 | No
61041 | Trevallyn-West Launceston-Prospect | Urban | 1670 | 17.43 | 2.27 | 6.7438 | 0.64971 | 1.2945 | 26 | 56.8622 | 56.825 | 1.1411 | 1.1381 | 20 | 79.4893 | 79.4893 | 0.29669 | 0.29669 | 8 | 8 | 8 | No
61043 | Riverside-Legana-Dilston-Turners Marsh-Lilydale | Short Rural | 2787 | 104.54 | 8.16 | 9.8002 | 1.3026 | 1.8403 | 85 | 60.9427 | 48.2879 | 0.45203 | 0.40971 | 32 | 65.9608 | 65.9608 | 0.32472 | 0.32472 | 6 | 6.0652 | 6.0652 | No
62004 | Mowbray Heights | Urban | 354 | 2.98 | 2.33 | 3.91 | 1.2668 | 0.01126 | 3 | 47.3751 | 47.3751 | 2.0009 | 2.0009 | 2 | 0.10323 | 0.10323 | 0.0017204 | 0.0017204 | 0 | 0 | 0 | No
62005 | Alanvale-Newnham | Urban | 1118 | 6.14 | 3.19 | 5.3869 | 2.2717 | 1.7802 | 21 | 42.7182 | 42.6974 | 1.0906 | 1.0896 | 10 | 58.519 | 58.519 | 0.17071 | 0.17071 | 8 | 8.3014 | 8.3014 | No
62006 | Remount Rd-Ravenswood | Short Rural | 915 | 6.9 | 4.27 | 3.3312 | 0.20515 | 0.010838 | 34 | 7.4139 | 7.2803 | 0.082668 | 0.074198 | 13 | 16.6379 | 16.5597 | 0.14563 | 0.14432 | 3 | 2.9035 | 2.9035 | No
62008 | Invermay-Inveresk | Urban | 1766 | 8.66 | 3.52 | 7.1233 | 1.1655 | 0.84039 | 25 | 13.4492 | 7.4557 | 0.1207 | 0.082436 | 9 | 24.7558 | 24.7558 | 0.079319 | 0.079319 | 0 | 0 | 0 | No
62009 | East Launceston | Urban | 830 | 9.04 | 3.44 | 5.9095 | 3.878 | 1.4996 | 23 | 188.316 | 188.2527 | 3.6227 | 3.6187 | 9 | 19.983 | 19.983 | 0.073236 | 0.073236 | 10 | 10.002 | 10.002 | No
62010 | Mayfield | Short Rural | 1620 | 14.27 | 5.16 | 5.5473 | 0.39216 | 5.0093 | 21 | 3.6923 | 3.6253 | 0.048595 | 0.043765 | 11 | 82.6516 | 82.6516 | 0.23792 | 0.23792 | 13 | 13.5959 | 13.5959 | No
62013 | Invermay | Urban | 668 | 5.59 | 4.37 | 6.2857 | 0.26818 | 0.42288 | 14 | 19.8413 | 19.2869 | 1.0212 | 1.0203 | 7 | 52.6203 | 52.6203 | 0.20464 | 0.20464 | 0 | 0 | 0 | No
65060 | Western Junction-Breadalbane-Perth-Evandale | Urban | 242 | 0.59 | 3.29 | 9.1773 | 4.3188 | 0.19879 | 30 | 88.2935 | 87.9335 | 4.06 | 4.052 | 12 | 1.152 | 1.152 | 0.0192 | 0.0192 | 0 | 0 | 0 | No
65061 | Techno Park Drive Norwood | Short Rural | 864 | 5.56 | 3.8 | 0.20055 | 0.14102 | 0.0079484 | 8 | 24.6468 | 24.6468 | 0.99727 | 0.99727 | 1 | 0.54585 | 0.54585 | 0.021834 | 0.021834 | 0 | 0 | 0 | No
65062 | Kings Meadows-South Launceston | Urban | 1183 | 7.47 | 2.95 | 5.082 | 2.0581 | 0.7822 | 18 | 24.4656 | 24.3989 | 0.076612 | 0.075291 | 8 | 57.7842 | 57.7842 | 0.23727 | 0.23727 | 1 | 1.0206 | 0 | No
65063 | St Leonards South | Urban | 509 | 5.73 | 1.59 | 2.9682 | 0.31251 | 0.43013 | 11 | 31.1176 | 31.107 | 0.40293 | 0.4008 | 10 | 88.7222 | 88.7222 | 0.3992 | 0.3992 | 1 | 1.0334 | 1.0334 | No
65064 | Norwood-Newstead-East Launceston | Urban | 1000 | 5.99 | 2.11 | 3.249 | 1.3829 | 0.00269 | 17 | 46.8639 | 46.8639 | 0.15949 | 0.15949 | 1 | 0.076251 | 0.076251 | 0.0012708 | 0.0012708 | 0 | 0 | 0 | No
65065 | Franklin Village | Urban | 991 | 5.74 | 4.94 | 8.1746 | 1.2814 | 0.90163 | 6 | 133.7832 | 133.7832 | 2.023 | 2.023 | 3 | 19.8149 | 19.8149 | 0.093494 | 0.093494 | 3 | 3.0008 | 3.0008 | No
65066 | Norwood-Punch Bowl-South Launceston | Long Rural | 1319 | 250.85 | 3.15 | 10.513 | 14.4911 | 7.9541 | 98 | 729.4089 | 725.9134 | 10.6306 | 10.612 | 36 | 238.6366 | 238.6366 | 0.71189 | 0.71189 | 2 | 2.0598 | 2.0598 | Yes
65067 | Waverley-White Hills | Short Rural | 582 | 143.63 | 3.09 | 7.26 | 14.4684 | 1.2958 | 85 | 1187.4434 | 1172.4664 | 4.2924 | 4.0567 | 36 | 168.2111 | 168.2111 | 0.48735 | 0.48735 | 1 | 1.0057 | 1.0057 | Yes
66101 | Waverley-St Leonards | Short Rural | 654 | 13.42 | 1.65 | 1.5974 | 1.0348 | 0.74003 | 17 | 94.7599 | 94.087 | 2.5439 | 2.5385 | 3 | 56.7617 | 56.7617 | 1.0738 | 1.0738 | 0 | 0 | 0 | No
66102 | Norwood-Newstead-East Launceston-Launceston | Urban | 1835 | 7.49 | 2.37 | 3.8554 | 3.3598 | 2.3788 | 8 | 147.6264 | 147.6264 | 1.5687 | 1.5687 | 7 | 53.1879 | 53.1879 | 0.34843 | 0.34843 | 0 | 0 | 0 | No
66103 | Norwood-Newstead-East Lton-South Lton-Launceston | Urban | 1504 | 8.82 | 3.53 | 7.4004 | 0.5985 | 0.048898 | 24 | 9.8875 | 4.286 | 0.11524 | 0.060644 | 8 | 1.7416 | 1.7416 | 0.09007 | 0.09007 | 0 | 0 | 0 | No
66105 | Ravenswood-Waverley | Urban | 1256 | 7.63 | 3.49 | 3.4842 | 1.3894 | 0.86489 | 24 | 64.3205 | 64.3086 | 1.1127 | 1.1111 | 7 | 44.3807 | 44.3328 | 1.1081 | 1.1073 | 0 | 0 | 0 | No
66106 | 0 | Urban | 1590 | 9.62 | 2.63 | 11.5579 | 10.0024 | 0.13712 | 37 | 213.2841 | 139.6716 | 0.85618 | 0.81598 | 10 | 10.0553 | 10.0553 | 0.20094 | 0.20094 | 0 | 0 | 0 | No
66107 | High St East Launceston | Urban | 609 | 4.59 | 2.5 | 3.6142 | 5.8431 | 0.13856 | 15 | 257.5888 | 244.0888 | 1.1874 | 1.1415 | 2 | 8.935 | 8.935 | 0.094765 | 0.094765 | 0 | 0 | 0 | No
66109 | St Leonards | Short Rural | 559 | 5.97 | 0.23 | 1.4175 | 0.51298 | 0.68078 | 6 | 19.5116 | 19.5116 | 0.5479 | 0.5479 | 6 | 35.2848 | 35.2848 | 0.75479 | 0.75479 | 0 | 0 | 0 | No
67081 | Prospect | Urban | 921 | 4.15 | 17.99 | 7.2801 | 1.4878 | 0.29255 | 8 | 66.6396 | 66.6396 | 1.2105 | 1.2105 | 3 | 11.6775 | 11.6775 | 0.056157 | 0.056157 | 0 | 0 | 0 | No
67082 | Carrick-Westbury | Long Rural | 1779 | 219.54 | 7.85 | 4.3721 | 15.0548 | 2.1966 | 123 | 961.4745 | 196.8359 | 5.1096 | 2.5548 | 48 | 128.9476 | 128.9476 | 0.4398 | 0.4398 | 13 | 13.3857 | 10.2967 | No
67083 | Pateena-Longford | Short Rural | 448 | 35.4 | 0.56 | 4.7331 | 3.8817 | 1.5025 | 29 | 88.6561 | 88.365 | 1.6076 | 1.6064 | 10 | 28.2511 | 28.2511 | 0.20164 | 0.20164 | 5 | 5.0009 | 5.0009 | No
67084 | Hagley-Westbury Nth-Quamby Bend-Selbourne | Short Rural | 472 | 96.92 | 23.22 | 5.455 | 10.5583 | 3.9879 | 60 | 178.0463 | 172.1883 | 1.0385 | 1.0258 | 19 | 77.431 | 77.431 | 0.21401 | 0.21401 | 7 | 7.0847 | 7.0847 | No
67085 | Blackstone Heights | Short Rural | 636 | 17.3 | 1.67 | 4.6127 | 7.6701 | 1.5241 | 19 | 201.3839 | 201.3653 | 1.8277 | 1.8255 | 5 | 23.0525 | 23.0525 | 0.06587 | 0.06587 | 5 | 5.0179 | 5.0179 | No
67086 | Prospect Vale | Urban | 1766 | 7.46 | 8.96 | 9.5062 | 0.66385 | 2.7631 | 25 | 19.7021 | 19.6902 | 0.12849 | 0.1279 | 18 | 90.52 | 90.4485 | 0.25766 | 0.25647 | 0 | 0 | 0 | No
67087 | Future | Short Rural | 1479 | 44.33 | 8.41 | 4.8133 | 2.5137 | 0.91936 | 42 | 165.11 | 165.11 | 2.2377 | 2.2377 | 20 | 34.5776 | 34.5776 | 0.26118 | 0.26118 | 7 | 6.9952 | 6.9952 | No
67088 | Travellers Rest-Hadspen | Short Rural | 989 | 19.54 | 0.54 | 3.0083 | 1.0586 | 0.94925 | 22 | 57.3282 | 57.279 | 0.52229 | 0.52119 | 16 | 48.0961 | 48.0961 | 0.17842 | 0.17842 | 0 | 0 | 0 | No
67089 | Trevallyn Terminal | Short Rural | 1223 | 16.05 | 3.37 | 4.332 | 1.3724 | 0.051264 | 25 | 91.1069 | 89.7904 | 2.1068 | 2.0779 | 26 | 5.2382 | 5.1715 | 0.082211 | 0.0811 | 5 | 5 | 5 | No
67090 | Evandale-Perth | Short Rural | 1734 | 80.34 | 6.9 | 8.6238 | 10.7294 | 0.5219 | 60 | 156.7717 | 122.5811 | 1.3217 | 1.2887 | 19 | 23.8125 | 23.8125 | 0.068652 | 0.068652 | 4 | 3.9453 | 3.9453 | No
67091 | Young Town-Kings Meadows-South Launceston | Urban | 1458 | 12.13 | 5.96 | 12.4544 | 1.9332 | 0.040991 | 23 | 30.9976 | 30.9592 | 1.1083 | 1.1058 | 5 | 0.44496 | 0.44496 | 0.00309 | 0.00309 | 0 | 0 | 0 | No
80001 | Wesley Vale-Port Sorell | Short Rural | 3091 | 76.5 | 5.18 | 8.3258 | 14.0669 | 0.5469 | 95 | 369.4567 | 358.9906 | 5.066 | 5.0503 | 28 | 148.9061 | 148.9061 | 0.54515 | 0.54515 | 3 | 3.0918 | 3.0918 | No
80002 | Quioba-Spreyton | Short Rural | 654 | 24.08 | 0.92 | 7.049 | 38.2687 | 1.2231 | 31 | 187.9477 | 22.4134 | 0.40794 | 0.26803 | 9 | 8.1162 | 8.1162 | 0.055688 | 0.055688 | 3 | 3.0255 | 3.0255 | No
80003 | Quoiba-Spreyton | Urban | 400 | 12.19 | 1.07 | 6.7418 | 25.1432 | 1.2069 | 12 | 195.3757 | 4.7345 | 1.0665 | 0.062309 | 12 | 56.2447 | 56.2447 | 0.16097 | 0.16097 | 7 | 7.0254 | 6.0218 | No
80004 | Devonport CDB-Marine Board Area | Urban | 1137 | 5.05 | 4.6 | 5.9288 | 5.9302 | 0.064965 | 14 | 131.0965 | 123.913 | 1.2549 | 1.1782 | 3 | 1.3411 | 1.3411 | 0.015907 | 0.015907 | 4 | 4.0127 | 4.0127 | No
80005 | Devonport | Urban | 1657 | 9.94 | 3.93 | 5.1959 | 3.9719 | 0.63237 | 26 | 86.873 | 85.3909 | 1.1 | 1.083 | 5 | 20.1255 | 20.1255 | 0.066253 | 0.066253 | 4 | 4.0029 | 4.0029 | No
80006 | Devonport (West)-Don-Forth-Leith | Short Rural | 743 | 69.29 | 1.06 | 4.1547 | 18.5985 | 1.2192 | 65 | 723.2593 | 93.0245 | 1.754 | 0.74724 | 37 | 13.2808 | 13.2808 | 0.069449 | 0.069449 | 4 | 3.9993 | 3.9993 | No
80007 | East Devonport-Airport | Short Rural | 1838 | 21.38 | 3.6 | 6.8702 | 6.5058 | 0.60144 | 59 | 221.3261 | 220.9395 | 2.2704 | 2.2686 | 13 | 15.6764 | 15.6764 | 0.063038 | 0.063038 | 4 | 4.0546 | 4.0546 | No
80008 | Devonport (Central) | Urban | 1847 | 8.37 | 2.2 | 6.4915 | 0.44454 | 0.15473 | 36 | 3.9727 | 3.3209 | 0.063905 | 0.049055 | 4 | 3.1448 | 3.1448 | 0.014849 | 0.014849 | 5 | 5 | 5 | No
80009 | James St | Urban | 1555 | 5.48 | 4.44 | 6.9163 | 4.081 | 0.58615 | 26 | 84.3372 | 12.901 | 1.0723 | 0.069417 | 11 | 35.4833 | 35.4833 | 0.23295 | 0.23295 | 6 | 6 | 5 | No
80010 | Devonport West-Don Heads | Urban | 1957 | 13.37 | 3.75 | 7.4249 | 14.7279 | 0.44544 | 37 | 264.287 | 262.7126 | 1.8013 | 1.7216 | 11 | 90.9073 | 90.9073 | 0.4523 | 0.4523 | 13 | 13.0067 | 8.0041 | Yes
80011 | Latrobe-Wesley Vale | Short Rural | 1360 | 53.8 | 3.91 | 5.2541 | 5.659 | 0.88775 | 61 | 97.9672 | 51.4333 | 0.73437 | 0.63818 | 21 | 31.9268 | 31.9268 | 0.14673 | 0.14673 | 7 | 7.0046 | 7.0046 | No
82001 | Kindred-Forth-Turners Beach | Short Rural | 593 | 95.12 | 0.19 | 4.5084 | 13.656 | 0.11643 | 77 | 889.6939 | 154.4214 | 2.1872 | 0.97873 | 48 | 3.9615 | 3.9615 | 0.02622 | 0.02622 | 4 | 4.0384 | 4.0384 | No
82002 | Ulverstone-Penguin | Short Rural | 2160 | 22.06 | 2.89 | 6.4779 | 24.0657 | 0.33378 | 47 | 776.6276 | 156.2085 | 3.1198 | 2.1183 | 8 | 11.9793 | 11.9793 | 0.11097 | 0.11097 | 4 | 4.0145 | 4.0145 | No
82003 | Ulverstone (West)-Penguin | Short Rural | 2191 | 64.44 | 1.99 | 6.5661 | 15.8608 | 4.1107 | 83 | 520.9978 | 438.4142 | 5.4382 | 5.2889 | 28 | 102.0989 | 102.0989 | 0.33922 | 0.33922 | 1 | 1.0084 | 1.0084 | No
82004 | Gawler-Preston-Gunns Plains-Nietta | Short Rural | 842 | 185.26 | 0.21 | 2.2983 | 18.0006 | 1.1632 | 112 | 1726.308 | 513.9316 | 5.3333 | 4.0518 | 26 | 147.6887 | 147.6887 | 0.55218 | 0.55218 | 3 | 3.1406 | 2.0938 | Yes
82005 | Ulverstone (East) | Urban | 1826 | 9.99 | 3.05 | 6.4217 | 11.7574 | 0.39294 | 42 | 265.2109 | 65.4864 | 2.1366 | 1.1297 | 9 | 9.1628 | 9.1628 | 0.05976 | 0.05976 | 1 | 1 | 0 | No
82006 | Simplot | Urban | 205 | 2.31 | 1.11 | 8.5115 | 0.00022086 | 0 | 4 | 0.096658 | 0.081068 | 0.003118 | 0.001559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
82007 | Gawler-Upper Castra | Short Rural | 541 | 102.31 | 1.84 | 2.186 | 6.5915 | 0.095575 | 64 | 832.8068 | 327.3743 | 2.6895 | 1.1638 | 11 | 11.39 | 11.39 | 0.050486 | 0.050486 | 7 | 7.0205 | 7.0205 | No
82008 | Turners Beach | Short Rural | 1738 | 21.39 | 6.54 | 6.0166 | 19.8034 | 0.81915 | 40 | 489.0487 | 104.0076 | 4.399 | 3.4076 | 7 | 56.7704 | 56.7704 | 0.26765 | 0.26765 | 7 | 7.0669 | 7.0669 | No
85001 | Beulah-Sheffield-Nook-Wilmot-Cradle Mountain | Long Rural | 2467 | 396.2 | 13.1 | 6.1048 | 40.3168 | 0.64565 | 208 | 1286.9607 | 664.7261 | 5.0169 | 3.924 | 44 | 20.0248 | 20.0248 | 0.089547 | 0.089547 | 2 | 2.0057 | 1.0029 | No
85002 | Elizabeth Town-Deloraine-Meander-Exton-Westbury | Long Rural | 1848 | 334.2 | 0.47 | 6.1169 | 24.6537 | 4.7391 | 210 | 582.452 | 374.757 | 5.2609 | 4.3472 | 41 | 92.5042 | 92.5042 | 0.40102 | 0.40102 | 3 | 3.0369 | 2.0246 | No
85003 | Big Bend-Tarleton-Melrose-Barrington | Short Rural | 1351 | 173.53 | 0.55 | 4.2878 | 19.9685 | 1.3106 | 99 | 1064.2287 | 304.3145 | 4.1525 | 1.8338 | 34 | 64.8285 | 64.8285 | 1.0099 | 1.0099 | 3 | 3.0291 | 2.0194 | No
85004 | Sassafras-Moriarty-Thirlstane-Port Sorell (South) | Long Rural | 1171 | 213.78 | 0.27 | 6.157 | 15.8276 | 0.10752 | 203 | 532.8137 | 385.3608 | 3.7137 | 3.5148 | 12 | 3.6132 | 3.6132 | 0.040712 | 0.040712 | 2 | 2.01 | 2.01 | No
85006 | Needles-Deloraine-Mole Creek-Western Creek | Long Rural | 2250 | 401.42 | 3.18 | 7.3443 | 30.5959 | 2.0371 | 222 | 846.9179 | 499.0653 | 6.8759 | 5.4937 | 32 | 39.7367 | 39.7367 | 0.13809 | 0.13809 | 5 | 5.0429 | 5.0429 | No
85008 | Latrobe | Short Rural | 1391 | 42.14 | 1.53 | 5.1462 | 7.7914 | 0.40021 | 41 | 286.9319 | 77.3628 | 1.9968 | 0.9486 | 10 | 21.4718 | 21.4718 | 0.088008 | 0.088008 | 1 | 1.0229 | 0 | No
89001 | Rowallan-Lemonthyme-Parsons Falls | Short Rural | 4 | 25.18 | 0.13 | #N/A | 0.25701 | 0 | 2 | 343.4651 | 343.4651 | 0.34884 | 0.34884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
90020 | Burnie CBD (East)-Marine Board | Urban | 108 | 0.92 | 3.43 | 1.9857 | 0.022443 | 0 | 1 | 4.9863 | 4.9863 | 0.027397 | 0.027397 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | No
90023 | Burnie CBD (West) | Urban | 470 | 1.74 | 1.67 | 4.3997 | 0.029907 | 1.6122 | 8 | 0.4685 | 0.26562 | 0.008366 | 0.0020915 | 2 | 27.6078 | 27.6078 | 0.078431 | 0.078431 | 1 | 1 | 1 | No
90024 | Burnie CBD (Central / West) | Urban | 199 | 0 | 3.12 | 3.1286 | 0.1459 | 0.26391 | 2 | 8.3932 | 8.3932 | 0.091325 | 0.091325 | 1 | 14.006 | 14.006 | 0.090361 | 0.090361 | 0 | 0 | 0 | No
91001 | Ridgley-Yolla-Calder-Hampshire-Preolenna | Short Rural | 809 | 96.66 | 0.42 | 4.6709 | 4.8446 | 1.2876 | 46 | 284.0845 | 244.5581 | 3.3418 | 3.0004 | 17 | 34.1047 | 34.1047 | 0.11176 | 0.11176 | 0 | 0 | 0 | No
91002 | Natone-Cuprona | Short Rural | 815 | 142.09 | 0.69 | 3.1018 | 4.2681 | 1.7323 | 75 | 286.7035 | 175.087 | 1.275 | 1.1892 | 47 | 112.5022 | 112.5022 | 0.39532 | 0.39532 | 3 | 2.9988 | 2.9988 | No
91003 | Upper Burnie-Wivenhoe | Urban | 1062 | 15.67 | 2.89 | 6.5581 | 16.8395 | 5.1384 | 19 | 483.5691 | 415.8906 | 3.8879 | 3.0698 | 16 | 385.7764 | 385.7764 | 0.44178 | 0.44178 | 3 | 3.1267 | 3.1267 | Yes
91004 | Wynyard (West)-Moorleah | Short Rural | 1754 | 168.85 | 1.28 | 7.4141 | 25.9205 | 7.7099 | 118 | 662.4362 | 556.6335 | 5.0215 | 4.6412 | 45 | 112.9314 | 110.0831 | 0.36295 | 0.355 | 5 | 5.0376 | 5.0376 | Yes
91005 | Somerset (South)-Wynyard (East)-Table Cape | Short Rural | 1321 | 41.66 | 3.83 | 6.7847 | 0.66253 | 2.0475 | 48 | 155.3351 | 154.8624 | 0.78734 | 0.78381 | 28 | 20.2032 | 20.2032 | 0.097797 | 0.097797 | 2 | 2.0055 | 2.0055 | No
91006 | Camdale-Somerset (North)-Wynyard (East) | Short Rural | 1933 | 33.85 | 4.99 | 8.7638 | 8.708 | 0.96706 | 55 | 287.589 | 286.3042 | 2.4874 | 2.4843 | 16 | 48.2105 | 48.2105 | 0.17403 | 0.17403 | 2 | 2 | 2 | No
91007 | Burnie (West)-Cooee | Urban | 1310 | 7.06 | 0.62 | 4.1045 | 0.89723 | 0.0073944 | 21 | 54.7873 | 53.8821 | 0.36249 | 0.35388 | 2 | 0.66641 | 0.66641 | 0.049654 | 0.049654 | 3 | 3 | 3 | No
91008 | Burnie (East) | Urban | 3088 | 17.35 | 2.92 | 8.5881 | 1.958 | 1.5391 | 52 | 29.0513 | 28.0332 | 0.29698 | 0.27987 | 9 | 29.3763 | 29.3763 | 0.11892 | 0.11892 | 3 | 4.0705 | 2.7137 | No
91009 | Wynyard | Short Rural | 2026 | 28.47 | 7.19 | 6.0916 | 2.2225 | 7.8954 | 32 | 55.1932 | 55.0839 | 1.1423 | 1.1379 | 27 | 110.4926 | 110.4926 | 0.40649 | 0.40649 | 2 | 2.0471 | 2.0471 | No
91010 | North West Private Hospital | Urban | 1341 | 10.3 | 5.43 | 9.8283 | 2.4893 | 0.06929 | 16 | 86.5844 | 86.5787 | 1.0416 | 1.0408 | 3 | 0.25922 | 0.25922 | 0.0104 | 0.0104 | 1 | 0.68445 | 0.68445 | No
91011 | Penguin-Riana | Short Rural | 1275 | 146.21 | 2.62 | 7.5035 | 3.407 | 2.3011 | 80 | 219.1497 | 196.9787 | 2.2379 | 2.2028 | 36 | 131.3541 | 131.3541 | 0.41283 | 0.41283 | 4 | 4.0575 | 1.0144 | No
91012 | Mooreville | Long Rural | 1159 | 263.9 | 7.13 | 3.8462 | 5.4312 | 1.2813 | 78 | 352.0405 | 144.7999 | 2.9756 | 1.8492 | 33 | 63.4488 | 63.4488 | 0.21105 | 0.21105 | 1 | 1.0051 | 1.0051 | No
93001 | Irishtown-Forest-Stanley-Mengha-Trowutta | Short Rural | 853 | 191.59 | 0.48 | 5.5601 | 14.2552 | 2.7224 | 93 | 310.8819 | 235.2333 | 2.8467 | 2.5449 | 21 | 78.6961 | 78.6961 | 0.28971 | 0.28971 | 0 | 0 | 0 | No
93002 | Marrawah-Mella | Short Rural | 942 | 180.23 | 3.67 | 7.2949 | 33.5861 | 2.3899 | 107 | 905.8762 | 835.9282 | 8.2107 | 7.2931 | 13 | 30.2561 | 30.2561 | 0.17087 | 0.17087 | 2 | 2.0063 | 2.0063 | Yes
93003 | Edith Creek-Trowutta-Togari-Marrawah-Woolnorth | Short Rural | 673 | 53.14 | 1.34 | 9.2106 | 3.7096 | 1.3044 | 31 | 96.3454 | 93.642 | 0.39553 | 0.3775 | 9 | 28.9189 | 28.9189 | 0.15545 | 0.15545 | 0 | 0 | 0 | No
93004 | Smithton-McCains | Urban | 293 | 2.4 | 0.29 | 4.0873 | 3.1053 | 0.020736 | 14 | 9.2328 | 9.2328 | 0.080467 | 0.080467 | 2 | 0.065911 | 0.065911 | 0.0010985 | 0.0010985 | 0 | 0 | 0 | No
93005 | Montague-Cape Grim | Short Rural | 1303 | 131.01 | 2.44 | 4.946 | 3.3006 | 0.20346 | 79 | 175.5674 | 148.9442 | 1.5593 | 1.4782 | 7 | 3.1024 | 3.1024 | 0.018334 | 0.018334 | 3 | 2.9994 | 2.9994 | No
94001 | Mawbanna-Stanley | Short Rural | 943 | 139.89 | 0.22 | 4.6765 | 4.9872 | 0.90944 | 75 | 494.3125 | 493.6516 | 6.9467 | 6.9196 | 32 | 33.7114 | 33.7114 | 0.15335 | 0.15335 | 3 | 2.999 | 2.999 | No
94002 | Montumana-Sisters Creek-Myalla | Short Rural | 1205 | 160.15 | 0.41 | 4.5084 | 7.8868 | 0.57884 | 71 | 636.4314 | 627.0703 | 5.1217 | 5.0657 | 34 | 33.0347 | 33.0347 | 0.1581 | 0.1581 | 12 | 12.1839 | 12.1839 | Yes
95001 | Savage River-Luina-Waratah | Short Rural | 252 | 60.32 | 0.24 | 1.2041 | 1.9191 | 0.041112 | 13 | 173.853 | 95.2622 | 2.4563 | 2.0047 | 4 | 3.7321 | 3.7321 | 1.6367 | 1.6367 | 1 | 1 | 1 | No
96101 | Que River Mine-Hellyer Mine | Short Rural | 252 | 10.68 | 0 | #N/A | 0.014644 | 0 | 1 | 139.9998 | 139.9998 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
96202 | Henty Gold | Urban | 1 | 10.68 | 0.4 | 5.0592 | 12.1852 | 0 | 3 | 445 | 201 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
97001 | Rosebery Village (South)-Williamsford-Mt Read | Short Rural | 438 | 19.12 | 2.3 | 1.2033 | 4.9271 | 0 | 14 | 870.1182 | 847.8439 | 3.3653 | 2.3579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
97002 | Rosebery Village (North) | Short Rural | 503 | 59.44 | 0.05 | 1.3938 | 2.106 | 0.38262 | 37 | 254.8695 | 219.5169 | 2.1506 | 1.0984 | 3 | 20.3509 | 20.3509 | 0.0705 | 0.0705 | 0 | 0 | 0 | No
97013 | Zeehan Zone Substation | Short Rural | 6 | 36.96 | 0 | 2.0641 | 38.7961 | 5.0157 | 6 | 2744.5717 | 2716.5717 | 5.1429 | 4.1429 | 2 | 359 | 359 | 2 | 2 | 4 | 4 | 3 | Yes
97014 | Renison Mine | Urban | 1 | 9.55 | 0 | 14.354 | 18.4605 | 0 | 2 | 190.0002 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
98001 | Strahan | Short Rural | 655 | 63.52 | 2.14 | 1.9012 | 19.8548 | 0.1619 | 40 | 1670.0182 | 433.7673 | 10.1931 | 4.4154 | 5 | 39.577 | 39.577 | 0.16067 | 0.16067 | 6 | 6.182 | 5.1517 | No
98002 | Queenstown (West)-John Butters Power Station | Short Rural | 845 | 17.07 | 1.78 | 3.0147 | 0.8278 | 0.0037234 | 30 | 139.4971 | 24.0352 | 7.034 | 1.0786 | 2 | 0.11697 | 0.11697 | 0.0019496 | 0.0019496 | 2 | 2 | 2 | No
98003 | Queenstown (East)-Gormanston-Lake Burbury | Short Rural | 563 | 10.95 | 0.41 | 1.6245 | 2.2073 | 0.84357 | 19 | 210.2607 | 114.6149 | 6.9207 | 0.27733 | 8 | 54.0494 | 54.0494 | 0.37362 | 0.37362 | 0 | 0 | 0 | No
99981 | Zeehan | Short Rural | 653 | 67.9 | 0.24 | 1.6846 | 37.8539 | 5.5702 | 31 | 3389.4744 | 3355.677 | 6.5964 | 5.5564 | 7 | 402.1865 | 402.1865 | 2.2358 | 2.2358 | 0 | 0 | 0 | Yes
99982 | Allegiance | Urban | 653 | 2.42 | 0.13 | 0.84232 | 37.8539 | 5.5702 | 5 | 3.7398 | 3.7003 | 0.0070562 | 0.0056449 | 2 | 0.50663 | 0.50663 | 0.0028225 | 0.0028225 | 0 | 0 | 0 | No
99983 | Zeehan Zinc | Short Rural | 3 | 4.24 | 0.22 | 0 | 0.2773 | 0.037552 | 5 | 2651.0044 | 2623.0044 | 5 | 4 | 2 | 359 | 359 | 2 | 2 | 0 | 0 | 0 | Yes
FUTURE |  | Short Rural |  |  |  |  | 0 | 0.043933 | 10 | 277.9886 | 257.8769 | 1.2291 | 1.1173 | 4 | 150.2793 | 150.2793 | 0.44693 | 0.44693 | 0 | 0 | 0 | No
Note
(1) The sum of the number of customers for each feeder category may not equal the average customer numbers shown on sheet 1a, due to rounding.
Contents
Contents

## 3b. Planned outages
TasNetworks
Reliability - planned outages
2013-14
The information in templates 3a and 3b is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
SAIDI | 17.9914 | 14.1596 | 33.4367 | 59.2101 | 92.936 | 51.9995
SAIFI | 0.11913 | 0.072448 | 0.14377 | 0.24106 | 0.35547 | 0.21182
MAIFI | 0 | 0 | 0 | 0 | 0 | 0
Contents