## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | TasNetworks
DNSP - Australian company number: |  | 24 167 357 299
Reporting year: |  | 2015-16
Business address | Address |  | 1-7 Maria Street
| Suburb |  | Lenah Valley
|  | State | Tas | Postcode | 7008
Postal address | Address |  | GPO Box 606
| Suburb |  | Moonah
|  | State | Tas | Postcode | 7009
Contact name/s | Kirstan Wilding
Contact phone/s | 03 6271 6696
Contact email address/s | revenue.reset@tasnetworks.com.au

## Contents
Electricity Distribution Network Service Provider Annual Reporting Template
Table of contents
Cover sheet
1. Service Target Performance Incentive Scheme | 2. Customer service
1a. STPIS - Reliability | 3. Network performance
1b. STPIS - Customer service | 3a. Feeder reliability
1c. STPIS - Daily performance | 3b. Planned outages
1d. STPIS - GSL

## 1a. STPIS Reliability
TasNetworks
STPIS Data Reporting
2015-16
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI (System Average Interruption Duration Index)
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Total | 19.2733 | 20.8995 | 118.7628 | 515.9085 | 733.8158 | 344.7542
Total (after removing excluded events and MED) | 14.57 | 11.3697 | 78.0602 | 254.2604 | 370.5336 | 181.7655
Table 2: SAIFI (System Average Interruption Frequency Index)
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Total | 0.19369 | 0.35513 | 1.2082 | 3.2714 | 4.0022 | 2.2547
Total (after removing excluded events and MED) | 0.16332 | 0.19209 | 0.97427 | 2.614 | 3.2201 | 1.8085
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Total | 0.61883 | 1.0918 | 2.6513 | 6.5969 | 8.8942 | 4.8757
Total (after removing excluded events and MED) | 0.61883 | 1.0493 | 2.0996 | 4.9736 | 6.9652 | 3.8019
Table 4: Customer numbers
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Customer numbers at the start of period | 1884 | 4690 | 190711 | 43077 | 43901 | 284263
Customer numbers at the end of period | 1869 | 4700 | 192176 | 43495 | 44146 | 286386
Average customer numbers | 1876.5 | 4695 | 191443.5 | 43286 | 44023.5 | 285324.5
Table 5: Average customer numbers (kVA)
Supply reliablity category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
Customer numbers at the start of period | 123030 | 135050 | 1874204 | 775372 | 954391 | 3862047
Customer numbers at the end of period | 125020 | 135800 | 1891592 | 787746 | 978348 | 3918506
Average customer numbers | 124025 | 135425 | 1882898 | 781559 | 966369.5 | 3890276.5
Contents
Contents

## 1b. STPIS Customer Service
TasNetworks
STPIS Data Reporting - AER Definitions
2015-16
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
| Total - after removing excluded events | Total
Number of calls | 44455 | 55628
Number of calls answered in 30 seconds | 32314 | 34895
Percentage of calls answered within 30 seconds | 72.69% | 62.73%
Table 2: New connections
Note: This is for newly energised properties only
Total
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date | #DIV/0!
Table 3: Streetlight repair
Total
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business
Faulty streetlights not repaired within 5 business days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 business days of fault report or agreed date | #DIV/0!
Contents

## 1c. STPIS Daily Performance
TasNetworks |  |  | 2013-07-01 | 2013-07-01
STPIS Data Reporting |  |  | 2014-07-01 | 2014-07-01
2015-16 |  |  | 2015-07-01 | 2015-07-01
Daily Performance Data |  |  | 2016-07-01 | 2016-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1 Daily Performance Data (unplanned)
*Customer service information must be reported as per the definitions in the STPIS, that is excluding: • calls to payment lines and automated interactive services • calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator (where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned).
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | Critical infrastructure SAIDI all events total | Critical infrastructure SAIDI all events after removing excluded events | High density commercial SAIDI all events total | High density commercial SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | HIgh density rural SAIDI all events total | High density rural SAIDI all events after removing excluded events | Low density rural SAIDI all events total | Low density rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | Critical infrastructure SAIFI all events total | Critical infrastructure SAIFI all events after removing excluded events | High density commercial SAIFI all events total | High density commercial SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | HIgh density rural SAIFI all events total | High density rural SAIFI all events after removing excluded events | Low density rural SAIFI all events total | Low density rural SAIFI all events after removing excluded events | Network MAIFI all events total | Network MAIFI all events after removing excluded events | Critical infrastructure MAIFI all events total | Critical infrastructure MAIFI all events after removing excluded events | High density commercial MAIFI all events total | High density commercial MAIFI all events after removing excluded events | Urban MAIFI all events total | Urban MAIFI all events after removing excluded events | HIgh density rural MAIFI all events total | High density rural MAIFI all events after removing excluded events | Low density rural MAIFI all events total | Low density rural MAIFI all events after removing excluded events | Total number of calls (after removing excluded events) | Total number of calls answered in 30 seconds (after removing excluded events) | MED - YES/NO
2015-07-01 | 1.7819 | 1.0374 | 0 | 0 | 0 | 0 | 0.044284 | 0.044241 | 2.9653 | 0.61578 | 4.689 | 3.5921 | 0.0095973 | 0.0057556 | 0 | 0 | 0 | 0 | 0.00030485 | 0.00029635 | 0.016937 | 0.0045576 | 0.024344 | 0.018907 | 0.0064137 | 0.0064137 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003145 | 0.003145 | 0.023276 | 0.023276 | 164 | 116 | NO
2015-07-02 | 0.58801 | 0.58795 | 0 | 0 | 0 | 0 | 0.017794 | 0.017666 | 1.2796 | 1.2796 | 1.2976 | 1.2976 | 0.0060212 | 0.006015 | 0 | 0 | 0 | 0 | 0.00028254 | 0.0002698 | 0.013651 | 0.013651 | 0.012648 | 0.012648 | 0.025248 | 0.025248 | 0 | 0 | 0 | 0 | 0.0046699 | 0.0046699 | 0.065119 | 0.065119 | 0.039876 | 0.039876 | 156 | 116 | NO
2015-07-03 | 0.14448 | 0.12826 | 0.94336 | 0.94336 | 0.07938 | 0 | 0.042679 | 0.019005 | 0.29855 | 0.2948 | 0.12481 | 0.11979 | 0.016685 | 0.00097114 | 0.0060472 | 0.0060472 | 0.07938 | 0 | 0.022941 | 0.00027776 | 0.0058345 | 0.002083 | 0.0058508 | 0.00090752 | 0.0047179 | 0.0047179 | 0 | 0 | 0 | 0 | 0.0037777 | 0.0037777 | 0.0050284 | 0.0050284 | 0.0075654 | 0.0075654 | 128 | 73 | NO
2015-07-04 | 0.0967 | 0.09462 | 0 | 0 | 0 | 0 | 0.0014276 | 0.0012194 | 0.065222 | 0.05537 | 0.33375 | 0.33375 | 0.00082385 | 0.00080894 | 0 | 0 | 0 | 0 | 2.5493e-05 | 2.1244e-05 | 0.00065638 | 0.00059241 | 0.002736 | 0.002736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 36 | NO
2015-07-05 | 0.10123 | 0.10123 | 0 | 0 | 0 | 0 | 0.0083085 | 0.0083085 | 0.00097241 | 0.00097241 | 0.39054 | 0.39054 | 0.00071949 | 0.00071949 | 0 | 0 | 0 | 0 | 0.00027405 | 0.00027405 | 1.0236e-05 | 1.0236e-05 | 0.0023542 | 0.0023542 | 0.015399 | 0.015399 | 0 | 0 | 0 | 0 | 0.0035647 | 0.0035647 | 0.030732 | 0.030732 | 0.03019 | 0.03019 | 50 | 44 | NO
2015-07-06 | 1.1415 | 1.1094 | 0 | 0 | 0.0017131 | 0.0017131 | 0.4808 | 0.48035 | 0.48092 | 0.47843 | 3.2694 | 3.1429 | 0.014557 | 0.014461 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.0044123 | 0.0043996 | 0.018301 | 0.01829 | 0.035195 | 0.034844 | 0.0014865 | 0.0014865 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073993 | 0.0073993 | 0 | 0 | 175 | 130 | NO
2015-07-07 | 0.43621 | 0.43611 | 0 | 0 | 0.0058483 | 0.0058483 | 0.19409 | 0.19398 | 0.18558 | 0.18558 | 1.2269 | 1.2268 | 0.011664 | 0.011658 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.0041617 | 0.0041574 | 0.00336 | 0.00336 | 0.036121 | 0.036104 | 0.0079627 | 0.0079627 | 0 | 0 | 0 | 0 | 0.0085347 | 0.0085347 | 0.019073 | 0.019073 | 0 | 0 | 164 | 85 | NO
2015-07-08 | 0.17756 | 0.172 | 0 | 0 | 0 | 0 | 0.010499 | 0.010435 | 0.044809 | 0.044809 | 0.6581 | 0.63583 | 0.0011375 | 0.0011313 | 0 | 0 | 0 | 0 | 0.00014871 | 0.00014021 | 0.00024566 | 0.00024566 | 0.0040906 | 0.0040823 | 0.0086351 | 0.0086351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018171 | 0.018171 | 0.020066 | 0.020066 | 144 | 89 | NO
2015-07-09 | 0.068055 | 0.068014 | 0 | 0 | 0 | 0 | 0.04983 | 0.049809 | 0.18918 | 0.18912 | 0.023878 | 0.023795 | 0.0013523 | 0.0013462 | 0 | 0 | 0 | 0 | 0.00086728 | 0.00086303 | 0.003841 | 0.0038308 | 0.00064779 | 0.00063951 | 0.0017852 | 0.0017852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0071867 | 0.0071867 | 107 | 75 | NO
2015-07-10 | 0.0093528 | 0.0093322 | 0 | 0 | 0 | 0 | 0.0029593 | 0.0029593 | 0.0033472 | 0.0032448 | 0.029178 | 0.029178 | 0.00010256 | 0.00010051 | 0 | 0 | 0 | 0 | 5.6296e-05 | 5.6296e-05 | 8.4447e-05 | 7.4211e-05 | 0.0002349 | 0.0002349 | 0.0016256 | 0.0016256 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078958 | 0.0078958 | 0.00015832 | 0.00015832 | 86 | 76 | NO
2015-07-11 | 0.027789 | 0.027653 | 0 | 0 | 0 | 0 | 0.029387 | 0.029387 | 0.063483 | 0.062808 | 0.0032679 | 0.0032679 | 0.00020487 | 0.00020281 | 0 | 0 | 0 | 0 | 0.00018482 | 0.00018482 | 0.00053227 | 0.00052203 | 3.4148e-05 | 3.4148e-05 | 0.0031335 | 0.0031335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002431 | 0.0002431 | 0.012418 | 0.012418 | 68 | 60 | NO
2015-07-12 | 0.070474 | 0.070317 | 0 | 0 | 0 | 0 | 0.025456 | 0.025134 | 0.0046574 | 0.0046574 | 0.23034 | 0.23034 | 0.0003609 | 0.00035679 | 0 | 0 | 0 | 0 | 0.00027829 | 0.0002698 | 4.2223e-05 | 4.2223e-05 | 0.00087648 | 0.00087648 | 0.011851 | 0.011851 | 0 | 0 | 0 | 0 | 0.0025131 | 0.0025131 | 0.0085764 | 0.0085764 | 0.035876 | 0.035876 | 49 | 46 | NO
2015-07-13 | 0.32696 | 0.32679 | 0 | 0 | 0 | 0 | 0.61441 | 0.61441 | 0.045696 | 0.045696 | 0.082162 | 0.081475 | 0.0050382 | 0.0050361 | 0 | 0 | 0 | 0 | 0.0089692 | 0.0089692 | 0.00055146 | 0.00055146 | 0.0023604 | 0.0023521 | 0.0054189 | 0.0054189 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039895 | 0.0039895 | 0.018588 | 0.018588 | 197 | 71 | NO
2015-07-14 | 0.04617 | 0.045498 | 0 | 0 | 0.004017 | 0 | 0.029497 | 0.029004 | 0.14899 | 0.14753 | 0.0073346 | 0.0073346 | 0.00036707 | 0.00035679 | 0 | 0 | 5.9073e-05 | 0 | 0.00031653 | 0.00030804 | 0.00091612 | 0.00089565 | 0.00011176 | 0.00011176 | 0.0013372 | 0.0013372 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0028712 | 0.0028712 | 0.0030609 | 0.0030609 | 110 | 60 | NO
2015-07-15 | 0.05662 | 0.056384 | 0 | 0 | 0.0028946 | 0.0028946 | 0.0069935 | 0.0065049 | 0.15363 | 0.15363 | 0.089652 | 0.089652 | 0.0003136 | 0.00030743 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.00013171 | 0.00011897 | 0.00063079 | 0.00063079 | 0.00048739 | 0.00048739 | 0.0029013 | 0.0029013 | 0 | 0 | 0 | 0 | 0.0025131 | 0.0025131 | 0.0048045 | 0.0048045 | 0.0028974 | 0.0028974 | 131 | 57 | NO
2015-07-16 | 0.13702 | 0.13674 | 0 | 0 | 0 | 0 | 0.27464 | 0.27407 | 0.014765 | 0.014765 | 0.0045469 | 0.0045055 | 0.00042131 | 0.00041514 | 0 | 0 | 0 | 0 | 0.00081364 | 0.00080514 | 7.4211e-05 | 7.4211e-05 | 5.0705e-05 | 4.2427e-05 | 0.0011318 | 0.0011318 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043951 | 0.0043951 | 0.0010017 | 0.0010017 | 115 | 82 | NO
2015-07-17 | 0.078417 | 0.078214 | 0 | 0 | 0 | 0 | 0.027392 | 0.026971 | 0 | 0 | 0.26231 | 0.26231 | 0.0018783 | 0.0018721 | 0 | 0 | 0 | 0 | 0.00049286 | 0.00048011 | 0 | 0 | 0.006601 | 0.006601 | 0.0049487 | 0.0049487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019922 | 0.019922 | 125 | 76 | NO
2015-07-18 | 0.089123 | 0.088156 | 0 | 0 | 0 | 0 | 0.0048351 | 0.0028637 | 0.0049644 | 0.0049644 | 0.34534 | 0.34529 | 0.0014752 | 0.0014685 | 0 | 0 | 0 | 0 | 4.2488e-05 | 3.399e-05 | 3.0708e-05 | 3.0708e-05 | 0.0058311 | 0.0058208 | 0.0017888 | 0.0017888 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014753 | 0.0014753 | 0.0060081 | 0.0060081 | 64 | 59 | NO
2015-07-19 | 0.13704 | 0.13704 | 0 | 0 | 0 | 0 | 0.035696 | 0.035696 | 0.012808 | 0.012808 | 0.47179 | 0.47179 | 0.0013074 | 0.0013074 | 0 | 0 | 0 | 0 | 0.00041001 | 0.00041001 | 0.0014778 | 0.0014778 | 0.0032689 | 0.0032689 | 0.0067363 | 0.0067363 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017913 | 0.0017913 | 0.025669 | 0.025669 | 72 | 69 | NO
2015-07-20 | 0.64699 | 0.64295 | 0 | 0 | 0 | 0 | 0.017783 | 0.017783 | 0.13473 | 0.13473 | 2.4609 | 2.4447 | 0.003956 | 0.0035599 | 0 | 0 | 0 | 0 | 0.00018854 | 0.00018854 | 0.0016787 | 0.0016787 | 0.014201 | 0.012606 | 0.011191 | 0.011191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04505 | 0.04505 | 127 | 84 | NO
2015-07-21 | 0.099276 | 0.09897 | 0 | 0 | 0 | 0 | 0.0097621 | 0.0094264 | 0.39528 | 0.39456 | 0.06095 | 0.06095 | 0.0010534 | 0.0010452 | 0 | 0 | 0 | 0 | 0.00024484 | 0.00023209 | 0.0038218 | 0.0038116 | 0.00067262 | 0.00067262 | 0.035787 | 0.035787 | 0 | 0 | 0 | 0 | 0.057412 | 0.057412 | 0 | 0 | 0.032203 | 0.032203 | 116 | 75 | NO
2015-07-22 | 4.1677 | 4.167 | 0 | 0 | 0 | 0 | 5.1542 | 5.1542 | 3.1531 | 3.1511 | 4.1849 | 4.1839 | 0.034326 | 0.034309 | 0 | 0 | 0 | 0 | 0.028091 | 0.028086 | 0.03808 | 0.038048 | 0.052655 | 0.052622 | 0.039688 | 0.039688 | 0 | 0 | 0 | 0 | 0.019699 | 0.019699 | 0.0428 | 0.0428 | 0.086775 | 0.086775 | 274 | 181 | NO
2015-07-23 | 0.069043 | 0.067362 | 0 | 0 | 0 | 0 | 0.0039487 | 0.00083701 | 0.1487 | 0.1487 | 0.14998 | 0.14928 | 0.00051693 | 0.00042979 | 0 | 0 | 0 | 0 | 0.00019279 | 1.6995e-05 | 0.00091868 | 0.00091868 | 0.00096236 | 0.00095409 | 0.0057662 | 0.0057662 | 0 | 0 | 0 | 0 | 0.0035876 | 0.0035876 | 0.0033318 | 0.0033318 | 0.013528 | 0.013528 | 123 | 97 | NO
2015-07-24 | 0.78957 | 0.78934 | 0 | 0 | 0 | 0 | 0.004474 | 0.0040406 | 0.34264 | 0.34253 | 2.8927 | 2.8927 | 0.0058567 | 0.0058525 | 0 | 0 | 0 | 0 | 3.8239e-05 | 3.399e-05 | 0.001085 | 0.0010748 | 0.022625 | 0.022625 | 0.0048516 | 0.0048516 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019254 | 0.019254 | 0.0039591 | 0.0039591 | 109 | 68 | NO
2015-07-25 | 0.76806 | 0.76795 | 6.5793 | 6.5793 | 0 | 0 | 0.049801 | 0.049801 | 0.085564 | 0.085031 | 2.0813 | 2.0813 | 0.013262 | 0.013257 | 0.048377 | 0.048377 | 0 | 0 | 0.00051251 | 0.00051251 | 0.0093441 | 0.0093237 | 0.038622 | 0.038622 | 0.0048189 | 0.0048189 | 0 | 0 | 0 | 0 | 0.0025583 | 0.0025583 | 0.0029403 | 0.0029403 | 0.012037 | 0.012037 | 80 | 67 | NO
2015-07-26 | 2.3965 | 2.3965 | 0 | 0 | 0 | 0 | 0.5488 | 0.54875 | 3.694 | 3.694 | 5.5908 | 5.5907 | 0.013279 | 0.013271 | 0 | 0 | 0 | 0 | 0.0046837 | 0.0046752 | 0.015734 | 0.015724 | 0.031605 | 0.031597 | 0.04544 | 0.04544 | 0 | 0 | 0 | 0 | 0.00081258 | 0.00081258 | 0.037975 | 0.037975 | 0.15063 | 0.15063 | 206 | 122 | NO
2015-07-27 | 0.55471 | 0.55464 | 0 | 0 | 0.0085656 | 0.0085656 | 0.055531 | 0.055468 | 0.34791 | 0.34781 | 1.8423 | 1.8422 | 0.0051423 | 0.005132 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.00019757 | 0.00018482 | 0.0024426 | 0.0024323 | 0.018333 | 0.018324 | 0.0084971 | 0.0084971 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020504 | 0.020504 | 0.017624 | 0.017624 | 164 | 122 | NO
2015-07-28 | 0.086333 | 0.086214 | 0 | 0 | 0 | 0 | 0.072012 | 0.07185 | 0.16086 | 0.16065 | 0.077144 | 0.077144 | 0.00064083 | 0.00063055 | 0 | 0 | 0 | 0 | 0.00059536 | 0.00058261 | 0.0011631 | 0.0011426 | 0.00047911 | 0.00047911 | 0.0018839 | 0.0018839 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036069 | 0.0036069 | 0.004667 | 0.004667 | 129 | 113 | NO
2015-07-29 | 0.14202 | 0.14163 | 0 | 0 | 0 | 0 | 0.20748 | 0.20708 | 0.14102 | 0.14005 | 0.053412 | 0.053412 | 0.0014045 | 0.0013942 | 0 | 0 | 0 | 0 | 0.0023305 | 0.0023177 | 0.0011132 | 0.0010927 | 0.00021317 | 0.00021317 | 0.0042784 | 0.0042784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017223 | 0.017223 | 109 | 73 | NO
2015-07-30 | 0.49444 | 0.49423 | 0 | 0 | 0 | 0 | 0.54424 | 0.54412 | 0.13501 | 0.13501 | 0.82084 | 0.82023 | 0.011302 | 0.011291 | 0 | 0 | 0 | 0 | 0.011641 | 0.011628 | 0.016031 | 0.016031 | 0.0098492 | 0.0098327 | 0.0033391 | 0.0033391 | 0 | 0 | 0 | 0 | 0.002971 | 0.002971 | 0.0073993 | 0.0073993 | 0.0016691 | 0.0016691 | 158 | 108 | NO
2015-07-31 | 0.46588 | 0.46561 | 0 | 0 | 0 | 0 | 0.13123 | 0.13084 | 0.19105 | 0.19095 | 1.4653 | 1.465 | 0.0058875 | 0.0058813 | 0 | 0 | 0 | 0 | 0.0034542 | 0.00345 | 0.0030644 | 0.0030542 | 0.014492 | 0.014484 | 0.00064211 | 0.00064211 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011567 | 0.0011567 | 0.0016495 | 0.0016495 | 121 | 81 | NO
2015-08-01 | 0.42899 | 0.42881 | 0 | 0 | 0 | 0 | 0.02037 | 0.020306 | 2.0607 | 2.0607 | 0.020658 | 0.020087 | 0.0037218 | 0.0037157 | 0 | 0 | 0 | 0 | 0.00018482 | 0.00017632 | 0.017785 | 0.017785 | 0.00023904 | 0.00023076 | 0.0031024 | 0.0031024 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049823 | 0.0049823 | 0.0084595 | 0.0084595 | 89 | 80 | NO
2015-08-02 | 2.4495 | 2.4492 | 0 | 0 | 0 | 0 | 0.76624 | 0.76615 | 4.0565 | 4.0564 | 5.0871 | 5.0864 | 0.016861 | 0.016855 | 0 | 0 | 0 | 0 | 0.0081284 | 0.0081242 | 0.030768 | 0.030758 | 0.027154 | 0.027146 | 0.015587 | 0.015587 | 0 | 0 | 0 | 0 | 0.0062993 | 0.0062993 | 0.0050591 | 0.0050591 | 0.046382 | 0.046382 | 231 | 125 | NO
2015-08-03 | 7.6805 | 0 | 0 | 0 | 0 | 0 | 0.87896 | 0 | 8.4838 | 0 | 22.345 | 0 | 0.024522 | 0 | 0 | 0 | 0 | 0 | 0.0034973 | 0 | 0.033413 | 0 | 0.064882 | 0 | 0.028082 | 0 | 0 | 0 | 0 | 0 | 0.021918 | 0 | 0.0159 | 0 | 0.057484 | 0 | 0 | 0 | YES
2015-08-04 | 1.113 | 1.113 | 0 | 0 | 0 | 0 | 0.049012 | 0.048969 | 0.044615 | 0.044512 | 4.349 | 4.349 | 0.0012655 | 0.0012614 | 0 | 0 | 0 | 0 | 0.00044612 | 0.00044187 | 0.00031859 | 0.00030836 | 0.0039674 | 0.0039674 | 0.010027 | 0.010027 | 0 | 0 | 0 | 0 | 0.0029678 | 0.0029678 | 0.029659 | 0.029659 | 0.010597 | 0.010597 | 141 | 107 | NO
2015-08-05 | 1.1097 | 1.1087 | 0.0038702 | 0.0038702 | 0 | 0 | 0.096131 | 0.096089 | 0.18155 | 0.17698 | 4.1326 | 4.1325 | 0.0026307 | 0.0026201 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 0.00090817 | 0.00090393 | 0.00094555 | 0.00091356 | 0.0080476 | 0.0080394 | 0.0079275 | 0.0079275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031913 | 0.031913 | 146 | 107 | NO
2015-08-06 | 0.13826 | 0.13723 | 0 | 0 | 0 | 0 | 0.016534 | 0.01585 | 0.2939 | 0.2919 | 0.28669 | 0.28548 | 0.0012927 | 0.0012824 | 0 | 0 | 0 | 0 | 0.00028254 | 0.0002698 | 0.0024016 | 0.0023914 | 0.0027112 | 0.0027029 | 0.0081295 | 0.0081295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012924 | 0.012924 | 0.022274 | 0.022274 | 108 | 77 | NO
2015-08-07 | 0.27389 | 0.27312 | 1.4513 | 1.4513 | 0 | 0 | 0.0222 | 0.021121 | 0.010917 | 0.010835 | 0.86424 | 0.86332 | 0.0092436 | 0.0092312 | 0.024189 | 0.024189 | 0 | 0 | 0.00042382 | 0.00041107 | 0.00016761 | 0.00015738 | 0.033146 | 0.033129 | 0.0055826 | 0.0055826 | 0 | 0 | 0 | 0 | 0.0026603 | 0.0026603 | 0.018788 | 0.018788 | 0.0020955 | 0.0020955 | 114 | 83 | NO
2015-08-08 | 1.8294 | 1.7356 | 0 | 0 | 0 | 0 | 0.14961 | 0.14957 | 0.98732 | 0.98732 | 6.2746 | 5.897 | 0.012921 | 0.012489 | 0 | 0 | 0 | 0 | 0.0037936 | 0.0037894 | 0.010519 | 0.010519 | 0.036118 | 0.034386 | 0.0032224 | 0.0032224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012972 | 0.012972 | 74 | 58 | NO
2015-08-09 | 0.20365 | 0.20323 | 0 | 0 | 0 | 0 | 0.0040703 | 0.0031993 | 0.79633 | 0.79633 | 0.16787 | 0.16787 | 0.0014878 | 0.0014837 | 0 | 0 | 0 | 0 | 3.399e-05 | 2.5493e-05 | 0.0054903 | 0.0054903 | 0.0014829 | 0.0014829 | 0.00029484 | 0.00029484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011869 | 0.0011869 | 48 | 45 | NO
2015-08-10 | 0.50386 | 0.50334 | 0 | 0 | 0 | 0 | 0.3116 | 0.31101 | 1.3347 | 1.3347 | 0.34176 | 0.34083 | 0.0034902 | 0.0034841 | 0 | 0 | 0 | 0 | 0.0032046 | 0.0031961 | 0.0083154 | 0.0083154 | 0.0010814 | 0.0010731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 79 | NO
2015-08-11 | 0.074407 | 0.074029 | 0 | 0 | 0 | 0 | 0.016407 | 0.015625 | 0.10888 | 0.10888 | 0.17951 | 0.17951 | 0.00040203 | 0.00039586 | 0 | 0 | 0 | 0 | 0.00018057 | 0.00016783 | 0.00095066 | 0.00095066 | 0.00049774 | 0.00049774 | 0.008247 | 0.008247 | 0 | 0 | 0 | 0 | 0.003331 | 0.003331 | 0.0017747 | 0.0017747 | 0.025274 | 0.025274 | 98 | 65 | NO
2015-08-12 | 0.031596 | 0.031513 | 0 | 0 | 0 | 0 | 0.043027 | 0.042942 | 0.0092124 | 0.0092124 | 0.035908 | 0.035742 | 0.00026656 | 0.00025834 | 0 | 0 | 0 | 0 | 0.00018907 | 0.00018057 | 0.00012795 | 0.00012795 | 0.00060122 | 0.00058466 | 0.010295 | 0.010295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016614 | 0.016614 | 0.028007 | 0.028007 | 101 | 68 | NO
2015-08-13 | 0.11077 | 0.11075 | 0 | 0 | 0 | 0 | 0.0078135 | 0.007771 | 0.0084344 | 0.0084344 | 0.42388 | 0.42388 | 0.00046423 | 0.00046218 | 0 | 0 | 0 | 0 | 2.1244e-05 | 1.6995e-05 | 7.4211e-05 | 7.4211e-05 | 0.0017674 | 0.0017674 | 0.0021559 | 0.0021559 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043951 | 0.0043951 | 0.0051243 | 0.0051243 | 82 | 52 | NO
2015-08-14 | 0.035604 | 0.035228 | 0 | 0 | 0 | 0 | 0.0029486 | 0.0024303 | 0.062521 | 0.062521 | 0.087022 | 0.086517 | 0.00042285 | 0.00041874 | 0 | 0 | 0 | 0 | 3.399e-05 | 2.9742e-05 | 0.00060392 | 0.00060392 | 0.0011476 | 0.0011393 | 0.005632 | 0.005632 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073942 | 0.0073942 | 0.016692 | 0.016692 | 86 | 48 | NO
2015-08-15 | 0.02884 | 0.028536 | 0 | 0 | 0 | 0 | 0.029513 | 0.028884 | 0.023328 | 0.023328 | 0.039731 | 0.039731 | 0.00027941 | 0.00027119 | 0 | 0 | 0 | 0 | 0.0002459 | 0.0002289 | 0.00027637 | 0.00027637 | 0.0004222 | 0.0004222 | 0.03079 | 0.03079 | 0 | 0 | 0 | 0 | 0.063615 | 0.063615 | 0 | 0 | 0 | 0 | 66 | 57 | NO
2015-08-16 | 2.9796 | 2.9792 | 0 | 0 | 0.13845 | 0.13845 | 0.9101 | 0.90968 | 0.19583 | 0.19583 | 10.0438 | 10.043 | 0.019322 | 0.019318 | 0 | 0 | 0.0055381 | 0.0055381 | 0.036272 | 0.036267 | 0.0019781 | 0.0019781 | 0.0047342 | 0.0047259 | 0.0089068 | 0.0089068 | 0 | 0 | 0 | 0 | 0.0041192 | 0.0041192 | 0.0039895 | 0.0039895 | 0.024603 | 0.024603 | 70 | 66 | NO
2015-08-17 | 0.17835 | 0.17793 | 0 | 0 | 0 | 0 | 0.039852 | 0.03941 | 0.77769 | 0.77667 | 0.011362 | 0.011362 | 0.002297 | 0.0022908 | 0 | 0 | 0 | 0 | 0.0010691 | 0.0010606 | 0.0087325 | 0.0087223 | 0.00010141 | 0.00010141 | 0.0036082 | 0.0036082 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009902 | 0.009902 | 0.0065172 | 0.0065172 | 138 | 102 | NO
2015-08-18 | 0.3808 | 0.38076 | 0 | 0 | 0 | 0 | 0.56672 | 0.56668 | 0.052221 | 0.052221 | 0.38654 | 0.38645 | 0.0051636 | 0.0051595 | 0 | 0 | 0 | 0 | 0.0096452 | 0.009641 | 0.00029556 | 0.00029556 | 0.001755 | 0.0017467 | 0.0014652 | 0.0014652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0058984 | 0.0058984 | 189 | 109 | NO
2015-08-19 | 0.075967 | 0.075646 | 0 | 0 | 0 | 0 | 0.089025 | 0.088405 | 0.09773 | 0.09773 | 0.053319 | 0.053236 | 0.00088066 | 0.00087449 | 0 | 0 | 0 | 0 | 0.00090446 | 0.00089596 | 0.0011925 | 0.0011925 | 0.00081853 | 0.00081025 | 0.00049662 | 0.00049662 | 0 | 0 | 0 | 0 | 0.0005927 | 0.0005927 | 0.0010441 | 0.0010441 | 0 | 0 | 106 | 74 | NO
2015-08-20 | 0.036309 | 0.036227 | 0.0025156 | 0.0025156 | 0 | 0 | 0.025807 | 0.025722 | 0.037617 | 0.037515 | 0.06514 | 0.065057 | 0.00047015 | 0.00046192 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 0.00055659 | 0.00054809 | 0.00028661 | 0.00027637 | 0.00056811 | 0.00055983 | 0.0071147 | 0.0071147 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021931 | 0.021931 | 0.010905 | 0.010905 | 100 | 71 | NO
2015-08-21 | 0.07417 | 0.074127 | 0 | 0 | 0 | 0 | 0.012361 | 0.012272 | 0.070596 | 0.070596 | 0.2174 | 0.2174 | 0.00040537 | 0.00040126 | 0 | 0 | 0 | 0 | 0.00010516 | 9.666e-05 | 0.00057577 | 0.00057577 | 0.00096133 | 0.00096133 | 0.0022245 | 0.0022245 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0096768 | 0.0096768 | 0.001129 | 0.001129 | 127 | 80 | NO
2015-08-22 | 0.044713 | 0.044692 | 0 | 0 | 0 | 0 | 0.0040491 | 0.0040066 | 0.13154 | 0.13154 | 0.065729 | 0.065729 | 0.0001915 | 0.00018945 | 0 | 0 | 0 | 0 | 3.399e-05 | 2.9742e-05 | 9.98e-05 | 9.98e-05 | 0.00062398 | 0.00062398 | 0.0064155 | 0.0064155 | 0 | 0 | 0 | 0 | 0.0025131 | 0.0025131 | 0.018499 | 0.018499 | 0.0059687 | 0.0059687 | 51 | 45 | NO
2015-08-23 | 0.13581 | 0.13579 | 0 | 0 | 0 | 0 | 0.0019374 | 0.0019374 | 0.44721 | 0.44711 | 0.18128 | 0.18128 | 0.00090174 | 0.00089968 | 0 | 0 | 0 | 0 | 1.2746e-05 | 1.2746e-05 | 0.0028917 | 0.0028814 | 0.0012666 | 0.0012666 | 0.0074673 | 0.0074673 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022135 | 0.0022135 | 0.028271 | 0.028271 | 54 | 48 | NO
2015-08-24 | 0.099897 | 0.098982 | 0.00064503 | 0 | 0 | 0 | 0.01358 | 0.013516 | 0.1841 | 0.1818 | 0.22672 | 0.2251 | 0.0019824 | 0.0019721 | 6.4503e-05 | 0 | 0 | 0 | 0.00019279 | 0.00018429 | 0.00053227 | 0.00052203 | 0.007166 | 0.0071577 | 0.0048773 | 0.0048773 | 0 | 0 | 0 | 0 | 0.0075713 | 0.0075713 | 0.0043951 | 0.0043951 | 0.0013276 | 0.0013276 | 113 | 84 | NO
2015-08-25 | 0.027459 | 0.027438 | 0 | 0 | 0 | 0 | 0.002477 | 0.0024345 | 0.12368 | 0.12368 | 0.0056862 | 0.0056862 | 0.00035319 | 0.00035113 | 0 | 0 | 0 | 0 | 3.4521e-05 | 3.0273e-05 | 0.0016173 | 0.0016173 | 4.6566e-05 | 4.6566e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 67 | NO
2015-08-26 | 0.18818 | 0.1881 | 0 | 0 | 0.055293 | 0.055293 | 0.23529 | 0.23513 | 0.037945 | 0.037945 | 0.26065 | 0.26065 | 0.0014762 | 0.0014742 | 0 | 0 | 0.00070888 | 0.00070888 | 0.0012629 | 0.0012587 | 0.00043375 | 0.00043375 | 0.003032 | 0.003032 | 0.0015166 | 0.0015166 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049312 | 0.0049312 | 0.0021172 | 0.0021172 | 105 | 91 | NO
2015-08-27 | 0.03595 | 0.035898 | 0 | 0 | 0 | 0 | 0.014024 | 0.01396 | 0.052367 | 0.052367 | 0.075044 | 0.074961 | 0.00032825 | 0.00032209 | 0 | 0 | 0 | 0 | 0.00015667 | 0.00014818 | 0.00089053 | 0.00089053 | 0.00029595 | 0.00028767 | 0.022424 | 0.022424 | 0 | 0 | 0 | 0 | 0.040245 | 0.040245 | 0.012961 | 0.012961 | 0.0013763 | 0.0013763 | 102 | 67 | NO
2015-08-28 | 0.11269 | 0.11264 | 0 | 0 | 0 | 0 | 0.042114 | 0.042071 | 0.071012 | 0.071012 | 0.31415 | 0.31406 | 0.00058196 | 0.00057785 | 0 | 0 | 0 | 0 | 0.00028254 | 0.00027829 | 0.00063975 | 0.00063975 | 0.0012749 | 0.0012666 | 0.010247 | 0.010247 | 0 | 0 | 0 | 0 | 1.3277e-05 | 1.3277e-05 | 0.0097728 | 0.0097728 | 0.03332 | 0.03332 | 90 | 57 | NO
2015-08-29 | 0.30736 | 0.30732 | 0 | 0 | 0 | 0 | 0.12108 | 0.121 | 0.91226 | 0.91226 | 0.26361 | 0.26361 | 0.0080565 | 0.0080544 | 0 | 0 | 0 | 0 | 0.0015434 | 0.0015391 | 0.027691 | 0.027691 | 0.0070304 | 0.0070304 | 0.023377 | 0.023377 | 0 | 0 | 0 | 0 | 0.003715 | 0.003715 | 0.08014 | 0.08014 | 0.022057 | 0.022057 | 74 | 67 | NO
2015-08-30 | 0.53736 | 0.53695 | 0 | 0 | 0 | 0 | 0.01763 | 0.016785 | 0.82791 | 0.82791 | 1.4593 | 1.4593 | 0.0037686 | 0.0037625 | 0 | 0 | 0 | 0 | 0.00026396 | 0.00025121 | 0.0055556 | 0.0055556 | 0.010164 | 0.010164 | 0.0046678 | 0.0046678 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065446 | 0.0065446 | 0.013498 | 0.013498 | 100 | 65 | NO
2015-08-31 | 0.056783 | 0.056721 | 0 | 0 | 0.0047849 | 0.0047849 | 0.0098444 | 0.0098444 | 0.0072675 | 0.0071652 | 0.20286 | 0.20269 | 0.00056705 | 0.00056089 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 8.2851e-05 | 8.2851e-05 | 0.00014842 | 0.00013819 | 0.001993 | 0.0019765 | 0.013363 | 0.013363 | 0 | 0 | 0 | 0 | 0.017065 | 0.017065 | 0.00084447 | 0.00084447 | 0.01986 | 0.01986 | 113 | 79 | NO
2015-09-01 | 0.67656 | 0.6761 | 0 | 0 | 0 | 0 | 0.017759 | 0.017695 | 0.12805 | 0.12805 | 2.5854 | 2.5837 | 0.0042763 | 0.0042701 | 0 | 0 | 0 | 0 | 0.00014977 | 0.00014127 | 0.00054634 | 0.00054634 | 0.016481 | 0.016473 | 0.01115 | 0.01115 | 0 | 0 | 0.20676 | 0.20676 | 0.004116 | 0.004116 | 0.0002623 | 0.0002623 | 0.0076813 | 0.0076813 | 111 | 90 | NO
2015-09-02 | 0.15833 | 0.15825 | 0 | 0 | 0 | 0 | 0.010834 | 0.010707 | 0.57025 | 0.5702 | 0.15506 | 0.15506 | 0.00071537 | 0.00071126 | 0 | 0 | 0 | 0 | 2.9742e-05 | 2.5493e-05 | 0.0018297 | 0.0018194 | 0.0013421 | 0.0013421 | 0.0045932 | 0.0045932 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037796 | 0.0037796 | 0.015434 | 0.015434 | 93 | 81 | NO
2015-09-03 | 0.24382 | 0.24377 | 0 | 0 | 0 | 0 | 0.03618 | 0.036117 | 1.0947 | 1.0946 | 0.025708 | 0.025708 | 0.0028389 | 0.0028327 | 0 | 0 | 0 | 0 | 0.00026555 | 0.00025705 | 0.012801 | 0.012791 | 0.00055776 | 0.00055776 | 0.008922 | 0.008922 | 0 | 0 | 0 | 0 | 0.0028913 | 0.0028913 | 0.02229 | 0.02229 | 0.012256 | 0.012256 | 116 | 89 | NO
2015-09-04 | 0.064743 | 0.064743 | 0 | 0 | 0 | 0 | 0.013526 | 0.013526 | 0.27982 | 0.27982 | 0.0079752 | 0.0079752 | 0.00058788 | 0.00058788 | 0 | 0 | 0 | 0 | 0.00019226 | 0.00019226 | 0.0024208 | 0.0024208 | 3.4148e-05 | 3.4148e-05 | 0.0054274 | 0.0054274 | 0 | 0 | 0 | 0 | 0.00057624 | 0.00057624 | 0.014993 | 0.014993 | 0.0086002 | 0.0086002 | 70 | 54 | NO
2015-09-05 | 0.046572 | 0.046521 | 0 | 0 | 0 | 0 | 0.025418 | 0.025333 | 0.016933 | 0.016882 | 0.12426 | 0.12426 | 0.00040074 | 0.00039457 | 0 | 0 | 0 | 0 | 0.00043337 | 0.00042488 | 9.4683e-05 | 8.4447e-05 | 0.00069228 | 0.00069228 | 0.010801 | 0.010801 | 0 | 0 | 0 | 0 | 0.0077652 | 0.0077652 | 0.0013473 | 0.0013473 | 0.027263 | 0.027263 | 59 | 53 | NO
2015-09-06 | 0.33656 | 0.33656 | 0 | 0 | 0 | 0 | 0.00068405 | 0.00068405 | 0.03026 | 0.03026 | 1.3291 | 1.3291 | 0.0014482 | 0.0014482 | 0 | 0 | 0 | 0 | 4.2488e-06 | 4.2488e-06 | 0.00073571 | 0.00073571 | 0.0052268 | 0.0052268 | 0.0029386 | 0.0029386 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004143 | 0.004143 | 0.0084792 | 0.0084792 | 35 | 33 | NO
2015-09-07 | 0.15741 | 0.15726 | 0 | 0 | 0 | 0 | 0.19508 | 0.19508 | 0.062055 | 0.061503 | 0.20338 | 0.20325 | 0.0039046 | 0.0038984 | 0 | 0 | 0 | 0 | 0.0064109 | 0.0064109 | 0.00168 | 0.0016697 | 0.0018689 | 0.0018523 | 0.0045555 | 0.0045555 | 0 | 0 | 0 | 0 | 0.0086298 | 0.0086298 | 0.0018847 | 0.0018847 | 0 | 0 | 130 | 104 | NO
2015-09-08 | 0.23133 | 0.23131 | 0 | 0 | 0 | 0 | 0.0017717 | 0.0017717 | 0.0064384 | 0.0063361 | 0.9226 | 0.92259 | 0.00088143 | 0.00087732 | 0 | 0 | 0 | 0 | 2.1244e-05 | 2.1244e-05 | 3.0708e-05 | 2.0472e-05 | 0.0034821 | 0.0034738 | 0.0036776 | 0.0036776 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074403 | 0.0074403 | 0.0087875 | 0.0087875 | 107 | 71 | NO
2015-09-09 | 0.016165 | 0.016155 | 0 | 0 | 0 | 0 | 0.0075246 | 0.0075246 | 0.050921 | 0.05087 | 0.0092325 | 0.0092325 | 0.0001532 | 0.00015115 | 0 | 0 | 0 | 0 | 7.0105e-05 | 7.0105e-05 | 0.00047085 | 0.00046062 | 9.9341e-05 | 9.9341e-05 | 0.0036828 | 0.0036828 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014155 | 0.014155 | 0.0033776 | 0.0033776 | 96 | 71 | NO
2015-09-10 | 0.23109 | 0.23027 | 0 | 0 | 0 | 0 | 0.056111 | 0.056069 | 0.60259 | 0.60259 | 0.33362 | 0.3304 | 0.0090235 | 0.0090174 | 0 | 0 | 0 | 0 | 0.0033672 | 0.0033587 | 0.021369 | 0.021369 | 0.012483 | 0.012475 | 0.021326 | 0.021326 | 0 | 0 | 0 | 0 | 0.0070445 | 0.0070445 | 0.030657 | 0.030657 | 0.047331 | 0.047331 | 97 | 52 | NO
2015-09-11 | 0.10645 | 0.10611 | 0 | 0 | 0 | 0 | 0.016081 | 0.015389 | 0.14717 | 0.14717 | 0.27815 | 0.27815 | 0.00058248 | 0.00057837 | 0 | 0 | 0 | 0 | 0.00023846 | 0.00022996 | 0.00072419 | 0.00072419 | 0.0012945 | 0.0012945 | 0.0038519 | 0.0038519 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065907 | 0.0065907 | 0.010176 | 0.010176 | 66 | 41 | NO
2015-09-12 | 0.17036 | 0.17034 | 0 | 0 | 0 | 0 | 0.00038239 | 0.0003399 | 0.034853 | 0.034853 | 0.65689 | 0.65689 | 0.00090868 | 0.00090662 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.2746e-05 | 0.00033011 | 0.00033011 | 0.0033579 | 0.0033579 | 0.03424 | 0.03424 | 0 | 0 | 0 | 0 | 0.060044 | 0.060044 | 0 | 0 | 0.020847 | 0.020847 | 31 | 31 | NO
2015-09-13 | 0.026608 | 0.02624 | 0 | 0 | 0 | 0 | 0.0063179 | 0.0062754 | 0.069942 | 0.069942 | 0.038238 | 0.036839 | 0.00022158 | 0.00021747 | 0 | 0 | 0 | 0 | 7.0105e-05 | 6.5856e-05 | 0.00056042 | 0.00056042 | 0.00030216 | 0.00029388 | 0.0050259 | 0.0050259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020232 | 0.020232 | 40 | 38 | NO
2015-09-14 | 0.35685 | 0.35668 | 0 | 0 | 0 | 0 | 0.2927 | 0.29239 | 0.2028 | 0.2028 | 0.70224 | 0.70216 | 0.0054528 | 0.0054467 | 0 | 0 | 0 | 0 | 0.0050778 | 0.0050693 | 0.0059241 | 0.0059241 | 0.0072664 | 0.0072581 | 0.012226 | 0.012226 | 0 | 0 | 0 | 0 | 0.0050263 | 0.0050263 | 0.009609 | 0.009609 | 0.031654 | 0.031654 | 153 | 95 | NO
2015-09-15 | 0.39335 | 0.39198 | 0 | 0 | 0 | 0 | 0.0027022 | 0.001844 | 0.39733 | 0.3942 | 1.2569 | 1.2556 | 0.0020783 | 0.0020618 | 0 | 0 | 0 | 0 | 3.8239e-05 | 2.5493e-05 | 0.0065766 | 0.0065561 | 0.002973 | 0.0029481 | 0.0013626 | 0.0013626 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065267 | 0.0065267 | 0.00020696 | 0.00020696 | 98 | 73 | NO
2015-09-16 | 0.02606 | 0.026039 | 0 | 0 | 0 | 0 | 0.0016018 | 0.0016018 | 0.022222 | 0.022222 | 0.083815 | 0.083732 | 0.00017685 | 0.00017479 | 0 | 0 | 0 | 0 | 2.1244e-05 | 2.1244e-05 | 0.00015866 | 0.00015866 | 0.00054224 | 0.00053396 | 0.0017024 | 0.0017024 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015252 | 0.0015252 | 0.00562 | 0.00562 | 77 | 69 | NO
2015-09-17 | 0.069296 | 0.069276 | 0 | 0 | 0 | 0 | 0.088948 | 0.088927 | 0.085675 | 0.085675 | 0.036364 | 0.036323 | 0.00077732 | 0.00077321 | 0 | 0 | 0 | 0 | 0.00043231 | 0.00042806 | 0.0018796 | 0.0018796 | 0.00076679 | 0.00075851 | 0.00058351 | 0.00058351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017747 | 0.0017747 | 0.00091373 | 0.00091373 | 92 | 89 | NO
2015-09-18 | 0.78949 | 0.78948 | 0 | 0 | 0 | 0 | 0.87241 | 0.87239 | 1.8079 | 1.8079 | 0.016246 | 0.016246 | 0.0036216 | 0.0036195 | 0 | 0 | 0 | 0 | 0.0044092 | 0.0044049 | 0.0072982 | 0.0072982 | 8.5888e-05 | 8.5888e-05 | 0.0040809 | 0.0040809 | 0 | 0 | 0 | 0 | 0.0046577 | 0.0046577 | 0.0089897 | 0.0089897 | 8.2784e-05 | 8.2784e-05 | 80 | 77 | NO
2015-09-19 | 0.028255 | 0.028234 | 0 | 0 | 0 | 0 | 0.001298 | 0.0012555 | 0.039313 | 0.039313 | 0.079421 | 0.079421 | 0.00029227 | 0.00029021 | 0 | 0 | 0 | 0 | 2.6024e-05 | 2.1775e-05 | 0.00028533 | 0.00028533 | 0.0008951 | 0.0008951 | 0.0088333 | 0.0088333 | 0 | 0 | 0 | 0 | 0.011158 | 0.011158 | 0.0038794 | 0.0038794 | 0.010681 | 0.010681 | 39 | 37 | NO
2015-09-20 | 0.0021356 | 0.0020307 | 0 | 0 | 0 | 0 | 0.0010675 | 0.0010463 | 0.0058447 | 0.0053739 | 0.0017902 | 0.0017902 | 2.9561e-05 | 2.3392e-05 | 0 | 0 | 0 | 0 | 2.0713e-05 | 1.6464e-05 | 8.4447e-05 | 6.3975e-05 | 1.0348e-05 | 1.0348e-05 | 0.0076529 | 0.0076529 | 0 | 0 | 0 | 0 | 0.0011668 | 0.0011668 | 0.012782 | 0.012782 | 0.018197 | 0.018197 | 24 | 22 | NO
2015-09-21 | 0.39302 | 0.39299 | 0 | 0 | 0 | 0 | 0.012575 | 0.012533 | 1.404 | 1.404 | 0.4222 | 0.42216 | 0.0030905 | 0.0030864 | 0 | 0 | 0 | 0 | 0.00019438 | 0.00019013 | 0.010535 | 0.010535 | 0.0035421 | 0.0035338 | 0.0049112 | 0.0049112 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01414 | 0.01414 | 0.0083353 | 0.0083353 | 112 | 100 | NO
2015-09-22 | 0.96917 | 0.96915 | 0 | 0 | 0 | 0 | 0.32492 | 0.32492 | 1.2242 | 1.2241 | 2.2784 | 2.2784 | 0.026289 | 0.026287 | 0 | 0 | 0 | 0 | 0.0059063 | 0.0059063 | 0.037301 | 0.037291 | 0.064157 | 0.064157 | 0.066852 | 0.066852 | 0 | 0 | 0 | 0 | 0.0093977 | 0.0093977 | 0.034679 | 0.034679 | 0.22277 | 0.22277 | 161 | 113 | NO
2015-09-23 | 0.0070134 | 0.0069928 | 0 | 0 | 0.051689 | 0.051689 | 0.0030506 | 0.0030506 | 0.013987 | 0.013987 | 0.0037336 | 0.0036508 | 0.00020024 | 0.00019819 | 0 | 0 | 0.0036921 | 0.0036921 | 3.8239e-05 | 3.8239e-05 | 0.0002124 | 0.0002124 | 4.2427e-05 | 3.4148e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 76 | NO
2015-09-24 | 0.080488 | 0.077709 | 0 | 0 | 0 | 0 | 0.1057 | 0.1057 | 0.060358 | 0.046859 | 0.069248 | 0.068979 | 0.0066566 | 0.0066391 | 0 | 0 | 0 | 0 | 0.0023135 | 0.0023135 | 0.012957 | 0.012893 | 0.01181 | 0.011792 | 0.0037455 | 0.0037455 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044309 | 0.0044309 | 0.011495 | 0.011495 | 72 | 40 | NO
2015-09-25 | 0.034936 | 0.034775 | 0 | 0 | 0 | 0 | 0.016262 | 0.016262 | 0.041841 | 0.041093 | 0.075116 | 0.075075 | 0.00032748 | 0.00032131 | 0 | 0 | 0 | 0 | 7.9133e-05 | 7.9133e-05 | 0.00062311 | 0.00060264 | 0.0006602 | 0.00065192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 62 | NO
2015-09-26 | 0.88242 | 0.88241 | 0 | 0 | 0 | 0 | 0.11474 | 0.11474 | 0.24401 | 0.24401 | 3.1314 | 3.1314 | 0.017524 | 0.017522 | 0 | 0 | 0 | 0 | 0.00086994 | 0.00086994 | 0.011091 | 0.011091 | 0.059883 | 0.059875 | 0.018322 | 0.018322 | 0 | 0 | 0 | 0 | 0.00069839 | 0.00069839 | 0.0082271 | 0.0082271 | 0.065742 | 0.065742 | 113 | 85 | NO
2015-09-27 | 0.31722 | 0.31715 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25447 | 0.25447 | 1.0712 | 1.071 | 0.01491 | 0.014904 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011344 | 0.011344 | 0.050848 | 0.050823 | 0.0039606 | 0.0039606 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0080672 | 0.0080672 | 0.0094198 | 0.0094198 | 47 | 45 | NO
2015-09-28 | 0.093897 | 0.093835 | 0 | 0 | 0 | 0 | 0.0046843 | 0.0045993 | 0.053429 | 0.053327 | 0.32566 | 0.32566 | 0.0035 | 0.0034938 | 0 | 0 | 0 | 0 | 7.8602e-05 | 7.0105e-05 | 0.00064486 | 0.00063463 | 0.013415 | 0.013415 | 0.0069735 | 0.0069735 | 0 | 0 | 0 | 0 | 0.0021116 | 0.0021116 | 0.011963 | 0.011963 | 0.014283 | 0.014283 | 107 | 101 | NO
2015-09-29 | 0.43077 | 0.42566 | 0 | 0 | 0 | 0 | 0.22939 | 0.22939 | 0.80775 | 0.79585 | 0.63391 | 0.62298 | 0.0050883 | 0.0050842 | 0 | 0 | 0 | 0 | 0.0049259 | 0.0049259 | 0.0073891 | 0.0073788 | 0.0049101 | 0.0049019 | 0.017036 | 0.017036 | 0 | 0 | 0 | 0 | 0.012831 | 0.012831 | 0.029583 | 0.029583 | 0.019657 | 0.019657 | 259 | 168 | NO
2015-09-30 | 0.52074 | 0.52052 | 0 | 0 | 0 | 0 | 0.0022986 | 0.0022986 | 1.0244 | 1.024 | 1.2633 | 1.2628 | 0.0095644 | 0.0095602 | 0 | 0 | 0 | 0 | 1.2746e-05 | 1.2746e-05 | 0.022066 | 0.022056 | 0.020632 | 0.020624 | 0.00083979 | 0.00083979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0033807 | 0.0033807 | 116 | 93 | NO
2015-10-01 | 0.15545 | 0.15485 | 0 | 0 | 0 | 0 | 0.0038069 | 0.0038069 | 0.014165 | 0.013224 | 0.60691 | 0.60528 | 0.0004339 | 0.00042362 | 0 | 0 | 0 | 0 | 8.2851e-05 | 8.2851e-05 | 0.00022007 | 0.00018937 | 0.0014073 | 0.0013908 | 0.012889 | 0.012889 | 0 | 0 | 0 | 0 | 0.018333 | 0.018333 | 0.0065382 | 0.0065382 | 0.010878 | 0.010878 | 101 | 79 | NO
2015-10-02 | 0.083663 | 0.083643 | 0 | 0 | 0 | 0 | 0.016795 | 0.016795 | 0.23796 | 0.23786 | 0.11162 | 0.11162 | 0.0024204 | 0.0024183 | 0 | 0 | 0 | 0 | 0.00029104 | 0.00029104 | 0.010466 | 0.010456 | 0.00071194 | 0.00071194 | 0.011067 | 0.011067 | 0 | 0 | 0 | 0 | 0.011158 | 0.011158 | 0.018019 | 0.018019 | 0.0082391 | 0.0082391 | 89 | 79 | NO
2015-10-03 | 2.0935 | 2.0935 | 0 | 0 | 0 | 0 | 0.062232 | 0.062232 | 1.9321 | 1.9321 | 6.744 | 6.744 | 0.017692 | 0.017692 | 0 | 0 | 0 | 0 | 0.00075628 | 0.00075628 | 0.023745 | 0.023745 | 0.050544 | 0.050544 | 0.0045339 | 0.0045339 | 0 | 0 | 0 | 0 | 0.0087259 | 0.0087259 | 0.0015136 | 0.0015136 | 2.587e-05 | 2.587e-05 | 160 | 133 | NO
2015-10-04 | 0.1275 | 0.1275 | 0.35074 | 0.35074 | 0 | 0 | 0.001708 | 0.001708 | 0.43948 | 0.43948 | 0.10948 | 0.10948 | 0.00065445 | 0.00065445 | 0.0060472 | 0.0060472 | 0 | 0 | 1.6995e-05 | 1.6995e-05 | 0.0012539 | 0.0012539 | 0.00081128 | 0.00081128 | 0.0053749 | 0.0053749 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01059 | 0.01059 | 0.013073 | 0.013073 | 68 | 65 | NO
2015-10-05 | 0.19796 | 0.10526 | 0 | 0 | 0 | 0 | 0.1934 | 0.0018695 | 0.1437 | 0.1437 | 0.30388 | 0.30388 | 0.0040624 | 0.0016891 | 0 | 0 | 0 | 0 | 0.0049249 | 2.1244e-05 | 0.0020062 | 0.0020062 | 0.0051357 | 0.0051357 | 0.0014762 | 0.0014762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0059429 | 0.0059429 | 99 | 67 | NO
2015-10-06 | 2.1852 | 2.1851 | 0 | 0 | 0 | 0 | 0.0016931 | 0.0016209 | 1.4863 | 1.4863 | 7.5915 | 7.5914 | 0.011587 | 0.011579 | 0 | 0 | 0 | 0 | 4.7799e-05 | 3.5052e-05 | 0.0064768 | 0.0064768 | 0.041314 | 0.041306 | 0.0092808 | 0.0092808 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011032 | 0.011032 | 0.028439 | 0.028439 | 177 | 118 | NO
2015-10-07 | 0.13649 | 0.12958 | 0 | 0 | 0 | 0 | 0.13186 | 0.13174 | 0.14536 | 0.14319 | 0.175 | 0.14914 | 0.0056286 | 0.0056155 | 0 | 0 | 0 | 0 | 0.0067205 | 0.0067162 | 0.0066854 | 0.0066751 | 0.0041578 | 0.0041216 | 0.012836 | 0.012836 | 0 | 0 | 0 | 0 | 0.018195 | 0.018195 | 0.0038794 | 0.0038794 | 0.013085 | 0.013085 | 107 | 97 | NO
2015-10-08 | 0.39377 | 0.39176 | 0 | 0 | 0.062854 | 0.01465 | 0.48957 | 0.4894 | 0.64752 | 0.64741 | 0.098801 | 0.097882 | 0.0043794 | 0.0043691 | 0 | 0 | 0.00017722 | 0.00011815 | 0.0074954 | 0.0074869 | 0.0017452 | 0.001735 | 0.0015895 | 0.0015812 | 0.0045146 | 0.0045146 | 0 | 0 | 0 | 0 | 0.0077354 | 0.0077354 | 0.0031987 | 0.0031987 | 0.00051533 | 0.00051533 | 78 | 70 | NO
2015-10-09 | 0.020104 | 0.01458 | 0 | 0 | 0.0023629 | 0.0023629 | 0.0014063 | 0.0014063 | 0.021232 | 0.020126 | 0.060689 | 0.039346 | 0.00013932 | 0.00012313 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 1.6995e-05 | 1.6995e-05 | 0.00018297 | 0.00017273 | 0.00037149 | 0.00031458 | 0.018023 | 0.018023 | 0 | 0 | 0 | 0 | 0.012154 | 0.012154 | 0.0090064 | 0.0090064 | 0.041591 | 0.041591 | 80 | 62 | NO
2015-10-10 | 0.089772 | 0.089752 | 0 | 0 | 0 | 0 | 0.0033629 | 0.0033629 | 0.02827 | 0.02827 | 0.33198 | 0.33189 | 0.0017122 | 0.0017102 | 0 | 0 | 0 | 0 | 3.877e-05 | 3.877e-05 | 0.00046446 | 0.00046446 | 0.0064416 | 0.0064334 | 0.0054112 | 0.0054112 | 0 | 0 | 0 | 0 | 0.007037 | 0.007037 | 0 | 0 | 0.0080725 | 0.0080725 | 62 | 58 | NO
2015-10-11 | 0.042497 | 0.042497 | 0 | 0 | 0 | 0 | 0.015427 | 0.015427 | 0.073332 | 0.073332 | 0.081711 | 0.081711 | 0.00033494 | 0.00033494 | 0 | 0 | 0 | 0 | 0.00019332 | 0.00019332 | 0.00041072 | 0.00041072 | 0.00063951 | 0.00063951 | 0.0047922 | 0.0047922 | 0 | 0 | 0 | 0 | 0.006951 | 0.006951 | 0.004944 | 0.004944 | 0.0017498 | 0.0017498 | 33 | 29 | NO
2015-10-12 | 0.29802 | 0.26949 | 0 | 0 | 0 | 0 | 0.0076223 | 0.0074523 | 0.30106 | 0.30095 | 0.94138 | 0.82697 | 0.0082094 | 0.0080984 | 0 | 0 | 0 | 0 | 7.6478e-05 | 5.9483e-05 | 0.013204 | 0.013194 | 0.02222 | 0.021815 | 0.011021 | 0.011021 | 0 | 0 | 0.035075 | 0.035075 | 0.0015402 | 0.0015402 | 0.0007549 | 0.0007549 | 0.03584 | 0.03584 | 302 | 130 | NO
2015-10-13 | 0.30894 | 0.072165 | 0 | 0 | 0 | 0 | 0.00010622 | 0.00010622 | 0.13002 | 0.13002 | 1.1383 | 0.18515 | 0.0019341 | 0.00036578 | 0 | 0 | 0 | 0 | 4.2488e-06 | 4.2488e-06 | 0.00066662 | 0.00066662 | 0.0072384 | 0.00092511 | 0.0098852 | 0.0098852 | 0 | 0 | 0 | 0 | 0.0093526 | 0.0093526 | 0.0039895 | 0.0039895 | 0.018345 | 0.018345 | 394 | 190 | NO
2015-10-14 | 0.74879 | 0.74857 | 0 | 0 | 0 | 0 | 1.1384 | 1.1383 | 0.17479 | 0.17387 | 0.65497 | 0.65488 | 0.014716 | 0.01471 | 0 | 0 | 0 | 0 | 0.011516 | 0.011512 | 0.0014036 | 0.0013934 | 0.03567 | 0.035661 | 0.0071013 | 0.0071013 | 0 | 0 | 0 | 0 | 0.0073451 | 0.0073451 | 0.0078958 | 0.0078958 | 0.0078904 | 0.0078904 | 350 | 140 | NO
2015-10-15 | 0.60682 | 0.45967 | 0 | 0 | 0.086129 | 0 | 0.05165 | 0.05165 | 1.0394 | 1.0389 | 1.4895 | 0.9096 | 0.0036247 | 0.0035692 | 0 | 0 | 5.9073e-05 | 0 | 0.00017632 | 0.00017632 | 0.0048403 | 0.0048301 | 0.010325 | 0.010118 | 0.012555 | 0.012555 | 0 | 0 | 0 | 0 | 0.010245 | 0.010245 | 0.023946 | 0.023946 | 0.011216 | 0.011216 | 199 | 116 | NO
2015-10-16 | 0.12868 | 0.12836 | 0 | 0 | 0 | 0 | 0.0083531 | 0.0081194 | 0.092281 | 0.092281 | 0.42712 | 0.42628 | 0.00041514 | 0.00040897 | 0 | 0 | 0 | 0 | 0.00014871 | 0.00014021 | 0.00080224 | 0.00080224 | 0.00073264 | 0.00072436 | 0.0016703 | 0.0016703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0067241 | 0.0067241 | 137 | 104 | NO
2015-10-17 | 2.6825 | 2.6823 | 0 | 0 | 0 | 0 | 1.6582 | 1.6577 | 1.6852 | 1.6851 | 6.2051 | 6.2051 | 0.022909 | 0.022902 | 0 | 0 | 0 | 0 | 0.023635 | 0.023627 | 0.0063808 | 0.0063706 | 0.04101 | 0.04101 | 0.033345 | 0.033345 | 0 | 0 | 0 | 0 | 0.014302 | 0.014302 | 0.023795 | 0.023795 | 0.087125 | 0.087125 | 295 | 153 | NO
2015-10-18 | 0.57901 | 0.54921 | 0 | 0 | 0.032077 | 0.032077 | 0.064921 | 0.064921 | 2.3032 | 2.2589 | 0.33715 | 0.25306 | 0.0029856 | 0.0027492 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.0016188 | 0.0016188 | 0.0066483 | 0.0062964 | 0.00348 | 0.0028126 | 0.0080436 | 0.0080436 | 0 | 0 | 0 | 0 | 0.00069839 | 0.00069839 | 0.017344 | 0.017344 | 0.016993 | 0.016993 | 65 | 56 | NO
2015-10-19 | 0.46837 | 0.46833 | 0 | 0 | 0 | 0 | 0.01116 | 0.01116 | 0.26097 | 0.26097 | 1.6527 | 1.6525 | 0.002578 | 0.0025739 | 0 | 0 | 0 | 0 | 0.00028626 | 0.00028626 | 0.0029198 | 0.0029198 | 0.0074588 | 0.0074423 | 0.0093194 | 0.0093194 | 0 | 0 | 0 | 0 | 0.01751 | 0.01751 | 0.0029403 | 0.0029403 | 0.0010224 | 0.0010224 | 215 | 119 | NO
2015-10-20 | 0.038558 | 0.038116 | 0 | 0 | 0 | 0 | 0.0060099 | 0.0052239 | 0.019429 | 0.019327 | 0.1278 | 0.12763 | 0.00032774 | 0.0003154 | 0 | 0 | 0 | 0 | 8.71e-05 | 7.4354e-05 | 0.00023415 | 0.00022391 | 0.0009603 | 0.00094374 | 0.00029484 | 0.00029484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011869 | 0.0011869 | 123 | 85 | NO
2015-10-21 | 0.2261 | 0.22436 | 0 | 0 | 0 | 0 | 0.033412 | 0.033191 | 0.076968 | 0.073518 | 0.78287 | 0.77908 | 0.0011238 | 0.0011135 | 0 | 0 | 0 | 0 | 0.00034415 | 0.0003399 | 0.00098905 | 0.00095834 | 0.0030537 | 0.0030454 | 0.018168 | 0.018168 | 0 | 0 | 0 | 0 | 0.003877 | 0.003877 | 0.0076335 | 0.0076335 | 0.059412 | 0.059412 | 114 | 95 | NO
2015-10-22 | 0.03926 | 0.039044 | 0 | 0 | 0 | 0 | 0.025165 | 0.025165 | 0.085356 | 0.085356 | 0.039982 | 0.039112 | 0.00027916 | 0.0002771 | 0 | 0 | 0 | 0 | 0.00016783 | 0.00016783 | 0.00066406 | 0.00066406 | 0.00025973 | 0.00025146 | 0.00098502 | 0.00098502 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004903 | 0.004903 | 0 | 0 | 85 | 74 | NO
2015-10-23 | 0.056666 | 0.056004 | 0 | 0 | 0 | 0 | 0.0013171 | 0.00048011 | 0.19377 | 0.19377 | 0.068841 | 0.067806 | 0.0002496 | 0.00022184 | 0 | 0 | 0 | 0 | 1.2746e-05 | 8.4976e-06 | 0.00045934 | 0.00045934 | 0.00060846 | 0.00050498 | 0.0048446 | 0.0048446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019503 | 0.019503 | 101 | 67 | NO
2015-10-24 | 0.14248 | 0.14248 | 0 | 0 | 0 | 0 | 0.14079 | 0.14079 | 0.024861 | 0.024861 | 0.27914 | 0.27914 | 0.0010616 | 0.0010616 | 0 | 0 | 0 | 0 | 0.00080939 | 0.00080939 | 0.00017913 | 0.00017913 | 0.0025518 | 0.0025518 | 0.0037144 | 0.0037144 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004903 | 0.004903 | 0.010988 | 0.010988 | 53 | 44 | NO
2015-10-25 | 0.28844 | 0.28844 | 0 | 0 | 0 | 0 | 0.074017 | 0.074017 | 0.069298 | 0.069298 | 0.96092 | 0.96092 | 0.0063584 | 0.0063584 | 0 | 0 | 0 | 0 | 0.00081948 | 0.00081948 | 0.00094683 | 0.00094683 | 0.023234 | 0.023234 | 0.014281 | 0.014281 | 0 | 0 | 0 | 0 | 0.011158 | 0.011158 | 0.0038794 | 0.0038794 | 0.032611 | 0.032611 | 62 | 48 | NO
2015-10-26 | 0.33703 | 0.33594 | 0 | 0 | 0 | 0 | 0.10522 | 0.10518 | 0.33739 | 0.33734 | 0.87887 | 0.87463 | 0.0041398 | 0.0041272 | 0 | 0 | 0 | 0 | 0.00074566 | 0.00073716 | 0.007677 | 0.0076667 | 0.0090038 | 0.0089779 | 0.001357 | 0.001357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054627 | 0.0054627 | 241 | 105 | NO
2015-10-27 | 0.069467 | 0.069446 | 0 | 0 | 0 | 0 | 0.0010027 | 0.0010027 | 0.10694 | 0.10694 | 0.19121 | 0.19113 | 0.00084493 | 0.00084287 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.6995e-05 | 0.00096986 | 0.00096986 | 0.0025839 | 0.0025756 | 0.00098502 | 0.00098502 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004903 | 0.004903 | 0 | 0 | 141 | 62 | NO
2015-10-28 | 1.2981 | 1.2979 | 0 | 0 | 0 | 0 | 0.27447 | 0.27415 | 0.32167 | 0.32136 | 4.4309 | 4.4309 | 0.0091929 | 0.0091868 | 0 | 0 | 0 | 0 | 0.0044548 | 0.0044463 | 0.0044322 | 0.0044219 | 0.024743 | 0.024743 | 0.0081495 | 0.0081495 | 0 | 0 | 0 | 0 | 0.0056456 | 0.0056456 | 0.012737 | 0.012737 | 0.011506 | 0.011506 | 140 | 86 | NO
2015-10-29 | 0.060482 | 0.054311 | 0 | 0 | 0 | 0 | 0.019389 | 0.014344 | 0.14217 | 0.13993 | 0.090721 | 0.077525 | 0.00048223 | 0.00034753 | 0 | 0 | 0 | 0 | 0.00027829 | 1.2746e-05 | 0.0013025 | 0.0012923 | 0.00034562 | 0.00032907 | 0.016388 | 0.016388 | 0 | 0 | 0.17537 | 0.17537 | 0.017715 | 0.017715 | 0 | 0 | 0.0068794 | 0.0068794 | 84 | 71 | NO
2015-10-30 | 0.81108 | 0.81076 | 0 | 0 | 0 | 0 | 0.00042063 | 0.00039938 | 0.014946 | 0.014946 | 3.2522 | 3.251 | 0.0014595 | 0.0014536 | 0 | 0 | 0 | 0 | 1.2746e-05 | 8.4976e-06 | 0.00029812 | 0.00029812 | 0.0056097 | 0.0055941 | 0.0026214 | 0.0026214 | 0 | 0 | 0 | 0 | 0.0036008 | 0.0036008 | 0 | 0 | 0.0035369 | 0.0035369 | 114 | 94 | NO
2015-10-31 | 0.12565 | 0.12563 | 0 | 0 | 0 | 0 | 0.17584 | 0.17579 | 0.071511 | 0.071511 | 0.1054 | 0.1054 | 0.0012596 | 0.0012575 | 0 | 0 | 0 | 0 | 0.0016533 | 0.0016491 | 0.00078433 | 0.00078433 | 0.0012149 | 0.0012149 | 0.00041925 | 0.00041925 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099801 | 0.00099801 | 0.00088062 | 0.00088062 | 89 | 57 | NO
2015-11-01 | 0.079278 | 0.079239 | 0 | 0 | 0 | 0 | 0.0015211 | 0.0014403 | 0.020024 | 0.020024 | 0.29999 | 0.29999 | 0.00039766 | 0.00039355 | 0 | 0 | 0 | 0 | 2.9742e-05 | 2.1244e-05 | 0.00012795 | 0.00012795 | 0.0014394 | 0.0014394 | 0.0016731 | 0.0016731 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023683 | 0.0023683 | 0.0048201 | 0.0048201 | 49 | 46 | NO
2015-11-02 | 0.12046 | 0.11999 | 0 | 0 | 0 | 0 | 0.14295 | 0.14198 | 0.050305 | 0.050305 | 0.16572 | 0.16572 | 0.002325 | 0.002323 | 0 | 0 | 0 | 0 | 0.0024908 | 0.0024866 | 0.00025334 | 0.00025334 | 0.0043017 | 0.0043017 | 0.0099504 | 0.0099504 | 0 | 0 | 0 | 0 | 0.020559 | 0.020559 | 0 | 0 | 0 | 0 | 110 | 76 | NO
2015-11-03 | 0.066761 | 0.066761 | 0 | 0 | 0 | 0 | 0.032278 | 0.032278 | 0.21993 | 0.21993 | 0.027993 | 0.027993 | 0.00084698 | 0.00084698 | 0 | 0 | 0 | 0 | 0.00046312 | 0.00046312 | 0.0029518 | 0.0029518 | 0.00012004 | 0.00012004 | 0.0078773 | 0.0078773 | 0 | 0 | 0 | 0 | 0.016275 | 0.016275 | 0 | 0 | 0 | 0 | 110 | 76 | NO
2015-11-04 | 0.20763 | 0.20672 | 0 | 0 | 0 | 0 | 0.043701 | 0.043536 | 0.58953 | 0.58953 | 0.27391 | 0.27057 | 0.0055788 | 0.0055747 | 0 | 0 | 0 | 0 | 0.0021069 | 0.0021026 | 0.0088643 | 0.0088643 | 0.011184 | 0.011176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 76 | NO
2015-11-05 | 0.15646 | 0.15614 | 0 | 0 | 0 | 0 | 0.078329 | 0.078053 | 0.35251 | 0.3516 | 0.19213 | 0.19213 | 0.0010698 | 0.0010657 | 0 | 0 | 0 | 0 | 0.00086144 | 0.00085719 | 0.0019845 | 0.0019743 | 0.0010234 | 0.0010234 | 0.0071165 | 0.0071165 | 0 | 0 | 0 | 0 | 0.011538 | 0.011538 | 0.00099801 | 0.00099801 | 0.0053603 | 0.0053603 | 110 | 76 | NO
2015-11-06 | 0.40162 | 0.40162 | 0 | 0 | 0 | 0 | 0.028879 | 0.028879 | 0.45654 | 0.45654 | 1.1913 | 1.1913 | 0.0031951 | 0.0031951 | 0 | 0 | 0 | 0 | 0.00034415 | 0.00034415 | 0.0089488 | 0.0089488 | 0.0049546 | 0.0049546 | 0.0026587 | 0.0026587 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004903 | 0.004903 | 0.0067376 | 0.0067376 | 110 | 76 | NO
2015-11-07 | 0.0258 | 0.0258 | 0 | 0 | 0 | 0 | 0.001024 | 0.001024 | 0.1217 | 0.1217 | 0.0034407 | 0.0034407 | 0.00020153 | 0.00020153 | 0 | 0 | 0 | 0 | 1.2746e-05 | 1.2746e-05 | 0.00092763 | 0.00092763 | 3.6218e-05 | 3.6218e-05 | 0.00091125 | 0.00091125 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002527 | 0.002527 | 0.0016246 | 0.0016246 | 110 | 76 | NO
2015-11-08 | 0.090677 | 0.090636 | 0 | 0 | 0 | 0 | 0.099644 | 0.099581 | 0.14021 | 0.14015 | 0.057494 | 0.057494 | 0.00096677 | 0.00096266 | 0 | 0 | 0 | 0 | 0.0012789 | 0.0012746 | 0.0011119 | 0.0011016 | 0.00050084 | 0.00050084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 76 | NO
2015-11-09 | 0.094497 | 0.094402 | 0 | 0 | 0.0027174 | 0 | 0.0024345 | 0.0024345 | 0.026102 | 0.026102 | 0.35418 | 0.35418 | 0.00112 | 0.0011179 | 0 | 0 | 5.9073e-05 | 0 | 2.1244e-05 | 2.1244e-05 | 0.00044782 | 0.00044782 | 0.0040968 | 0.0040968 | 0.0051421 | 0.0051421 | 0 | 0 | 0 | 0 | 0.0062669 | 0.0062669 | 0.00039664 | 0.00039664 | 0.0081687 | 0.0081687 | 110 | 76 | NO
2015-11-10 | 0.023384 | 0.022842 | 0.0032897 | 0.0032897 | 0 | 0 | 0.0040703 | 0.0039386 | 0.051251 | 0.049266 | 0.044335 | 0.044012 | 0.00023803 | 0.00022363 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 3.8239e-05 | 2.1244e-05 | 0.00055274 | 0.00053227 | 0.00042841 | 0.00042013 | 0.0025273 | 0.0025273 | 0 | 0 | 0 | 0 | 0.00032025 | 0.00032025 | 0.006226 | 0.006226 | 0.0045148 | 0.0045148 | 110 | 76 | NO
2015-11-11 | 0.3043 | 0.30426 | 0 | 0 | 0 | 0 | 0.0017006 | 0.0016581 | 0.14792 | 0.14792 | 1.102 | 1.102 | 0.0015349 | 0.0015307 | 0 | 0 | 0 | 0 | 3.5052e-05 | 3.0804e-05 | 0.0020331 | 0.0020331 | 0.0044662 | 0.0044579 | 0.0047683 | 0.0047683 | 0 | 0 | 0 | 0 | 0.0050125 | 0.0050125 | 0 | 0 | 0.0094291 | 0.0094291 | 110 | 76 | NO
2015-11-12 | 0.13037 | 0.13032 | 0 | 0 | 0 | 0 | 0.056146 | 0.056083 | 0.061089 | 0.061089 | 0.36601 | 0.36593 | 0.0020387 | 0.0020325 | 0 | 0 | 0 | 0 | 0.00098465 | 0.00097616 | 0.0012322 | 0.0012322 | 0.005292 | 0.0052837 | 0.01231 | 0.01231 | 0 | 0 | 0 | 0 | 0.0025583 | 0.0025583 | 0.0075836 | 0.0075836 | 0.03844 | 0.03844 | 110 | 76 | NO
2015-11-13 | 0.66314 | 0.64426 | 0 | 0 | 0 | 0 | 0.2724 | 0.23344 | 1.7765 | 1.7765 | 0.70206 | 0.70197 | 0.010339 | 0.0040522 | 0 | 0 | 0 | 0 | 0.014153 | 0.0011684 | 0.011947 | 0.011947 | 0.0043824 | 0.0043741 | 0.021828 | 0.021828 | 0 | 0 | 0 | 0 | 0.011949 | 0.011949 | 0.079275 | 0.079275 | 0.00047497 | 0.00047497 | 110 | 76 | NO
2015-11-14 | 0.058323 | 0.058313 | 0 | 0 | 0 | 0 | 0.010816 | 0.010816 | 0.20974 | 0.20969 | 0.044083 | 0.044083 | 0.00033545 | 0.0003334 | 0 | 0 | 0 | 0 | 4.7799e-05 | 4.7799e-05 | 0.00088285 | 0.00087261 | 0.00054327 | 0.00054327 | 0.0046544 | 0.0046544 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092981 | 0.0092981 | 0.011217 | 0.011217 | 110 | 76 | NO
2015-11-15 | 0.029922 | 0.029034 | 0 | 0 | 0 | 0 | 0.0028424 | 0.001007 | 0.075201 | 0.075201 | 0.054098 | 0.054098 | 0.00031489 | 0.00031077 | 0 | 0 | 0 | 0 | 2.1244e-05 | 1.2746e-05 | 0.00079201 | 0.00079201 | 0.0005857 | 0.0005857 | 0.010637 | 0.010637 | 0 | 0 | 0 | 0 | 0.0046179 | 0.0046179 | 0.0011835 | 0.0011835 | 0.032866 | 0.032866 | 110 | 76 | NO
2015-11-16 | 0.10668 | 0.10638 | 0 | 0 | 0 | 0 | 0.030861 | 0.030249 | 0.1088 | 0.1088 | 0.28131 | 0.28131 | 0.00097628 | 0.00097217 | 0 | 0 | 0 | 0 | 0.00017632 | 0.00016783 | 0.0013716 | 0.0013716 | 0.0024773 | 0.0024773 | 0.0013182 | 0.0013182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053065 | 0.0053065 | 41 | 32 | NO
2015-11-17 | 0.083132 | 0.080367 | 0 | 0 | 0 | 0 | 0.0010027 | 0.00087525 | 0.29258 | 0.29248 | 0.09608 | 0.085277 | 0.00066114 | 0.00065085 | 0 | 0 | 0 | 0 | 2.9742e-05 | 1.6995e-05 | 0.0022097 | 0.0021995 | 0.00081646 | 0.00080818 | 0.0067275 | 0.0067275 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020298 | 0.020298 | 0.010667 | 0.010667 | 81 | 65 | NO
2015-11-18 | 0.14667 | 0.14633 | 0 | 0 | 0 | 0 | 0.0077731 | 0.0076457 | 0.16004 | 0.16004 | 0.44585 | 0.44475 | 0.0017937 | 0.0017814 | 0 | 0 | 0 | 0 | 0.00018907 | 0.00017632 | 0.0025488 | 0.0025488 | 0.0047911 | 0.0047663 | 0.00047863 | 0.00047863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019268 | 0.0019268 | 79 | 65 | NO
2015-11-19 | 0.32411 | 0.32403 | 0 | 0 | 0 | 0 | 0.063328 | 0.063243 | 0.29174 | 0.29174 | 0.94541 | 0.94525 | 0.0031376 | 0.0031273 | 0 | 0 | 0 | 0 | 0.00029529 | 0.00028254 | 0.0017926 | 0.0017926 | 0.010606 | 0.010589 | 0.0027294 | 0.0027294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010988 | 0.010988 | 101 | 91 | NO
2015-11-20 | 0.42834 | 0.42814 | 0 | 0 | 0 | 0 | 0.069857 | 0.069436 | 0.43553 | 0.43553 | 1.236 | 1.236 | 0.0021849 | 0.0021829 | 0 | 0 | 0 | 0 | 0.00059005 | 0.0005858 | 0.0035608 | 0.0035608 | 0.0047663 | 0.0047663 | 0.0039771 | 0.0039771 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0089194 | 0.0089194 | 0.0087968 | 0.0087968 | 110 | 94 | NO
2015-11-21 | 0.070294 | 0.070283 | 0 | 0 | 0 | 0 | 0.0086717 | 0.0086505 | 0.19746 | 0.19746 | 0.10638 | 0.10638 | 0.00063517 | 0.00063312 | 0 | 0 | 0 | 0 | 0.00012746 | 0.00012321 | 0.0015712 | 0.0015712 | 0.0010379 | 0.0010379 | 0.011326 | 0.011326 | 0 | 0 | 0 | 0 | 0.006251 | 0.006251 | 0.015537 | 0.015537 | 0.020848 | 0.020848 | 58 | 51 | NO
2015-11-22 | 0.5606 | 0.56024 | 0 | 0 | 0 | 0 | 1.103 | 1.1023 | 0.10597 | 0.10576 | 0.022007 | 0.022007 | 0.00098296 | 0.00097474 | 0 | 0 | 0 | 0 | 0.0012513 | 0.0012428 | 0.001538 | 0.0015175 | 0.00027526 | 0.00027526 | 0.0020528 | 0.0020528 | 0 | 0 | 0 | 0 | 0.00021934 | 0.00021934 | 0.0025283 | 0.0025283 | 0.0057918 | 0.0057918 | 12 | 12 | NO
2015-11-23 | 0.083363 | 0.082676 | 0 | 0 | 0 | 0 | 0.024084 | 0.022992 | 0.22392 | 0.22313 | 0.10757 | 0.10757 | 0.00068144 | 0.00067733 | 0 | 0 | 0 | 0 | 0.00028254 | 0.00027829 | 0.0016544 | 0.0016441 | 0.00085475 | 0.00085475 | 0.0028476 | 0.0028476 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014155 | 0.014155 | 1.5522e-05 | 1.5522e-05 | 122 | 76 | NO
2015-11-24 | 0.42576 | 0.42478 | 0 | 0 | 0 | 0 | 0.2358 | 0.23386 | 0.23726 | 0.23716 | 1.0626 | 1.0625 | 0.0085179 | 0.0085117 | 0 | 0 | 0 | 0 | 0.0046699 | 0.0046657 | 0.0027714 | 0.0027611 | 0.02295 | 0.022942 | 0.0089143 | 0.0089143 | 0 | 0 | 0 | 0 | 0.0046179 | 0.0046179 | 0.0011835 | 0.0011835 | 0.025931 | 0.025931 | 162 | 121 | NO
2015-11-25 | 2.6319 | 1.9332 | 0 | 0 | 0 | 0 | 0.73072 | 0.73036 | 3.644 | 3.6342 | 6.2244 | 3.4201 | 0.023211 | 0.017638 | 0 | 0 | 0 | 0 | 0.012057 | 0.012049 | 0.026581 | 0.026251 | 0.04845 | 0.026296 | 0.044254 | 0.044254 | 0 | 0 | 0 | 0 | 0.003193 | 0.003193 | 0.076104 | 0.076104 | 0.11038 | 0.11038 | 324 | 208 | NO
2015-11-26 | 0.3941 | 0.3941 | 0 | 0 | 0 | 0 | 0.17663 | 0.17663 | 0.7168 | 0.7168 | 0.66267 | 0.66267 | 0.019173 | 0.019173 | 0 | 0 | 0 | 0 | 0.025762 | 0.025762 | 0.01942 | 0.01942 | 0.011283 | 0.011283 | 0.0043012 | 0.0043012 | 0 | 0 | 0 | 0 | 0.0012215 | 0.0012215 | 0.013057 | 0.013057 | 0.0043751 | 0.0043751 | 168 | 116 | NO
2015-11-27 | 0.18557 | 0.18532 | 0 | 0 | 0 | 0 | 0.090037 | 0.089833 | 0.052759 | 0.051981 | 0.52895 | 0.52895 | 0.0067466 | 0.0067425 | 0 | 0 | 0 | 0 | 0.0032583 | 0.003254 | 0.00076898 | 0.00075874 | 0.020189 | 0.020189 | 0.0032818 | 0.0032818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013211 | 0.013211 | 87 | 76 | NO
2015-11-28 | 0.016707 | 0.015872 | 0 | 0 | 0 | 0 | 0.019793 | 0.019793 | 0.023082 | 0.023082 | 0.010024 | 0.006661 | 8.5341e-05 | 7.8915e-05 | 0 | 0 | 0 | 0 | 7.8602e-05 | 7.8602e-05 | 0.0001126 | 0.0001126 | 9.9341e-05 | 7.3471e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | NO
2015-11-29 | 0.078069 | 0.078069 | 0 | 0 | 0 | 0 | 0.00054809 | 0.00054809 | 0.0078049 | 0.0078049 | 0.3069 | 0.3069 | 0.00095135 | 0.00095135 | 0 | 0 | 0 | 0 | 8.4976e-06 | 8.4976e-06 | 9.5962e-05 | 9.5962e-05 | 0.0037356 | 0.0037356 | 0.0046896 | 0.0046896 | 0 | 0 | 0 | 0 | 0.007037 | 0.007037 | 0 | 0 | 0.0051678 | 0.0051678 | 52 | 48 | NO
2015-11-30 | 0.3562 | 0.35414 | 0 | 0 | 0 | 0 | 0.28678 | 0.28676 | 0.1797 | 0.16954 | 0.72982 | 0.72982 | 0.0076737 | 0.0076632 | 0 | 0 | 0 | 0 | 0.0048478 | 0.0048436 | 0.00077921 | 0.00073699 | 0.020816 | 0.020816 | 0.0087385 | 0.0087385 | 0 | 0 | 0 | 0 | 7.9664e-06 | 7.9664e-06 | 0.013794 | 0.013794 | 0.024006 | 0.024006 | 127 | 93 | NO
2015-12-01 | 0.067961 | 0.06792 | 0 | 0 | 0.0011815 | 0.0011815 | 0.021601 | 0.021558 | 0.020325 | 0.020222 | 0.2149 | 0.2149 | 0.00021001 | 0.0002059 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.00011472 | 0.00011047 | 0.00011899 | 0.00010876 | 0.0005174 | 0.0005174 | 0.0028083 | 0.0028083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011305 | 0.011305 | 81 | 72 | NO
2015-12-02 | 0.13394 | 0.13392 | 0 | 0 | 0 | 0 | 0.25176 | 0.25172 | 0.013161 | 0.013161 | 0.038016 | 0.038016 | 0.0026759 | 0.0026738 | 0 | 0 | 0 | 0 | 0.0053476 | 0.0053434 | 7.4211e-05 | 7.4211e-05 | 0.00029285 | 0.00029285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 93 | NO
2015-12-03 | 0.05287 | 0.047698 | 0 | 0 | 0 | 0 | 0.019653 | 0.0089883 | 0 | 0 | 0.17455 | 0.1745 | 0.00037401 | 0.00024137 | 0 | 0 | 0 | 0 | 0.00044187 | 0.00017208 | 0 | 0 | 0.00064468 | 0.0006364 | 0.0070689 | 0.0070689 | 0.024189 | 0.024189 | 0.066457 | 0.066457 | 0.008232 | 0.008232 | 0 | 0 | 0 | 0 | 99 | 75 | NO
2015-12-04 | 0.2027 | 0.20253 | 0 | 0 | 0 | 0 | 0.014265 | 0.013951 | 0.39633 | 0.39623 | 0.46768 | 0.46768 | 0.0057281 | 0.005722 | 0 | 0 | 0 | 0 | 0.00043762 | 0.00042913 | 0.017557 | 0.017547 | 0.0080073 | 0.0080073 | 0.0026988 | 0.0026988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010864 | 0.010864 | 104 | 95 | NO
2015-12-05 | 0.1321 | 0.13206 | 0 | 0 | 0 | 0 | 0.15487 | 0.15483 | 0.15106 | 0.15096 | 0.10785 | 0.10785 | 0.00062361 | 0.00061949 | 0 | 0 | 0 | 0 | 0.00050401 | 0.00049976 | 0.00091356 | 0.00090332 | 0.00078955 | 0.00078955 | 0.0045513 | 0.0045513 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054187 | 0.0054187 | 0.01394 | 0.01394 | 51 | 48 | NO
2015-12-06 | 0.10574 | 0.10554 | 0 | 0 | 0 | 0 | 0.0031898 | 0.0031473 | 0.43799 | 0.43799 | 0.06523 | 0.064526 | 0.0026109 | 0.0026047 | 0 | 0 | 0 | 0 | 9.9315e-05 | 9.0818e-05 | 0.0074799 | 0.0074799 | 0.0042675 | 0.0042592 | 0.0080051 | 0.0080051 | 0 | 0 | 0 | 0 | 0.0085347 | 0.0085347 | 0.019285 | 0.019285 | 0 | 0 | 42 | 42 | NO
2015-12-07 | 0.79741 | 0.79721 | 0 | 0 | 0 | 0 | 0.005755 | 0.0053853 | 0.094082 | 0.094082 | 3.1228 | 3.1227 | 0.0016446 | 0.0016384 | 0 | 0 | 0 | 0 | 0.00051729 | 0.00050879 | 0.001387 | 0.001387 | 0.004491 | 0.0044828 | 0.0018369 | 0.0018369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073947 | 0.0073947 | 130 | 104 | NO
2015-12-08 | 0.42078 | 0.42071 | 0 | 0 | 0 | 0 | 0.030498 | 0.030498 | 1.9549 | 1.9547 | 0.05345 | 0.053367 | 0.0040334 | 0.0040272 | 0 | 0 | 0 | 0 | 0.0039078 | 0.0039078 | 0.0099366 | 0.0099161 | 0.00058673 | 0.00057845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 83 | NO
2015-12-09 | 1.927 | 1.9269 | 0 | 0 | 0.51748 | 0.51748 | 0.40687 | 0.40683 | 0.05472 | 0.054495 | 6.8479 | 6.8479 | 0.016002 | 0.015996 | 0 | 0 | 0.025904 | 0.025904 | 0.014461 | 0.014456 | 0.00073443 | 0.00071396 | 0.032019 | 0.032019 | 0.0303 | 0.0303 | 0 | 0 | 0 | 0 | 0.030928 | 0.030928 | 0.014605 | 0.014605 | 0.049905 | 0.049905 | 257 | 182 | NO
2015-12-10 | 0.017536 | 0.01675 | 0.0016126 | 0.0016126 | 0 | 0 | 0.0036794 | 0.0020776 | 0.04645 | 0.046398 | 0.02565 | 0.02565 | 0.00035087 | 0.00034676 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 3.8239e-05 | 3.399e-05 | 0.0005489 | 0.00053867 | 0.00088579 | 0.00088579 | 0.0092716 | 0.0092716 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015037 | 0.015037 | 0.025163 | 0.025163 | 95 | 88 | NO
2015-12-11 | 0.033427 | 0.033222 | 0 | 0 | 0 | 0 | 0.042107 | 0.041704 | 0.043383 | 0.043331 | 0.017437 | 0.017437 | 0.00016246 | 0.00015629 | 0 | 0 | 0 | 0 | 0.00010516 | 9.666e-05 | 0.00039153 | 0.00038129 | 0.00013245 | 0.00013245 | 0.019685 | 0.019685 | 0 | 0 | 0 | 0 | 0.016435 | 0.016435 | 0.020732 | 0.020732 | 0.030458 | 0.030458 | 81 | 73 | NO
2015-12-12 | 0.073306 | 0.073306 | 0 | 0 | 0 | 0 | 0.022653 | 0.022653 | 0.16417 | 0.16417 | 0.1182 | 0.1182 | 0.000802 | 0.000802 | 0 | 0 | 0 | 0 | 0.00023315 | 0.00023315 | 0.0017926 | 0.0017926 | 0.0013245 | 0.0013245 | 0.00091921 | 0.00091921 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040829 | 0.0040829 | 0.0003984 | 0.0003984 | 51 | 51 | NO
2015-12-13 | 0.76432 | 0.76429 | 0 | 0 | 0 | 0 | 0.00081151 | 0.00081151 | 1.9107 | 1.9105 | 1.53 | 1.53 | 0.0035499 | 0.0035458 | 0 | 0 | 0 | 0 | 8.4976e-06 | 8.4976e-06 | 0.0089155 | 0.008895 | 0.0070636 | 0.0070636 | 0.018374 | 0.018374 | 0 | 0 | 0 | 0 | 0.0080419 | 0.0080419 | 0.034141 | 0.034141 | 0.030686 | 0.030686 | 65 | 59 | NO
2015-12-14 | 0.022933 | 0.022069 | 0 | 0 | 0 | 0 | 0.0013299 | 0.0013299 | 0.011587 | 0.007288 | 0.080357 | 0.080357 | 0.00024651 | 0.00024446 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.6995e-05 | 0.00014842 | 0.00013819 | 0.00083922 | 0.00083922 | 0.0048331 | 0.0048331 | 0 | 0 | 0 | 0 | 6.6387e-05 | 6.6387e-05 | 0.0060725 | 0.0060725 | 0.014416 | 0.014416 | 85 | 80 | NO
2015-12-15 | 0.23522 | 0.23516 | 0 | 0 | 0 | 0 | 0.043684 | 0.043556 | 0.04858 | 0.04858 | 0.8225 | 0.8225 | 0.0049598 | 0.0049536 | 0 | 0 | 0 | 0 | 0.00029529 | 0.00028254 | 0.00063975 | 0.00063975 | 0.018874 | 0.018874 | 0.014054 | 0.014054 | 0 | 0 | 0 | 0 | 0.012627 | 0.012627 | 0.0087824 | 0.0087824 | 0.02487 | 0.02487 | 121 | 99 | NO
2015-12-16 | 0.32205 | 0.32197 | 0 | 0 | 0 | 0 | 0.058564 | 0.05842 | 0.64348 | 0.64344 | 0.66195 | 0.66195 | 0.010912 | 0.010904 | 0 | 0 | 0 | 0 | 0.0029672 | 0.0029545 | 0.0038654 | 0.0038551 | 0.035022 | 0.035022 | 0.0032738 | 0.0032738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013179 | 0.013179 | 148 | 91 | NO
2015-12-17 | 0.51489 | 0.51456 | 0 | 0 | 0 | 0 | 0.069061 | 0.069018 | 0.62945 | 0.62794 | 1.4291 | 1.4291 | 0.0094109 | 0.0094027 | 0 | 0 | 0 | 0 | 0.0025992 | 0.0025949 | 0.027922 | 0.027892 | 0.010238 | 0.010238 | 0.0096142 | 0.0096142 | 0 | 0 | 0 | 0 | 0.0028913 | 0.0028913 | 0.018389 | 0.018389 | 0.018198 | 0.018198 | 134 | 124 | NO
2015-12-18 | 0.1693 | 0.16911 | 0 | 0 | 0 | 0 | 0.13013 | 0.12989 | 0.1494 | 0.1494 | 0.30716 | 0.30687 | 0.0024114 | 0.0024052 | 0 | 0 | 0 | 0 | 0.0022529 | 0.0022444 | 0.0026345 | 0.0026345 | 0.0031872 | 0.0031789 | 0.0054893 | 0.0054893 | 0 | 0 | 0 | 0 | 0.0019003 | 0.0019003 | 0.00019192 | 0.00019192 | 0.01824 | 0.01824 | 138 | 86 | NO
2015-12-19 | 0.16913 | 0.16913 | 0 | 0 | 0 | 0 | 0.02987 | 0.02987 | 0.20286 | 0.20286 | 0.45861 | 0.45861 | 0.0024898 | 0.0024898 | 0 | 0 | 0 | 0 | 0.00073344 | 0.00073344 | 0.0011362 | 0.0011362 | 0.0076751 | 0.0076751 | 0.0056988 | 0.0056988 | 0 | 0 | 0 | 0 | 0.00057624 | 0.00057624 | 0.0087364 | 0.0087364 | 0.014753 | 0.014753 | 61 | 54 | NO
2015-12-20 | 1.3135 | 1.3135 | 0 | 0 | 0 | 0 | 0.25746 | 0.25746 | 2.9936 | 2.9934 | 2.3651 | 2.365 | 0.013515 | 0.013509 | 0 | 0 | 0 | 0 | 0.0098816 | 0.0098816 | 0.027908 | 0.027888 | 0.012584 | 0.012576 | 0.016467 | 0.016467 | 0 | 0 | 0 | 0 | 0.019422 | 0.019422 | 0.020683 | 0.020683 | 0.011719 | 0.011719 | 134 | 120 | NO
2015-12-21 | 3.0582 | 3.0579 | 0 | 0 | 0 | 0 | 4.3223 | 4.3222 | 1.5584 | 1.558 | 2.6292 | 2.6284 | 0.021604 | 0.021592 | 0 | 0 | 0 | 0 | 0.023533 | 0.023529 | 0.023626 | 0.023595 | 0.022012 | 0.021996 | 0.029592 | 0.029592 | 0 | 0 | 0 | 0 | 0.04056 | 0.04056 | 0.025275 | 0.025275 | 0.019657 | 0.019657 | 138 | 122 | NO
2015-12-22 | 0.078095 | 0.077922 | 0 | 0 | 0 | 0 | 0.11493 | 0.11458 | 0.066827 | 0.066827 | 0.036398 | 0.036398 | 0.0028913 | 0.0028893 | 0 | 0 | 0 | 0 | 0.0056264 | 0.0056222 | 0.00028533 | 0.00028533 | 0.000446 | 0.000446 | 0.012158 | 0.012158 | 0 | 0 | 0 | 0 | 0.0067285 | 0.0067285 | 0.01682 | 0.01682 | 0.022231 | 0.022231 | 98 | 85 | NO
2015-12-23 | 0.82808 | 0.82788 | 0.5644 | 0.5644 | 0 | 0 | 0.00031866 | 0.00031866 | 0.54329 | 0.54329 | 2.8211 | 2.8203 | 0.0064404 | 0.0064384 | 0.0080629 | 0.0080629 | 0 | 0 | 8.4976e-06 | 8.4976e-06 | 0.0056323 | 0.0056323 | 0.02032 | 0.020312 | 0.013724 | 0.013724 | 0 | 0 | 0 | 0 | 0.013834 | 0.013834 | 0.025235 | 0.025235 | 0.0078841 | 0.0078841 | 127 | 120 | NO
2015-12-24 | 0.12075 | 0.090287 | 0 | 0 | 0 | 0 | 0.034366 | 0.033992 | 0.42437 | 0.27364 | 0.075927 | 0.075927 | 0.0012372 | 0.0011205 | 0 | 0 | 0 | 0 | 0.00054119 | 0.00051145 | 0.0039767 | 0.0034674 | 0.00070987 | 0.00070987 | 0.0046012 | 0.0046012 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066841 | 0.0066841 | 0.013117 | 0.013117 | 63 | 59 | NO
2015-12-25 | 2.3386 | 2.3382 | 0 | 0 | 0 | 0 | 0.54611 | 0.54548 | 0.90304 | 0.90304 | 7.6198 | 7.6198 | 0.011146 | 0.011115 | 0 | 0 | 0 | 0 | 0.0078454 | 0.0077816 | 0.0085713 | 0.0085713 | 0.022652 | 0.022652 | 0.0090042 | 0.0090042 | 0 | 0 | 0 | 0 | 0.0040682 | 0.0040682 | 0.004143 | 0.004143 | 0.024971 | 0.024971 | 136 | 100 | NO
2015-12-26 | 0.74523 | 0.7452 | 0 | 0 | 0 | 0 | 0.085432 | 0.085389 | 0.10844 | 0.10844 | 2.7459 | 2.7459 | 0.0081827 | 0.0081807 | 0 | 0 | 0 | 0 | 0.0079606 | 0.0079564 | 0.0012526 | 0.0012526 | 0.016417 | 0.016417 | 0.034137 | 0.034137 | 0 | 0 | 0 | 0 | 0.020061 | 0.020061 | 0.051471 | 0.051471 | 0.056708 | 0.056708 | 101 | 91 | NO
2015-12-27 | 0.57768 | 0.57711 | 0 | 0 | 0 | 0 | 0.28576 | 0.2852 | 0.45082 | 0.45082 | 1.4042 | 1.403 | 0.023897 | 0.023891 | 0 | 0 | 0 | 0 | 0.0064438 | 0.0064395 | 0.023325 | 0.023325 | 0.064781 | 0.064764 | 0.015301 | 0.015301 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028672 | 0.028672 | 0.038407 | 0.038407 | 94 | 83 | NO
2015-12-28 | 0.059867 | 0.054212 | 0 | 0 | 0 | 0 | 0.019272 | 0.019272 | 0.10706 | 0.078913 | 0.11687 | 0.11687 | 0.00052593 | 0.00047452 | 0 | 0 | 0 | 0 | 0.00012746 | 0.00012746 | 0.0013435 | 0.0010876 | 0.00078231 | 0.00078231 | 0.018724 | 0.018724 | 0 | 0 | 0 | 0 | 0.0097902 | 0.0097902 | 0.050531 | 0.050531 | 0.015434 | 0.015434 | 61 | 53 | NO
2015-12-29 | 0.42073 | 0.42035 | 0 | 0 | 0.00029537 | 0 | 0.011085 | 0.010851 | 1.0955 | 1.0942 | 0.78611 | 0.78611 | 0.0077365 | 0.0077303 | 0 | 0 | 5.9073e-05 | 0 | 0.00018907 | 0.00018482 | 0.013857 | 0.013847 | 0.019561 | 0.019561 | 0.0051701 | 0.0051701 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0042172 | 0.0042172 | 0.017402 | 0.017402 | 81 | 72 | NO
2015-12-30 | 0.44119 | 0.44119 | 0 | 0 | 0 | 0 | 0.027413 | 0.027413 | 0.80107 | 0.80107 | 1.0748 | 1.0748 | 0.010453 | 0.010453 | 0 | 0 | 0 | 0 | 0.00055234 | 0.00055234 | 0.018505 | 0.018505 | 0.026039 | 0.026039 | 0.0044987 | 0.0044987 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010594 | 0.010594 | 0.0095419 | 0.0095419 | 68 | 58 | NO
2015-12-31 | 0.87955 | 0.87955 | 0 | 0 | 0 | 0 | 0.13646 | 0.13646 | 1.5786 | 1.5786 | 1.9982 | 1.9982 | 0.015039 | 0.015039 | 0 | 0 | 0 | 0 | 0.0046391 | 0.0046391 | 0.02233 | 0.02233 | 0.033442 | 0.033442 | 0.012748 | 0.012748 | 0 | 0 | 0 | 0 | 0.0002204 | 0.0002204 | 0.042468 | 0.042468 | 0.016542 | 0.016542 | 133 | 109 | NO
2016-01-01 | 0.78401 | 0.78396 | 0 | 0 | 0 | 0 | 0.7588 | 0.7588 | 0.095267 | 0.095165 | 1.6006 | 1.6006 | 0.011185 | 0.011181 | 0 | 0 | 0 | 0 | 0.011362 | 0.011362 | 0.0023645 | 0.0023543 | 0.020979 | 0.02097 | 0.031686 | 0.031686 | 0 | 0 | 0 | 0 | 0.010895 | 0.010895 | 0.032321 | 0.032321 | 0.080189 | 0.080189 | 124 | 110 | NO
2016-01-02 | 0.94563 | 0.9456 | 0 | 0 | 0 | 0 | 0.26628 | 0.26628 | 1.0919 | 1.0917 | 2.4049 | 2.4049 | 0.014184 | 0.01418 | 0 | 0 | 0 | 0 | 0.0073663 | 0.0073663 | 0.031604 | 0.031583 | 0.017187 | 0.017187 | 0.0077213 | 0.0077213 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010424 | 0.010424 | 0.022653 | 0.022653 | 77 | 73 | NO
2016-01-03 | 1.2681 | 1.2681 | 0 | 0 | 0 | 0 | 2.5572 | 2.5572 | 0.054307 | 0.054307 | 0.078606 | 0.078606 | 0.0028995 | 0.0028995 | 0 | 0 | 0 | 0 | 0.0054857 | 0.0054857 | 0.00034035 | 0.00034035 | 0.00070884 | 0.00070884 | 0.0031964 | 0.0031964 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0051321 | 0.0051321 | 0.0087172 | 0.0087172 | 55 | 52 | NO
2016-01-04 | 0.85826 | 0.18751 | 0 | 0 | 0 | 0 | 0.054467 | 0.053277 | 2.5997 | 0.13687 | 1.2464 | 0.54035 | 0.0026096 | 0.0007637 | 0 | 0 | 0 | 0 | 0.00030379 | 0.00029104 | 0.0081939 | 0.0014279 | 0.0032865 | 0.0013525 | 0.0034712 | 0.0034712 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006766 | 0.006766 | 0.0085019 | 0.0085019 | 150 | 124 | NO
2016-01-05 | 0.23279 | 0.23263 | 0 | 0 | 0 | 0 | 0.20525 | 0.20497 | 0.19882 | 0.19872 | 0.37643 | 0.37639 | 0.0046112 | 0.004601 | 0 | 0 | 0 | 0 | 0.005243 | 0.0052302 | 0.0049772 | 0.004967 | 0.0043224 | 0.0043141 | 0.0050503 | 0.0050503 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00089565 | 0.00089565 | 0.019606 | 0.019606 | 172 | 131 | NO
2016-01-06 | 0.79054 | 0.789 | 0 | 0 | 0 | 0 | 0.0032673 | 0.0031611 | 0.22255 | 0.22255 | 2.9961 | 2.9901 | 0.0053071 | 0.0052693 | 0 | 0 | 0 | 0 | 2.5493e-05 | 2.1244e-05 | 0.0012066 | 0.0012066 | 0.020339 | 0.020195 | 0.013491 | 0.013491 | 0 | 0 | 0.012553 | 0.012553 | 0.0057242 | 0.0057242 | 0.0027586 | 0.0027586 | 0.039165 | 0.039165 | 118 | 102 | NO
2016-01-07 | 0.317 | 0.31668 | 0 | 0 | 0 | 0 | 0.25813 | 0.25813 | 0.7829 | 0.78278 | 0.14002 | 0.1388 | 0.0057477 | 0.0057389 | 0 | 0 | 0 | 0 | 0.009001 | 0.009001 | 0.0035097 | 0.0034866 | 0.0027619 | 0.0027453 | 0.010152 | 0.010152 | 0 | 0 | 0 | 0 | 0.0030538 | 0.0030538 | 0.034798 | 0.034798 | 0.0067738 | 0.0067738 | 130 | 114 | NO
2016-01-08 | 0.10279 | 0.10275 | 0 | 0 | 0 | 0 | 0.0062287 | 0.0062287 | 0.11076 | 0.11076 | 0.31208 | 0.31191 | 0.00055112 | 0.000547 | 0 | 0 | 0 | 0 | 0.00011897 | 0.00011897 | 0.00092507 | 0.00092507 | 0.0012387 | 0.0012221 | 0.0071162 | 0.0071162 | 0 | 0 | 0 | 0 | 0.0010303 | 0.0010303 | 0.02874 | 0.02874 | 0.0033962 | 0.0033962 | 109 | 97 | NO
2016-01-09 | 1.2844 | 1.2844 | 0 | 0 | 0 | 0 | 1.2658 | 1.2657 | 2.4839 | 2.4839 | 0.69539 | 0.69539 | 0.0083603 | 0.0083583 | 0 | 0 | 0 | 0 | 0.0053476 | 0.0053434 | 0.023607 | 0.023607 | 0.0041444 | 0.0041444 | 0.0054605 | 0.0054605 | 0 | 0 | 0 | 0 | 0.0062643 | 0.0062643 | 0.0020037 | 0.0020037 | 0.0081563 | 0.0081563 | 183 | 91 | NO
2016-01-10 | 0.22845 | 0.22823 | 0 | 0 | 0 | 0 | 0.37736 | 0.37732 | 0.069125 | 0.069125 | 0.12849 | 0.12768 | 0.0016503 | 0.0016462 | 0 | 0 | 0 | 0 | 0.0025604 | 0.0025562 | 0.00041584 | 0.00041584 | 0.0013183 | 0.0013101 | 0.002058 | 0.002058 | 0 | 0 | 0 | 0 | 0.0041723 | 0.0041723 | 0.00019192 | 0.00019192 | 0 | 0 | 55 | 51 | NO
2016-01-11 | 0.31612 | 0.31605 | 0 | 0 | 0 | 0 | 0.61272 | 0.61258 | 0.0083116 | 0.0083116 | 0.072017 | 0.072017 | 0.0026165 | 0.0026145 | 0 | 0 | 0 | 0 | 0.0048181 | 0.0048139 | 3.0708e-05 | 3.0708e-05 | 0.0011207 | 0.0011207 | 0.0071856 | 0.0071856 | 0 | 0 | 0 | 0 | 0.0040682 | 0.0040682 | 0.018393 | 0.018393 | 0.006125 | 0.006125 | 97 | 86 | NO
2016-01-12 | 0.13852 | 0.13759 | 0 | 0 | 0 | 0 | 0.027453 | 0.027411 | 0.062159 | 0.062159 | 0.45388 | 0.4502 | 0.005069 | 0.0050649 | 0 | 0 | 0 | 0 | 0.00024643 | 0.00024218 | 0.00070884 | 0.00070884 | 0.019353 | 0.019345 | 0.0032134 | 0.0032134 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047636 | 0.0047636 | 0.0090835 | 0.0090835 | 96 | 87 | NO
2016-01-13 | 0.89547 | 0.8951 | 0 | 0 | 0 | 0 | 0.018309 | 0.018267 | 1.7627 | 1.761 | 2.1436 | 2.1436 | 0.0060384 | 0.0060281 | 0 | 0 | 0 | 0 | 0.00015827 | 0.00015402 | 0.011376 | 0.011345 | 0.0148 | 0.014791 | 0.02907 | 0.02907 | 0 | 0 | 0 | 0 | 0.011706 | 0.011706 | 0.067936 | 0.067936 | 0.039275 | 0.039275 | 192 | 157 | NO
2016-01-14 | 0.37284 | 0.37194 | 0 | 0 | 0 | 0 | 0.11791 | 0.11759 | 0.75465 | 0.75454 | 0.66086 | 0.65794 | 0.0017819 | 0.0017737 | 0 | 0 | 0 | 0 | 0.00067662 | 0.00067237 | 0.0051397 | 0.0051295 | 0.0016981 | 0.0016816 | 0.01054 | 0.01054 | 0 | 0 | 0 | 0 | 0.0093372 | 0.0093372 | 0.02826 | 0.02826 | 0.0013835 | 0.0013835 | 134 | 114 | NO
2016-01-15 | 0.20092 | 0.20092 | 0 | 0 | 0 | 0 | 0.016574 | 0.016574 | 0.70975 | 0.70975 | 0.20251 | 0.20251 | 0.0014565 | 0.0014565 | 0 | 0 | 0 | 0 | 0.00017686 | 0.00017686 | 0.0038602 | 0.0038602 | 0.0023966 | 0.0023966 | 0.0085272 | 0.0085272 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025811 | 0.025811 | 0.013452 | 0.013452 | 66 | 60 | NO
2016-01-16 | 0.44869 | 0.23079 | 0 | 0 | 0 | 0 | 0.0092963 | 0.0092963 | 0.19994 | 0.19994 | 1.6265 | 0.74925 | 0.0025607 | 0.0010817 | 0 | 0 | 0 | 0 | 0.00016358 | 0.00016358 | 0.0015981 | 0.0015981 | 0.0086975 | 0.0027433 | 0.0024834 | 0.0024834 | 0 | 0 | 0 | 0 | 0.0042859 | 0.0042859 | 0.0020357 | 0.0020357 | 0 | 0 | 72 | 65 | NO
2016-01-17 | 0.4222 | 0.42206 | 0 | 0 | 0.08861 | 0.08861 | 0.28917 | 0.28917 | 0.1298 | 0.1298 | 1.0188 | 1.0182 | 0.012615 | 0.012612 | 0 | 0 | 0.0055381 | 0.0055381 | 0.015596 | 0.015596 | 0.002582 | 0.002582 | 0.017531 | 0.017522 | 0.0050277 | 0.0050277 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00089565 | 0.00089565 | 0.019515 | 0.019515 | 57 | 54 | NO
2016-01-18 | 0.092183 | 0.091852 | 0 | 0 | 0 | 0 | 0.01239 | 0.011779 | 0.052302 | 0.052302 | 0.30466 | 0.30452 | 0.00052464 | 0.00051847 | 0 | 0 | 0 | 0 | 0.00015827 | 0.00015402 | 0.00067685 | 0.00067685 | 0.0012562 | 0.0012397 | 0.0046614 | 0.0046614 | 0 | 0 | 0 | 0 | 0.0061862 | 0.0061862 | 0.0045627 | 0.0045627 | 0.0030216 | 0.0030216 | 97 | 81 | NO
2016-01-19 | 0.15791 | 0.021294 | 0 | 0 | 0 | 0 | 0.0017208 | 0.0011684 | 0.027388 | 0.027388 | 0.61017 | 0.061296 | 0.00065445 | 0.00023109 | 0 | 0 | 0 | 0 | 2.9742e-05 | 2.1244e-05 | 0.00037873 | 0.00037873 | 0.0022704 | 0.00058259 | 0.014274 | 0.014274 | 0 | 0 | 0 | 0 | 0.0028913 | 0.0028913 | 0.025505 | 0.025505 | 0.0312 | 0.0312 | 77 | 75 | NO
2016-01-20 | 0.04477 | 0.043927 | 0 | 0 | 0 | 0 | 0.069523 | 0.067824 | 0.048788 | 0.048686 | 0.0053116 | 0.0053116 | 0.0053444 | 0.005332 | 0 | 0 | 0 | 0 | 0.010137 | 0.010115 | 0.0021137 | 0.0021035 | 5.4844e-05 | 5.4844e-05 | 0.01141 | 0.01141 | 0 | 0 | 0 | 0 | 7.9664e-06 | 7.9664e-06 | 0.011629 | 0.011629 | 0.036512 | 0.036512 | 94 | 90 | NO
2016-01-21 | 0.81338 | 0.81321 | 0 | 0 | 0 | 0 | 0.1473 | 0.14701 | 2.2278 | 2.2278 | 1.1856 | 1.1856 | 0.0095456 | 0.0095353 | 0 | 0 | 0 | 0 | 0.0031133 | 0.0031005 | 0.028833 | 0.028833 | 0.0090421 | 0.0090255 | 0.0079709 | 0.0079709 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028639 | 0.028639 | 0.0089262 | 0.0089262 | 91 | 75 | NO
2016-01-22 | 11.0532 | 0.13912 | 0.95142 | 0.95142 | 0 | 0 | 0.020704 | 0.020415 | 0.4698 | 0.25055 | 43.9541 | 0.19552 | 0.0019397 | 0.00087423 | 0.0080629 | 0.0080629 | 0 | 0 | 0.0004509 | 0.0004424 | 0.0022353 | 0.0010837 | 0.0040875 | 0.00074609 | 0.012608 | 0.012608 | 0 | 0 | 0 | 0 | 0.0073451 | 0.0073451 | 0.024488 | 0.024488 | 0.016639 | 0.016639 | 86 | 80 | NO
2016-01-23 | 0.12934 | 0.12934 | 0 | 0 | 0 | 0 | 0.0008625 | 0.0008625 | 0.10602 | 0.10602 | 0.43325 | 0.43325 | 0.00039303 | 0.00039303 | 0 | 0 | 0 | 0 | 8.4976e-06 | 8.4976e-06 | 0.00064103 | 0.00064103 | 0.0010472 | 0.0010472 | 0.0037702 | 0.0037702 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010326 | 0.010326 | 0.0068266 | 0.0068266 | 38 | 36 | NO
2016-01-24 | 1.1476 | 1.1476 | 0 | 0 | 0 | 0 | 0.28748 | 0.28743 | 0.10753 | 0.10753 | 3.9729 | 3.9729 | 0.0061564 | 0.0061543 | 0 | 0 | 0 | 0 | 0.0052053 | 0.005201 | 0.0027624 | 0.0027624 | 0.012407 | 0.012407 | 0.023664 | 0.023664 | 0 | 0 | 0 | 0 | 0.01405 | 0.01405 | 0.024143 | 0.024143 | 0.048363 | 0.048363 | 68 | 62 | NO
2016-01-25 | 0.35623 | 0.34667 | 0 | 0 | 0 | 0 | 0.13529 | 0.13529 | 1.1371 | 1.0895 | 0.25079 | 0.25079 | 0.0029409 | 0.0028895 | 0 | 0 | 0 | 0 | 0.0019858 | 0.0019858 | 0.0079111 | 0.0076552 | 0.0015719 | 0.0015719 | 0.0058289 | 0.0058289 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017694 | 0.017694 | 0.0091549 | 0.0091549 | 119 | 101 | NO
2016-01-26 | 0.70656 | 0.70579 | 0 | 0 | 0 | 0 | 0.025061 | 0.025061 | 2.5947 | 2.5909 | 0.69702 | 0.69702 | 0.01255 | 0.012548 | 0 | 0 | 0 | 0 | 0.0024712 | 0.0024712 | 0.044739 | 0.044729 | 0.0095253 | 0.0095253 | 0.0073529 | 0.0073529 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011798 | 0.011798 | 0.020059 | 0.020059 | 59 | 54 | NO
2016-01-27 | 0.87319 | 0.87319 | 0 | 0 | 0 | 0 | 0.469 | 0.469 | 0.12017 | 0.12017 | 2.5042 | 2.5042 | 0.011183 | 0.011183 | 0 | 0 | 0 | 0 | 0.0050247 | 0.0050247 | 0.0032166 | 0.0032166 | 0.032628 | 0.032628 | 0.035749 | 0.035749 | 0 | 0 | 0 | 0 | 0.027123 | 0.027123 | 0.037639 | 0.037639 | 0.060627 | 0.060627 | 150 | 140 | NO
2016-01-28 | 23.1033 | 0 | 0 | 0 | 0 | 0 | 12.4961 | 0 | 39.5121 | 0 | 36.7028 | 0 | 0.06653 | 0 | 0 | 0 | 0 | 0 | 0.031988 | 0 | 0.096807 | 0 | 0.12721 | 0 | 0.25034 | 0 | 0 | 0 | 0 | 0 | 0.1173 | 0 | 0.45603 | 0 | 0.41044 | 0 | 0 | 0 | YES
2016-01-29 | 16.9532 | 0 | 0 | 0 | 0 | 0 | 0.4997 | 0 | 40.6016 | 0 | 34.4376 | 0 | 0.042368 | 0 | 0 | 0 | 0 | 0 | 0.0048431 | 0 | 0.068869 | 0 | 0.10542 | 0 | 0.17416 | 0 | 0 | 0 | 0 | 0 | 0.029135 | 0 | 0.25673 | 0 | 0.43672 | 0 | 0 | 0 | YES
2016-01-30 | 2.5587 | 2.5074 | 0 | 0 | 0 | 0 | 0.30175 | 0.19679 | 4.9057 | 4.9037 | 5.7448 | 5.7447 | 0.016503 | 0.016097 | 0 | 0 | 0 | 0 | 0.0049349 | 0.0041091 | 0.014646 | 0.014626 | 0.044973 | 0.044965 | 0.026889 | 0.026889 | 0 | 0 | 0 | 0 | 0.015126 | 0.015126 | 0.058864 | 0.058864 | 0.031168 | 0.031168 | 1365 | 235 | NO
2016-01-31 | 3.0525 | 3.0524 | 0 | 0 | 0 | 0 | 2.0557 | 2.0556 | 5.3372 | 5.337 | 3.9664 | 3.9664 | 0.023476 | 0.023465 | 0 | 0 | 0 | 0 | 0.017222 | 0.017214 | 0.043361 | 0.04334 | 0.02588 | 0.025872 | 0.0049369 | 0.0049369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019874 | 0.019874 | 447 | 190 | NO
2016-02-01 | 0.14164 | 0.14029 | 0 | 0 | 0 | 0 | 0.025019 | 0.022236 | 0.5189 | 0.5189 | 0.10176 | 0.10176 | 0.0022495 | 0.0021127 | 0 | 0 | 0 | 0 | 0.00057783 | 0.00029529 | 0.0074275 | 0.0074275 | 0.0019227 | 0.0019227 | 0.02229 | 0.02229 | 0 | 0 | 0 | 0 | 0.00076106 | 0.00076106 | 0.077304 | 0.077304 | 0.025728 | 0.025728 | 244 | 140 | NO
2016-02-02 | 0.55779 | 0.54693 | 0 | 0 | 0.0044896 | 0 | 0.36486 | 0.36484 | 1.1942 | 1.1869 | 0.56812 | 0.53097 | 0.010652 | 0.010614 | 0 | 0 | 5.9073e-05 | 0 | 0.0049928 | 0.0049886 | 0.01931 | 0.019268 | 0.017527 | 0.017424 | 0.0032612 | 0.0032612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013129 | 0.013129 | 178 | 114 | NO
2016-02-03 | 0.71033 | 0.70989 | 0 | 0 | 0 | 0 | 0.010065 | 0.010002 | 1.8724 | 1.8719 | 1.3256 | 1.3244 | 0.0061458 | 0.0061356 | 0 | 0 | 0 | 0 | 5.2048e-05 | 4.355e-05 | 0.013455 | 0.013445 | 0.013758 | 0.013741 | 0.0044218 | 0.0044218 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065216 | 0.0065216 | 0.012526 | 0.012526 | 159 | 129 | NO
2016-02-04 | 0.36903 | 0.36808 | 0 | 0 | 0 | 0 | 0.40236 | 0.40227 | 0.24414 | 0.24228 | 0.50415 | 0.50201 | 0.010587 | 0.010577 | 0 | 0 | 0 | 0 | 0.010614 | 0.010606 | 0.0035442 | 0.0035237 | 0.019072 | 0.019064 | 0.012135 | 0.012135 | 0 | 0 | 0 | 0 | 0.01408 | 0.01408 | 0.010667 | 0.010667 | 0.012791 | 0.012791 | 113 | 99 | NO
2016-02-05 | 0.083595 | 0.083564 | 0 | 0 | 0 | 0 | 0.039288 | 0.039267 | 0.12614 | 0.12604 | 0.15796 | 0.15796 | 0.00065162 | 0.00064751 | 0 | 0 | 0 | 0 | 0.0006097 | 0.00060545 | 0.00063847 | 0.00062823 | 0.0009189 | 0.0009189 | 0.0077493 | 0.0077493 | 0 | 0 | 0 | 0 | 0.00069733 | 0.00069733 | 0.029524 | 0.029524 | 0.0059594 | 0.0059594 | 95 | 93 | NO
2016-02-06 | 0.12709 | 0.12707 | 0 | 0 | 0 | 0 | 0.051222 | 0.051222 | 0.19689 | 0.19684 | 0.25259 | 0.25255 | 0.0013035 | 0.0012994 | 0 | 0 | 0 | 0 | 0.00054756 | 0.00054756 | 0.00031092 | 0.00030068 | 0.0039291 | 0.0039209 | 0.0092621 | 0.0092621 | 0 | 0 | 0 | 0 | 0.00057624 | 0.00057624 | 0.0087364 | 0.0087364 | 0.029098 | 0.029098 | 53 | 51 | NO
2016-02-07 | 0.56194 | 0.5619 | 0 | 0 | 0 | 0 | 0.27698 | 0.27689 | 1.3676 | 1.3676 | 0.61646 | 0.61646 | 0.004238 | 0.0042298 | 0 | 0 | 0 | 0 | 0.0012555 | 0.0012385 | 0.011276 | 0.011276 | 0.0054948 | 0.0054948 | 0.0097045 | 0.0097045 | 0 | 0 | 0 | 0 | 0.0012215 | 0.0012215 | 0.020463 | 0.020463 | 0.020137 | 0.020137 | 89 | 73 | NO
2016-02-08 | 0.6351 | 0.6351 | 0 | 0 | 0 | 0 | 0.4029 | 0.4029 | 1.7796 | 1.7796 | 0.33245 | 0.33245 | 0.014242 | 0.014242 | 0 | 0 | 0 | 0 | 0.018132 | 0.018132 | 0.02462 | 0.02462 | 0.0020934 | 0.0020934 | 0.0090582 | 0.0090582 | 0 | 0 | 0 | 0 | 0.0085347 | 0.0085347 | 0.020212 | 0.020212 | 0.0034893 | 0.0034893 | 156 | 137 | NO
2016-02-09 | 0.059259 | 0.059208 | 0 | 0 | 0 | 0 | 0.089442 | 0.089442 | 0.032291 | 0.032239 | 0.038172 | 0.038006 | 0.00047169 | 0.00046552 | 0 | 0 | 0 | 0 | 0.00053269 | 0.00053269 | 0.00052715 | 0.00051692 | 0.00043462 | 0.00041806 | 0.0024317 | 0.0024317 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036069 | 0.0036069 | 0.0068721 | 0.0068721 | 87 | 75 | NO
2016-02-10 | 0.15005 | 0.14934 | 0 | 0 | 0 | 0 | 0.17185 | 0.17151 | 0.17026 | 0.17026 | 0.1315 | 0.12932 | 0.00077475 | 0.00077064 | 0 | 0 | 0 | 0 | 0.00065431 | 0.00065006 | 0.00093787 | 0.00093787 | 0.0010855 | 0.0010772 | 0.026771 | 0.026771 | 0 | 0 | 0 | 0 | 0.046313 | 0.046313 | 0.0024758 | 0.0024758 | 0.015531 | 0.015531 | 117 | 104 | NO
2016-02-11 | 0.064034 | 0.064014 | 0 | 0 | 0 | 0 | 0.012268 | 0.012268 | 0.14968 | 0.14958 | 0.11282 | 0.11282 | 0.00059122 | 0.00058916 | 0 | 0 | 0 | 0 | 0.00015933 | 0.00015933 | 0.00073955 | 0.00072931 | 0.0014715 | 0.0014715 | 0.0072332 | 0.0072332 | 0 | 0 | 0 | 0 | 0.0042859 | 0.0042859 | 0.010103 | 0.010103 | 0.012597 | 0.012597 | 101 | 89 | NO
2016-02-12 | 0.70329 | 0.70259 | 0 | 0 | 0 | 0 | 1.363 | 1.3629 | 0.091236 | 0.089884 | 0.10163 | 0.10026 | 0.0025242 | 0.002514 | 0 | 0 | 0 | 0 | 0.0044378 | 0.0044293 | 0.0010761 | 0.0010556 | 0.00064468 | 0.0006364 | 0.016991 | 0.016991 | 0 | 0 | 0 | 0 | 0.018195 | 0.018195 | 0.017743 | 0.017743 | 0.018598 | 0.018598 | 96 | 78 | NO
2016-02-13 | 0.074408 | 0.074262 | 0 | 0 | 0 | 0 | 0.00164 | 0.00164 | 0.034457 | 0.034457 | 0.26848 | 0.26789 | 0.00069352 | 0.00069147 | 0 | 0 | 0 | 0 | 1.2746e-05 | 1.2746e-05 | 0.00047853 | 0.00047853 | 0.00238 | 0.0023718 | 0.0022556 | 0.0022556 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097152 | 0.0097152 | 0.0012231 | 0.0012231 | 60 | 56 | NO
2016-02-14 | 0.57574 | 0.47219 | 3.2473 | 0 | 0 | 0 | 0.015648 | 0.015648 | 1.4926 | 1.4926 | 0.66333 | 0.66323 | 0.0047524 | 0.004557 | 0.0060472 | 0 | 0 | 0 | 0.0003314 | 0.0003314 | 0.014184 | 0.014184 | 0.0062378 | 0.0062274 | 0.0094096 | 0.0094096 | 0 | 0 | 0 | 0 | 0.0042663 | 0.0042663 | 0.0037783 | 0.0037783 | 0.026512 | 0.026512 | 77 | 68 | NO
2016-02-15 | 1.3473 | 1.3423 | 0 | 0 | 0 | 0 | 0.74199 | 0.74155 | 2.6867 | 2.6825 | 1.8052 | 1.7892 | 0.021285 | 0.021273 | 0 | 0 | 0 | 0 | 0.013616 | 0.013608 | 0.027912 | 0.027892 | 0.036582 | 0.036566 | 0.040179 | 0.040179 | 0.072566 | 0.072566 | 0.011076 | 0.011076 | 0.0056748 | 0.0056748 | 0.060871 | 0.060871 | 0.090596 | 0.090596 | 231 | 171 | NO
2016-02-16 | 0.057195 | 0.057148 | 0 | 0 | 0 | 0 | 0.0052164 | 0.0051612 | 0.052376 | 0.052274 | 0.17772 | 0.17772 | 0.00064109 | 0.00063697 | 0 | 0 | 0 | 0 | 0.00029476 | 0.00029051 | 0.0008611 | 0.00085086 | 0.0013101 | 0.0013101 | 0.018875 | 0.018875 | 0.18948 | 0.18948 | 0.029537 | 0.029537 | 0.0070561 | 0.0070561 | 0.021339 | 0.021339 | 0.016521 | 0.016521 | 89 | 82 | NO
2016-02-17 | 0.19553 | 0.17709 | 0 | 0 | 0 | 0 | 0.022501 | 0.022459 | 0.29556 | 0.21151 | 0.50427 | 0.49807 | 0.001594 | 0.001321 | 0 | 0 | 0 | 0 | 0.00022943 | 0.00022518 | 0.0022685 | 0.0010326 | 0.0041351 | 0.004044 | 0.053103 | 0.053103 | 0.090708 | 0.090708 | 0 | 0 | 0.023601 | 0.023601 | 0.019064 | 0.019064 | 0.14073 | 0.14073 | 129 | 84 | NO
2016-02-18 | 0.32302 | 0.32278 | 0 | 0 | 0.0090973 | 0.0090973 | 0.16596 | 0.16596 | 0.79984 | 0.79984 | 0.32886 | 0.32788 | 0.012039 | 0.012035 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.0051745 | 0.0051745 | 0.036467 | 0.036467 | 0.0088827 | 0.0088662 | 0.031077 | 0.031077 | 0.048377 | 0.048377 | 0.16688 | 0.16688 | 0.034377 | 0.034377 | 0.015168 | 0.015168 | 0.016264 | 0.016264 | 91 | 70 | NO
2016-02-19 | 0.21988 | 0.21842 | 0 | 0 | 0 | 0 | 0.012698 | 0.012698 | 0.5928 | 0.59265 | 0.381 | 0.37522 | 0.0037296 | 0.0037172 | 0 | 0 | 0 | 0 | 0.00017579 | 0.00017579 | 0.0087517 | 0.0087415 | 0.0075934 | 0.007552 | 0.0064039 | 0.0064039 | 0 | 0 | 0 | 0 | 0.0072649 | 0.0072649 | 0.0080672 | 0.0080672 | 0.0051005 | 0.0051005 | 116 | 95 | NO
2016-02-20 | 0.029217 | 0.029176 | 0 | 0 | 0 | 0 | 0.010864 | 0.010864 | 0.056119 | 0.056119 | 0.051065 | 0.0509 | 0.00032774 | 0.00032363 | 0 | 0 | 0 | 0 | 0.00024218 | 0.00024218 | 0.00078945 | 0.00078945 | 0.00020903 | 0.00019247 | 0.011802 | 0.011802 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030874 | 0.0030874 | 0.045013 | 0.045013 | 58 | 51 | NO
2016-02-21 | 0.16827 | 0.16822 | 0 | 0 | 0 | 0 | 0.01268 | 0.012595 | 0.087377 | 0.087377 | 0.58201 | 0.58201 | 0.0015127 | 0.0015107 | 0 | 0 | 0 | 0 | 0.00013224 | 0.00012799 | 0.00097242 | 0.00097242 | 0.0050457 | 0.0050457 | 0.0082801 | 0.0082801 | 0 | 0 | 0 | 0 | 0.0044378 | 0.0044378 | 0.0036222 | 0.0036222 | 0.021757 | 0.021757 | 46 | 44 | NO
2016-02-22 | 0.2092 | 0.20916 | 0 | 0 | 0 | 0 | 0.045144 | 0.045101 | 0.38087 | 0.38076 | 0.44618 | 0.44618 | 0.0035378 | 0.0035337 | 0 | 0 | 0 | 0 | 0.0046901 | 0.0046859 | 0.0029236 | 0.0029134 | 0.0027391 | 0.0027391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 121 | NO
2016-02-23 | 0.69026 | 0.67918 | 0 | 0 | 0 | 0 | 1.2197 | 1.2191 | 0.41403 | 0.41201 | 0.067399 | 0.025601 | 0.0060019 | 0.0046274 | 0 | 0 | 0 | 0 | 0.0075426 | 0.0075256 | 0.0046535 | 0.0046433 | 0.0057018 | 0.00021006 | 0.033688 | 0.033688 | 0.076606 | 0.076606 | 0.044674 | 0.044674 | 0.0073451 | 0.0073451 | 0.00097625 | 0.00097625 | 0.10442 | 0.10442 | 82 | 71 | NO
2016-02-24 | 0.35318 | 0.32537 | 0 | 0 | 0 | 0 | 0.11237 | 0.056653 | 0.0095924 | 0.0095924 | 1.1951 | 1.1917 | 0.0011169 | 0.0010904 | 0 | 0 | 0 | 0 | 0.00022678 | 0.00017632 | 0.00011388 | 0.00011388 | 0.0039623 | 0.003954 | 0.0071154 | 0.0071154 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0032256 | 0.0032256 | 0.026036 | 0.026036 | 119 | 106 | NO
2016-02-25 | 0.30559 | 0.30536 | 0 | 0 | 0 | 0 | 0.46229 | 0.4619 | 0.058735 | 0.058633 | 0.28195 | 0.28186 | 0.006909 | 0.0069008 | 0 | 0 | 0 | 0 | 0.013189 | 0.01318 | 0.00049005 | 0.00047981 | 0.0017198 | 0.0017116 | 0.0071383 | 0.0071383 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011622 | 0.011622 | 0.019337 | 0.019337 | 148 | 114 | NO
2016-02-26 | 0.46538 | 0.46473 | 0 | 0 | 0 | 0 | 0.4328 | 0.43214 | 0.46572 | 0.46551 | 0.65354 | 0.65237 | 0.0072612 | 0.007247 | 0 | 0 | 0 | 0 | 0.0099639 | 0.0099554 | 0.0033779 | 0.0033574 | 0.0070853 | 0.0070615 | 0.014192 | 0.014192 | 0.012094 | 0.012094 | 0.014768 | 0.014768 | 0.0084073 | 0.0084073 | 0.025475 | 0.025475 | 0.016528 | 0.016528 | 160 | 142 | NO
2016-02-27 | 0.12318 | 0.12318 | 0 | 0 | 0 | 0 | 0.016532 | 0.016532 | 0.0047904 | 0.0047904 | 0.45979 | 0.45979 | 0.0034828 | 0.0034828 | 0 | 0 | 0 | 0 | 0.00017579 | 0.00017579 | 7.4211e-05 | 7.4211e-05 | 0.013618 | 0.013618 | 0.0046794 | 0.0046794 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078958 | 0.0078958 | 0.012452 | 0.012452 | 34 | 33 | NO
2016-02-28 | 0.19756 | 0.19756 | 0 | 0 | 0 | 0 | 0.24993 | 0.24993 | 0.037694 | 0.037694 | 0.27787 | 0.27787 | 0.0060754 | 0.0060754 | 0 | 0 | 0 | 0 | 0.01061 | 0.01061 | 0.0018847 | 0.0018847 | 0.002261 | 0.002261 | 0.00026219 | 0.00026219 | 0 | 0 | 0 | 0 | 0.00021934 | 0.00021934 | 0 | 0 | 0.00062812 | 0.00062812 | 36 | 33 | NO
2016-02-29 | 0.37126 | 0.37119 | 0 | 0 | 0.0008861 | 0.0008861 | 0.0061267 | 0.0060418 | 0.56798 | 0.56798 | 1.0231 | 1.023 | 0.0035419 | 0.0035357 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.00028254 | 0.00027405 | 0.0058921 | 0.0058921 | 0.0089345 | 0.0089262 | 0.0040483 | 0.0040483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016297 | 0.016297 | 97 | 86 | NO
2016-03-01 | 0.58071 | 0.5804 | 0 | 0 | 0 | 0 | 0.281 | 0.281 | 2.1204 | 2.1189 | 0.075319 | 0.075319 | 0.0071609 | 0.0071589 | 0 | 0 | 0 | 0 | 0.0063275 | 0.0063275 | 0.019945 | 0.019935 | 0.00036839 | 0.00036839 | 0.03558 | 0.03558 | 0 | 0 | 0 | 0 | 0.014584 | 0.014584 | 0.09027 | 0.09027 | 0.041811 | 0.041811 | 153 | 138 | NO
2016-03-02 | 0.12376 | 0.12366 | 0 | 0 | 0 | 0 | 0.074774 | 0.074608 | 0.34996 | 0.34996 | 0.069493 | 0.06941 | 0.00062155 | 0.00061744 | 0 | 0 | 0 | 0 | 0.00044559 | 0.00044134 | 0.0014445 | 0.0014445 | 0.00046566 | 0.00045738 | 0.0013626 | 0.0013626 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065267 | 0.0065267 | 0.00020696 | 0.00020696 | 110 | 87 | NO
2016-03-03 | 0.13419 | 0.13395 | 0 | 0 | 0 | 0 | 0.069593 | 0.069572 | 0.27949 | 0.27833 | 0.17857 | 0.17857 | 0.012378 | 0.012372 | 0 | 0 | 0 | 0 | 0.0099049 | 0.0099007 | 0.032663 | 0.032642 | 0.0041154 | 0.0041154 | 0.0014613 | 0.0014613 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025449 | 0.0025449 | 0.0038246 | 0.0038246 | 93 | 72 | NO
2016-03-04 | 0.98586 | 0.98567 | 0 | 0 | 0 | 0 | 0.0014913 | 0.0010877 | 0.049145 | 0.049145 | 3.9261 | 3.9261 | 0.0018497 | 0.0018456 | 0 | 0 | 0 | 0 | 2.1244e-05 | 1.2746e-05 | 0.00071652 | 0.00071652 | 0.0068255 | 0.0068255 | 0.0042272 | 0.0042272 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011567 | 0.0011567 | 0.016082 | 0.016082 | 84 | 80 | NO
2016-03-05 | 0.014295 | 0.014295 | 0 | 0 | 0.0043124 | 0.0043124 | 0.001024 | 0.001024 | 0.013403 | 0.013403 | 0.044108 | 0.044108 | 0.0001239 | 0.0001239 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 1.2746e-05 | 1.2746e-05 | 0.00015994 | 0.00015994 | 0.00033631 | 0.00033631 | 0.0026427 | 0.0026427 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062567 | 0.0062567 | 0.0055786 | 0.0055786 | 41 | 41 | NO
2016-03-06 | 0.065517 | 0.06548 | 0 | 0 | 0 | 0 | 0.031581 | 0.031505 | 0.081924 | 0.081924 | 0.13596 | 0.13596 | 0.00065882 | 0.00065677 | 0 | 0 | 0 | 0 | 0.00029104 | 0.00028679 | 0.0010287 | 0.0010287 | 0.0012531 | 0.0012531 | 0.0064358 | 0.0064358 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013725 | 0.013725 | 0.014808 | 0.014808 | 68 | 48 | NO
2016-03-07 | 0.16917 | 0.16911 | 0 | 0 | 0 | 0 | 0.084712 | 0.084666 | 0.078822 | 0.078668 | 0.4522 | 0.4522 | 0.0046696 | 0.0046634 | 0 | 0 | 0 | 0 | 0.0044331 | 0.0044288 | 0.0034572 | 0.0034367 | 0.0073647 | 0.0073647 | 0.054551 | 0.054551 | 0 | 0 | 0 | 0 | 0.062923 | 0.062923 | 0.042653 | 0.042653 | 0.062508 | 0.062508 | 102 | 85 | NO
2016-03-08 | 0.81521 | 0.81487 | 0 | 0 | 0 | 0 | 1.0779 | 1.0772 | 0.3698 | 0.3698 | 0.88248 | 0.88248 | 0.0059351 | 0.0059309 | 0 | 0 | 0 | 0 | 0.0070307 | 0.0070222 | 0.002353 | 0.002353 | 0.0082908 | 0.0082908 | 0.0026556 | 0.0026556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010691 | 0.010691 | 113 | 88 | NO
2016-03-09 | 1.7548 | 1.7513 | 0.0018061 | 0.0018061 | 0 | 0 | 1.526 | 1.526 | 0.88214 | 0.88214 | 3.377 | 3.3633 | 0.013398 | 0.013392 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 0.006985 | 0.0069765 | 0.0087389 | 0.0087389 | 0.033251 | 0.033243 | 0.042633 | 0.042633 | 0 | 0 | 0 | 0 | 0.022001 | 0.022001 | 0.083122 | 0.083122 | 0.061533 | 0.061533 | 289 | 211 | NO
2016-03-10 | 2.4319 | 2.4313 | 0 | 0 | 2.0434 | 2.0434 | 2.5381 | 2.5368 | 3.1168 | 3.1168 | 2.0376 | 2.0376 | 0.024522 | 0.024514 | 0 | 0 | 0.025904 | 0.025904 | 0.025529 | 0.025516 | 0.035361 | 0.035361 | 0.016749 | 0.016741 | 0.025909 | 0.025909 | 0 | 0 | 0 | 0 | 0.022407 | 0.022407 | 0.045474 | 0.045474 | 0.023866 | 0.023866 | 221 | 140 | NO
2016-03-11 | 1.8829 | 1.8824 | 0 | 0 | 1.0079 | 1.0079 | 3.2914 | 3.2914 | 0.84867 | 0.84857 | 0.33923 | 0.33723 | 0.013745 | 0.013734 | 0 | 0 | 0.025845 | 0.025845 | 0.021234 | 0.02123 | 0.0035992 | 0.003589 | 0.0074257 | 0.0074009 | 0.0069021 | 0.0069021 | 0 | 0 | 0 | 0 | 0.012505 | 0.012505 | 0.003557 | 0.003557 | 0.00054327 | 0.00054327 | 105 | 73 | NO
2016-03-12 | 0.29022 | 0.29022 | 0 | 0 | 0 | 0 | 0.00044612 | 0.00044612 | 0.58791 | 0.58791 | 0.69198 | 0.69198 | 0.0032221 | 0.0032221 | 0 | 0 | 0 | 0 | 8.4976e-06 | 8.4976e-06 | 0.005164 | 0.005164 | 0.0087782 | 0.0087782 | 0.010322 | 0.010322 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027926 | 0.027926 | 0.018969 | 0.018969 | 47 | 41 | NO
2016-03-13 | 0.042297 | 0.042005 | 0 | 0 | 0 | 0 | 0.025809 | 0.025809 | 0.13241 | 0.13241 | 0.012898 | 0.011722 | 0.00047477 | 0.00047272 | 0 | 0 | 0 | 0 | 0.00038451 | 0.00038451 | 0.0012936 | 0.0012936 | 0.0001159 | 0.00010762 | 0.027732 | 0.027732 | 0 | 0 | 0 | 0 | 0.015138 | 0.015138 | 0.053348 | 0.053348 | 0.039 | 0.039 | 52 | 52 | NO
2016-03-14 | 0.089925 | 0.089914 | 0 | 0 | 0 | 0 | 0.061484 | 0.061484 | 0.16735 | 0.16735 | 0.10687 | 0.10683 | 0.00078092 | 0.00077886 | 0 | 0 | 0 | 0 | 0.00022518 | 0.00022518 | 0.0017567 | 0.0017567 | 0.0012842 | 0.0012759 | 0.015255 | 0.015255 | 0 | 0 | 0 | 0 | 0.0045717 | 0.0045717 | 0.027785 | 0.027785 | 0.030032 | 0.030032 | 52 | 51 | NO
2016-03-15 | 0.99506 | 0.99323 | 0 | 0 | 0.020262 | 0.020262 | 0.11806 | 0.11806 | 2.7083 | 2.6993 | 1.5826 | 1.5825 | 0.0078653 | 0.007847 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.0046296 | 0.0046296 | 0.013798 | 0.013717 | 0.011475 | 0.011467 | 0.012555 | 0.012555 | 0 | 0 | 0 | 0 | 8.7631e-05 | 8.7631e-05 | 0.034667 | 0.034667 | 0.022335 | 0.022335 | 189 | 152 | NO
2016-03-16 | 0.76645 | 0.76483 | 0.0059988 | 0.0059988 | 0 | 0 | 0.0013893 | 0.00073079 | 0.91478 | 0.91276 | 2.3421 | 2.3385 | 0.0024153 | 0.002407 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 8.4976e-06 | 4.2488e-06 | 0.0046778 | 0.0046676 | 0.0059149 | 0.0058984 | 0.0035046 | 0.0035046 | 0 | 0 | 0 | 0 | 0.0030591 | 0.0030591 | 0.0042594 | 0.0042594 | 0.0047032 | 0.0047032 | 90 | 85 | NO
2016-03-17 | 0.12221 | 0.1222 | 0 | 0 | 0 | 0 | 0.013133 | 0.013133 | 0.24348 | 0.24342 | 0.26947 | 0.26947 | 0.00070998 | 0.00070792 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.6995e-05 | 0.0018169 | 0.0018066 | 0.0013556 | 0.0013556 | 0.014628 | 0.014628 | 0 | 0 | 0 | 0 | 0.011185 | 0.011185 | 0.026178 | 0.026178 | 0.015922 | 0.015922 | 98 | 81 | NO
2016-03-18 | 2.1009 | 2.0914 | 0 | 0 | 0.099686 | 0.099686 | 0.82489 | 0.82489 | 2.82 | 2.8199 | 4.5556 | 4.5175 | 0.02807 | 0.028062 | 0 | 0 | 0.0055381 | 0.0055381 | 0.014811 | 0.014811 | 0.043928 | 0.043917 | 0.047841 | 0.047816 | 0.056708 | 0.056708 | 0 | 0 | 0 | 0 | 0.018673 | 0.018673 | 0.11222 | 0.11222 | 0.10114 | 0.10114 | 496 | 253 | NO
2016-03-19 | 0.36581 | 0.36517 | 0 | 0 | 0 | 0 | 0.25555 | 0.25555 | 0.082498 | 0.082498 | 0.90796 | 0.9054 | 0.0019646 | 0.0019585 | 0 | 0 | 0 | 0 | 0.0011769 | 0.0011769 | 0.0012258 | 0.0012258 | 0.0046245 | 0.0045997 | 0.0048912 | 0.0048912 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015252 | 0.0015252 | 0.018457 | 0.018457 | 93 | 83 | NO
2016-03-20 | 0.14209 | 0.14199 | 0 | 0 | 0 | 0 | 0.00673 | 0.0065304 | 0.13258 | 0.13258 | 0.45165 | 0.45165 | 0.0010755 | 0.0010734 | 0 | 0 | 0 | 0 | 0.00012321 | 0.00011897 | 0.0010108 | 0.0010108 | 0.003272 | 0.003272 | 0.00087166 | 0.00087166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003509 | 0.003509 | 35 | 33 | NO
2016-03-21 | 0.82003 | 0.81993 | 0 | 0 | 0 | 0 | 0.038118 | 0.03799 | 1.4586 | 1.4584 | 2.0473 | 2.0472 | 0.0026368 | 0.0026265 | 0 | 0 | 0 | 0 | 0.0003484 | 0.00033565 | 0.001671 | 0.0016608 | 0.0085847 | 0.0085764 | 0.020589 | 0.020589 | 0 | 0 | 0 | 0 | 0.015776 | 0.015776 | 0.021722 | 0.021722 | 0.034577 | 0.034577 | 110 | 85 | NO
2016-03-22 | 0.06033 | 0.060207 | 0 | 0 | 0 | 0 | 0.0035902 | 0.0035902 | 0.032369 | 0.032266 | 0.2097 | 0.20928 | 0.0005321 | 0.00052361 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.6995e-05 | 0.00027637 | 0.00026613 | 0.0018854 | 0.0018595 | 0.0018333 | 0.0018333 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0035544 | 0.0035544 | 0.0045055 | 0.0045055 | 95 | 78 | NO
2016-03-23 | 0.58949 | 0.58883 | 0 | 0 | 0 | 0 | 0.0085039 | 0.0085039 | 1.0369 | 1.0337 | 1.5179 | 1.5179 | 0.012364 | 0.012362 | 0 | 0 | 0 | 0 | 0.0042849 | 0.0042849 | 0.022689 | 0.022679 | 0.023074 | 0.023074 | 0.025616 | 0.025616 | 0 | 0 | 0 | 0 | 0.0095072 | 0.0095072 | 0.03057 | 0.03057 | 0.059874 | 0.059874 | 113 | 93 | NO
2016-03-24 | 0.1713 | 0.1713 | 0 | 0 | 0 | 0 | 0.045172 | 0.045172 | 0.16444 | 0.16444 | 0.46857 | 0.46857 | 0.001551 | 0.001551 | 0 | 0 | 0 | 0 | 0.00053057 | 0.00053057 | 0.0015239 | 0.0015239 | 0.0039778 | 0.0039778 | 0.011396 | 0.011396 | 0 | 0 | 0 | 0 | 0.01685 | 0.01685 | 0.0093621 | 0.0093621 | 0.0054762 | 0.0054762 | 107 | 93 | NO
2016-03-25 | 0.1564 | 0.15639 | 0 | 0 | 0 | 0 | 0.0071804 | 0.0071804 | 0.38423 | 0.38423 | 0.30488 | 0.30484 | 0.0061111 | 0.0061091 | 0 | 0 | 0 | 0 | 0.00011047 | 0.00011047 | 0.011307 | 0.011307 | 0.015242 | 0.015233 | 0.010466 | 0.010466 | 0 | 0 | 0 | 0 | 0.00026555 | 0.00026555 | 0.015616 | 0.015616 | 0.028985 | 0.028985 | 46 | 37 | NO
2016-03-26 | 0.84463 | 0.84428 | 0 | 0 | 0 | 0 | 0.62116 | 0.62045 | 2.0013 | 2.0013 | 0.57129 | 0.57129 | 0.0090662 | 0.0090559 | 0 | 0 | 0 | 0 | 0.0041787 | 0.0041574 | 0.02728 | 0.02728 | 0.0062926 | 0.0062926 | 0.0011256 | 0.0011256 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002623 | 0.0002623 | 0.0043193 | 0.0043193 | 66 | 64 | NO
2016-03-27 | 0.22127 | 0.2212 | 0 | 0 | 0 | 0 | 0.00074778 | 0.00059908 | 0 | 0 | 0.8893 | 0.8893 | 0.0017893 | 0.0017749 | 0 | 0 | 0 | 0 | 3.8239e-05 | 8.4976e-06 | 0 | 0 | 0.0071287 | 0.0071287 | 0.0055148 | 0.0055148 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014488 | 0.014488 | 0.010484 | 0.010484 | 44 | 42 | NO
2016-03-28 | 0.075576 | 0.075533 | 0 | 0 | 0 | 0 | 0.062397 | 0.062329 | 0.041539 | 0.041488 | 0.14907 | 0.14907 | 0.00077424 | 0.00077013 | 0 | 0 | 0 | 0 | 0.00080514 | 0.00080089 | 0.00042607 | 0.00041584 | 0.0012035 | 0.0012035 | 0.0055919 | 0.0055919 | 0 | 0 | 0 | 0 | 0.0072649 | 0.0072649 | 0 | 0 | 0.008356 | 0.008356 | 62 | 61 | NO
2016-03-29 | 0.60521 | 0.6045 | 0 | 0 | 0 | 0 | 0.16625 | 0.16595 | 2.1776 | 2.1748 | 0.35126 | 0.35126 | 0.003874 | 0.0038678 | 0 | 0 | 0 | 0 | 0.0010431 | 0.0010388 | 0.013975 | 0.013954 | 0.002261 | 0.002261 | 0.011463 | 0.011463 | 0 | 0 | 0 | 0 | 0.0010303 | 0.0010303 | 0.024803 | 0.024803 | 0.024081 | 0.024081 | 118 | 100 | NO
2016-03-30 | 0.12947 | 0.12933 | 0 | 0 | 0 | 0 | 0.013429 | 0.01314 | 0.15903 | 0.15902 | 0.36642 | 0.36642 | 0.00066319 | 0.00065908 | 0 | 0 | 0 | 0 | 0.00026449 | 0.00026024 | 0.0015405 | 0.0015303 | 0.00090856 | 0.00090856 | 0.017584 | 0.017584 | 0 | 0 | 0 | 0 | 0.00027883 | 0.00027883 | 0.024666 | 0.024666 | 0.050295 | 0.050295 | 105 | 92 | NO
2016-03-31 | 0.43857 | 0.43623 | 0 | 0 | 0 | 0 | 0.8311 | 0.83105 | 0.099621 | 0.089385 | 0.065619 | 0.064592 | 0.0039136 | 0.0038966 | 0 | 0 | 0 | 0 | 0.0076313 | 0.0076271 | 0.00058601 | 0.00052203 | 0.00041185 | 0.00040357 | 0.0042809 | 0.0042809 | 0 | 0 | 0 | 0 | 0.0042769 | 0.0042769 | 0.01008 | 0.01008 | 0.00074816 | 0.00074816 | 155 | 116 | NO
2016-04-01 | 0.39085 | 0.39085 | 0 | 0 | 0 | 0 | 0.07815 | 0.07815 | 0.087215 | 0.087215 | 1.3506 | 1.3506 | 0.003298 | 0.003298 | 0 | 0 | 0 | 0 | 0.0025211 | 0.0025211 | 0.0049721 | 0.0049721 | 0.0043431 | 0.0043431 | 0.011375 | 0.011375 | 0 | 0 | 0 | 0 | 0.0025131 | 0.0025131 | 0.024248 | 0.024248 | 0.021283 | 0.021283 | 104 | 89 | NO
2016-04-02 | 1.2989 | 1.2989 | 0 | 0 | 0 | 0 | 1.922 | 1.922 | 0.62538 | 0.62538 | 0.97829 | 0.97829 | 0.011437 | 0.011437 | 0 | 0 | 0 | 0 | 0.0064576 | 0.0064576 | 0.013224 | 0.013224 | 0.022766 | 0.022766 | 0.018679 | 0.018679 | 0 | 0 | 0 | 0 | 0.0072272 | 0.0072272 | 0.03937 | 0.03937 | 0.029272 | 0.029272 | 117 | 102 | NO
2016-04-03 | 0.039951 | 0.039941 | 0 | 0 | 0 | 0 | 0.018637 | 0.018616 | 0.016141 | 0.016141 | 0.11146 | 0.11146 | 0.00047195 | 0.00046989 | 0 | 0 | 0 | 0 | 0.00022784 | 0.00022359 | 0.00017273 | 0.00017273 | 0.0013163 | 0.0013163 | 0.00061255 | 0.00061255 | 0 | 0 | 0 | 0 | 0.00021934 | 0.00021934 | 0 | 0 | 0.0020386 | 0.0020386 | 35 | 33 | NO
2016-04-04 | 0.065524 | 0.065483 | 0 | 0 | 0 | 0 | 0.039471 | 0.039429 | 0.086784 | 0.086784 | 0.11668 | 0.1166 | 0.00031437 | 0.00031026 | 0 | 0 | 0 | 0 | 0.00012746 | 0.00012321 | 0.00066662 | 0.00066662 | 0.00047808 | 0.0004698 | 0.0029126 | 0.0029126 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013089 | 0.013089 | 0.0011393 | 0.0011393 | 86 | 79 | NO
2016-04-05 | 0.22888 | 0.22879 | 0 | 0 | 0.00059073 | 0 | 0.0010367 | 0.00090499 | 0.25068 | 0.25068 | 0.71653 | 0.71653 | 0.00060921 | 0.0006051 | 0 | 0 | 5.9073e-05 | 0 | 1.6995e-05 | 1.2746e-05 | 0.00081376 | 0.00081376 | 0.001753 | 0.001753 | 0.014305 | 0.014305 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038098 | 0.038098 | 0.026774 | 0.026774 | 104 | 70 | NO
2016-04-06 | 0.0049027 | 0.004656 | 0 | 0 | 0 | 0 | 0.00023368 | 8.0727e-05 | 0.019451 | 0.019451 | 0.0035504 | 0.002855 | 5.2439e-05 | 4.8326e-05 | 0 | 0 | 0 | 0 | 8.4976e-06 | 4.2488e-06 | 0.00015738 | 0.00015738 | 6.7262e-05 | 5.8984e-05 | 0.0032738 | 0.0032738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013179 | 0.013179 | 76 | 55 | NO
2016-04-07 | 1.5545 | 1.5531 | 0 | 0 | 0 | 0 | 0.31266 | 0.30985 | 3.2874 | 3.2874 | 2.9898 | 2.9898 | 0.01317 | 0.013164 | 0 | 0 | 0 | 0 | 0.0055781 | 0.0055654 | 0.041553 | 0.041553 | 0.0085444 | 0.0085444 | 0.020393 | 0.020393 | 0 | 0 | 0 | 0 | 0.0078979 | 0.0078979 | 0.053338 | 0.053338 | 0.023568 | 0.023568 | 126 | 103 | NO
2016-04-08 | 0.02014 | 0.019019 | 0 | 0 | 0 | 0 | 0.0012874 | 0.0012364 | 0.048103 | 0.042647 | 0.039665 | 0.039665 | 0.00015706 | 0.00015089 | 0 | 0 | 0 | 0 | 2.1244e-05 | 1.6995e-05 | 0.00033267 | 0.0003122 | 0.00032182 | 0.00032182 | 0.0042719 | 0.0042719 | 0 | 0 | 0 | 0 | 0.0002204 | 0.0002204 | 0.020537 | 0.020537 | 0.00015832 | 0.00015832 | 87 | 65 | NO
2016-04-09 | 0.32115 | 0.25762 | 0 | 0 | 0 | 0 | 0.11117 | 0.028106 | 0.49757 | 0.40338 | 0.67383 | 0.65611 | 0.0026332 | 0.00067502 | 0 | 0 | 0 | 0 | 0.0027675 | 0.00023421 | 0.0037579 | 0.00080736 | 0.0021689 | 0.0016081 | 0.0089346 | 0.0089346 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021913 | 0.021913 | 0.018246 | 0.018246 | 77 | 71 | NO
2016-04-10 | 0.24686 | 0.24653 | 0 | 0 | 0 | 0 | 0.037572 | 0.037529 | 0.50417 | 0.50258 | 0.51283 | 0.51283 | 0.0088971 | 0.0088909 | 0 | 0 | 0 | 0 | 0.0023166 | 0.0023124 | 0.028265 | 0.028245 | 0.0084429 | 0.0084429 | 0.0077401 | 0.0077401 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014557 | 0.014557 | 0.019386 | 0.019386 | 62 | 49 | NO
2016-04-11 | 0.040823 | 0.040782 | 0 | 0 | 0 | 0 | 0.00292 | 0.0028775 | 0.028533 | 0.028533 | 0.13558 | 0.13549 | 0.00029561 | 0.00028944 | 0 | 0 | 0 | 0 | 4.3019e-05 | 3.4521e-05 | 0.00017273 | 0.00017273 | 0.0009665 | 0.00095823 | 0.0026181 | 0.0026181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010539 | 0.010539 | 86 | 51 | NO
2016-04-12 | 1.0013 | 0.9952 | 0 | 0 | 0.59812 | 0.59812 | 0.45659 | 0.44397 | 0.34849 | 0.34849 | 2.7757 | 2.7756 | 0.017596 | 0.017592 | 0 | 0 | 0.011076 | 0.011076 | 0.011731 | 0.011727 | 0.013789 | 0.013789 | 0.035274 | 0.035266 | 0.0035501 | 0.0035501 | 0 | 0 | 0 | 0 | 0.0034532 | 0.0034532 | 0.0083103 | 0.0083103 | 0.00084233 | 0.00084233 | 146 | 119 | NO
2016-04-13 | 0.29132 | 0.29119 | 0.0041282 | 0.0041282 | 0 | 0 | 0.12861 | 0.12834 | 0.22276 | 0.22276 | 0.74147 | 0.74147 | 0.0060723 | 0.006062 | 6.4503e-05 | 6.4503e-05 | 0 | 0 | 0.0030379 | 0.0030166 | 0.0031898 | 0.0031898 | 0.015938 | 0.015938 | 0.020866 | 0.020866 | 0 | 0 | 0 | 0 | 0.015312 | 0.015312 | 0.037616 | 0.037616 | 0.023744 | 0.023744 | 104 | 97 | NO
2016-04-14 | 0.76786 | 0.7678 | 0 | 0 | 0 | 0 | 0.10892 | 0.10888 | 3.3041 | 3.3039 | 0.20671 | 0.20671 | 0.0077442 | 0.007738 | 0 | 0 | 0 | 0 | 0.00085666 | 0.00085241 | 0.02778 | 0.02776 | 0.0070387 | 0.0070387 | 0.005304 | 0.005304 | 0 | 0 | 0 | 0 | 0.0037777 | 0.0037777 | 0.010438 | 0.010438 | 0.0055496 | 0.0055496 | 95 | 81 | NO
2016-04-15 | 0.12921 | 0.12917 | 0 | 0 | 0 | 0 | 0.029191 | 0.029149 | 0.10643 | 0.10633 | 0.3772 | 0.3772 | 0.00069661 | 0.0006925 | 0 | 0 | 0 | 0 | 0.0003484 | 0.00034415 | 0.000911 | 0.00090076 | 0.0013887 | 0.0013887 | 0.0056289 | 0.0056289 | 0 | 0 | 0 | 0 | 0.0091141 | 0.0091141 | 0.0036837 | 0.0036837 | 0.0019227 | 0.0019227 | 69 | 55 | NO
2016-04-16 | 0.91249 | 0.91247 | 0 | 0 | 0 | 0 | 0.48871 | 0.48871 | 3.2471 | 3.2471 | 0.095075 | 0.094992 | 0.0049966 | 0.0049945 | 0 | 0 | 0 | 0 | 0.0026576 | 0.0026576 | 0.017205 | 0.017205 | 0.0010213 | 0.0010131 | 0.0026181 | 0.0026181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010539 | 0.010539 | 66 | 65 | NO
2016-04-17 | 0.39375 | 0.39323 | 0 | 0 | 0.52058 | 0.52058 | 0.18332 | 0.18332 | 0.23443 | 0.23184 | 0.96537 | 0.96537 | 0.0056685 | 0.0056664 | 0 | 0 | 0.011076 | 0.011076 | 0.0011758 | 0.0011758 | 0.0046663 | 0.0046561 | 0.015202 | 0.015202 | 0.011996 | 0.011996 | 0 | 0 | 0 | 0 | 0.0051203 | 0.0051203 | 0.031856 | 0.031856 | 0.012551 | 0.012551 | 90 | 78 | NO
2016-04-18 | 0.16331 | 0.16294 | 0 | 0 | 0 | 0 | 0.1271 | 0.12643 | 0.1143 | 0.1141 | 0.31734 | 0.31734 | 0.0011477 | 0.0011395 | 0 | 0 | 0 | 0 | 0.0011482 | 0.0011397 | 0.00083039 | 0.00080992 | 0.0017116 | 0.0017116 | 0.0088271 | 0.0088271 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02056 | 0.02056 | 0.018907 | 0.018907 | 138 | 103 | NO
2016-04-19 | 0.088035 | 0.079449 | 0 | 0 | 0 | 0 | 0.0010027 | 0.00096022 | 0.28347 | 0.24099 | 0.12318 | 0.12306 | 0.00074468 | 0.0006871 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.2746e-05 | 0.0021956 | 0.0019397 | 0.001189 | 0.0011724 | 0.0054991 | 0.0054991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022137 | 0.022137 | 71 | 54 | NO
2016-04-20 | 2.449 | 2.1788 | 0 | 0 | 0 | 0 | 0.70656 | 0.70524 | 8.8891 | 8.1076 | 1.2929 | 0.84001 | 0.014896 | 0.013774 | 0 | 0 | 0 | 0 | 0.0053492 | 0.0053317 | 0.053203 | 0.049394 | 0.0065172 | 0.005115 | 0.015796 | 0.015796 | 0 | 0 | 0 | 0 | 1.3277e-05 | 1.3277e-05 | 0.0067877 | 0.0067877 | 0.058074 | 0.058074 | 230 | 133 | NO
2016-04-21 | 0.14038 | 0.14002 | 0.0039992 | 0 | 0.71995 | 0.71995 | 0.023118 | 0.022646 | 0.23183 | 0.23183 | 0.23117 | 0.23117 | 0.0016274 | 0.0016212 | 6.4503e-05 | 0 | 0.011076 | 0.011076 | 0.00047108 | 0.00046259 | 0.003438 | 0.003438 | 0.0012925 | 0.0012925 | 0.017492 | 0.017492 | 0 | 0 | 0 | 0 | 0.01963 | 0.01963 | 0.0097472 | 0.0097472 | 0.024286 | 0.024286 | 148 | 122 | NO
2016-04-22 | 0.11187 | 0.1117 | 0 | 0 | 0 | 0 | 0.0068267 | 0.0065335 | 0.028789 | 0.028789 | 0.41376 | 0.41367 | 0.00048377 | 0.00047966 | 0 | 0 | 0 | 0 | 9.0818e-05 | 8.6569e-05 | 0.00057577 | 0.00057577 | 0.0013049 | 0.0012966 | 0.0007511 | 0.0007511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030237 | 0.0030237 | 64 | 58 | NO
2016-04-23 | 0.09488 | 0.09488 | 0 | 0 | 0 | 0 | 0.001691 | 0.001691 | 0.082507 | 0.082507 | 0.31193 | 0.31193 | 0.00079583 | 0.00079583 | 0 | 0 | 0 | 0 | 2.1244e-05 | 2.1244e-05 | 0.0015264 | 0.0015264 | 0.0019278 | 0.0019278 | 0.0021266 | 0.0021266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0085609 | 0.0085609 | 55 | 52 | NO
2016-04-24 | 0.13059 | 0.13022 | 0 | 0 | 0.046136 | 0.046136 | 0.0037984 | 0.003501 | 0.014925 | 0.014925 | 0.49976 | 0.49887 | 0.0018359 | 0.0018297 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 3.8239e-05 | 2.9742e-05 | 0.00040304 | 0.00040304 | 0.0069818 | 0.0069735 | 0.010345 | 0.010345 | 0 | 0 | 0 | 0 | 0.0058925 | 0.0058925 | 0.02903 | 0.02903 | 0.0066869 | 0.0066869 | 59 | 55 | NO
2016-04-25 | 0.083713 | 0.071527 | 0 | 0 | 0 | 0 | 0.068628 | 0.068628 | 0.014699 | 0.0045345 | 0.19139 | 0.15056 | 0.0013899 | 0.00088066 | 0 | 0 | 0 | 0 | 0.00027405 | 0.00027405 | 3.0708e-05 | 2.0472e-05 | 0.0050364 | 0.0029947 | 0.0072841 | 0.0072841 | 0 | 0 | 0 | 0 | 0.0039583 | 0.0039583 | 0.0050438 | 0.0050438 | 0.017532 | 0.017532 | 95 | 36 | NO
2016-04-26 | 0.67608 | 0.67566 | 0 | 0 | 0 | 0 | 0.0098901 | 0.0090276 | 2.2272 | 2.2272 | 0.90112 | 0.90112 | 0.0051989 | 0.0051968 | 0 | 0 | 0 | 0 | 5.6296e-05 | 5.2048e-05 | 0.015148 | 0.015148 | 0.0085682 | 0.0085682 | 0.012961 | 0.012961 | 0 | 0 | 0 | 0 | 0.006251 | 0.006251 | 0.039042 | 0.039042 | 0.0084222 | 0.0084222 | 125 | 108 | NO
2016-04-27 | 0.075427 | 0.075427 | 0 | 0 | 0 | 0 | 0.00053959 | 0.00053959 | 0.19117 | 0.19117 | 0.14799 | 0.14799 | 0.00246 | 0.00246 | 0 | 0 | 0 | 0 | 4.2488e-06 | 4.2488e-06 | 0.0058985 | 0.0058985 | 0.0051243 | 0.0051243 | 0.0016793 | 0.0016793 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054187 | 0.0054187 | 0.002378 | 0.002378 | 66 | 59 | NO
2016-04-28 | 0.47112 | 0.47108 | 0 | 0 | 0 | 0 | 0.73557 | 0.73552 | 0.1348 | 0.1348 | 0.35436 | 0.35428 | 0.0040781 | 0.004074 | 0 | 0 | 0 | 0 | 0.0052451 | 0.0052409 | 0.0019039 | 0.0019039 | 0.0046576 | 0.0046494 | 0.006378 | 0.006378 | 0 | 0 | 0 | 0 | 0.011847 | 0.011847 | 0 | 0 | 0.0025922 | 0.0025922 | 103 | 70 | NO
2016-04-29 | 0.20064 | 0.17265 | 0 | 0 | 0 | 0 | 0.22072 | 0.2155 | 0.029858 | 0.029756 | 0.35353 | 0.25109 | 0.0016102 | 0.0014888 | 0 | 0 | 0 | 0 | 0.0024324 | 0.0024282 | 0.00045678 | 0.00044654 | 0.0013732 | 0.00090131 | 0.0043565 | 0.0043565 | 0 | 0 | 0 | 0 | 0.0021244 | 0.0021244 | 0 | 0 | 0.013399 | 0.013399 | 151 | 107 | NO
2016-04-30 | 0.083096 | 0.082664 | 0 | 0 | 0.0023629 | 0 | 0.087306 | 0.086906 | 0.10414 | 0.10346 | 0.079852 | 0.07977 | 0.00061461 | 0.00060638 | 0 | 0 | 5.9073e-05 | 0 | 0.00043762 | 0.00043337 | 0.0014906 | 0.0014804 | 0.00040771 | 0.00039943 | 0.00678 | 0.00678 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065907 | 0.0065907 | 0.021964 | 0.021964 | 79 | 68 | NO
2016-05-01 | 6.0835 | 6.0833 | 0 | 0 | 0 | 0 | 0.89198 | 0.89185 | 14.4313 | 14.4308 | 11.0808 | 11.0807 | 0.046091 | 0.046072 | 0 | 0 | 0 | 0 | 0.008822 | 0.0088093 | 0.083893 | 0.083841 | 0.10051 | 0.1005 | 0.071643 | 0.071643 | 0 | 0 | 0 | 0 | 0.020647 | 0.020647 | 0.099995 | 0.099995 | 0.16731 | 0.16731 | 609 | 259 | NO
2016-05-02 | 3.8775 | 3.8683 | 0 | 0 | 0 | 0 | 0.71729 | 0.71687 | 13.1217 | 13.0922 | 3.5998 | 3.5874 | 0.020189 | 0.020162 | 0 | 0 | 0 | 0 | 0.0073254 | 0.0073127 | 0.051927 | 0.051896 | 0.025004 | 0.024946 | 0.039691 | 0.039691 | 0 | 0 | 0 | 0 | 0.043601 | 0.043601 | 0.06482 | 0.06482 | 0.022404 | 0.022404 | 268 | 182 | NO
2016-05-03 | 27.9987 | 0 | 0 | 0 | 0 | 0 | 14.9111 | 0 | 58.75 | 0 | 36.1458 | 0 | 0.11386 | 0 | 0 | 0 | 0 | 0 | 0.062306 | 0 | 0.19236 | 0 | 0.18139 | 0 | 0.2935 | 0 | 0 | 0 | 0 | 0 | 0.16941 | 0 | 0.5614 | 0 | 0.39741 | 0 | 0 | 0 | YES
2016-05-04 | 0.74533 | 0.74226 | 0 | 0 | 0 | 0 | 0.21239 | 0.21222 | 2.9402 | 2.9253 | 0.2087 | 0.2087 | 0.0095294 | 0.0095109 | 0 | 0 | 0 | 0 | 0.0055101 | 0.0054889 | 0.032417 | 0.032376 | 0.0014084 | 0.0014084 | 0.029508 | 0.029508 | 0 | 0 | 0 | 0 | 0.048657 | 0.048657 | 0.020582 | 0.020582 | 0.0073409 | 0.0073409 | 456 | 269 | NO
2016-05-05 | 0.43849 | 0.42153 | 0 | 0 | 0 | 0 | 0.11912 | 0.11407 | 0.21939 | 0.21584 | 1.3557 | 1.3001 | 0.0021235 | 0.0021091 | 0 | 0 | 0 | 0 | 0.00054544 | 0.00053269 | 0.00062695 | 0.00060648 | 0.0069787 | 0.0069621 | 0.007455 | 0.007455 | 0 | 0 | 0 | 0 | 0.00083117 | 0.00083117 | 0.024638 | 0.024638 | 0.0084657 | 0.0084657 | 209 | 180 | NO
2016-05-06 | 0.61232 | 0.61224 | 0 | 0 | 0 | 0 | 0.58004 | 0.57992 | 0.68656 | 0.68656 | 0.77958 | 0.7795 | 0.0073208 | 0.0073126 | 0 | 0 | 0 | 0 | 0.0077991 | 0.0077864 | 0.0080634 | 0.0080634 | 0.0077538 | 0.0077455 | 0.011203 | 0.011203 | 0 | 0 | 0 | 0 | 0.00083117 | 0.00083117 | 0.024638 | 0.024638 | 0.023555 | 0.023555 | 125 | 117 | NO
2016-05-07 | 0.24205 | 0.24201 | 0 | 0 | 0 | 0 | 0.016963 | 0.016963 | 0.19981 | 0.19961 | 0.77976 | 0.77976 | 0.0033517 | 0.0033476 | 0 | 0 | 0 | 0 | 0.00017208 | 0.00017208 | 0.0065357 | 0.0065152 | 0.0078717 | 0.0078717 | 0.0040221 | 0.0040221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0080595 | 0.0080595 | 0.0096733 | 0.0096733 | 79 | 68 | NO
2016-05-08 | 0.43754 | 0.43731 | 0 | 0 | 0 | 0 | 0.80565 | 0.80525 | 0.20203 | 0.20203 | 0.028232 | 0.028108 | 0.0049323 | 0.0049261 | 0 | 0 | 0 | 0 | 0.0099172 | 0.0099129 | 0.00050284 | 0.00050284 | 0.00012625 | 0.00010969 | 0.006335 | 0.006335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039613 | 0.0039613 | 0.022299 | 0.022299 | 61 | 58 | NO
2016-05-09 | 0.17098 | 0.17048 | 0 | 0 | 0 | 0 | 0.25812 | 0.25712 | 0.1235 | 0.1235 | 0.085492 | 0.085451 | 0.0072815 | 0.0072733 | 0 | 0 | 0 | 0 | 0.013318 | 0.013305 | 0.0026985 | 0.0026985 | 0.0011817 | 0.0011735 | 0.013463 | 0.013463 | 0 | 0 | 0 | 0 | 0.015332 | 0.015332 | 0.0052562 | 0.0052562 | 0.020075 | 0.020075 | 232 | 177 | NO
2016-05-10 | 2.488 | 2.4866 | 0 | 0 | 0 | 0 | 0.52328 | 0.52204 | 1.5802 | 1.5775 | 7.7183 | 7.7172 | 0.020539 | 0.020527 | 0 | 0 | 0 | 0 | 0.004133 | 0.0041287 | 0.0061019 | 0.006061 | 0.069695 | 0.069687 | 0.013833 | 0.013833 | 0 | 0 | 0 | 0 | 0.0024085 | 0.0024085 | 0.033141 | 0.033141 | 0.024192 | 0.024192 | 294 | 189 | NO
2016-05-11 | 1.1642 | 1.1608 | 0 | 0 | 0 | 0 | 0.63727 | 0.63656 | 1.4136 | 1.3987 | 2.3017 | 2.3016 | 0.014168 | 0.014156 | 0 | 0 | 0 | 0 | 0.0014541 | 0.0014456 | 0.029488 | 0.029468 | 0.030355 | 0.030338 | 0.018546 | 0.018546 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048112 | 0.048112 | 0.035748 | 0.035748 | 245 | 147 | NO
2016-05-12 | 5.148 | 5.0768 | 0 | 0 | 0 | 0 | 0.62684 | 0.6263 | 8.7561 | 8.7561 | 12.4212 | 12.1357 | 0.024184 | 0.023982 | 0 | 0 | 0 | 0 | 0.0044421 | 0.0043954 | 0.049861 | 0.049861 | 0.048378 | 0.047654 | 0.044844 | 0.044844 | 0 | 0 | 0 | 0 | 0.00333 | 0.00333 | 0.10553 | 0.10553 | 0.088692 | 0.088692 | 431 | 259 | NO
2016-05-13 | 5.5958 | 5.5948 | 1.4513 | 1.4513 | 1.1852 | 1.1852 | 0.94714 | 0.94515 | 4.7088 | 4.7087 | 16.521 | 16.5208 | 0.023349 | 0.023333 | 0.012094 | 0.012094 | 0.011076 | 0.011076 | 0.0047453 | 0.0047241 | 0.024154 | 0.024144 | 0.06211 | 0.062093 | 0.042946 | 0.042946 | 0 | 0 | 0 | 0 | 0.0052207 | 0.0052207 | 0.048004 | 0.048004 | 0.12389 | 0.12389 | 453 | 354 | NO
2016-05-14 | 0.80765 | 0.80739 | 0 | 0 | 0 | 0 | 0.40493 | 0.40493 | 2.086 | 2.086 | 0.77533 | 0.77427 | 0.008494 | 0.0084878 | 0 | 0 | 0 | 0 | 0.0048489 | 0.0048489 | 0.021485 | 0.021485 | 0.0073699 | 0.007345 | 0.0094767 | 0.0094767 | 0.012094 | 0.012094 | 0.011076 | 0.011076 | 0.00097987 | 0.00097987 | 0.032151 | 0.032151 | 0.0071339 | 0.0071339 | 156 | 127 | NO
2016-05-15 | 2.1009 | 2.0972 | 0 | 0 | 0 | 0 | 0.48192 | 0.48013 | 1.3471 | 1.3466 | 6.4289 | 6.4181 | 0.016573 | 0.016549 | 0 | 0 | 0 | 0 | 0.0084742 | 0.0084657 | 0.016944 | 0.016934 | 0.036501 | 0.036432 | 0.035073 | 0.035073 | 0 | 0 | 0 | 0 | 0.02074 | 0.02074 | 0.026656 | 0.026656 | 0.079224 | 0.079224 | 204 | 170 | NO
2016-05-16 | 0.65578 | 0.60896 | 1.4513 | 0 | 0 | 0 | 0.70514 | 0.70514 | 1.0711 | 1.0697 | 0.21347 | 0.21243 | 0.013695 | 0.012892 | 0.024189 | 0 | 0 | 0 | 0.010332 | 0.010332 | 0.032408 | 0.032378 | 0.0056852 | 0.0055817 | 0.02678 | 0.02678 | 0 | 0 | 0 | 0 | 0.010616 | 0.010616 | 0.043183 | 0.043183 | 0.052201 | 0.052201 | 198 | 170 | NO
2016-05-17 | 0.40837 | 0.38994 | 0 | 0 | 0 | 0 | 0.014114 | 0.013859 | 0.90253 | 0.90243 | 0.88651 | 0.81293 | 0.0063029 | 0.0062217 | 0 | 0 | 0 | 0 | 0.00011047 | 0.00010622 | 0.0079149 | 0.0079047 | 0.018757 | 0.018446 | 0.010375 | 0.010375 | 0 | 0 | 0 | 0 | 0.0037225 | 0.0037225 | 0.0031463 | 0.0031463 | 0.03197 | 0.03197 | 229 | 191 | NO
2016-05-18 | 0.19552 | 0.19547 | 0 | 0 | 0 | 0 | 0.0014881 | 0.0014371 | 0.18474 | 0.18474 | 0.63478 | 0.6347 | 0.0022628 | 0.0022546 | 0 | 0 | 0 | 0 | 5.6296e-05 | 4.355e-05 | 0.0064359 | 0.0064359 | 0.0037946 | 0.0037863 | 0.0033972 | 0.0033972 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065446 | 0.0065446 | 0.0083829 | 0.0083829 | 90 | 76 | NO
2016-05-19 | 1.4265 | 1.4262 | 0 | 0 | 0 | 0 | 0.071106 | 0.07049 | 0.92537 | 0.92526 | 4.8557 | 4.8557 | 0.014064 | 0.014002 | 0 | 0 | 0 | 0 | 0.0013203 | 0.0012013 | 0.021813 | 0.021792 | 0.036403 | 0.036403 | 0.022184 | 0.022184 | 0 | 0 | 0 | 0 | 0.0098232 | 0.0098232 | 0.047551 | 0.047551 | 0.031709 | 0.031709 | 206 | 150 | NO
2016-05-20 | 0.42272 | 0.41957 | 0 | 0 | 0 | 0 | 0.07538 | 0.075316 | 0.7866 | 0.77103 | 0.91871 | 0.91871 | 0.0090711 | 0.0090649 | 0 | 0 | 0 | 0 | 0.0025949 | 0.0025864 | 0.028949 | 0.028938 | 0.0080487 | 0.0080487 | 0.011828 | 0.011828 | 0 | 0 | 0 | 0 | 0.0046179 | 0.0046179 | 0.0011835 | 0.0011835 | 0.03766 | 0.03766 | 121 | 95 | NO
2016-05-21 | 0.16987 | 0.16987 | 0 | 0 | 0 | 0 | 0.047792 | 0.047792 | 0.46267 | 0.46267 | 0.21654 | 0.21654 | 0.0050588 | 0.0050588 | 0 | 0 | 0 | 0 | 0.00046099 | 0.00046099 | 0.015062 | 0.015062 | 0.007285 | 0.007285 | 0.012643 | 0.012643 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028755 | 0.028755 | 0.027638 | 0.027638 | 53 | 50 | NO
2016-05-22 | 0.11428 | 0.11428 | 0 | 0 | 0 | 0 | 0.00040363 | 0.00040363 | 0.45748 | 0.45748 | 0.089257 | 0.089257 | 0.0011768 | 0.0011768 | 0 | 0 | 0 | 0 | 4.2488e-06 | 4.2488e-06 | 0.0044411 | 0.0044411 | 0.0011372 | 0.0011372 | 0.010414 | 0.010414 | 0 | 0 | 0 | 0 | 0.011203 | 0.011203 | 0.004697 | 0.004697 | 0.016297 | 0.016297 | 51 | 50 | NO
2016-05-23 | 0.29482 | 0.29391 | 0 | 0 | 0 | 0 | 0.0038111 | 0.0033438 | 0.23761 | 0.2358 | 0.98727 | 0.98595 | 0.0033519 | 0.0033437 | 0 | 0 | 0 | 0 | 5.4703e-05 | 5.0454e-05 | 0.0078331 | 0.0078126 | 0.0070522 | 0.0070439 | 0.012572 | 0.012572 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032252 | 0.032252 | 0.024526 | 0.024526 | 145 | 107 | NO
2016-05-24 | 0.068374 | 0.068311 | 0 | 0 | 0.00059073 | 0 | 0.0075458 | 0.0074566 | 0.11699 | 0.11699 | 0.16585 | 0.16585 | 0.00061692 | 0.0006087 | 0 | 0 | 5.9073e-05 | 0 | 0.00023793 | 0.00022518 | 0.00095322 | 0.00095322 | 0.0012407 | 0.0012407 | 0.0021523 | 0.0021523 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049823 | 0.0049823 | 0.0046349 | 0.0046349 | 134 | 112 | NO
2016-05-25 | 0.11037 | 0.11001 | 0 | 0 | 0 | 0 | 0.058845 | 0.058144 | 0.23261 | 0.23261 | 0.14155 | 0.14147 | 0.0011225 | 0.0011123 | 0 | 0 | 0 | 0 | 0.0005226 | 0.0005056 | 0.0017478 | 0.0017478 | 0.0020872 | 0.0020789 | 0.0028515 | 0.0028515 | 0 | 0 | 0 | 0 | 8.6569e-05 | 8.6569e-05 | 0.0098675 | 0.0098675 | 0.00333 | 0.00333 | 114 | 97 | NO
2016-05-26 | 0.17146 | 0.17128 | 0 | 0 | 0.091918 | 0.091918 | 0.086146 | 0.086104 | 0.16129 | 0.16113 | 0.37907 | 0.37853 | 0.0014937 | 0.0014855 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.00045834 | 0.00045409 | 0.0021777 | 0.0021572 | 0.0033507 | 0.0033424 | 0.0017973 | 0.0017973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072353 | 0.0072353 | 121 | 101 | NO
2016-05-27 | 0.23802 | 0.23741 | 0 | 0 | 0 | 0 | 0.0036624 | 0.0024048 | 1.0997 | 1.0997 | 0.0617 | 0.0617 | 0.001049 | 0.0010449 | 0 | 0 | 0 | 0 | 5.2048e-05 | 4.355e-05 | 0.0048019 | 0.0048019 | 0.000238 | 0.000238 | 0.0052778 | 0.0052778 | 0 | 0 | 0 | 0 | 0.0071448 | 0.0071448 | 0.0024963 | 0.0024963 | 0.0053065 | 0.0053065 | 112 | 97 | NO
2016-05-28 | 0.015205 | 0.015205 | 0 | 0 | 0 | 0 | 0.0011684 | 0.0011684 | 0.068037 | 0.068037 | 0.0039064 | 0.0039064 | 8.2513e-05 | 8.2513e-05 | 0 | 0 | 0 | 0 | 1.6995e-05 | 1.6995e-05 | 0.00022263 | 0.00022263 | 0.000119 | 0.000119 | 0.0024659 | 0.0024659 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002527 | 0.002527 | 0.0078831 | 0.0078831 | 39 | 37 | NO
2016-05-29 | 0.069358 | 0.069216 | 0 | 0 | 0 | 0 | 0.02098 | 0.020687 | 0.13716 | 0.13716 | 0.1274 | 0.1274 | 0.00072463 | 0.00072257 | 0 | 0 | 0 | 0 | 0.00028254 | 0.00027829 | 0.002138 | 0.002138 | 0.00063744 | 0.00063744 | 0.0019484 | 0.0019484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078438 | 0.0078438 | 70 | 66 | NO
2016-05-30 | 0.37867 | 0.37865 | 0 | 0 | 0 | 0 | 0.12229 | 0.12228 | 0.71001 | 0.71001 | 0.71191 | 0.71183 | 0.0098222 | 0.0098181 | 0 | 0 | 0 | 0 | 0.0053752 | 0.005371 | 0.031799 | 0.031799 | 0.0033497 | 0.0033414 | 0.0015942 | 0.0015942 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011515 | 0.0011515 | 0.0054865 | 0.0054865 | 126 | 116 | NO
2016-05-31 | 0.080431 | 0.07965 | 0 | 0 | 0 | 0 | 0.044001 | 0.043394 | 0.087571 | 0.087571 | 0.16723 | 0.16527 | 0.00080071 | 0.00078426 | 0 | 0 | 0 | 0 | 0.00070105 | 0.00067555 | 0.0013307 | 0.0013307 | 0.00078127 | 0.00076472 | 0.0011256 | 0.0011256 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002623 | 0.0002623 | 0.0043193 | 0.0043193 | 121 | 103 | NO
2016-06-01 | 0.091332 | 0.090622 | 0 | 0 | 0.0066162 | 0.0066162 | 0.0137 | 0.012319 | 0.070237 | 0.070134 | 0.28325 | 0.28316 | 0.00038481 | 0.00037658 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.00018854 | 0.00018004 | 0.00074978 | 0.00073955 | 0.00056707 | 0.00055879 | 0.041674 | 0.041674 | 0 | 0 | 0 | 0 | 0.086102 | 0.086102 | 0 | 0 | 0 | 0 | 123 | 86 | NO
2016-06-02 | 0.021325 | 0.021148 | 0 | 0 | 0 | 0 | 0.0083021 | 0.0082596 | 0.0077537 | 0.0077537 | 0.0634 | 0.062771 | 0.00031335 | 0.00030923 | 0 | 0 | 0 | 0 | 0.00029529 | 0.00029104 | 5.118e-05 | 5.118e-05 | 0.00064468 | 0.0006364 | 0.0017204 | 0.0017204 | 0 | 0 | 0 | 0 | 0.0034484 | 0.0034484 | 0.0002559 | 0.0002559 | 0 | 0 | 101 | 88 | NO
2016-06-03 | 0.20055 | 0.20049 | 0 | 0 | 0 | 0 | 0.070522 | 0.07045 | 0.037789 | 0.037789 | 0.63939 | 0.63927 | 0.0018914 | 0.0018852 | 0 | 0 | 0 | 0 | 0.00042806 | 0.00041957 | 0.0003557 | 0.0003557 | 0.0064923 | 0.0064841 | 0.034424 | 0.034424 | 0 | 0 | 0 | 0 | 0.067911 | 0.067911 | 0 | 0 | 0.0062585 | 0.0062585 | 95 | 84 | NO
2016-06-04 | 1.588 | 1.5879 | 0 | 0 | 0 | 0 | 0.24156 | 0.24156 | 1.4635 | 1.4629 | 4.7386 | 4.7385 | 0.010842 | 0.010838 | 0 | 0 | 0 | 0 | 0.0046949 | 0.0046949 | 0.028103 | 0.028093 | 0.011771 | 0.011763 | 0.0040773 | 0.0040773 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010523 | 0.010523 | 0.0079038 | 0.0079038 | 64 | 60 | NO
2016-06-05 | 31.4528 | 0 | 0 | 0 | 3.9154 | 0 | 3.7184 | 0 | 37.2867 | 0 | 88.6686 | 0 | 0.074869 | 0 | 0 | 0 | 0.0055381 | 0 | 0.044373 | 0 | 0.12099 | 0 | 0.11631 | 0 | 0.12531 | 0 | 0 | 0 | 0 | 0 | 0.036649 | 0 | 0.20721 | 0 | 0.26545 | 0 | 0 | 0 | YES
2016-06-06 | 28.3521 | 0 | 0 | 0 | 3.2625 | 0 | 3.8423 | 0 | 50.9558 | 0 | 64.9813 | 0 | 0.033803 | 0 | 0 | 0 | 0.035134 | 0 | 0.0089622 | 0 | 0.051931 | 0 | 0.071694 | 0 | 0.14487 | 0 | 0 | 0 | 0 | 0 | 0.09471 | 0 | 0.10836 | 0 | 0.31102 | 0 | 0 | 0 | YES
2016-06-07 | 12.1101 | 0 | 0 | 0 | 2.1229 | 0 | 3.2058 | 0 | 19.4505 | 0 | 26.4765 | 0 | 0.037596 | 0 | 0 | 0 | 0.042459 | 0 | 0.02862 | 0 | 0.056056 | 0 | 0.044297 | 0 | 0.057552 | 0 | 0 | 0 | 0.042459 | 0 | 0.08258 | 0 | 0.017707 | 0 | 0.050513 | 0 | 0 | 0 | YES
2016-06-08 | 0.71875 | 0.71392 | 0 | 0 | 0 | 0 | 0.06644 | 0.065102 | 1.2955 | 1.2937 | 1.7162 | 1.7008 | 0.0038817 | 0.0038211 | 0 | 0 | 0 | 0 | 0.005022 | 0.0049796 | 0.00103 | 0.00089181 | 0.0050084 | 0.0049588 | 0.012625 | 0.012625 | 0 | 0 | 0.12554 | 0.12554 | 0.013127 | 0.013127 | 0 | 0 | 0.0076524 | 0.0076524 | 276 | 182 | NO
2016-06-09 | 2.6946 | 2.689 | 1.5602 | 1.5602 | 0 | 0 | 0.018722 | 0.017652 | 12.0124 | 12.0121 | 0.89575 | 0.87559 | 0.0052377 | 0.005196 | 0.048377 | 0.048377 | 0 | 0 | 0.00017154 | 0.00015455 | 0.0085342 | 0.0085035 | 0.0076399 | 0.0075302 | 0.010059 | 0.010059 | 0 | 0 | 0 | 0 | 0.0052212 | 0.0052212 | 0.0076437 | 0.0076437 | 0.024141 | 0.024141 | 216 | 156 | NO
2016-06-10 | 0.92258 | 0.92212 | 0 | 0 | 0.0027174 | 0.0027174 | 0.40871 | 0.40871 | 2.5075 | 2.5061 | 0.88928 | 0.88857 | 0.0056975 | 0.0056811 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 0.0079075 | 0.0079075 | 0.0017913 | 0.0017606 | 0.0060722 | 0.0060308 | 0.023342 | 0.023342 | 0 | 0 | 0 | 0 | 0.010361 | 0.010361 | 0.046017 | 0.046017 | 0.036561 | 0.036561 | 200 | 131 | NO
2016-06-11 | 0.26499 | 0.26419 | 0.6947 | 0.6947 | 0.45413 | 0.45413 | 0.11698 | 0.11545 | 0.24847 | 0.24827 | 0.4851 | 0.48502 | 0.0086112 | 0.0085475 | 0.0016126 | 0.0016126 | 0.0036921 | 0.0036921 | 0.0041282 | 0.0040135 | 0.0032474 | 0.0032166 | 0.023272 | 0.023263 | 0.010451 | 0.010451 | 0 | 0 | 0 | 0 | 0.0033263 | 0.0033263 | 0.027608 | 0.027608 | 0.013265 | 0.013265 | 89 | 86 | NO
2016-06-12 | 0.097191 | 0.097106 | 0 | 0 | 0 | 0 | 0.0085868 | 0.0085443 | 0.14328 | 0.14296 | 0.25865 | 0.25865 | 0.00064597 | 0.00063749 | 0 | 0 | 0 | 0 | 0.00014446 | 0.00014021 | 0.00114 | 0.001108 | 0.001397 | 0.001397 | 0.013406 | 0.013406 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00089565 | 0.00089565 | 0.053243 | 0.053243 | 56 | 55 | NO
2016-06-13 | 0.48355 | 0.48355 | 0 | 0 | 0.42459 | 0.42459 | 0.096915 | 0.096915 | 0.85414 | 0.85414 | 1.0075 | 1.0075 | 0.018596 | 0.018596 | 0 | 0 | 0.0036921 | 0.0036921 | 0.0051856 | 0.0051856 | 0.041406 | 0.041406 | 0.030752 | 0.030752 | 0.0040154 | 0.0040154 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012232 | 0.012232 | 0.0062719 | 0.0062719 | 115 | 73 | NO
2016-06-14 | 0.14663 | 0.14635 | 0 | 0 | 0 | 0 | 0.076309 | 0.076266 | 0.47812 | 0.47791 | 0.054917 | 0.054048 | 0.0011333 | 0.001121 | 0 | 0 | 0 | 0 | 0.00072866 | 0.00072442 | 0.0035468 | 0.0035263 | 0.00027422 | 0.00024939 | 0.030153 | 0.030153 | 0 | 0 | 0 | 0 | 0.058022 | 0.058022 | 0.0043605 | 0.0043605 | 0.0048077 | 0.0048077 | 144 | 106 | NO
2016-06-15 | 0.17455 | 0.17324 | 0 | 0 | 0.00023629 | 0.00023629 | 0.0029656 | 0.0018142 | 0.49909 | 0.49785 | 0.29321 | 0.29119 | 0.00083439 | 0.00081794 | 0 | 0 | 5.9073e-05 | 5.9073e-05 | 3.399e-05 | 2.1244e-05 | 0.0017734 | 0.0017427 | 0.0018502 | 0.0018337 | 0.0037576 | 0.0037576 | 0 | 0 | 0 | 0 | 0.0018588 | 0.0018588 | 0.0046804 | 0.0046804 | 0.0077196 | 0.0077196 | 157 | 114 | NO
2016-06-16 | 0.25326 | 0.2504 | 0 | 0 | 0 | 0 | 0.12626 | 0.12626 | 0.46245 | 0.45471 | 0.39951 | 0.39425 | 0.011826 | 0.011769 | 0 | 0 | 0 | 0 | 0.0042334 | 0.0042334 | 0.013418 | 0.013337 | 0.028508 | 0.028344 | 0.0076306 | 0.0076306 | 0 | 0 | 0 | 0 | 0.0058421 | 0.0058421 | 0.0054187 | 0.0054187 | 0.014953 | 0.014953 | 175 | 127 | NO
2016-06-17 | 0.21778 | 0.21588 | 0 | 0 | 0 | 0 | 0.044863 | 0.043049 | 0.31694 | 0.31694 | 0.53296 | 0.52885 | 0.0018089 | 0.0017965 | 0 | 0 | 0 | 0 | 0.0004185 | 0.00041001 | 0.0021815 | 0.0021815 | 0.0047021 | 0.004669 | 0.01027 | 0.01027 | 0 | 0 | 0 | 0 | 0.0042769 | 0.0042769 | 0.010392 | 0.010392 | 0.024604 | 0.024604 | 157 | 103 | NO
2016-06-18 | 0.44184 | 0.44123 | 0 | 0 | 0 | 0 | 0.46182 | 0.46177 | 0.1625 | 0.1596 | 0.74744 | 0.74744 | 0.0037445 | 0.0037383 | 0 | 0 | 0 | 0 | 0.0034819 | 0.0034776 | 0.0019295 | 0.001909 | 0.0067293 | 0.0067293 | 0.019 | 0.019 | 0 | 0 | 0 | 0 | 0.0031866 | 0.0031866 | 0.014788 | 0.014788 | 0.05832 | 0.05832 | 99 | 83 | NO
2016-06-19 | 0.039122 | 0.038634 | 0 | 0 | 0 | 0 | 0.0015763 | 0.001555 | 0.01387 | 0.011495 | 0.1432 | 0.1432 | 0.00047683 | 0.00047272 | 0 | 0 | 0 | 0 | 2.5493e-05 | 2.1244e-05 | 0.00014842 | 0.00013819 | 0.0017498 | 0.0017498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | NO
2016-06-20 | 1.0166 | 0.78873 | 0 | 0 | 3.2084 | 3.2084 | 1.4507 | 0.98121 | 0.17036 | 0.16846 | 0.67835 | 0.67748 | 0.0043948 | 0.0038704 | 0 | 0 | 0.040613 | 0.040613 | 0.0023751 | 0.0013129 | 0.0015072 | 0.0014765 | 0.006154 | 0.0061374 | 0.019089 | 0.019089 | 0.04233 | 0.04233 | 0.095994 | 0.095994 | 0.011489 | 0.011489 | 0.017227 | 0.017227 | 0.021644 | 0.021644 | 185 | 155 | NO
2016-06-21 | 0.60065 | 0.60001 | 0 | 0 | 0 | 0 | 0.10955 | 0.10922 | 0.84752 | 0.84514 | 1.5191 | 1.5191 | 0.002817 | 0.0028067 | 0 | 0 | 0 | 0 | 0.000666 | 0.00065325 | 0.0064781 | 0.0064576 | 0.0048035 | 0.0048035 | 0.02544 | 0.02544 | 0 | 0 | 0.027691 | 0.027691 | 0.017236 | 0.017236 | 0.055892 | 0.055892 | 0.019747 | 0.019747 | 154 | 122 | NO
2016-06-22 | 1.43 | 1.4297 | 0 | 0 | 0 | 0 | 0.94516 | 0.94509 | 2.3865 | 2.385 | 1.985 | 1.985 | 0.026663 | 0.026654 | 0 | 0 | 0 | 0 | 0.011423 | 0.011415 | 0.06475 | 0.06473 | 0.03271 | 0.03271 | 0.028923 | 0.028923 | 0.050393 | 0.050393 | 0.025845 | 0.025845 | 0.0051808 | 0.0051808 | 0.0088464 | 0.0088464 | 0.089095 | 0.089095 | 172 | 147 | NO
2016-06-23 | 0.30971 | 0.28255 | 0 | 0 | 0 | 0 | 0.067775 | 0.011653 | 0.3863 | 0.3863 | 0.80231 | 0.80231 | 0.0021844 | 0.0016662 | 0 | 0 | 0 | 0 | 0.0012231 | 0.00015242 | 0.0044424 | 0.0044424 | 0.0028178 | 0.0028178 | 0.0097214 | 0.0097214 | 0 | 0 | 0 | 0 | 0.0025131 | 0.0025131 | 0.016708 | 0.016708 | 0.020726 | 0.020726 | 151 | 115 | NO
2016-06-24 | 0.41722 | 0.41465 | 0 | 0 | 0 | 0 | 0.13849 | 0.13849 | 1.0137 | 1.0137 | 0.58989 | 0.57954 | 0.0096415 | 0.0095901 | 0 | 0 | 0 | 0 | 0.0035817 | 0.0035817 | 0.029285 | 0.029285 | 0.0081501 | 0.0079431 | 0.027792 | 0.027792 | 0 | 0 | 0 | 0 | 0.0041532 | 0.0041532 | 0.035717 | 0.035717 | 0.074901 | 0.074901 | 133 | 118 | NO
2016-06-25 | 0.34046 | 0.34044 | 0 | 0 | 0 | 0 | 0.03929 | 0.039248 | 0.93909 | 0.93909 | 0.53452 | 0.53452 | 0.0045678 | 0.0045657 | 0 | 0 | 0 | 0 | 0.00070689 | 0.00070264 | 0.015902 | 0.015902 | 0.0041506 | 0.0041506 | 0.0088091 | 0.0088091 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012433 | 0.012433 | 0.025407 | 0.025407 | 96 | 80 | NO
2016-06-26 | 0.040203 | 0.040138 | 0 | 0 | 0 | 0 | 0.0067938 | 0.0067938 | 0.15567 | 0.15536 | 0.022701 | 0.022701 | 0.00041951 | 0.00041308 | 0 | 0 | 0 | 0 | 0.00012746 | 0.00012746 | 0.0013 | 0.001268 | 0.00038909 | 0.00038909 | 0.0040401 | 0.0040401 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012377 | 0.012377 | 0.0062543 | 0.0062543 | 83 | 61 | NO
2016-06-27 | 0.14774 | 0.14669 | 0 | 0 | 0 | 0 | 0.04307 | 0.04211 | 0.12007 | 0.11727 | 0.41372 | 0.41364 | 0.0011413 | 0.001131 | 0 | 0 | 0 | 0 | 0.00051623 | 0.00050773 | 0.0012552 | 0.0012347 | 0.0025735 | 0.0025653 | 0.0046727 | 0.0046727 | 0 | 0 | 0 | 0 | 0.0019003 | 0.0019003 | 0.01414 | 0.01414 | 0.0036725 | 0.0036725 | 314 | 217 | NO
2016-06-28 | 0.18114 | 0.18111 | 0 | 0 | 0 | 0 | 0.051591 | 0.051548 | 0.29113 | 0.29113 | 0.39322 | 0.39318 | 0.0046719 | 0.0046678 | 0 | 0 | 0 | 0 | 0.0005773 | 0.00057305 | 0.013863 | 0.013863 | 0.0064706 | 0.0064623 | 0.0040193 | 0.0040193 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01414 | 0.01414 | 0.0047446 | 0.0047446 | 188 | 177 | NO
2016-06-29 | 0.088654 | 0.088567 | 0 | 0 | 0 | 0 | 0.16036 | 0.16031 | 0.020197 | 0.019869 | 0.028116 | 0.028116 | 0.00049148 | 0.00048737 | 0 | 0 | 0 | 0 | 0.00082214 | 0.00081789 | 0.00036977 | 0.00035954 | 7.761e-05 | 7.761e-05 | 0.002052 | 0.002052 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0050425 | 0.0050425 | 0.0041827 | 0.0041827 | 121 | 111 | NO
2016-06-30 | 0.65186 | 0.65177 | 0 | 0 | 0 | 0 | 0.53531 | 0.53527 | 0.57587 | 0.57587 | 1.1154 | 1.1151 | 0.0034566 | 0.0034483 | 0 | 0 | 0 | 0 | 0.0033135 | 0.0033093 | 0.0035826 | 0.0035826 | 0.0045614 | 0.0045366 | 0.0084279 | 0.0084279 | 0 | 0 | 0 | 0 | 0.0018323 | 0.0018323 | 0.0080416 | 0.0080416 | 0.023854 | 0.023854 | 194 | 162 | NO
| 344.7542 | 181.7655 | 19.2733 | 14.57 | 20.8995 | 11.3697 | 118.7628 | 78.0602 | 515.9085 | 254.2604 | 733.8158 | 370.5336 | 2.2547 | 1.8085 | 0.19369 | 0.16332 | 0.35513 | 0.19209 | 1.2082 | 0.97427 | 3.2714 | 2.614 | 4.0022 | 3.2201 | 4.8757 | 3.8019 | 0.61883 | 0.61883 | 1.0918 | 1.0493 | 2.6513 | 2.0996 | 6.5969 | 4.9736 | 8.8942 | 6.9652 | 44455 | 32314
Contents
Contents

## 1d. STPIS GSL
Table | TasNetworks
STPIS Data Reporting
2015-16
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
| Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
| Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Customer Service
TasNetworks
Customer Service | The information is required to assess the outturn level of service provided to the DNSP's customers, and will inform the AER’s review of future regulatory proposals. The information may be used in performance reports.
2015-16
Table 1 Quality of supply
Over voltage events - due to high voltage injection |  | 2
Customers receiving over-voltage - due to high voltage injection |  | 15
Over voltage events - due to lightning |  | 81
Customers receiving over-voltage - due to lightning |  | 127
Over voltage events - due to voltage regulation or other cause |  | 98
Customers receiving over-voltage - due to voltage regulation or other cause |  | 98
Voltage variations - steady state (zone sub) |  | 15
Voltage variations - one minute (zone sub) |  | 3
Voltage variations - 10 seconds (zone sub) Min<0.7 |  | -
Voltage variations - 10 seconds (zone sub) Min<0.8 |  | -
Voltage variations - 10 seconds (zone sub) Min<0.9 |  | -
Voltage variations - steady state (feeder) |  | 306
Voltage variations - % zone subs monitored |  | 100
Voltage variations - % feeders monitored |  | 5.94
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number |  | 362
Complaints by category (%)
Low voltage supply |  | 5.249%
Voltage dips |  | 6.077%
Voltage swell |  | 18.51%
Voltage spike (impulsive transient) |  | 0.5525%
Waveform distortion |  | 0%
TV or radio interference |  | 3.867%
Noise from appliances |  | 0%
Other |  | 65.75%
Complaints by Likely Cause (%)
Network equipment faulty |  | 2.21%
Network interference by NSP equipment |  | 0%
Network interference by another customer |  | 0.2762%
Network limitation |  | 36.74%
Customer internal problem |  | 2.21%
No problem identified |  | 53.59%
Environmental |  | 0%
Other |  | 4.972%
Table 3 Customer service
Timely provision of services
Connections made |  | 0
Connections not made on agreed date |  | 0
Timely repair of faulty streetlights
Streetlights - average monthly number "out" |  | 203
Streetlights - not repaired by "fix by" date |  | 1524
Streetlights - average number of days to repair |  | 10.8
Total streetlights |  | 42927
Call Centre Performance (number, unless stated)
Calls to call centre fault line |  | 54046
Calls to fault line answered within 30 seconds |  | 33792
Calls to fault line - average waiting time before call answered |  | 56.6
Calls abandoned - percentage |  | 5
Call centre - number of overload events |  | N/A
Customer complaints (number)
Complaint - reliability of supply |  | 109
Complaint - technical quality of supply |  | 362
Complaint - administrative process or customer service |  | 0
Complaint - connection or augmentation |  | 154
Complaint - other |  | 1613
Total complaints |  | 2238
Contents

## 3a. Feeder Reliability
TasNetworks
Annual Feeder Reliability
2015-16
Table 1 Annual Feeder Reliability Data
Feeder ID / name | Description of the feeder service area | Feeder classification | Number of Customers(1) | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply (including excluded events and MEDs) | Planned customer minutes off-supply (after removing excluded events and MED) | Planned interruptions (SAIFI) (including excluded events and MEDs) | Planned interruptions (SAIFI) (after removing excluded events and MEDs) | Total number of momentary feeder outages | Momentary interruptions due to feeder outages (MAIFI) (including excluded events and MEDs) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events and MEDs) | Low Reliability Feeder (SAIDI)
12017 | Enterprise Rd-Mt Nelson-Taroona | Urban | 1004 | 6.514 | 2.734 | 3.1888 | 0.235 | 1.4 | 11 | 20.5527 | 19.4401 | 2.0444 | 2.0072 | 9 | 198.1156 | 198.1156 | 0.51452 | 0.51452 | 0 | 0 | 0 | No
12018 | Upper Sandy Bay | Urban | 909 | 0.02 | 4.863 | 3.6327 | 0.014 | 0.29 | 5 | 0.62286 | 0.33143 | 0.0071429 | 0.0028571 | 5 | 14.4214 | 14.4214 | 0.048571 | 0.048571 | 0 | 0 | 0 | No
12019 | Lower Sandy Bay | Urban | 1137 | 2.199 | 3.558 | 3.9686 | 5.997 | 0.523 | 13 | 144.7481 | 144.6968 | 1.6757 | 1.6749 | 3 | 21.8405 | 21.8405 | 0.085936 | 0.085936 | 0 | 0 | 0 | No
12030 | Lower Sandy Bay-Taroona (North)-Station Supply | Urban | 941 | 6.18 | 5.242 | 3.5704 | 0.199 | 0.2 | 9 | 35.0882 | 35.0764 | 0.11807 | 0.11699 | 2 | 15.2639 | 15.2639 | 0.075756 | 0.075756 | 0 | 0 | 0 | No
12031 | Mt Nelson-Taroona | Short Rural | 1004 | 10.19 | 4.067 | 4.2233 | 3.187 | 0.239 | 11 | 168.0263 | 168.0026 | 2.0412 | 2.0393 | 8 | 97.9392 | 97.9392 | 0.20088 | 0.20088 | 0 | 0 | 0 | No
12032 | Sandy Bay-Dynnyrne-Waterworks Reserve | Short Rural | 681 | 2.749 | 4 | 1.9935 | 0.024 | 0.246 | 4 | 2.3743 | 2.2949 | 0.13973 | 0.13836 | 9 | 56.214 | 56.214 | 0.2887 | 0.2887 | 0 | 0 | 0 | No
12033 | Sandy Bay | Urban | 347 | 0.683 | 2.39 | 1.2784 | 0.013 | 0.968 | 5 | 2.7048 | 2.7048 | 0.019048 | 0.019048 | 3 | 86.4953 | 86.4953 | 0.25333 | 0.25333 | 0 | 0 | 0 | No
12035 | Sandy Bay | Urban | 850 | 1.266 | 4.329 | 3.2662 | 0.062 | 1.723 | 10 | 3.9332 | 3.9045 | 0.053525 | 0.050072 | 10 | 115.0849 | 115.0849 | 0.35856 | 0.35856 | 0 | 0 | 0 | No
12036 | Sandy Bay-Fitzroy Place | Urban | 1 | 0.294 | 3.506 | 4.5936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
12037 | Casino-Battery Point | Urban | 205 | 0 | 2.847 | 2.7804 | 5.351 | 8.701 | 9 | 28.2494 | 28.2373 | 0.27532 | 0.27411 | 8 | 91.6112 | 91.6112 | 0.30551 | 0.30551 | 0 | 0 | 0 | No
12038 | Tolmans Hill-Mt Nelson-Taroona-Sandy Bay | Short Rural | 733 | 25.546 | 4.727 | 2.9296 | 0.606 | 0.882 | 9 | 32.0031 | 31.9943 | 0.25628 | 0.25566 | 12 | 24.3484 | 24.3484 | 0.096165 | 0.096165 | 0 | 0 | 0 | No
12039 | West Hobart Zone | Urban | 1203 | 0.521 | 4.8 | 4.1738 | 0.264 | 1.241 | 13 | 8.3726 | 8.1623 | 0.068703 | 0.067781 | 12 | 50.1487 | 50.1487 | 0.21164 | 0.21164 | 0 | 0 | 0 | No
13043 | Lynton Avenue South Hobart | Urban | 452 | 0 | 1.471 | 1.683 | 0.072 | 0.003 | 5 | 5.344 | 1.1973 | 0.013333 | 0.010667 | 2 | 0.32 | 0.32 | 0.0053333 | 0.0053333 | 3 | 3 | 3 | No
13044 | City | Urban | 326 | 0 | 3.362 | 4.2741 | 0.013 | 0 | 2 | 0.1027 | 0.1027 | 0.0014884 | 0.0014884 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | No
13045 | South Hobart-Cascades | Short Rural | 1534 | 10.822 | 4.358 | 4.2932 | 2.06 | 0.949 | 18 | 51.3475 | 51.3244 | 0.29423 | 0.29159 | 12 | 25.684 | 25.684 | 0.13878 | 0.13878 | 2 | 1.1144 | 1.1144 | No
13046 | City (South)(Collins St) | Urban | 8 | 0 | 0.894 | 1.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
13047 | City (South-East)(Macquarie St)-Salamanca | Urban | 183 | 0 | 1.907 | 0.8574 | 0.525 | 0.007 | 4 | 113.7294 | 113.5001 | 1.0053 | 1 | 2 | 0.32 | 0.32 | 0.0053333 | 0.0053333 | 2 | 2 | 2 | No
13048 | City (North)(Melville St) | Urban | 330 | 0 | 1.915 | 2.9214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.0526 | 1.0526 | No
13049 | West Hobart (Hill St - Arthur St) | Urban | 1042 | 0.534 | 3.76 | 3.8931 | 0.009 | 0.186 | 3 | 0.68037 | 0.52336 | 0.004486 | 0.0029907 | 4 | 25.5028 | 25.5028 | 0.097944 | 0.097944 | 2 | 2 | 2 | No
13050 | Sandy Bay | Urban | 293 | 0.043 | 2.833 | 1.448 | 0.004 | 0.38 | 2 | 0.16119 | 0.13748 | 0.0047407 | 0.0023704 | 3 | 99.3955 | 99.3955 | 0.33541 | 0.33541 | 1 | 1.037 | 1.037 | No
13052 | Battery Point | Urban | 739 | 0.126 | 5.968 | 5.0997 | 0 | 1.177 | 0 | 0 | 0 | 0 | 0 | 3 | 14.3208 | 14.3208 | 0.041326 | 0.041326 | 1 | 1.0001 | 1.0001 | No
13053 | Battery Point (Hampton Road) | Urban | 761 | 0 | 3.733 | 2.9976 | 0.201 | 0.306 | 8 | 3.6869 | 3.6823 | 0.12526 | 0.12434 | 8 | 9.3989 | 9.3989 | 0.042057 | 0.042057 | 2 | 2.0002 | 2.0002 | No
13054 | St Davids Park | Urban | 216 | 0 | 2.082 | 3.6009 | 0.662 | 0.017 | 3 | 18.9973 | 18.9973 | 0.61621 | 0.61621 | 2 | 0.098462 | 0.098462 | 0.001641 | 0.001641 | 1 | 1 | 1 | No
13055 | South Hobart | Urban | 998 | 2.505 | 2.117 | 3.5057 | 0.882 | 0.011 | 10 | 11.0663 | 10.9982 | 0.059871 | 0.057806 | 4 | 0.24774 | 0.24774 | 0.004129 | 0.004129 | 1 | 0.90323 | 0.90323 | No
13056 | South Hobart - Sandy Bay Zone | Urban | 516 | 0.583 | 2.202 | 1.6004 | 0.673 | 0.209 | 4 | 81.91 | 81.424 | 1.006 | 1.004 | 6 | 13.59 | 13.59 | 0.064 | 0.064 | 3 | 3 | 3 | No
13057 | Huon Road-Mount Wellington-Nieka | Short Rural | 870 | 38.871 | 0.932 | 3.1564 | 2.326 | 2.736 | 19 | 383.814 | 380.879 | 2.2694 | 1.6418 | 33 | 135.8695 | 135.8086 | 0.47171 | 0.4707 | 4 | 2.8828 | 2.8828 | No
13058 | MacQuarie St | Urban | 30 | 0 | 1.126 | 1.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
14060 | Evans St | Urban | 124 | 0 | 1.424 | 1.9307 | 0.133 | 0 | 3 | 27.7797 | 27.7231 | 0.464 | 0.46277 | 0 | 0 | 0 | 0 | 0 | 1 | 2.7692 | 2.7692 | No
14061 | Domain-Tasman Bridge | Urban | 429 | 3.127 | 4.541 | 3.639 | 0.099 | 0 | 3 | 0.84842 | 0.84014 | 0.0024832 | 0.0016555 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | No
14062 | City (East)-Marine Board Group | Short Rural | 8 | 0 | 3.243 | 0.6732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
14063 | Argyle St North Hobart | Urban | 217 | 0 | 2.453 | 2.6928 | 20.138 | 1.207 | 5 | 231.6227 | 231.6227 | 0.792 | 0.792 | 4 | 9.1284 | 9.1284 | 0.037053 | 0.037053 | 1 | 1.0001 | 1.0001 | No
14064 | Collins Street | Urban | 110 | 0 | 1.285 | 3.5438 | 1.294 | 1.705 | 2 | 61.8859 | 61.8859 | 0.45527 | 0.45527 | 2 | 29.4218 | 29.4218 | 0.14073 | 0.14073 | 0 | 0 | 0 | No
14065 | Collins Street | Urban | 151 | 0 | 0.658 | 3.8232 | 0.171 | 0 | 1 | 21.5385 | 21.5385 | 0.30769 | 0.30769 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
14066 | Brooker Ave (University - Tech College) | Urban | 77 | 0 | 0.639 | 2.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.99956 | 0.99956 | No
14067 | West Hobart Zone Substation | Urban | 95 | 0 | 1.863 | 3.1246 | 0 | 0.043 | 0 | 0 | 0 | 0 | 0 | 2 | 14.24 | 0.029474 | 0.23768 | 0.00084211 | 1 | 1 | 1 | No
14068 | Town Hall | Urban | 167 | 0 | 1.604 | 4.0645 | 0 | 0.119 | 0 | 0 | 0 | 0 | 0 | 3 | 65.3572 | 65.3572 | 0.208 | 0.208 | 0 | 0 | 0 | No
14069 | Trafalgar Place | Urban | 164 | 0 | 1.58 | 2.8007 | 0.036 | 0.018 | 2 | 50.3828 | 0.039 | 0.09475 | 0.001 | 1 | 33.75 | 33.75 | 0.09375 | 0.09375 | 1 | 1 | 1 | No
14070 | Mawson Place - West Hobart Zone | Urban | 146 | 0 | 3.051 | 4.6488 | 0.977 | 0.229 | 1 | 11.1429 | 11.1429 | 0.071429 | 0.071429 | 3 | 12.6384 | 12.6384 | 0.049905 | 0.049905 | 1 | 1 | 1 | No
16091 | Albert Rpad-Charles St Moonah | Urban | 1173 | 2.646 | 2.6 | 3.6644 | 2.991 | 1.112 | 16 | 121.7875 | 121.7367 | 2.5894 | 2.5873 | 21 | 24.0466 | 24.0466 | 0.13402 | 0.13402 | 3 | 7 | 7 | No
16092 | Moonah-Gormanston Rd | Urban | 640 | 0 | 2.588 | 2.2037 | 0.343 | 0.59 | 10 | 16.5009 | 16.3098 | 0.091333 | 0.086 | 11 | 20.4191 | 20.4191 | 0.11511 | 0.11511 | 10 | 12.0013 | 12.0013 | No
16093 | Moonah-Birdwood Dr | Urban | 312 | 0 | 3.482 | 2.3816 | 0.035 | 0 | 4 | 0.74274 | 0.74274 | 0.0067368 | 0.0067368 | 0 | 0 | 0 | 0 | 0 | 21 | 23 | 23 | No
16094 | Lutana | Urban | 896 | 3.347 | 2.111 | 4.0836 | 0.012 | 0.435 | 7 | 0.47667 | 0.40535 | 0.008321 | 0.0035661 | 19 | 20.6746 | 20.6746 | 0.065973 | 0.065973 | 9 | 19 | 19 | No
16095 | Selfs Point-Lenox Avenue | Urban | 359 | 1.527 | 2.604 | 2.0958 | 0.532 | 0.212 | 7 | 69.0773 | 68.9569 | 0.20428 | 0.20216 | 4 | 9.4484 | 9.4484 | 0.051201 | 0.051201 | 8 | 17 | 0 | No
16096 | North Hobart | Urban | 1140 | 1.725 | 8.376 | 3.7788 | 0.447 | 0.599 | 10 | 9.9895 | 6.4775 | 0.10029 | 0.038537 | 23 | 57.1417 | 51.9321 | 0.26895 | 0.25316 | 11 | 13.8375 | 0 | No
16097 | New Town (Cross St) | Urban | 204 | 0 | 1.249 | 1.2384 | 0.007 | 0.326 | 4 | 0.39556 | 0.35111 | 0.017778 | 0.0088889 | 4 | 25.9556 | 25.9556 | 0.14667 | 0.14667 | 6 | 7 | 7 | No
16098 | Augusta Rd Lenah Valley-Creek Road Lenah Valley | Urban | 1031 | 4.966 | 4.91 | 3.8105 | 0.84 | 1.251 | 11 | 39.5155 | 39.0613 | 1.0128 | 1.0111 | 13 | 77.0695 | 77.0695 | 0.35128 | 0.35128 | 1 | 1.0262 | 1.0262 | No
17100 | Eady St nr Cooper St-Derwent Pk (East) | Urban | 64 | 0 | 4.692 | 2.5594 | 0.5 | 0 | 5 | 25.9275 | 25.9182 | 1.0037 | 1.0028 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 6 | No
17101 | East Derwent Hwy Bowen Bridge | Short Rural | 339 | 10.114 | 6.353 | 2.2863 | 0.97 | 0.538 | 16 | 36.4118 | 36.4118 | 1.1022 | 1.1022 | 24 | 17.7424 | 17.7424 | 0.11604 | 0.11604 | 1 | 1 | 1 | No
17102 | Derwent Park (HEC Garage) | Urban | 1 | 0 | 0.878 | 0.3493 | 2.908 | 0 | 3 | 519.0002 | 25 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
17103 | Dowsing Point-Grove Road | Urban | 632 | 2.07 | 4.775 | 3.0484 | 2.453 | 0.34 | 27 | 101.9739 | 101.8662 | 2.3365 | 2.3257 | 9 | 9.1255 | 9.1255 | 0.025857 | 0.025857 | 0 | 0 | 0 | No
17104 | Derwent Park (Sunderland Street) | Urban | 169 | 0 | 1.863 | 1.9751 | 0.089 | 0 | 4 | 29.5535 | 29.5349 | 1.12 | 1.1181 | 0 | 0 | 0 | 0 | 0 | 6 | 7 | 7 | No
17105 | Goodwood | Urban | 881 | 2.715 | 3.945 | 3.9375 | 1.75 | 0.35 | 14 | 52.3488 | 52.3366 | 2.028 | 2.0263 | 26 | 18.8979 | 18.8979 | 0.071547 | 0.071547 | 0 | 0 | 0 | No
17106 | Brooker Hwy Lutana | Urban | 492 | 2.58 | 3.397 | 3.4295 | 2.495 | 0.801 | 11 | 525.3216 | 39.2916 | 2.0831 | 1.0819 | 15 | 15.2459 | 15.2459 | 0.10074 | 0.10074 | 6 | 6.9897 | 5.9912 | No
17107 | Main Rd Moonah | Urban | 299 | 0 | 3.158 | 2.5086 | 1.075 | 2.687 | 5 | 113.3462 | 113.3462 | 1.5 | 1.5 | 6 | 65.7785 | 65.7785 | 0.34985 | 0.34985 | 13 | 13 | 13 | No
17108 | Derwent Park (Howard Road) | Urban | 25 | 0 | 1.445 | 0.8447 | 0.129 | 0 | 1 | 25 | 25 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
17109 | Moonah (Lampton Ave)-Moonah (HEC Depot) | Urban | 67 | 0 | 1.42 | 1.1622 | 0.194 | 0.396 | 2 | 25.0983 | 25.0983 | 1.0023 | 1.0023 | 1 | 128.1428 | 128.1428 | 0.42857 | 0.42857 | 6 | 6 | 6 | No
18131 | A-City (West), B-North Hobart-City (West/South) | Urban | 615 | 0 | 4.746 | 6.5655 | 1.128 | 0.324 | 13 | 15.4001 | 6.463 | 0.19901 | 0.048099 | 6 | 35.0598 | 35.0598 | 0.20938 | 0.20938 | 0 | 0 | 0 | No
18132 | A-Websters, B-RHH | Urban | 40 | 0 | 2.241 | 3.258 | 0.057 | 0 | 1 | 0.84267 | 0.84267 | 0.010667 | 0.010667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
18133 | A-RHH, B-North Hobart (Brisbane Street) | Urban | 122 | 0 | 3.658 | 3.9706 | 0 | 1.888 | 0 | 0 | 0 | 0 | 0 | 2 | 14.2398 | 14.2398 | 0.071312 | 0.071312 | 0 | 0 | 0 | No
18134 | A-North Hobart, B-Domain | Urban | 1218 | 1.197 | 2.705 | 4.7937 | 0.001 | 0.169 | 2 | 0.16675 | 0.1469 | 0.0039702 | 0.0019851 | 8 | 34.0753 | 30.7593 | 0.23325 | 0.21737 | 0 | 0 | 0 | No
18135 | A-New Town Substation, B-Augusta Rd | Urban | 606 | 0.555 | 2.688 | 2.7131 | 0.008 | 0.582 | 5 | 0.65855 | 0.63536 | 0.011594 | 0.0092754 | 6 | 51.4203 | 51.4203 | 0.15652 | 0.15652 | 0 | 0 | 0 | No
18136 | A-New Town-Mt Stuart, B-Stn Supp No1 (Transend) | Urban | 476 | 0.429 | 3.333 | 2.092 | 0.004 | 1.387 | 2 | 0.22519 | 0.22519 | 0.0039506 | 0.0039506 | 7 | 97.2326 | 97.2326 | 0.36247 | 0.36247 | 0 | 0 | 0 | No
18141 | A-Stn Supp No2 (Transend), B-North Hobart | Urban | 426 | 0 | 2.986 | 3.4828 | 0.075 | 0.224 | 3 | 14.8575 | 14.8575 | 0.28225 | 0.28225 | 4 | 4.71 | 4.71 | 0.017 | 0.017 | 0 | 0 | 0 | No
18142 | A-City (West), B-City (West) | Urban | 237 | 0 | 2.648 | 5.6472 | 1.25 | 0 | 4 | 72.8138 | 72.6881 | 0.576 | 0.57371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
18143 | A-North Hobart, B-Mount Stuart-City(North) | Urban | 1416 | 1.637 | 5.637 | 6.2455 | 0.008 | 0.007 | 6 | 0.35646 | 0.33316 | 0.0060759 | 0.0040506 | 5 | 0.3038 | 0.3038 | 0.0050633 | 0.0050633 | 0 | 0 | 0 | No
18144 | A-North Hobart, B-Lenah Valley-New Town | Urban | 1235 | 2.464 | 7.803 | 5.0756 | 2.388 | 0.936 | 28 | 49.5689 | 49.3978 | 0.12544 | 0.11796 | 11 | 78.0383 | 78.0383 | 0.3486 | 0.3486 | 0 | 0 | 0 | No
18145 | Noth Hobart Substation | Urban | 149 | 0 | 3.835 | 1.2422 | 0 | 0.584 | 0 | 0 | 0 | 0 | 0 | 5 | 15.5768 | 15.5768 | 0.050581 | 0.050581 | 0 | 0 | 0 | No
18146 | A-Mount Stuart, B-New Town, Ogilvie High School | Urban | 1992 | 8.231 | 8.169 | 8.425 | 1.546 | 5.662 | 24 | 17.4288 | 17.2279 | 0.10754 | 0.10625 | 33 | 62.1276 | 62.1276 | 0.2231 | 0.2231 | 0 | 0 | 0 | No
20534 | Glenorchy (East) | Short Rural | 297 | 1.51 | 2.109 | 1.0199 | 0.017 | 0.265 | 3 | 1.6544 | 0.7456 | 0.0096 | 0.0064 | 3 | 33.072 | 33.072 | 0.1312 | 0.1312 | 0 | 0 | 0 | No
20535 | West Moonah | Urban | 1744 | 4.654 | 5.787 | 4.7511 | 2.576 | 2.591 | 24 | 42.2514 | 42.1033 | 0.31813 | 0.31366 | 34 | 64.6743 | 64.6743 | 0.23458 | 0.23458 | 0 | 0 | 0 | No
20536 | Glenorchy (Central) | Urban | 898 | 2.321 | 2.812 | 2.4886 | 0.265 | 0.712 | 8 | 13.5138 | 13.4834 | 0.19882 | 0.19593 | 15 | 48.5758 | 48.5758 | 0.28429 | 0.28429 | 4 | 7.0095 | 7.0095 | No
20537 | Merton-Glenorchy (Central) | Urban | 834 | 2.845 | 4.84 | 2.3645 | 0.459 | 0.046 | 10 | 14.5468 | 14.5468 | 0.10762 | 0.10762 | 16 | 22.0508 | 22.0508 | 0.11665 | 0.11665 | 2 | 2 | 2 | No
20539 | Glenorchy (Central) | Short Rural | 129 | 0.113 | 3.922 | 0.5335 | 0 | 0.073 | 0 | 0 | 0 | 0 | 0 | 2 | 95.4 | 95.4 | 0.5 | 0.5 | 0 | 0 | 0 | No
20540 | Northgate-Nichols St | Urban | 188 | 0 | 3.428 | 2.6597 | 0.008 | 0.449 | 1 | 0.068 | 0.068 | 0.0013333 | 0.0013333 | 8 | 3.62 | 3.62 | 0.046667 | 0.046667 | 3 | 5 | 5 | No
20541 | Rosetta-Berriedale | Urban | 755 | 2.992 | 7.561 | 4.1036 | 0.117 | 1.197 | 3 | 1.8155 | 1.8155 | 0.043451 | 0.043451 | 15 | 12.3548 | 12.3548 | 0.093638 | 0.093638 | 0 | 0 | 0 | No
20544 | Glenorchy (North)-Montrose | Urban | 845 | 3.117 | 3.864 | 2.7639 | 0.737 | 1.006 | 10 | 19.779 | 16.7711 | 1.1703 | 0.16839 | 12 | 52.3003 | 52.3003 | 0.29155 | 0.29155 | 2 | 3.0028 | 3.0028 | No
20545 | Glenorchy (West) | Urban | 316 | 0 | 1.894 | 2.8334 | 0.112 | 0.667 | 8 | 10.432 | 7.3467 | 1.3547 | 0.34756 | 6 | 93.2785 | 93.2785 | 0.44978 | 0.44978 | 3 | 3 | 3 | No
20547 | Stn Service No2 (Transend)-Merton-West Moonah | Urban | 945 | 3.967 | 0.761 | 2.4414 | 0.604 | 0.584 | 16 | 21.801 | 18.8083 | 1.2535 | 0.30672 | 20 | 38.1859 | 38.1859 | 0.21563 | 0.21563 | 5 | 5.3053 | 5.3053 | No
20548 | Lenah Valley | Short Rural | 1623 | 13.587 | 5 | 5.2647 | 7.357 | 2.944 | 24 | 170.2848 | 167.2656 | 3.2442 | 2.2411 | 26 | 73.3163 | 73.3163 | 0.3274 | 0.3274 | 0 | 0 | 0 | No
20549 | Rosetta-Berriedale-Chigwell | Urban | 975 | 1.787 | 6.843 | 3.0294 | 1.369 | 0.468 | 18 | 56.5248 | 55.625 | 0.24481 | 0.2388 | 26 | 16.3092 | 16.3092 | 0.083609 | 0.083609 | 1 | 2 | 2 | No
20551 | Glenorchy (West) | Urban | 213 | 2.293 | 0.636 | 1.4267 | 0.009 | 0.014 | 3 | 0.5193 | 0.31345 | 0.014035 | 0.0093567 | 3 | 0.84211 | 0.84211 | 0.014035 | 0.014035 | 1 | 1.9883 | 1.9883 | No
20552 | Montrose | Urban | 1036 | 5.508 | 2.94 | 3.3097 | 1.252 | 0.553 | 18 | 46.6649 | 43.2904 | 0.24901 | 0.19317 | 12 | 30.9683 | 30.9683 | 0.099047 | 0.099047 | 1 | 1 | 1 | No
20553 | Rosetta (West)-Glenlusk-Collinsvale-Collins Cap | Short Rural | 958 | 47.463 | 2.585 | 2.6473 | 3.925 | 2.072 | 24 | 212.7147 | 212.6044 | 2.3388 | 2.3377 | 27 | 114.9362 | 114.9362 | 0.40813 | 0.40813 | 0 | 0 | 0 | No
20554 | Glenorchy (Central) | Urban | 423 | 0.466 | 2.875 | 2.7441 | 0.072 | 0.251 | 6 | 1.419 | 0.92459 | 0.0078689 | 0.0065574 | 5 | 4.977 | 4.977 | 0.017049 | 0.017049 | 0 | 0 | 0 | No
21081 | Claremont | Urban | 867 | 2.731 | 4.361 | 2.2863 | 0.059 | 1.681 | 12 | 5.0723 | 5.0532 | 0.092386 | 0.089838 | 34 | 100.3441 | 100.3441 | 0.46687 | 0.46687 | 2 | 2 | 2 | No
21082 | Battersby Drive | Urban | 227 | 0 | 1.668 | 0.7875 | 0.001 | 0.159 | 1 | 0.083375 | 0.083375 | 0.0039702 | 0.0039702 | 17 | 35.9304 | 35.9304 | 0.46402 | 0.46402 | 1 | 1 | 1 | No
21083 | Cadburys | Urban | 326 | 0 | 3.875 | 3.3088 | 0.618 | 2.196 | 4 | 1.4984 | 1.4984 | 0.020836 | 0.020836 | 19 | 6.4823 | 6.4823 | 0.046045 | 0.046045 | 0 | 0 | 0 | No
21084 | Cadburys | Urban | 113 | 0 | 2.527 | 2.534 | 0.106 | 0.017 | 1 | 4.0133 | 4.0133 | 0.013333 | 0.013333 | 1 | 0.8 | 0.8 | 0.013333 | 0.013333 | 7 | 188.4283 | 188.4283 | No
21085 | Claremont | Urban | 964 | 2.086 | 3.415 | 4.8457 | 1.416 | 3.214 | 21 | 23.6572 | 22.8943 | 0.22586 | 0.21323 | 40 | 194.1975 | 194.1975 | 0.7617 | 0.7617 | 6 | 6 | 6 | No
21086 | Claremont (East) | Urban | 722 | 2.374 | 2.654 | 2.5149 | 0.008 | 1.404 | 7 | 0.36508 | 0.35921 | 0.0082172 | 0.0070433 | 17 | 46.8085 | 46.8085 | 0.32399 | 0.32399 | 1 | 1 | 1 | No
21087 | Rosetta | Urban | 617 | 1.393 | 3.4 | 1.7909 | 0.004 | 0.009 | 2 | 0.77263 | 0 | 0.0042105 | 0 | 8 | 1.0105 | 1.0105 | 0.016842 | 0.016842 | 3 | 3 | 3 | No
21088 | Claremont-Chigwell (Nth) | Urban | 348 | 1.071 | 1.248 | 1.0225 | 0.001 | 0.141 | 3 | 0.17892 | 0.14452 | 0.010323 | 0.0034409 | 11 | 98.2774 | 98.2774 | 0.68688 | 0.68688 | 4 | 4 | 4 | No
21089 | Claremont West-Austins Ferry | Short Rural | 949 | 13.415 | 3.463 | 2.2037 | 0.006 | 1.554 | 7 | 8.1274 | 8.1171 | 0.22046 | 0.21944 | 26 | 64.7014 | 64.7014 | 0.32583 | 0.32583 | 7 | 7.2694 | 7.2694 | No
22323 | Shorline-Howrah-Tranmere | Urban | 490 | 1.389 | 3.161 | 2.0062 | 0.003 | 0.026 | 2 | 0.30172 | 0.30172 | 0.0058024 | 0.0058024 | 11 | 1.9148 | 1.9148 | 0.031913 | 0.031913 | 1 | 1.0027 | 1.0027 | No
22324 | Mornington | Short Rural | 317 | 9.777 | 3.421 | 1.5661 | 1.347 | 0.449 | 3 | 308.0195 | 307.9704 | 1.0004 | 0.99946 | 7 | 25.8554 | 25.8554 | 0.11081 | 0.11081 | 0 | 0 | 0 | No
22325 | Ninabah St Howrah | Urban | 892 | 0 | 6.093 | 2.8077 | 2.05 | 0.496 | 7 | 139.1665 | 138.8505 | 1.09 | 1.0887 | 29 | 55.805 | 55.805 | 0.34033 | 0.34033 | 1 | 1 | 1 | No
22326 | Rokeby-Rokeby Terminal | Urban | 348 | 0 | 2.779 | 0.9463 | 0.006 | 0.04 | 6 | 1.3217 | 1.3217 | 0.02087 | 0.02087 | 24 | 8.713 | 8.713 | 0.21043 | 0.21043 | 0 | 0 | 0 | No
22328 | Clarence St Bellerive | Urban | 797 | 2.815 | 4.909 | 2.9093 | 0.556 | 0.047 | 8 | 17.1909 | 17.1909 | 0.086096 | 0.086096 | 19 | 2.016 | 2.016 | 0.027651 | 0.027651 | 0 | 0 | 0 | No
22329 | Howrah-Rokeby-Bellerive Zone | Urban | 1001 | 4.967 | 6.313 | 4.0963 | 0.015 | 0.782 | 5 | 0.72424 | 0.3801 | 0.0064205 | 0.0025682 | 37 | 159.5241 | 73.4526 | 0.46324 | 0.26982 | 0 | 0 | 0 | No
22330 | Rokeby | Short Rural | 73 | 0.785 | 0.185 | 0.2128 | 0.002 | 0.011 | 1 | 2.2133 | 2.2133 | 0.026667 | 0.026667 | 8 | 12.8 | 12.8 | 0.21333 | 0.21333 | 0 | 0 | 0 | No
22331 | Howrah-Tranmere | Urban | 945 | 0 | 6.654 | 3.4403 | 0.008 | 0.08 | 6 | 0.54061 | 0.54061 | 0.0072727 | 0.0072727 | 17 | 6.2545 | 6.2545 | 0.053333 | 0.053333 | 0 | 0 | 0 | No
26161 | Risdon-Otago Bay | Short Rural | 660 | 13.305 | 6.225 | 2.0513 | 0.157 | 6.277 | 15 | 7.2154 | 7.0776 | 0.056665 | 0.051684 | 46 | 185.5612 | 185.5612 | 0.55327 | 0.55327 | 0 | 0 | 0 | No
26162 | Lindisfarne (West)-Geilston Bay | Urban | 578 | 0.089 | 1.914 | 3.0357 | 6.428 | 0.006 | 16 | 363.7904 | 362.4389 | 1.2604 | 1.223 | 3 | 1.457 | 1.457 | 0.010213 | 0.010213 | 1 | 2.2128 | 2.2128 | Yes
26163 | Lindisfarne-Rose Bay-Montagu Bay | Urban | 624 | 3.343 | 1.43 | 1.8672 | 0.108 | 0.052 | 12 | 23.8329 | 23.5982 | 0.31151 | 0.30068 | 2 | 1.8014 | 1.8014 | 0.11467 | 0.11467 | 1 | 2 | 2 | No
26164 | Risdon Brook | Short Rural | 1306 | 9.458 | 4.89 | 3.6962 | 0.585 | 0.128 | 16 | 15.1625 | 14.5565 | 0.27291 | 0.26837 | 13 | 5.0199 | 5.0199 | 0.032709 | 0.032709 | 2 | 2 | 2 | No
26165 | Flagstaff Gully-Warrane (North) - Kennedy Drive | Urban | 369 | 4.321 | 4.522 | 2.8769 | 0.011 | 1.503 | 2 | 3.6369 | 3.6311 | 0.015562 | 0.014409 | 16 | 89.1527 | 89.1527 | 0.13141 | 0.13141 | 2 | 2.0692 | 2.0692 | No
26166 | Lindisfarne (East)-Rosny Park | Urban | 1135 | 4.699 | 4.247 | 3.9439 | 1.406 | 0.067 | 12 | 101.8431 | 101.7859 | 2.0097 | 2.0068 | 4 | 4.2275 | 4.2275 | 0.015003 | 0.015003 | 1 | 1 | 1 | No
26167 | Risdon Vale | Short Rural | 761 | 9.109 | 4.404 | 3.5247 | 1.039 | 6.7 | 25 | 33.1136 | 32.9684 | 2.1677 | 2.163 | 36 | 180.4171 | 180.4171 | 0.55327 | 0.55327 | 2 | 3.0033 | 3.0033 | No
26169 | Lindisfarne (Central)-Montagu Bay-Rosny Matric | Urban | 927 | 2.612 | 5.185 | 3.4041 | 1.143 | 0.175 | 10 | 50.6207 | 50.5829 | 1.1558 | 1.1534 | 11 | 99.6427 | 99.6427 | 0.28289 | 0.28289 | 1 | 1 | 1 | No
27171 | Mornington (West)-Bellerive (East)-Station Service | Urban | 1328 | 4.097 | 3.606 | 4.3186 | 0.326 | 0.439 | 20 | 20.6927 | 20.4768 | 1.0516 | 1.0468 | 21 | 12.4588 | 12.4588 | 0.068966 | 0.068966 | 0 | 0 | 0 | No
27172 | Warrane-Rosny Park | Urban | 783 | 0 | 4.2 | 3.5692 | 3.966 | 0.066 | 13 | 101.948 | 8.7116 | 1.1516 | 0.14954 | 26 | 1.6314 | 1.6314 | 0.02719 | 0.02719 | 1 | 1 | 1 | No
27173 | Cambridge | Short Rural | 181 | 8.586 | 2.168 | 0.5462 | 0.005 | 0.297 | 4 | 1.4887 | 1.0647 | 0.026769 | 0.022398 | 12 | 86.1732 | 86.1732 | 0.32286 | 0.32286 | 2 | 2.1721 | 2.1721 | No
27175 | Warrane-Bellerive (West) | Urban | 1316 | 2.676 | 3.971 | 4.3567 | 0.344 | 0.098 | 8 | 16.9394 | 16.8637 | 1.1349 | 1.134 | 21 | 4.7593 | 4.7593 | 0.04071 | 0.04071 | 0 | 0 | 0 | No
27176 | Warrane-Rosny | Urban | 266 | 0.326 | 5.212 | 3.8613 | 4.32 | 0.036 | 5 | 252.2043 | 252.1954 | 0.86302 | 0.86212 | 4 | 0.21453 | 0.21453 | 0.0035754 | 0.0035754 | 1 | 1.0001 | 1.0001 | No
27178 | Howrah (North) | Urban | 667 | 3.66 | 2.531 | 2.5022 | 0.389 | 0.742 | 5 | 29.699 | 29.6685 | 0.27051 | 0.26959 | 12 | 18.772 | 8.5097 | 0.055347 | 0.032286 | 4 | 3.9804 | 3.9804 | No
28221 | Tranmere-Droughty Point | Short Rural | 902 | 10.772 | 3.432 | 3.6924 | 0.241 | 0.018 | 6 | 2.9252 | 2.9252 | 0.035617 | 0.035617 | 6 | 2.4714 | 2.4714 | 0.016551 | 0.016551 | 0 | 0 | 0 | No
28222 | Howrah-Rokeby | Urban | 745 | 0 | 4.712 | 2.0291 | 0.425 | 0.412 | 12 | 21.2433 | 1.4759 | 0.079184 | 0.016327 | 32 | 48.2539 | 48.2539 | 0.27102 | 0.27102 | 0 | 0 | 0 | No
28223 | Sandford-Cremorne | Short Rural | 966 | 66.841 | 1.833 | 3.0484 | 0.419 | 1.394 | 33 | 55.3549 | 44.3238 | 0.22342 | 0.17843 | 12 | 49.0328 | 49.0328 | 0.17745 | 0.17745 | 3 | 2.0239 | 2.0239 | No
28224 | Lauderdale-Acton | Short Rural | 1298 | 28.197 | 3.209 | 4.363 | 1.445 | 1.029 | 25 | 26.1112 | 26.0687 | 0.33371 | 0.33221 | 22 | 27.0886 | 27.0886 | 0.12727 | 0.12727 | 1 | 0.97548 | 0.97548 | No
28225 | Rokeby Village | Urban | 778 | 0 | 4.788 | 2.0443 | 0.004 | 0.24 | 2 | 0.26362 | 0.24838 | 0.0030476 | 0.0015238 | 32 | 16.48 | 16.48 | 0.094476 | 0.094476 | 0 | 0 | 0 | No
28227 | Clarendon Vale-Pass Road | Short Rural | 585 | 1.414 | 5.731 | 1.9186 | 0.013 | 0.048 | 12 | 0.68265 | 0.56079 | 0.01354 | 0.0078984 | 23 | 2.5472 | 2.2087 | 0.02835 | 0.022708 | 0 | 0 | 0 | No
28228 | Sandford-South Arm-Opossum Bay | Short Rural | 1279 | 79.867 | 3.784 | 3.3475 | 1.153 | 0.343 | 46 | 43.5994 | 35.9962 | 1.1538 | 1.1274 | 24 | 26.2917 | 26.2917 | 0.20814 | 0.20814 | 8 | 6.0115 | 6.0115 | No
28229 | Howrah (South) | Short Rural | 10 | 0.974 | 2.466 | 0.0934 | 0.016 | 0.152 | 1 | 17 | 17 | 1 | 1 | 1 | 222.2727 | 222.2727 | 0.36142 | 0.36142 | 0 | 0 | 0 | No
28230 | Howrah (North) | Short Rural | 76 | 1.616 | 0.661 | 0.2077 | 0.002 | 0.007 | 2 | 1.6254 | 1.6254 | 0.050794 | 0.050794 | 4 | 6.0952 | 6.0952 | 0.10159 | 0.10159 | 0 | 0 | 0 | No
29481 | Mount Rumney-Mornington-Bellerive Zone | Short Rural | 370 | 14.791 | 6.449 | 1.467 | 0.287 | 0.613 | 13 | 28.7565 | 28.7565 | 1.4209 | 1.4209 | 18 | 93.8094 | 93.8094 | 0.33503 | 0.33503 | 0 | 0 | 0 | No
29482 | Backhouse Lane | Short Rural | 90 | 6.283 | 0.699 | 0.9526 | 1.122 | 0.738 | 6 | 93.9143 | 93.9143 | 2.2807 | 2.2807 | 3 | 169.992 | 169.992 | 1.1109 | 1.1109 | 0 | 0 | 0 | No
29483 | Seven Mile Beach | Short Rural | 709 | 23.962 | 1.528 | 2.8198 | 1.31 | 0.32 | 8 | 76.099 | 75.9497 | 2.0163 | 1.9875 | 14 | 21.8116 | 21.8116 | 0.11558 | 0.11558 | 0 | 0 | 0 | No
29485 | Hobart Airport | Short Rural | 1 | 4.164 | 6.177 | 1.9434 | 1.206 | 0 | 1 | 6 | 6 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
29486 | Cranston Parade | Short Rural | 6 | 0.86 | 2.723 | 0.8574 | 1.062 | 0.442 | 1 | 5.9508 | 5.9508 | 0.99181 | 0.99181 | 2 | 2.245 | 2.245 | 0.049161 | 0.049161 | 4 | 4.0328 | 4.0328 | No
29488 | Cambridge-Richmond Golf Course-Brighton | Short Rural | 436 | 39.399 | 2.745 | 3.8677 | 8.73 | 1.694 | 24 | 247.2481 | 247.24 | 4.2333 | 4.2326 | 12 | 44.6098 | 44.6098 | 0.22716 | 0.22716 | 0 | 0 | 0 | No
29489 | Pittwater Road | Short Rural | 205 | 12.664 | 3.793 | 1.9434 | 0.194 | 0.118 | 9 | 7.8617 | 7.8617 | 1.034 | 1.034 | 4 | 48.8431 | 48.8431 | 0.14067 | 0.14067 | 0 | 0 | 0 | No
29490 | Acton Park | Short Rural | 333 | 13.475 | 2.861 | 1.3718 | 0.052 | 0.023 | 9 | 11.4327 | 10.2199 | 1.1084 | 1.0813 | 11 | 1.5813 | 1.5813 | 0.045181 | 0.045181 | 0 | 0 | 0 | No
29491 | Cambridge Park | Urban | 31 | 0 | 2.211 | 1.7528 | 0.446 | 0 | 2 | 32.9566 | 32.9566 | 1.2174 | 1.2174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
30603 | Huonville (North)-Ranelagh-Judbury-Lonnavale | Short Rural | 984 | 39.004 | 1.454 | 5.0489 | 9.382 | 6.677 | 36 | 199.4076 | 199.1132 | 2.3749 | 2.3716 | 36 | 76.5465 | 76.5465 | 0.28778 | 0.28778 | 2 | 2.1313 | 1.0657 | No
30604 | Huonville (Central)-South Franklin-Glen Huon | Short Rural | 968 | 122.902 | 1.83 | 2.6674 | 13.808 | 1.603 | 40 | 439.5935 | 380.8116 | 2.4595 | 2.3961 | 61 | 41.7402 | 41.6672 | 0.16426 | 0.16305 | 5 | 3.6311 | 2.6683 | No
30605 | Huonville (South)-Franklin | Short Rural | 722 | 33.395 | 0.882 | 2.9017 | 0.342 | 0.494 | 12 | 12.27 | 11.4728 | 0.082609 | 0.079239 | 36 | 12.9082 | 11.0071 | 0.097717 | 0.09 | 0 | 0 | 0 | No
30606 | Cradoc-Cygnet-Glaziers Bay | Short Rural | 979 | 71.197 | 0.673 | 3.1513 | 1.387 | 0.272 | 29 | 31.963 | 29.3828 | 0.23226 | 0.20435 | 25 | 10.6634 | 10.6216 | 0.051054 | 0.049529 | 1 | 0.15416 | 0.15416 | No
30607 | Pelverata-Lower Woodstock-Verona Sands | Short Rural | 1516 | 138.768 | 0.804 | 2.4635 | 17.913 | 0.653 | 53 | 771.6286 | 653.8999 | 4.7517 | 4.1821 | 53 | 27.0499 | 26.9938 | 0.14367 | 0.14273 | 9 | 5.281 | 4.2225 | Yes
30608 | Grove-Crabtree-Lower Longley-Mountain River | Short Rural | 1278 | 130.67 | 0.221 | 3.9972 | 4.464 | 8.508 | 57 | 79.2605 | 77.3581 | 1.024 | 1.0134 | 99 | 170.0852 | 170.0852 | 0.57725 | 0.57725 | 3 | 2.4116 | 1.0179 | No
31002 | Wattle Grove-Petcheys Bay-Lymington | Short Rural | 405 | 57.261 | 1.564 | 0.7297 | 1.449 | 0.465 | 9 | 253.0371 | 253.0371 | 1.7285 | 1.7285 | 12 | 61.2549 | 61.1917 | 0.18948 | 0.18843 | 10 | 8.5575 | 8.5575 | No
31007 | Geeveston-Police Point-Surveyors Bay | Short Rural | 1070 | 94.827 | 2.012 | 2.247 | 7.295 | 1.965 | 36 | 410.9831 | 338.3004 | 0.98681 | 0.50754 | 26 | 70.9655 | 70.9655 | 0.2394 | 0.2394 | 6 | 1.6405 | 1.51 | No
31008 | Dover-Southport-Lune River | Short Rural | 1138 | 95.741 | 11.365 | 2.5255 | 11.884 | 1.44 | 32 | 472.9684 | 455.4935 | 4.0161 | 3.8997 | 34 | 44.1561 | 44.0717 | 0.18797 | 0.18657 | 3 | 1.9671 | 1.9671 | No
31010 | Port Huon-Castle Forbes Bay | Short Rural | 460 | 28.95 | 0.378 | 1.1734 | 0.852 | 1.186 | 21 | 84.8596 | 78.3512 | 1.1594 | 1.1251 | 21 | 96.6449 | 96.6449 | 0.3515 | 0.3515 | 0 | 0 | 0 | No
32374 | Kingston (Summerleas Rd)-Kingston Terminal | Urban | 1111 | 3.165 | 7.982 | 4.2043 | 0.132 | 0.242 | 5 | 5.6339 | 5.5315 | 0.037965 | 0.03709 | 51 | 9.6171 | 9.6171 | 0.12473 | 0.12473 | 0 | 0 | 0 | No
32377 | Kingston | Urban | 318 | 0.269 | 2.509 | 3.131 | 0 | 0.366 | 0 | 0 | 0 | 0 | 0 | 3 | 2.3944 | 2.3944 | 0.029259 | 0.029259 | 0 | 0 | 0 | No
32379 | Kingston (Whitewater Cr)-Firthside-Kingston Beach | Short Rural | 1432 | 11.219 | 5.588 | 4.8393 | 1.339 | 0.108 | 14 | 27.8954 | 10.5229 | 0.13335 | 0.099838 | 29 | 5.6042 | 5.6042 | 0.038058 | 0.038058 | 0 | 0 | 0 | No
33271 | Snug-Conningham-Oyster Cove-Bruny Is | Short Rural | 1452 | 144.521 | 3.014 | 2.1889 | 4.472 | 7.258 | 31 | 385.8176 | 244.1762 | 1.4608 | 1.1434 | 43 | 261.9516 | 261.9516 | 0.96516 | 0.96516 | 12 | 3.0832 | 2.897 | No
33272 | Nierinna-West Margate-Kaoota-Sandfly-Longley | Short Rural | 1446 | 115.514 | 0.585 | 4.4404 | 1.569 | 0.589 | 45 | 54.1966 | 28.4807 | 0.89096 | 0.85868 | 103 | 16.0925 | 16.0925 | 0.10305 | 0.10305 | 5 | 1.142 | 1.142 | No
33273 | Electrona Abalone Plant | Urban | 1 | 0.249 | 0.227 | 0.2477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
33274 | Margate,Kingston Term,Huntingfield,Blackmans Bay | Short Rural | 846 | 12.286 | 1.908 | 3.4487 | 1.952 | 1.329 | 11 | 30.9651 | 30.5692 | 1.0259 | 1.022 | 52 | 23.7495 | 23.7495 | 0.27421 | 0.27421 | 0 | 0 | 0 | No
33275 | Tinderbox-Dennes Point-Killora | Short Rural | 64 | 4.616 | 0.725 | 0.1867 | 0.002 | 0.084 | 2 | 3 | 3 | 1 | 1 | 5 | 57.84 | 57.84 | 0.464 | 0.464 | 0 | 0 | 0 | No
33276 | Lower Snug-Nicolls Rivulet-Kettering-Gordon | Short Rural | 1712 | 157.82 | 0.385 | 3.8462 | 6.439 | 0.358 | 55 | 194.0043 | 193.6331 | 1.6162 | 1.6116 | 90 | 11.0402 | 11.0197 | 0.075126 | 0.074785 | 6 | 1.9497 | 1.9497 | No
34251 | Channel Hwy Margate-North Bruny | Short Rural | 1225 | 66.407 | 6.582 | 3.5571 | 8.165 | 0.417 | 28 | 611.3765 | 611.3308 | 3.1683 | 3.166 | 63 | 18.1611 | 18.1611 | 0.12959 | 0.12959 | 4 | 4.0703 | 4.0703 | Yes
34252 | Sirius Drive-Margate - Blackmans Bay | Urban | 1321 | 5.995 | 5.754 | 4.9441 | 0.667 | 0.77 | 10 | 23.5845 | 23.5012 | 0.21284 | 0.21095 | 64 | 39.5395 | 39.5395 | 0.15519 | 0.15519 | 0 | 0 | 0 | No
34253 | North West Blackmans Bay | Urban | 610 | 1.862 | 5.135 | 2.4864 | 1.798 | 0.385 | 5 | 71.0617 | 70.9953 | 0.22794 | 0.22573 | 30 | 37.8811 | 37.8811 | 0.28658 | 0.28658 | 0 | 0 | 0 | No
34254 | Huntingfield Avenue | Short Rural | 1 | 0 | 2.125 | 0.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
34255 | Maranoa Heights-Redwood Village | Short Rural | 390 | 0 | 4.231 | 1.288 | 1.124 | 0.03 | 2 | 110.0002 | 110.0002 | 2 | 2 | 12 | 1.44 | 1.44 | 0.024 | 0.024 | 0 | 0 | 0 | No
34256 | Channel Hwy-Redwood Rd | Short Rural | 884 | 3.191 | 6.555 | 2.7626 | 0.666 | 0.447 | 9 | 26.2949 | 26.2255 | 0.22764 | 0.22497 | 50 | 33.2018 | 33.2018 | 0.24985 | 0.24985 | 0 | 0 | 0 | No
34257 | Summerleas Zone-Huon Hwy-Kingston | Short Rural | 5 | 0 | 3.467 | 0.5239 | 0 | 0.315 | 0 | 0 | 0 | 0 | 0 | 2 | 104.0815 | 104.0815 | 1.2245 | 1.2245 | 0 | 0 | 0 | No
34258 | Legana Ave-Maronoa Rd-Channel Hwy | Urban | 262 | 0.593 | 4.141 | 2.8465 | 0.068 | 0.034 | 4 | 3.0695 | 0.17879 | 0.055302 | 0.0026101 | 4 | 0.31321 | 0.31321 | 0.0052202 | 0.0052202 | 0 | 0 | 0 | No
34259 | Channel Hwy-Kingston (North) | Urban | 1547 | 7.263 | 8.184 | 5.0585 | 0.314 | 0.221 | 12 | 25.7678 | 25.6919 | 1.0554 | 1.0539 | 35 | 15.8597 | 15.8597 | 0.0681 | 0.0681 | 0 | 0 | 0 | No
34260 | Redwood Road | Urban | 709 | 0.086 | 5.483 | 2.2291 | 1.14 | 0.133 | 4 | 94.1694 | 94.1694 | 0.95784 | 0.95784 | 39 | 6.9405 | 6.9405 | 0.073514 | 0.073514 | 0 | 0 | 0 | No
34261 | Leslie Vale-Longley-Bonnet Hill | Short Rural | 445 | 43.558 | 0.184 | 2.6674 | 3.702 | 1.718 | 19 | 315.2867 | 93.0338 | 3.4064 | 2.4084 | 33 | 138.478 | 138.478 | 0.43853 | 0.43853 | 2 | 2.0082 | 1.0041 | No
35010 | New Norfolk Township (South) | Short Rural | 917 | 80.903 | 0.27 | 2.2304 | 4.425 | 2.029 | 25 | 430.8167 | 124.877 | 1.0209 | 0.56168 | 54 | 160.4948 | 160.4948 | 0.37074 | 0.37074 | 3 | 1.2467 | 1.2467 | No
35011 | Lachlan Park-Molesworth-Lachlan | Short Rural | 1103 | 102.515 | 1.707 | 2.4025 | 2.342 | 0.182 | 30 | 97.3135 | 52.7739 | 0.48264 | 0.14244 | 69 | 11.3821 | 11.3489 | 0.083593 | 0.083039 | 14 | 4.602 | 3.9359 | No
35012 | New Norfolk Township (South) | Urban | 479 | 1.945 | 2.26 | 2.6394 | 0.014 | 0.328 | 6 | 0.2985 | 0.26991 | 0.006862 | 0.0022873 | 16 | 4.2845 | 4.2845 | 0.15182 | 0.15182 | 0 | 0 | 0 | No
37001 | Gretna | Short Rural | 120 | 35.48 | 0 | 0.5144 | 0.589 | 0.042 | 11 | 273.7263 | 229.9304 | 0.88094 | 0.68187 | 4 | 44.225 | 44.225 | 0.14727 | 0.14727 | 0 | 0 | 0 | No
37002 | Bushy Park-Plenty | Short Rural | 184 | 30.783 | 0 | 0.7748 | 1.624 | 0.131 | 19 | 241.7312 | 241.6186 | 1.2732 | 1.2692 | 8 | 28.3042 | 28.3042 | 0.10262 | 0.10262 | 0 | 0 | 0 | No
39565 | ANM Backup-New Norfolk Township (North)-Magra | Short Rural | 1635 | 48.791 | 0.99 | 4.7288 | 0.261 | 2.571 | 26 | 9.1978 | 9.12 | 0.15086 | 0.1469 | 102 | 56.8743 | 56.6369 | 0.23659 | 0.23264 | 5 | 2.9268 | 2.9268 | No
39568 | Dromedary | Short Rural | 225 | 32.774 | 1.035 | 0.8497 | 2.476 | 0.095 | 12 | 244.2924 | 1.6476 | 1.0456 | 0.032711 | 17 | 7.2265 | 7.2265 | 0.089317 | 0.089317 | 1 | 0.82751 | 0.82751 | No
39569 | Boyer | Short Rural | 5 | 1.753 | 1.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | No
39570 | Metropolitan Water Board (Lawitta) | Urban | 23 | 12.012 | 0.8 | 5.2356 | 4.8 | 0.571 | 6 | 21.9539 | 21.3665 | 1.0092 | 1.0044 | 3 | 187.1825 | 187.1825 | 0.82602 | 0.82602 | 2 | 1.9981 | 1.9981 | No
39571 | Black Hills-Hayes-Glenora-Westerway Zone Sub | Long Rural | 1054 | 203.483 | 2.533 | 3.9389 | 8.392 | 1.893 | 52 | 285.8297 | 211.4044 | 1.4205 | 1.2434 | 52 | 48.4126 | 48.4126 | 0.17502 | 0.17502 | 16 | 9.762 | 8.6535 | No
40001 | Richmond | Short Rural | 211 | 2.305 | 0.44 | 0.6402 | 1.279 | 0.455 | 2 | 205.3282 | 0.32821 | 1.0595 | 0.0082051 | 4 | 113.3949 | 113.3949 | 0.38564 | 0.38564 | 0 | 0 | 0 | No
40002 | Campania-Colebrook-Rhyndaston | Long Rural | 959 | 223.125 | 0 | 1.8468 | 14.559 | 2.097 | 50 | 662.3688 | 372.6986 | 4.8016 | 2.8183 | 37 | 74.05 | 73.9736 | 0.27571 | 0.27531 | 7 | 2.0644 | 2.0644 | No
40003 | Tea Tree | Short Rural | 260 | 50.945 | 0.152 | 0.6884 | 2.589 | 0.074 | 17 | 364.4576 | 167.7609 | 2.1392 | 1.1306 | 13 | 15.081 | 15.081 | 0.064006 | 0.064006 | 0 | 0 | 0 | No
41511 | Midway Point | Short Rural | 1381 | 16.62 | 2.4 | 3.8983 | 0.894 | 1.148 | 24 | 13.7514 | 13.5732 | 0.18957 | 0.18559 | 60 | 47.1253 | 47.0656 | 0.2411 | 0.2401 | 1 | 1.0591 | 1.0591 | No
41512 | Penna-Richmond-Richmond Zone Sub-Grasstree Hill | Short Rural | 387 | 68.134 | 2.307 | 4.1662 | 4.248 | 2.598 | 29 | 148.2566 | 146.9783 | 2.7505 | 2.7212 | 15 | 74.6015 | 6.9341 | 0.21251 | 0.039008 | 0 | 0 | 0 | No
41513 | Sorell | Short Rural | 1293 | 12.678 | 4.49 | 4.778 | 3.075 | 1.349 | 19 | 94.9899 | 94.9154 | 2.2862 | 2.2856 | 51 | 34.4788 | 26.8805 | 0.12772 | 0.1041 | 1 | 1.02 | 1.02 | No
41514 | Pawlena-Carlton River-Connellys Marsh-Port Arthur | Short Rural | 891 | 132.011 | 5.819 | 1.9434 | 24.634 | 0.48 | 42 | 1196.5636 | 158.7284 | 3.3384 | 1.938 | 37 | 11.8677 | 11.7766 | 0.10153 | 0.10001 | 20 | 14.3441 | 10.9087 | No
41515 | Forcett-Copping-Nubeena-Highcroft-Saltwater River | Long Rural | 2998 | 332.254 | 12.919 | 4.3985 | 80.019 | 0.649 | 165 | 1469.7458 | 403.9496 | 5.2948 | 4.5205 | 61 | 16.6722 | 16.6722 | 0.12001 | 0.12001 | 45 | 12.7088 | 9.7358 | No
41516 | Orielton-Runnymede-Levendale-Buckland-Oatlands | Long Rural | 2170 | 529.541 | 2.038 | 4.1535 | 10.128 | 1.93 | 127 | 271.617 | 261.4365 | 2.9773 | 2.944 | 58 | 51.8322 | 51.8322 | 0.19492 | 0.19492 | 39 | 9.0453 | 7.8841 | No
41517 | Lewisham-Dodges Ferry-Carlton (Nth)-Primrose Sands | Short Rural | 1836 | 46.919 | 2.693 | 3.8105 | 1.034 | 0.169 | 47 | 22.289 | 21.2733 | 0.19075 | 0.17662 | 25 | 4.8826 | 4.6729 | 0.055695 | 0.052201 | 5 | 3.3614 | 3.3614 | No
41518 | Wattle Hill-Nugent-Forcett-Dodges Ferry-Carlton | Short Rural | 2005 | 110.267 | 3.516 | 4.2512 | 7.384 | 0.474 | 81 | 477.2556 | 343.84 | 5.4361 | 5.0339 | 19 | 20.8762 | 20.4707 | 0.082965 | 0.081303 | 11 | 5.5268 | 5.1536 | No
43505 | Chip Mill | Short Rural | 3 | 9.523 | 0.738 | 0 | 0.027 | 0.004 | 5 | 54.5291 | 54.5291 | 2.0046 | 2.0046 | 1 | 0.13558 | 0.13558 | 0.00077474 | 0.00077474 | 0 | 0 | 0 | No
43506 | Triabunna Township | Short Rural | 1742 | 81.7 | 1.217 | 3.4676 | 5.581 | 1.193 | 48 | 258.4726 | 188.0566 | 1.8041 | 1.4106 | 54 | 43.7187 | 43.6619 | 0.19618 | 0.19523 | 3 | 1.2439 | 0 | No
43507 | Swansea | Long Rural | 1448 | 204.769 | 0.562 | 3.3914 | 13.948 | 1.045 | 114 | 585.2257 | 293.4139 | 5.5705 | 4.5493 | 52 | 30.9421 | 21.8631 | 0.12436 | 0.099825 | 43 | 18.8472 | 12.3617 | No
45001 | Gretna-Gretna Zone Substation | Short Rural | 53 | 28.378 | 0.072 | 2.4387 | 5.671 | 1.334 | 15 | 409.2279 | 409.2279 | 3.2596 | 3.2596 | 3 | 80.2945 | 80.2945 | 0.30683 | 0.30683 | 0 | 0 | 0 | No
45002 | Hollow Tree-Bothwell-Jericho | Long Rural | 704 | 291.286 | 0.72 | 1.9434 | 4.613 | 0.561 | 50 | 333.2583 | 333.2327 | 2.5674 | 2.5645 | 21 | 47.8577 | 47.8577 | 0.16578 | 0.16578 | 31 | 12.5552 | 12.3943 | No
45003 | Hamilton Zone Sub-Ouse-Strickland-Lawrenny | Short Rural | 614 | 184.399 | 0.24 | 3.3914 | 23.604 | 2.011 | 66 | 1194.9208 | 1054.1806 | 7.8431 | 7.5405 | 29 | 115.5771 | 115.5771 | 0.41016 | 0.41016 | 31 | 17.4882 | 16.9342 | Yes
48180 | Gagebrook (West)-Old Beach-Austins Ferry-Granton | Short Rural | 1064 | 3.51 | 9.017 | 3.6028 | 0.338 | 1.424 | 12 | 23.8327 | 23.8276 | 1.0483 | 1.0472 | 49 | 35.1213 | 35.1213 | 0.21181 | 0.21181 | 0 | 0 | 0 | No
48181 | Gagebrook (Lamprill Circle-Highway Side) | Short Rural | 313 | 0 | 6.248 | 1.0708 | 0.005 | 0.018 | 4 | 0.48523 | 0.32348 | 0.0099533 | 0.007465 | 15 | 2.2395 | 2.2395 | 0.037325 | 0.037325 | 0 | 0 | 0 | No
48182 | Gagebrook-Old Beach-Austins Ferry | Short Rural | 1469 | 19.343 | 13.556 | 5.3557 | 0.057 | 0.767 | 11 | 13.8607 | 13.8245 | 0.054323 | 0.052383 | 87 | 18.2222 | 18.2222 | 0.18593 | 0.18593 | 0 | 0 | 0 | No
48183 | Bridgewater--Gagebrook | Short Rural | 827 | 47.015 | 2.815 | 2.5645 | 0.21 | 1.523 | 17 | 6.1033 | 5.2349 | 1.0553 | 1.0116 | 60 | 89.964 | 89.964 | 0.31348 | 0.31348 | 0 | 0 | 0 | No
48184 | Bridgewater (East) | Urban | 1139 | 0 | 7.898 | 3.6962 | 1.335 | 1.752 | 12 | 24.2628 | 23.9577 | 0.14698 | 0.14326 | 62 | 19.6047 | 19.6047 | 0.13395 | 0.13395 | 0 | 0 | 0 | No
48185 | Granton-Dromedary-Broadmarsh-Elderslie--Pelham | Short Rural | 1170 | 176.464 | 5.217 | 2.9836 | 2.961 | 1.466 | 52 | 203.423 | 192.8894 | 2.7346 | 2.7126 | 64 | 85.324 | 85.324 | 0.31479 | 0.31479 | 10 | 4.6046 | 3.963 | No
48187 | Bridgewater (West) | Urban | 562 | 1.794 | 3.093 | 1.951 | 0.613 | 3.25 | 5 | 23.7748 | 23.7614 | 0.14089 | 0.13955 | 33 | 101.0727 | 100.5891 | 0.38556 | 0.3775 | 0 | 0 | 0 | No
48188 | Brighton (West) | Short Rural | 1410 | 31.003 | 4.637 | 4.3059 | 0.635 | 0.888 | 22 | 27.6241 | 27.6217 | 0.2579 | 0.2573 | 82 | 37.9745 | 37.9745 | 0.1814 | 0.1814 | 0 | 0 | 0 | No
48190 | Brighton (East)-Dysart-Kempton-Melton Mowbray | Short Rural | 1605 | 158.684 | 2.959 | 4.4888 | 7.882 | 1.593 | 48 | 197.6946 | 197.4743 | 1.8496 | 1.8453 | 128 | 60.4406 | 60.4406 | 0.27788 | 0.27788 | 6 | 3.5402 | 3.5402 | No
48191 | Bridgewater (North) | Short Rural | 98 | 6.245 | 5.723 | 3.2732 | 2.287 | 0.002 | 2 | 4.8276 | 4.8276 | 0.026275 | 0.026275 | 1 | 0.10344 | 0.10344 | 0.0051722 | 0.0051722 | 0 | 0 | 0 | No
49101 | Tods Corner Power Station-Wilburville | Short Rural | 1 | 6.016 | 0.105 | 1.5014 | 28.164 | 1.361 | 3 | 772.4575 | 772.4575 | 1.9474 | 1.9474 | 1 | 60.5263 | 60.5263 | 0.26316 | 0.26316 | 0 | 0 | 0 | Yes
49202 | Tods Corner-Liawenee | Short Rural | 747 | 109.258 | 0.63 | 0.7621 | 7.458 | 4.477 | 14 | 1477.0009 | 1459.2843 | 3.3023 | 3.2229 | 20 | 830.0596 | 830.0596 | 2.9361 | 2.9361 | 12 | 11.6534 | 10.6823 | Yes
49303 | Bronte Park | Short Rural | 273 | 97.945 | 0.71 | 0.7557 | 7.25 | 0.162 | 32 | 2690.7061 | 2571.1663 | 4.0316 | 2.5056 | 7 | 86.7938 | 86.7938 | 0.26752 | 0.26752 | 21 | 11.66 | 11.66 | Yes
49307 | Tarraleah | Short Rural | 12 | 6.942 | 0.349 | 0.4528 | 0.296 | 0.009 | 6 | 1831.9904 | 1826.0191 | 5.9904 | 4.9952 | 2 | 49.8804 | 3.2297 | 0.25359 | 0.014354 | 11 | 11.0526 | 11.0526 | Yes
49411 | Wayatinah | Short Rural | 63 | 10.803 | 0.345 | 0.4954 | 1.68 | 3.373 | 4 | 355.4774 | 36.4772 | 1.2435 | 0.24351 | 6 | 749.5193 | 749.5193 | 2.1299 | 2.1299 | 10 | 10 | 10 | Yes
49412 | Wayatinah-Catagunya-Repulse-Cluny | Short Rural | 24 | 50.042 | 0.355 | 0 | 0 | 0 | 4 | 78.0202 | 78.0202 | 0.069519 | 0.069519 | 9 | 561.3729 | 561.3729 | 1.5762 | 1.5762 | 0 | 0 | 0 | Yes
49621 | Lake St Clair-Derwent Bridge | Short Rural | 40 | 11.889 | 2.2 | 0 | 0 | 0 | 5 | 1916.4016 | 48.306 | 5.0191 | 2.0128 | 2 | 4.2703 | 4.2703 | 1.0105 | 1.0105 | 1 | 0.69523 | 0.69523 | No
49801 | Gordon Area-Strathgordon | Short Rural | 26 | 19.932 | 0 | 0 | 1.505 | 2.106 | 3 | 745.9778 | 745.9778 | 1.1338 | 1.1338 | 2 | 553.2537 | 553.2537 | 1.8346 | 1.8346 | 2 | 0.33084 | 0.33084 | Yes
51001 | Poatina | Short Rural | 52 | 26.981 | 0.197 | 1.7909 | 1.218 | 0 | 24 | 1345.0451 | 1255.6003 | 7.4401 | 7.1064 | 0 | 0 | 0 | 0 | 0 | 6 | 3.187 | 3.187 | Yes
51002 | Bracknell-Liffey-Bishopsbourne-Oaks-Cluan | Long Rural | 783 | 203.388 | 0.335 | 3.273 | 6.034 | 1.712 | 120 | 402.385 | 331.6383 | 4.7415 | 4.2252 | 37 | 83.1227 | 83.1227 | 1.0028 | 1.0028 | 20 | 7.9084 | 4.4786 | No
51003 | Delmont-Cressy-Epping Forest-Blessington | Long Rural | 931 | 237.6 | 3.654 | 9.7146 | 15.672 | 3.148 | 116 | 434.1453 | 319.1706 | 8.8254 | 7.2148 | 35 | 46.7247 | 46.7247 | 0.27902 | 0.27902 | 40 | 14.2074 | 13.4108 | No
53001 | Bell Bay Industrial | Short Rural | 986 | 27.013 | 7.131 | 4.0391 | 14.642 | 0.512 | 28 | 322.3983 | 20.9979 | 1.1314 | 0.21697 | 42 | 31.9962 | 31.9962 | 0.1749 | 0.1749 | 3 | 3.0165 | 0 | No
53002 | Long Reach | Urban | 1 | 7.416 | 1.975 | 3.3533 | 2.878 | 7.896 | 1 | 22.0064 | 22.0064 | 1.0003 | 1.0003 | 1 | 422.8767 | 422.8767 | 0.99971 | 0.99971 | 2 | 1.9965 | 0 | Yes
53003 | George Town (North) | Short Rural | 2086 | 49.23 | 5.849 | 5.3347 | 27.294 | 4.346 | 68 | 678.3887 | 571.4612 | 3.6556 | 3.4768 | 63 | 132.1151 | 132.1151 | 0.48681 | 0.48681 | 2 | 1.972 | 0 | Yes
53004 | Bell Bay Power Station Standby - Beaconsfield Gold | Short Rural | 632 | 66.382 | 13.702 | 1.7909 | 2.902 | 1.265 | 40 | 137.7878 | 47.9336 | 2.7078 | 2.095 | 38 | 43.614 | 43.614 | 0.1923 | 0.1923 | 14 | 8.8031 | 7.2286 | No
53006 | East Tamar Hwy (Sth of GT Sub) | Short Rural | 2 | 0.476 | 0.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | No
53007 | Bell Bay Power Station Main Feeder | Short Rural | 5 | 5.477 | 1.175 | 0.4954 | 0.053 | 0.006 | 3 | 234.2422 | 225 | 2.9242 | 2 | 1 | 62.5968 | 62.5968 | 0.96303 | 0.96303 | 5 | 4.9692 | 2.9815 | No
53008 | Hillwood-The Glen-Pipers River-Weymouth | Long Rural | 1244 | 201.907 | 1.43 | 2.3244 | 36.107 | 4.303 | 77 | 708.2285 | 461.2382 | 2.9756 | 2.0033 | 67 | 149.7536 | 149.7536 | 0.59579 | 0.59579 | 26 | 16.1636 | 6.4886 | No
53009 | George Town (South)-Greens Beach-Beauty Point | Short Rural | 1646 | 101.546 | 3.292 | 3.277 | 9.732 | 3.41 | 62 | 410.938 | 61.2196 | 3.7861 | 2.0089 | 64 | 78.4047 | 78.4047 | 0.45909 | 0.45909 | 11 | 3.5778 | 0.85175 | No
53010 | Bell Bay | Urban | 55 | 7.561 | 2.432 | 4.6488 | 1.957 | 0.888 | 11 | 146.1294 | 108.7572 | 4.7681 | 4.2388 | 6 | 104.5005 | 104.5005 | 0.47107 | 0.47107 | 0 | 0 | 0 | No
54003 | Ringarooma Rd-Scottsdale | Long Rural | 2031 | 296.937 | 1.68 | 5.0045 | 9.982 | 2.977 | 137 | 322.4465 | 248.7916 | 1.8692 | 1.6074 | 56 | 92.4134 | 92.4134 | 0.31496 | 0.31496 | 46 | 11.1472 | 9.5856 | No
54004 | Tongah | Short Rural | 148 | 30.4 | 0.135 | 0.5843 | 0.782 | 0.429 | 17 | 162.9692 | 26.5893 | 0.48957 | 0.3844 | 4 | 47.1746 | 47.1746 | 0.15552 | 0.15552 | 1 | 1.1242 | 1.1242 | No
54005 | Scottsdale-Springfield-Golconda-Lillydale | Long Rural | 1512 | 312.42 | 2.124 | 3.747 | 20.666 | 3.98 | 187 | 514.9824 | 258.6679 | 4.9422 | 3.4361 | 76 | 92.517 | 91.9123 | 0.39333 | 0.39118 | 44 | 14.2336 | 9.8984 | No
54006 | Derby Terminal-Mt Horror-North Scottsdale | Short Rural | 144 | 59.013 | 6.695 | 1.7147 | 0.844 | 0.032 | 23 | 433.2014 | 152.0706 | 3.58 | 1.5621 | 4 | 11.8153 | 11.8153 | 0.17963 | 0.17963 | 2 | 2.0284 | 2.0284 | No
54007 | North Scottsdale-Forester-Bridport-Waterhouse | Urban | 1055 | 10.665 | 1.874 | 4.1027 | 0.516 | 0.755 | 17 | 7.7819 | 7.1935 | 0.11347 | 0.10413 | 26 | 61.9281 | 61.7157 | 0.2419 | 0.24061 | 0 | 0 | 0 | No
55001 | Derby-Branxholm-Legerwood-Ringarooma | Short Rural | 868 | 153.532 | 0.351 | 4.471 | 12.543 | 1.166 | 108 | 553.7586 | 330.1962 | 5.5294 | 4.8329 | 26 | 67.5709 | 67.5709 | 0.45455 | 0.45455 | 25 | 18.6823 | 16.5969 | No
55002 | Herrick-Gladstone-Weldborough | Short Rural | 632 | 174.898 | 14.286 | 1.2194 | 8.404 | 0.706 | 37 | 1014.3289 | 1011.5428 | 4.5735 | 4.5674 | 14 | 45.7553 | 45.7553 | 0.28127 | 0.28127 | 29 | 24.6116 | 24.6116 | Yes
55003 | Winnaleah-Telita | Short Rural | 279 | 72.107 | 1.284 | 1.4353 | 2.843 | 0.745 | 51 | 331.2651 | 181.1505 | 3.1617 | 2.4552 | 11 | 114.8865 | 114.8865 | 0.6589 | 0.6589 | 15 | 7.5618 | 6.6231 | No
56001 | Royal George | Short Rural | 97 | 52.455 | 0.187 | 0.4192 | 0.869 | 0.541 | 22 | 339.2733 | 304.2141 | 3.3607 | 3.2249 | 9 | 450.8359 | 450.8359 | 1.5598 | 1.5598 | 7 | 7 | 3 | Yes
56002 | Rossarden-Storeys Creek | Short Rural | 63 | 31.823 | 0.217 | 0 | 0.582 | 0.953 | 9 | 1130.6222 | 522.9234 | 4.0568 | 3.0409 | 13 | 1866.6937 | 1865.7365 | 5.4118 | 5.3958 | 4 | 4 | 2 | Yes
56003 | Fingal-Mangana-Mathinna-Upper Esk | Short Rural | 494 | 147.662 | 0.366 | 1.6004 | 11.159 | 2.209 | 41 | 789.1557 | 256.8162 | 2.2954 | 1.937 | 31 | 290.8774 | 290.255 | 0.92011 | 0.90973 | 12 | 7.0998 | 5.6111 | No
56004 | Conara-Campbell Town-Ross-Oatlands | Long Rural | 1819 | 524.347 | 3.844 | 6.173 | 13.707 | 6.169 | 190 | 326.3224 | 202.1003 | 1.8117 | 1.4814 | 91 | 226.1587 | 226.1488 | 0.71791 | 0.71775 | 53 | 9.8726 | 6.3114 | No
57003 | Dianas Beach | Short Rural | 536 | 34.803 | 6.979 | 0.9526 | 3.151 | 0.355 | 30 | 364.1322 | 262.64 | 4.5127 | 3.3809 | 22 | 35.7778 | 35.7778 | 0.11109 | 0.11109 | 6 | 6.0783 | 4.0522 | No
57004 | Chain of Lagoons-Bicheno-Coles Bay | Long Rural | 2034 | 214.82 | 4.66 | 5.9063 | 9.115 | 1.942 | 71 | 217.1279 | 143.1985 | 1.403 | 1.1988 | 83 | 36.2792 | 36.2792 | 0.14877 | 0.14877 | 17 | 9.4365 | 6.7067 | No
57005 | St Marys-German Town-Mt Nicholas | Short Rural | 293 | 49.903 | 0.362 | 2.2863 | 0.533 | 0.394 | 13 | 57.163 | 46.2717 | 0.81513 | 0.72333 | 20 | 8.9462 | 8.9462 | 0.051187 | 0.051187 | 3 | 2.985 | 1.99 | No
57006 | Binalong Bay. and Weldborough | Long Rural | 3409 | 216.729 | 19.415 | 6.4398 | 15.845 | 15.203 | 122 | 261.5983 | 207.5392 | 5.0735 | 4.7146 | 91 | 179.6828 | 179.6828 | 0.55672 | 0.55672 | 29 | 12.1736 | 9.4766 | No
61021 | Riverside-Newnham-Alanvale | Short Rural | 1531 | 105.973 | 5.296 | 5.1061 | 10.714 | 0.97 | 58 | 282.9806 | 38.8362 | 2.4941 | 1.3415 | 20 | 33.3162 | 33.3162 | 0.18912 | 0.18912 | 18 | 17.2462 | 15.2437 | No
61022 | Prospect Vale | Short Rural | 10 | 6.558 | 0.91 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 1 | 34.4445 | 34.4445 | 0.11111 | 0.11111 | 1 | 1 | 1 | No
61023 | Glengarry-Birralee-Beaconsfield-Beauty Point | Long Rural | 1693 | 323.384 | 0.8 | 4.0772 | 16.724 | 1.877 | 143 | 458.66 | 315.6277 | 4.7396 | 4.4915 | 92 | 45.205 | 45.205 | 0.21588 | 0.21588 | 61 | 16.5852 | 13.7293 | No
61024 | City (North) | Urban | 326 | 0 | 6.9 | 6.7827 | 0.276 | 0.828 | 8 | 2.8969 | 0.055107 | 0.15629 | 0.00038005 | 5 | 10.2 | 10.2 | 0.083895 | 0.083895 | 2 | 2.0001 | 2.0001 | No
61025 | Trevallyn-City (South) | Urban | 1709 | 12.75 | 4.787 | 6.1095 | 6.196 | 4.669 | 37 | 174.6257 | 173.7245 | 1.0913 | 1.0866 | 32 | 81.1602 | 81.1602 | 0.30913 | 0.30913 | 8 | 8.005 | 8.005 | No
61026 | City (Central) | Urban | 215 | 1.457 | 4.997 | 4.5345 | 0.367 | 0.67 | 1 | 0.69615 | 0.69615 | 0.00044285 | 0.00044285 | 6 | 6.7755 | 6.7755 | 0.085248 | 0.085248 | 2 | 2 | 2 | No
61027 | Trevallyn-West Launceston | Urban | 2311 | 12.433 | 3.901 | 7.3924 | 0.43 | 5.509 | 26 | 10.619 | 9.4603 | 0.098497 | 0.095292 | 62 | 78.599 | 78.599 | 0.42124 | 0.42124 | 0 | 0 | 0 | No
61028 | Rosevears-Exeter-Deviot | Short Rural | 1619 | 69.531 | 2.905 | 4.7758 | 12.621 | 2.313 | 64 | 267.658 | 190.0467 | 2.5953 | 1.6238 | 56 | 57.4593 | 57.3382 | 0.26646 | 0.26444 | 25 | 16.267 | 12.4222 | No
61029 | Alanvale-Rocherlea | Urban | 2007 | 12.996 | 11.606 | 7.7734 | 0.207 | 2.97 | 24 | 2.4714 | 2.4186 | 0.038098 | 0.037458 | 41 | 18.3288 | 18.2904 | 0.14127 | 0.14063 | 0 | 0 | 0 | No
61037 | West Riverside-Summerhill-Prospect | Short Rural | 865 | 22.567 | 1.776 | 3.1246 | 0.272 | 1.005 | 15 | 17.7745 | 13.7885 | 0.18354 | 0.15661 | 15 | 306.7404 | 306.7404 | 0.77862 | 0.77862 | 7 | 6.7936 | 4.8525 | No
61039 | City (Central / North) | Urban | 636 | 0 | 7.953 | 5.792 | 0.823 | 0.612 | 8 | 10.8974 | 10.8974 | 0.18115 | 0.18115 | 8 | 2.9435 | 2.9435 | 0.012369 | 0.012369 | 0 | 0 | 0 | No
61040 | City (Central)-Launceston General Hospital | Urban | 1145 | 0 | 8.82 | 7.0494 | 0.33 | 0.291 | 10 | 2.7897 | 1.7858 | 1.0392 | 0.038832 | 11 | 1.6253 | 1.6253 | 0.0073966 | 0.0073966 | 0 | 0 | 0 | No
61041 | Trevallyn-West Launceston-Prospect | Short Rural | 1730 | 17.33 | 2.354 | 4.6869 | 0.412 | 1.318 | 22 | 25.167 | 23.881 | 1.3149 | 0.32744 | 55 | 25.3191 | 25.3191 | 0.16427 | 0.16427 | 9 | 9.1408 | 9.1408 | No
61043 | Riverside-Legana-Dilston-Turners Marsh-Lilydale | Short Rural | 2949 | 105.287 | 8.966 | 9.8692 | 8.117 | 5.777 | 90 | 97.9334 | 88.9104 | 2.4085 | 1.4036 | 47 | 94.1784 | 94.1613 | 0.31908 | 0.3188 | 26 | 14.3321 | 13.2159 | No
62004 | Mowbray Heights | Urban | 393 | 3.637 | 3.342 | 5.1357 | 1.716 | 0.136 | 9 | 3.8171 | 3.8171 | 0.036378 | 0.036378 | 14 | 0.54568 | 0.54568 | 0.0090946 | 0.0090946 | 0 | 0 | 0 | No
62005 | Alanvale-Newnham | Urban | 1161 | 6.135 | 3.185 | 5.5738 | 3.688 | 2.555 | 17 | 59.7162 | 5.5647 | 1.0505 | 0.047284 | 44 | 12.9887 | 12.9887 | 0.061516 | 0.061516 | 0 | 0 | 0 | No
62006 | Remount Rd-Ravenswood | Short Rural | 919 | 7.329 | 4.156 | 3.0484 | 3.904 | 0.664 | 31 | 234.1053 | 206.2311 | 4.4387 | 3.4045 | 29 | 45.1147 | 45.1147 | 0.18483 | 0.18483 | 1 | 0.93531 | 0.93531 | No
62008 | Invermay-Inveresk | Urban | 1798 | 8.658 | 3.709 | 6.6152 | 1.513 | 0.641 | 34 | 14.3475 | 12.98 | 0.078205 | 0.073647 | 40 | 29.321 | 29.321 | 0.27208 | 0.27208 | 0 | 0 | 0 | No
62009 | East Launceston | Urban | 849 | 9.044 | 3.44 | 6.4677 | 1.924 | 1.843 | 19 | 62.2921 | 62.0823 | 2.0353 | 2.0326 | 25 | 23.1454 | 23.1454 | 0.13079 | 0.13079 | 0 | 0 | 0 | No
62010 | Mayfield | Short Rural | 1651 | 14.48 | 5.173 | 4.6083 | 8.184 | 0.502 | 48 | 213.5168 | 211.8805 | 1.5299 | 1.5197 | 86 | 9.7825 | 9.712 | 0.089052 | 0.087877 | 1 | 1.0073 | 1.0073 | No
62013 | Invermay | Urban | 679 | 5.582 | 4.391 | 4.434 | 0.854 | 1.249 | 19 | 47.2207 | 46.284 | 1.1083 | 1.0899 | 16 | 68.8464 | 68.8464 | 0.39659 | 0.39659 | 0 | 0 | 0 | No
65060 | Western Junction-Breadalbane-Perth-Evandale | Urban | 247 | 0.594 | 3.753 | 1.8214 | 0.335 | 0.052 | 5 | 18.4352 | 17.4112 | 1.0048 | 1.0016 | 1 | 27 | 27 | 0.15 | 0.15 | 0 | 0 | 0 | No
65061 | Techno Park Drive Norwood | Urban | 901 | 5.505 | 3.665 | 3.5781 | 1.238 | 0.632 | 12 | 17.4448 | 17.0776 | 1.0289 | 1.0281 | 29 | 7.6132 | 7.6132 | 0.1237 | 0.1237 | 0 | 0 | 0 | No
65062 | Kings Meadows-South Launceston | Urban | 1245 | 7.473 | 2.953 | 4.8012 | 0.139 | 2.035 | 8 | 15.59 | 0.95584 | 0.079707 | 0.018035 | 21 | 38.7247 | 38.7247 | 0.28952 | 0.28952 | 1 | 1.0046 | 1.0046 | No
65063 | St Leonards South | Urban | 519 | 5.731 | 1.588 | 3.9058 | 6.87 | 0.777 | 20 | 364.8857 | 71.185 | 2.394 | 1.2759 | 7 | 20.8729 | 20.8729 | 0.10392 | 0.10392 | 6 | 6 | 4 | No
65064 | South Norwood-Punchbowl | Urban | 537 | 0 | 0.869 | 3.902 | 0 | 4.047 | 7 | 10.1496 | 8.5925 | 0.1012 | 0.081345 | 26 | 62.0752 | 31.6509 | 0.26837 | 0.18831 | 0 | 0 | 0 | No
65065 | Franklin Village | Urban | 1006 | 5.735 | 4.945 | 7.7506 | 2.192 | 1.928 | 16 | 200.4527 | 195.3486 | 2.0741 | 2.0506 | 37 | 45.2497 | 45.2497 | 0.25421 | 0.25421 | 5 | 4.9966 | 4.9966 | No
65066 | Relbia-Evandale-Upper Blessington | Long Rural | 1833 | 256.886 | 4.401 | 4.7327 | 3.566 | 2.624 | 94 | 167.8054 | 151.6971 | 1.8772 | 1.8076 | 56 | 107.7793 | 107.7793 | 0.42219 | 0.42219 | 31 | 12.8985 | 11.8926 | No
65067 | Waverley-White Hills | Short Rural | 611 | 143.627 | 3.088 | 1.9167 | 11.849 | 1.455 | 90 | 997.4808 | 758.3608 | 4.8044 | 3.9812 | 38 | 76.8635 | 76.8635 | 0.40434 | 0.40434 | 37 | 13.9953 | 13.2907 | Yes
66101 | Waverley-St Leonards | Short Rural | 664 | 13.42 | 1.644 | 1.9929 | 0.54 | 2.197 | 23 | 35.1909 | 29.2092 | 0.25198 | 0.21662 | 27 | 68.6738 | 68.6738 | 0.20046 | 0.20046 | 0 | 0 | 0 | No
66102 | Norwood-Newstead-East Launceston-Launceston | Urban | 1211 | 7.483 | 2.413 | 6.3636 | 18.492 | 3.363 | 36 | 450.8399 | 349.0325 | 5.2695 | 5.229 | 21 | 70.7541 | 64.419 | 0.29375 | 0.27152 | 0 | 0 | 0 | Yes
66103 | Norwood-Newstead-East Lton-South Lton-Launceston | Urban | 1550 | 8.825 | 3.552 | 6.2873 | 2.539 | 0.297 | 17 | 79.109 | 78.8826 | 1.0207 | 1.0197 | 24 | 20.0086 | 20.0086 | 0.095184 | 0.095184 | 0 | 0 | 0 | No
66105 | Ravenswood-Waverley | Urban | 1273 | 7.623 | 3.471 | 3.5857 | 0.187 | 1.53 | 16 | 3.9737 | 3.9248 | 0.043631 | 0.040421 | 59 | 55.1454 | 55.1093 | 0.26399 | 0.26319 | 0 | 0 | 0 | No
66106 | Newstead-South Launceston | Urban | 1621 | 9.617 | 2.58 | 5.4224 | 13.069 | 1.039 | 29 | 405.3763 | 405.0379 | 4.1267 | 4.1116 | 21 | 17.9751 | 17.9404 | 0.11121 | 0.11063 | 6 | 6 | 6 | Yes
66107 | High St East Launceston | Urban | 1270 | 4.593 | 2.707 | 7.24 | 7.038 | 0.391 | 23 | 613.2509 | 278.0064 | 3.4645 | 3.3357 | 11 | 18.0835 | 18.0835 | 0.13421 | 0.13421 | 0 | 0 | 0 | Yes
66109 | St Leonards | Urban | 580 | 5.951 | 0.229 | 1.9738 | 0.396 | 1.843 | 9 | 60.4345 | 60.4201 | 0.2614 | 0.25995 | 19 | 74.8725 | 74.8725 | 0.23155 | 0.23155 | 0 | 0 | 0 | No
67081 | Prospect | Short Rural | 932 | 4.241 | 18.39 | 4.6488 | 0.176 | 1.359 | 9 | 0.91456 | 0.91456 | 0.036582 | 0.036582 | 23 | 33.2692 | 33.2692 | 0.44284 | 0.44284 | 0 | 0 | 0 | No
67082 | Carrick-Westbury | Long Rural | 1383 | 223.452 | 7.845 | 4.5726 | 42.089 | 2.181 | 206 | 1460.7518 | 911.8448 | 13.1679 | 12.9226 | 60 | 22.8738 | 22.8738 | 0.15222 | 0.15222 | 12 | 1.556 | 1.3913 | Yes
67083 | Pateena-Longford | Short Rural | 463 | 35.402 | 0.559 | 4.5726 | 26.17 | 2.959 | 49 | 931.6965 | 517.6492 | 1.3646 | 0.35208 | 12 | 15.8384 | 15.8384 | 0.049145 | 0.049145 | 4 | 4.0179 | 3.0134 | No
67084 | Hagley-Westbury Nth-Quamby Bend-Selbourne | Short Rural | 917 | 98.056 | 23.215 | 5.4109 | 5.585 | 2.051 | 87 | 172.3698 | 114.5571 | 3.1733 | 2.1194 | 20 | 32.6347 | 32.6347 | 0.14541 | 0.14541 | 27 | 6.119 | 5.7332 | No
67085 | Blackstone Heights | Short Rural | 650 | 17.399 | 1.67 | 4.3059 | 2.222 | 1.016 | 17 | 63.8576 | 63.8576 | 3.1179 | 3.1179 | 21 | 11.2214 | 11.2214 | 0.058946 | 0.058946 | 7 | 7.143 | 7.143 | No
67086 | Prospect Vale | Urban | 1839 | 7.462 | 8.953 | 6.2111 | 0.124 | 1.655 | 10 | 2.9548 | 2.9463 | 0.041239 | 0.0401 | 45 | 49.3305 | 49.3305 | 0.35741 | 0.35741 | 4 | 4.057 | 3.0427 | No
67087 | Cressy | Short Rural | 1940 | 181.761 | 8.67 | 6.2873 | 25.287 | 3.602 | 183 | 1269.7033 | 285.5238 | 7.978 | 4.8624 | 84 | 81.0584 | 81.0584 | 0.372 | 0.372 | 6 | 2.2692 | 1.9575 | No
67088 | Travellers Rest-Hadspen | Short Rural | 1045 | 19.539 | 0.536 | 3.0484 | 3.589 | 0.151 | 26 | 165.4188 | 14.9973 | 1.1623 | 0.1544 | 19 | 13.6486 | 13.6486 | 0.074382 | 0.074382 | 3 | 3.0077 | 2.0051 | No
67089 | Trevallyn Terminal | Short Rural | 1248 | 16.045 | 2.968 | 4.4583 | 2.893 | 2.156 | 14 | 96.9398 | 96.8221 | 1.2844 | 1.2833 | 52 | 62.9774 | 62.9774 | 0.52132 | 0.52132 | 7 | 7 | 7 | No
67090 | Evandale-Perth | Short Rural | 1840 | 80.396 | 6.842 | 8.0783 | 29.584 | 3.654 | 112 | 415.3571 | 318.7915 | 6.4722 | 6.0775 | 67 | 54.1665 | 43.2282 | 0.30201 | 0.2649 | 15 | 8.0235 | 7.2698 | No
67091 | Young Town-Kings Meadows-South Launceston | Short Rural | 1493 | 12.183 | 6.126 | 5.2966 | 0.205 | 0.986 | 23 | 5.6691 | 4.4213 | 0.081523 | 0.079062 | 13 | 20.2692 | 20.2323 | 0.10998 | 0.10936 | 0 | 0 | 0 | No
80001 | Wesley Vale-Port Sorell | Short Rural | 3237 | 76.564 | 5.182 | 8.4433 | 9.049 | 1.034 | 117 | 241.5904 | 159.0497 | 2.4162 | 2.2594 | 94 | 13.4677 | 13.4677 | 0.14185 | 0.14185 | 9 | 7.5046 | 6.0937 | No
80002 | Quioba-Spreyton | Urban | 717 | 24.131 | 0.911 | 8.1844 | 66.29 | 4.208 | 37 | 586.972 | 347.7572 | 1.4576 | 1.3257 | 18 | 26.696 | 26.696 | 0.10836 | 0.10836 | 5 | 5.0066 | 4.0053 | Yes
80003 | Quoiba-Spreyton | Urban | 424 | 11.903 | 1.369 | 6.4779 | 44.515 | 20.832 | 19 | 339.9893 | 219.9741 | 2.0448 | 1.0133 | 23 | 125.3447 | 125.2769 | 0.50018 | 0.49905 | 3 | 3.053 | 2.0353 | Yes
80004 | Devonport CDB-Marine Board Area | Urban | 1177 | 5.07 | 4.59 | 5.1667 | 11.877 | 0.392 | 23 | 166.3016 | 144.4672 | 3.1156 | 3.0893 | 37 | 10.7557 | 10.7557 | 0.10819 | 0.10819 | 0 | 0 | 0 | No
80005 | Devonport | Urban | 1685 | 9.934 | 3.932 | 5.1511 | 10.708 | 0.107 | 35 | 129.323 | 34.9961 | 0.24079 | 0.16549 | 34 | 2.3408 | 2.3408 | 0.076468 | 0.076468 | 3 | 3.0022 | 0 | No
80006 | Devonport (West)-Don-Forth-Leith | Short Rural | 782 | 68.99 | 1.004 | 4.496 | 15.068 | 0.398 | 63 | 624.9159 | 174.9261 | 1.4695 | 0.38001 | 33 | 33.5155 | 33.5155 | 0.13072 | 0.13072 | 11 | 6.6718 | 2.5594 | No
80007 | East Devonport-Airport | Short Rural | 1901 | 21.397 | 3.63 | 6.5079 | 37.879 | 0.444 | 50 | 845.5291 | 382.5064 | 3.067 | 2.044 | 86 | 8.636 | 8.636 | 0.090612 | 0.090612 | 4 | 4.0041 | 3.0031 | No
80008 | Devonport (Central) | Urban | 1879 | 8.373 | 2.196 | 5.2204 | 3.908 | 0.279 | 32 | 38.4447 | 4.6645 | 0.095393 | 0.07345 | 43 | 4.7305 | 4.7305 | 0.039244 | 0.039244 | 0 | 0 | 0 | No
80009 | James St | Urban | 1592 | 5.476 | 4.441 | 6.3552 | 5.318 | 1.252 | 28 | 94.8603 | 0.98495 | 1.0576 | 0.0072816 | 39 | 10.5716 | 10.5716 | 0.11153 | 0.11153 | 1 | 1 | 0 | No
80010 | Devonport West-Don Heads | Urban | 2001 | 13.367 | 3.739 | 7.3154 | 10.92 | 0.279 | 34 | 276.8646 | 14.1283 | 1.0996 | 0.0971 | 57 | 16.2409 | 16.2409 | 0.082496 | 0.082496 | 1 | 1.0005 | 0 | No
80011 | Latrobe-Wesley Vale-Port Sorell | Short Rural | 1960 | 99.157 | 3.908 | 6.2873 | 31.925 | 0.911 | 101 | 506.1269 | 210.2536 | 1.8471 | 1.5485 | 74 | 14.8713 | 14.8166 | 0.13696 | 0.13605 | 19 | 6.7951 | 4.887 | No
82001 | Kindred-Forth-Turners Beach | Short Rural | 597 | 95.122 | 0.186 | 4.645 | 51.544 | 1.275 | 155 | 1325.836 | 762.6165 | 7.024 | 6.0593 | 30 | 89.3329 | 89.3329 | 0.18033 | 0.18033 | 59 | 28.6255 | 25.0311 | Yes
82002 | Ulverstone-Penguin | Short Rural | 2217 | 22.237 | 2.892 | 6.3788 | 31.941 | 2.535 | 78 | 677.2073 | 387.39 | 4.2662 | 3.2394 | 104 | 52.8648 | 52.8342 | 0.26586 | 0.26535 | 11 | 8.3437 | 3.2606 | No
82003 | Ulverstone (West)-Penguin | Short Rural | 2265 | 64.643 | 1.981 | 6.3064 | 6.404 | 1.36 | 83 | 341.9842 | 52.4449 | 0.49895 | 0.36426 | 94 | 11.9128 | 11.8037 | 0.079189 | 0.077371 | 9 | 3.1011 | 2.7969 | No
82004 | Gawler-Preston-Gunns Plains-Nietta | Short Rural | 856 | 185.258 | 0.213 | 2.5416 | 40.653 | 0.487 | 127 | 1871.6358 | 799.1776 | 7.9889 | 6.2533 | 48 | 57.0161 | 56.936 | 0.2893 | 0.28797 | 16 | 5.0642 | 4.619 | Yes
82005 | Ulverstone (East) | Urban | 1874 | 9.99 | 3.051 | 6.2835 | 8.425 | 0.479 | 47 | 80.0127 | 3.773 | 0.73881 | 0.039329 | 49 | 36.0866 | 36.0531 | 0.14446 | 0.1439 | 5 | 3.1491 | 2.614 | No
82006 | Simplot | Urban | 211 | 2.311 | 1.108 | 7.6782 | 8.078 | 0.08 | 6 | 551.2691 | 551.2613 | 4.0016 | 4.0008 | 6 | 0.28062 | 0.28062 | 0.004677 | 0.004677 | 0 | 0 | 0 | Yes
82007 | Gawler-Upper Castra | Short Rural | 546 | 101.825 | 1.835 | 1.9815 | 30.676 | 0.095 | 80 | 2039.6755 | 380.2176 | 6.6076 | 4.4794 | 26 | 5.1481 | 5.1037 | 0.05787 | 0.05713 | 13 | 4.6812 | 1.8191 | No
82008 | Turners Beach | Short Rural | 1786 | 21.556 | 6.522 | 6.0587 | 16.25 | 3.599 | 72 | 468.2787 | 69.7038 | 8.5475 | 3.7 | 64 | 60.9878 | 60.9878 | 0.22483 | 0.22483 | 4 | 1.6965 | 1.6965 | No
85001 | Beulah-Sheffield-Nook-Wilmot-Cradle Mountain | Long Rural | 2518 | 397.147 | 13.16 | 6.4969 | 161.263 | 3.213 | 190 | 3622.8675 | 598.2546 | 7.5452 | 5.3295 | 112 | 56.9546 | 56.942 | 0.23973 | 0.23952 | 76 | 9.8362 | 6.9375 | No
85002 | Elizabeth Town-Deloraine-Meander-Exton-Westbury | Long Rural | 1879 | 336.146 | 1.945 | 5.5519 | 71.192 | 6.476 | 212 | 1127.9476 | 267.4607 | 5.1303 | 1.9196 | 97 | 116.8427 | 115.2344 | 0.46744 | 0.45979 | 42 | 16.1724 | 8.5201 | No
85003 | Big Bend-Tarleton-Melrose-Barrington | Short Rural | 1390 | 174.163 | 0.548 | 4.0811 | 35.702 | 0.536 | 145 | 1196.1129 | 501.9164 | 7.4666 | 5.1734 | 45 | 24.5455 | 24.5063 | 0.082756 | 0.082104 | 20 | 8.7357 | 5.8953 | No
85004 | Sassafras-Moriarty-Thirlstane | Short Rural | 640 | 166.668 | 0.297 | 5.2242 | 39.066 | 1.688 | 195 | 900.0858 | 195.3345 | 4.0948 | 1.8301 | 27 | 45.0517 | 45.032 | 0.15467 | 0.15435 | 33 | 9.9346 | 4.8141 | No
85005 | Goliath Portland Cement (South) | Urban | 1 | 0.412 | 0.576 | 11.4392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
85006 | Needles-Deloraine-Mole Creek-Western Creek | Long Rural | 2294 | 406.222 | 3.181 | 8.3793 | 22.335 | 8.654 | 210 | 356.4187 | 301.4122 | 4.2525 | 4.2008 | 113 | 106.7148 | 103.8998 | 0.44933 | 0.4368 | 50 | 14.1555 | 12.1921 | No
85008 | Latrobe | Short Rural | 1445 | 42.025 | 1.536 | 5.7158 | 26.734 | 2.074 | 67 | 1239.6404 | 170.3619 | 1.641 | 1.3231 | 88 | 37.9448 | 37.7051 | 0.54806 | 0.54407 | 2 | 2.0072 | 0 | No
89001 | Rowallan-Lemonthyme-Parsons Falls | Short Rural | 3 | 25.184 | 0.132 | 0 | 0 | 0 | 1 | 1764.6738 | 1764.6738 | 0.30233 | 0.30233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes
90019 | Massey Sawmill | Urban | 4 | 0.666 | 0.121 | 2.8579 | 0 | 0.374 | 0 | 0 | 0 | 0 | 0 | 1 | 0.1901 | 0.1901 | 0.0031683 | 0.0031683 | 0 | 0 | 0 | No
90020 | Burnie CBD (East)-Marine Board | Urban | 111 | 0.921 | 2.602 | 1.8576 | 0 | 0.057 | 0 | 0 | 0 | 0 | 0 | 2 | 7.6589 | 7.6589 | 0.068119 | 0.068119 | 0 | 0 | 0 | No
90021 | Burnie CBD (North)-Marine Board | Urban | 181 | 1.016 | 3.426 | 2.0148 | 0 | 0.041 | 0 | 0 | 0 | 0 | 0 | 1 | 9.4118 | 9.4118 | 0.078431 | 0.078431 | 0 | 0 | 0 | No
90023 | Burnie CBD (West) | Urban | 480 | 1.735 | 1.713 | 3.9725 | 0.022 | 0.996 | 4 | 0.32611 | 0.32611 | 0.0040764 | 0.0040764 | 11 | 32.6739 | 32.6739 | 0.17197 | 0.17197 | 1 | 1 | 1 | No
90024 | Burnie CBD (Central / West) | Urban | 202 | 0 | 3.975 | 2.5221 | 0.667 | 0.484 | 5 | 15.0355 | 14.9373 | 0.11636 | 0.11455 | 8 | 62.1114 | 62.1114 | 0.38909 | 0.38909 | 3 | 3.1705 | 3.1705 | No
91001 | Ridgley-Yolla-Calder-Hampshire-Preolenna | Short Rural | 819 | 96.619 | 0.424 | 4.5726 | 44.341 | 3.6 | 83 | 949.6313 | 320.5957 | 2.3419 | 1.116 | 49 | 72.3073 | 72.3073 | 0.22251 | 0.22251 | 8 | 5.6794 | 3.4493 | No
91002 | Natone-Cuprona | Short Rural | 822 | 141.452 | 0.687 | 3.2008 | 20.873 | 0.123 | 102 | 1036.1055 | 539.5967 | 4.8471 | 3.4931 | 34 | 4.7473 | 4.688 | 0.042079 | 0.04109 | 35 | 19.5809 | 13.0077 | No
91003 | Upper Burnie-Wivenhoe | Urban | 1090 | 15.675 | 2.891 | 7.1765 | 27.725 | 6.562 | 29 | 79.5312 | 28.8686 | 0.11206 | 0.072867 | 60 | 21.5925 | 21.5541 | 0.12642 | 0.12578 | 2 | 2.0043 | 1.0021 | No
91004 | Wynyard (West)-Moorleah | Short Rural | 1813 | 168.867 | 1.281 | 7.8624 | 49.091 | 2.363 | 188 | 876.4142 | 412.6159 | 5.3376 | 3.7951 | 74 | 25.5911 | 25.5629 | 0.12772 | 0.12725 | 29 | 8.9932 | 5.4597 | No
91005 | Somerset (South)-Wynyard (East)-Table Cape | Short Rural | 1374 | 41.66 | 4.122 | 3.8613 | 1.796 | 0.239 | 41 | 74.2724 | 25.1934 | 0.37638 | 0.27332 | 56 | 14.9855 | 14.9855 | 0.15874 | 0.15874 | 2 | 1.7846 | 0.8923 | No
91006 | Camdale-Somerset (North)-Wynyard (East) | Short Rural | 1962 | 33.877 | 4.983 | 8.5991 | 27.775 | 1.669 | 61 | 423.0661 | 399.7224 | 1.6595 | 1.6488 | 96 | 27.8298 | 27.8298 | 0.13531 | 0.13531 | 8 | 7.5812 | 4.0512 | No
91007 | Burnie (West)-Cooee | Urban | 1328 | 7.079 | 0.619 | 4.001 | 3.031 | 2.89 | 33 | 71.4462 | 3.6929 | 0.21281 | 0.080204 | 41 | 62.9766 | 62.9067 | 0.34047 | 0.3393 | 0 | 0 | 0 | No
91008 | Burnie (East) | Urban | 3692 | 22.039 | 4.843 | 10.7202 | 20.974 | 2.591 | 81 | 446.0354 | 87.8541 | 2.2633 | 1.2591 | 150 | 25.181 | 25.026 | 0.15118 | 0.1486 | 2 | 1.996 | 0.99798 | No
91009 | Wynyard | Short Rural | 2113 | 28.599 | 7.171 | 6.1857 | 5.521 | 2.771 | 53 | 436.0861 | 342.8126 | 1.45 | 1.3357 | 88 | 64.3224 | 64.197 | 0.35213 | 0.35004 | 3 | 2.1167 | 2.0131 | No
91010 | North West Private Hospital | Urban | 850 | 5.602 | 3.495 | 6.1222 | 9.413 | 3.235 | 12 | 74.3153 | 74.3046 | 2.0608 | 2.0597 | 35 | 28.8779 | 28.8779 | 0.11931 | 0.11931 | 1 | 1.0001 | 1.0001 | No
91011 | Penguin-Riana | Short Rural | 1304 | 146.242 | 2.615 | 3.8867 | 29.43 | 0.828 | 136 | 1014.1528 | 519.5941 | 5.438 | 4.2733 | 60 | 24.0986 | 24.0329 | 0.1073 | 0.1062 | 39 | 20.693 | 10.8515 | No
91012 | Mooreville | Long Rural | 1178 | 258.598 | 7.132 | 3.7978 | 34.585 | 4.197 | 101 | 1194.2402 | 1101.7022 | 7.908 | 7.8467 | 83 | 127.6128 | 122.4484 | 0.37697 | 0.36018 | 36 | 12.5199 | 9.0704 | Yes
93001 | Irishtown-Forest-Stanley-Mengha-Trowutta | Short Rural | 865 | 191.406 | 0.475 | 5.4152 | 14.952 | 2.989 | 88 | 320.587 | 200.7536 | 2.3268 | 1.7672 | 30 | 63.9141 | 63.9141 | 0.22819 | 0.22819 | 16 | 3.7595 | 3.6214 | No
93002 | Marrawah-Mella | Short Rural | 950 | 180.365 | 3.736 | 6.7043 | 13.016 | 5.756 | 75 | 213.6944 | 163.3492 | 2.4749 | 1.5167 | 36 | 110.4044 | 110.4044 | 0.33299 | 0.33299 | 20 | 5.1686 | 4.9326 | No
93003 | Edith Creek-Trowutta-Togari-Marrawah-Woolnorth | Short Rural | 678 | 53.818 | 1.336 | 5.5909 | 14.861 | 7.225 | 37 | 341.8956 | 341.8095 | 2.1767 | 2.1731 | 33 | 184.8069 | 184.8069 | 0.76965 | 0.76965 | 4 | 2.1951 | 2.1951 | No
93004 | Smithton-McCains | Urban | 295 | 2.403 | 0.287 | 3.9629 | 0.835 | 0.038 | 2 | 62.3842 | 62.3749 | 0.94562 | 0.94507 | 3 | 148.8814 | 148.8814 | 0.87648 | 0.87648 | 3 | 3 | 2 | No
93005 | Montague-Cape Grim | Short Rural | 1331 | 150.764 | 2.806 | 4.9627 | 2.103 | 1.982 | 75 | 97.0502 | 90.7881 | 0.74009 | 0.72061 | 53 | 73.0668 | 73.0668 | 0.30379 | 0.30379 | 12 | 4.499 | 4.499 | No
93006 | Irish Town | Urban | 1 | 0 | 1.822 | 2.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
94001 | Mawbanna-Stanley | Short Rural | 959 | 139.888 | 0.224 | 4.1002 | 10.886 | 1.474 | 92 | 477.7172 | 425.6588 | 3.4463 | 3.1729 | 21 | 53.8812 | 53.8812 | 0.18139 | 0.18139 | 23 | 6.7809 | 5.7029 | No
94002 | Montumana-Sisters Creek-Myalla | Short Rural | 1227 | 159.988 | 0.408 | 4.4658 | 5.616 | 0.568 | 72 | 189.1269 | 91.1585 | 1.7042 | 1.4684 | 33 | 67.3141 | 67.3141 | 0.26592 | 0.26592 | 13 | 5.3261 | 5.1061 | No
95001 | Savage River-Luina-Waratah | Short Rural | 258 | 60.96 | 0.24 | 1.1281 | 11.532 | 0.007 | 10 | 955.0507 | 861.1047 | 2.354 | 1.8888 | 2 | 0.19508 | 0.19508 | 0.0032514 | 0.0032514 | 7 | 3.7811 | 3.3176 | Yes
96202 | Henty Gold | Urban | 1 | 10.677 | 0.397 | 3.8258 | 21.908 | 11.76 | 1 | 1.7397 | 1.7397 | 0.0045662 | 0.0045662 | 1 | 7.1233 | 7.1233 | 0.17808 | 0.17808 | 1 | 1 | 1 | No
96303 | Hampshire Mill | Short Rural | 2 | 7.534 | 0.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
97001 | Rosebery Village (South)-Williamsford-Mt Read | Short Rural | 444 | 19.421 | 2.298 | 1.0873 | 2.632 | 0.104 | 7 | 221.8398 | 221.8291 | 1.0355 | 1.0333 | 5 | 40.7601 | 16.0811 | 0.22401 | 0.14128 | 5 | 1.1563 | 1.1563 | No
97002 | Rosebery-Anthony-Tribute-Tullah-Mackintosh-Reece | Short Rural | 514 | 59.992 | 0.045 | 1.3887 | 2.053 | 4.472 | 27 | 243.0964 | 242.8782 | 1.0482 | 1.0435 | 11 | 336.853 | 332.3946 | 1.0224 | 0.98717 | 11 | 5.2415 | 4.765 | No
97013 | Zeehan Zone Substation | Short Rural | 6 | 36.958 | 0 | 1.7856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.0769 | 1.0769 | No
97014 | Renison Mine | Urban | 1 | 9.546 | 0 | 14.3236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No
98001 | Strahan | Short Rural | 666 | 64.104 | 2.139 | 1.8517 | 4.13 | 0.478 | 36 | 185.142 | 185.0985 | 2.6034 | 2.5998 | 14 | 56.8808 | 48.1484 | 0.31197 | 0.27353 | 13 | 7.7656 | 5.76 | No
98002 | Queenstown (West)-John Butters Power Station | Short Rural | 850 | 17.072 | 1.776 | 2.5602 | 2.662 | 0.205 | 20 | 330.6718 | 330.0295 | 1.2757 | 1.2699 | 11 | 11.8725 | 11.8725 | 0.11266 | 0.11266 | 1 | 1.0015 | 1.0015 | No
98003 | Queenstown (East)-Gormanston-Lake Burbury | Short Rural | 568 | 10.84 | 0.413 | 1.4099 | 0.286 | 0.056 | 15 | 161.7581 | 129.2057 | 1.4747 | 1.2223 | 9 | 4.1418 | 4.1418 | 0.071888 | 0.071888 | 2 | 2 | 1 | No
99981 | Zeehan | Short Rural | 657 | 67.924 | 0.238 | 1.5115 | 3.832 | 0.122 | 24 | 384.7461 | 20.6044 | 2.2595 | 1.2551 | 17 | 6.6143 | 6.6143 | 0.11398 | 0.11398 | 14 | 9.4464 | 9.4464 | No
99983 | Zeehan Zinc | Short Rural | 3 | 4.24 | 0.219 | 0 | 0 | 0 | 1 | 5 | 5 | 1 | 1 | 1 | 165 | 165 | 1 | 1 | 3 | 3 | 3 | No
Note
(1) The sum of the number of customers for each feeder category may not equal the average customer numbers shown on sheet 1a, due to rounding.
Contents
Contents

## 3b. Planned outages
TasNetworks
Reliability - planned outages
2015-16
The information in templates 3a and 3b is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Supply reliability category
| Critical infrastructure | High density commercial | Urban | High density rural | Low density rural | Whole network
SAIDI | 20.3203 | 7.0032 | 32.9979 | 56.3534 | 110.0261 | 55.5152
SAIFI | 0.099593 | 0.042577 | 0.16965 | 0.24259 | 0.4117 | 0.23778
MAIFI | 0 | 0 | 0 | 0 | 0 | 0
Contents