## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | United Energy Distribution Pty Limited
DNSP - Australian business number: |  | 70 064 651 029
Reporting year: |  | CY 2013
Business address | Address |  | Level 3, 6 Nexus Court
| Suburb |  | Mulgrave
|  | State | VIC | Postcode | 3170
Postal address | Address |  | PO BOX 449
| Suburb |  | Mount Waverley
|  | State | VIC | Postcode | 3149
Contact name/s | Mathew Abraham
Contact phone/s | 03 8846 9758
Contact email address/s | Mathew.Abraham@ue.com.au

## Contents
Electricity Distribution Network Service Provider Annual Reporting Template
Table of contents
Cover Sheet
1. Service Target Performance Incentive Scheme |  | 2. Demand |  | 6. Outages
3. Asset Installation
4. Customer Service
5. General Information
Cover sheet
1a. STPIS - Reliability
1b. STPIS - Customer Service
1d. STPIS - MED Threshold
1c. STPIS - Daily Performance
6a. Planned Outages
1e. STPIS - Exclusions
2. Demand
6b. Annual Feeder Reliability
6c. Cause of Outages
3. Asset Installation (not inc)
4. Customer Services
5. General Information

## 1a. STPIS Reliability
United Energy Distribution Pty Limited
STPIS Data Reporting
2013
Reliability
Table 1: SAIDI (System Average Interruption Duration Index)
Network categorisation
Unplanned SAIDI 1 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | 0 | 101.4937 | 234.0399 | 0 | 110.3562
Total (after removing excluded events and MED) | 0 | 66.6129 | 170.5304 | 0 | 73.5611
Table 2: SAIFI (System Average Interruption Frequency Index)
Network categorisation
Unplanned SAIFI 2 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | 0 | 1.6451 | 3.4932 | 0 | 1.7767
Total (after removing excluded events and MED) | 0 | 0.93405 | 2.014 | 0 | 1.0143
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Network categorisation
MAIFI 3 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | 0 | 1.2244 | 3.8554 | 0 | 1.4003
Total (after removing excluded events and MED) | 0 | 1.1317 | 3.6671 | 0 | 1.3012
Table 4: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI | 0 | 47.6952 | 84.8093 | 0 | 50.1768
SAIFI | 0 | 0.14095 | 0.27813 | 0 | 0.15013
Table 5: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period | 0 | 601848 | 43298 | 0 | 645146
Customer numbers at the end of period | 0 | 606136 | 43259 | 0 | 649395
Average distribution customer numbers | 0 | 603992 | 43278.5 | 0 | 647270.5
Note - the AER's Electricity distribution network service providers, Service target performance incentive scheme, November 2009, p. 22, defines SAIDI and SAIFI as follows;
1) Unplanned SAIDI - The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less).
2) Unplanned SAIFI - The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
The AER will apply the ESCV's definition of MAIFI for transitional reasons. The ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30, defines MAIFI as follows:
3) MAIFI - The total number of momentary interruptions divided by the total number of distribution customers (where the distribution customers are network or per feeder based, as appropriate).
4) Total includes the impact of excluded events and MED.
Contents
Contents

## 1b. STPIS Customer Service
United Energy Distribution Pty Limited
STPIS Data Reporting - AER Definitions
2013
Customer service
Table 1: Telephone answering
Telephone answering | Total | Total after removing MED
Number of calls received | 285910 | 234156
Number of calls answered within 30 seconds | 89637 | 88122
Percentage of calls answered within 30 seconds | 52.38% | 60.84%
Note:
Telephone answering has the same meaning as defined in the Electricity DNSPs' STPIS, November 2009.
Table 2: New connections
Note: This is for newly energised properties only
New connections | Total
Number of new connections | 10741
Number of new connections not provided on or before the agreed date | 260
Percentage of new connections not provided on or before the agreed date | 2.421%
Table 3: Streetlight repair
Note:
Streetlight repair has the same meaning as defined in the Electricity DNSPs' STPIS, November 2009
Streetlight repair | Total
Total number of streetlights | 118739
Total number of streetlight faults | 6064
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | 11
Faulty streetlights not repaired within 5 business days of fault report or agreed date | 11
Percentage of faulty streetlights not repaired within 5 business days of fault report or agreed date | 0.1814%
Table 4 Guaranteed service levels - jurisdictional GSL scheme
Appointments
Customer arranged appointments Central - number |  |  | 4267
Appointments not met within 15 minutes of agreed time - number |  |  | 5
Appointments - GSL payments - number |  |  | 5
Appointments - GSL payments - ($) |  |  | 100
Connections
Connections made |  |  | 10741
Connections not made on agreed date |  |  | 260
Connections - GSL payments - 1-4 day delay - number |  |  | 222
Connections - GSL payments - 1-4 day delay - ($) |  |  | 24250
Connections - GSL payments - 5+ day delay - number |  |  | 38
Connections - GSL payments - 5+ day delay - ($) |  |  | 9500
Reliability of supply
Low reliability payments - 20 hours - number |  |  | 1817
Low reliability payments - 20 hours - ($) |  |  | 181700
Low reliability payments - 30 hours - number |  |  | 593
Low reliability payments - 30 hours - ($) |  |  | 88950
Low reliability payments - 60 hours - number |  |  | 43
Low reliability payments - 60 hours - ($) |  |  | 12900
Low reliability payments - 10 events - number |  |  | 114
Low reliability payments - 10 events - ($) |  |  | 11400
Low reliability payments - 15 events - number |  |  | 0
Low reliability payments - 15 events - ($) |  |  | 0
Low reliability payments - 30 events - number |  |  | 0
Low reliability payments - 30 events - ($) |  |  | 0
Low reliability payments - 24 momentary events - number |  |  | 0
Low reliability payments - 24 momentary events - ($) |  |  | 0
Low reliability payments - 36 momentary events - number |  |  | 0
Low reliability payments - 36 momentary events - ($) |  |  | 0
Street lights
Street lights |  |  | 118739
Street lights "out" during period |  |  | 6064
Street lights not repaired by "fix by" date |  |  | 364
Street lights not repaired in 2 business days |  |  | 11
Street lights – number of business days to repair |  |  | 12.33
Street lights - GSL payments - number |  |  | 11
Street lights - GSL payments - ($) |  |  | 110
Planned interruptions
Planned interruptions - 4 business days notice not given |  |  | 0
Total GSL payments made ($) |  |  | 328910
Contents

## 1c. STPIS Daily Performance
United Energy Distribution Pty Limited
STPIS Data Reporting
2013
Daily Performance Data
Instruction This regulatory template requires the input of historical daily performance recorded for the calculation of the parameters under the STPIS, such as MED day boundary and performance targets. STPIS definitions apply to SAIDI and Calls not answered within 30 seconds. Please note: The AER's definition of calls answered within 30 seconds is as follows: Calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: - calls to payment lines and automated interactive services; - calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator. Where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned. Note: Being placed in a queuing system (automated or otherwise) does not constitute a response. 'Calls answered within 30 seconds' and 'Calls received' should be calculated excluding calls abandoned within 30 seconds of being queued for a human operator; and calls to payment lines and automated interactive services. Exclusions refer to the exclusions listed in Section 3.3(a) of the STPIS.
Table 1 Daily Performance Data (unplanned)
Customer service
Date | CBD SAIDI All events | CBD SAIDI (after removing excluded events) | Urban SAIDI All events | Urban SAIDI (after removing excluded events) | Long Rural SAIDI All events | Long Rural SAIDI (after removing excluded events) | Short Rural SAIDI All events | Short Rural SAIDI (after removing excluded events) | Network SAIDI All events | Network SAIDI (after removing excluded events) | CBD SAIFI All events | CBD SAIFI (after removing excluded events) | Urban SAIFI All events | Urban SAIFI (after removing excluded events) | Long Rural SAIFI All events | Long Rural SAIFI (after removing excluded events) | Short Rural SAIFI All events | Short Rural SAIFI (after removing excluded events) | Network SAIFI All events | Network SAIFI (after removing excluded events) | CBD MAIFI All events | CBD MAIFI (after removing excluded events) | Urban MAIFI All events | Urban MAIFI (after removing excluded events) | Long Rural MAIFI All events | Long Rural MAIFI (after removing excluded events) | Short Rural MAIFI All events | Short Rural MAIFI (after removing excluded events) | Network MAIFI All events | Network MAIFI (after removing excluded events) | Number of calls received | Calls not answered in 30 seconds | MED | Comments / basis for exclusion - refer to category of exclusion under 3.3(a) of STPIS
2013-01-01 |  |  | 0.092466 | 0.092466 |  |  | 0.063174 | 0.063174 | 0.090508 | 0.090508 |  |  | 0.0012549 | 0.0012549 |  |  | 0.00054161 | 0.00054161 | 0.0012072 | 0.0012072 |  |  | 0.0024884 | 0.0024884 |  |  | 0 | 0 | 0.0023221 | 0.0023221 | 170 | 21 | NO
2013-01-02 |  |  | 0.020169 | 0.020169 |  |  | 0.18332 | 0.18332 | 0.031078 | 0.031078 |  |  | 8.3594e-05 | 8.3594e-05 |  |  | 0.0010449 | 0.0010449 | 0.00014787 | 0.00014787 |  |  | 0.0019818 | 0.0019818 |  |  | 0.039535 | 0.039535 | 0.0044927 | 0.0044927 | 368 | 18 | NO
2013-01-03 |  |  | 0.020871 | 0.020871 |  |  | 0.0080929 | 0.0080929 | 0.020016 | 0.020016 |  |  | 0.00012874 | 0.00012874 |  |  | 0.00011553 | 0.00011553 | 0.00012786 | 0.00012786 |  |  | 0.0066557 | 0.0066557 |  |  | 0 | 0 | 0.0062107 | 0.0062107 | 460 | 27 | NO
2013-01-04 |  |  | 4.6881 | 0 |  |  | 21.7963 | 0 | 5.832 | 0 |  |  | 0.055478 | 0 |  |  | 0.24297 | 0 | 0.068014 | 0 |  |  | 0.0097766 | 0 |  |  | 0.075788 | 0 | 0.01419 | 0 | 11852 | 1079 | Yes | MED
2013-01-05 |  |  | 1.9366 | 1.9366 |  |  | 0.028415 | 0.028415 | 1.809 | 1.809 |  |  | 0.0096659 | 0.0096659 |  |  | 0.00016174 | 0.00016174 | 0.0090304 | 0.0090304 |  |  | 0.0070282 | 0.0070282 |  |  | 0.12505 | 0.12505 | 0.01492 | 0.01492 | 1548 | 562 | NO
2013-01-06 |  |  | 0.02869 | 0.02869 |  |  | 0 | 0 | 0.026772 | 0.026772 |  |  | 0.00037762 | 0.00037762 |  |  | 0 | 0 | 0.00035237 | 0.00035237 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 308 | 58 | NO
2013-01-07 |  |  | 0.046505 | 0.046505 |  |  | 0.010173 | 0.010173 | 0.044076 | 0.044076 |  |  | 0.00045376 | 0.00045376 |  |  | 9.2425e-05 | 9.2425e-05 | 0.0004296 | 0.0004296 |  |  | 0.0038808 | 0.0038808 |  |  | 0 | 0 | 0.0036214 | 0.0036214 | 546 | 95 | NO
2013-01-08 |  |  | 0.81857 | 0.81857 |  |  | 0.00305 | 0.00305 | 0.76404 | 0.76404 |  |  | 0.014063 | 0.014063 |  |  | 0.00027727 | 0.00027727 | 0.013141 | 0.013141 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1338 | 148 | NO
2013-01-09 |  |  | 0.4215 | 0.4215 |  |  | 0.78673 | 0.78673 | 0.44592 | 0.44592 |  |  | 0.0022475 | 0.0022475 |  |  | 0.002464 | 0.002464 | 0.0022619 | 0.0022619 |  |  | 0.012633 | 0.012633 |  |  | 0 | 0 | 0.011788 | 0.011788 | 696 | 280 | NO
2013-01-10 |  |  | 0.30778 | 0.30778 |  |  | 0.0042993 | 0.0042993 | 0.28749 | 0.28749 |  |  | 0.00076332 | 0.00076332 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00071537 | 0.00071537 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 418 | 52 | NO
2013-01-11 |  |  | 0.071125 | 0.071125 |  |  | 0.3023 | 0.3023 | 0.086581 | 0.086581 |  |  | 0.00073968 | 0.00073968 |  |  | 0.0032654 | 0.0032654 | 0.00090855 | 0.00090855 |  |  | 0.0037269 | 0.0037269 |  |  | 0 | 0 | 0.0034777 | 0.0034777 | 494 | 33 | NO
2013-01-12 |  |  | 0.041954 | 0.041954 |  |  | 0 | 0 | 0.039149 | 0.039149 |  |  | 0.00022065 | 0.00022065 |  |  | 0 | 0 | 0.0002059 | 0.0002059 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 226 | 47 | NO
2013-01-13 |  |  | 0.47551 | 0.47551 |  |  | 0.081489 | 0.081489 | 0.44917 | 0.44917 |  |  | 0.0045089 | 0.0045089 |  |  | 0.00056471 | 0.00056471 | 0.0042452 | 0.0042452 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 490 | 21 | NO
2013-01-14 |  |  | 0.031008 | 0.031008 |  |  | 0 | 0 | 0.028935 | 0.028935 |  |  | 0.00023596 | 0.00023596 |  |  | 0 | 0 | 0.00022019 | 0.00022019 |  |  | 0.0019239 | 0.0019239 |  |  | 0 | 0 | 0.0017952 | 0.0017952 | 447 | 74 | NO
2013-01-15 |  |  | 0.0020837 | 0.0020837 |  |  | 0.0038241 | 0.0038241 | 0.0022 | 0.0022 |  |  | 1.8212e-05 | 1.8212e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 2.0084e-05 | 2.0084e-05 |  |  | 0.0043825 | 0.0043825 |  |  | 0.07461 | 0.07461 | 0.0090781 | 0.0090781 | 400 | 47 | NO
2013-01-16 |  |  | 0.0061596 | 0.0061596 |  |  | 0.057237 | 0.057237 | 0.0095748 | 0.0095748 |  |  | 7.8859e-05 | 7.8859e-05 |  |  | 0.00067008 | 0.00067008 | 0.00011839 | 0.00011839 |  |  | 0.0054554 | 0.0054554 |  |  | 0 | 0 | 0.0050906 | 0.0050906 | 430 | 95 | NO
2013-01-17 |  |  | 0.11749 | 0.11749 |  |  | 0.037158 | 0.037158 | 0.11212 | 0.11212 |  |  | 0.0012182 | 0.0012182 |  |  | 0.00019247 | 0.00019247 | 0.0011496 | 0.0011496 |  |  | 0.001245 | 0.001245 |  |  | 0.068394 | 0.068394 | 0.0057349 | 0.0057349 | 963 | 204 | NO
2013-01-18 |  |  | 0.43636 | 0.43636 |  |  | 0.010409 | 0.010409 | 0.40788 | 0.40788 |  |  | 0.0050704 | 0.0050704 |  |  | 9.2425e-05 | 9.2425e-05 | 0.0047376 | 0.0047376 |  |  | 0.0050398 | 0.0050398 |  |  | 0.052405 | 0.052405 | 0.0082068 | 0.0082068 | 1227 | 131 | NO
2013-01-19 |  |  | 0.014483 | 0.014483 |  |  | 0.49191 | 0.49191 | 0.046405 | 0.046405 |  |  | 6.8743e-05 | 6.8743e-05 |  |  | 0.0010601 | 0.0010601 | 0.00013503 | 0.00013503 |  |  | 0.0093809 | 0.0093809 |  |  | 0 | 0 | 0.0087537 | 0.0087537 | 267 | 70 | NO
2013-01-20 |  |  | 0.07158 | 0.07158 |  |  | 0.0062052 | 0.0062052 | 0.067209 | 0.067209 |  |  | 0.001676 | 0.001676 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0015655 | 0.0015655 |  |  | 0.0045266 | 0.0045266 |  |  | 0 | 0 | 0.0042239 | 0.0042239 | 251 | 84 | NO
2013-01-21 |  |  | 0.056801 | 0.056801 |  |  | 0.73429 | 0.73429 | 0.1021 | 0.1021 |  |  | 0.00012856 | 0.00012856 |  |  | 0.0045057 | 0.0045057 | 0.00042123 | 0.00042123 |  |  | 0.0016788 | 0.0016788 |  |  | 0 | 0 | 0.0015666 | 0.0015666 | 554 | 52 | NO
2013-01-22 |  |  | 0.01673 | 0.01673 |  |  | 0.08577 | 0.08577 | 0.021346 | 0.021346 |  |  | 9.318e-05 | 9.318e-05 |  |  | 0.0013171 | 0.0013171 | 0.00017501 | 0.00017501 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 419 | 64 | NO
2013-01-23 |  |  | 0.0043828 | 0.0043828 |  |  | 0.0055905 | 0.0055905 | 0.0044636 | 0.0044636 |  |  | 5.4256e-05 | 5.4256e-05 |  |  | 6.9318e-05 | 6.9318e-05 | 5.5263e-05 | 5.5263e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 388 | 28 | NO
2013-01-24 |  |  | 0.24046 | 0.24046 |  |  | 0.13362 | 0.13362 | 0.23332 | 0.23332 |  |  | 0.0040145 | 0.0040145 |  |  | 0.0010546 | 0.0010546 | 0.0038166 | 0.0038166 |  |  | 0.00093048 | 0.00093048 |  |  | 0.02001 | 0.02001 | 0.0022062 | 0.0022062 | 830 | 150 | NO
2013-01-25 |  |  | 0.11635 | 0.11635 |  |  | 3.4092 | 3.4092 | 0.33652 | 0.33652 |  |  | 0.0072103 | 0.0072103 |  |  | 0.095891 | 0.095891 | 0.01314 | 0.01314 |  |  | 0.0089289 | 0.0089289 |  |  | 0 | 0 | 0.0083319 | 0.0083319 | 921 | 260 | NO
2013-01-26 |  |  | 0.0085636 | 0.0085636 |  |  | 0.0020823 | 0.0020823 | 0.0081303 | 0.0081303 |  |  | 8.9041e-05 | 8.9041e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 8.4632e-05 | 8.4632e-05 |  |  | 0.0038808 | 0.0038808 |  |  | 0.023753 | 0.023753 | 0.0052096 | 0.0052096 | 273 | 84 | NO
2013-01-27 |  |  | 5.3927 | 0 |  |  | 1.354 | 0 | 5.1227 | 0 |  |  | 0.038688 | 0 |  |  | 0.0016405 | 0 | 0.036211 | 0 |  |  | 0.013586 | 0 |  |  | 0.02001 | 0 | 0.014016 | 0 | 6014 | 1502 | Yes | MED
2013-01-28 |  |  | 0.029259 | 0.029259 |  |  | 0.0084407 | 0.0084407 | 0.027867 | 0.027867 |  |  | 0.00045022 | 0.00045022 |  |  | 6.9318e-05 | 6.9318e-05 | 0.00042475 | 0.00042475 |  |  | 0.0018312 | 0.0018312 |  |  | 0 | 0 | 0.0017087 | 0.0017087 | 297 | 61 | NO
2013-01-29 |  |  | 0.92421 | 0.92421 |  |  | 5.0886 | 5.0886 | 1.2026 | 1.2026 |  |  | 0.0062791 | 0.0062791 |  |  | 0.088103 | 0.088103 | 0.01175 | 0.01175 |  |  | 0.011611 | 0.011611 |  |  | 0 | 0 | 0.010835 | 0.010835 | 1169 | 381 | NO
2013-01-30 |  |  | 0.023903 | 0.023903 |  |  | 0.01116 | 0.01116 | 0.023051 | 0.023051 |  |  | 0.0093174 | 0.0093174 |  |  | 9.2425e-05 | 9.2425e-05 | 0.0087006 | 0.0087006 |  |  | 0.0040199 | 0.0040199 |  |  | 0 | 0 | 0.0037511 | 0.0037511 | 425 | 102 | NO
2013-01-31 |  |  | 1.4322 | 1.4322 |  |  | 0.0058543 | 0.0058543 | 1.3369 | 1.3369 |  |  | 0.010142 | 0.010142 |  |  | 6.9318e-05 | 6.9318e-05 | 0.0094685 | 0.0094685 |  |  | 0.0016871 | 0.0016871 |  |  | 0 | 0 | 0.0015743 | 0.0015743 | 2433 | 717 | NO
2013-02-01 |  |  | 0.14623 | 0.14623 |  |  | 0.0066553 | 0.0066553 | 0.1369 | 0.1369 |  |  | 0.0013349 | 0.0013349 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0012488 | 0.0012488 |  |  | 0.00038742 | 0.00038742 |  |  | 0 | 0 | 0.00036152 | 0.00036152 | 826 | 304 | NO
2013-02-02 |  |  | 0.0089466 | 0.0089466 |  |  | 0 | 0 | 0.0083484 | 0.0083484 |  |  | 2.9802e-05 | 2.9802e-05 |  |  | 0 | 0 | 2.7809e-05 | 2.7809e-05 |  |  | 0.0028295 | 0.0028295 |  |  | 0 | 0 | 0.0026403 | 0.0026403 | 270 | 104 | NO
2013-02-03 |  |  | 0.20984 | 0.20984 |  |  | 0.0032681 | 0.0032681 | 0.19603 | 0.19603 |  |  | 0.0034098 | 0.0034098 |  |  | 4.6443e-05 | 4.6443e-05 | 0.003185 | 0.003185 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 293 | 51 | NO
2013-02-04 |  |  | 0.43008 | 0.43008 |  |  | 0.035855 | 0.035855 | 0.40372 | 0.40372 |  |  | 0.01014 | 0.01014 |  |  | 0.0007625 | 0.0007625 | 0.0095131 | 0.0095131 |  |  | 0 | 0 |  |  | 0.046906 | 0.046906 | 0.0031362 | 0.0031362 | 1050 | 230 | NO
2013-02-05 |  |  | 0.067097 | 0.067097 |  |  | 0.13811 | 0.13811 | 0.071846 | 0.071846 |  |  | 0.0034305 | 0.0034305 |  |  | 0.00055478 | 0.00055478 | 0.0032382 | 0.0032382 |  |  | 0.0095101 | 0.0095101 |  |  | 0 | 0 | 0.0088742 | 0.0088742 | 596 | 167 | NO
2013-02-06 |  |  | 0.11428 | 0.11428 |  |  | 1.1868 | 1.1868 | 0.18599 | 0.18599 |  |  | 0.0011769 | 0.0011769 |  |  | 0.028929 | 0.028929 | 0.0030325 | 0.0030325 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 853 | 195 | NO
2013-02-07 |  |  | 0.010642 | 0.010642 |  |  | 0.024862 | 0.024862 | 0.011593 | 0.011593 |  |  | 0.00019013 | 0.00019013 |  |  | 0.00011553 | 0.00011553 | 0.00018515 | 0.00018515 |  |  | 0 | 0 |  |  | 0.023152 | 0.023152 | 0.001548 | 0.001548 | 468 | 89 | NO
2013-02-08 |  |  | 0.5193 | 0.5193 |  |  | 0.36386 | 0.36386 | 0.50891 | 0.50891 |  |  | 0.0083256 | 0.0083256 |  |  | 0.0030962 | 0.0030962 | 0.007976 | 0.007976 |  |  | 0.0056673 | 0.0056673 |  |  | 0.023499 | 0.023499 | 0.0068596 | 0.0068596 | 454 | 64 | NO
2013-02-09 |  |  | 0.12924 | 0.12924 |  |  | 0.22244 | 0.22244 | 0.13547 | 0.13547 |  |  | 0.0035195 | 0.0035195 |  |  | 0.002349 | 0.002349 | 0.0034412 | 0.0034412 |  |  | 0.0036573 | 0.0036573 |  |  | 0.065806 | 0.065806 | 0.0078128 | 0.0078128 | 308 | 51 | NO
2013-02-10 |  |  | 0.001894 | 0.001894 |  |  | 0.052687 | 0.052687 | 0.0052902 | 0.0052902 |  |  | 1.159e-05 | 1.159e-05 |  |  | 0.00053144 | 0.00053144 | 4.6348e-05 | 4.6348e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 176 | 20 | NO
2013-02-11 |  |  | 0.1012 | 0.1012 |  |  | 0.45483 | 0.45483 | 0.12484 | 0.12484 |  |  | 0.0050712 | 0.0050712 |  |  | 0.0041462 | 0.0041462 | 0.0050094 | 0.0050094 |  |  | 0.0074869 | 0.0074869 |  |  | 0.024493 | 0.024493 | 0.0086239 | 0.0086239 | 568 | 184 | NO
2013-02-12 |  |  | 0.573 | 0.033381 |  |  | 0.011761 | 0.011761 | 0.53548 | 0.031935 |  |  | 0.021933 | 0.00011283 |  |  | 6.9318e-05 | 6.9318e-05 | 0.020471 | 0.00010992 |  |  | 0.012942 | 0.012942 |  |  | 0.039119 | 0.039119 | 0.014692 | 0.014692 | 1324 | 162 | NO
2013-02-13 |  |  | 0.006774 | 0.006774 |  |  | 0.040237 | 0.040237 | 0.0090114 | 0.0090114 |  |  | 7.8445e-05 | 7.8445e-05 |  |  | 0.00038287 | 0.00038287 | 9.8799e-05 | 9.8799e-05 |  |  | 0.0022434 | 0.0022434 |  |  | 0.045796 | 0.045796 | 0.0051555 | 0.0051555 | 450 | 130 | NO
2013-02-14 |  |  | 1.1074 | 1.1074 |  |  | 0.0049459 | 0.0049459 | 1.0336 | 1.0336 |  |  | 0.014348 | 0.014348 |  |  | 4.6212e-05 | 4.6212e-05 | 0.013392 | 0.013392 |  |  | 0.023826 | 0.023826 |  |  | 0 | 0 | 0.022233 | 0.022233 | 1326 | 323 | NO
2013-02-15 |  |  | 0.086402 | 0.086402 |  |  | 0.73068 | 0.73068 | 0.12948 | 0.12948 |  |  | 0.00060691 | 0.00060691 |  |  | 0.0033767 | 0.0033767 | 0.00079211 | 0.00079211 |  |  | 0.0085365 | 0.0085365 |  |  | 0 | 0 | 0.0079658 | 0.0079658 | 1092 | 484 | NO
2013-02-16 |  |  | 0.059559 | 0.059559 |  |  | 0.054638 | 0.054638 | 0.05923 | 0.05923 |  |  | 0.00022785 | 0.00022785 |  |  | 0.00034659 | 0.00034659 | 0.00023579 | 0.00023579 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 314 | 72 | NO
2013-02-17 |  |  | 0.30066 | 0.30066 |  |  | 0 | 0 | 0.28056 | 0.28056 |  |  | 0.0025337 | 0.0025337 |  |  | 0 | 0 | 0.0023643 | 0.0023643 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 646 | 208 | NO
2013-02-18 |  |  | 0.25891 | 0.25891 |  |  | 0.089125 | 0.089125 | 0.24756 | 0.24756 |  |  | 0.0013237 | 0.0013237 |  |  | 0.0027838 | 0.0027838 | 0.0014213 | 0.0014213 |  |  | 0.0083693 | 0.0083693 |  |  | 0 | 0 | 0.0078097 | 0.0078097 | 1152 | 535 | NO
2013-02-19 |  |  | 0.03589 | 0.03589 |  |  | 0.74336 | 0.74336 | 0.083193 | 0.083193 |  |  | 0.00010753 | 0.00010753 |  |  | 0.0015028 | 0.0015028 | 0.00020083 | 0.00020083 |  |  | 0.010043 | 0.010043 |  |  | 0 | 0 | 0.0093717 | 0.0093717 | 465 | 125 | NO
2013-02-20 |  |  | 1.0197 | 1.0197 |  |  | 1.5562 | 1.5562 | 1.0555 | 1.0555 |  |  | 0.0076567 | 0.0076567 |  |  | 0.051896 | 0.051896 | 0.010615 | 0.010615 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1081 | 194 | NO
2013-02-21 |  |  | 0.52174 | 0.52174 |  |  | 0.0034987 | 0.0034987 | 0.48709 | 0.48709 |  |  | 0.0085114 | 0.0085114 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0079438 | 0.0079438 |  |  | 0.0085846 | 0.0085846 |  |  | 0.10007 | 0.10007 | 0.014702 | 0.014702 | 1202 | 312 | NO
2013-02-22 |  |  | 0.033512 | 0.033512 |  |  | 0.72077 | 0.72077 | 0.079464 | 0.079464 |  |  | 0.00022714 | 0.00022714 |  |  | 0.0087113 | 0.0087113 | 0.00079441 | 0.00079441 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 501 | 139 | NO
2013-02-23 |  |  | 0.063786 | 0.063786 |  |  | 0.41052 | 0.41052 | 0.086969 | 0.086969 |  |  | 0.0009011 | 0.0009011 |  |  | 0.0037044 | 0.0037044 | 0.0010885 | 0.0010885 |  |  | 0.0088428 | 0.0088428 |  |  | 0 | 0 | 0.0082516 | 0.0082516 | 430 | 121 | NO
2013-02-24 |  |  | 0.0065922 | 0.0065922 |  |  | 2.6958e-05 | 2.6958e-05 | 0.0061532 | 0.0061532 |  |  | 8.5879e-05 | 8.5879e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 8.1681e-05 | 8.1681e-05 |  |  | 0 | 0 |  |  | 4.6212e-05 | 4.6212e-05 | 3.0899e-06 | 3.0899e-06 | 140 | 18 | NO
2013-02-25 |  |  | 0.11991 | 0.11991 |  |  | 0.030291 | 0.030291 | 0.11392 | 0.11392 |  |  | 0.00076324 | 0.00076324 |  |  | 0.00012339 | 0.00012339 | 0.00072046 | 0.00072046 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 556 | 189 | NO
2013-02-26 |  |  | 0.44678 | 0.44678 |  |  | 0.011292 | 0.011292 | 0.41767 | 0.41767 |  |  | 0.0073974 | 0.0073974 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0069059 | 0.0069059 |  |  | 0.0019355 | 0.0019355 |  |  | 0 | 0 | 0.001806 | 0.001806 | 1279 | 622 | NO
2013-02-27 |  |  | 0.0862 | 0.0862 |  |  | 0.10057 | 0.10057 | 0.087161 | 0.087161 |  |  | 0.0047434 | 0.0047434 |  |  | 0.0007119 | 0.0007119 | 0.0044739 | 0.0044739 |  |  | 0.0051772 | 0.0051772 |  |  | 0 | 0 | 0.0048311 | 0.0048311 | 493 | 84 | NO
2013-02-28 |  |  | 0.028355 | 0.028355 |  |  | 0.0075068 | 0.0075068 | 0.026961 | 0.026961 |  |  | 0.00016722 | 0.00016722 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00015913 | 0.00015913 |  |  | 0.0028742 | 0.0028742 |  |  | 0 | 0 | 0.002682 | 0.002682 | 470 | 117 | NO
2013-03-01 |  |  | 0.32909 | 0.32909 |  |  | 0 | 0 | 0.30709 | 0.30709 |  |  | 0.0048935 | 0.0048935 |  |  | 0 | 0 | 0.0045663 | 0.0045663 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 603 | 322 | NO
2013-03-02 |  |  | 0.013435 | 0.013435 |  |  | 0.0047749 | 0.0047749 | 0.012856 | 0.012856 |  |  | 6.1127e-05 | 6.1127e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 5.8584e-05 | 5.8584e-05 |  |  | 0.000952 | 0.000952 |  |  | 0 | 0 | 0.00088835 | 0.00088835 | 297 | 81 | NO
2013-03-03 |  |  | 0.15838 | 0.15838 |  |  | 0.027047 | 0.027047 | 0.1496 | 0.1496 |  |  | 0.0020446 | 0.0020446 |  |  | 4.6212e-05 | 4.6212e-05 | 0.001911 | 0.001911 |  |  | 0.0017434 | 0.0017434 |  |  | 0 | 0 | 0.0016268 | 0.0016268 | 225 | 43 | NO
2013-03-04 |  |  | 0.46919 | 0.46919 |  |  | 0.30814 | 0.30814 | 0.45843 | 0.45843 |  |  | 0.0035539 | 0.0035539 |  |  | 0.0027034 | 0.0027034 | 0.003497 | 0.003497 |  |  | 0 | 0 |  |  | 0.11126 | 0.11126 | 0.0074389 | 0.0074389 | 1082 | 298 | NO
2013-03-05 |  |  | 0.063477 | 0.063477 |  |  | 0.049324 | 0.049324 | 0.06253 | 0.06253 |  |  | 0.0011036 | 0.0011036 |  |  | 0.00075811 | 0.00075811 | 0.0010805 | 0.0010805 |  |  | 0.0011739 | 0.0011739 |  |  | 0 | 0 | 0.0010954 | 0.0010954 | 716 | 321 | NO
2013-03-06 |  |  | 0.96121 | 0.96121 |  |  | 0.021937 | 0.021937 | 0.89841 | 0.89841 |  |  | 0.014649 | 0.014649 |  |  | 8.4337e-05 | 8.4337e-05 | 0.013675 | 0.013675 |  |  | 0.011689 | 0.011689 |  |  | 0 | 0 | 0.010907 | 0.010907 | 1799 | 327 | NO
2013-03-07 |  |  | 0.3266 | 0.3266 |  |  | 0.10479 | 0.10479 | 0.31177 | 0.31177 |  |  | 0.0072857 | 0.0072857 |  |  | 0.00085493 | 0.00085493 | 0.0068557 | 0.0068557 |  |  | 0 | 0 |  |  | 0.059822 | 0.059822 | 0.0039999 | 0.0039999 | 1314 | 505 | NO
2013-03-08 |  |  | 0.12425 | 0.12425 |  |  | 0.0045881 | 0.0045881 | 0.11625 | 0.11625 |  |  | 0.0013098 | 0.0013098 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0012253 | 0.0012253 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 719 | 331 | NO
2013-03-09 |  |  | 3.2445 | 3.2445 |  |  | 20.9888 | 20.9888 | 4.431 | 4.431 |  |  | 0.020934 | 0.020934 |  |  | 0.15501 | 0.15501 | 0.029899 | 0.029899 |  |  | 0.0093246 | 0.0093246 |  |  | 0.059822 | 0.059822 | 0.012701 | 0.012701 | 3063 | 466 | NO
2013-03-10 |  |  | 0.66658 | 0.66658 |  |  | 5.931 | 5.931 | 1.0186 | 1.0186 |  |  | 0.0037188 | 0.0037188 |  |  | 0.015916 | 0.015916 | 0.0045343 | 0.0045343 |  |  | 0.00025994 | 0.00025994 |  |  | 0 | 0 | 0.00024256 | 0.00024256 | 1574 | 131 | NO
2013-03-11 |  |  | 0.23865 | 0.23865 |  |  | 0.023348 | 0.023348 | 0.22425 | 0.22425 |  |  | 0.001636 | 0.001636 |  |  | 9.2425e-05 | 9.2425e-05 | 0.0015328 | 0.0015328 |  |  | 0.011073 | 0.011073 |  |  | 0 | 0 | 0.010333 | 0.010333 | 1435 | 833 | NO
2013-03-12 |  |  | 1.0223 | 1.0223 |  |  | 0.24129 | 0.24129 | 0.97007 | 0.97007 |  |  | 0.0074003 | 0.0074003 |  |  | 0.0015102 | 0.0015102 | 0.0070064 | 0.0070064 |  |  | 0.0061988 | 0.0061988 |  |  | 0.00041591 | 0.00041591 | 0.0058121 | 0.0058121 | 4727 | 3012 | NO
2013-03-13 |  |  | 0.12258 | 0.12258 |  |  | 1.0706 | 1.0706 | 0.18597 | 0.18597 |  |  | 0.00068403 | 0.00068403 |  |  | 0.018901 | 0.018901 | 0.0019021 | 0.0019021 |  |  | 0.014778 | 0.014778 |  |  | 0 | 0 | 0.01379 | 0.01379 | 1163 | 514 | NO
2013-03-14 |  |  | 0.012401 | 0.012401 |  |  | 0.086096 | 0.086096 | 0.017328 | 0.017328 |  |  | 0.0002053 | 0.0002053 |  |  | 0.00078561 | 0.00078561 | 0.0002441 | 0.0002441 |  |  | 0.0052666 | 0.0052666 |  |  | 0.11414 | 0.11414 | 0.012547 | 0.012547 | 511 | 168 | NO
2013-03-15 |  |  | 0.021166 | 0.021166 |  |  | 0.54438 | 0.54438 | 0.05615 | 0.05615 |  |  | 0.00011803 | 0.00011803 |  |  | 0.017861 | 0.017861 | 0.0013044 | 0.0013044 |  |  | 0.0040232 | 0.0040232 |  |  | 0.025994 | 0.025994 | 0.0054923 | 0.0054923 | 525 | 127 | NO
2013-03-16 |  |  | 1.7197 | 1.7197 |  |  | 0.020834 | 0.020834 | 1.6061 | 1.6061 |  |  | 0.019603 | 0.019603 |  |  | 0.00011553 | 0.00011553 | 0.0183 | 0.0183 |  |  | 0.0010563 | 0.0010563 |  |  | 0.087965 | 0.087965 | 0.0068673 | 0.0068673 | 1888 | 666 | NO
2013-03-17 |  |  | 0.049614 | 0.049614 |  |  | 1.9677 | 1.9677 | 0.17786 | 0.17786 |  |  | 0.00042055 | 0.00042055 |  |  | 0.024539 | 0.024539 | 0.0020332 | 0.0020332 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 485 | 196 | NO
2013-03-18 |  |  | 0.15275 | 0.15275 |  |  | 0.043879 | 0.043879 | 0.14547 | 0.14547 |  |  | 0.0096131 | 0.0096131 |  |  | 0.00034659 | 0.00034659 | 0.0089935 | 0.0089935 |  |  | 0.0029934 | 0.0029934 |  |  | 0 | 0 | 0.0027933 | 0.0027933 | 866 | 217 | NO
2013-03-19 |  |  | 0.077272 | 0.077272 |  |  | 0.16166 | 0.16166 | 0.082915 | 0.082915 |  |  | 0.00047517 | 0.00047517 |  |  | 0.0010167 | 0.0010167 | 0.00051138 | 0.00051138 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 582 | 200 | NO
2013-03-20 |  |  | 0.022296 | 0.022296 |  |  | 0.0047283 | 0.0047283 | 0.021122 | 0.021122 |  |  | 0.00019851 | 0.00019851 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00018678 | 0.00018678 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 490 | 227 | NO
2013-03-21 |  |  | 2.2181 | 2.2181 |  |  | 1.1671 | 1.1671 | 2.1478 | 2.1478 |  |  | 0.020199 | 0.020199 |  |  | 0.015874 | 0.015874 | 0.01991 | 0.01991 |  |  | 0.041275 | 0.041275 |  |  | 0.1272 | 0.1272 | 0.047021 | 0.047021 | 4069 | 1179 | NO
2013-03-22 |  |  | 0.31463 | 0.31463 |  |  | 6.4559 | 6.4559 | 0.72526 | 0.72526 |  |  | 0.00098331 | 0.00098331 |  |  | 0.027404 | 0.027404 | 0.0027499 | 0.0027499 |  |  | 0.0037848 | 0.0037848 |  |  | 0 | 0 | 0.0035318 | 0.0035318 | 927 | 240 | NO
2013-03-23 |  |  | 0.012015 | 0.012015 |  |  | 0.017345 | 0.017345 | 0.012372 | 0.012372 |  |  | 0.00014247 | 0.00014247 |  |  | 9.2425e-05 | 9.2425e-05 | 0.00013912 | 0.00013912 |  |  | 0.00090895 | 0.00090895 |  |  | 0 | 0 | 0.00084818 | 0.00084818 | 299 | 88 | NO
2013-03-24 |  |  | 0.020351 | 0.020351 |  |  | 0 | 0 | 0.01899 | 0.01899 |  |  | 0.00018321 | 0.00018321 |  |  | 0 | 0 | 0.00017096 | 0.00017096 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 151 | 30 | NO
2013-03-25 |  |  | 0.19307 | 0.19307 |  |  | 0.043428 | 0.043428 | 0.18307 | 0.18307 |  |  | 0.00078542 | 0.00078542 |  |  | 0.00013864 | 0.00013864 | 0.00074218 | 0.00074218 |  |  | 0.043141 | 0.043141 |  |  | 0 | 0 | 0.040257 | 0.040257 | 839 | 379 | NO
2013-03-26 |  |  | 0.028196 | 0.028196 |  |  | 0 | 0 | 0.026311 | 0.026311 |  |  | 0.00033004 | 0.00033004 |  |  | 0 | 0 | 0.00030797 | 0.00030797 |  |  | 0 | 0 |  |  | 0.075742 | 0.075742 | 0.0050643 | 0.0050643 | 546 | 222 | NO
2013-03-27 |  |  | 0.61618 | 0.61618 |  |  | 2.2651 | 2.2651 | 0.72643 | 0.72643 |  |  | 0.0059747 | 0.0059747 |  |  | 0.0032492 | 0.0032492 | 0.0057925 | 0.0057925 |  |  | 0.0099472 | 0.0099472 |  |  | 0 | 0 | 0.0092821 | 0.0092821 | 973 | 355 | NO
2013-03-28 |  |  | 2.7116 | 2.7116 |  |  | 3.595 | 3.595 | 2.7707 | 2.7707 |  |  | 0.041011 | 0.041011 |  |  | 0.047358 | 0.047358 | 0.041435 | 0.041435 |  |  | 0.012182 | 0.012182 |  |  | 0.02306 | 0.02306 | 0.01291 | 0.01291 | 4154 | 1268 | NO
2013-03-29 |  |  | 0.44104 | 0.44104 |  |  | 0.01893 | 0.01893 | 0.41282 | 0.41282 |  |  | 0.0092286 | 0.0092286 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0086146 | 0.0086146 |  |  | 0.0076475 | 0.0076475 |  |  | 0 | 0 | 0.0071361 | 0.0071361 | 1027 | 314 | NO
2013-03-30 |  |  | 0.0090496 | 0.0090496 |  |  | 0.0017884 | 0.0017884 | 0.0085641 | 0.0085641 |  |  | 0.00012234 | 0.00012234 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0001157 | 0.0001157 |  |  | 0.0051905 | 0.0051905 |  |  | 0 | 0 | 0.0048434 | 0.0048434 | 324 | 88 | NO
2013-03-31 |  |  | 0.0053394 | 0.0053394 |  |  | 0.54699 | 0.54699 | 0.041556 | 0.041556 |  |  | 5.6623e-05 | 5.6623e-05 |  |  | 0.010005 | 0.010005 | 0.0007218 | 0.0007218 |  |  | 0.00029802 | 0.00029802 |  |  | 0 | 0 | 0.00027809 | 0.00027809 | 145 | 25 | NO
2013-04-01 |  |  | 0.031489 | 0.031489 |  |  | 0.038644 | 0.038644 | 0.031967 | 0.031967 |  |  | 0.00011278 | 0.00011278 |  |  | 0.00032349 | 0.00032349 | 0.00012687 | 0.00012687 |  |  | 0.018969 | 0.018969 |  |  | 0 | 0 | 0.0177 | 0.0177 | 223 | 30 | NO
2013-04-02 |  |  | 0.1027 | 0.1027 |  |  | 0.0079716 | 0.0079716 | 0.096363 | 0.096363 |  |  | 0.00079817 | 0.00079817 |  |  | 0.00013864 | 0.00013864 | 0.00075407 | 0.00075407 |  |  | 0.0080465 | 0.0080465 |  |  | 0.10259 | 0.10259 | 0.014368 | 0.014368 | 569 | 235 | NO
2013-04-03 |  |  | 0.0032487 | 0.0032487 |  |  | 0.0021797 | 0.0021797 | 0.0031773 | 0.0031773 |  |  | 2.8527e-05 | 2.8527e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 2.9709e-05 | 2.9709e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 452 | 128 | NO
2013-04-04 |  |  | 0.0099285 | 0.0099285 |  |  | 0.076734 | 0.076734 | 0.014395 | 0.014395 |  |  | 0.00011093 | 0.00011093 |  |  | 0.00079347 | 0.00079347 | 0.00015657 | 0.00015657 |  |  | 0 | 0 |  |  | 0.039465 | 0.039465 | 0.0026388 | 0.0026388 | 555 | 282 | NO
2013-04-05 |  |  | 0.071769 | 0.071769 |  |  | 0.0024254 | 0.0024254 | 0.067133 | 0.067133 |  |  | 0.0003957 | 0.0003957 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00037079 | 0.00037079 |  |  | 0.0017004 | 0.0017004 |  |  | 0.048269 | 0.048269 | 0.0048141 | 0.0048141 | 588 | 265 | NO
2013-04-06 |  |  | 0.026042 | 0.026042 |  |  | 0 | 0 | 0.024301 | 0.024301 |  |  | 0.0004538 | 0.0004538 |  |  | 0 | 0 | 0.00042346 | 0.00042346 |  |  | 0.0040232 | 0.0040232 |  |  | 0 | 0 | 0.0037542 | 0.0037542 | 274 | 97 | NO
2013-04-07 |  |  | 0.0022533 | 0.0022533 |  |  | 0 | 0 | 0.0021026 | 0.0021026 |  |  | 7.6673e-05 | 7.6673e-05 |  |  | 0 | 0 | 7.1547e-05 | 7.1547e-05 |  |  | 0.0028543 | 0.0028543 |  |  | 0 | 0 | 0.0026635 | 0.0026635 | 195 | 28 | NO
2013-04-08 |  |  | 0.030556 | 0.030556 |  |  | 0.10006 | 0.10006 | 0.035203 | 0.035203 |  |  | 0.00021386 | 0.00021386 |  |  | 0.0011322 | 0.0011322 | 0.00027526 | 0.00027526 |  |  | 0 | 0 |  |  | 0.039673 | 0.039673 | 0.0026527 | 0.0026527 | 490 | 200 | NO
2013-04-09 |  |  | 0.01065 | 0.01065 |  |  | 0.0019409 | 0.0019409 | 0.010068 | 0.010068 |  |  | 9.8445e-05 | 9.8445e-05 |  |  | 0.00013864 | 0.00013864 | 0.00010113 | 0.00010113 |  |  | 0.010727 | 0.010727 |  |  | 0 | 0 | 0.01001 | 0.01001 | 422 | 143 | NO
2013-04-10 |  |  | 0.11348 | 0.11348 |  |  | 0.0038626 | 0.0038626 | 0.10615 | 0.10615 |  |  | 0.0033924 | 0.0033924 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0031671 | 0.0031671 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 679 | 283 | NO
2013-04-11 |  |  | 0.024338 | 0.024338 |  |  | 0.12635 | 0.12635 | 0.031159 | 0.031159 |  |  | 0.00028779 | 0.00028779 |  |  | 0.0011713 | 0.0011713 | 0.00034686 | 0.00034686 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 464 | 179 | NO
2013-04-12 |  |  | 0.017148 | 0.017148 |  |  | 0 | 0 | 0.016002 | 0.016002 |  |  | 0.00059271 | 0.00059271 |  |  | 0 | 0 | 0.00055308 | 0.00055308 |  |  | 0.0043097 | 0.0043097 |  |  | 0.02001 | 0.02001 | 0.0053594 | 0.0053594 | 347 | 79 | NO
2013-04-13 |  |  | 0.011914 | 0.011914 |  |  | 0 | 0 | 0.011117 | 0.011117 |  |  | 0.0001755 | 0.0001755 |  |  | 0 | 0 | 0.00016376 | 0.00016376 |  |  | 0.0047252 | 0.0047252 |  |  | 0 | 0 | 0.0044093 | 0.0044093 | 171 | 20 | NO
2013-04-14 |  |  | 0.020545 | 0.020545 |  |  | 0.15162 | 0.15162 | 0.029309 | 0.029309 |  |  | 0.00026822 | 0.00026822 |  |  | 0.0020911 | 0.0020911 | 0.0003901 | 0.0003901 |  |  | 0.0046623 | 0.0046623 |  |  | 0.064882 | 0.064882 | 0.0086888 | 0.0086888 | 250 | 56 | NO
2013-04-15 |  |  | 0.041038 | 0.041038 |  |  | 0 | 0 | 0.038294 | 0.038294 |  |  | 0.00012252 | 0.00012252 |  |  | 0 | 0 | 0.00011433 | 0.00011433 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 438 | 159 | NO
2013-04-16 |  |  | 0.090299 | 0.090299 |  |  | 0.0071868 | 0.0071868 | 0.084741 | 0.084741 |  |  | 0.0016225 | 0.0016225 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0015171 | 0.0015171 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 671 | 236 | NO
2013-04-17 |  |  | 0.18314 | 0.18314 |  |  | 0.1513 | 0.1513 | 0.18101 | 0.18101 |  |  | 0.0036006 | 0.0036006 |  |  | 0.0017099 | 0.0017099 | 0.0034742 | 0.0034742 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 668 | 243 | NO
2013-04-18 |  |  | 0.18212 | 0.18212 |  |  | 0 | 0 | 0.16994 | 0.16994 |  |  | 0.0027435 | 0.0027435 |  |  | 0 | 0 | 0.0025601 | 0.0025601 |  |  | 0.0072633 | 0.0072633 |  |  | 0 | 0 | 0.0067777 | 0.0067777 | 709 | 166 | NO
2013-04-19 |  |  | 0.082983 | 0.082983 |  |  | 0.56387 | 0.56387 | 0.11514 | 0.11514 |  |  | 0.0015862 | 0.0015862 |  |  | 0.0045519 | 0.0045519 | 0.0017845 | 0.0017845 |  |  | 0.0048213 | 0.0048213 |  |  | 0 | 0 | 0.0044989 | 0.0044989 | 614 | 211 | NO
2013-04-20 |  |  | 0.71335 | 0.71335 |  |  | 0.00032349 | 0.00032349 | 0.66567 | 0.66567 |  |  | 0.0064785 | 0.0064785 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0060484 | 0.0060484 |  |  | 0.010851 | 0.010851 |  |  | 0 | 0 | 0.010126 | 0.010126 | 875 | 131 | NO
2013-04-21 |  |  | 0.0085439 | 0.0085439 |  |  | 0.01507 | 0.01507 | 0.0089802 | 0.0089802 |  |  | 0.0038447 | 0.0038447 |  |  | 0.00018485 | 0.00018485 | 0.0035999 | 0.0035999 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 138 | 27 | NO
2013-04-22 |  |  | 0.0025406 | 0.0025406 |  |  | 0.012755 | 0.012755 | 0.0032236 | 0.0032236 |  |  | 2.1523e-05 | 2.1523e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 2.3174e-05 | 2.3174e-05 |  |  | 0 | 0 |  |  | 2.3106e-05 | 2.3106e-05 | 1.5449e-06 | 1.5449e-06 | 534 | 205 | NO
2013-04-23 |  |  | 0.5144 | 0.5144 |  |  | 0.0016625 | 0.0016625 | 0.48012 | 0.48012 |  |  | 0.012004 | 0.012004 |  |  | 4.6212e-05 | 4.6212e-05 | 0.011204 | 0.011204 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1109 | 289 | NO
2013-04-24 |  |  | 0.16598 | 0.16598 |  |  | 0.030339 | 0.030339 | 0.15691 | 0.15691 |  |  | 0.00054668 | 0.00054668 |  |  | 0.00092263 | 0.00092263 | 0.00057182 | 0.00057182 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 551 | 274 | NO
2013-04-25 |  |  | 0.00015847 | 0.00015847 |  |  | 0.0031567 | 0.0031567 | 0.00035894 | 0.00035894 |  |  | 4.967e-06 | 4.967e-06 |  |  | 2.3106e-05 | 2.3106e-05 | 6.1798e-06 | 6.1798e-06 |  |  | 0.0015265 | 0.0015265 |  |  | 0.039558 | 0.039558 | 0.0040694 | 0.0040694 | 115 | 14 | NO
2013-04-26 |  |  | 0.0027097 | 0.0027097 |  |  | 0.004094 | 0.004094 | 0.0028023 | 0.0028023 |  |  | 0.0001755 | 0.0001755 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00016531 | 0.00016531 |  |  | 0.0085051 | 0.0085051 |  |  | 0 | 0 | 0.0079364 | 0.0079364 | 454 | 121 | NO
2013-04-27 |  |  | 0.22083 | 0.22083 |  |  | 1.8094 | 1.8094 | 0.32704 | 0.32704 |  |  | 0.0038771 | 0.0038771 |  |  | 0.048246 | 0.048246 | 0.0068438 | 0.0068438 |  |  | 0.0040746 | 0.0040746 |  |  | 0 | 0 | 0.0038021 | 0.0038021 | 744 | 82 | NO
2013-04-28 |  |  | 0.022391 | 0.022391 |  |  | 0 | 0 | 0.020894 | 0.020894 |  |  | 6.5647e-05 | 6.5647e-05 |  |  | 0 | 0 | 6.1257e-05 | 6.1257e-05 |  |  | 0.0024156 | 0.0024156 |  |  | 0 | 0 | 0.0022541 | 0.0022541 | 118 | 6 | NO
2013-04-29 |  |  | 0.035072 | 0.035072 |  |  | 0.0055228 | 0.0055228 | 0.033097 | 0.033097 |  |  | 0.00046615 | 0.00046615 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00043807 | 0.00043807 |  |  | 0.00013245 | 0.00013245 |  |  | 0 | 0 | 0.0001236 | 0.0001236 | 495 | 172 | NO
2013-04-30 |  |  | 0.027132 | 0.027132 |  |  | 0.012622 | 0.012622 | 0.026162 | 0.026162 |  |  | 0.00018543 | 0.00018543 |  |  | 0.00013864 | 0.00013864 | 0.0001823 | 0.0001823 |  |  | 0.0039669 | 0.0039669 |  |  | 0 | 0 | 0.0037017 | 0.0037017 | 419 | 91 | NO
2013-05-01 |  |  | 0.0058542 | 0.0058542 |  |  | 0.0028729 | 0.0028729 | 0.0056548 | 0.0056548 |  |  | 0.00013667 | 0.00013667 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00013063 | 0.00013063 |  |  | 0.008313 | 0.008313 |  |  | 0 | 0 | 0.0077572 | 0.0077572 | 444 | 147 | NO
2013-05-02 |  |  | 0.030554 | 0.030554 |  |  | 0.011638 | 0.011638 | 0.029289 | 0.029289 |  |  | 0.0002963 | 0.0002963 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00027803 | 0.00027803 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 386 | 55 | NO
2013-05-03 |  |  | 0.21239 | 0.21239 |  |  | 0.025629 | 0.025629 | 0.1999 | 0.1999 |  |  | 0.011495 | 0.011495 |  |  | 0.00018485 | 0.00018485 | 0.010739 | 0.010739 |  |  | 0.0019189 | 0.0019189 |  |  | 0 | 0 | 0.0017906 | 0.0017906 | 756 | 147 | NO
2013-05-04 |  |  | 0.0056083 | 0.0056083 |  |  | 0 | 0 | 0.0052333 | 0.0052333 |  |  | 6.8461e-05 | 6.8461e-05 |  |  | 0 | 0 | 6.3884e-05 | 6.3884e-05 |  |  | 0 | 0 |  |  | 0.076574 | 0.076574 | 0.00512 | 0.00512 | 566 | 148 | NO
2013-05-05 |  |  | 0.33232 | 0.33232 |  |  | 0.12298 | 0.12298 | 0.31832 | 0.31832 |  |  | 0.0015827 | 0.0015827 |  |  | 0.00032349 | 0.00032349 | 0.0014985 | 0.0014985 |  |  | 0.0051855 | 0.0051855 |  |  | 0 | 0 | 0.0048388 | 0.0048388 | 613 | 133 | NO
2013-05-06 |  |  | 0.034909 | 0.034909 |  |  | 0 | 0 | 0.032575 | 0.032575 |  |  | 0.00027202 | 0.00027202 |  |  | 0 | 0 | 0.00025384 | 0.00025384 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 488 | 164 | NO
2013-05-07 |  |  | 0.035566 | 0.035566 |  |  | 0 | 0 | 0.033188 | 0.033188 |  |  | 0.0001384 | 0.0001384 |  |  | 0 | 0 | 0.00012914 | 0.00012914 |  |  | 0 | 0 |  |  | 0.075673 | 0.075673 | 0.0050597 | 0.0050597 | 473 | 157 | NO
2013-05-08 |  |  | 0.02505 | 0.02505 |  |  | 0.010021 | 0.010021 | 0.024045 | 0.024045 |  |  | 0.00057948 | 0.00057948 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00054382 | 0.00054382 |  |  | 0.0044173 | 0.0044173 |  |  | 0 | 0 | 0.0041219 | 0.0041219 | 472 | 46 | NO
2013-05-09 |  |  | 0.036458 | 0.036458 |  |  | 0.016521 | 0.016521 | 0.035125 | 0.035125 |  |  | 0.0003762 | 0.0003762 |  |  | 6.9318e-05 | 6.9318e-05 | 0.00035568 | 0.00035568 |  |  | 0.0021871 | 0.0021871 |  |  | 0.059845 | 0.059845 | 0.0060423 | 0.0060423 | 406 | 53 | NO
2013-05-10 |  |  | 0.0021115 | 0.0021115 |  |  | 0.0084245 | 0.0084245 | 0.0025336 | 0.0025336 |  |  | 1.159e-05 | 1.159e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 1.3905e-05 | 1.3905e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 332 | 33 | NO
2013-05-11 |  |  | 0.011618 | 0.011618 |  |  | 2.1842 | 2.1842 | 0.15689 | 0.15689 |  |  | 0.00036921 | 0.00036921 |  |  | 0.064882 | 0.064882 | 0.0046827 | 0.0046827 |  |  | 0.014709 | 0.014709 |  |  | 0 | 0 | 0.013725 | 0.013725 | 427 | 42 | NO
2013-05-12 |  |  | 0.59502 | 0.59502 |  |  | 1.452 | 1.452 | 0.65232 | 0.65232 |  |  | 0.0060911 | 0.0060911 |  |  | 0.0016364 | 0.0016364 | 0.0057933 | 0.0057933 |  |  | 0.00060928 | 0.00060928 |  |  | 0 | 0 | 0.00056854 | 0.00056854 | 571 | 46 | NO
2013-05-13 |  |  | 0.019898 | 0.019898 |  |  | 0.018927 | 0.018927 | 0.019833 | 0.019833 |  |  | 0.0038411 | 0.0038411 |  |  | 0.00011553 | 0.00011553 | 0.003592 | 0.003592 |  |  | 0.0068544 | 0.0068544 |  |  | 0 | 0 | 0.0063961 | 0.0063961 | 537 | 129 | NO
2013-05-14 |  |  | 0.009017 | 0.009017 |  |  | 0 | 0 | 0.0084141 | 0.0084141 |  |  | 0.0017695 | 0.0017695 |  |  | 0 | 0 | 0.0016512 | 0.0016512 |  |  | 0.0057997 | 0.0057997 |  |  | 0 | 0 | 0.005412 | 0.005412 | 468 | 82 | NO
2013-05-15 |  |  | 0.15655 | 0.15655 |  |  | 5.4718 | 5.4718 | 0.51194 | 0.51194 |  |  | 0.002198 | 0.002198 |  |  | 0.059822 | 0.059822 | 0.0060509 | 0.0060509 |  |  | 0.0054521 | 0.0054521 |  |  | 0 | 0 | 0.0050875 | 0.0050875 | 1124 | 157 | NO
2013-05-16 |  |  | 0.012945 | 0.012945 |  |  | 0.01743 | 0.01743 | 0.013245 | 0.013245 |  |  | 0.0034296 | 0.0034296 |  |  | 0.00025417 | 0.00025417 | 0.0032173 | 0.0032173 |  |  | 0.0016308 | 0.0016308 |  |  | 0 | 0 | 0.0015218 | 0.0015218 | 469 | 63 | NO
2013-05-17 |  |  | 0.10816 | 0.10816 |  |  | 0.056312 | 0.056312 | 0.1047 | 0.1047 |  |  | 0.00068213 | 0.00068213 |  |  | 0.00048454 | 0.00048454 | 0.00066892 | 0.00066892 |  |  | 0.00039073 | 0.00039073 |  |  | 0 | 0 | 0.00036461 | 0.00036461 | 622 | 109 | NO
2013-05-18 |  |  | 0.12416 | 0.12416 |  |  | 0.01144 | 0.01144 | 0.11662 | 0.11662 |  |  | 0.00030464 | 0.00030464 |  |  | 6.1231e-05 | 6.1231e-05 | 0.00028836 | 0.00028836 |  |  | 0.0040944 | 0.0040944 |  |  | 0 | 0 | 0.0038207 | 0.0038207 | 318 | 90 | NO
2013-05-19 |  |  | 0.016596 | 0.016596 |  |  | 0 | 0 | 0.015486 | 0.015486 |  |  | 0.00015364 | 0.00015364 |  |  | 0 | 0 | 0.00014337 | 0.00014337 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 198 | 53 | NO
2013-05-20 |  |  | 0.080713 | 0.080713 |  |  | 2.647 | 2.647 | 0.25231 | 0.25231 |  |  | 0.00089408 | 0.00089408 |  |  | 0.052151 | 0.052151 | 0.0043213 | 0.0043213 |  |  | 0.0030961 | 0.0030961 |  |  | 0 | 0 | 0.0028891 | 0.0028891 | 1099 | 281 | NO
2013-05-21 |  |  | 0.021246 | 0.021246 |  |  | 0.0035618 | 0.0035618 | 0.020063 | 0.020063 |  |  | 0.00019922 | 0.00019922 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00018745 | 0.00018745 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 491 | 73 | NO
2013-05-22 |  |  | 0.010418 | 0.010418 |  |  | 0 | 0 | 0.0097217 | 0.0097217 |  |  | 0.0005934 | 0.0005934 |  |  | 0 | 0 | 0.00055373 | 0.00055373 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 480 | 170 | NO
2013-05-23 |  |  | 0.023353 | 0.023353 |  |  | 0 | 0 | 0.021791 | 0.021791 |  |  | 0.00017782 | 0.00017782 |  |  | 0 | 0 | 0.00016593 | 0.00016593 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 486 | 68 | NO
2013-05-24 |  |  | 0.011832 | 0.011832 |  |  | 0.0050776 | 0.0050776 | 0.011381 | 0.011381 |  |  | 0.00011715 | 0.00011715 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00011241 | 0.00011241 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 547 | 125 | NO
2013-05-25 |  |  | 0.0091265 | 0.0091265 |  |  | 0 | 0 | 0.0085163 | 0.0085163 |  |  | 0.0045216 | 0.0045216 |  |  | 0 | 0 | 0.0042193 | 0.0042193 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 170 | 32 | NO
2013-05-26 |  |  | 0.02066 | 0.02066 |  |  | 0.22484 | 0.22484 | 0.034312 | 0.034312 |  |  | 0.00022593 | 0.00022593 |  |  | 0.00099356 | 0.00099356 | 0.00027726 | 0.00027726 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 172 | 32 | NO
2013-05-27 |  |  | 0.01875 | 0.01875 |  |  | 0.0019421 | 0.0019421 | 0.017626 | 0.017626 |  |  | 0.00012369 | 0.00012369 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00011697 | 0.00011697 |  |  | 0.003957 | 0.003957 |  |  | 0 | 0 | 0.0036924 | 0.0036924 | 472 | 70 | NO
2013-05-28 |  |  | 0.013731 | 0.013731 |  |  | 0.020033 | 0.020033 | 0.014152 | 0.014152 |  |  | 0.0002279 | 0.0002279 |  |  | 0.00013864 | 0.00013864 | 0.00022193 | 0.00022193 |  |  | 0.0017633 | 0.0017633 |  |  | 0 | 0 | 0.0016454 | 0.0016454 | 454 | 102 | NO
2013-05-29 |  |  | 0.03048 | 0.03048 |  |  | 0.016087 | 0.016087 | 0.029517 | 0.029517 |  |  | 0.00020979 | 0.00020979 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00019885 | 0.00019885 |  |  | 0.0033759 | 0.0033759 |  |  | 0 | 0 | 0.0031502 | 0.0031502 | 529 | 160 | NO
2013-05-30 |  |  | 0.0074221 | 0.0074221 |  |  | 0.0030346 | 0.0030346 | 0.0071287 | 0.0071287 |  |  | 0.00013576 | 0.00013576 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00012823 | 0.00012823 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 554 | 72 | NO
2013-05-31 |  |  | 0.30291 | 0.30291 |  |  | 0.010801 | 0.010801 | 0.28338 | 0.28338 |  |  | 0.0053879 | 0.0053879 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0050307 | 0.0050307 |  |  | 0.0093909 | 0.0093909 |  |  | 0 | 0 | 0.008763 | 0.008763 | 809 | 178 | NO
2013-06-01 |  |  | 0.39811 | 0.39811 |  |  | 0.017484 | 0.017484 | 0.37266 | 0.37266 |  |  | 0.0061409 | 0.0061409 |  |  | 9.2425e-05 | 9.2425e-05 | 0.0057365 | 0.0057365 |  |  | 0.0014354 | 0.0014354 |  |  | 0 | 0 | 0.0013395 | 0.0013395 | 949 | 545 | NO
2013-06-02 |  |  | 0.38363 | 0.38363 |  |  | 0 | 0 | 0.35798 | 0.35798 |  |  | 0.0019104 | 0.0019104 |  |  | 0 | 0 | 0.0017827 | 0.0017827 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 353 | 74 | NO
2013-06-03 |  |  | 0.014734 | 0.014734 |  |  | 0 | 0 | 0.013749 | 0.013749 |  |  | 0.00022419 | 0.00022419 |  |  | 0 | 0 | 0.0002092 | 0.0002092 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 534 | 196 | NO
2013-06-04 |  |  | 0.0090998 | 0.0090998 |  |  | 0.035129 | 0.035129 | 0.01084 | 0.01084 |  |  | 6.6226e-05 | 6.6226e-05 |  |  | 0.0005185 | 0.0005185 | 9.6467e-05 | 9.6467e-05 |  |  | 0.0047236 | 0.0047236 |  |  | 0 | 0 | 0.0044077 | 0.0044077 | 550 | 203 | NO
2013-06-05 |  |  | 0.51364 | 0.51364 |  |  | 0.98169 | 0.98169 | 0.54493 | 0.54493 |  |  | 0.035418 | 0.035418 |  |  | 0.067815 | 0.067815 | 0.037584 | 0.037584 |  |  | 4.967e-06 | 4.967e-06 |  |  | 0 | 0 | 4.6348e-06 | 4.6348e-06 | 1534 | 232 | NO
2013-06-06 |  |  | 0.0046386 | 0.0046386 |  |  | 0.28559 | 0.28559 | 0.023424 | 0.023424 |  |  | 2.4835e-05 | 2.4835e-05 |  |  | 0.00069318 | 0.00069318 | 6.9523e-05 | 6.9523e-05 |  |  | 1.6557e-06 | 1.6557e-06 |  |  | 0 | 0 | 1.5449e-06 | 1.5449e-06 | 401 | 76 | NO
2013-06-07 |  |  | 0.057526 | 0.057526 |  |  | 0.010223 | 0.010223 | 0.054363 | 0.054363 |  |  | 0.00042651 | 0.00042651 |  |  | 9.2425e-05 | 9.2425e-05 | 0.00040417 | 0.00040417 |  |  | 0.0081309 | 0.0081309 |  |  | 0 | 0 | 0.0075872 | 0.0075872 | 489 | 145 | NO
2013-06-08 |  |  | 0.0049334 | 0.0049334 |  |  | 0.010441 | 0.010441 | 0.0053016 | 0.0053016 |  |  | 4.8676e-05 | 4.8676e-05 |  |  | 0.00013864 | 0.00013864 | 5.4691e-05 | 5.4691e-05 |  |  | 0 | 0 |  |  | 0.039073 | 0.039073 | 0.0026125 | 0.0026125 | 231 | 80 | NO
2013-06-09 |  |  | 0.0060246 | 0.0060246 |  |  | 0.0046975 | 0.0046975 | 0.0059359 | 0.0059359 |  |  | 6.9008e-05 | 6.9008e-05 |  |  | 9.2425e-05 | 9.2425e-05 | 7.0573e-05 | 7.0573e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 159 | 21 | NO
2013-06-10 |  |  | 0.0021203 | 0.0021203 |  |  | 0 | 0 | 0.0019785 | 0.0019785 |  |  | 1.6557e-05 | 1.6557e-05 |  |  | 0 | 0 | 1.5449e-05 | 1.5449e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 123 | 17 | NO
2013-06-11 |  |  | 0.10593 | 0.10593 |  |  | 0.015923 | 0.015923 | 0.099912 | 0.099912 |  |  | 0.0012967 | 0.0012967 |  |  | 0.00013725 | 0.00013725 | 0.0012191 | 0.0012191 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 597 | 251 | NO
2013-06-12 |  |  | 0.025861 | 0.025861 |  |  | 0 | 0 | 0.024132 | 0.024132 |  |  | 0.00019639 | 0.00019639 |  |  | 0 | 0 | 0.00018326 | 0.00018326 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 566 | 111 | NO
2013-06-13 |  |  | 0.048964 | 0.048964 |  |  | 0.052058 | 0.052058 | 0.049171 | 0.049171 |  |  | 0.00032305 | 0.00032305 |  |  | 0.00071722 | 0.00071722 | 0.00034941 | 0.00034941 |  |  | 0 | 0 |  |  | 0.019964 | 0.019964 | 0.0013348 | 0.0013348 | 596 | 43 | NO
2013-06-14 |  |  | 0.11122 | 0.11122 |  |  | 0 | 0 | 0.10379 | 0.10379 |  |  | 0.0032794 | 0.0032794 |  |  | 0 | 0 | 0.0030602 | 0.0030602 |  |  | 0.0035183 | 0.0035183 |  |  | 0.022113 | 0.022113 | 0.0047615 | 0.0047615 | 822 | 153 | NO
2013-06-15 |  |  | 0.00090203 | 0.00090203 |  |  | 0 | 0 | 0.00084171 | 0.00084171 |  |  | 9.9339e-06 | 9.9339e-06 |  |  | 0 | 0 | 9.2697e-06 | 9.2697e-06 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 228 | 49 | NO
2013-06-16 |  |  | 0.0018788 | 0.0018788 |  |  | 0.010614 | 0.010614 | 0.0024629 | 0.0024629 |  |  | 6.6226e-05 | 6.6226e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 6.4888e-05 | 6.4888e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 211 | 25 | NO
2013-06-17 |  |  | 0.31865 | 0.31865 |  |  | 0.073333 | 0.073333 | 0.30225 | 0.30225 |  |  | 0.0046674 | 0.0046674 |  |  | 0.00071791 | 0.00071791 | 0.0044033 | 0.0044033 |  |  | 0.0073395 | 0.0073395 |  |  | 0 | 0 | 0.0068488 | 0.0068488 | 1146 | 235 | NO
2013-06-18 |  |  | 0.017541 | 0.017541 |  |  | 0.0058201 | 0.0058201 | 0.016757 | 0.016757 |  |  | 0.00022081 | 0.00022081 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00020759 | 0.00020759 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 557 | 159 | NO
2013-06-19 |  |  | 0.039665 | 0.039665 |  |  | 0.039392 | 0.039392 | 0.039647 | 0.039647 |  |  | 0.0024914 | 0.0024914 |  |  | 0.00032788 | 0.00032788 | 0.0023467 | 0.0023467 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 761 | 174 | NO
2013-06-20 |  |  | 0.040668 | 0.040668 |  |  | 0.013203 | 0.013203 | 0.038832 | 0.038832 |  |  | 0.00057968 | 0.00057968 |  |  | 0.00028975 | 0.00028975 | 0.00056029 | 0.00056029 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 651 | 283 | NO
2013-06-21 |  |  | 0.009288 | 0.009288 |  |  | 0.011859 | 0.011859 | 0.0094599 | 0.0094599 |  |  | 0.000146 | 0.000146 |  |  | 5.3606e-05 | 5.3606e-05 | 0.00013982 | 0.00013982 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 540 | 204 | NO
2013-06-22 |  |  | 0.0048156 | 0.0048156 |  |  | 0.016921 | 0.016921 | 0.0056251 | 0.0056251 |  |  | 6.2484e-05 | 6.2484e-05 |  |  | 0.00025417 | 0.00025417 | 7.5301e-05 | 7.5301e-05 |  |  | 0.0040746 | 0.0040746 |  |  | 0 | 0 | 0.0038021 | 0.0038021 | 246 | 68 | NO
2013-06-23 |  |  | 0.00080925 | 0.00080925 |  |  | 0.0049239 | 0.0049239 | 0.0010844 | 0.0010844 |  |  | 9.9339e-06 | 9.9339e-06 |  |  | 2.3106e-05 | 2.3106e-05 | 1.0815e-05 | 1.0815e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 249 | 52 | NO
2013-06-24 |  |  | 0.051954 | 0.051954 |  |  | 1.574 | 1.574 | 0.15372 | 0.15372 |  |  | 0.00060997 | 0.00060997 |  |  | 0.0729 | 0.0729 | 0.0054435 | 0.0054435 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 683 | 234 | NO
2013-06-25 |  |  | 0.097205 | 0.097205 |  |  | 0.00099703 | 0.00099703 | 0.090772 | 0.090772 |  |  | 0.00059484 | 0.00059484 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00055661 | 0.00055661 |  |  | 0 | 0 |  |  | 0.019987 | 0.019987 | 0.0013364 | 0.0013364 | 609 | 193 | NO
2013-06-26 |  |  | 0.012653 | 0.012653 |  |  | 0.013263 | 0.013263 | 0.012694 | 0.012694 |  |  | 0.00019752 | 0.00019752 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00018586 | 0.00018586 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 460 | 137 | NO
2013-06-27 |  |  | 0.025953 | 0.025953 |  |  | 0.0027693 | 0.0027693 | 0.024403 | 0.024403 |  |  | 0.00021129 | 0.00021129 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00019871 | 0.00019871 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 552 | 119 | NO
2013-06-28 |  |  | 0.0026566 | 0.0026566 |  |  | 0 | 0 | 0.0024789 | 0.0024789 |  |  | 2.4719e-05 | 2.4719e-05 |  |  | 0 | 0 | 2.3066e-05 | 2.3066e-05 |  |  | 0.0015364 | 0.0015364 |  |  | 0 | 0 | 0.0014337 | 0.0014337 | 363 | 76 | NO
2013-06-29 |  |  | 0.016792 | 0.016792 |  |  | 1.9037 | 1.9037 | 0.14296 | 0.14296 |  |  | 0.00013929 | 0.00013929 |  |  | 0.0031193 | 0.0031193 | 0.00033854 | 0.00033854 |  |  | 0.0086541 | 0.0086541 |  |  | 0.039673 | 0.039673 | 0.010728 | 0.010728 | 357 | 74 | NO
2013-06-30 |  |  | 0.0033744 | 0.0033744 |  |  | 0.0019355 | 0.0019355 | 0.0032782 | 0.0032782 |  |  | 1.9868e-05 | 1.9868e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 2.0084e-05 | 2.0084e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 186 | 62 | NO
2013-07-01 |  |  | 0.29391 | 0.29391 |  |  | 0.0087301 | 0.0087301 | 0.27484 | 0.27484 |  |  | 0.007962 | 0.007962 |  |  | 0.00010398 | 0.00010398 | 0.0074366 | 0.0074366 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 743 | 147 | NO
2013-07-02 |  |  | 0.10449 | 0.10449 |  |  | 0 | 0 | 0.097503 | 0.097503 |  |  | 0.0063986 | 0.0063986 |  |  | 0 | 0 | 0.0059707 | 0.0059707 |  |  | 0.0018312 | 0.0018312 |  |  | 0 | 0 | 0.0017087 | 0.0017087 | 614 | 78 | NO
2013-07-03 |  |  | 0.057388 | 0.057388 |  |  | 0.031116 | 0.031116 | 0.055632 | 0.055632 |  |  | 0.00051319 | 0.00051319 |  |  | 0.00027473 | 0.00027473 | 0.00049724 | 0.00049724 |  |  | 0.0077352 | 0.0077352 |  |  | 0 | 0 | 0.007218 | 0.007218 | 513 | 149 | NO
2013-07-04 |  |  | 0.024255 | 0.024255 |  |  | 4.725 | 4.725 | 0.33856 | 0.33856 |  |  | 0.00023669 | 0.00023669 |  |  | 0.065544 | 0.065544 | 0.0046033 | 0.0046033 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 915 | 41 | NO
2013-07-05 |  |  | 0.034148 | 0.034148 |  |  | 0.042782 | 0.042782 | 0.034726 | 0.034726 |  |  | 0.00011497 | 0.00011497 |  |  | 0.0011414 | 0.0011414 | 0.0001836 | 0.0001836 |  |  | 0 | 0 |  |  | 0.052081 | 0.052081 | 0.0034823 | 0.0034823 | 481 | 71 | NO
2013-07-06 |  |  | 0.027633 | 0.027633 |  |  | 0 | 0 | 0.025785 | 0.025785 |  |  | 0.00029166 | 0.00029166 |  |  | 0 | 0 | 0.00027216 | 0.00027216 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 250 | 56 | NO
2013-07-07 |  |  | 0.064663 | 0.064663 |  |  | 0 | 0 | 0.06034 | 0.06034 |  |  | 0.00031146 | 0.00031146 |  |  | 0 | 0 | 0.00029064 | 0.00029064 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 189 | 43 | NO
2013-07-08 |  |  | 0.002396 | 0.002396 |  |  | 0.0054326 | 0.0054326 | 0.002599 | 0.002599 |  |  | 1.6557e-05 | 1.6557e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 1.6994e-05 | 1.6994e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 571 | 174 | NO
2013-07-09 |  |  | 0.088757 | 0.088757 |  |  | 0.0074059 | 0.0074059 | 0.083318 | 0.083318 |  |  | 0.0023182 | 0.0023182 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0021663 | 0.0021663 |  |  | 0.061859 | 0.061859 |  |  | 0.20302 | 0.20302 | 0.071298 | 0.071298 | 791 | 386 | NO
2013-07-10 |  |  | 0.016263 | 0.016263 |  |  | 0 | 0 | 0.015175 | 0.015175 |  |  | 0.00010353 | 0.00010353 |  |  | 0 | 0 | 9.6606e-05 | 9.6606e-05 |  |  | 0.0039669 | 0.0039669 |  |  | 0 | 0 | 0.0037017 | 0.0037017 | 531 | 123 | NO
2013-07-11 |  |  | 0.013964 | 0.013964 |  |  | 0.0058357 | 0.0058357 | 0.013421 | 0.013421 |  |  | 0.00014437 | 0.00014437 |  |  | 7.6481e-05 | 7.6481e-05 | 0.00013983 | 0.00013983 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 495 | 75 | NO
2013-07-12 |  |  | 0.031509 | 0.031509 |  |  | 0.047337 | 0.047337 | 0.032567 | 0.032567 |  |  | 0.00032947 | 0.00032947 |  |  | 0.00015019 | 0.00015019 | 0.00031749 | 0.00031749 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 489 | 101 | NO
2013-07-13 |  |  | 0.034403 | 0.034403 |  |  | 0.0040028 | 0.0040028 | 0.032371 | 0.032371 |  |  | 0.00027411 | 0.00027411 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00025733 | 0.00025733 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 356 | 137 | NO
2013-07-14 |  |  | 0.63176 | 0.63176 |  |  | 0.002512 | 0.002512 | 0.58969 | 0.58969 |  |  | 0.011148 | 0.011148 |  |  | 2.3106e-05 | 2.3106e-05 | 0.010405 | 0.010405 |  |  | 0.0028146 | 0.0028146 |  |  | 0 | 0 | 0.0026264 | 0.0026264 | 1091 | 249 | NO
2013-07-15 |  |  | 0.00087316 | 0.00087316 |  |  | 0 | 0 | 0.00081478 | 0.00081478 |  |  | 1.3245e-05 | 1.3245e-05 |  |  | 0 | 0 | 1.236e-05 | 1.236e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 432 | 88 | NO
2013-07-16 |  |  | 0.0037724 | 0.0037724 |  |  | 0.041422 | 0.041422 | 0.0062898 | 0.0062898 |  |  | 5.2054e-05 | 5.2054e-05 |  |  | 0.00018439 | 0.00018439 | 6.0902e-05 | 6.0902e-05 |  |  | 0 | 0 |  |  | 0.020056 | 0.020056 | 0.001341 | 0.001341 | 426 | 51 | NO
2013-07-17 |  |  | 0.028785 | 0.028785 |  |  | 0.00097084 | 0.00097084 | 0.026925 | 0.026925 |  |  | 0.00028222 | 0.00028222 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0002649 | 0.0002649 |  |  | 1.6557e-06 | 1.6557e-06 |  |  | 0 | 0 | 1.5449e-06 | 1.5449e-06 | 406 | 68 | NO
2013-07-18 |  |  | 0.99872 | 0.99872 |  |  | 0.32953 | 0.32953 | 0.95397 | 0.95397 |  |  | 0.017149 | 0.017149 |  |  | 0.001473 | 0.001473 | 0.016101 | 0.016101 |  |  | 0.0092286 | 0.0092286 |  |  | 0 | 0 | 0.0086115 | 0.0086115 | 2138 | 405 | NO
2013-07-19 |  |  | 0.048696 | 0.048696 |  |  | 0 | 0 | 0.04544 | 0.04544 |  |  | 0.00034838 | 0.00034838 |  |  | 0 | 0 | 0.00032509 | 0.00032509 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 525 | 64 | NO
2013-07-20 |  |  | 0.15538 | 0.15538 |  |  | 0.04109 | 0.04109 | 0.14774 | 0.14774 |  |  | 0.00076665 | 0.00076665 |  |  | 0.00037386 | 0.00037386 | 0.00074039 | 0.00074039 |  |  | 0.0042269 | 0.0042269 |  |  | 0 | 0 | 0.0039443 | 0.0039443 | 464 | 203 | NO
2013-07-21 |  |  | 0.50092 | 0.50092 |  |  | 0 | 0 | 0.46743 | 0.46743 |  |  | 0.0037914 | 0.0037914 |  |  | 0 | 0 | 0.0035379 | 0.0035379 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 987 | 373 | NO
2013-07-22 |  |  | 0.014405 | 0.014405 |  |  | 0 | 0 | 0.013442 | 0.013442 |  |  | 0.00049492 | 0.00049492 |  |  | 0 | 0 | 0.00046183 | 0.00046183 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 510 | 134 | NO
2013-07-23 |  |  | 0.14449 | 0.14449 |  |  | 0.0045092 | 0.0045092 | 0.13513 | 0.13513 |  |  | 0.002846 | 0.002846 |  |  | 6.9318e-05 | 6.9318e-05 | 0.0026603 | 0.0026603 |  |  | 0.010831 | 0.010831 |  |  | 0 | 0 | 0.010107 | 0.010107 | 601 | 188 | NO
2013-07-24 |  |  | 0.013022 | 0.013022 |  |  | 0 | 0 | 0.012151 | 0.012151 |  |  | 9.6276e-05 | 9.6276e-05 |  |  | 0 | 0 | 8.9839e-05 | 8.9839e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 396 | 60 | NO
2013-07-25 |  |  | 0.077986 | 0.077986 |  |  | 0.0044556 | 0.0044556 | 0.07307 | 0.07307 |  |  | 0.0006541 | 0.0006541 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00061345 | 0.00061345 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 581 | 131 | NO
2013-07-26 |  |  | 0.0089964 | 0.0089964 |  |  | 0.78351 | 0.78351 | 0.060783 | 0.060783 |  |  | 6.0315e-05 | 6.0315e-05 |  |  | 0.012708 | 0.012708 | 0.000906 | 0.000906 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 434 | 77 | NO
2013-07-27 |  |  | 0.18632 | 0.18632 |  |  | 1.0618 | 1.0618 | 0.24486 | 0.24486 |  |  | 0.0092518 | 0.0092518 |  |  | 0.00080872 | 0.00080872 | 0.0086872 | 0.0086872 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 574 | 55 | NO
2013-07-28 |  |  | 0.00067286 | 0.00067286 |  |  | 0.051121 | 0.051121 | 0.004046 | 0.004046 |  |  | 9.9339e-06 | 9.9339e-06 |  |  | 0.00023106 | 0.00023106 | 2.4719e-05 | 2.4719e-05 |  |  | 0.0063246 | 0.0063246 |  |  | 0 | 0 | 0.0059017 | 0.0059017 | 198 | 71 | NO
2013-07-29 |  |  | 0.010722 | 0.010722 |  |  | 0.015967 | 0.015967 | 0.011073 | 0.011073 |  |  | 0.00017328 | 0.00017328 |  |  | 6.9318e-05 | 6.9318e-05 | 0.00016633 | 0.00016633 |  |  | 0.0015066 | 0.0015066 |  |  | 0 | 0 | 0.0014059 | 0.0014059 | 415 | 64 | NO
2013-07-30 |  |  | 0.0040385 | 0.0040385 |  |  | 0 | 0 | 0.0037684 | 0.0037684 |  |  | 7.1988e-05 | 7.1988e-05 |  |  | 0 | 0 | 6.7174e-05 | 6.7174e-05 |  |  | 0.00088908 | 0.00088908 |  |  | 0 | 0 | 0.00082964 | 0.00082964 | 399 | 85 | NO
2013-07-31 |  |  | 0.030077 | 0.030077 |  |  | 0.0024724 | 0.0024724 | 0.028231 | 0.028231 |  |  | 0.0002632 | 0.0002632 |  |  | 3.4659e-05 | 3.4659e-05 | 0.00024792 | 0.00024792 |  |  | 0.0010298 | 0.0010298 |  |  | 0 | 0 | 0.00096096 | 0.00096096 | 418 | 135 | NO
2013-08-01 |  |  | 0.037031 | 0.037031 |  |  | 0 | 0 | 0.034555 | 0.034555 |  |  | 0.00018421 | 0.00018421 |  |  | 0 | 0 | 0.00017189 | 0.00017189 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 373 | 66 | NO
2013-08-02 |  |  | 0.094001 | 0.094001 |  |  | 0.0085963 | 0.0085963 | 0.088291 | 0.088291 |  |  | 0.0024239 | 0.0024239 |  |  | 0.00013864 | 0.00013864 | 0.0022711 | 0.0022711 |  |  | 0 | 0 |  |  | 0.059776 | 0.059776 | 0.0039968 | 0.0039968 | 538 | 78 | NO
2013-08-03 |  |  | 0.0088763 | 0.0088763 |  |  | 0.024878 | 0.024878 | 0.0099463 | 0.0099463 |  |  | 9.6773e-05 | 9.6773e-05 |  |  | 0.00017099 | 0.00017099 | 0.00010173 | 0.00010173 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 223 | 31 | NO
2013-08-04 |  |  | 0.0016829 | 0.0016829 |  |  | 0 | 0 | 0.0015704 | 0.0015704 |  |  | 1.3245e-05 | 1.3245e-05 |  |  | 0 | 0 | 1.236e-05 | 1.236e-05 |  |  | 0.0036408 | 0.0036408 |  |  | 0 | 0 | 0.0033973 | 0.0033973 | 204 | 60 | NO
2013-08-05 |  |  | 0.0096109 | 0.0096109 |  |  | 0.019984 | 0.019984 | 0.010305 | 0.010305 |  |  | 6.9074e-05 | 6.9074e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 6.6e-05 | 6.6e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 403 | 48 | NO
2013-08-06 |  |  | 0.082892 | 0.082892 |  |  | 0.90093 | 0.90093 | 0.13759 | 0.13759 |  |  | 0.0045426 | 0.0045426 |  |  | 0.0035815 | 0.0035815 | 0.0044783 | 0.0044783 |  |  | 0 | 0 |  |  | 0.04575 | 0.04575 | 0.003059 | 0.003059 | 624 | 206 | NO
2013-08-07 |  |  | 0.013519 | 0.013519 |  |  | 0 | 0 | 0.012615 | 0.012615 |  |  | 0.00023179 | 0.00023179 |  |  | 0 | 0 | 0.00021629 | 0.00021629 |  |  | 0.0021126 | 0.0021126 |  |  | 0 | 0 | 0.0019714 | 0.0019714 | 483 | 141 | NO
2013-08-08 |  |  | 0.013205 | 0.013205 |  |  | 0.018611 | 0.018611 | 0.013566 | 0.013566 |  |  | 0.00017507 | 0.00017507 |  |  | 0.00054161 | 0.00054161 | 0.00019958 | 0.00019958 |  |  | 0 | 0 |  |  | 2.3106e-05 | 2.3106e-05 | 1.5449e-06 | 1.5449e-06 | 493 | 115 | NO
2013-08-09 |  |  | 0.38599 | 0.38599 |  |  | 0.016507 | 0.016507 | 0.36128 | 0.36128 |  |  | 0.0033301 | 0.0033301 |  |  | 0.00012246 | 0.00012246 | 0.0031156 | 0.0031156 |  |  | 0.0023527 | 0.0023527 |  |  | 0 | 0 | 0.0021954 | 0.0021954 | 1226 | 353 | NO
2013-08-10 |  |  | 0.0028446 | 0.0028446 |  |  | 0.0050229 | 0.0050229 | 0.0029903 | 0.0029903 |  |  | 3.1772e-05 | 3.1772e-05 |  |  | 5.3606e-05 | 5.3606e-05 | 3.3232e-05 | 3.3232e-05 |  |  | 0.0052186 | 0.0052186 |  |  | 0 | 0 | 0.0048697 | 0.0048697 | 242 | 18 | NO
2013-08-11 |  |  | 0.0048868 | 0.0048868 |  |  | 0.0009539 | 0.0009539 | 0.0046238 | 0.0046238 |  |  | 4.5481e-05 | 4.5481e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 4.3985e-05 | 4.3985e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 152 | 33 | NO
2013-08-12 |  |  | 3.675 | 3.675 |  |  | 0.0060973 | 0.0060973 | 3.4297 | 3.4297 |  |  | 0.036178 | 0.036178 |  |  | 2.3106e-05 | 2.3106e-05 | 0.03376 | 0.03376 |  |  | 0.010715 | 0.010715 |  |  | 0 | 0 | 0.0099989 | 0.0099989 | 4345 | 835 | NO
2013-08-13 |  |  | 0.0064795 | 0.0064795 |  |  | 0.0027177 | 0.0027177 | 0.0062279 | 0.0062279 |  |  | 7.0928e-05 | 7.0928e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 6.7731e-05 | 6.7731e-05 |  |  | 0.0041391 | 0.0041391 |  |  | 0 | 0 | 0.0038624 | 0.0038624 | 949 | 382 | NO
2013-08-14 |  |  | 0.13262 | 0.13262 |  |  | 0.011281 | 0.011281 | 0.1245 | 0.1245 |  |  | 0.0032963 | 0.0032963 |  |  | 0.00011553 | 0.00011553 | 0.0030836 | 0.0030836 |  |  | 0 | 0 |  |  | 0.07491 | 0.07491 | 0.0050087 | 0.0050087 | 709 | 113 | NO
2013-08-15 |  |  | 0.014372 | 0.014372 |  |  | 0.0073104 | 0.0073104 | 0.013899 | 0.013899 |  |  | 0.0001648 | 0.0001648 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00015687 | 0.00015687 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 509 | 93 | NO
2013-08-16 |  |  | 0.85526 | 0.85526 |  |  | 0.0044572 | 0.0044572 | 0.79837 | 0.79837 |  |  | 0.019385 | 0.019385 |  |  | 4.6212e-05 | 4.6212e-05 | 0.018092 | 0.018092 |  |  | 0.007015 | 0.007015 |  |  | 0.13443 | 0.13443 | 0.015534 | 0.015534 | 2095 | 326 | NO
2013-08-17 |  |  | 0.15903 | 0.15903 |  |  | 0.03105 | 0.03105 | 0.15047 | 0.15047 |  |  | 0.00083485 | 0.00083485 |  |  | 0.00041591 | 0.00041591 | 0.00080683 | 0.00080683 |  |  | 0.00251 | 0.00251 |  |  | 0 | 0 | 0.0023421 | 0.0023421 | 590 | 169 | NO
2013-08-18 |  |  | 0.014216 | 0.014216 |  |  | 1.1789 | 1.1789 | 0.092087 | 0.092087 |  |  | 0.00015451 | 0.00015451 |  |  | 0.0017792 | 0.0017792 | 0.00026314 | 0.00026314 |  |  | 0.0068627 | 0.0068627 |  |  | 0 | 0 | 0.0064038 | 0.0064038 | 658 | 230 | NO
2013-08-19 |  |  | 0.01216 | 0.01216 |  |  | 0.015325 | 0.015325 | 0.012372 | 0.012372 |  |  | 0.00015724 | 0.00015724 |  |  | 0.00020796 | 0.00020796 | 0.00016063 | 0.00016063 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 510 | 31 | NO
2013-08-20 |  |  | 0.0033695 | 0.0033695 |  |  | 0.0029707 | 0.0029707 | 0.0033428 | 0.0033428 |  |  | 2.3179e-05 | 2.3179e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 2.3174e-05 | 2.3174e-05 |  |  | 0.0024884 | 0.0024884 |  |  | 0 | 0 | 0.0023221 | 0.0023221 | 475 | 55 | NO
2013-08-21 |  |  | 0.022225 | 0.022225 |  |  | 0 | 0 | 0.020739 | 0.020739 |  |  | 0.00021192 | 0.00021192 |  |  | 0 | 0 | 0.00019775 | 0.00019775 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 444 | 63 | NO
2013-08-22 |  |  | 0.089219 | 0.089219 |  |  | 0.0021947 | 0.0021947 | 0.083401 | 0.083401 |  |  | 0.00069339 | 0.00069339 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00064857 | 0.00064857 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 521 | 94 | NO
2013-08-23 |  |  | 0.040408 | 0.040408 |  |  | 0 | 0 | 0.037706 | 0.037706 |  |  | 0.00034603 | 0.00034603 |  |  | 0 | 0 | 0.00032289 | 0.00032289 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 465 | 83 | NO
2013-08-24 |  |  | 0.0084472 | 0.0084472 |  |  | 0 | 0 | 0.0078824 | 0.0078824 |  |  | 7.616e-05 | 7.616e-05 |  |  | 0 | 0 | 7.1068e-05 | 7.1068e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 254 | 58 | NO
2013-08-25 |  |  | 0.10721 | 0.10721 |  |  | 0.005934 | 0.005934 | 0.10044 | 0.10044 |  |  | 0.0024099 | 0.0024099 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0022503 | 0.0022503 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 348 | 120 | NO
2013-08-26 |  |  | 0.019055 | 0.019055 |  |  | 0.0030157 | 0.0030157 | 0.017983 | 0.017983 |  |  | 0.00014641 | 0.00014641 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00013816 | 0.00013816 |  |  | 0.001457 | 0.001457 |  |  | 0 | 0 | 0.0013596 | 0.0013596 | 508 | 100 | NO
2013-08-27 |  |  | 0.01091 | 0.01091 |  |  | 0 | 0 | 0.01018 | 0.01018 |  |  | 0.00024221 | 0.00024221 |  |  | 0 | 0 | 0.00022601 | 0.00022601 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 422 | 67 | NO
2013-08-28 |  |  | 0.011041 | 0.011041 |  |  | 0.0034197 | 0.0034197 | 0.010531 | 0.010531 |  |  | 0.00010821 | 0.00010821 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00010252 | 0.00010252 |  |  | 0.007419 | 0.007419 |  |  | 0 | 0 | 0.0069229 | 0.0069229 | 366 | 79 | NO
2013-08-29 |  |  | 0.0045036 | 0.0045036 |  |  | 0.23859 | 0.23859 | 0.020156 | 0.020156 |  |  | 3.7087e-05 | 3.7087e-05 |  |  | 0.040043 | 0.040043 | 0.002712 | 0.002712 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 379 | 54 | NO
2013-08-30 |  |  | 0.006317 | 0.006317 |  |  | 0 | 0 | 0.0058946 | 0.0058946 |  |  | 8.7087e-05 | 8.7087e-05 |  |  | 0 | 0 | 8.1264e-05 | 8.1264e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 499 | 106 | NO
2013-08-31 |  |  | 0.075563 | 0.075563 |  |  | 6.1345 | 6.1345 | 0.48068 | 0.48068 |  |  | 0.00048865 | 0.00048865 |  |  | 0.039356 | 0.039356 | 0.0030875 | 0.0030875 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 784 | 61 | NO
2013-09-01 |  |  | 0.037653 | 0.037653 |  |  | 0.033987 | 0.033987 | 0.037408 | 0.037408 |  |  | 0.00023179 | 0.00023179 |  |  | 0.00011553 | 0.00011553 | 0.00022402 | 0.00022402 |  |  | 0.0058196 | 0.0058196 |  |  | 0 | 0 | 0.0054305 | 0.0054305 | 221 | 39 | NO
2013-09-02 |  |  | 0.067021 | 0.067021 |  |  | 0.0082269 | 0.0082269 | 0.06309 | 0.06309 |  |  | 0.00098972 | 0.00098972 |  |  | 6.9318e-05 | 6.9318e-05 | 0.00092817 | 0.00092817 |  |  | 0.0030812 | 0.0030812 |  |  | 0 | 0 | 0.0028752 | 0.0028752 | 566 | 93 | NO
2013-09-03 |  |  | 0.016584 | 0.016584 |  |  | 0.017729 | 0.017729 | 0.01666 | 0.01666 |  |  | 0.00055276 | 0.00055276 |  |  | 0.00026734 | 0.00026734 | 0.00053367 | 0.00053367 |  |  | 0.0084819 | 0.0084819 |  |  | 0 | 0 | 0.0079148 | 0.0079148 | 466 | 81 | NO
2013-09-04 |  |  | 0.012034 | 0.012034 |  |  | 0 | 0 | 0.01123 | 0.01123 |  |  | 8.6889e-05 | 8.6889e-05 |  |  | 0 | 0 | 8.1079e-05 | 8.1079e-05 |  |  | 0.0025696 | 0.0025696 |  |  | 0.038495 | 0.038495 | 0.0049716 | 0.0049716 | 443 | 77 | NO
2013-09-05 |  |  | 0.0017891 | 0.0017891 |  |  | 2.2079 | 2.2079 | 0.1493 | 0.1493 |  |  | 1.8212e-05 | 1.8212e-05 |  |  | 0.0098201 | 0.0098201 | 0.0006736 | 0.0006736 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 734 | 99 | NO
2013-09-06 |  |  | 0.0041645 | 0.0041645 |  |  | 0.022686 | 0.022686 | 0.0054029 | 0.0054029 |  |  | 5.6292e-05 | 5.6292e-05 |  |  | 0.00016174 | 0.00016174 | 6.3343e-05 | 6.3343e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 458 | 53 | NO
2013-09-07 |  |  | 0.0097984 | 0.0097984 |  |  | 0.0021134 | 0.0021134 | 0.0092846 | 0.0092846 |  |  | 0.00012881 | 0.00012881 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00012174 | 0.00012174 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 327 | 97 | NO
2013-09-08 |  |  | 0.0094741 | 0.0094741 |  |  | 0.0016532 | 0.0016532 | 0.0089512 | 0.0089512 |  |  | 4.4703e-05 | 4.4703e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 4.3259e-05 | 4.3259e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 148 | 32 | NO
2013-09-09 |  |  | 8.7086 | 0.64229 |  |  | 1.2691 | 1.2691 | 8.2112 | 0.6842 |  |  | 0.34613 | 0.0098605 |  |  | 0.028605 | 0.028605 | 0.3249 | 0.011114 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 23134 | 18947 | Yes | MED
2013-09-10 |  |  | 0.0020658 | 0.0020658 |  |  | 0 | 0 | 0.0019277 | 0.0019277 |  |  | 1.8212e-05 | 1.8212e-05 |  |  | 0 | 0 | 1.6994e-05 | 1.6994e-05 |  |  | 0.009275 | 0.009275 |  |  | 0 | 0 | 0.0086548 | 0.0086548 | 514 | 101 | NO
2013-09-11 |  |  | 0.047038 | 0.047038 |  |  | 0.080977 | 0.080977 | 0.049308 | 0.049308 |  |  | 0.00045489 | 0.00045489 |  |  | 0.00032349 | 0.00032349 | 0.0004461 | 0.0004461 |  |  | 0.0033262 | 0.0033262 |  |  | 0.023199 | 0.023199 | 0.0046549 | 0.0046549 | 524 | 122 | NO
2013-09-12 |  |  | 0.34414 | 0.34414 |  |  | 0.099258 | 0.099258 | 0.32777 | 0.32777 |  |  | 0.008949 | 0.008949 |  |  | 0.0010513 | 0.0010513 | 0.0084209 | 0.0084209 |  |  | 0 | 0 |  |  | 0.0091038 | 0.0091038 | 0.00060871 | 0.00060871 | 1193 | 156 | NO
2013-09-13 |  |  | 0.23977 | 0.23977 |  |  | 0.074598 | 0.074598 | 0.22872 | 0.22872 |  |  | 0.0033405 | 0.0033405 |  |  | 0.00050834 | 0.00050834 | 0.0031511 | 0.0031511 |  |  | 0.0077931 | 0.0077931 |  |  | 0 | 0 | 0.0072721 | 0.0072721 | 451 | 76 | NO
2013-09-14 |  |  | 0.19949 | 0.19949 |  |  | 0.063971 | 0.063971 | 0.19043 | 0.19043 |  |  | 0.0075918 | 0.0075918 |  |  | 0.00057765 | 0.00057765 | 0.0071228 | 0.0071228 |  |  | 0.00011755 | 0.00011755 |  |  | 0.028351 | 0.028351 | 0.0020053 | 0.0020053 | 524 | 86 | NO
2013-09-15 |  |  | 0.021054 | 0.021054 |  |  | 0.014224 | 0.014224 | 0.020597 | 0.020597 |  |  | 0.00014239 | 0.00014239 |  |  | 0.00011553 | 0.00011553 | 0.00014059 | 0.00014059 |  |  | 0.013086 | 0.013086 |  |  | 0 | 0 | 0.012211 | 0.012211 | 158 | 10 | NO
2013-09-16 |  |  | 0.34765 | 0.34765 |  |  | 0.033531 | 0.033531 | 0.32665 | 0.32665 |  |  | 0.009818 | 0.009818 |  |  | 0.00011553 | 0.00011553 | 0.0091693 | 0.0091693 |  |  | 0.0052252 | 0.0052252 |  |  | 0.01183 | 0.01183 | 0.0056669 | 0.0056669 | 922 | 100 | NO
2013-09-17 |  |  | 0.0035404 | 0.0035404 |  |  | 0.0062052 | 0.0062052 | 0.0037186 | 0.0037186 |  |  | 2.9686e-05 | 2.9686e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 3.0791e-05 | 3.0791e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 481 | 81 | NO
2013-09-18 |  |  | 0.47502 | 0.47502 |  |  | 0 | 0 | 0.44326 | 0.44326 |  |  | 0.0016126 | 0.0016126 |  |  | 0 | 0 | 0.0015048 | 0.0015048 |  |  | 0.005116 | 0.005116 |  |  | 0 | 0 | 0.0047739 | 0.0047739 | 835 | 214 | NO
2013-09-19 |  |  | 1.1624 | 0.15104 |  |  | 6.8828 | 0.0015081 | 1.5449 | 0.14104 |  |  | 0.12978 | 0.00063536 |  |  | 0.78233 | 2.3106e-05 | 0.17341 | 0.00059442 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 2835 | 169 | NO
2013-09-20 |  |  | 0.016251 | 0.016251 |  |  | 0.053355 | 0.053355 | 0.018732 | 0.018732 |  |  | 7.823e-05 | 7.823e-05 |  |  | 0.00018393 | 0.00018393 | 8.5297e-05 | 8.5297e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 483 | 60 | NO
2013-09-21 |  |  | 0.061853 | 0.061853 |  |  | 0.68928 | 0.68928 | 0.10381 | 0.10381 |  |  | 0.00021866 | 0.00021866 |  |  | 0.0092194 | 0.0092194 | 0.00082048 | 0.00082048 |  |  | 0.001654 | 0.001654 |  |  | 0 | 0 | 0.0015434 | 0.0015434 | 254 | 52 | NO
2013-09-22 |  |  | 0.0010972 | 0.0010972 |  |  | 0 | 0 | 0.0010238 | 0.0010238 |  |  | 1.755e-05 | 1.755e-05 |  |  | 0 | 0 | 1.6376e-05 | 1.6376e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 128 | 8 | NO
2013-09-23 |  |  | 0.0081452 | 0.0081452 |  |  | 0.023857 | 0.023857 | 0.0091957 | 0.0091957 |  |  | 8.3544e-05 | 8.3544e-05 |  |  | 9.2425e-05 | 9.2425e-05 | 8.4138e-05 | 8.4138e-05 |  |  | 0.0024437 | 0.0024437 |  |  | 0 | 0 | 0.0022803 | 0.0022803 | 581 | 95 | NO
2013-09-24 |  |  | 0.015497 | 0.015497 |  |  | 0 | 0 | 0.014461 | 0.014461 |  |  | 0.00010845 | 0.00010845 |  |  | 0 | 0 | 0.00010119 | 0.00010119 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 489 | 112 | NO
2013-09-25 |  |  | 0.021802 | 0.021802 |  |  | 0.12146 | 0.12146 | 0.028465 | 0.028465 |  |  | 6.7484e-05 | 6.7484e-05 |  |  | 0.00078561 | 0.00078561 | 0.0001155 | 0.0001155 |  |  | 0.0042633 | 0.0042633 |  |  | 0.0098201 | 0.0098201 | 0.0046348 | 0.0046348 | 425 | 37 | NO
2013-09-26 |  |  | 2.3582 | 2.3582 |  |  | 3.2979 | 3.2979 | 2.421 | 2.421 |  |  | 0.032568 | 0.032568 |  |  | 0.017629 | 0.017629 | 0.031569 | 0.031569 |  |  | 0.027893 | 0.027893 |  |  | 0.039719 | 0.039719 | 0.028684 | 0.028684 | 3432 | 789 | NO
2013-09-27 |  |  | 0.27721 | 0.27721 |  |  | 0.054191 | 0.054191 | 0.2623 | 0.2623 |  |  | 0.0041012 | 0.0041012 |  |  | 0.00027496 | 0.00027496 | 0.0038454 | 0.0038454 |  |  | 0.012239 | 0.012239 |  |  | 0 | 0 | 0.01142 | 0.01142 | 1148 | 251 | NO
2013-09-28 |  |  | 0.23234 | 0.23234 |  |  | 0.11847 | 0.11847 | 0.22473 | 0.22473 |  |  | 0.00054792 | 0.00054792 |  |  | 0.00016174 | 0.00016174 | 0.0005221 | 0.0005221 |  |  | 0.0069902 | 0.0069902 |  |  | 0.020056 | 0.020056 | 0.0078638 | 0.0078638 | 505 | 197 | NO
2013-09-29 |  |  | 0.20078 | 0.20078 |  |  | 0 | 0 | 0.18735 | 0.18735 |  |  | 0.0095547 | 0.0095547 |  |  | 0 | 0 | 0.0089159 | 0.0089159 |  |  | 0.003154 | 0.003154 |  |  | 0 | 0 | 0.0029431 | 0.0029431 | 563 | 126 | NO
2013-09-30 |  |  | 0.63581 | 0.63581 |  |  | 3.069 | 3.069 | 0.7985 | 0.7985 |  |  | 0.0021387 | 0.0021387 |  |  | 0.066061 | 0.066061 | 0.0064127 | 0.0064127 |  |  | 0.0065216 | 0.0065216 |  |  | 0 | 0 | 0.0060856 | 0.0060856 | 802 | 135 | NO
2013-10-01 |  |  | 14.7231 | 0 |  |  | 33.1187 | 0 | 15.9531 | 0 |  |  | 0.088935 | 0 |  |  | 0.42046 | 0 | 0.1111 | 0 |  |  | 0.069311 | 0 |  |  | 0.092494 | 0 | 0.070861 | 0 | 10754 | 3251 | Yes | MED
2013-10-02 |  |  | 0.47795 | 0.47795 |  |  | 13.9181 | 13.9181 | 1.3766 | 1.3766 |  |  | 0.010722 | 0.010722 |  |  | 0.076135 | 0.076135 | 0.015095 | 0.015095 |  |  | 0.0034686 | 0.0034686 |  |  | 0.0039974 | 0.0039974 | 0.0035039 | 0.0035039 | 1881 | 588 | NO
2013-10-03 |  |  | 0.069513 | 0.069513 |  |  | 10.6837 | 10.6837 | 0.77921 | 0.77921 |  |  | 0.00073676 | 0.00073676 |  |  | 0.12695 | 0.12695 | 0.0091755 | 0.0091755 |  |  | 0.0074471 | 0.0074471 |  |  | 0 | 0 | 0.0069492 | 0.0069492 | 785 | 245 | NO
2013-10-04 |  |  | 0.00056609 | 0.00056609 |  |  | 0.015431 | 0.015431 | 0.00156 | 0.00156 |  |  | 6.6226e-06 | 6.6226e-06 |  |  | 9.9819e-05 | 9.9819e-05 | 1.2854e-05 | 1.2854e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 435 | 31 | NO
2013-10-05 |  |  | 0.012452 | 0.012452 |  |  | 0.047657 | 0.047657 | 0.014806 | 0.014806 |  |  | 0.00020278 | 0.00020278 |  |  | 0.0014326 | 0.0014326 | 0.00028501 | 0.00028501 |  |  | 0.0035034 | 0.0035034 |  |  | 0 | 0 | 0.0032691 | 0.0032691 | 264 | 50 | NO
2013-10-06 |  |  | 0.55476 | 0.55476 |  |  | 0.20637 | 0.20637 | 0.53147 | 0.53147 |  |  | 0.002774 | 0.002774 |  |  | 0.0003928 | 0.0003928 | 0.0026148 | 0.0026148 |  |  | 0.006707 | 0.006707 |  |  | 0 | 0 | 0.0062586 | 0.0062586 | 913 | 77 | NO
2013-10-07 |  |  | 0.018824 | 0.018824 |  |  | 0.0099938 | 0.0099938 | 0.018233 | 0.018233 |  |  | 0.00021532 | 0.00021532 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00020247 | 0.00020247 |  |  | 0 | 0 |  |  | 6.9318e-05 | 6.9318e-05 | 4.6348e-06 | 4.6348e-06 | 492 | 88 | NO
2013-10-08 |  |  | 0.012248 | 0.012248 |  |  | 0.017056 | 0.017056 | 0.01257 | 0.01257 |  |  | 0.00024742 | 0.00024742 |  |  | 9.2425e-05 | 9.2425e-05 | 0.00023706 | 0.00023706 |  |  | 0.0017616 | 0.0017616 |  |  | 0 | 0 | 0.0016438 | 0.0016438 | 413 | 30 | NO
2013-10-09 |  |  | 0.033553 | 0.033553 |  |  | 4.4 | 4.4 | 0.32551 | 0.32551 |  |  | 0.00016182 | 0.00016182 |  |  | 0.10272 | 0.10272 | 0.0070192 | 0.0070192 |  |  | 0.0046722 | 0.0046722 |  |  | 0 | 0 | 0.0043598 | 0.0043598 | 905 | 204 | NO
2013-10-10 |  |  | 0.01441 | 0.01441 |  |  | 0.0020699 | 0.0020699 | 0.013585 | 0.013585 |  |  | 0.0002649 | 0.0002649 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00024874 | 0.00024874 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 555 | 137 | NO
2013-10-11 |  |  | 0.0977 | 0.0977 |  |  | 0.0068699 | 0.0068699 | 0.091626 | 0.091626 |  |  | 0.0054338 | 0.0054338 |  |  | 9.1963e-05 | 9.1963e-05 | 0.0050767 | 0.0050767 |  |  | 0.0041491 | 0.0041491 |  |  | 0 | 0 | 0.0038716 | 0.0038716 | 447 | 65 | NO
2013-10-12 |  |  | 0.025881 | 0.025881 |  |  | 0 | 0 | 0.02415 | 0.02415 |  |  | 0.00030106 | 0.00030106 |  |  | 0 | 0 | 0.00028093 | 0.00028093 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 208 | 18 | NO
2013-10-13 |  |  | 0.37191 | 0.37191 |  |  | 0.015485 | 0.015485 | 0.34807 | 0.34807 |  |  | 0.0042191 | 0.0042191 |  |  | 0.00016174 | 0.00016174 | 0.0039478 | 0.0039478 |  |  | 0 | 0 |  |  | 0.0082951 | 0.0082951 | 0.00055464 | 0.00055464 | 377 | 154 | NO
2013-10-14 |  |  | 0.073815 | 0.073815 |  |  | 0.0077067 | 0.0077067 | 0.069394 | 0.069394 |  |  | 0.00041557 | 0.00041557 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00039087 | 0.00039087 |  |  | 0 | 0 |  |  | 0.078838 | 0.078838 | 0.0052714 | 0.0052714 | 465 | 73 | NO
2013-10-15 |  |  | 0.40161 | 0.40161 |  |  | 0.044947 | 0.044947 | 0.37776 | 0.37776 |  |  | 0.0056977 | 0.0056977 |  |  | 0.00049285 | 0.00049285 | 0.0053496 | 0.0053496 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 758 | 196 | NO
2013-10-16 |  |  | 0.16982 | 0.16982 |  |  | 0.010099 | 0.010099 | 0.15914 | 0.15914 |  |  | 0.0060299 | 0.0060299 |  |  | 9.2425e-05 | 9.2425e-05 | 0.0056329 | 0.0056329 |  |  | 0.002058 | 0.002058 |  |  | 0 | 0 | 0.0019204 | 0.0019204 | 626 | 44 | NO
2013-10-17 |  |  | 2.3722 | 2.3722 |  |  | 0.55017 | 0.55017 | 2.2504 | 2.2504 |  |  | 0.023616 | 0.023616 |  |  | 0.0032349 | 0.0032349 | 0.022253 | 0.022253 |  |  | 0.0047352 | 0.0047352 |  |  | 0.0082951 | 0.0082951 | 0.0049732 | 0.0049732 | 3426 | 777 | NO
2013-10-18 |  |  | 0.24675 | 0.24675 |  |  | 0.0025929 | 0.0025929 | 0.23042 | 0.23042 |  |  | 0.0056106 | 0.0056106 |  |  | 2.3106e-05 | 2.3106e-05 | 0.005237 | 0.005237 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1200 | 490 | NO
2013-10-19 |  |  | 0.0014888 | 0.0014888 |  |  | 0.0054842 | 0.0054842 | 0.001756 | 0.001756 |  |  | 9.9339e-06 | 9.9339e-06 |  |  | 2.3106e-05 | 2.3106e-05 | 1.0815e-05 | 1.0815e-05 |  |  | 0.0015795 | 0.0015795 |  |  | 0 | 0 | 0.0014739 | 0.0014739 | 241 | 72 | NO
2013-10-20 |  |  | 0.29062 | 0.29062 |  |  | 0.007441 | 0.007441 | 0.27168 | 0.27168 |  |  | 0.0036351 | 0.0036351 |  |  | 9.9125e-05 | 9.9125e-05 | 0.0033987 | 0.0033987 |  |  | 0.0026192 | 0.0026192 |  |  | 0 | 0 | 0.0024441 | 0.0024441 | 578 | 54 | NO
2013-10-21 |  |  | 0.032465 | 0.032465 |  |  | 0.29316 | 0.29316 | 0.049896 | 0.049896 |  |  | 0.00034603 | 0.00034603 |  |  | 0.0013633 | 0.0013633 | 0.00041405 | 0.00041405 |  |  | 0.010003 | 0.010003 |  |  | 0 | 0 | 0.0093346 | 0.0093346 | 545 | 93 | NO
2013-10-22 |  |  | 0.33798 | 0.33798 |  |  | 0 | 0 | 0.31538 | 0.31538 |  |  | 0.0034197 | 0.0034197 |  |  | 0 | 0 | 0.0031911 | 0.0031911 |  |  | 0.002712 | 0.002712 |  |  | 0 | 0 | 0.0025306 | 0.0025306 | 811 | 120 | NO
2013-10-23 |  |  | 0.058243 | 0.058243 |  |  | 0.0069268 | 0.0069268 | 0.054811 | 0.054811 |  |  | 0.00028341 | 0.00028341 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00026601 | 0.00026601 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 731 | 154 | NO
2013-10-24 |  |  | 0.89494 | 0.89494 |  |  | 0 | 0 | 0.8351 | 0.8351 |  |  | 0.0084092 | 0.0084092 |  |  | 0 | 0 | 0.0078469 | 0.0078469 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1247 | 128 | NO
2013-10-25 |  |  | 0.095621 | 0.095621 |  |  | 0.0016802 | 0.0016802 | 0.08934 | 0.08934 |  |  | 0.0052217 | 0.0052217 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0048741 | 0.0048741 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 594 | 108 | NO
2013-10-26 |  |  | 0.00078326 | 0.00078326 |  |  | 0.0033019 | 0.0033019 | 0.00095166 | 0.00095166 |  |  | 8.2451e-06 | 8.2451e-06 |  |  | 6.9318e-05 | 6.9318e-05 | 1.2329e-05 | 1.2329e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 224 | 64 | NO
2013-10-27 |  |  | 0.00072026 | 0.00072026 |  |  | 0 | 0 | 0.0006721 | 0.0006721 |  |  | 4.967e-06 | 4.967e-06 |  |  | 0 | 0 | 4.6348e-06 | 4.6348e-06 |  |  | 0.0015315 | 0.0015315 |  |  | 0 | 0 | 0.0014291 | 0.0014291 | 111 | 9 | NO
2013-10-28 |  |  | 0.014237 | 0.014237 |  |  | 0.039403 | 0.039403 | 0.01592 | 0.01592 |  |  | 0.00015851 | 0.00015851 |  |  | 4.6212e-05 | 4.6212e-05 | 0.000151 | 0.000151 |  |  | 0.0028212 | 0.0028212 |  |  | 0 | 0 | 0.0026326 | 0.0026326 | 547 | 65 | NO
2013-10-29 |  |  | 0.007553 | 0.007553 |  |  | 0.0066322 | 0.0066322 | 0.0074914 | 0.0074914 |  |  | 2.8875e-05 | 2.8875e-05 |  |  | 9.2425e-05 | 9.2425e-05 | 3.3124e-05 | 3.3124e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 486 | 113 | NO
2013-10-30 |  |  | 0.0053104 | 0.0053104 |  |  | 0 | 0 | 0.0049553 | 0.0049553 |  |  | 3.0133e-05 | 3.0133e-05 |  |  | 0 | 0 | 2.8118e-05 | 2.8118e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 445 | 71 | NO
2013-10-31 |  |  | 0.0031493 | 0.0031493 |  |  | 0.19114 | 0.19114 | 0.015719 | 0.015719 |  |  | 2.4123e-05 | 2.4123e-05 |  |  | 0.0013864 | 0.0013864 | 0.00011521 | 0.00011521 |  |  | 0.0051954 | 0.0051954 |  |  | 0 | 0 | 0.0048481 | 0.0048481 | 474 | 84 | NO
2013-11-01 |  |  | 0.037356 | 0.037356 |  |  | 0.60307 | 0.60307 | 0.075181 | 0.075181 |  |  | 0.00023651 | 0.00023651 |  |  | 0.0080409 | 0.0080409 | 0.00075834 | 0.00075834 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 482 | 70 | NO
2013-11-02 |  |  | 0.00065829 | 0.00065829 |  |  | 0.011924 | 0.011924 | 0.0014115 | 0.0014115 |  |  | 6.6226e-06 | 6.6226e-06 |  |  | 2.3106e-05 | 2.3106e-05 | 7.7247e-06 | 7.7247e-06 |  |  | 0.00061756 | 0.00061756 |  |  | 0.0073247 | 0.0073247 | 0.001066 | 0.001066 | 223 | 40 | NO
2013-11-03 |  |  | 0.013869 | 0.013869 |  |  | 0.013156 | 0.013156 | 0.013822 | 0.013822 |  |  | 0.00019355 | 0.00019355 |  |  | 3.0731e-05 | 3.0731e-05 | 0.00018266 | 0.00018266 |  |  | 0.0093611 | 0.0093611 |  |  | 0 | 0 | 0.0087351 | 0.0087351 | 256 | 33 | NO
2013-11-04 |  |  | 0.52341 | 0.52341 |  |  | 0.15066 | 0.15066 | 0.49849 | 0.49849 |  |  | 0.01073 | 0.01073 |  |  | 0.00046212 | 0.00046212 | 0.010043 | 0.010043 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1232 | 202 | NO
2013-11-05 |  |  | 0.042713 | 0.042713 |  |  | 0 | 0 | 0.039857 | 0.039857 |  |  | 0.00015894 | 0.00015894 |  |  | 0 | 0 | 0.00014832 | 0.00014832 |  |  | 0.0017302 | 0.0017302 |  |  | 0 | 0 | 0.0016145 | 0.0016145 | 177 | 23 | NO
2013-11-06 |  |  | 0.095198 | 0.095198 |  |  | 0.013598 | 0.013598 | 0.089742 | 0.089742 |  |  | 0.00046012 | 0.00046012 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00043245 | 0.00043245 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 577 | 143 | NO
2013-11-07 |  |  | 0.0023679 | 0.0023679 |  |  | 0.0042292 | 0.0042292 | 0.0024923 | 0.0024923 |  |  | 1.4901e-05 | 1.4901e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 1.5449e-05 | 1.5449e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 537 | 86 | NO
2013-11-08 |  |  | 0.10334 | 0.10334 |  |  | 1.3361 | 1.3361 | 0.18577 | 0.18577 |  |  | 0.0012239 | 0.0012239 |  |  | 0.038541 | 0.038541 | 0.003719 | 0.003719 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 670 | 76 | NO
2013-11-09 |  |  | 0.096844 | 0.096844 |  |  | 0.0016744 | 0.0016744 | 0.09048 | 0.09048 |  |  | 0.00043477 | 0.00043477 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00040725 | 0.00040725 |  |  | 0.0031242 | 0.0031242 |  |  | 0.067031 | 0.067031 | 0.0073972 | 0.0073972 | 274 | 65 | NO
2013-11-10 |  |  | 0.0011037 | 0.0011037 |  |  | 0 | 0 | 0.0010299 | 0.0010299 |  |  | 8.2783e-06 | 8.2783e-06 |  |  | 0 | 0 | 7.7247e-06 | 7.7247e-06 |  |  | 0.0024934 | 0.0024934 |  |  | 0 | 0 | 0.0023267 | 0.0023267 | 151 | 17 | NO
2013-11-11 |  |  | 0.016135 | 0.016135 |  |  | 0.12941 | 0.12941 | 0.023709 | 0.023709 |  |  | 0.00012749 | 0.00012749 |  |  | 0.0008004 | 0.0008004 | 0.00017248 | 0.00017248 |  |  | 0.0058577 | 0.0058577 |  |  | 0 | 0 | 0.005466 | 0.005466 | 843 | 275 | NO
2013-11-12 |  |  | 0.037216 | 0.037216 |  |  | 0.027757 | 0.027757 | 0.036583 | 0.036583 |  |  | 0.00011699 | 0.00011699 |  |  | 0.00018485 | 0.00018485 | 0.00012153 | 0.00012153 |  |  | 0.0023808 | 0.0023808 |  |  | 0 | 0 | 0.0022216 | 0.0022216 | 607 | 65 | NO
2013-11-13 |  |  | 0.73768 | 0.73768 |  |  | 0.015932 | 0.015932 | 0.68942 | 0.68942 |  |  | 0.0076155 | 0.0076155 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0071094 | 0.0071094 |  |  | 0.0061656 | 0.0061656 |  |  | 0 | 0 | 0.0057534 | 0.0057534 | 1238 | 394 | NO
2013-11-14 |  |  | 0.039768 | 0.039768 |  |  | 4.1624 | 4.1624 | 0.31542 | 0.31542 |  |  | 9.5945e-05 | 9.5945e-05 |  |  | 0.05051 | 0.05051 | 0.0034668 | 0.0034668 |  |  | 0.0047401 | 0.0047401 |  |  | 0 | 0 | 0.0044232 | 0.0044232 | 878 | 98 | NO
2013-11-15 |  |  | 0.027712 | 0.027712 |  |  | 0.097648 | 0.097648 | 0.032388 | 0.032388 |  |  | 0.00017065 | 0.00017065 |  |  | 0.0012708 | 0.0012708 | 0.00024421 | 0.00024421 |  |  | 4.1391e-05 | 4.1391e-05 |  |  | 0.038518 | 0.038518 | 0.0026141 | 0.0026141 | 583 | 135 | NO
2013-11-16 |  |  | 0.029601 | 0.029601 |  |  | 0.012391 | 0.012391 | 0.028451 | 0.028451 |  |  | 0.00028865 | 0.00028865 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00027244 | 0.00027244 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 228 | 28 | NO
2013-11-17 |  |  | 0.0012613 | 0.0012613 |  |  | 0.019508 | 0.019508 | 0.0024813 | 0.0024813 |  |  | 1.159e-05 | 1.159e-05 |  |  | 9.2425e-05 | 9.2425e-05 | 1.6994e-05 | 1.6994e-05 |  |  | 0.00451 | 0.00451 |  |  | 0 | 0 | 0.0042084 | 0.0042084 | 107 | 5 | NO
2013-11-18 |  |  | 0.30582 | 0.30582 |  |  | 0 | 0 | 0.28538 | 0.28538 |  |  | 0.0083337 | 0.0083337 |  |  | 0 | 0 | 0.0077765 | 0.0077765 |  |  | 0.0023941 | 0.0023941 |  |  | 0.020056 | 0.020056 | 0.003575 | 0.003575 | 1116 | 126 | NO
2013-11-19 |  |  | 0.050014 | 0.050014 |  |  | 0.0061971 | 0.0061971 | 0.047084 | 0.047084 |  |  | 0.00021696 | 0.00021696 |  |  | 0.00011553 | 0.00011553 | 0.00021017 | 0.00021017 |  |  | 0.0001308 | 0.0001308 |  |  | 0 | 0 | 0.00012205 | 0.00012205 | 647 | 172 | NO
2013-11-20 |  |  | 0.013115 | 0.013115 |  |  | 0 | 0 | 0.012239 | 0.012239 |  |  | 0.00014315 | 0.00014315 |  |  | 0 | 0 | 0.00013358 | 0.00013358 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 561 | 106 | NO
2013-11-21 |  |  | 0.34423 | 0.34423 |  |  | 0 | 0 | 0.32121 | 0.32121 |  |  | 0.0093726 | 0.0093726 |  |  | 0 | 0 | 0.008746 | 0.008746 |  |  | 0.0067849 | 0.0067849 |  |  | 0 | 0 | 0.0063312 | 0.0063312 | 575 | 68 | NO
2013-11-22 |  |  | 0.1872 | 0.1872 |  |  | 0.02771 | 0.02771 | 0.17654 | 0.17654 |  |  | 0.00078804 | 0.00078804 |  |  | 0.00011553 | 0.00011553 | 0.00074307 | 0.00074307 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 773 | 215 | NO
2013-11-23 |  |  | 0.0075827 | 0.0075827 |  |  | 0.0023865 | 0.0023865 | 0.0072353 | 0.0072353 |  |  | 4.0448e-05 | 4.0448e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 3.9288e-05 | 3.9288e-05 |  |  | 0.0041093 | 0.0041093 |  |  | 0.019247 | 0.019247 | 0.0051215 | 0.0051215 | 275 | 52 | NO
2013-11-24 |  |  | 0.0081449 | 0.0081449 |  |  | 0 | 0 | 0.0076003 | 0.0076003 |  |  | 8.5796e-05 | 8.5796e-05 |  |  | 0 | 0 | 8.0059e-05 | 8.0059e-05 |  |  | 0.0076756 | 0.0076756 |  |  | 0 | 0 | 0.0071624 | 0.0071624 | 157 | 7 | NO
2013-11-25 |  |  | 0.14818 | 0.14818 |  |  | 0.0048219 | 0.0048219 | 0.1386 | 0.1386 |  |  | 0.0019558 | 0.0019558 |  |  | 6.1925e-05 | 6.1925e-05 | 0.0018291 | 0.0018291 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 805 | 202 | NO
2013-11-26 |  |  | 0.015705 | 0.015705 |  |  | 0.015488 | 0.015488 | 0.01569 | 0.01569 |  |  | 8.4802e-05 | 8.4802e-05 |  |  | 0.00016867 | 0.00016867 | 9.041e-05 | 9.041e-05 |  |  | 0.00012417 | 0.00012417 |  |  | 0 | 0 | 0.00011587 | 0.00011587 | 671 | 157 | NO
2013-11-27 |  |  | 0.038056 | 0.038056 |  |  | 0.0052135 | 0.0052135 | 0.03586 | 0.03586 |  |  | 0.00061994 | 0.00061994 |  |  | 0.00011553 | 0.00011553 | 0.00058622 | 0.00058622 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 646 | 80 | NO
2013-11-28 |  |  | 0.50906 | 0.50906 |  |  | 0.001111 | 0.001111 | 0.47509 | 0.47509 |  |  | 0.0041189 | 0.0041189 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0038451 | 0.0038451 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 983 | 256 | NO
2013-11-29 |  |  | 0.34332 | 0.34332 |  |  | 1.6549 | 1.6549 | 0.43102 | 0.43102 |  |  | 0.0040878 | 0.0040878 |  |  | 0.02031 | 0.02031 | 0.0051725 | 0.0051725 |  |  | 0.0049769 | 0.0049769 |  |  | 0 | 0 | 0.0046441 | 0.0046441 | 1108 | 172 | NO
2013-11-30 |  |  | 0.062747 | 0.062747 |  |  | 0.018095 | 0.018095 | 0.059762 | 0.059762 |  |  | 0.00016391 | 0.00016391 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00015604 | 0.00015604 |  |  | 0.0023113 | 0.0023113 |  |  | 0 | 0 | 0.0021567 | 0.0021567 | 315 | 72 | NO
2013-12-01 |  |  | 0.0021327 | 0.0021327 |  |  | 0.0043517 | 0.0043517 | 0.0022811 | 0.0022811 |  |  | 2.9553e-05 | 2.9553e-05 |  |  | 4.6212e-05 | 4.6212e-05 | 3.0667e-05 | 3.0667e-05 |  |  | 0.0041656 | 0.0041656 |  |  | 0 | 0 | 0.0038871 | 0.0038871 | 110 | 12 | NO
2013-12-02 |  |  | 0.012833 | 0.012833 |  |  | 0.0014665 | 0.0014665 | 0.012073 | 0.012073 |  |  | 0.0001227 | 0.0001227 |  |  | 2.3106e-05 | 2.3106e-05 | 0.00011604 | 0.00011604 |  |  | 6.2915e-05 | 6.2915e-05 |  |  | 0 | 0 | 5.8708e-05 | 5.8708e-05 | 607 | 91 | NO
2013-12-03 |  |  | 0.030755 | 0.030755 |  |  | 0.0021104 | 0.0021104 | 0.028839 | 0.028839 |  |  | 0.0018144 | 0.0018144 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0016946 | 0.0016946 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 591 | 71 | NO
2013-12-04 |  |  | 0.089789 | 0.089789 |  |  | 0.0053876 | 0.0053876 | 0.084146 | 0.084146 |  |  | 0.00023475 | 0.00023475 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00022215 | 0.00022215 |  |  | 0 | 0 |  |  | 0.077059 | 0.077059 | 0.0051524 | 0.0051524 | 821 | 288 | NO
2013-12-05 |  |  | 0.15134 | 0.15134 |  |  | 0.029487 | 0.029487 | 0.14319 | 0.14319 |  |  | 0.019074 | 0.019074 |  |  | 0.00030038 | 0.00030038 | 0.017819 | 0.017819 |  |  | 0.0014205 | 0.0014205 |  |  | 0 | 0 | 0.0013256 | 0.0013256 | 827 | 189 | NO
2013-12-06 |  |  | 0.089655 | 0.089655 |  |  | 0 | 0 | 0.08366 | 0.08366 |  |  | 0.013459 | 0.013459 |  |  | 0 | 0 | 0.012559 | 0.012559 |  |  | 0.0041126 | 0.0041126 |  |  | 0 | 0 | 0.0038377 | 0.0038377 | 562 | 174 | NO
2013-12-07 |  |  | 0.48355 | 0.023933 |  |  | 0.35935 | 0 | 0.47525 | 0.022333 |  |  | 0.040966 | 0.00028312 |  |  | 0.031808 | 0 | 0.040354 | 0.00026419 |  |  | 0.0017302 | 0.0017302 |  |  | 0 | 0 | 0.0016145 | 0.0016145 | 832 | 162 | NO
2013-12-08 |  |  | 0.14555 | 0.14555 |  |  | 0.40395 | 0.40395 | 0.16283 | 0.16283 |  |  | 0.0019404 | 0.0019404 |  |  | 0.004344 | 0.004344 | 0.0021011 | 0.0021011 |  |  | 0.0029305 | 0.0029305 |  |  | 0.15398 | 0.15398 | 0.01303 | 0.01303 | 235 | 64 | NO
2013-12-09 |  |  | 0.037312 | 0.037312 |  |  | 7.4656 | 7.4656 | 0.53399 | 0.53399 |  |  | 0.00015601 | 0.00015601 |  |  | 0.044202 | 0.044202 | 0.0031011 | 0.0031011 |  |  | 0 | 0 |  |  | 0.090206 | 0.090206 | 0.0060315 | 0.0060315 | 772 | 138 | NO
2013-12-10 |  |  | 0.096377 | 0.096377 |  |  | 3.2715 | 3.2715 | 0.30867 | 0.30867 |  |  | 0.0018595 | 0.0018595 |  |  | 0.022321 | 0.022321 | 0.0032276 | 0.0032276 |  |  | 0.0011639 | 0.0011639 |  |  | 0.078884 | 0.078884 | 0.0063606 | 0.0063606 | 864 | 223 | NO
2013-12-11 |  |  | 0.069595 | 0.069595 |  |  | 0.71691 | 0.71691 | 0.11288 | 0.11288 |  |  | 0.00057585 | 0.00057585 |  |  | 0.001964 | 0.001964 | 0.00066867 | 0.00066867 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 609 | 65 | NO
2013-12-12 |  |  | 0.026687 | 0.026687 |  |  | 0.48979 | 0.48979 | 0.057651 | 0.057651 |  |  | 5.7103e-05 | 5.7103e-05 |  |  | 0.039165 | 0.039165 | 0.002672 | 0.002672 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 544 | 101 | NO
2013-12-13 |  |  | 0.0034616 | 0.0034616 |  |  | 0.0035098 | 0.0035098 | 0.0034648 | 0.0034648 |  |  | 3.914e-05 | 3.914e-05 |  |  | 2.3106e-05 | 2.3106e-05 | 3.8068e-05 | 3.8068e-05 |  |  | 0.0019189 | 0.0019189 |  |  | 0 | 0 | 0.0017906 | 0.0017906 | 453 | 93 | NO
2013-12-14 |  |  | 0.0016367 | 0.0016367 |  |  | 0.03457 | 0.03457 | 0.0038388 | 0.0038388 |  |  | 1.3245e-05 | 1.3245e-05 |  |  | 0.011022 | 0.011022 | 0.0007493 | 0.0007493 |  |  | 0.0039007 | 0.0039007 |  |  | 0 | 0 | 0.0036399 | 0.0036399 | 290 | 78 | NO
2013-12-15 |  |  | 0.011973 | 0.011973 |  |  | 0.011559 | 0.011559 | 0.011945 | 0.011945 |  |  | 0.00011643 | 0.00011643 |  |  | 0.00020796 | 0.00020796 | 0.00012255 | 0.00012255 |  |  | 0.0010613 | 0.0010613 |  |  | 0 | 0 | 0.00099031 | 0.00099031 | 182 | 33 | NO
2013-12-16 |  |  | 0.0073322 | 0.0073322 |  |  | 0.028956 | 0.028956 | 0.008778 | 0.008778 |  |  | 9.4902e-05 | 9.4902e-05 |  |  | 0.0003734 | 0.0003734 | 0.00011352 | 0.00011352 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 483 | 113 | NO
2013-12-17 |  |  | 0.0011197 | 0.0011197 |  |  | 0 | 0 | 0.0010448 | 0.0010448 |  |  | 1.159e-05 | 1.159e-05 |  |  | 0 | 0 | 1.0815e-05 | 1.0815e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 387 | 40 | NO
2013-12-18 |  |  | 0.055134 | 0.055134 |  |  | 0.010011 | 0.010011 | 0.052117 | 0.052117 |  |  | 0.00030552 | 0.00030552 |  |  | 6.9318e-05 | 6.9318e-05 | 0.00028972 | 0.00028972 |  |  | 0.0016888 | 0.0016888 |  |  | 0 | 0 | 0.0015758 | 0.0015758 | 484 | 84 | NO
2013-12-19 |  |  | 0.26432 | 0.26432 |  |  | 0.0043825 | 0.0043825 | 0.24694 | 0.24694 |  |  | 0.005299 | 0.005299 |  |  | 4.6212e-05 | 4.6212e-05 | 0.0049478 | 0.0049478 |  |  | 0.003909 | 0.003909 |  |  | 0 | 0 | 0.0036476 | 0.0036476 | 898 | 127 | NO
2013-12-20 |  |  | 0.028016 | 0.028016 |  |  | 0.0062864 | 0.0062864 | 0.026563 | 0.026563 |  |  | 0.00021934 | 0.00021934 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00020776 | 0.00020776 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 524 | 64 | NO
2013-12-21 |  |  | 0.0036499 | 0.0036499 |  |  | 0.002702 | 0.002702 | 0.0035865 | 0.0035865 |  |  | 5.2567e-05 | 5.2567e-05 |  |  | 3.0962e-05 | 3.0962e-05 | 5.1122e-05 | 5.1122e-05 |  |  | 0 | 0 |  |  | 0.039604 | 0.039604 | 0.002648 | 0.002648 | 230 | 29 | NO
2013-12-22 |  |  | 0.016476 | 0.016476 |  |  | 6.4462 | 6.4462 | 0.44639 | 0.44639 |  |  | 0.00015407 | 0.00015407 |  |  | 0.091292 | 0.091292 | 0.0062479 | 0.0062479 |  |  | 0.0018908 | 0.0018908 |  |  | 0 | 0 | 0.0017643 | 0.0017643 | 223 | 26 | NO
2013-12-23 |  |  | 0.028923 | 0.028923 |  |  | 0.011359 | 0.011359 | 0.027749 | 0.027749 |  |  | 0.00028881 | 0.00028881 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00027259 | 0.00027259 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 453 | 47 | NO
2013-12-24 |  |  | 0.00043905 | 0.00043905 |  |  | 0.26558 | 0.26558 | 0.018167 | 0.018167 |  |  | 4.967e-06 | 4.967e-06 |  |  | 0.001647 | 0.001647 | 0.00011476 | 0.00011476 |  |  | 0.00058113 | 0.00058113 |  |  | 0 | 0 | 0.00054228 | 0.00054228 | 246 | 43 | NO
2013-12-25 |  |  | 0.0087485 | 0.0087485 |  |  | 0 | 0 | 0.0081636 | 0.0081636 |  |  | 8.6574e-05 | 8.6574e-05 |  |  | 0 | 0 | 8.0785e-05 | 8.0785e-05 |  |  | 0.0073478 | 0.0073478 |  |  | 0 | 0 | 0.0068565 | 0.0068565 | 123 | 12 | NO
2013-12-26 |  |  | 0.045493 | 0.045493 |  |  | 0.00548 | 0.00548 | 0.042818 | 0.042818 |  |  | 0.00016888 | 0.00016888 |  |  | 4.6212e-05 | 4.6212e-05 | 0.00016067 | 0.00016067 |  |  | 0.0033891 | 0.0033891 |  |  | 0 | 0 | 0.0031625 | 0.0031625 | 121 | 2 | NO
2013-12-27 |  |  | 0.0092045 | 0.0092045 |  |  | 0.0027477 | 0.0027477 | 0.0087727 | 0.0087727 |  |  | 0.00032798 | 0.00032798 |  |  | 2.3106e-05 | 2.3106e-05 | 0.0003076 | 0.0003076 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 269 | 11 | NO
2013-12-28 |  |  | 1.1722 | 1.1722 |  |  | 0.34619 | 0.34619 | 1.1169 | 1.1169 |  |  | 0.013733 | 0.013733 |  |  | 0.0010167 | 0.0010167 | 0.012883 | 0.012883 |  |  | 0.0071094 | 0.0071094 |  |  | 0 | 0 | 0.006634 | 0.006634 | 1418 | 137 | NO
2013-12-29 |  |  | 0.044487 | 0.044487 |  |  | 0.060247 | 0.060247 | 0.045541 | 0.045541 |  |  | 0.00010932 | 0.00010932 |  |  | 0.00032349 | 0.00032349 | 0.00012364 | 0.00012364 |  |  | 0 | 0 |  |  | 0.039627 | 0.039627 | 0.0026496 | 0.0026496 | 163 | 22 | NO
2013-12-30 |  |  | 0.0021959 | 0.0021959 |  |  | 0 | 0 | 0.0020491 | 0.0020491 |  |  | 1.1391e-05 | 1.1391e-05 |  |  | 0 | 0 | 1.0629e-05 | 1.0629e-05 |  |  | 0.0027103 | 0.0027103 |  |  | 0 | 0 | 0.0025291 | 0.0025291 | 341 | 29 | NO
2013-12-31 |  |  | 0.0011748 | 0.0011748 |  |  | 0.0045357 | 0.0045357 | 0.0013995 | 0.0013995 |  |  | 9.9339e-06 | 9.9339e-06 |  |  | 4.6212e-05 | 4.6212e-05 | 1.236e-05 | 1.236e-05 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 257 | 9 | NO
Contents
Contents

## 1d. STPIS MED Threshold
United Energy Distribution Pty Limited
STPIS Data Reporting
2013
MED Threshold
Table 1 MED Threshold
MED Threshold (Timed) year ending 31 December | 4.961
Alpha - average of Ln(SAIDI) | -3.0912
Beta - Standard deviation of Ln(SAIDI) | 1.8771
X Beta from the mean | 2.5
Table 2 MED Calculation
Date | Network SAIDI All Events | Network SAIDI (after removing excluded events) | Ln (SAIDI)
2008-01-01 | 0.33982 | 0.33982 | -1.0793
2008-01-02 | 0.025608 | 0.025608 | -3.6649
2008-01-03 | 0.31847 | 0.31847 | -1.1442
2008-01-04 | 0.045205 | 0.045205 | -3.0965
2008-01-05 | 0.28295 | 0.28295 | -1.2625
2008-01-06 | 0.034792 | 0.034792 | -3.3584
2008-01-07 | 0.0066921 | 0.0066921 | -5.0068
2008-01-08 | 0.0025627 | 0.0025627 | -5.9667
2008-01-09 | 0.0020571 | 0.0020571 | -6.1865
2008-01-10 | 0.49856 | 0.49856 | -0.69604
2008-01-11 | 0.20041 | 0.20041 | -1.6074
2008-01-12 | 0.071726 | 0.071726 | -2.6349
2008-01-13 | 0.28562 | 0.28562 | -1.2531
2008-01-14 | 0.55565 | 0.55565 | -0.58762
2008-01-15 | 0.42628 | 0.42628 | -0.85266
2008-01-16 | 0.3567 | 0.3567 | -1.0309
2008-01-17 | 0.62971 | 0.62971 | -0.4625
2008-01-18 | 0.74993 | 0.74993 | -0.28778
2008-01-19 | 1.1154 | 1.1154 | 0.10924
2008-01-20 | 1.0303 | 1.0303 | 0.029815
2008-01-21 | 0.023473 | 0.023473 | -3.7519
2008-01-22 | 0.016733 | 0.016733 | -4.0904
2008-01-23 | 0.23723 | 0.23723 | -1.4387
2008-01-24 | 0.006959 | 0.006959 | -4.9677
2008-01-25 | 0.049395 | 0.049395 | -3.0079
2008-01-26 | 1.2813 | 1.2813 | 0.24786
2008-01-27 | 0.029123 | 0.029123 | -3.5362
2008-01-28 | 0.021761 | 0.021761 | -3.8276
2008-01-29 | 0.011371 | 0.011371 | -4.4767
2008-01-30 | 0.10012 | 0.10012 | -2.3014
2008-01-31 | 0.019803 | 0.019803 | -3.9219
2008-02-01 | 0.0059141 | 0.0059141 | -5.1304
2008-02-02 | 0.0041975 | 0.0041975 | -5.4733
2008-02-03 | 0.12372 | 0.12372 | -2.0898
2008-02-04 | 0.021935 | 0.021935 | -3.8197
2008-02-05 | 0.27862 | 0.27862 | -1.2779
2008-02-06 | 0.020233 | 0.020233 | -3.9004
2008-02-07 | 0.032015 | 0.032015 | -3.4415
2008-02-08 | 0.0064948 | 0.0064948 | -5.0368
2008-02-09 | 0.000941 | 0.000941 | -6.9686
2008-02-10 | 0.24536 | 0.24536 | -1.405
2008-02-11 | 0.011119 | 0.011119 | -4.4991
2008-02-12 | 0.24794 | 0.24794 | -1.3946
2008-02-13 | 0.039594 | 0.039594 | -3.2291
2008-02-14 | 0.020824 | 0.020824 | -3.8716
2008-02-15 | 0.0024843 | 0.0024843 | -5.9978
2008-02-16 | 0.0042219 | 0.0042219 | -5.4675
2008-02-17 | 0.095005 | 0.095005 | -2.3538
2008-02-18 | 0.043909 | 0.043909 | -3.1256
2008-02-19 | 0.26672 | 0.26672 | -1.3216
2008-02-20 | 4.4348 | 4.4348 | 1.4895
2008-02-21 | 0.041138 | 0.041138 | -3.1908
2008-02-22 | 0.075313 | 0.075313 | -2.5861
2008-02-23 | 0.022656 | 0.022656 | -3.7873
2008-02-24 | 0.1827 | 0.1827 | -1.6999
2008-02-25 | 0.0086013 | 0.0086013 | -4.7558
2008-02-26 | 0.014112 | 0.014112 | -4.2608
2008-02-27 | 0.0038016 | 0.0038016 | -5.5723
2008-02-28 | 0.32983 | 0.32983 | -1.1092
2008-02-29 | 0.013664 | 0.013664 | -4.293
2008-03-01 | 0.72484 | 0.72484 | -0.32181
2008-03-02 | 0.07328 | 0.07328 | -2.6135
2008-03-03 | 0.0081734 | 0.0081734 | -4.8069
2008-03-04 | 0.21688 | 0.21688 | -1.5284
2008-03-05 | 0.018487 | 0.018487 | -3.9907
2008-03-06 | 0.10858 | 0.10858 | -2.2203
2008-03-07 | 0.32745 | 0.32745 | -1.1164
2008-03-08 | 0.0013475 | 0.0013475 | -6.6095
2008-03-09 | 0.00098592 | 0.00098592 | -6.9219
2008-03-10 | 0.14129 | 0.14129 | -1.9569
2008-03-11 | 0.017059 | 0.017059 | -4.0711
2008-03-12 | 0.089821 | 0.089821 | -2.4099
2008-03-13 | 0.34634 | 0.34634 | -1.0603
2008-03-14 | 0.78206 | 0.78206 | -0.24582
2008-03-15 | 0.1755 | 0.1755 | -1.7401
2008-03-16 | 0.20718 | 0.20718 | -1.5741
2008-03-17 | 0.86703 | 0.86703 | -0.14268
2008-03-18 | 0.015825 | 0.015825 | -4.1462
2008-03-19 | 0.09403 | 0.09403 | -2.3641
2008-03-20 | 0.016258 | 0.016258 | -4.1192
2008-03-21 | 0.033262 | 0.033262 | -3.4033
2008-03-22 | 0.0042118 | 0.0042118 | -5.4699
2008-03-23 | 0.038237 | 0.038237 | -3.2639
2008-03-24 | 0.091541 | 0.091541 | -2.391
2008-03-25 | 0.2586 | 0.2586 | -1.3525
2008-03-26 | 0.013435 | 0.013435 | -4.3099
2008-03-27 | 0.12585 | 0.12585 | -2.0726
2008-03-28 | 0.038051 | 0.038051 | -3.2688
2008-03-29 | 0.0074527 | 0.0074527 | -4.8992
2008-03-30 | 0.48168 | 0.48168 | -0.73047
2008-03-31 | 0.027209 | 0.027209 | -3.6042
2008-04-01 | 0.003397 | 0.003397 | -5.6849
2008-04-02 | 232.2816 | 0 | 5.448
2008-04-03 | 6.5557 | 6.5557 | 1.8803
2008-04-04 | 0.30451 | 0.30451 | -1.1891
2008-04-05 | 0.094295 | 0.094295 | -2.3613
2008-04-06 | 0.50672 | 0.50672 | -0.6798
2008-04-07 | 0.31858 | 0.31858 | -1.1439
2008-04-08 | 0.0089616 | 0.0089616 | -4.7148
2008-04-09 | 0.011438 | 0.011438 | -4.4708
2008-04-10 | 0.50593 | 0.50593 | -0.68135
2008-04-11 | 0.45981 | 0.45981 | -0.77695
2008-04-12 | 0.22373 | 0.22373 | -1.4973
2008-04-13 | 0.32174 | 0.32174 | -1.134
2008-04-14 | 0.15358 | 0.15358 | -1.8735
2008-04-15 | 0.016952 | 0.016952 | -4.0774
2008-04-16 | 0.025995 | 0.025995 | -3.6498
2008-04-17 | 0.0044696 | 0.0044696 | -5.4105
2008-04-18 | 0.028401 | 0.028401 | -3.5613
2008-04-19 | 0.0042971 | 0.0042971 | -5.4498
2008-04-20 | 0.26829 | 0.26829 | -1.3157
2008-04-21 | 0.23134 | 0.23134 | -1.4639
2008-04-22 | 0.0088345 | 0.0088345 | -4.7291
2008-04-23 | 0.0047531 | 0.0047531 | -5.349
2008-04-24 | 0.28091 | 0.28091 | -1.2697
2008-04-25 | 0.010135 | 0.010135 | -4.5918
2008-04-26 | 0.58455 | 0.58455 | -0.53692
2008-04-27 | 0.0050712 | 0.0050712 | -5.2842
2008-04-28 | 0.084454 | 0.084454 | -2.4715
2008-04-29 | 0.27936 | 0.27936 | -1.2753
2008-04-30 | 0.013821 | 0.013821 | -4.2816
2008-05-01 | 0.0040407 | 0.0040407 | -5.5113
2008-05-02 | 0.2114 | 0.2114 | -1.554
2008-05-03 | 0.019964 | 0.019964 | -3.9138
2008-05-04 | 0.00090556 | 0.00090556 | -7.007
2008-05-05 | 0.0075285 | 0.0075285 | -4.8891
2008-05-06 | 0.8751 | 0.8751 | -0.13342
2008-05-07 | 0.097776 | 0.097776 | -2.3251
2008-05-08 | 0.036184 | 0.036184 | -3.3191
2008-05-09 | 0.017774 | 0.017774 | -4.03
2008-05-10 | 0.001762 | 0.001762 | -6.3413
2008-05-11 | 0.014811 | 0.014811 | -4.2124
2008-05-12 | 0.0031319 | 0.0031319 | -5.7661
2008-05-13 | 0.0024115 | 0.0024115 | -6.0275
2008-05-14 | 0.0080345 | 0.0080345 | -4.824
2008-05-15 | 0.28578 | 0.28578 | -1.2525
2008-05-16 | 0.2361 | 0.2361 | -1.4435
2008-05-17 | 0.44845 | 0.44845 | -0.80197
2008-05-18 | 0.18963 | 0.18963 | -1.6627
2008-05-19 | 0.36724 | 0.36724 | -1.0017
2008-05-20 | 0.0033757 | 0.0033757 | -5.6912
2008-05-21 | 0.10083 | 0.10083 | -2.2943
2008-05-22 | 0.0088062 | 0.0088062 | -4.7323
2008-05-23 | 0.044545 | 0.044545 | -3.1113
2008-05-24 | 0.029349 | 0.029349 | -3.5285
2008-05-25 | 0.011843 | 0.011843 | -4.436
2008-05-26 | 0.002012 | 0.002012 | -6.2086
2008-05-27 | 0.61708 | 0.61708 | -0.48275
2008-05-28 | 0.0053667 | 0.0053667 | -5.2275
2008-05-29 | 0.033468 | 0.033468 | -3.3972
2008-05-30 | 0.12549 | 0.12549 | -2.0755
2008-05-31 | 0.017061 | 0.017061 | -4.0709
2008-06-01 | 0.30541 | 0.30541 | -1.1861
2008-06-02 | 0.039579 | 0.039579 | -3.2294
2008-06-03 | 0.21627 | 0.21627 | -1.5312
2008-06-04 | 0.26307 | 0.26307 | -1.3353
2008-06-05 | 0.025657 | 0.025657 | -3.6629
2008-06-06 | 0.0021232 | 0.0021232 | -6.1548
2008-06-07 | 0.57287 | 0.57287 | -0.5571
2008-06-08 | 0.56222 | 0.56222 | -0.57586
2008-06-09 | 0.14723 | 0.14723 | -1.9158
2008-06-10 | 0.016097 | 0.016097 | -4.1291
2008-06-11 | 0.15569 | 0.15569 | -1.8599
2008-06-12 | 0.18001 | 0.18001 | -1.7147
2008-06-13 | 0.17763 | 0.17763 | -1.728
2008-06-14 | 0.091758 | 0.091758 | -2.3886
2008-06-15 | 0.024283 | 0.024283 | -3.718
2008-06-16 | 0.19371 | 0.19371 | -1.6414
2008-06-17 | 0.0038479 | 0.0038479 | -5.5602
2008-06-18 | 0.011489 | 0.011489 | -4.4664
2008-06-19 | 0.0045912 | 0.0045912 | -5.3836
2008-06-20 | 0.26197 | 0.26197 | -1.3395
2008-06-21 | 0.58858 | 0.58858 | -0.53005
2008-06-22 | 0.097781 | 0.097781 | -2.325
2008-06-23 | 0.4297 | 0.4297 | -0.84468
2008-06-24 | 0.017668 | 0.017668 | -4.036
2008-06-25 | 0.28381 | 0.28381 | -1.2594
2008-06-26 | 0.043089 | 0.043089 | -3.1445
2008-06-27 | 0.15515 | 0.15515 | -1.8634
2008-06-28 | 0.34221 | 0.34221 | -1.0723
2008-06-29 | 0.92122 | 0.92122 | -0.082053
2008-06-30 | 0.019107 | 0.019107 | -3.9577
2008-07-01 | 2.4049 | 2.4049 | 0.87752
2008-07-02 | 0.045255 | 0.045255 | -3.0954
2008-07-03 | 0.027807 | 0.027807 | -3.5825
2008-07-04 | 0.2641 | 0.2641 | -1.3314
2008-07-05 | 0.064021 | 0.064021 | -2.7485
2008-07-06 | 0.0038486 | 0.0038486 | -5.56
2008-07-07 | 0.048441 | 0.048441 | -3.0274
2008-07-08 | 0.26721 | 0.26721 | -1.3197
2008-07-09 | 0.76009 | 0.76009 | -0.27431
2008-07-10 | 0.083138 | 0.083138 | -2.4873
2008-07-11 | 0.018897 | 0.018897 | -3.9688
2008-07-12 | 0.022028 | 0.022028 | -3.8154
2008-07-13 | 0.083085 | 0.083085 | -2.4879
2008-07-14 | 0.0048961 | 0.0048961 | -5.3193
2008-07-15 | 0.030595 | 0.030595 | -3.4869
2008-07-16 | 0.004615 | 0.004615 | -5.3784
2008-07-17 | 0.086232 | 0.086232 | -2.4507
2008-07-18 | 0.031028 | 0.031028 | -3.4729
2008-07-19 | 0.094948 | 0.094948 | -2.3544
2008-07-20 | 0.0033569 | 0.0033569 | -5.6967
2008-07-21 | 0.0073699 | 0.0073699 | -4.9103
2008-07-22 | 0.048645 | 0.048645 | -3.0232
2008-07-23 | 0.015959 | 0.015959 | -4.1377
2008-07-24 | 0.067983 | 0.067983 | -2.6885
2008-07-25 | 0.018715 | 0.018715 | -3.9784
2008-07-26 | 0.012709 | 0.012709 | -4.3654
2008-07-27 | 0.26722 | 0.26722 | -1.3197
2008-07-28 | 0.014934 | 0.014934 | -4.2041
2008-07-29 | 0.034284 | 0.034284 | -3.3731
2008-07-30 | 0.0083079 | 0.0083079 | -4.7905
2008-07-31 | 0.0099073 | 0.0099073 | -4.6145
2008-08-01 | 0.018413 | 0.018413 | -3.9947
2008-08-02 | 0.022262 | 0.022262 | -3.8049
2008-08-03 | 0.0011178 | 0.0011178 | -6.7964
2008-08-04 | 0.11754 | 0.11754 | -2.141
2008-08-05 | 0.052138 | 0.052138 | -2.9539
2008-08-06 | 0.0076361 | 0.0076361 | -4.8749
2008-08-07 | 0.0063929 | 0.0063929 | -5.0526
2008-08-08 | 0.0035297 | 0.0035297 | -5.6465
2008-08-09 | 0.0036344 | 0.0036344 | -5.6173
2008-08-10 | 0.064226 | 0.064226 | -2.7453
2008-08-11 | 0.034718 | 0.034718 | -3.3605
2008-08-12 | 0.15353 | 0.15353 | -1.8739
2008-08-13 | 0.010293 | 0.010293 | -4.5762
2008-08-14 | 0.52499 | 0.52499 | -0.64438
2008-08-15 | 0.010768 | 0.010768 | -4.5312
2008-08-16 | 0.0048039 | 0.0048039 | -5.3383
2008-08-17 | 0.001661 | 0.001661 | -6.4003
2008-08-18 | 0.0052316 | 0.0052316 | -5.253
2008-08-19 | 0.0027057 | 0.0027057 | -5.9124
2008-08-20 | 0.4821 | 0.4821 | -0.7296
2008-08-21 | 0.081602 | 0.081602 | -2.5059
2008-08-22 | 0.010581 | 0.010581 | -4.5487
2008-08-23 | 0.82878 | 0.82878 | -0.1878
2008-08-24 | 0.00037386 | 0.00037386 | -7.8916
2008-08-25 | 0.10832 | 0.10832 | -2.2227
2008-08-26 | 0.0014154 | 0.0014154 | -6.5603
2008-08-27 | 0.013642 | 0.013642 | -4.2946
2008-08-28 | 0.034243 | 0.034243 | -3.3743
2008-08-29 | 0.028869 | 0.028869 | -3.545
2008-08-30 | 0.85901 | 0.85901 | -0.15197
2008-08-31 | 0.014601 | 0.014601 | -4.2267
2008-09-01 | 0.0074964 | 0.0074964 | -4.8933
2008-09-02 | 0.021586 | 0.021586 | -3.8357
2008-09-03 | 0.13669 | 0.0060684 | -1.99
2008-09-04 | 0.0025782 | 0.0025782 | -5.9607
2008-09-05 | 0.0747 | 0.0747 | -2.5943
2008-09-06 | 0.0019904 | 0.0019904 | -6.2194
2008-09-07 | 0.0019075 | 0.0019075 | -6.2619
2008-09-08 | 0.0019837 | 0.0019837 | -6.2228
2008-09-09 | 0.038904 | 0.038904 | -3.2466
2008-09-10 | 0.0015577 | 0.0015577 | -6.4645
2008-09-11 | 0.072488 | 0.072488 | -2.6243
2008-09-12 | 0.09578 | 0.09578 | -2.3457
2008-09-13 | 0.0060038 | 0.0060038 | -5.1154
2008-09-14 | 0.11272 | 0.11272 | -2.1829
2008-09-15 | 0.40187 | 0.40187 | -0.91162
2008-09-16 | 0.017428 | 0.017428 | -4.0497
2008-09-17 | 0.047613 | 0.047613 | -3.0446
2008-09-18 | 0.0052752 | 0.0052752 | -5.2447
2008-09-19 | 0.18518 | 0.18518 | -1.6864
2008-09-20 | 0.026531 | 0.026531 | -3.6294
2008-09-21 | 0.14376 | 0.14376 | -1.9396
2008-09-22 | 0.15445 | 0.15445 | -1.8679
2008-09-23 | 0.031674 | 0.031674 | -3.4523
2008-09-24 | 0.0077823 | 0.0077823 | -4.8559
2008-09-25 | 0.016894 | 0.016894 | -4.0808
2008-09-26 | 0.00066052 | 0.00066052 | -7.3225
2008-09-27 | 0.0068828 | 0.0068828 | -4.9787
2008-09-28 | 0.025946 | 0.025946 | -3.6518
2008-09-29 | 0.0092267 | 0.0092267 | -4.6857
2008-09-30 | 0.008629 | 0.008629 | -4.7526
2008-10-01 | 0.089626 | 0.089626 | -2.4121
2008-10-02 | 0.00079251 | 0.00079251 | -7.1403
2008-10-03 | 0.031501 | 0.031501 | -3.4577
2008-10-04 | 0.016351 | 0.016351 | -4.1135
2008-10-05 | 0.005031 | 0.005031 | -5.2921
2008-10-06 | 0.026975 | 0.026975 | -3.6128
2008-10-07 | 0.0048126 | 0.0048126 | -5.3365
2008-10-08 | 0.004353 | 0.004353 | -5.4369
2008-10-09 | 0.05606 | 0.05606 | -2.8813
2008-10-10 | 0.29778 | 0.29778 | -1.2114
2008-10-11 | 0.18888 | 0.18888 | -1.6667
2008-10-12 | 0.023192 | 0.023192 | -3.764
2008-10-13 | 0.16061 | 0.16061 | -1.8288
2008-10-14 | 0.0078919 | 0.0078919 | -4.8419
2008-10-15 | 0.0061756 | 0.0061756 | -5.0871
2008-10-16 | 0.0013537 | 0.0013537 | -6.6049
2008-10-17 | 0.0058966 | 0.0058966 | -5.1334
2008-10-18 | 0.025147 | 0.025147 | -3.683
2008-10-19 | 0.059167 | 0.059167 | -2.8274
2008-10-20 | 0.0024243 | 0.0024243 | -6.0222
2008-10-21 | 0.0043621 | 0.0043621 | -5.4348
2008-10-22 | 0.0017768 | 0.0017768 | -6.3329
2008-10-23 | 0.023802 | 0.023802 | -3.738
2008-10-24 | 0.0012454 | 0.0012454 | -6.6883
2008-10-25 | 0.034121 | 0.034121 | -3.3778
2008-10-26 | 0.038841 | 0.038841 | -3.2483
2008-10-27 | 0.006562 | 0.006562 | -5.0265
2008-10-28 | 0.011321 | 0.011321 | -4.4811
2008-10-29 | 0.21407 | 0.21407 | -1.5415
2008-10-30 | 0.19404 | 0.19404 | -1.6397
2008-10-31 | 0.0088846 | 0.0088846 | -4.7234
2008-11-01 | 0.0010193 | 0.0010193 | -6.8887
2008-11-02 | 0.0014866 | 0.0014866 | -6.5112
2008-11-03 | 0.41792 | 0.41792 | -0.87247
2008-11-04 | 0.096723 | 0.096723 | -2.3359
2008-11-05 | 0.024331 | 0.024331 | -3.716
2008-11-06 | 0.12901 | 0.12901 | -2.0479
2008-11-07 | 0.078528 | 0.078528 | -2.5443
2008-11-08 | 0.0073713 | 0.0073713 | -4.9102
2008-11-09 | 0.050442 | 0.050442 | -2.9869
2008-11-10 | 0.0060701 | 0.0060701 | -5.1044
2008-11-11 | 0.0020718 | 0.0020718 | -6.1793
2008-11-12 | 0.51765 | 0.51765 | -0.65846
2008-11-13 | 0.036307 | 0.036307 | -3.3158
2008-11-14 | 1.6929 | 1.6929 | 0.52646
2008-11-15 | 0.0064349 | 0.0064349 | -5.046
2008-11-16 | 0.001097 | 0.001097 | -6.8151
2008-11-17 | 0.27024 | 0.27024 | -1.3084
2008-11-18 | 0.1381 | 0.1381 | -1.9798
2008-11-19 | 0.04778 | 0.04778 | -3.0412
2008-11-20 | 0.15336 | 0.15336 | -1.875
2008-11-21 | 0.013398 | 0.013398 | -4.3127
2008-11-22 | 0.89693 | 0.89693 | -0.10877
2008-11-23 | 0.17453 | 0.17453 | -1.7456
2008-11-24 | 0.019289 | 0.019289 | -3.9482
2008-11-25 | 0.056301 | 0.056301 | -2.877
2008-11-26 | 0.22743 | 0.22743 | -1.4809
2008-11-27 | 0.49356 | 0.49356 | -0.7061
2008-11-28 | 0.022594 | 0.022594 | -3.7901
2008-11-29 | 0.044614 | 0.044614 | -3.1097
2008-11-30 | 0.1316 | 0.1316 | -2.028
2008-12-01 | 0.065244 | 0.065244 | -2.7296
2008-12-02 | 0.0026913 | 0.0026913 | -5.9177
2008-12-03 | 0.0021789 | 0.0021789 | -6.129
2008-12-04 | 0.090351 | 0.090351 | -2.404
2008-12-05 | 0.1614 | 0.1614 | -1.8239
2008-12-06 | 0.0038618 | 0.0038618 | -5.5566
2008-12-07 | 1.058 | 1.058 | 0.056409
2008-12-08 | 0.44513 | 0.44513 | -0.8094
2008-12-09 | 0.071613 | 0.071613 | -2.6365
2008-12-10 | 0.0024918 | 0.0024918 | -5.9947
2008-12-11 | 0.013261 | 0.013261 | -4.3229
2008-12-12 | 0.65606 | 0.65606 | -0.4215
2008-12-13 | 1.532 | 1.532 | 0.4266
2008-12-14 | 0.1189 | 0.1189 | -2.1295
2008-12-15 | 0.015814 | 0.015814 | -4.1468
2008-12-16 | 0.0028346 | 0.0028346 | -5.8658
2008-12-17 | 0.0048023 | 0.0048023 | -5.3387
2008-12-18 | 0.0069558 | 0.0069558 | -4.9682
2008-12-19 | 0.41997 | 0.41997 | -0.86758
2008-12-20 | 0.031541 | 0.031541 | -3.4565
2008-12-21 | 0.54678 | 0.54678 | -0.60372
2008-12-22 | 0.153 | 0.153 | -1.8773
2008-12-23 | 0.0074384 | 0.0074384 | -4.9011
2008-12-24 | 0.0018824 | 0.0018824 | -6.2752
2008-12-25 | 0.22954 | 0.22954 | -1.4717
2008-12-26 | 0.080709 | 0.080709 | -2.5169
2008-12-27 | 0.30218 | 0.30218 | -1.1967
2008-12-28 | 0.017652 | 0.017652 | -4.0369
2008-12-29 | 0.011615 | 0.011615 | -4.4555
2008-12-30 | 0.11661 | 0.11661 | -2.1489
2008-12-31 | 0.0028062 | 0.0028062 | -5.8759
2009-01-01 | 0.0060508 | 0.0060508 | -5.1076
2009-01-02 | 0.17922 | 0.17922 | -1.7191
2009-01-03 | 0.0011289 | 0.0011289 | -6.7865
2009-01-04 | 0.15676 | 0.15676 | -1.8531
2009-01-05 | 0.0021601 | 0.0021601 | -6.1376
2009-01-06 | 0.018641 | 0.018641 | -3.9824
2009-01-07 | 0.0084295 | 0.0084295 | -4.776
2009-01-08 | 0.054881 | 0.054881 | -2.9026
2009-01-09 | 0.003302 | 0.003302 | -5.7132
2009-01-10 | 0.030878 | 0.030878 | -3.4777
2009-01-11 | 0.24208 | 0.24208 | -1.4185
2009-01-12 | 0.087376 | 0.087376 | -2.4375
2009-01-13 | 0.21968 | 0.21968 | -1.5156
2009-01-14 | 0.35396 | 0.35396 | -1.0386
2009-01-15 | 0.37109 | 0.37109 | -0.9913
2009-01-16 | 0.25067 | 0.25067 | -1.3836
2009-01-17 | 0.0021566 | 0.0021566 | -6.1392
2009-01-18 | 0.0020375 | 0.0020375 | -6.196
2009-01-19 | 0.24731 | 0.24731 | -1.3971
2009-01-20 | 0.10603 | 0.10603 | -2.244
2009-01-21 | 0.0098803 | 0.0098803 | -4.6172
2009-01-22 | 0.64848 | 0.64848 | -0.43313
2009-01-23 | 0.015141 | 0.015141 | -4.1904
2009-01-24 | 3.2748 | 3.2748 | 1.1863
2009-01-25 | 0.46215 | 0.46215 | -0.77187
2009-01-26 | 0.45262 | 0.45262 | -0.7927
2009-01-27 | 0.50705 | 0.50705 | -0.67914
2009-01-28 | 14.7037 | 0 | 2.6881
2009-01-29 | 16.2694 | 13.7285 | 2.7893
2009-01-30 | 8.7611 | 0 | 2.1703
2009-01-31 | 0.27499 | 0.27499 | -1.291
2009-02-01 | 0.8261 | 0.8261 | -0.19104
2009-02-02 | 0.75369 | 0.75369 | -0.28277
2009-02-03 | 0.47717 | 0.47717 | -0.73989
2009-02-04 | 1.2143 | 1.2143 | 0.19419
2009-02-05 | 0.33969 | 0.33969 | -1.0797
2009-02-06 | 0.82235 | 0.82235 | -0.19559
2009-02-07 | 2.5328 | 2.5328 | 0.92932
2009-02-08 | 4.715 | 4.715 | 1.5508
2009-02-09 | 0.028051 | 0.028051 | -3.5737
2009-02-10 | 0.0092727 | 0.0092727 | -4.6807
2009-02-11 | 0.011731 | 0.011731 | -4.4455
2009-02-12 | 0.20596 | 0.20596 | -1.5801
2009-02-13 | 0.051882 | 0.051882 | -2.9588
2009-02-14 | 0.0189 | 0.0189 | -3.9686
2009-02-15 | 1.3094 | 1.3094 | 0.26954
2009-02-16 | 0.027885 | 0.027885 | -3.5797
2009-02-17 | 0.19602 | 0.19602 | -1.6296
2009-02-18 | 0.021936 | 0.021936 | -3.8196
2009-02-19 | 0.19943 | 0.19943 | -1.6123
2009-02-20 | 0.013131 | 0.013131 | -4.3328
2009-02-21 | 0.70993 | 0.70993 | -0.34259
2009-02-22 | 0.29761 | 0.29761 | -1.212
2009-02-23 | 0.09407 | 0.09407 | -2.3637
2009-02-24 | 0.19126 | 0.19126 | -1.6541
2009-02-25 | 0.016472 | 0.016472 | -4.1061
2009-02-26 | 0.0054237 | 0.0054237 | -5.217
2009-02-27 | 0.031982 | 0.031982 | -3.4426
2009-02-28 | 0.05618 | 0.05618 | -2.8792
2009-03-01 | 0.25086 | 0.25086 | -1.3829
2009-03-02 | 0.0068491 | 0.0068491 | -4.9836
2009-03-03 | 5.6497 | 5.6497 | 1.7316
2009-03-04 | 1.3658 | 1.3658 | 0.31172
2009-03-05 | 0.18992 | 0.18992 | -1.6612
2009-03-06 | 0.11154 | 0.11154 | -2.1934
2009-03-07 | 0.044495 | 0.044495 | -3.1124
2009-03-08 | 0.08822 | 0.08822 | -2.4279
2009-03-09 | 0.005905 | 0.005905 | -5.1319
2009-03-10 | 0.010763 | 0.010763 | -4.5316
2009-03-11 | 0.024172 | 0.024172 | -3.7226
2009-03-12 | 0.3569 | 0.3569 | -1.0303
2009-03-13 | 0.078516 | 0.078516 | -2.5445
2009-03-14 | 1.4574 | 1.4574 | 0.37664
2009-03-15 | 0.045084 | 0.045084 | -3.0992
2009-03-16 | 0.030958 | 0.030958 | -3.4751
2009-03-17 | 0.055704 | 0.055704 | -2.8877
2009-03-18 | 0.023623 | 0.023623 | -3.7455
2009-03-19 | 0.039323 | 0.039323 | -3.236
2009-03-20 | 0.0015655 | 0.0015655 | -6.4596
2009-03-21 | 0.34042 | 0.34042 | -1.0776
2009-03-22 | 0.002025 | 0.002025 | -6.2022
2009-03-23 | 0.0047917 | 0.0047917 | -5.3409
2009-03-24 | 0.51799 | 0.51799 | -0.6578
2009-03-25 | 0.031565 | 0.031565 | -3.4557
2009-03-26 | 0.014536 | 0.014536 | -4.2311
2009-03-27 | 0.014065 | 0.014065 | -4.264
2009-03-28 | 0.037209 | 0.037209 | -3.2912
2009-03-29 | 0.0026317 | 0.0026317 | -5.9401
2009-03-30 | 0.014523 | 0.014523 | -4.232
2009-03-31 | 0.0096789 | 0.0096789 | -4.6378
2009-04-01 | 0.18659 | 0.18659 | -1.6789
2009-04-02 | 0.012653 | 0.012653 | -4.3698
2009-04-03 | 2.3754 | 2.3754 | 0.86515
2009-04-04 | 0.12069 | 0.12069 | -2.1146
2009-04-05 | 0.001304 | 0.001304 | -6.6423
2009-04-06 | 0.021221 | 0.021221 | -3.8528
2009-04-07 | 0.077287 | 0.077287 | -2.5602
2009-04-08 | 0.034907 | 0.034907 | -3.3551
2009-04-09 | 0.098227 | 0.098227 | -2.3205
2009-04-10 | 0.32838 | 0.32838 | -1.1136
2009-04-11 | 0.0010826 | 0.0010826 | -6.8284
2009-04-12 | 0.37515 | 0.37515 | -0.98043
2009-04-13 | 0.13383 | 0.13383 | -2.0112
2009-04-14 | 0.0037247 | 0.0037247 | -5.5928
2009-04-15 | 1.8226 | 1.8226 | 0.60026
2009-04-16 | 0.025525 | 0.025525 | -3.6681
2009-04-17 | 0.011275 | 0.011275 | -4.4852
2009-04-18 | 0.014643 | 0.014643 | -4.2238
2009-04-19 | 0.0056177 | 0.0056177 | -5.1818
2009-04-20 | 0.011961 | 0.011961 | -4.4261
2009-04-21 | 0.096152 | 0.096152 | -2.3418
2009-04-22 | 0.0044124 | 0.0044124 | -5.4233
2009-04-23 | 0.11378 | 0.062397 | -2.1735
2009-04-24 | 1.1031 | 1.1031 | 0.098121
2009-04-25 | 0.12405 | 0.12405 | -2.0871
2009-04-26 | 3.8366 | 3.8366 | 1.3446
2009-04-27 | 0.12314 | 0.12314 | -2.0944
2009-04-28 | 0.042826 | 0.042826 | -3.1506
2009-04-29 | 0.042054 | 0.042054 | -3.1688
2009-04-30 | 0.023865 | 0.023865 | -3.7354
2009-05-01 | 0.0029131 | 0.0029131 | -5.8386
2009-05-02 | 0.5803 | 0.5803 | -0.54422
2009-05-03 | 0.001332 | 0.001332 | -6.6211
2009-05-04 | 0.57241 | 0.57241 | -0.55789
2009-05-05 | 0.0083436 | 0.0083436 | -4.7863
2009-05-06 | 0.0079401 | 0.0079401 | -4.8358
2009-05-07 | 0.012597 | 0.012597 | -4.3743
2009-05-08 | 0.42957 | 0.42957 | -0.84497
2009-05-09 | 0.0067677 | 0.0067677 | -4.9956
2009-05-10 | 0.13744 | 0.13744 | -1.9846
2009-05-11 | 0.021108 | 0.021108 | -3.8581
2009-05-12 | 0.025713 | 0.025713 | -3.6608
2009-05-13 | 0.20177 | 0.20177 | -1.6006
2009-05-14 | 0.15614 | 0.15614 | -1.857
2009-05-15 | 0.25607 | 0.25607 | -1.3623
2009-05-16 | 0.43803 | 0.43803 | -0.82546
2009-05-17 | 0.0099161 | 0.0099161 | -4.6136
2009-05-18 | 0.0013882 | 0.0013882 | -6.5797
2009-05-19 | 0.0025973 | 0.0025973 | -5.9533
2009-05-20 | 0.0010167 | 0.0010167 | -6.8912
2009-05-21 | 0.010314 | 0.010314 | -4.5743
2009-05-22 | 0.033014 | 0.033014 | -3.4108
2009-05-23 | 0.0091583 | 0.0091583 | -4.6931
2009-05-24 | 0.00093722 | 0.00093722 | -6.9726
2009-05-25 | 0.011454 | 0.011454 | -4.4694
2009-05-26 | 0.13003 | 0.13003 | -2.04
2009-05-27 | 0.02013 | 0.02013 | -3.9055
2009-05-28 | 0.14959 | 0.14959 | -1.8998
2009-05-29 | 0.035893 | 0.035893 | -3.3272
2009-05-30 | 0.31441 | 0.31441 | -1.157
2009-05-31 | 0.012544 | 0.012544 | -4.3785
2009-06-01 | 0.0066552 | 0.0066552 | -5.0124
2009-06-02 | 0.033802 | 0.033802 | -3.3872
2009-06-03 | 0.10546 | 0.10546 | -2.2494
2009-06-04 | 0.0018275 | 0.0018275 | -6.3048
2009-06-05 | 0.011522 | 0.011522 | -4.4635
2009-06-06 | 0.037985 | 0.037985 | -3.2706
2009-06-07 | 0.0017361 | 0.0017361 | -6.3561
2009-06-08 | 0.098398 | 0.098398 | -2.3187
2009-06-09 | 0.53534 | 0.53534 | -0.62485
2009-06-10 | 0.45161 | 0.45161 | -0.79493
2009-06-11 | 0.013145 | 0.013145 | -4.3317
2009-06-12 | 0.34163 | 0.34163 | -1.074
2009-06-13 | 0.017502 | 0.017502 | -4.0454
2009-06-14 | 0.0063729 | 0.0063729 | -5.0557
2009-06-15 | 0.017579 | 0.017579 | -4.0411
2009-06-16 | 0.10184 | 0.10184 | -2.2844
2009-06-17 | 0.015929 | 0.015929 | -4.1396
2009-06-18 | 0.0070047 | 0.0070047 | -4.9612
2009-06-19 | 0.025481 | 0.025481 | -3.6698
2009-06-20 | 0.052323 | 0.052323 | -2.9503
2009-06-21 | 0.0031045 | 0.0031045 | -5.7749
2009-06-22 | 0.0056488 | 0.0056488 | -5.1763
2009-06-23 | 0.0034957 | 0.0034957 | -5.6562
2009-06-24 | 0.016753 | 0.016753 | -4.0892
2009-06-25 | 0.05561 | 0.05561 | -2.8894
2009-06-26 | 0.49754 | 0.49754 | -0.69808
2009-06-27 | 0.015734 | 0.015734 | -4.1519
2009-06-28 | 0.20144 | 0.20144 | -1.6022
2009-06-29 | 0.007835 | 0.007835 | -4.8492
2009-06-30 | 0.37152 | 0.37152 | -0.99014
2009-07-01 | 0.31898 | 0.31898 | -1.1426
2009-07-02 | 0.78089 | 0.3265 | -0.24732
2009-07-03 | 0.17237 | 0.17237 | -1.7581
2009-07-04 | 0.011496 | 0.011496 | -4.4658
2009-07-05 | 0.00084055 | 0.00084055 | -7.0815
2009-07-06 | 0.020833 | 0.020833 | -3.8712
2009-07-07 | 0.0047506 | 0.0047506 | -5.3495
2009-07-08 | 0.031893 | 0.031893 | -3.4454
2009-07-09 | 0.013654 | 0.013654 | -4.2937
2009-07-10 | 0.0095179 | 0.0095179 | -4.6546
2009-07-11 | 0.02 | 0.02 | -3.912
2009-07-12 | 0.42579 | 0.42579 | -0.85382
2009-07-13 | 0.29364 | 0.29364 | -1.2254
2009-07-14 | 0.7883 | 0.7883 | -0.23787
2009-07-15 | 0.0098836 | 0.0098836 | -4.6169
2009-07-16 | 0.028951 | 0.028951 | -3.5421
2009-07-17 | 0.014864 | 0.014864 | -4.2088
2009-07-18 | 0.010672 | 0.010672 | -4.5401
2009-07-19 | 0.20265 | 0.20265 | -1.5963
2009-07-20 | 0.14649 | 0.14649 | -1.9208
2009-07-21 | 0.0021495 | 0.0021495 | -6.1425
2009-07-22 | 0.42174 | 0.42174 | -0.86336
2009-07-23 | 0.14711 | 0.14711 | -1.9166
2009-07-24 | 0.0031625 | 0.0031625 | -5.7564
2009-07-25 | 0.006617 | 0.006617 | -5.0181
2009-07-26 | 0.0021776 | 0.0021776 | -6.1295
2009-07-27 | 0.0016652 | 0.0016652 | -6.3978
2009-07-28 | 0.025597 | 0.025597 | -3.6653
2009-07-29 | 0.012273 | 0.012273 | -4.4004
2009-07-30 | 0.042123 | 0.042123 | -3.1672
2009-07-31 | 0.19786 | 0.19786 | -1.6202
2009-08-01 | 0.0028814 | 0.0028814 | -5.8495
2009-08-02 | 0.15391 | 0.15391 | -1.8714
2009-08-03 | 0.25368 | 0.25368 | -1.3717
2009-08-04 | 0.036393 | 0.036393 | -3.3134
2009-08-05 | 0.022921 | 0.022921 | -3.7757
2009-08-06 | 0.25536 | 0.25536 | -1.3651
2009-08-07 | 0.046591 | 0.046591 | -3.0663
2009-08-08 | 0.015448 | 0.015448 | -4.1703
2009-08-09 | 0.026442 | 0.026442 | -3.6328
2009-08-10 | 0.0070119 | 0.0070119 | -4.9602
2009-08-11 | 0.037563 | 0.037563 | -3.2817
2009-08-12 | 0.08051 | 0.08051 | -2.5194
2009-08-13 | 0.076221 | 0.076221 | -2.5741
2009-08-14 | 0.20851 | 0.20851 | -1.5678
2009-08-15 | 0.6608 | 0.6608 | -0.41431
2009-08-16 | 2.5129 | 2.5129 | 0.92145
2009-08-17 | 0.010497 | 0.010497 | -4.5566
2009-08-18 | 0.0089575 | 0.0089575 | -4.7153
2009-08-19 | 0.50971 | 0.50971 | -0.67391
2009-08-20 | 0.63184 | 0.63184 | -0.45913
2009-08-21 | 1.7966 | 1.7966 | 0.58592
2009-08-22 | 1.0086 | 1.0086 | 0.0085481
2009-08-23 | 0.072571 | 0.072571 | -2.6232
2009-08-24 | 0.0065241 | 0.0065241 | -5.0323
2009-08-25 | 1.6814 | 1.6814 | 0.51964
2009-08-26 | 0.91265 | 0.91265 | -0.091403
2009-08-27 | 0.03566 | 0.03566 | -3.3337
2009-08-28 | 0.093821 | 0.093821 | -2.3664
2009-08-29 | 0.0078655 | 0.0078655 | -4.8453
2009-08-30 | 0.01251 | 0.01251 | -4.3812
2009-08-31 | 0.017417 | 0.017417 | -4.0503
2009-09-01 | 0.079751 | 0.079751 | -2.5289
2009-09-02 | 0.30756 | 0.30756 | -1.1791
2009-09-03 | 0.26319 | 0.26319 | -1.3349
2009-09-04 | 0.038169 | 0.038169 | -3.2657
2009-09-05 | 0.01771 | 0.01771 | -4.0336
2009-09-06 | 0.0012596 | 0.0012596 | -6.677
2009-09-07 | 0.0030386 | 0.0030386 | -5.7964
2009-09-08 | 0.1968 | 0.1968 | -1.6256
2009-09-09 | 0.051615 | 0.051615 | -2.9639
2009-09-10 | 0.024295 | 0.024295 | -3.7175
2009-09-11 | 0.82454 | 0.82454 | -0.19293
2009-09-12 | 0.042733 | 0.042733 | -3.1528
2009-09-13 | 0.041408 | 0.041408 | -3.1843
2009-09-14 | 0.022292 | 0.022292 | -3.8035
2009-09-15 | 0.0092317 | 0.0092317 | -4.6851
2009-09-16 | 0.39507 | 0.39507 | -0.92869
2009-09-17 | 0.14145 | 0.14145 | -1.9558
2009-09-18 | 0.046462 | 0.046462 | -3.0691
2009-09-19 | 0.009095 | 0.009095 | -4.7
2009-09-20 | 0.091787 | 0.091787 | -2.3883
2009-09-21 | 0.090045 | 0.090045 | -2.4074
2009-09-22 | 0.011456 | 0.011456 | -4.4693
2009-09-23 | 0.0024833 | 0.0024833 | -5.9982
2009-09-24 | 0.1129 | 0.1129 | -2.1813
2009-09-25 | 0.030291 | 0.030291 | -3.4969
2009-09-26 | 0.13734 | 0.13734 | -1.9853
2009-09-27 | 0.77395 | 0.77395 | -0.25624
2009-09-28 | 0.1015 | 0.1015 | -2.2877
2009-09-29 | 0.043174 | 0.043174 | -3.1425
2009-09-30 | 0.11669 | 0.11669 | -2.1483
2009-10-01 | 0.0021904 | 0.0021904 | -6.1237
2009-10-02 | 0.0035484 | 0.0035484 | -5.6413
2009-10-03 | 0.26465 | 0.26465 | -1.3294
2009-10-04 | 0.4465 | 0.4465 | -0.80631
2009-10-05 | 0.0018512 | 0.0018512 | -6.2919
2009-10-06 | 0.01045 | 0.01045 | -4.5611
2009-10-07 | 0.011504 | 0.011504 | -4.4651
2009-10-08 | 0.022385 | 0.022385 | -3.7993
2009-10-09 | 0.071036 | 0.071036 | -2.6446
2009-10-10 | 0.011826 | 0.011826 | -4.4374
2009-10-11 | 0.83804 | 0.83804 | -0.1767
2009-10-12 | 0.036289 | 0.036289 | -3.3162
2009-10-13 | 0.57539 | 0.57539 | -0.55271
2009-10-14 | 0.0027687 | 0.0027687 | -5.8894
2009-10-15 | 0.033374 | 0.033374 | -3.4
2009-10-16 | 0.012961 | 0.012961 | -4.3458
2009-10-17 | 0.27436 | 0.27436 | -1.2933
2009-10-18 | 0.03949 | 0.03949 | -3.2317
2009-10-19 | 0.020286 | 0.020286 | -3.8978
2009-10-20 | 0.036842 | 0.036842 | -3.3011
2009-10-21 | 0.0053714 | 0.0053714 | -5.2267
2009-10-22 | 0.11331 | 0.11331 | -2.1776
2009-10-23 | 0.0016458 | 0.0016458 | -6.4095
2009-10-24 | 0.0049173 | 0.0049173 | -5.315
2009-10-25 | 0.41043 | 0.41043 | -0.89055
2009-10-26 | 0.0074129 | 0.0074129 | -4.9045
2009-10-27 | 0.056145 | 0.056145 | -2.8798
2009-10-28 | 0.0010369 | 0.0010369 | -6.8715
2009-10-29 | 0.22353 | 0.22353 | -1.4982
2009-10-30 | 0.029044 | 0.029044 | -3.5389
2009-10-31 | 0.057853 | 0.057853 | -2.8498
2009-11-01 | 0.014407 | 0.014407 | -4.2401
2009-11-02 | 0.013465 | 0.013465 | -4.3077
2009-11-03 | 0.016422 | 0.016422 | -4.1091
2009-11-04 | 0.17134 | 0.17134 | -1.7641
2009-11-05 | 0.012974 | 0.012974 | -4.3448
2009-11-06 | 0.00027951 | 0.00027951 | -8.1825
2009-11-07 | 0.1076 | 0.1076 | -2.2293
2009-11-08 | 0.14119 | 0.14119 | -1.9576
2009-11-09 | 0.54487 | 0.54487 | -0.60721
2009-11-10 | 0.69798 | 0.69798 | -0.35957
2009-11-11 | 0.064602 | 0.064602 | -2.7395
2009-11-12 | 0.04768 | 0.04768 | -3.0432
2009-11-13 | 0.06742 | 0.06742 | -2.6968
2009-11-14 | 0.083483 | 0.083483 | -2.4831
2009-11-15 | 0.0045016 | 0.0045016 | -5.4033
2009-11-16 | 0.27553 | 0.27553 | -1.289
2009-11-17 | 0.010737 | 0.010737 | -4.534
2009-11-18 | 0.014103 | 0.014103 | -4.2614
2009-11-19 | 0.054317 | 0.054317 | -2.9129
2009-11-20 | 0.55315 | 0.55315 | -0.59213
2009-11-21 | 0.22596 | 0.22596 | -1.4874
2009-11-22 | 0.35264 | 0.35264 | -1.0423
2009-11-23 | 0.010384 | 0.010384 | -4.5674
2009-11-24 | 0.031242 | 0.031242 | -3.466
2009-11-25 | 0.031753 | 0.031753 | -3.4498
2009-11-26 | 6.0443 | 6.0443 | 1.7991
2009-11-27 | 0.33287 | 0.33287 | -1.1
2009-11-28 | 0.0093209 | 0.0093209 | -4.6755
2009-11-29 | 0.0035595 | 0.0035595 | -5.6381
2009-11-30 | 0.035986 | 0.035986 | -3.3246
2009-12-01 | 0.0017406 | 0.0017406 | -6.3535
2009-12-02 | 0.14545 | 0.14545 | -1.928
2009-12-03 | 0.42767 | 0.42767 | -0.84941
2009-12-04 | 0.0094005 | 0.0094005 | -4.667
2009-12-05 | 0.0092354 | 0.0092354 | -4.6847
2009-12-06 | 0.0095849 | 0.0095849 | -4.6476
2009-12-07 | 0.026776 | 0.026776 | -3.6202
2009-12-08 | 0.066142 | 0.066142 | -2.7159
2009-12-09 | 0.097198 | 0.097198 | -2.331
2009-12-10 | 0.055384 | 0.055384 | -2.8935
2009-12-11 | 0.039565 | 0.039565 | -3.2298
2009-12-12 | 0.16198 | 0.16198 | -1.8203
2009-12-13 | 0.0088301 | 0.0088301 | -4.7296
2009-12-14 | 0.1233 | 0.1233 | -2.0931
2009-12-15 | 0.15793 | 0.15793 | -1.8456
2009-12-16 | 0.26364 | 0.26364 | -1.3332
2009-12-17 | 0.037882 | 0.037882 | -3.2733
2009-12-18 | 0.003945 | 0.003945 | -5.5353
2009-12-19 | 0.18549 | 0.18549 | -1.6848
2009-12-20 | 0.64715 | 0.64715 | -0.43518
2009-12-21 | 0.085656 | 0.085656 | -2.4574
2009-12-22 | 0.035286 | 0.035286 | -3.3443
2009-12-23 | 0.76798 | 0.76798 | -0.264
2009-12-24 | 0.020358 | 0.020358 | -3.8943
2009-12-25 | 0.074511 | 0.074511 | -2.5968
2009-12-26 | 0.032533 | 0.032533 | -3.4255
2009-12-27 | 0.036379 | 0.036379 | -3.3138
2009-12-28 | 0.10455 | 0.10455 | -2.2581
2009-12-29 | 0.26431 | 0.26431 | -1.3306
2009-12-30 | 0.34854 | 0.34854 | -1.054
2009-12-31 | 2.616 | 2.616 | 0.96165
2010-01-01 | 0.076507 | 0.076507 | -2.5704
2010-01-02 | 0.0082107 | 0.0082107 | -4.8023
2010-01-03 | 0.37621 | 0.37621 | -0.97762
2010-01-04 | 0.088594 | 0.088594 | -2.4237
2010-01-05 | 0.022913 | 0.022913 | -3.7761
2010-01-06 | 0.088734 | 0.088734 | -2.4221
2010-01-07 | 0.0081983 | 0.0081983 | -4.8038
2010-01-08 | 1.2261 | 1.2261 | 0.2038
2010-01-09 | 0.058729 | 0.058729 | -2.8348
2010-01-10 | 0.0087317 | 0.0087317 | -4.7408
2010-01-11 | 3.4421 | 3.4421 | 1.2361
2010-01-12 | 0.20465 | 0.20465 | -1.5865
2010-01-13 | 0.081199 | 0.0047598 | -2.5108
2010-01-14 | 0.060891 | 0.060891 | -2.7987
2010-01-15 | 0.0080684 | 0.0080684 | -4.8198
2010-01-16 | 0.012182 | 0.012182 | -4.4078
2010-01-17 | 0.20849 | 0.20849 | -1.5679
2010-01-18 | 0.079927 | 0.079927 | -2.5266
2010-01-19 | 0.073413 | 0.073413 | -2.6117
2010-01-20 | 0.015411 | 0.015411 | -4.1727
2010-01-21 | 0.24741 | 0.24741 | -1.3967
2010-01-22 | 0.055219 | 0.055219 | -2.8965
2010-01-23 | 0.018366 | 0.018366 | -3.9973
2010-01-24 | 0.0003803 | 0.0003803 | -7.8746
2010-01-25 | 0.012559 | 0.012559 | -4.3773
2010-01-26 | 0.00022496 | 0.00022496 | -8.3996
2010-01-27 | 0.0011457 | 0.0011457 | -6.7718
2010-01-28 | 0.011366 | 0.011366 | -4.4771
2010-01-29 | 0.021522 | 0.021522 | -3.8387
2010-01-30 | 0.10574 | 0.10574 | -2.2467
2010-01-31 | 0.72101 | 0.72101 | -0.3271
2010-02-01 | 0.0158 | 0.0158 | -4.1478
2010-02-02 | 0.058586 | 0.058586 | -2.8373
2010-02-03 | 0.25666 | 0.25666 | -1.36
2010-02-04 | 0.17119 | 0.17119 | -1.765
2010-02-05 | 0.30123 | 0.30123 | -1.1999
2010-02-06 | 0.42759 | 0.42759 | -0.8496
2010-02-07 | 0.11046 | 0.11046 | -2.2031
2010-02-08 | 0.14153 | 0.14153 | -1.9552
2010-02-09 | 0.1744 | 0.1744 | -1.7464
2010-02-10 | 0.03874 | 0.03874 | -3.2509
2010-02-11 | 2.5114 | 2.5114 | 0.92082
2010-02-12 | 0.094169 | 0.094169 | -2.3627
2010-02-13 | 0.60122 | 0.60122 | -0.5088
2010-02-14 | 0.1915 | 0.1915 | -1.6529
2010-02-15 | 0.042501 | 0.042501 | -3.1582
2010-02-16 | 0.1981 | 0.1981 | -1.619
2010-02-17 | 0.040578 | 0.040578 | -3.2045
2010-02-18 | 0.021937 | 0.021937 | -3.8196
2010-02-19 | 0.066419 | 0.066419 | -2.7118
2010-02-20 | 0.052193 | 0.052193 | -2.9528
2010-02-21 | 0.0072524 | 0.0072524 | -4.9264
2010-02-22 | 0.39847 | 0.39847 | -0.92012
2010-02-23 | 0.0039691 | 0.0039691 | -5.5292
2010-02-24 | 0.38357 | 0.38357 | -0.95823
2010-02-25 | 0.086979 | 0.086979 | -2.4421
2010-02-26 | 0.33437 | 0.33437 | -1.0955
2010-02-27 | 0.79737 | 0.79737 | -0.22643
2010-02-28 | 0.0057244 | 0.0057244 | -5.163
2010-03-01 | 0.0018156 | 0.0018156 | -6.3113
2010-03-02 | 0.44738 | 0.44738 | -0.80434
2010-03-03 | 0.38598 | 0.38598 | -0.95198
2010-03-04 | 0.16524 | 0.16524 | -1.8003
2010-03-05 | 0.23743 | 0.23743 | -1.4379
2010-03-06 | 0.72475 | 0.72475 | -0.32193
2010-03-07 | 0.013021 | 0.013021 | -4.3412
2010-03-08 | 0.031738 | 0.031738 | -3.4503
2010-03-09 | 0.036148 | 0.036148 | -3.3201
2010-03-10 | 0.0071072 | 0.0071072 | -4.9467
2010-03-11 | 0.054335 | 0.054335 | -2.9126
2010-03-12 | 0.12395 | 0.12395 | -2.0879
2010-03-13 | 0.19388 | 0.19388 | -1.6405
2010-03-14 | 0.014056 | 0.014056 | -4.2647
2010-03-15 | 0.022068 | 0.022068 | -3.8136
2010-03-16 | 0.084147 | 0.084147 | -2.4752
2010-03-17 | 0.027025 | 0.027025 | -3.611
2010-03-18 | 0.015479 | 0.015479 | -4.1683
2010-03-19 | 0.012213 | 0.012213 | -4.4053
2010-03-20 | 0.042129 | 0.042129 | -3.167
2010-03-21 | 0.015592 | 0.015592 | -4.161
2010-03-22 | 0.14326 | 0.14326 | -1.9431
2010-03-23 | 0.0039042 | 0.0039042 | -5.5457
2010-03-24 | 0.19372 | 0.19372 | -1.6413
2010-03-25 | 0.046894 | 0.046894 | -3.0599
2010-03-26 | 0.0027514 | 0.0027514 | -5.8956
2010-03-27 | 0.0055207 | 0.0055207 | -5.1993
2010-03-28 | 0.015253 | 0.015253 | -4.183
2010-03-29 | 0.019826 | 0.019826 | -3.9208
2010-03-30 | 0.0064404 | 0.0064404 | -5.0452
2010-03-31 | 0.14739 | 0.14739 | -1.9147
2010-04-01 | 0.18301 | 0.18301 | -1.6982
2010-04-02 | 0.010607 | 0.010607 | -4.5462
2010-04-03 | 0.0012736 | 0.0012736 | -6.6659
2010-04-04 | 0.0020299 | 0.0020299 | -6.1998
2010-04-05 | 0.26584 | 0.26584 | -1.3249
2010-04-06 | 0.0027309 | 0.0027309 | -5.9031
2010-04-07 | 0.0047057 | 0.0047057 | -5.359
2010-04-08 | 0.013893 | 0.013893 | -4.2764
2010-04-09 | 0.0013832 | 0.0013832 | -6.5834
2010-04-10 | 0.040866 | 0.040866 | -3.1975
2010-04-11 | 0.79362 | 0.79362 | -0.23115
2010-04-12 | 0.021284 | 0.021284 | -3.8498
2010-04-13 | 0.0064452 | 0.0064452 | -5.0444
2010-04-14 | 0.011633 | 0.011633 | -4.4539
2010-04-15 | 0.0027448 | 0.0027448 | -5.898
2010-04-16 | 0.0025997 | 0.0025997 | -5.9524
2010-04-17 | 0.001934 | 0.001934 | -6.2482
2010-04-18 | 0.0025911 | 0.0025911 | -5.9557
2010-04-19 | 0.0052179 | 0.0052179 | -5.2557
2010-04-20 | 0.95545 | 0.95545 | -0.045578
2010-04-21 | 0.054505 | 0.054505 | -2.9095
2010-04-22 | 0.013712 | 0.013712 | -4.2895
2010-04-23 | 0.3479 | 0.3479 | -1.0558
2010-04-24 | 0.1805 | 0.1805 | -1.712
2010-04-25 | 0.01103 | 0.01103 | -4.5071
2010-04-26 | 0.044932 | 0.044932 | -3.1026
2010-04-27 | 0.010387 | 0.010387 | -4.5672
2010-04-28 | 0.042784 | 0.042784 | -3.1516
2010-04-29 | 0.04085 | 0.04085 | -3.1978
2010-04-30 | 0.12606 | 0.12606 | -2.071
2010-05-01 | 0.19964 | 0.19964 | -1.6113
2010-05-02 | 0.008142 | 0.008142 | -4.8107
2010-05-03 | 0.0025109 | 0.0025109 | -5.9871
2010-05-04 | 0.34406 | 0.34406 | -1.0669
2010-05-05 | 0.044794 | 0.044794 | -3.1057
2010-05-06 | 0.067029 | 0.067029 | -2.7026
2010-05-07 | 0.0091308 | 0.0091308 | -4.6961
2010-05-08 | 0.0069146 | 0.0069146 | -4.9741
2010-05-09 | 0.0014026 | 0.0014026 | -6.5694
2010-05-10 | 0.0037508 | 0.0037508 | -5.5858
2010-05-11 | 0.0066545 | 0.0066545 | -5.0125
2010-05-12 | 0.03538 | 0.03538 | -3.3416
2010-05-13 | 0.0093124 | 0.0093124 | -4.6764
2010-05-14 | 0.0085273 | 0.0085273 | -4.7645
2010-05-15 | 0.33249 | 0.33249 | -1.1012
2010-05-16 | 0.023386 | 0.023386 | -3.7556
2010-05-17 | 0.0055461 | 0.0055461 | -5.1947
2010-05-18 | 0.051401 | 0.051401 | -2.9681
2010-05-19 | 0.030102 | 0.030102 | -3.5032
2010-05-20 | 0.16877 | 0.16877 | -1.7792
2010-05-21 | 0.16981 | 0.16981 | -1.7731
2010-05-22 | 0.16151 | 0.16151 | -1.8232
2010-05-23 | 0.067547 | 0.067547 | -2.6949
2010-05-24 | 0.017428 | 0.017428 | -4.0497
2010-05-25 | 0.09318 | 0.09318 | -2.3732
2010-05-26 | 0.76692 | 0.76692 | -0.26538
2010-05-27 | 0.0017631 | 0.0017631 | -6.3407
2010-05-28 | 0.022831 | 0.022831 | -3.7796
2010-05-29 | 0.23812 | 0.23812 | -1.435
2010-05-30 | 0.36041 | 0.36041 | -1.0205
2010-05-31 | 0.13149 | 0.13149 | -2.0288
2010-06-01 | 0.027059 | 0.027059 | -3.6097
2010-06-02 | 0.019601 | 0.019601 | -3.9322
2010-06-03 | 0.20863 | 0.20863 | -1.5672
2010-06-04 | 0.16347 | 0.16347 | -1.8111
2010-06-05 | 0.173 | 0.173 | -1.7545
2010-06-06 | 0.88262 | 0.88262 | -0.12486
2010-06-07 | 0.041182 | 0.041182 | -3.1897
2010-06-08 | 0.32634 | 0.32634 | -1.1198
2010-06-09 | 0.52397 | 0.52397 | -0.64633
2010-06-10 | 0.037907 | 0.037907 | -3.2726
2010-06-11 | 0.28586 | 0.28586 | -1.2523
2010-06-12 | 0.023996 | 0.023996 | -3.7299
2010-06-13 | 0.04789 | 0.04789 | -3.0388
2010-06-14 | 0.0078351 | 0.0078351 | -4.8491
2010-06-15 | 0.033809 | 0.033809 | -3.387
2010-06-16 | 0.073081 | 0.073081 | -2.6162
2010-06-17 | 2.1208 | 2.1208 | 0.75178
2010-06-18 | 0.016362 | 0.016362 | -4.1128
2010-06-19 | 0.0056576 | 0.0056576 | -5.1748
2010-06-20 | 0.14655 | 0.14655 | -1.9204
2010-06-21 | 0.17857 | 0.17857 | -1.7227
2010-06-22 | 0.048469 | 0.048469 | -3.0268
2010-06-23 | 0.018094 | 0.018094 | -4.0122
2010-06-24 | 0.11629 | 0.11629 | -2.1517
2010-06-25 | 0.051451 | 0.051451 | -2.9671
2010-06-26 | 0.0043808 | 0.0043808 | -5.4305
2010-06-27 | 0.041549 | 0.041549 | -3.1809
2010-06-28 | 0.32033 | 0.32033 | -1.1384
2010-06-29 | 0.248 | 0.248 | -1.3943
2010-06-30 | 0.030348 | 0.030348 | -3.495
2010-07-01 | 0.014917 | 0.014917 | -4.2052
2010-07-02 | 0.01867 | 0.01867 | -3.9808
2010-07-03 | 0.0035964 | 0.0035964 | -5.6278
2010-07-04 | 0.018361 | 0.018361 | -3.9975
2010-07-05 | 0.056468 | 0.056468 | -2.8741
2010-07-06 | 0.017261 | 0.017261 | -4.0593
2010-07-07 | 0.018764 | 0.018764 | -3.9758
2010-07-08 | 0.02743 | 0.02743 | -3.5961
2010-07-09 | 0.0090735 | 0.0090735 | -4.7024
2010-07-10 | 0.42155 | 0.42155 | -0.86381
2010-07-11 | 0.00063243 | 0.00063243 | -7.3659
2010-07-12 | 0.22747 | 0.22747 | -1.4807
2010-07-13 | 0.0056729 | 0.0056729 | -5.172
2010-07-14 | 0.14836 | 0.14836 | -1.9081
2010-07-15 | 0.17725 | 0.17725 | -1.7302
2010-07-16 | 0.089476 | 0.089476 | -2.4138
2010-07-17 | 0.071642 | 0.071642 | -2.6361
2010-07-18 | 0.030703 | 0.030703 | -3.4834
2010-07-19 | 0.019574 | 0.019574 | -3.9335
2010-07-20 | 0.026075 | 0.026075 | -3.6468
2010-07-21 | 0.11186 | 0.11186 | -2.1905
2010-07-22 | 0.087053 | 0.087053 | -2.4412
2010-07-23 | 0.045845 | 0.045845 | -3.0825
2010-07-24 | 0.0065693 | 0.0065693 | -5.0254
2010-07-25 | 0.080622 | 0.080622 | -2.518
2010-07-26 | 0.035158 | 0.035158 | -3.3479
2010-07-27 | 0.18091 | 0.18091 | -1.7098
2010-07-28 | 0.3921 | 0.3921 | -0.93625
2010-07-29 | 0.0023999 | 0.0023999 | -6.0323
2010-07-30 | 0.0092267 | 0.0092267 | -4.6857
2010-07-31 | 0.023994 | 0.023994 | -3.73
2010-08-01 | 0.44748 | 0.44748 | -0.80412
2010-08-02 | 0.65253 | 0.65253 | -0.42689
2010-08-03 | 0.0030839 | 0.0030839 | -5.7816
2010-08-04 | 0.24014 | 0.24014 | -1.4265
2010-08-05 | 0.0047384 | 0.0047384 | -5.3521
2010-08-06 | 0.043061 | 0.043061 | -3.1451
2010-08-07 | 0.078072 | 0.078072 | -2.5501
2010-08-08 | 0.35433 | 0.35433 | -1.0375
2010-08-09 | 0.029738 | 0.029738 | -3.5153
2010-08-10 | 0.042378 | 0.042378 | -3.1611
2010-08-11 | 0.048571 | 0.048571 | -3.0247
2010-08-12 | 1.7429 | 1.7429 | 0.55557
2010-08-13 | 0.0025565 | 0.0025565 | -5.9691
2010-08-14 | 1.0412 | 1.0412 | 0.040408
2010-08-15 | 0.011693 | 0.011693 | -4.4487
2010-08-16 | 0.041973 | 0.041973 | -3.1707
2010-08-17 | 0.027301 | 0.027301 | -3.6008
2010-08-18 | 0.12474 | 0.12474 | -2.0815
2010-08-19 | 0.010944 | 0.010944 | -4.5149
2010-08-20 | 0.0040505 | 0.0040505 | -5.5089
2010-08-21 | 0.0066297 | 0.0066297 | -5.0162
2010-08-22 | 0.0078691 | 0.0078691 | -4.8448
2010-08-23 | 0.015959 | 0.015959 | -4.1377
2010-08-24 | 0.026727 | 0.026727 | -3.6221
2010-08-25 | 0.030797 | 0.030797 | -3.4803
2010-08-26 | 0.012777 | 0.012777 | -4.3601
2010-08-27 | 0.32751 | 0.32751 | -1.1162
2010-08-28 | 0.0031383 | 0.0031383 | -5.7641
2010-08-29 | 0.0021853 | 0.0021853 | -6.126
2010-08-30 | 0.21988 | 0.21988 | -1.5147
2010-08-31 | 0.11528 | 0.11528 | -2.1604
2010-09-01 | 0.032182 | 0.032182 | -3.4364
2010-09-02 | 0.0025431 | 0.0025431 | -5.9744
2010-09-03 | 0.0058349 | 0.0058349 | -5.1439
2010-09-04 | 0.0043766 | 0.0043766 | -5.4315
2010-09-05 | 23.5877 | 23.5877 | 3.1607
2010-09-06 | 0.49354 | 0.49354 | -0.70615
2010-09-07 | 0.095926 | 0.095926 | -2.3442
2010-09-08 | 0.021974 | 0.021974 | -3.8179
2010-09-09 | 0.057195 | 0.057195 | -2.8613
2010-09-10 | 0.0056183 | 0.0056183 | -5.1817
2010-09-11 | 0.0045589 | 0.0045589 | -5.3907
2010-09-12 | 0.011063 | 0.011063 | -4.5041
2010-09-13 | 0.55253 | 0.55253 | -0.59324
2010-09-14 | 0.30776 | 0.30776 | -1.1784
2010-09-15 | 0.031097 | 0.031097 | -3.4707
2010-09-16 | 0.04685 | 0.04685 | -3.0608
2010-09-17 | 0.11187 | 0.11187 | -2.1904
2010-09-18 | 0.0078277 | 0.0078277 | -4.8501
2010-09-19 | 0.0076394 | 0.0076394 | -4.8744
2010-09-20 | 0.022331 | 0.022331 | -3.8018
2010-09-21 | 0.1746 | 0.1746 | -1.7452
2010-09-22 | 0.014895 | 0.014895 | -4.2067
2010-09-23 | 0.0020096 | 0.0020096 | -6.2098
2010-09-24 | 0.0028733 | 0.0028733 | -5.8523
2010-09-25 | 0.37447 | 0.37447 | -0.98225
2010-09-26 | 0.1833 | 0.1833 | -1.6966
2010-09-27 | 0.012447 | 0.012447 | -4.3863
2010-09-28 | 0.028339 | 0.028339 | -3.5635
2010-09-29 | 0.056753 | 0.056753 | -2.869
2010-09-30 | 0.0029641 | 0.0029641 | -5.8212
2010-10-01 | 0.012813 | 0.012813 | -4.3573
2010-10-02 | 0.16632 | 0.16632 | -1.7939
2010-10-03 | 0.083263 | 0.083263 | -2.4858
2010-10-04 | 0.013636 | 0.013636 | -4.295
2010-10-05 | 0.010696 | 0.010696 | -4.5379
2010-10-06 | 0.23597 | 0.23597 | -1.4441
2010-10-07 | 0.1282 | 0.1282 | -2.0541
2010-10-08 | 0.033733 | 0.033733 | -3.3893
2010-10-09 | 0.0081448 | 0.0081448 | -4.8104
2010-10-10 | 0.0078158 | 0.0078158 | -4.8516
2010-10-11 | 0.063447 | 0.063447 | -2.7576
2010-10-12 | 0.11049 | 0.11049 | -2.2028
2010-10-13 | 0.10627 | 0.10627 | -2.2418
2010-10-14 | 0.0026925 | 0.0026925 | -5.9173
2010-10-15 | 0.39204 | 0.39204 | -0.93639
2010-10-16 | 0.053941 | 0.053941 | -2.9199
2010-10-17 | 0.10385 | 0.10385 | -2.2648
2010-10-18 | 0.165 | 0.165 | -1.8018
2010-10-19 | 0.001114 | 0.001114 | -6.7998
2010-10-20 | 0.081092 | 0.081092 | -2.5122
2010-10-21 | 0.16451 | 0.16451 | -1.8048
2010-10-22 | 0.089549 | 0.089549 | -2.413
2010-10-23 | 0.18893 | 0.18893 | -1.6664
2010-10-24 | 0.0042363 | 0.0042363 | -5.4641
2010-10-25 | 0.0028059 | 0.0028059 | -5.876
2010-10-26 | 0.0028097 | 0.0028097 | -5.8747
2010-10-27 | 0.056565 | 0.056565 | -2.8724
2010-10-28 | 0.049856 | 0.049856 | -2.9986
2010-10-29 | 0.075 | 0.075 | -2.5903
2010-10-30 | 1.0821 | 1.0821 | 0.078935
2010-10-31 | 0.31376 | 0.31376 | -1.1591
2010-11-01 | 0.017773 | 0.017773 | -4.0301
2010-11-02 | 0.010492 | 0.010492 | -4.5572
2010-11-03 | 0.043107 | 0.043107 | -3.1441
2010-11-04 | 0.25936 | 0.25936 | -1.3496
2010-11-05 | 0.21361 | 0.21361 | -1.5436
2010-11-06 | 0.0075555 | 0.0075555 | -4.8855
2010-11-07 | 0.019458 | 0.019458 | -3.9395
2010-11-08 | 0.1273 | 0.1273 | -2.0612
2010-11-09 | 0.24062 | 0.24062 | -1.4246
2010-11-10 | 0.1624 | 0.1624 | -1.8177
2010-11-11 | 0.1014 | 0.1014 | -2.2887
2010-11-12 | 1.6956 | 1.6956 | 0.52803
2010-11-13 | 0.060154 | 0.060154 | -2.8108
2010-11-14 | 0.023836 | 0.023836 | -3.7366
2010-11-15 | 0.029087 | 0.029087 | -3.5375
2010-11-16 | 0.0025963 | 0.0025963 | -5.9537
2010-11-17 | 0.14808 | 0.14808 | -1.91
2010-11-18 | 0.041598 | 0.041598 | -3.1797
2010-11-19 | 0.0035914 | 0.0035914 | -5.6292
2010-11-20 | 0.012315 | 0.012315 | -4.397
2010-11-21 | 0.040121 | 0.040121 | -3.2159
2010-11-22 | 0.40867 | 0.40867 | -0.89484
2010-11-23 | 0.053046 | 0.053046 | -2.9366
2010-11-24 | 0.030722 | 0.030722 | -3.4828
2010-11-25 | 0.18081 | 0.18081 | -1.7103
2010-11-26 | 0.018689 | 0.018689 | -3.9798
2010-11-27 | 0.11582 | 0.11582 | -2.1557
2010-11-28 | 0.011787 | 0.011787 | -4.4407
2010-11-29 | 0.041073 | 0.041073 | -3.1924
2010-11-30 | 0.13954 | 0.13954 | -1.9694
2010-12-01 | 0.065913 | 0.065913 | -2.7194
2010-12-02 | 1.8352 | 1.8352 | 0.60716
2010-12-03 | 1.1802 | 1.1802 | 0.16568
2010-12-04 | 0.31358 | 0.31358 | -1.1597
2010-12-05 | 0.10797 | 0.10797 | -2.2259
2010-12-06 | 0.0073052 | 0.0073052 | -4.9192
2010-12-07 | 0.0085575 | 0.0085575 | -4.7609
2010-12-08 | 0.14604 | 0.14604 | -1.9239
2010-12-09 | 0.0091223 | 0.0091223 | -4.697
2010-12-10 | 0.013521 | 0.013521 | -4.3035
2010-12-11 | 0.089688 | 0.089688 | -2.4114
2010-12-12 | 0.26452 | 0.26452 | -1.3298
2010-12-13 | 0.086076 | 0.086076 | -2.4525
2010-12-14 | 0.0042159 | 0.0042159 | -5.4689
2010-12-15 | 0.0077928 | 0.0077928 | -4.8546
2010-12-16 | 0.0035159 | 0.0035159 | -5.6505
2010-12-17 | 0.28734 | 0.28734 | -1.2471
2010-12-18 | 0.065281 | 0.065281 | -2.7291
2010-12-19 | 0.39441 | 0.39441 | -0.93036
2010-12-20 | 0.44394 | 0.44394 | -0.81207
2010-12-21 | 0.0044484 | 0.0044484 | -5.4152
2010-12-22 | 0.0073188 | 0.0073188 | -4.9173
2010-12-23 | 0.0025052 | 0.0025052 | -5.9894
2010-12-24 | 0.13274 | 0.13274 | -2.0193
2010-12-25 | 0.0036535 | 0.0036535 | -5.6121
2010-12-26 | 0.042694 | 0.042694 | -3.1537
2010-12-27 | 0.012026 | 0.012026 | -4.4207
2010-12-28 | 0.10144 | 0.10144 | -2.2883
2010-12-29 | 0.047387 | 0.047387 | -3.0494
2010-12-30 | 0.32968 | 0.32968 | -1.1096
2010-12-31 | 0.9745 | 0.9745 | -0.025827
2011-01-01 | 0.33689 | 0.33689 | -1.088
2011-01-02 | 0.011058 | 0.011058 | -4.5046
2011-01-03 | 0.12321 | 0.12321 | -2.0939
2011-01-04 | 0.16704 | 0.16704 | -1.7895
2011-01-05 | 0.0025561 | 0.0025561 | -5.9693
2011-01-06 | 0.001788 | 0.001788 | -6.3267
2011-01-07 | 0.18639 | 0.18639 | -1.6799
2011-01-08 | 0.058479 | 0.058479 | -2.8391
2011-01-09 | 0.46833 | 0.46833 | -0.75858
2011-01-10 | 0.024497 | 0.024497 | -3.7092
2011-01-11 | 0.24507 | 0.24507 | -1.4062
2011-01-12 | 0.28215 | 0.28215 | -1.2653
2011-01-13 | 0.52703 | 0.52703 | -0.6405
2011-01-14 | 0.51835 | 0.51835 | -0.65711
2011-01-15 | 0.020336 | 0.020336 | -3.8953
2011-01-16 | 0.035118 | 0.035118 | -3.349
2011-01-17 | 0.023788 | 0.023788 | -3.7386
2011-01-18 | 0.020465 | 0.020465 | -3.8891
2011-01-19 | 0.039983 | 0.039983 | -3.2193
2011-01-20 | 0.034409 | 0.034409 | -3.3694
2011-01-21 | 0.45834 | 0.45834 | -0.78015
2011-01-22 | 0.0056764 | 0.0056764 | -5.1714
2011-01-23 | 0.0065656 | 0.0065656 | -5.0259
2011-01-24 | 0.17822 | 0.17822 | -1.7247
2011-01-25 | 0.066132 | 0.066132 | -2.7161
2011-01-26 | 0.21386 | 0.21386 | -1.5424
2011-01-27 | 0.03002 | 0.03002 | -3.5059
2011-01-28 | 0.0084786 | 0.0084786 | -4.7702
2011-01-29 | 0.0077445 | 0.0077445 | -4.8608
2011-01-30 | 0.24956 | 0.24956 | -1.388
2011-01-31 | 0.029318 | 0.029318 | -3.5296
2011-02-01 | 0.818 | 0.818 | -0.20089
2011-02-02 | 0.57881 | 0.57881 | -0.54677
2011-02-03 | 1.3616 | 1.3616 | 0.3087
2011-02-04 | 1.438 | 1.438 | 0.36329
2011-02-05 | 0.64373 | 0.64373 | -0.44048
2011-02-06 | 0.034579 | 0.034579 | -3.3645
2011-02-07 | 0.015674 | 0.015674 | -4.1558
2011-02-08 | 0.004359 | 0.004359 | -5.4355
2011-02-09 | 0.037576 | 0.037576 | -3.2814
2011-02-10 | 0.0086317 | 0.0086317 | -4.7523
2011-02-11 | 0.027123 | 0.027123 | -3.6074
2011-02-12 | 0.17153 | 0.17153 | -1.763
2011-02-13 | 0.025642 | 0.025642 | -3.6635
2011-02-14 | 0.009378 | 0.009378 | -4.6694
2011-02-15 | 0.26269 | 0.26269 | -1.3368
2011-02-16 | 0.14841 | 0.14841 | -1.9077
2011-02-17 | 0.013453 | 0.013453 | -4.3085
2011-02-18 | 0.15734 | 0.15734 | -1.8493
2011-02-19 | 0.63119 | 0.63119 | -0.46014
2011-02-20 | 0.053586 | 0.053586 | -2.9265
2011-02-21 | 0.020434 | 0.020434 | -3.8906
2011-02-22 | 0.086806 | 0.086806 | -2.4441
2011-02-23 | 0.43852 | 0.43852 | -0.82436
2011-02-24 | 0.016618 | 0.016618 | -4.0973
2011-02-25 | 0.0068251 | 0.0068251 | -4.9872
2011-02-26 | 0.5674 | 0.5674 | -0.56668
2011-02-27 | 0.25321 | 0.25321 | -1.3735
2011-02-28 | 0.015633 | 0.015633 | -4.1584
2011-03-01 | 0.03164 | 0.03164 | -3.4533
2011-03-02 | 0.022071 | 0.022071 | -3.8135
2011-03-03 | 0.019918 | 0.019918 | -3.9161
2011-03-04 | 0.0021923 | 0.0021923 | -6.1228
2011-03-05 | 0.010485 | 0.010485 | -4.5578
2011-03-06 | 0.047202 | 0.047202 | -3.0533
2011-03-07 | 0.090113 | 0.090113 | -2.4067
2011-03-08 | 0.089406 | 0.089406 | -2.4146
2011-03-09 | 0.0078824 | 0.0078824 | -4.8431
2011-03-10 | 0.037301 | 0.037301 | -3.2887
2011-03-11 | 0.055451 | 0.055451 | -2.8923
2011-03-12 | 0.024751 | 0.024751 | -3.6989
2011-03-13 | 0.14737 | 0.14737 | -1.9148
2011-03-14 | 0.040175 | 0.040175 | -3.2145
2011-03-15 | 0.055632 | 0.055632 | -2.889
2011-03-16 | 0.21566 | 0.21566 | -1.5341
2011-03-17 | 0.025395 | 0.025395 | -3.6732
2011-03-18 | 0.027933 | 0.027933 | -3.5779
2011-03-19 | 0.037524 | 0.037524 | -3.2828
2011-03-20 | 0.0030649 | 0.0030649 | -5.7878
2011-03-21 | 0.0063117 | 0.0063117 | -5.0653
2011-03-22 | 0.066467 | 0.066467 | -2.7111
2011-03-23 | 0.15894 | 0.15894 | -1.8392
2011-03-24 | 0.14659 | 0.14659 | -1.9201
2011-03-25 | 0.57902 | 0.57902 | -0.54642
2011-03-26 | 0.018765 | 0.018765 | -3.9758
2011-03-27 | 0.038922 | 0.038922 | -3.2462
2011-03-28 | 0.0069977 | 0.0069977 | -4.9622
2011-03-29 | 0.31407 | 0.31407 | -1.1581
2011-03-30 | 0.14043 | 0.14043 | -1.963
2011-03-31 | 0.0066307 | 0.0066307 | -5.016
2011-04-01 | 0.073118 | 0.073118 | -2.6157
2011-04-02 | 0.0056109 | 0.0056109 | -5.183
2011-04-03 | 0.014577 | 0.014577 | -4.2283
2011-04-04 | 0.001286 | 0.001286 | -6.6562
2011-04-05 | 0.21483 | 0.21483 | -1.5379
2011-04-06 | 0.0019778 | 0.0019778 | -6.2258
2011-04-07 | 0.031242 | 0.031242 | -3.466
2011-04-08 | 0.12791 | 0.12791 | -2.0564
2011-04-09 | 0.1846 | 0.1846 | -1.6896
2011-04-10 | 0.025202 | 0.025202 | -3.6808
2011-04-11 | 0.21626 | 0.21626 | -1.5313
2011-04-12 | 0.19705 | 0.19705 | -1.6243
2011-04-13 | 0.22623 | 0.22623 | -1.4862
2011-04-14 | 0.039213 | 0.039213 | -3.2387
2011-04-15 | 0.036371 | 0.036371 | -3.314
2011-04-16 | 0.011972 | 0.011972 | -4.4252
2011-04-17 | 0.069188 | 0.069188 | -2.6709
2011-04-18 | 0.0075886 | 0.0075886 | -4.8811
2011-04-19 | 0.0023944 | 0.0023944 | -6.0346
2011-04-20 | 0.028106 | 0.028106 | -3.5718
2011-04-21 | 0.099305 | 0.099305 | -2.3096
2011-04-22 | 0.0033958 | 0.0033958 | -5.6852
2011-04-23 | 0.12956 | 0.12956 | -2.0436
2011-04-24 | 0.012808 | 0.012808 | -4.3577
2011-04-25 | 0.0073496 | 0.0073496 | -4.9131
2011-04-26 | 0.043314 | 0.043314 | -3.1393
2011-04-27 | 0.0036953 | 0.0036953 | -5.6007
2011-04-28 | 0.10811 | 0.10811 | -2.2246
2011-04-29 | 0.0014291 | 0.0014291 | -6.5507
2011-04-30 | 0.26012 | 0.26012 | -1.3466
2011-05-01 | 0.24419 | 0.24419 | -1.4098
2011-05-02 | 0.13659 | 0.13659 | -1.9908
2011-05-03 | 0.0041871 | 0.0041871 | -5.4757
2011-05-04 | 0.049948 | 0.049948 | -2.9968
2011-05-05 | 0.02374 | 0.02374 | -3.7406
2011-05-06 | 0.1021 | 0.1021 | -2.2818
2011-05-07 | 0.22741 | 0.22741 | -1.481
2011-05-08 | 0.0024206 | 0.0024206 | -6.0238
2011-05-09 | 0.0073334 | 0.0073334 | -4.9153
2011-05-10 | 0.04581 | 0.04581 | -3.0833
2011-05-11 | 0.40694 | 0.40694 | -0.8991
2011-05-12 | 0.59571 | 0.59571 | -0.51801
2011-05-13 | 0.81423 | 0.81423 | -0.20551
2011-05-14 | 0.10331 | 0.10331 | -2.27
2011-05-15 | 0.0029269 | 0.0029269 | -5.8338
2011-05-16 | 0.25159 | 0.25159 | -1.3799
2011-05-17 | 0.013759 | 0.013759 | -4.2861
2011-05-18 | 0.25828 | 0.25828 | -1.3537
2011-05-19 | 0.006291 | 0.006291 | -5.0686
2011-05-20 | 0.0078786 | 0.0078786 | -4.8436
2011-05-21 | 0.07656 | 0.07656 | -2.5697
2011-05-22 | 0.12701 | 0.12701 | -2.0635
2011-05-23 | 0.0032436 | 0.0032436 | -5.7311
2011-05-24 | 0.0077484 | 0.0077484 | -4.8603
2011-05-25 | 0.015526 | 0.015526 | -4.1652
2011-05-26 | 0.016637 | 0.016637 | -4.0961
2011-05-27 | 0.034073 | 0.034073 | -3.3792
2011-05-28 | 0.20649 | 0.20649 | -1.5775
2011-05-29 | 0.0031399 | 0.0031399 | -5.7636
2011-05-30 | 0.032706 | 0.032706 | -3.4202
2011-05-31 | 0.05269 | 0.05269 | -2.9433
2011-06-01 | 0.072257 | 0.072257 | -2.6275
2011-06-02 | 0.027783 | 0.027783 | -3.5833
2011-06-03 | 0.031113 | 0.031113 | -3.4701
2011-06-04 | 0.97869 | 0.97869 | -0.021537
2011-06-05 | 0.089037 | 0.089037 | -2.4187
2011-06-06 | 0.060381 | 0.060381 | -2.8071
2011-06-07 | 0.63739 | 0.63739 | -0.45037
2011-06-08 | 0.13943 | 0.13943 | -1.9702
2011-06-09 | 0.0096555 | 0.0096555 | -4.6402
2011-06-10 | 0.0021869 | 0.0021869 | -6.1253
2011-06-11 | 0.003876 | 0.003876 | -5.5529
2011-06-12 | 0.0090154 | 0.0090154 | -4.7088
2011-06-13 | 0.0020587 | 0.0020587 | -6.1857
2011-06-14 | 0.017009 | 0.017009 | -4.074
2011-06-15 | 0.015592 | 0.015592 | -4.161
2011-06-16 | 0.0093167 | 0.0093167 | -4.6759
2011-06-17 | 0.21625 | 0.21625 | -1.5313
2011-06-18 | 0.025375 | 0.025375 | -3.674
2011-06-19 | 0.13016 | 0.13016 | -2.039
2011-06-20 | 2.229 | 2.229 | 0.80157
2011-06-21 | 0.97542 | 0.97542 | -0.024885
2011-06-22 | 0.021578 | 0.021578 | -3.8361
2011-06-23 | 0.021933 | 0.021933 | -3.8198
2011-06-24 | 0.003131 | 0.003131 | -5.7664
2011-06-25 | 0.10728 | 0.10728 | -2.2324
2011-06-26 | 0.23218 | 0.23218 | -1.4602
2011-06-27 | 0.0019346 | 0.0019346 | -6.2479
2011-06-28 | 0.033234 | 0.033234 | -3.4042
2011-06-29 | 0.004638 | 0.004638 | -5.3735
2011-06-30 | 0.034673 | 0.034673 | -3.3618
2011-07-01 | 0.023176 | 0.023176 | -3.7646
2011-07-02 | 0.017636 | 0.017636 | -4.0378
2011-07-03 | 0.033414 | 0.033414 | -3.3988
2011-07-04 | 0.039833 | 0.039833 | -3.2231
2011-07-05 | 0.32166 | 0.32166 | -1.1342
2011-07-06 | 0.017775 | 0.017775 | -4.03
2011-07-07 | 0.90134 | 0.90134 | -0.10388
2011-07-08 | 0.15688 | 0.15688 | -1.8523
2011-07-09 | 0.0036271 | 0.0036271 | -5.6193
2011-07-10 | 0.50657 | 0.50657 | -0.68008
2011-07-11 | 0.087317 | 0.087317 | -2.4382
2011-07-12 | 0.028073 | 0.028073 | -3.5729
2011-07-13 | 0.35496 | 0.35496 | -1.0358
2011-07-14 | 0.2234 | 0.2234 | -1.4988
2011-07-15 | 0.010294 | 0.010294 | -4.5762
2011-07-16 | 0.049156 | 0.049156 | -3.0128
2011-07-17 | 0.0052525 | 0.0052525 | -5.2491
2011-07-18 | 0.042214 | 0.042214 | -3.165
2011-07-19 | 0.071192 | 0.071192 | -2.6424
2011-07-20 | 0.011195 | 0.011195 | -4.4923
2011-07-21 | 0.082549 | 0.082549 | -2.4944
2011-07-22 | 0.0035042 | 0.0035042 | -5.6538
2011-07-23 | 0.006775 | 0.006775 | -4.9945
2011-07-24 | 0.018065 | 0.018065 | -4.0138
2011-07-25 | 0.16361 | 0.16361 | -1.8103
2011-07-26 | 0.016738 | 0.016738 | -4.0901
2011-07-27 | 0.012324 | 0.012324 | -4.3962
2011-07-28 | 0.41536 | 0.41536 | -0.87862
2011-07-29 | 0.069634 | 0.069634 | -2.6645
2011-07-30 | 0.30925 | 0.30925 | -1.1736
2011-07-31 | 0.0024082 | 0.0024082 | -6.0289
2011-08-01 | 0.021385 | 0.021385 | -3.8451
2011-08-02 | 0.031426 | 0.031426 | -3.4601
2011-08-03 | 0.12372 | 0.12372 | -2.0897
2011-08-04 | 0.89836 | 0.89836 | -0.10719
2011-08-05 | 0.0021315 | 0.0021315 | -6.1509
2011-08-06 | 0.080837 | 0.080837 | -2.5153
2011-08-07 | 0.22607 | 0.22607 | -1.4869
2011-08-08 | 0.059145 | 0.059145 | -2.8278
2011-08-09 | 0.050271 | 0.050271 | -2.9903
2011-08-10 | 0.1375 | 0.1375 | -1.9841
2011-08-11 | 0.020713 | 0.020713 | -3.877
2011-08-12 | 0.1077 | 0.1077 | -2.2284
2011-08-13 | 0.047733 | 0.047733 | -3.0421
2011-08-14 | 0.11308 | 0.11308 | -2.1797
2011-08-15 | 0.008862 | 0.008862 | -4.726
2011-08-16 | 0.032011 | 0.032011 | -3.4417
2011-08-17 | 0.026758 | 0.026758 | -3.6209
2011-08-18 | 0.0017536 | 0.0017536 | -6.3461
2011-08-19 | 0.21106 | 0.21106 | -1.5556
2011-08-20 | 0.073573 | 0.073573 | -2.6095
2011-08-21 | 0.0076046 | 0.0076046 | -4.879
2011-08-22 | 0.077532 | 0.077532 | -2.5571
2011-08-23 | 0.20509 | 0.20509 | -1.5843
2011-08-24 | 0.068266 | 0.068266 | -2.6843
2011-08-25 | 0.012767 | 0.012767 | -4.3609
2011-08-26 | 0.13628 | 0.13628 | -1.9931
2011-08-27 | 0.07408 | 0.07408 | -2.6026
2011-08-28 | 0.0011423 | 0.0011423 | -6.7747
2011-08-29 | 0.015214 | 0.015214 | -4.1856
2011-08-30 | 0.001916 | 0.001916 | -6.2575
2011-08-31 | 0.072701 | 0.072701 | -2.6214
2011-09-01 | 0.0097984 | 0.0097984 | -4.6255
2011-09-02 | 0.012169 | 0.012169 | -4.4089
2011-09-03 | 0.14951 | 0.14951 | -1.9004
2011-09-04 | 0.3694 | 0.3694 | -0.99588
2011-09-05 | 0.021909 | 0.021909 | -3.8209
2011-09-06 | 1.1267 | 1.1267 | 0.11928
2011-09-07 | 0.0018417 | 0.0018417 | -6.2971
2011-09-08 | 0.0012065 | 0.0012065 | -6.72
2011-09-09 | 0.023337 | 0.023337 | -3.7577
2011-09-10 | 0.020219 | 0.020219 | -3.9011
2011-09-11 | 0.12638 | 0.12638 | -2.0684
2011-09-12 | 0.014483 | 0.014483 | -4.2348
2011-09-13 | 0.0079171 | 0.0079171 | -4.8387
2011-09-14 | 0.0042253 | 0.0042253 | -5.4667
2011-09-15 | 0.0062223 | 0.0062223 | -5.0796
2011-09-16 | 0.16363 | 0.16363 | -1.8101
2011-09-17 | 0.077296 | 0.077296 | -2.5601
2011-09-18 | 0.0062446 | 0.0062446 | -5.076
2011-09-19 | 0.17604 | 0.17604 | -1.737
2011-09-20 | 0.10687 | 0.10687 | -2.2362
2011-09-21 | 0.0047969 | 0.0047969 | -5.3398
2011-09-22 | 0.16522 | 0.16522 | -1.8005
2011-09-23 | 0.037148 | 0.037148 | -3.2928
2011-09-24 | 0.0012112 | 0.0012112 | -6.7162
2011-09-25 | 0.013796 | 0.013796 | -4.2834
2011-09-26 | 0.07594 | 0.07594 | -2.5778
2011-09-27 | 0.012217 | 0.012217 | -4.405
2011-09-28 | 4.708 | 4.708 | 1.5493
2011-09-29 | 2.1993 | 2.1993 | 0.78815
2011-09-30 | 0.12424 | 0.12424 | -2.0856
2011-10-01 | 0.0047284 | 0.0047284 | -5.3542
2011-10-02 | 0.0092764 | 0.0092764 | -4.6803
2011-10-03 | 0.017086 | 0.017086 | -4.0695
2011-10-04 | 0.040883 | 0.040883 | -3.197
2011-10-05 | 0.012379 | 0.012379 | -4.3917
2011-10-06 | 0.38105 | 0.38105 | -0.96483
2011-10-07 | 0.0024483 | 0.0024483 | -6.0124
2011-10-08 | 0.0041558 | 0.0041558 | -5.4832
2011-10-09 | 0.19451 | 0.19451 | -1.6373
2011-10-10 | 0.029777 | 0.029777 | -3.514
2011-10-11 | 0.91699 | 0.91699 | -0.086661
2011-10-12 | 0.24772 | 0.24772 | -1.3954
2011-10-13 | 0.10122 | 0.10122 | -2.2905
2011-10-14 | 0.01742 | 0.01742 | -4.0501
2011-10-15 | 0.10837 | 0.10837 | -2.2222
2011-10-16 | 0.049379 | 0.049379 | -3.0082
2011-10-17 | 0.041181 | 0.041181 | -3.1898
2011-10-18 | 0.0051942 | 0.0051942 | -5.2602
2011-10-19 | 0.10621 | 0.10621 | -2.2424
2011-10-20 | 0.12556 | 0.12556 | -2.075
2011-10-21 | 0.062555 | 0.062555 | -2.7717
2011-10-22 | 0.0011482 | 0.0011482 | -6.7696
2011-10-23 | 0.0079238 | 0.0079238 | -4.8379
2011-10-24 | 0.28022 | 0.28022 | -1.2722
2011-10-25 | 0.017667 | 0.017667 | -4.0361
2011-10-26 | 0.0018754 | 0.0018754 | -6.279
2011-10-27 | 0.0043887 | 0.0043887 | -5.4287
2011-10-28 | 0.056419 | 0.056419 | -2.875
2011-10-29 | 0.39779 | 0.39779 | -0.92183
2011-10-30 | 0.061725 | 0.061725 | -2.7851
2011-10-31 | 0.016637 | 0.016637 | -4.0961
2011-11-01 | 0.04178 | 0.04178 | -3.1753
2011-11-02 | 0.0025269 | 0.0025269 | -5.9808
2011-11-03 | 0.057583 | 0.057583 | -2.8545
2011-11-04 | 0.16647 | 0.16647 | -1.7929
2011-11-05 | 0.14836 | 0.14836 | -1.9081
2011-11-06 | 0.036958 | 0.036958 | -3.298
2011-11-07 | 0.010118 | 0.010118 | -4.5934
2011-11-08 | 0.20927 | 0.20927 | -1.5641
2011-11-09 | 0.46842 | 0.46842 | -0.75839
2011-11-10 | 0.09296 | 0.09296 | -2.3756
2011-11-11 | 0.087108 | 0.087108 | -2.4406
2011-11-12 | 0.031564 | 0.031564 | -3.4558
2011-11-13 | 0.0044656 | 0.0044656 | -5.4113
2011-11-14 | 0.059289 | 0.059289 | -2.8253
2011-11-15 | 0.0021178 | 0.0021178 | -6.1574
2011-11-16 | 0.21134 | 0.21134 | -1.5543
2011-11-17 | 0.038297 | 0.038297 | -3.2624
2011-11-18 | 0.55638 | 0.55638 | -0.5863
2011-11-19 | 0.17432 | 0.17432 | -1.7468
2011-11-20 | 0.62008 | 0.62008 | -0.4779
2011-11-21 | 0.027951 | 0.027951 | -3.5773
2011-11-22 | 0.085168 | 0.085168 | -2.4631
2011-11-23 | 0.0073238 | 0.0073238 | -4.9166
2011-11-24 | 0.010395 | 0.010395 | -4.5664
2011-11-25 | 0.0020529 | 0.0020529 | -6.1885
2011-11-26 | 0.29458 | 0.29458 | -1.2222
2011-11-27 | 0.79754 | 0.79754 | -0.22622
2011-11-28 | 0.080052 | 0.080052 | -2.5251
2011-11-29 | 0.038311 | 0.038311 | -3.262
2011-11-30 | 0.12685 | 0.12685 | -2.0647
2011-12-01 | 0.0024862 | 0.0024862 | -5.997
2011-12-02 | 0.01767 | 0.01767 | -4.0359
2011-12-03 | 0.2353 | 0.2353 | -1.4469
2011-12-04 | 0.0065114 | 0.0065114 | -5.0342
2011-12-05 | 0.0079213 | 0.0079213 | -4.8382
2011-12-06 | 0.1467 | 0.1467 | -1.9193
2011-12-07 | 0.013224 | 0.013224 | -4.3257
2011-12-08 | 0.25504 | 0.25504 | -1.3663
2011-12-09 | 0.54141 | 0.54141 | -0.61359
2011-12-10 | 0.90696 | 0.90696 | -0.097657
2011-12-11 | 3.056 | 3.056 | 1.1171
2011-12-12 | 0.074274 | 0.074274 | -2.6
2011-12-13 | 0.013239 | 0.013239 | -4.3246
2011-12-14 | 0.36303 | 0.36303 | -1.0133
2011-12-15 | 0.051628 | 0.051628 | -2.9637
2011-12-16 | 0.052427 | 0.052427 | -2.9483
2011-12-17 | 0.0012292 | 0.0012292 | -6.7014
2011-12-18 | 0.074185 | 0.074185 | -2.6012
2011-12-19 | 0.038154 | 0.038154 | -3.2661
2011-12-20 | 0.061016 | 0.061016 | -2.7966
2011-12-21 | 0.0025666 | 0.0025666 | -5.9652
2011-12-22 | 0.01844 | 0.01844 | -3.9932
2011-12-23 | 0.13658 | 0.13658 | -1.9909
2011-12-24 | 0.13524 | 0.13524 | -2.0007
2011-12-25 | 3.2233 | 3.2233 | 1.1704
2011-12-26 | 0.056198 | 0.056198 | -2.8789
2011-12-27 | 0.0067234 | 0.0067234 | -5.0022
2011-12-28 | 0.015731 | 0.015731 | -4.1522
2011-12-29 | 0.0024684 | 0.0024684 | -6.0042
2011-12-30 | 0.0057564 | 0.0057564 | -5.1574
2011-12-31 | 0.012553 | 0.012553 | -4.3778
2012-01-01 | 0.099285 | 0.099285 | -2.3098
2012-01-02 | 1.8071 | 1.8071 | 0.59173
2012-01-03 | 0.24564 | 0.24564 | -1.4039
2012-01-04 | 0.82044 | 0.82044 | -0.19791
2012-01-05 | 0.0062393 | 0.0062393 | -5.0769
2012-01-06 | 0.0021554 | 0.0021554 | -6.1398
2012-01-07 | 0.55822 | 0.55822 | -0.583
2012-01-08 | 0.32546 | 0.32546 | -1.1225
2012-01-09 | 0.0021615 | 0.0021615 | -6.137
2012-01-10 | 0.11514 | 0.11514 | -2.1616
2012-01-11 | 3.0843 | 3.0843 | 1.1263
2012-01-12 | 0.10228 | 0.10228 | -2.2801
2012-01-13 | 0.051457 | 0.051457 | -2.967
2012-01-14 | 0.56058 | 0.56058 | -0.57878
2012-01-15 | 0.33186 | 0.33186 | -1.103
2012-01-16 | 0.32948 | 0.32948 | -1.1102
2012-01-17 | 0.14598 | 0.14598 | -1.9243
2012-01-18 | 0.031 | 0.031 | -3.4738
2012-01-19 | 0.13713 | 0.13713 | -1.9868
2012-01-20 | 0.049816 | 0.049816 | -2.9994
2012-01-21 | 1.0118 | 1.0118 | 0.011734
2012-01-22 | 0.37605 | 0.37605 | -0.97803
2012-01-23 | 0.065179 | 0.065179 | -2.7306
2012-01-24 | 0.64545 | 0.64545 | -0.43781
2012-01-25 | 0.049295 | 0.049295 | -3.0099
2012-01-26 | 0.020488 | 0.020488 | -3.8879
2012-01-27 | 0.031435 | 0.031435 | -3.4598
2012-01-28 | 0.026236 | 0.026236 | -3.6406
2012-01-29 | 0.054152 | 0.054152 | -2.916
2012-01-30 | 1.517 | 1.517 | 0.41673
2012-01-31 | 0.16125 | 0.16125 | -1.8248
2012-02-01 | 0.0083867 | 0.0083867 | -4.7811
2012-02-02 | 0.045393 | 0.045393 | -3.0924
2012-02-03 | 0.010907 | 0.010907 | -4.5184
2012-02-04 | 0.010119 | 0.010119 | -4.5934
2012-02-05 | 6.9033 | 0 | 1.932
2012-02-06 | 0.533 | 0.533 | -0.62924
2012-02-07 | 0.18602 | 0.18602 | -1.6819
2012-02-08 | 0.0040801 | 0.0040801 | -5.5016
2012-02-09 | 0.0011116 | 0.0011116 | -6.8019
2012-02-10 | 0.0069964 | 0.0069964 | -4.9624
2012-02-11 | 0.019655 | 0.019655 | -3.9294
2012-02-12 | 0.0031937 | 0.0031937 | -5.7466
2012-02-13 | 0.0085631 | 0.0085631 | -4.7603
2012-02-14 | 0.0011319 | 0.0011319 | -6.7839
2012-02-15 | 0.28304 | 0.28304 | -1.2621
2012-02-16 | 0.3445 | 0.3445 | -1.0657
2012-02-17 | 0.17148 | 0.17148 | -1.7633
2012-02-18 | 0.58703 | 0.58703 | -0.53268
2012-02-19 | 0.34048 | 0.34048 | -1.0774
2012-02-20 | 0.013154 | 0.013154 | -4.331
2012-02-21 | 0.12154 | 0.12154 | -2.1075
2012-02-22 | 0.10678 | 0.10678 | -2.237
2012-02-23 | 0.013525 | 0.013525 | -4.3032
2012-02-24 | 0.15463 | 0.15463 | -1.8667
2012-02-25 | 0.41631 | 0.41631 | -0.87632
2012-02-26 | 0.32707 | 0.32707 | -1.1176
2012-02-27 | 0.31358 | 0.31358 | -1.1597
2012-02-28 | 0.11168 | 0.11168 | -2.1921
2012-02-29 | 0.4356 | 0.4356 | -0.83103
2012-03-01 | 0.27414 | 0.27414 | -1.2941
2012-03-02 | 1.3065 | 1.3065 | 0.26732
2012-03-03 | 0.057299 | 0.057299 | -2.8595
2012-03-04 | 0.71607 | 0.71607 | -0.33398
2012-03-05 | 0.0086569 | 0.0086569 | -4.7494
2012-03-06 | 0.023175 | 0.023175 | -3.7647
2012-03-07 | 0.080618 | 0.080618 | -2.518
2012-03-08 | 0.20573 | 0.20573 | -1.5812
2012-03-09 | 0.021122 | 0.021122 | -3.8575
2012-03-10 | 0.014484 | 0.014484 | -4.2347
2012-03-11 | 0.62616 | 0.62616 | -0.46814
2012-03-12 | 0.12251 | 0.12251 | -2.0995
2012-03-13 | 0.057086 | 0.057086 | -2.8632
2012-03-14 | 0.036913 | 0.036913 | -3.2992
2012-03-15 | 1.0494 | 1.0494 | 0.048199
2012-03-16 | 0.055607 | 0.055607 | -2.8894
2012-03-17 | 0.05626 | 0.05626 | -2.8778
2012-03-18 | 0.94359 | 0.94359 | -0.058068
2012-03-19 | 0.18773 | 0.18773 | -1.6728
2012-03-20 | 0.18534 | 0.18534 | -1.6856
2012-03-21 | 0.51645 | 0.51645 | -0.66078
2012-03-22 | 0.053484 | 0.053484 | -2.9284
2012-03-23 | 0.10096 | 0.10096 | -2.293
2012-03-24 | 0.17542 | 0.17542 | -1.7406
2012-03-25 | 0.0047824 | 0.0047824 | -5.3428
2012-03-26 | 0.019674 | 0.019674 | -3.9285
2012-03-27 | 0.00088321 | 0.00088321 | -7.0319
2012-03-28 | 0.0013255 | 0.0013255 | -6.626
2012-03-29 | 0.31937 | 0.31937 | -1.1414
2012-03-30 | 0.0081092 | 0.0081092 | -4.8148
2012-03-31 | 0.020717 | 0.020717 | -3.8768
2012-04-01 | 0.62922 | 0.62922 | -0.46328
2012-04-02 | 0.02177 | 0.02177 | -3.8272
2012-04-03 | 0.023586 | 0.023586 | -3.7471
2012-04-04 | 0.0092787 | 0.0092787 | -4.68
2012-04-05 | 0.0096855 | 0.0096855 | -4.6371
2012-04-06 | 1.5647 | 1.5647 | 0.44767
2012-04-07 | 2.0744 | 2.0744 | 0.72965
2012-04-08 | 0.6204 | 0.6204 | -0.47739
2012-04-09 | 0.068244 | 0.068244 | -2.6847
2012-04-10 | 0.3093 | 0.3093 | -1.1735
2012-04-11 | 0.32517 | 0.32517 | -1.1234
2012-04-12 | 0.004859 | 0.004859 | -5.3269
2012-04-13 | 0.016565 | 0.016565 | -4.1005
2012-04-14 | 0.21801 | 0.21801 | -1.5232
2012-04-15 | 0.033787 | 0.033787 | -3.3877
2012-04-16 | 0.49606 | 0.49606 | -0.70107
2012-04-17 | 0.0015286 | 0.0015286 | -6.4834
2012-04-18 | 0.18868 | 0.18868 | -1.6677
2012-04-19 | 0.074795 | 0.074795 | -2.593
2012-04-20 | 0.0099861 | 0.0099861 | -4.6066
2012-04-21 | 0.013252 | 0.013252 | -4.3236
2012-04-22 | 0.2101 | 0.2101 | -1.5602
2012-04-23 | 0.04739 | 0.04739 | -3.0493
2012-04-24 | 0.35963 | 0.35963 | -1.0227
2012-04-25 | 0.14529 | 0.14529 | -1.929
2012-04-26 | 0.28462 | 0.28462 | -1.2566
2012-04-27 | 0.020071 | 0.020071 | -3.9085
2012-04-28 | 0.33215 | 0.33215 | -1.1022
2012-04-29 | 0.0037368 | 0.0037368 | -5.5895
2012-04-30 | 0.0036601 | 0.0036601 | -5.6103
2012-05-01 | 0.0014437 | 0.0014437 | -6.5405
2012-05-02 | 0.013708 | 0.013708 | -4.2898
2012-05-03 | 0.29086 | 0.29086 | -1.2349
2012-05-04 | 0.017648 | 0.017648 | -4.0371
2012-05-05 | 0.57944 | 0.57944 | -0.54569
2012-05-06 | 0.044401 | 0.044401 | -3.1145
2012-05-07 | 0.045431 | 0.045431 | -3.0916
2012-05-08 | 0.16419 | 0.16419 | -1.8067
2012-05-09 | 0.096674 | 0.096674 | -2.3364
2012-05-10 | 0.29221 | 0.29221 | -1.2303
2012-05-11 | 0.035086 | 0.035086 | -3.35
2012-05-12 | 0.015967 | 0.015967 | -4.1372
2012-05-13 | 0.099794 | 0.099794 | -2.3046
2012-05-14 | 0.23022 | 0.23022 | -1.4687
2012-05-15 | 0.24735 | 0.24735 | -1.3969
2012-05-16 | 0.018371 | 0.018371 | -3.997
2012-05-17 | 0.090669 | 0.090669 | -2.4005
2012-05-18 | 0.0020868 | 0.0020868 | -6.1721
2012-05-19 | 0.15019 | 0.15019 | -1.8959
2012-05-20 | 0.12035 | 0.12035 | -2.1173
2012-05-21 | 0.23432 | 0.23432 | -1.4511
2012-05-22 | 0.012708 | 0.012708 | -4.3656
2012-05-23 | 0.92966 | 0.92966 | -0.072938
2012-05-24 | 0.0098891 | 0.0098891 | -4.6163
2012-05-25 | 5.3749 | 0.026894 | 1.6817
2012-05-26 | 0.16042 | 0.16042 | -1.83
2012-05-27 | 0.058009 | 0.058009 | -2.8472
2012-05-28 | 0.29777 | 0.29777 | -1.2114
2012-05-29 | 0.40832 | 0.40832 | -0.89571
2012-05-30 | 0.030331 | 0.030331 | -3.4956
2012-05-31 | 0.0096676 | 0.0096676 | -4.639
2012-06-01 | 0.031599 | 0.031599 | -3.4546
2012-06-02 | 0.0070808 | 0.0070808 | -4.9504
2012-06-03 | 0.0028445 | 0.0028445 | -5.8624
2012-06-04 | 1.6001 | 1.6001 | 0.47009
2012-06-05 | 0.019741 | 0.019741 | -3.9251
2012-06-06 | 0.023976 | 0.023976 | -3.7307
2012-06-07 | 0.085037 | 0.085037 | -2.4647
2012-06-08 | 0.10429 | 0.10429 | -2.2605
2012-06-09 | 0.32654 | 0.32654 | -1.1192
2012-06-10 | 0.12975 | 0.12975 | -2.0422
2012-06-11 | 0.0055761 | 0.0055761 | -5.1893
2012-06-12 | 0.066942 | 0.066942 | -2.7039
2012-06-13 | 0.088298 | 0.088298 | -2.427
2012-06-14 | 0.1029 | 0.1029 | -2.274
2012-06-15 | 0.064466 | 0.064466 | -2.7416
2012-06-16 | 0.10554 | 0.10554 | -2.2487
2012-06-17 | 0.17963 | 0.17963 | -1.7169
2012-06-18 | 0.16735 | 0.16735 | -1.7877
2012-06-19 | 0.011088 | 0.011088 | -4.5019
2012-06-20 | 1.2689 | 1.2689 | 0.23811
2012-06-21 | 0.18198 | 0.18198 | -1.7038
2012-06-22 | 0.10273 | 0.10273 | -2.2757
2012-06-23 | 0.087862 | 0.087862 | -2.432
2012-06-24 | 0.32349 | 0.32349 | -1.1286
2012-06-25 | 0.0060285 | 0.0060285 | -5.1113
2012-06-26 | 0.042046 | 0.042046 | -3.169
2012-06-27 | 0.1364 | 0.1364 | -1.9921
2012-06-28 | 0.48529 | 0.48529 | -0.723
2012-06-29 | 0.040222 | 0.040222 | -3.2134
2012-06-30 | 0.15426 | 0.15426 | -1.8691
2012-07-01 | 0.0068988 | 0.0068988 | -4.9764
2012-07-02 | 0.22492 | 0.22492 | -1.492
2012-07-03 | 0.284 | 0.284 | -1.2588
2012-07-04 | 0.011716 | 0.011716 | -4.4468
2012-07-05 | 0.18168 | 0.18168 | -1.7055
2012-07-06 | 0.00286 | 0.00286 | -5.8569
2012-07-07 | 0.030043 | 0.030043 | -3.5051
2012-07-08 | 0.0045687 | 0.0045687 | -5.3885
2012-07-09 | 0.018709 | 0.018709 | -3.9787
2012-07-10 | 0.080515 | 0.080515 | -2.5193
2012-07-11 | 0.020973 | 0.020973 | -3.8645
2012-07-12 | 0.017801 | 0.017801 | -4.0285
2012-07-13 | 0.0038681 | 0.0038681 | -5.555
2012-07-14 | 0.18917 | 0.18917 | -1.6651
2012-07-15 | 0.016209 | 0.016209 | -4.1222
2012-07-16 | 0.21759 | 0.21759 | -1.5251
2012-07-17 | 0.014971 | 0.014971 | -4.2016
2012-07-18 | 0.077903 | 0.077903 | -2.5523
2012-07-19 | 0.030322 | 0.030322 | -3.4959
2012-07-20 | 0.0032962 | 0.0032962 | -5.715
2012-07-21 | 0.0013988 | 0.0013988 | -6.5721
2012-07-22 | 0.035251 | 0.035251 | -3.3453
2012-07-23 | 0.030492 | 0.030492 | -3.4903
2012-07-24 | 0.060616 | 0.060616 | -2.8032
2012-07-25 | 0.29334 | 0.29334 | -1.2264
2012-07-26 | 0.0024979 | 0.0024979 | -5.9923
2012-07-27 | 0.013749 | 0.013749 | -4.2868
2012-07-28 | 0.0023682 | 0.0023682 | -6.0456
2012-07-29 | 0.0047444 | 0.0047444 | -5.3508
2012-07-30 | 0.017642 | 0.017642 | -4.0375
2012-07-31 | 0.020376 | 0.020376 | -3.8934
2012-08-01 | 0.02054 | 0.02054 | -3.8854
2012-08-02 | 0.095785 | 0.095785 | -2.3457
2012-08-03 | 0.0040035 | 0.0040035 | -5.5206
2012-08-04 | 0.015324 | 0.015324 | -4.1783
2012-08-05 | 0.037321 | 0.037321 | -3.2882
2012-08-06 | 0.0029474 | 0.0029474 | -5.8268
2012-08-07 | 0.1159 | 0.1159 | -2.155
2012-08-08 | 0.29906 | 0.29906 | -1.2071
2012-08-09 | 0.45021 | 0.45021 | -0.79804
2012-08-10 | 0.21804 | 0.21804 | -1.5231
2012-08-11 | 0.20133 | 0.20133 | -1.6028
2012-08-12 | 0.38114 | 0.38114 | -0.96459
2012-08-13 | 0.0067257 | 0.0067257 | -5.0018
2012-08-14 | 0.032474 | 0.032474 | -3.4273
2012-08-15 | 0.015934 | 0.015934 | -4.1393
2012-08-16 | 0.087501 | 0.087501 | -2.4361
2012-08-17 | 0.08451 | 0.08451 | -2.4709
2012-08-18 | 0.012725 | 0.012725 | -4.3642
2012-08-19 | 0.047218 | 0.047218 | -3.053
2012-08-20 | 0.11269 | 0.11269 | -2.1831
2012-08-21 | 0.011665 | 0.011665 | -4.4512
2012-08-22 | 0.0025334 | 0.0025334 | -5.9782
2012-08-23 | 0.021966 | 0.021966 | -3.8183
2012-08-24 | 0.0017354 | 0.0017354 | -6.3565
2012-08-25 | 0.010326 | 0.010326 | -4.5731
2012-08-26 | 0.17525 | 0.17525 | -1.7415
2012-08-27 | 0.0072044 | 0.0072044 | -4.9331
2012-08-28 | 0.03409 | 0.03409 | -3.3787
2012-08-29 | 0.1164 | 0.1164 | -2.1507
2012-08-30 | 0.05535 | 0.05535 | -2.8941
2012-08-31 | 0.27411 | 0.27411 | -1.2942
2012-09-01 | 0.00058723 | 0.00058723 | -7.4401
2012-09-02 | 0.22229 | 0.22229 | -1.5038
2012-09-03 | 0.68736 | 0.68736 | -0.37489
2012-09-04 | 0.067473 | 0.067473 | -2.696
2012-09-05 | 3.9381 | 3.9381 | 1.3707
2012-09-06 | 0.26373 | 0.26373 | -1.3328
2012-09-07 | 0.15353 | 0.15353 | -1.8739
2012-09-08 | 0.3534 | 0.3534 | -1.0402
2012-09-09 | 0.0080115 | 0.0080115 | -4.8269
2012-09-10 | 0.14154 | 0.14154 | -1.9552
2012-09-11 | 0.00063835 | 0.00063835 | -7.3566
2012-09-12 | 0.098271 | 0.098271 | -2.32
2012-09-13 | 0.10916 | 0.10916 | -2.215
2012-09-14 | 0.032657 | 0.032657 | -3.4217
2012-09-15 | 0.012464 | 0.012464 | -4.3849
2012-09-16 | 1.3371 | 1.3371 | 0.29048
2012-09-17 | 0.056213 | 0.056213 | -2.8786
2012-09-18 | 0.0063017 | 0.0063017 | -5.0669
2012-09-19 | 0.012384 | 0.012384 | -4.3914
2012-09-20 | 0.012895 | 0.012895 | -4.3509
2012-09-21 | 0.0081838 | 0.0081838 | -4.8056
2012-09-22 | 0.00040391 | 0.00040391 | -7.8143
2012-09-23 | 0.0055276 | 0.0055276 | -5.198
2012-09-24 | 0.006014 | 0.006014 | -5.1137
2012-09-25 | 0.013915 | 0.013915 | -4.2748
2012-09-26 | 0.14062 | 0.14062 | -1.9617
2012-09-27 | 0.051174 | 0.051174 | -2.9725
2012-09-28 | 0.23078 | 0.23078 | -1.4663
2012-09-29 | 0.33904 | 0.33904 | -1.0817
2012-09-30 | 0.021323 | 0.021323 | -3.848
2012-10-01 | 0.0053336 | 0.0053336 | -5.2337
2012-10-02 | 0.82326 | 0.82326 | -0.19449
2012-10-03 | 0.040587 | 0.040587 | -3.2043
2012-10-04 | 0.48913 | 0.48913 | -0.71513
2012-10-05 | 0.033421 | 0.033421 | -3.3986
2012-10-06 | 0.0046016 | 0.0046016 | -5.3814
2012-10-07 | 0.34264 | 0.34264 | -1.0711
2012-10-08 | 0.14027 | 0.14027 | -1.9642
2012-10-09 | 0.29868 | 0.29868 | -1.2084
2012-10-10 | 0.0022883 | 0.0022883 | -6.0799
2012-10-11 | 0.0040555 | 0.0040555 | -5.5077
2012-10-12 | 0.043613 | 0.043613 | -3.1324
2012-10-13 | 0.21474 | 0.21474 | -1.5383
2012-10-14 | 0.32007 | 0.32007 | -1.1392
2012-10-15 | 0.16218 | 0.16218 | -1.819
2012-10-16 | 0.023408 | 0.023408 | -3.7547
2012-10-17 | 0.0047858 | 0.0047858 | -5.3421
2012-10-18 | 0.011353 | 0.011353 | -4.4783
2012-10-19 | 0.09693 | 0.09693 | -2.3338
2012-10-20 | 0.13036 | 0.13036 | -2.0375
2012-10-21 | 0.094432 | 0.094432 | -2.3599
2012-10-22 | 0.34298 | 0.34298 | -1.0701
2012-10-23 | 0.6237 | 0.6237 | -0.47209
2012-10-24 | 0.23659 | 0.23659 | -1.4414
2012-10-25 | 0.15308 | 0.15308 | -1.8768
2012-10-26 | 0.0056315 | 0.0056315 | -5.1794
2012-10-27 | 0.0041937 | 0.0041937 | -5.4742
2012-10-28 | 0.0084379 | 0.0084379 | -4.775
2012-10-29 | 0.0061455 | 0.0061455 | -5.092
2012-10-30 | 0.14299 | 0.14299 | -1.945
2012-10-31 | 0.01813 | 0.01813 | -4.0102
2012-11-01 | 2.7507 | 2.7507 | 1.0119
2012-11-02 | 0.0095996 | 0.0095996 | -4.646
2012-11-03 | 0.010545 | 0.010545 | -4.5521
2012-11-04 | 0.17734 | 0.17734 | -1.7297
2012-11-05 | 0.48754 | 0.48754 | -0.71839
2012-11-06 | 0.22373 | 0.22373 | -1.4973
2012-11-07 | 0.027125 | 0.027125 | -3.6073
2012-11-08 | 0.42501 | 0.42501 | -0.85565
2012-11-09 | 1.4277 | 1.4277 | 0.35605
2012-11-10 | 0.0017923 | 0.0017923 | -6.3242
2012-11-11 | 0.097162 | 0.097162 | -2.3314
2012-11-12 | 0.069923 | 0.069923 | -2.6604
2012-11-13 | 0.0079358 | 0.0079358 | -4.8364
2012-11-14 | 0.096349 | 0.096349 | -2.3398
2012-11-15 | 0.021212 | 0.021212 | -3.8532
2012-11-16 | 0.041056 | 0.041056 | -3.1928
2012-11-17 | 0.38015 | 0.38015 | -0.9672
2012-11-18 | 0.022335 | 0.022335 | -3.8016
2012-11-19 | 0.076783 | 0.076783 | -2.5668
2012-11-20 | 0.057243 | 0.057243 | -2.8604
2012-11-21 | 0.060045 | 0.060045 | -2.8127
2012-11-22 | 0.15481 | 0.15481 | -1.8656
2012-11-23 | 0.0019169 | 0.0019169 | -6.257
2012-11-24 | 0.005311 | 0.005311 | -5.238
2012-11-25 | 0.25851 | 0.25851 | -1.3528
2012-11-26 | 0.18906 | 0.18906 | -1.6657
2012-11-27 | 0.21976 | 0.21976 | -1.5152
2012-11-28 | 0.15795 | 0.15795 | -1.8455
2012-11-29 | 1.0495 | 1.0495 | 0.048304
2012-11-30 | 0.088411 | 0.088411 | -2.4258
2012-12-01 | 2.5216 | 2.5216 | 0.9249
2012-12-02 | 0.011332 | 0.011332 | -4.4801
2012-12-03 | 0.1374 | 0.1374 | -1.9849
2012-12-04 | 1.0741 | 1.0741 | 0.071524
2012-12-05 | 1.5261 | 1.5261 | 0.42272
2012-12-06 | 0.02145 | 0.02145 | -3.842
2012-12-07 | 0.40217 | 0.40217 | -0.91088
2012-12-08 | 0.30904 | 0.30904 | -1.1743
2012-12-09 | 0.022474 | 0.022474 | -3.7954
2012-12-10 | 0.0034471 | 0.0034471 | -5.6702
2012-12-11 | 0.13284 | 0.13284 | -2.0186
2012-12-12 | 0.031955 | 0.031955 | -3.4434
2012-12-13 | 0.69875 | 0.69875 | -0.35846
2012-12-14 | 0.20126 | 0.20126 | -1.6032
2012-12-15 | 0.029644 | 0.029644 | -3.5185
2012-12-16 | 0.016367 | 0.016367 | -4.1125
2012-12-17 | 0.0020282 | 0.0020282 | -6.2006
2012-12-18 | 0.29151 | 0.29151 | -1.2327
2012-12-19 | 0.026404 | 0.026404 | -3.6342
2012-12-20 | 0.16112 | 0.16112 | -1.8256
2012-12-21 | 0.084894 | 0.084894 | -2.4664
2012-12-22 | 0.1841 | 0.1841 | -1.6923
2012-12-23 | 0.1288 | 0.1288 | -2.0495
2012-12-24 | 0.16542 | 0.16542 | -1.7993
2012-12-25 | 0.00063816 | 0.00063816 | -7.3569
2012-12-26 | 0.0045828 | 0.0045828 | -5.3855
2012-12-27 | 0.082955 | 0.082955 | -2.4895
2012-12-28 | 0.18869 | 0.18869 | -1.6676
2012-12-29 | 0.0013543 | 0.0013543 | -6.6044
2012-12-30 | 0.032495 | 0.032495 | -3.4267
2012-12-31 | 0.15654 | 0.15654 | -1.8544
Note: Exclusions refer to upstream events only and do not refer MED exclusions. MED calculation starts from 5 years prior to the relevant regulatory reporting year (e.g. 2013 requires data from 1 January 2008 to 31 December 2012).
Contents

## 1e. STPIS Exclusions
United Energy Distribution Pty Limited
STPIS Data Reporting
2013
Exclusions
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Feeder ID / name | Feeder classification | Number of interruptions (unplanned) | Duration of interruption (unplanned) (mins) | Total unplanned minutes off supply | Event category (use Exclusion categories listed in section 3.3 (a) of the AER's STPIS) | Effect on unplanned SAIDI | Effect on unplanned SAIFI | Effect on unplaned MAIFI | Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning | Cause of event (Use categories listed in table 1, Template 6C)
2013-01-04 | BR10 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0010197 | MED | Animals
2013-01-04 | LWN35 | URBAN | 39.27 | 0 | 3337.95 |  | 0.005157 | 6.067e-05 | 0 | MED | Equipment failure
2013-01-04 | FSH31 | URBAN | 94 | 0 | 27303.8698 |  | 0.042183 | 0.00014523 | 0 | MED | Equipment failure
2013-01-04 | DMA13 | RURAL SHORT | 1 | 0 | 0 |  | 0 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | NP6 | URBAN | 1 | 0 | 107.3167 |  | 0.0001658 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | EW2 | URBAN | 2286 | 0 | 214430.1106 |  | 0.33128 | 0.0035318 | 0 | MED | Vegetation
2013-01-04 | RBD12 | RURAL SHORT | 1 | 0 | 1697.25 |  | 0.0026222 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | SS22 | URBAN | 1 | 0 | 209.0333 |  | 0.00032295 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | STO22 | URBAN | 1 | 0 | 1655.2833 |  | 0.0025573 | 1.5449e-06 | 0 | MED | Vegetation
2013-01-04 | GW11 | URBAN | 1104 | 0 | 37425.6 |  | 0.057821 | 0.0017056 | 0 | MED | Vegetation
2013-01-04 | GW5 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0 | MED | Equipment failure
2013-01-04 | LD2 | URBAN | 37 | 0 | 7142.85 |  | 0.011035 | 5.7163e-05 | 0 | MED | Equipment failure
2013-01-04 | EM6 | URBAN | 24.42 | 0 | 3312.1652 |  | 0.0051171 | 3.7728e-05 | 0 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0.0050659 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 985 | 0 | 165870.0926 |  | 0.25626 | 0.0015218 | 0 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 1.5449e-06 | MED | Other
2013-01-04 | STO22 | URBAN | 1 | 0 | 1709.7167 |  | 0.0026414 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | STO13 | RURAL SHORT | 19.47 | 0 | 31864.9271 |  | 0.04923 | 3.008e-05 | 0 | MED | Equipment failure
2013-01-04 | EB12 | URBAN | 1 | 0 | 306.5333 |  | 0.00047358 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 1 | 0 | 3.7833 |  | 5.845e-06 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | STO13 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0 | MED | Equipment failure
2013-01-04 | FTN12 | URBAN | 1 | 0 | 286.8833 |  | 0.00044322 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | OAK32 | URBAN | 27.72 | 0 | 6881.49 |  | 0.010632 | 4.2826e-05 | 0 | MED | Equipment failure
2013-01-04 | MR15 | URBAN | 1607 | 0 | 11249 |  | 0.017379 | 0.0024827 | 0 | MED | Vegetation
2013-01-04 | RWT18 | URBAN | 1 | 0 | 340.3833 |  | 0.00052587 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | EL8 | URBAN | 1 | 0 | 622.65 |  | 0.00096196 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | EW2 | URBAN | 70 | 0 | 12040 |  | 0.018601 | 0.00010815 | 0 | MED | Vegetation
2013-01-04 | MR22 | URBAN | 38.28 | 0 | 5689.6827 |  | 0.0087903 | 5.9141e-05 | 0 | MED | Equipment failure
2013-01-04 | MR23 | URBAN | 9.24 | 0 | 1288.056 |  | 0.00199 | 1.4275e-05 | 0 | MED | Equipment failure
2013-01-04 | OE15 | URBAN | 75.9 | 0 | 13292.3699 |  | 0.020536 | 0.00011726 | 0 | MED | Equipment failure
2013-01-04 | SR15 | URBAN | 1 | 0 | 204.0833 |  | 0.0003153 | 1.5449e-06 | 0 | MED | Vegetation
2013-01-04 | DN25 | URBAN | 16.5 | 0 | 1658.5256 |  | 0.0025623 | 2.5492e-05 | 0 | MED | Equipment failure
2013-01-04 | DMA13 | RURAL SHORT | 868 | 0 | 91860.497 |  | 0.14192 | 0.001341 | 0 | MED | Other
2013-01-04 | DMA12 | URBAN | 33.33 | 0 | 7814.7751 |  | 0.012073 | 5.1493e-05 | 0 | MED | Other
2013-01-04 | LD2 | URBAN | 12.21 | 0 | 21459.2789 |  | 0.033153 | 1.8864e-05 | 0 | MED | Equipment failure
2013-01-04 | STO12 | URBAN | 610 | 0 | 210084 |  | 0.32457 | 0.00094242 | 0 | MED | Vegetation
2013-01-04 | BT2 | URBAN | 1 | 0 | 147.7333 |  | 0.00022824 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | M17 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0016052 | MED | Animals
2013-01-04 | RBD23 | URBAN | 18.48 | 0 | 4039.1126 |  | 0.0062402 | 2.8551e-05 | 0 | MED | Other
2013-01-04 | MGE11 | URBAN | 25.41 | 0 | 4142.2543 |  | 0.0063996 | 3.9257e-05 | 0 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 52.14 | 0 | 56763.0817 |  | 0.087696 | 8.0554e-05 | 0 | MED | Equipment failure
2013-01-04 | NB23 | URBAN | 28.05 | 0 | 4373.2197 |  | 0.0067564 | 4.3336e-05 | 0 | MED | Equipment failure
2013-01-04 | OAK32 | URBAN | 11.88 | 0 | 858.924 |  | 0.001327 | 1.8354e-05 | 0 | MED | Equipment failure
2013-01-04 | HGS23 | RURAL SHORT | 19.14 | 0 | 4611.783 |  | 0.007125 | 2.957e-05 | 0 | MED | Equipment failure
2013-01-04 | RBD21 | RURAL SHORT | 509 | 0 | 31507.1 |  | 0.048677 | 0.00078638 | 0 | MED | Equipment failure
2013-01-04 | DC5 | URBAN | 1 | 0 | 364.9667 |  | 0.00056385 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | LD6 | URBAN | 25.41 | 0 | 9063.3227 |  | 0.014002 | 3.9257e-05 | 0 | MED | Equipment failure
2013-01-04 | CDA22 | URBAN | 20.13 | 0 | 4671.1665 |  | 0.0072167 | 3.11e-05 | 0 | MED | Equipment failure
2013-01-04 | STO22 | URBAN | 1641.0638 | 0 | 176934.3322 |  | 0.27335 | 0.0025354 | 0 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 3136.7653 | 0 | 338196.1595 |  | 0.5225 | 0.0048461 | 0 | MED | Equipment failure
2013-01-04 | STO21 | URBAN | 3341.4201 | 0 | 360261.3967 |  | 0.55659 | 0.0051623 | 0 | MED | Equipment failure
2013-01-04 | STO23 | URBAN | 3535.5553 | 0 | 381192.4395 |  | 0.58892 | 0.0054623 | 0 | MED | Equipment failure
2013-01-04 | STO12 | URBAN | 5120.1955 | 0 | 552043.3652 |  | 0.85288 | 0.0079104 | 0 | MED | Equipment failure
2013-01-04 | DMA15 | RURAL SHORT | 1816.3554 | 0 | 63822.3398 |  | 0.098602 | 0.0028062 | 0 | MED | Equipment failure
2013-01-04 | DMA14 | URBAN | 2676.7342 | 0 | 94053.9745 |  | 0.14531 | 0.0041354 | 0 | MED | Equipment failure
2013-01-04 | DMA13 | RURAL SHORT | 3017.2337 | 0 | 106018.3043 |  | 0.16379 | 0.0046615 | 0 | MED | Equipment failure
2013-01-04 | DMA11 | URBAN | 3406.0691 | 0 | 119681.0406 |  | 0.1849 | 0.0052622 | 0 | MED | Equipment failure
2013-01-04 | DMA12 | URBAN | 5181.6075 | 0 | 182069.1705 |  | 0.28129 | 0.0080053 | 0 | MED | Equipment failure
2013-01-04 | RBD14 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0026434 | MED | Equipment failure
2013-01-04 | DMA15 | RURAL SHORT | 1 | 0 | 78.7167 |  | 0.00012161 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | RBD12 | RURAL SHORT | 1 | 0 | 1111.8 |  | 0.0017177 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | RWT28 | URBAN | 37.62 | 0 | 4207.1687 |  | 0.0064999 | 5.8121e-05 | 0 | MED | Equipment failure
2013-01-04 | LWN31 | RURAL SHORT | 1 | 0 | 38.2833 |  | 5.9146e-05 | 1.5449e-06 | 0 | MED | Vegetation
2013-01-04 | DN25 | URBAN | 16.5 | 0 | 2940.8495 |  | 0.0045435 | 2.5492e-05 | 0 | MED | Equipment failure
2013-01-04 | MC3 | URBAN | 1 | 0 | 482.4833 |  | 0.00074541 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | MTN1 | URBAN | 1 | 0 | 0 |  | 0 | 1.5449e-06 | 0 | MED | Other
2013-01-04 | EM6 | URBAN | 64.02 | 0 | 4657.455 |  | 0.0071955 | 9.8908e-05 | 0 | MED | Equipment failure
2013-01-04 | DN13 | URBAN | 1 | 0 | 368.3667 |  | 0.00056911 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | DC1 | URBAN | 1 | 0 | 107.1667 |  | 0.00016557 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | MGE22 | URBAN | 18.15 | 0 | 1840.1069 |  | 0.0028429 | 2.8041e-05 | 0 | MED | Equipment failure
2013-01-04 | BR1 | URBAN | 1461 | 0 | 160076.9487 |  | 0.24731 | 0.0022572 | 0 | MED | Vegetation
2013-01-04 | EL9 | URBAN | 20.13 | 0 | 1975.4233 |  | 0.0030519 | 3.11e-05 | 0 | MED | Equipment failure
2013-01-04 | CFD26 | URBAN | 1 | 0 | 365.05 |  | 0.00056398 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | BU2 | URBAN | 21.78 | 0 | 2587.8277 |  | 0.0039981 | 3.3649e-05 | 0 | MED | Equipment failure
2013-01-04 | MTN5 | RURAL SHORT | 1 | 0 | 282 |  | 0.00043568 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | BW21 | URBAN | 96.69 | 0 | 12158.4047 |  | 0.018784 | 0.00014938 | 0 | MED | Equipment failure
2013-01-04 | HGS23 | RURAL SHORT | 26.4 | 0 | 3929.64 |  | 0.0060711 | 4.0787e-05 | 0 | MED | Equipment failure
2013-01-04 | FSH34 | URBAN | 39.27 | 0 | 6876.8328 |  | 0.010624 | 6.067e-05 | 0 | MED | Equipment failure
2013-01-04 | WD9 | URBAN | 1 | 0 | 238.2667 |  | 0.00036811 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | BW21 | URBAN | 1 | 0 | 189.0833 |  | 0.00029212 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-04 | STO23 | URBAN | 32.34 | 0 | 27592.488 |  | 0.042629 | 4.9964e-05 | 0 | MED | Equipment failure
2013-01-04 | OR9 | URBAN | 36.96 | 0 | 3466.2308 |  | 0.0053552 | 5.7101e-05 | 0 | MED | Equipment failure
2013-01-04 | RBD13 | URBAN | 214 | 0 | 41776.3738 |  | 0.064542 | 0.00033062 | 0 | MED | Equipment failure
2013-01-04 | BR4 | URBAN | 34.98 | 0 | 1865.0182 |  | 0.0028814 | 5.4042e-05 | 0 | MED | Equipment failure
2013-01-04 | STO12 | URBAN | 36.63 | 0 | 12386.4345 |  | 0.019136 | 5.6591e-05 | 0 | MED | Equipment failure
2013-01-04 | MR31 | URBAN | 39.6 | 0 | 10643.8187 |  | 0.016444 | 6.118e-05 | 0 | MED | Equipment failure
2013-01-04 | RWT28 | URBAN | 63.69 | 0 | 4455.4506 |  | 0.0068834 | 9.8398e-05 | 0 | MED | Equipment failure
2013-01-04 | DN25 | URBAN | 16.5 | 0 | 2586.375 |  | 0.0039958 | 2.5492e-05 | 0 | MED | Equipment failure
2013-01-04 | GW7 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0038546 | MED | Animals
2013-01-04 | RBD21 | RURAL SHORT | 0 | 0 | 3308.4 |  | 0.0051113 | 0 | 0 | MED | Vegetation
2013-01-04 | NB23 | URBAN | 24.09 | 0 | 2808.894 |  | 0.0043396 | 3.7218e-05 | 0 | MED | Equipment failure
2013-01-04 | STO22 | URBAN | 43.56 | 0 | 30406.3305 |  | 0.046976 | 6.7298e-05 | 0 | MED | Equipment failure
2013-01-04 | STO13 | RURAL SHORT | 58.74 | 0 | 40203.1245 |  | 0.062112 | 9.075e-05 | 0 | MED | Equipment failure
2013-01-04 | STO12 | URBAN | 28.05 | 0 | 6627.2809 |  | 0.010239 | 4.3336e-05 | 0 | MED | Equipment failure
2013-01-04 | LWN34 | URBAN | 27.06 | 0 | 3905.6591 |  | 0.006034 | 4.1806e-05 | 0 | MED | Equipment failure
2013-01-04 | RBD21 | RURAL SHORT | 0 | 0 | 2142 |  | 0.0033093 | 0 | 0 | MED | Equipment failure
2013-01-04 | CRM22 | URBAN | 1 | 0 | 208.0667 |  | 0.00032145 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | FSH33 | URBAN | 1389 | 0 | 74388.7902 |  | 0.11493 | 0.0021459 | 0 | MED | Equipment failure
2013-01-27 | FSH33 | URBAN | 2428 | 0 | 289235.1634 |  | 0.44685 | 0.0037511 | 0 | MED | Equipment failure
2013-01-27 | DMA13 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0.0013379 | MED | Other
2013-01-27 | DMA14 | URBAN | 1 | 0 | 807.0667 |  | 0.0012469 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | HT11 | URBAN | 1798 | 0 | 130964.75 |  | 0.20233 | 0.0027778 | 0 | MED | Equipment failure
2013-01-27 | EW1 | URBAN | 1 | 0 | 262.8167 |  | 0.00040604 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | K10 | URBAN | 1 | 0 | 85.1 |  | 0.00013148 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | HGS33 | RURAL SHORT | 28 | 0 | 23943.7324 |  | 0.036992 | 4.3259e-05 | 0 | MED | Equipment failure
2013-01-27 | FTN11 | URBAN | 2130 | 0 | 311984.2052 |  | 0.482 | 0.0032907 | 0 | MED | Equipment failure
2013-01-27 | MC2 | URBAN | 807 | 0 | 209144.3673 |  | 0.32312 | 0.0012468 | 0 | MED | Equipment failure
2013-01-27 | DMA13 | RURAL SHORT | 37 | 0 | 33818 |  | 0.052247 | 5.7163e-05 | 0 | MED | Equipment failure
2013-01-27 | MGE31 | URBAN | 2122 | 0 | 316932.5374 |  | 0.48964 | 0.0032784 | 0 | MED | Equipment failure
2013-01-27 | HT1 | URBAN | 1110 | 0 | 254433.2862 |  | 0.39309 | 0.0017149 | 0 | MED | Equipment failure
2013-01-27 | MC1 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.003178 | MED | Other
2013-01-27 | MC6 | URBAN | 2672 | 0 | 390589.1601 |  | 0.60344 | 0.0041281 | 0 | MED | Equipment failure
2013-01-27 | LWN35 | URBAN | 1760 | 0 | 284238.108 |  | 0.43913 | 0.0027191 | 0 | MED | Equipment failure
2013-01-27 | LD3 | URBAN | 1 | 0 | 157.9833 |  | 0.00024408 | 1.5449e-06 | 0 | MED | Weather
2013-01-27 | CFD14 | URBAN | 1 | 0 | 1617.2333 |  | 0.0024985 | 1.5449e-06 | 0 | MED | Vegetation
2013-01-27 | HT1 | URBAN | 55 | 0 | 12518.9185 |  | 0.019341 | 8.4972e-05 | 0 | MED | Other
2013-01-27 | BH22 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0022649 | MED | Equipment failure
2013-01-27 | SS14 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0009625 | MED | Equipment failure
2013-01-27 | EB23 | URBAN | 444 | 0 | 128087.1852 |  | 0.19789 | 0.00068596 | 0 | MED | Equipment failure
2013-01-27 | DSH24 | URBAN | 3527 | 0 | 331211.9106 |  | 0.51171 | 0.005449 | 0 | MED | Equipment failure
2013-01-27 | CDA24 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0053965 | MED | Equipment failure
2013-01-27 | SS14 | URBAN | 10 | 0 | 4183.667 |  | 0.0064636 | 1.5449e-05 | 0 | MED | Equipment failure
2013-01-27 | MGE32 | URBAN | 928 | 0 | 141198.9568 |  | 0.21815 | 0.0014337 | 0 | MED | Equipment failure
2013-01-27 | NP34 | URBAN | 73 | 0 | 3917 |  | 0.0060516 | 0.00011278 | 0 | MED | Equipment failure
2013-01-27 | SS14 | URBAN | 432 | 0 | 135655.2144 |  | 0.20958 | 0.00066742 | 0 | MED | Equipment failure
2013-01-27 | NW22 | URBAN | 1 | 0 | 1321.15 |  | 0.0020411 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | DMA13 | RURAL SHORT | 2 | 0 | 299.0666 |  | 0.00046204 | 3.0899e-06 | 0 | MED | Equipment failure
2013-01-27 | BH22 | URBAN | 812 | 0 | 1664.6 |  | 0.0025717 | 0.0012545 | 0 | MED | Equipment failure
2013-01-27 | BH22 | URBAN | 182 | 0 | 32558 |  | 0.0503 | 0.00028118 | 0 | MED | Equipment failure
2013-01-27 | MGE24 | URBAN | 1 | 0 | 711.5 |  | 0.0010992 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | SVW54 | URBAN | 176 | 0 | 104221.3392 |  | 0.16102 | 0.00027191 | 0 | MED | Equipment failure
2013-01-27 | MGE31 | URBAN | 8.58 | 0 | 4707.5603 |  | 0.0072729 | 1.3256e-05 | 0 | MED | Other
2013-01-27 | HGS33 | RURAL SHORT | 4 | 0 | 537.6668 |  | 0.00083067 | 6.1798e-06 | 0 | MED | Other
2013-01-27 | MGE31 | URBAN | 44.89 | 0 | 19899.737 |  | 0.030744 | 6.9353e-05 | 0 | MED | Other
2013-01-27 | EW14 | URBAN | 1 | 0 | 702.6833 |  | 0.0010856 | 1.5449e-06 | 0 | MED | Vegetation
2013-01-27 | RWT18 | URBAN | 1 | 0 | 505 |  | 0.0007802 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | CDA21 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.00087599 | MED | Equipment failure
2013-01-27 | RWT18 | URBAN | 1 | 0 | 374.0333 |  | 0.00057786 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | MC1 | URBAN | 1 | 0 | 136.3167 |  | 0.0002106 | 1.5449e-06 | 0 | MED | Equipment failure
2013-01-27 | CDA21 | URBAN | 182 | 0 | 37856 |  | 0.058486 | 0.00028118 | 0 | MED | Equipment failure
2013-01-27 | DC12 | URBAN | 1 | 0 | 973.7167 |  | 0.0015043 | 1.5449e-06 | 0 | MED | Other
2013-01-27 | SS21 | URBAN | 111 | 0 | 6771 |  | 0.010461 | 0.00017149 | 0 | MED | Equipment failure
2013-01-27 | MC6 | URBAN | 1 | 0 | 13.1833 |  | 2.0368e-05 | 1.5449e-06 | 0 | MED | Other
2013-01-27 | MTN8 | URBAN | 1 | 0 | 193.6 |  | 0.0002991 | 1.5449e-06 | 0 | MED | Other
2013-01-27 | MTN8 | URBAN | 1 | 0 | 1.2667 |  | 1.957e-06 | 1.5449e-06 | 0 | MED | Other
2013-01-27 | MC6 | URBAN | 1 | 0 | 6.1667 |  | 9.5272e-06 | 1.5449e-06 | 0 | MED | Other
2013-01-27 | MC6 | URBAN | 1 | 0 | 1.3 |  | 2.0084e-06 | 1.5449e-06 | 0 | MED | Other
2013-01-27 | MGE21 | URBAN | 149 | 0 | 22923.65 |  | 0.035416 | 0.0002302 | 0 | MED | Equipment failure
2013-02-12 | RWT31 | URBAN | 2464 | 0 | 23413.7512 | 5 | 0.036173 | 0.0038068 | 0 |  | Transmission failure
2013-02-12 | RWT28 | URBAN | 2677.7385 | 0 | 47960.4231 | 5 | 0.074096 | 0.004137 | 0 |  | Transmission failure
2013-02-12 | RWT24 | URBAN | 3032.2615 | 0 | 54310.2129 | 5 | 0.083907 | 0.0046847 | 0 |  | Transmission failure
2013-02-12 | RWT13 | URBAN | 1.0004 | 0 | 40.0248 | 5 | 6.1836e-05 | 1.5456e-06 | 0 |  | Transmission failure
2013-02-12 | RWT16 | URBAN | 1684.6732 | 0 | 67401.8279 | 5 | 0.10413 | 0.0026027 | 0 |  | Transmission failure
2013-02-12 | RWT18 | URBAN | 3319.3264 | 0 | 132802.4138 | 5 | 0.20517 | 0.0051282 | 0 |  | Transmission failure
2013-09-09 | OE6 | URBAN | 25.7847 | 0 | 566.3365 | 5 | 0.00087496 | 3.9836e-05 | 0 |  | Transmission failure
2013-09-09 | OE1 | URBAN | 91.7934 | 0 | 2016.1579 | 5 | 0.0031149 | 0.00014182 | 0 |  | Transmission failure
2013-09-09 | OE14 | URBAN | 185.6496 | 0 | 4077.6228 | 5 | 0.0062997 | 0.00028682 | 0 |  | Transmission failure
2013-09-09 | NO3 | URBAN | 196.9948 | 0 | 4326.8109 | 5 | 0.0066847 | 0.00030435 | 0 |  | Transmission failure
2013-09-09 | OE10 | URBAN | 226.905 | 0 | 4983.7612 | 5 | 0.0076997 | 0.00035056 | 0 |  | Transmission failure
2013-09-09 | NO2 | URBAN | 244.4386 | 0 | 5368.87 | 5 | 0.0082946 | 0.00037765 | 0 |  | Transmission failure
2013-09-09 | NO4 | URBAN | 263.0036 | 0 | 5776.6323 | 5 | 0.0089246 | 0.00040633 | 0 |  | Transmission failure
2013-09-09 | OE2 | URBAN | 303.2277 | 0 | 6660.1173 | 5 | 0.01029 | 0.00046847 | 0 |  | Transmission failure
2013-09-09 | OE5 | URBAN | 362.0167 | 0 | 7951.3645 | 5 | 0.012284 | 0.0005593 | 0 |  | Transmission failure
2013-09-09 | EB23 | URBAN | 461.0298 | 0 | 10126.0967 | 5 | 0.015644 | 0.00071227 | 0 |  | Transmission failure
2013-09-09 | EB13 | URBAN | 517.7561 | 0 | 11372.037 | 5 | 0.017569 | 0.00079991 | 0 |  | Transmission failure
2013-09-09 | OE15 | URBAN | 526.0072 | 0 | 11553.2646 | 5 | 0.017849 | 0.00081265 | 0 |  | Transmission failure
2013-09-09 | OE9 | URBAN | 637.3969 | 0 | 13999.8383 | 5 | 0.021629 | 0.00098475 | 0 |  | Transmission failure
2013-09-09 | NO6 | URBAN | 659.056 | 0 | 14475.561 | 5 | 0.022364 | 0.0010182 | 0 |  | Transmission failure
2013-09-09 | CDA21 | URBAN | 666.2757 | 0 | 14634.1352 | 5 | 0.022609 | 0.0010294 | 0 |  | Transmission failure
2013-09-09 | NO5 | URBAN | 676.5896 | 0 | 14860.6698 | 5 | 0.022959 | 0.0010453 | 0 |  | Transmission failure
2013-09-09 | GW1 | URBAN | 729.1903 | 0 | 16015.9963 | 5 | 0.024744 | 0.0011266 | 0 |  | Transmission failure
2013-09-09 | GW10 | URBAN | 1040.6691 | 0 | 22857.3412 | 5 | 0.035313 | 0.0016078 | 0 |  | Transmission failure
2013-09-09 | EB24 | URBAN | 1080.8931 | 0 | 23740.8262 | 5 | 0.036678 | 0.0016699 | 0 |  | Transmission failure
2013-09-09 | GW4 | URBAN | 1138.6508 | 0 | 25009.4199 | 5 | 0.038638 | 0.0017592 | 0 |  | Transmission failure
2013-09-09 | GW6 | URBAN | 1192.2829 | 0 | 26187.3999 | 5 | 0.040458 | 0.001842 | 0 |  | Transmission failure
2013-09-09 | EB11 | URBAN | 1239.7267 | 0 | 27229.459 | 5 | 0.042068 | 0.0019153 | 0 |  | Transmission failure
2013-09-09 | EB21 | URBAN | 1286.1391 | 0 | 28248.8647 | 5 | 0.043643 | 0.001987 | 0 |  | Transmission failure
2013-09-09 | CDA23 | URBAN | 1468.6945 | 0 | 32258.5272 | 5 | 0.049838 | 0.0022691 | 0 |  | Transmission failure
2013-09-09 | GW5 | URBAN | 1510.9813 | 0 | 33187.319 | 5 | 0.051273 | 0.0023344 | 0 |  | Transmission failure
2013-09-09 | NO7 | URBAN | 1597.6178 | 0 | 35090.2097 | 5 | 0.054213 | 0.0024682 | 0 |  | Transmission failure
2013-09-09 | GW3 | URBAN | 1700.7565 | 0 | 37355.5557 | 5 | 0.057712 | 0.0026276 | 0 |  | Transmission failure
2013-09-09 | OE4 | URBAN | 1725.5097 | 0 | 37899.2387 | 5 | 0.058552 | 0.0026658 | 0 |  | Transmission failure
2013-09-09 | EB12 | URBAN | 1841.025 | 0 | 40436.4263 | 5 | 0.062472 | 0.0028443 | 0 |  | Transmission failure
2013-09-09 | EB22 | URBAN | 1975.1053 | 0 | 43381.3761 | 5 | 0.067022 | 0.0030514 | 0 |  | Transmission failure
2013-09-09 | CDA22 | URBAN | 2033.8943 | 0 | 44672.6233 | 5 | 0.069017 | 0.0031423 | 0 |  | Transmission failure
2013-09-09 | EB31 | URBAN | 2034.9257 | 0 | 44695.2768 | 5 | 0.069052 | 0.0031439 | 0 |  | Transmission failure
2013-09-09 | EB14 | URBAN | 2107.1228 | 0 | 46281.019 | 5 | 0.071502 | 0.0032554 | 0 |  | Transmission failure
2013-09-09 | GW8 | URBAN | 2263.8935 | 0 | 49724.3449 | 5 | 0.076822 | 0.0034976 | 0 |  | Transmission failure
2013-09-09 | GW12 | URBAN | 2297.9293 | 0 | 50471.9091 | 5 | 0.077977 | 0.0035502 | 0 |  | Transmission failure
2013-09-09 | GW11 | URBAN | 2451.6059 | 0 | 53847.2746 | 5 | 0.083191 | 0.0037876 | 0 |  | Transmission failure
2013-09-09 | GW7 | URBAN | 2488.7358 | 0 | 54662.7992 | 5 | 0.084451 | 0.003845 | 0 |  | Transmission failure
2013-09-09 | EB33 | URBAN | 2526.8971 | 0 | 55500.9772 | 5 | 0.085746 | 0.0039039 | 0 |  | Transmission failure
2013-09-09 | GW2 | URBAN | 2655.8204 | 0 | 58332.6597 | 5 | 0.090121 | 0.0041031 | 0 |  | Transmission failure
2013-09-09 | CDA24 | URBAN | 3601.6019 | 0 | 79105.8826 | 5 | 0.12221 | 0.0055643 | 0 |  | Transmission failure
2013-09-09 | EB32 | URBAN | 3843.9778 | 0 | 84429.4458 | 5 | 0.13044 | 0.0059388 | 0 |  | Transmission failure
2013-09-09 | CDA11 | URBAN | 5292.0445 | 0 | 116234.9037 | 5 | 0.17958 | 0.0081759 | 0 |  | Transmission failure
2013-09-09 | RD2 | URBAN | 145.4255 | 0 | 3194.1379 | 5 | 0.0049348 | 0.00022468 | 0 |  | Transmission failure
2013-09-09 | RD10 | URBAN | 960.2209 | 0 | 21090.3713 | 5 | 0.032584 | 0.0014835 | 0 |  | Transmission failure
2013-09-09 | RD4 | URBAN | 2028.7374 | 0 | 44559.356 | 5 | 0.068842 | 0.0031343 | 0 |  | Transmission failure
2013-09-09 | SVW43 | URBAN | 0.95028 | 0 | 18.7093 | 5 | 2.8905e-05 | 1.4681e-06 | 0 |  | Transmission failure
2013-09-09 | SVW44 | URBAN | 0.95028 | 0 | 18.7093 | 5 | 2.8905e-05 | 1.4681e-06 | 0 |  | Transmission failure
2013-09-09 | SV34 | URBAN | 9.5028 | 0 | 187.0929 | 5 | 0.00028905 | 1.4681e-05 | 0 |  | Transmission failure
2013-09-09 | SVW52 | URBAN | 14.2542 | 0 | 280.6394 | 5 | 0.00043357 | 2.2022e-05 | 0 |  | Transmission failure
2013-09-09 | SV14 | URBAN | 15.2045 | 0 | 299.3487 | 5 | 0.00046248 | 2.349e-05 | 0 |  | Transmission failure
2013-09-09 | SV22 | URBAN | 32.3095 | 0 | 636.116 | 5 | 0.00098277 | 4.9917e-05 | 0 |  | Transmission failure
2013-09-09 | SV31 | URBAN | 73.1716 | 0 | 1440.6156 | 5 | 0.0022257 | 0.00011305 | 0 |  | Transmission failure
2013-09-09 | NP15 | URBAN | 76.0224 | 0 | 1496.7435 | 5 | 0.0023124 | 0.00011745 | 0 |  | Transmission failure
2013-09-09 | SV20 | URBAN | 80.7738 | 0 | 1590.2899 | 5 | 0.0024569 | 0.00012479 | 0 |  | Transmission failure
2013-09-09 | SS24 | URBAN | 103.5806 | 0 | 2039.313 | 5 | 0.0031506 | 0.00016003 | 0 |  | Transmission failure
2013-09-09 | SV23 | URBAN | 154.8957 | 0 | 3049.6148 | 5 | 0.0047115 | 0.00023931 | 0 |  | Transmission failure
2013-09-09 | SS21 | URBAN | 366.8083 | 0 | 7221.7873 | 5 | 0.011157 | 0.0005667 | 0 |  | Transmission failure
2013-09-09 | NP18 | URBAN | 455.1844 | 0 | 8961.7516 | 5 | 0.013845 | 0.00070324 | 0 |  | Transmission failure
2013-09-09 | SVW45 | URBAN | 475.1403 | 0 | 9354.6467 | 5 | 0.014452 | 0.00073407 | 0 |  | Transmission failure
2013-09-09 | SVW42 | URBAN | 552.113 | 0 | 10870.0995 | 5 | 0.016794 | 0.00085299 | 0 |  | Transmission failure
2013-09-09 | SS14 | URBAN | 597.7265 | 0 | 11768.1456 | 5 | 0.018181 | 0.00092346 | 0 |  | Transmission failure
2013-09-09 | SVW54 | URBAN | 600.5773 | 0 | 11824.2735 | 5 | 0.018268 | 0.00092786 | 0 |  | Transmission failure
2013-09-09 | SVW55 | URBAN | 787.7826 | 0 | 15510.0043 | 5 | 0.023962 | 0.0012171 | 0 |  | Transmission failure
2013-09-09 | NP31 | URBAN | 921.7722 | 0 | 18148.0146 | 5 | 0.028038 | 0.0014241 | 0 |  | Transmission failure
2013-09-09 | SVW41 | URBAN | 946.4795 | 0 | 18634.4563 | 5 | 0.028789 | 0.0014623 | 0 |  | Transmission failure
2013-09-09 | SV21 | URBAN | 993.9935 | 0 | 19569.921 | 5 | 0.030235 | 0.0015357 | 0 |  | Transmission failure
2013-09-09 | SV16 | URBAN | 1021.5516 | 0 | 20112.4905 | 5 | 0.031073 | 0.0015782 | 0 |  | Transmission failure
2013-09-09 | SS12 | URBAN | 1036.7561 | 0 | 20411.8392 | 5 | 0.031535 | 0.0016017 | 0 |  | Transmission failure
2013-09-09 | SS22 | URBAN | 1172.6462 | 0 | 23087.2681 | 5 | 0.035669 | 0.0018117 | 0 |  | Transmission failure
2013-09-09 | SV33 | URBAN | 1411.1667 | 0 | 27783.3008 | 5 | 0.042924 | 0.0021802 | 0 |  | Transmission failure
2013-09-09 | SS13 | URBAN | 1828.3398 | 0 | 35996.6806 | 5 | 0.055613 | 0.0028247 | 0 |  | Transmission failure
2013-09-09 | SVW53 | URBAN | 1870.1522 | 0 | 36819.8895 | 5 | 0.056885 | 0.0028893 | 0 |  | Transmission failure
2013-09-09 | SV32 | URBAN | 1954.7272 | 0 | 38485.0166 | 5 | 0.059457 | 0.00302 | 0 |  | Transmission failure
2013-09-09 | SS11 | URBAN | 1987.987 | 0 | 39139.8419 | 5 | 0.060469 | 0.0030713 | 0 |  | Transmission failure
2013-09-09 | NP24 | URBAN | 2245.513 | 0 | 44210.0604 | 5 | 0.068302 | 0.0034692 | 0 |  | Transmission failure
2013-09-09 | NP34 | URBAN | 2764.3662 | 0 | 54425.3347 | 5 | 0.084084 | 0.0042708 | 0 |  | Transmission failure
2013-09-09 | NP33 | URBAN | 3152.0807 | 0 | 62058.7264 | 5 | 0.095878 | 0.0048698 | 0 |  | Transmission failure
2013-09-09 | SS23 | URBAN | 3353.5402 | 0 | 66025.0966 | 5 | 0.10201 | 0.005181 | 0 |  | Transmission failure
2013-09-09 | NP23 | URBAN | 3785.9179 | 0 | 74537.8251 | 5 | 0.11516 | 0.0058491 | 0 |  | Transmission failure
2013-09-09 | NP36 | URBAN | 4254.4062 | 0 | 83761.5068 | 5 | 0.12941 | 0.0065728 | 0 |  | Transmission failure
2013-09-09 | NP25 | URBAN | 4421.6556 | 0 | 87054.3424 | 5 | 0.13449 | 0.0068312 | 0 |  | Transmission failure
2013-09-09 | CM14 | URBAN | 8.9428 | 0 | 239.8619 | 5 | 0.00037057 | 1.3816e-05 | 0 |  | Transmission failure
2013-09-09 | CM11 | URBAN | 47.6951 | 0 | 1279.2635 | 5 | 0.0019764 | 7.3686e-05 | 0 |  | Transmission failure
2013-09-09 | CM21 | URBAN | 59.6188 | 0 | 1599.0794 | 5 | 0.0024705 | 9.2108e-05 | 0 |  | Transmission failure
2013-09-09 | CM15 | URBAN | 69.5553 | 0 | 1865.5926 | 5 | 0.0028822 | 0.00010746 | 0 |  | Transmission failure
2013-09-09 | CM23 | URBAN | 94.3965 | 0 | 2531.8757 | 5 | 0.0039116 | 0.00014584 | 0 |  | Transmission failure
2013-09-09 | HT6 | URBAN | 156.0026 | 0 | 4184.2578 | 5 | 0.0064645 | 0.00024102 | 0 |  | Transmission failure
2013-09-09 | CM12 | URBAN | 179.8501 | 0 | 4823.8895 | 5 | 0.0074527 | 0.00027786 | 0 |  | Transmission failure
2013-09-09 | SR12 | URBAN | 271.2656 | 0 | 7275.8113 | 5 | 0.011241 | 0.00041909 | 0 |  | Transmission failure
2013-09-09 | HT9 | URBAN | 277.2275 | 0 | 7435.7192 | 5 | 0.011488 | 0.0004283 | 0 |  | Transmission failure
2013-09-09 | MC10 | URBAN | 287.164 | 0 | 7702.2325 | 5 | 0.0119 | 0.00044365 | 0 |  | Transmission failure
2013-09-09 | HT13 | URBAN | 295.1131 | 0 | 7915.4431 | 5 | 0.012229 | 0.00045593 | 0 |  | Transmission failure
2013-09-09 | CM24 | URBAN | 307.0369 | 0 | 8235.259 | 5 | 0.012723 | 0.00047436 | 0 |  | Transmission failure
2013-09-09 | MC4 | URBAN | 325.9162 | 0 | 8741.6341 | 5 | 0.013505 | 0.00050352 | 0 |  | Transmission failure
2013-09-09 | HT4 | URBAN | 331.8781 | 0 | 8901.542 | 5 | 0.013752 | 0.00051273 | 0 |  | Transmission failure
2013-09-09 | MC5 | URBAN | 335.8527 | 0 | 9008.1473 | 5 | 0.013917 | 0.00051888 | 0 |  | Transmission failure
2013-09-09 | HT7 | URBAN | 346.7828 | 0 | 9301.3119 | 5 | 0.01437 | 0.00053576 | 0 |  | Transmission failure
2013-09-09 | MC9 | URBAN | 348.7701 | 0 | 9354.6145 | 5 | 0.014452 | 0.00053883 | 0 |  | Transmission failure
2013-09-09 | HT8 | URBAN | 364.6684 | 0 | 9781.0357 | 5 | 0.015111 | 0.00056339 | 0 |  | Transmission failure
2013-09-09 | HT3 | URBAN | 370.6303 | 0 | 9940.9437 | 5 | 0.015358 | 0.0005726 | 0 |  | Transmission failure
2013-09-09 | CM22 | URBAN | 392.4905 | 0 | 10527.2728 | 5 | 0.016264 | 0.00060638 | 0 |  | Transmission failure
2013-09-09 | M21 | URBAN | 480.9251 | 0 | 12899.2406 | 5 | 0.019929 | 0.000743 | 0 |  | Transmission failure
2013-09-09 | M31 | URBAN | 586.2517 | 0 | 15724.2808 | 5 | 0.024293 | 0.00090573 | 0 |  | Transmission failure
2013-09-09 | HT10 | URBAN | 587.2453 | 0 | 15750.9322 | 5 | 0.024334 | 0.00090726 | 0 |  | Transmission failure
2013-09-09 | NB15 | URBAN | 610.0992 | 0 | 16363.9126 | 5 | 0.025281 | 0.00094257 | 0 |  | Transmission failure
2013-09-09 | MR23 | URBAN | 642.8895 | 0 | 17243.4063 | 5 | 0.02664 | 0.00099323 | 0 |  | Transmission failure
2013-09-09 | BT5 | URBAN | 721.3877 | 0 | 19348.8608 | 5 | 0.029893 | 0.0011145 | 0 |  | Transmission failure
2013-09-09 | MR13 | URBAN | 732.3178 | 0 | 19642.0254 | 5 | 0.030346 | 0.0011314 | 0 |  | Transmission failure
2013-09-09 | SR14 | URBAN | 737.286 | 0 | 19775.282 | 5 | 0.030552 | 0.0011391 | 0 |  | Transmission failure
2013-09-09 | M34 | URBAN | 774.0509 | 0 | 20761.381 | 5 | 0.032075 | 0.0011959 | 0 |  | Transmission failure
2013-09-09 | M33 | URBAN | 780.0128 | 0 | 20921.2889 | 5 | 0.032322 | 0.0012051 | 0 |  | Transmission failure
2013-09-09 | NB13 | URBAN | 787.962 | 0 | 21134.4995 | 5 | 0.032652 | 0.0012174 | 0 |  | Transmission failure
2013-09-09 | NB11 | URBAN | 804.854 | 0 | 21587.572 | 5 | 0.033352 | 0.0012435 | 0 |  | Transmission failure
2013-09-09 | SR19 | URBAN | 811.8095 | 0 | 21774.1313 | 5 | 0.03364 | 0.0012542 | 0 |  | Transmission failure
2013-09-09 | M23 | URBAN | 820.7523 | 0 | 22013.9932 | 5 | 0.03401 | 0.001268 | 0 |  | Transmission failure
2013-09-09 | CM13 | URBAN | 887.3267 | 0 | 23799.6319 | 5 | 0.036769 | 0.0013709 | 0 |  | Transmission failure
2013-09-09 | SR25 | URBAN | 913.1615 | 0 | 24492.5663 | 5 | 0.03784 | 0.0014108 | 0 |  | Transmission failure
2013-09-09 | BT6 | URBAN | 926.0789 | 0 | 24839.0335 | 5 | 0.038375 | 0.0014307 | 0 |  | Transmission failure
2013-09-09 | MR11 | URBAN | 1006.5643 | 0 | 26997.7907 | 5 | 0.04171 | 0.0015551 | 0 |  | Transmission failure
2013-09-09 | BT15 | URBAN | 1019.4817 | 0 | 27344.2579 | 5 | 0.042245 | 0.001575 | 0 |  | Transmission failure
2013-09-09 | MR21 | URBAN | 1027.4309 | 0 | 27557.4685 | 5 | 0.042575 | 0.0015873 | 0 |  | Transmission failure
2013-09-09 | BR10 | URBAN | 1030.4118 | 0 | 27637.4224 | 5 | 0.042698 | 0.0015919 | 0 |  | Transmission failure
2013-09-09 | M35 | URBAN | 1051.2784 | 0 | 28197.1002 | 5 | 0.043563 | 0.0016242 | 0 |  | Transmission failure
2013-09-09 | MR24 | URBAN | 1096.9862 | 0 | 29423.0611 | 5 | 0.045457 | 0.0016948 | 0 |  | Transmission failure
2013-09-09 | BT14 | URBAN | 1099.9671 | 0 | 29503.0151 | 5 | 0.045581 | 0.0016994 | 0 |  | Transmission failure
2013-09-09 | NB14 | URBAN | 1121.8274 | 0 | 30089.3442 | 5 | 0.046487 | 0.0017332 | 0 |  | Transmission failure
2013-09-09 | MR31 | URBAN | 1140.7066 | 0 | 30595.7193 | 5 | 0.047269 | 0.0017623 | 0 |  | Transmission failure
2013-09-09 | SR11 | URBAN | 1142.6939 | 0 | 30649.022 | 5 | 0.047351 | 0.0017654 | 0 |  | Transmission failure
2013-09-09 | NB23 | URBAN | 1151.6368 | 0 | 30888.8839 | 5 | 0.047722 | 0.0017792 | 0 |  | Transmission failure
2013-09-09 | CM25 | URBAN | 1167.5351 | 0 | 31315.3051 | 5 | 0.048381 | 0.0018038 | 0 |  | Transmission failure
2013-09-09 | SR20 | URBAN | 1168.5288 | 0 | 31341.9564 | 5 | 0.048422 | 0.0018053 | 0 |  | Transmission failure
2013-09-09 | BR6 | URBAN | 1205.2937 | 0 | 32328.0554 | 5 | 0.049945 | 0.0018621 | 0 |  | Transmission failure
2013-09-09 | MR12 | URBAN | 1212.2492 | 0 | 32514.6146 | 5 | 0.050233 | 0.0018729 | 0 |  | Transmission failure
2013-09-09 | HT2 | URBAN | 1220.1984 | 0 | 32727.8252 | 5 | 0.050563 | 0.0018851 | 0 |  | Transmission failure
2013-09-09 | NB25 | URBAN | 1226.1603 | 0 | 32887.7332 | 5 | 0.05081 | 0.0018944 | 0 |  | Transmission failure
2013-09-09 | NB24 | URBAN | 1266.8998 | 0 | 33980.4374 | 5 | 0.052498 | 0.0019573 | 0 |  | Transmission failure
2013-09-09 | BR15 | URBAN | 1272.8617 | 0 | 34140.3454 | 5 | 0.052745 | 0.0019665 | 0 |  | Transmission failure
2013-09-09 | MR32 | URBAN | 1282.7982 | 0 | 34406.8586 | 5 | 0.053157 | 0.0019819 | 0 |  | Transmission failure
2013-09-09 | M25 | URBAN | 1317.5758 | 0 | 35339.6549 | 5 | 0.054598 | 0.0020356 | 0 |  | Transmission failure
2013-09-09 | M22 | URBAN | 1317.5758 | 0 | 35339.6549 | 5 | 0.054598 | 0.0020356 | 0 |  | Transmission failure
2013-09-09 | BR4 | URBAN | 1373.22 | 0 | 36832.129 | 5 | 0.056904 | 0.0021216 | 0 |  | Transmission failure
2013-09-09 | BR13 | URBAN | 1407.004 | 0 | 37738.274 | 5 | 0.058304 | 0.0021737 | 0 |  | Transmission failure
2013-09-09 | BR1 | URBAN | 1450.7245 | 0 | 38910.9323 | 5 | 0.060115 | 0.0022413 | 0 |  | Transmission failure
2013-09-09 | BR9 | URBAN | 1451.7181 | 0 | 38937.5836 | 5 | 0.060157 | 0.0022428 | 0 |  | Transmission failure
2013-09-09 | BT2 | URBAN | 1453.7054 | 0 | 38990.8862 | 5 | 0.060239 | 0.0022459 | 0 |  | Transmission failure
2013-09-09 | M11 | URBAN | 1546.1146 | 0 | 41469.4593 | 5 | 0.064068 | 0.0023887 | 0 |  | Transmission failure
2013-09-09 | MEN12 | URBAN | 1561.0193 | 0 | 41869.2292 | 5 | 0.064686 | 0.0024117 | 0 |  | Transmission failure
2013-09-09 | NB22 | URBAN | 1630.5746 | 0 | 43734.8218 | 5 | 0.067568 | 0.0025192 | 0 |  | Transmission failure
2013-09-09 | M13 | URBAN | 1644.4856 | 0 | 44107.9403 | 5 | 0.068145 | 0.0025406 | 0 |  | Transmission failure
2013-09-09 | SR13 | URBAN | 1721.9901 | 0 | 46186.7436 | 5 | 0.071356 | 0.0026604 | 0 |  | Transmission failure
2013-09-09 | MR15 | URBAN | 1728.9456 | 0 | 46373.3028 | 5 | 0.071644 | 0.0026711 | 0 |  | Transmission failure
2013-09-09 | SR24 | URBAN | 1796.5136 | 0 | 48185.5928 | 5 | 0.074444 | 0.0027755 | 0 |  | Transmission failure
2013-09-09 | MC7 | URBAN | 1806.4501 | 0 | 48452.1061 | 5 | 0.074856 | 0.0027909 | 0 |  | Transmission failure
2013-09-09 | SR23 | URBAN | 1825.3294 | 0 | 48958.4812 | 5 | 0.075638 | 0.00282 | 0 |  | Transmission failure
2013-09-09 | NB21 | URBAN | 1835.2658 | 0 | 49224.9944 | 5 | 0.07605 | 0.0028354 | 0 |  | Transmission failure
2013-09-09 | MR22 | URBAN | 1892.8973 | 0 | 50770.7712 | 5 | 0.078438 | 0.0029244 | 0 |  | Transmission failure
2013-09-09 | NB12 | URBAN | 1943.5733 | 0 | 52129.9887 | 5 | 0.080538 | 0.0030027 | 0 |  | Transmission failure
2013-09-09 | BT10 | URBAN | 1958.478 | 0 | 52529.7585 | 5 | 0.081156 | 0.0030257 | 0 |  | Transmission failure
2013-09-09 | BT4 | URBAN | 1959.4717 | 0 | 52556.4099 | 5 | 0.081197 | 0.0030273 | 0 |  | Transmission failure
2013-09-09 | BT9 | URBAN | 1974.3764 | 0 | 52956.1797 | 5 | 0.081815 | 0.0030503 | 0 |  | Transmission failure
2013-09-09 | M32 | URBAN | 1985.3065 | 0 | 53249.3443 | 5 | 0.082268 | 0.0030672 | 0 |  | Transmission failure
2013-09-09 | HT1 | URBAN | 2020.0842 | 0 | 54182.1406 | 5 | 0.083709 | 0.0031209 | 0 |  | Transmission failure
2013-09-09 | SR15 | URBAN | 2022.0714 | 0 | 54235.4433 | 5 | 0.083791 | 0.003124 | 0 |  | Transmission failure
2013-09-09 | MC1 | URBAN | 2035.9825 | 0 | 54608.5618 | 5 | 0.084367 | 0.0031455 | 0 |  | Transmission failure
2013-09-09 | MR14 | URBAN | 2252.5975 | 0 | 60418.5503 | 5 | 0.093344 | 0.0034801 | 0 |  | Transmission failure
2013-09-09 | HT11 | URBAN | 2301.2862 | 0 | 61724.4651 | 5 | 0.095361 | 0.0035554 | 0 |  | Transmission failure
2013-09-09 | MC2 | URBAN | 2458.2824 | 0 | 65935.3743 | 5 | 0.10187 | 0.0037979 | 0 |  | Transmission failure
2013-09-09 | MC3 | URBAN | 2556.6535 | 0 | 68573.8553 | 5 | 0.10594 | 0.0039499 | 0 |  | Transmission failure
2013-09-09 | MC6 | URBAN | 2666.9483 | 0 | 71532.1522 | 5 | 0.11051 | 0.0041203 | 0 |  | Transmission failure
2013-09-09 | HT6 | URBAN | 0 | 0 | 705.6041 | 5 | 0.0010901 | 0 | 0 |  | Transmission failure
2013-09-09 | HT9 | URBAN | 0 | 0 | 1253.9079 | 5 | 0.0019372 | 0 | 0 |  | Transmission failure
2013-09-09 | HT13 | URBAN | 0 | 0 | 1334.8052 | 5 | 0.0020622 | 0 | 0 |  | Transmission failure
2013-09-09 | HT4 | URBAN | 0 | 0 | 1501.0941 | 5 | 0.0023191 | 0 | 0 |  | Transmission failure
2013-09-09 | HT7 | URBAN | 0 | 0 | 1568.5085 | 5 | 0.0024233 | 0 | 0 |  | Transmission failure
2013-09-09 | HT8 | URBAN | 0 | 0 | 1649.4058 | 5 | 0.0025482 | 0 | 0 |  | Transmission failure
2013-09-09 | HT3 | URBAN | 0 | 0 | 1676.3716 | 5 | 0.0025899 | 0 | 0 |  | Transmission failure
2013-09-09 | HT10 | URBAN | 0 | 0 | 2656.1276 | 5 | 0.0041036 | 0 | 0 |  | Transmission failure
2013-09-09 | HT2 | URBAN | 0 | 0 | 5518.9927 | 5 | 0.0085266 | 0 | 0 |  | Transmission failure
2013-09-09 | HT1 | URBAN | 0 | 0 | 9136.8991 | 5 | 0.014116 | 0 | 0 |  | Transmission failure
2013-09-09 | HT11 | URBAN | 0 | 0 | 10408.7842 | 5 | 0.016081 | 0 | 0 |  | Transmission failure
2013-09-19 | HGS21 | URBAN | 1.967 | 0 | 17.8341 | 5 | 2.7553e-05 | 3.0389e-06 | 0 |  | Transmission failure
2013-09-19 | HGS31 | RURAL SHORT | 2013.21 | 0 | 18253.1712 | 5 | 0.0282 | 0.0031103 | 0 |  | Transmission failure
2013-09-19 | HGS22 | RURAL SHORT | 2919.007 | 0 | 26465.7607 | 5 | 0.040888 | 0.0045097 | 0 |  | Transmission failure
2013-09-19 | HGS32 | URBAN | 3111.7716 | 0 | 28213.4996 | 5 | 0.043588 | 0.0048075 | 0 |  | Transmission failure
2013-09-19 | HGS33 | RURAL SHORT | 3815.9525 | 0 | 34598.0968 | 5 | 0.053452 | 0.0058955 | 0 |  | Transmission failure
2013-09-19 | HGS23 | RURAL SHORT | 4880.0919 | 0 | 44246.329 | 5 | 0.068358 | 0.0075395 | 0 |  | Transmission failure
2013-09-19 | DMA15 | RURAL SHORT | 1684.5577 | 0 | 18782.8188 | 5 | 0.029018 | 0.0026026 | 0 |  | Transmission failure
2013-09-19 | RBD12 | RURAL SHORT | 2239.083 | 0 | 24965.7752 | 5 | 0.038571 | 0.0034593 | 0 |  | Transmission failure
2013-09-19 | DMA14 | URBAN | 2409.9367 | 0 | 26870.7942 | 5 | 0.041514 | 0.0037232 | 0 |  | Transmission failure
2013-09-19 | DMA13 | RURAL SHORT | 2807.5962 | 0 | 31304.698 | 5 | 0.048364 | 0.0043376 | 0 |  | Transmission failure
2013-09-19 | RBD24 | URBAN | 3075.367 | 0 | 34290.3418 | 5 | 0.052977 | 0.0047513 | 0 |  | Transmission failure
2013-09-19 | DMA11 | URBAN | 3163.2917 | 0 | 35270.7025 | 5 | 0.054491 | 0.0048871 | 0 |  | Transmission failure
2013-09-19 | RBD13 | URBAN | 3481.0197 | 0 | 38813.3694 | 5 | 0.059965 | 0.005378 | 0 |  | Transmission failure
2013-09-19 | RBD21 | RURAL SHORT | 4678.994 | 0 | 52170.7832 | 5 | 0.080601 | 0.0072288 | 0 |  | Transmission failure
2013-09-19 | RBD23 | URBAN | 4792.8965 | 0 | 53440.7959 | 5 | 0.082563 | 0.0074048 | 0 |  | Transmission failure
2013-09-19 | DMA12 | URBAN | 4825.8683 | 0 | 53808.4311 | 5 | 0.083131 | 0.0074557 | 0 |  | Transmission failure
2013-09-19 | RBD14 | URBAN | 7342.7134 | 0 | 81871.2547 | 5 | 0.12649 | 0.011344 | 0 |  | Transmission failure
2013-09-19 | RBD22 | URBAN | 9722.6758 | 0 | 108407.8351 | 5 | 0.16748 | 0.015021 | 0 |  | Transmission failure
2013-09-19 | MTN32 | RURAL SHORT | 774.9859 | 0 | 5290.5636 | 5 | 0.0081737 | 0.0011973 | 0 |  | Transmission failure
2013-09-19 | MTN22 | RURAL SHORT | 1017.922 | 0 | 6949.0045 | 5 | 0.010736 | 0.0015726 | 0 |  | Transmission failure
2013-09-19 | MTN24 | RURAL SHORT | 1622.2504 | 0 | 11074.5475 | 5 | 0.01711 | 0.0025063 | 0 |  | Transmission failure
2013-09-19 | MTN23 | URBAN | 2173.3738 | 0 | 14836.8784 | 5 | 0.022922 | 0.0033578 | 0 |  | Transmission failure
2013-09-19 | MTN35 | RURAL SHORT | 2470.5187 | 0 | 16865.3846 | 5 | 0.026056 | 0.0038168 | 0 |  | Transmission failure
2013-09-19 | MTN21 | URBAN | 2736.5436 | 0 | 18681.4459 | 5 | 0.028862 | 0.0042278 | 0 |  | Transmission failure
2013-09-19 | MTN34 | URBAN | 3793.6165 | 0 | 25897.7198 | 5 | 0.040011 | 0.0058609 | 0 |  | Transmission failure
2013-09-19 | MTN31 | URBAN | 5914.7891 | 0 | 40378.239 | 5 | 0.062382 | 0.009138 | 0 |  | Transmission failure
2013-09-19 | FSH32 | RURAL SHORT | 942.7544 | 0 | 2199.7287 | 5 | 0.0033985 | 0.0014565 | 0 |  | Transmission failure
2013-09-19 | FSH23 | URBAN | 1195.0266 | 0 | 2788.3555 | 5 | 0.0043079 | 0.0018463 | 0 |  | Transmission failure
2013-09-19 | FSH12 | URBAN | 1555.8462 | 0 | 3630.256 | 5 | 0.0056086 | 0.0024037 | 0 |  | Transmission failure
2013-09-19 | FSH21 | RURAL SHORT | 1990.0359 | 0 | 4643.3507 | 5 | 0.0071737 | 0.0030745 | 0 |  | Transmission failure
2013-09-19 | FSH22 | URBAN | 2325.7288 | 0 | 5426.6229 | 5 | 0.0083839 | 0.0035931 | 0 |  | Transmission failure
2013-09-19 | FSH11 | URBAN | 2418.1951 | 0 | 5642.3746 | 5 | 0.0087172 | 0.003736 | 0 |  | Transmission failure
2013-09-19 | FSH13 | URBAN | 3218.2297 | 0 | 7509.0953 | 5 | 0.011601 | 0.004972 | 0 |  | Transmission failure
2013-09-19 | FSH34 | URBAN | 3221.2449 | 0 | 7516.1307 | 5 | 0.011612 | 0.0049767 | 0 |  | Transmission failure
2013-09-19 | FSH31 | URBAN | 3713.7285 | 0 | 8665.2428 | 5 | 0.013387 | 0.0057375 | 0 |  | Transmission failure
2013-09-19 | FSH33 | URBAN | 3809.21 | 0 | 8888.0298 | 5 | 0.013732 | 0.005885 | 0 |  | Transmission failure
2013-10-01 | EB31 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0030497 | MED | Vegetation
2013-10-01 | M23 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0016083 | MED | Weather
2013-10-01 | EM3 | URBAN | 358 | 0 | 63446.55 |  | 0.098022 | 0.00055309 | 0 | MED | Vegetation
2013-10-01 | OR13 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0017211 | MED | Vegetation
2013-10-01 | HT3 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.00057627 | MED | Equipment failure
2013-10-01 | CDA23 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0021985 | MED | Vegetation
2013-10-01 | NB21 | URBAN | 2440 | 0 | 351799.4017 |  | 0.54351 | 0.0037697 | 0 | MED | Vegetation
2013-10-01 | CDA22 | URBAN | 1972 | 0 | 477651.3324 |  | 0.73795 | 0.0030466 | 0 | MED | Vegetation
2013-10-01 | CDA23 | URBAN | 1423 | 0 | 139264.3141 |  | 0.21516 | 0.0021985 | 0 | MED | Vegetation
2013-10-01 | SS14 | URBAN | 627 | 0 | 63227.0499 |  | 0.097683 | 0.00096868 | 0 | MED | Vegetation
2013-10-01 | NP23 | URBAN | 1674 | 0 | 1048649.3442 |  | 1.6201 | 0.0025862 | 0 | MED | Vegetation
2013-10-01 | NP15 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.00013132 | MED | Vegetation
2013-10-01 | NP18 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.00077645 | MED | Vegetation
2013-10-01 | NP31 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0015907 | MED | Vegetation
2013-10-01 | NP34 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0022932 | MED | Vegetation
2013-10-01 | NP12 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0025296 | MED | Vegetation
2013-10-01 | NP25 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0027988 | MED | Vegetation
2013-10-01 | NP24 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0032946 | MED | Vegetation
2013-10-01 | NP11 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0035277 | MED | Vegetation
2013-10-01 | NP33 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0044568 | MED | Vegetation
2013-10-01 | NP14 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0053991 | MED | Vegetation
2013-10-01 | NP36 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0062297 | MED | Vegetation
2013-10-01 | NP16 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0064562 | MED | Vegetation
2013-10-01 | OR9 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0023869 | MED | Vegetation
2013-10-01 | BR15 | URBAN | 1281 | 0 | 638503.3355 |  | 0.98646 | 0.0019791 | 0 | MED | Vegetation
2013-10-01 | EL13 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0017643 | MED | Vegetation
2013-10-01 | NB25 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0031548 | MED | Vegetation
2013-10-01 | DC8 | URBAN | 1687 | 0 | 276745 |  | 0.42756 | 0.0026063 | 0 | MED | Vegetation
2013-10-01 | DSH32 | URBAN | 185 | 0 | 73753.5292 |  | 0.11395 | 0.00028582 | 0 | MED | Vegetation
2013-10-01 | DSH14 | URBAN | 141 | 0 | 183.3 |  | 0.00028319 | 0.00021784 | 0 | MED | Vegetation
2013-10-01 | EB12 | URBAN | 1787 | 0 | 309965.7071 |  | 0.47888 | 0.0027608 | 0 | MED | Vegetation
2013-10-01 | DVY24 | RURAL SHORT | 1235 | 0 | 357331.4515 |  | 0.55206 | 0.001908 | 0 | MED | Vegetation
2013-10-01 | DN24 | URBAN | 60 | 0 | 18217.002 |  | 0.028144 | 9.2697e-05 | 0 | MED | Vegetation
2013-10-01 | DVY34 | URBAN | 713 | 0 | 227224.131 |  | 0.35105 | 0.0011015 | 0 | MED | Vegetation
2013-10-01 | FTN23 | URBAN | 2632 | 0 | 464284.8 |  | 0.7173 | 0.0040663 | 0 | MED | Vegetation
2013-10-01 | FSH31 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0031811 | MED | Weather
2013-10-01 | LWN31 | RURAL SHORT | 4374 | 0 | 237988.629 |  | 0.36768 | 0.0067576 | 0 | MED | Vegetation
2013-10-01 | NW32 | URBAN | 760 | 0 | 127262 |  | 0.19661 | 0.0011742 | 0 | MED | Equipment failure
2013-10-01 | NW33 | URBAN | 2349 | 0 | 204088.8717 |  | 0.31531 | 0.0036291 | 0 | MED | Vegetation
2013-10-01 | BR15 | URBAN | 1 | 0 | 425.5833 |  | 0.0006575 | 1.5449e-06 | 0 | MED | Inter-distributor connection failure
2013-10-01 | HGS33 | RURAL SHORT | 1699 | 0 | 351129.9655 |  | 0.54248 | 0.0026249 | 0 | MED | Vegetation
2013-10-01 | CRM33 | URBAN | 1 | 0 | 1473.5833 |  | 0.0022766 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | BU6 | URBAN | 26.73 | 0 | 6460.6954 |  | 0.0099814 | 4.1296e-05 | 0 | MED | Weather
2013-10-01 | EL13 | URBAN | 23.1 | 0 | 10628.31 |  | 0.01642 | 3.5688e-05 | 0 | MED | Vegetation
2013-10-01 | MR32 | URBAN | 12.07 | 0 | 2552.805 |  | 0.003944 | 1.8648e-05 | 0 | MED | Weather
2013-10-01 | FSH13 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 1.5449e-06 | MED | Other
2013-10-01 | NP34 | URBAN | 3.55 | 0 | 2415.7157 |  | 0.0037322 | 5.4846e-06 | 0 | MED | Other
2013-10-01 | FTN25 | URBAN | 1 | 0 | 304.8333 |  | 0.00047095 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | LWN31 | RURAL SHORT | 515 | 0 | 30923.0165 |  | 0.047774 | 0.00079565 | 0 | MED | Weather
2013-10-01 | SS22 | URBAN | 22.77 | 0 | 16000.0987 |  | 0.024719 | 3.5178e-05 | 0 | MED | Equipment failure
2013-10-01 | NW33 | URBAN | 2351 | 0 | 31987.15 |  | 0.049419 | 0.0036322 | 0 | MED | Vegetation
2013-10-01 | FSH32 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0.0047461 | MED | Vegetation
2013-10-01 | OR13 | URBAN | 19.8 | 0 | 9254.52 |  | 0.014298 | 3.059e-05 | 0 | MED | Weather
2013-10-01 | LWN31 | RURAL SHORT | 10 | 0 | 40.333 |  | 6.2312e-05 | 1.5449e-05 | 0 | MED | Weather
2013-10-01 | OR9 | URBAN | 387 | 0 | 79341.4629 |  | 0.12258 | 0.0005979 | 0 | MED | Vegetation
2013-10-01 | BT4 | URBAN | 1 | 0 | 367.3 |  | 0.00056746 | 1.5449e-06 | 0 | MED | Weather
2013-10-01 | RD4 | URBAN | 1965 | 0 | 498192.9345 |  | 0.76968 | 0.0030358 | 0 | MED | Vegetation
2013-10-01 | HGS33 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0.00025337 | MED | Weather
2013-10-01 | FTN23 | URBAN | 1 | 0 | 1103.8333 |  | 0.0017054 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | DSH32 | URBAN | 1 | 0 | 1316.8333 |  | 0.0020344 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | HGS33 | RURAL SHORT | 1287 | 0 | 2316.6 |  | 0.003579 | 0.0019883 | 0 | MED | Weather
2013-10-01 | DN24 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 1.5449e-06 | MED | Vegetation
2013-10-01 | DN10 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0048728 | MED | Vegetation
2013-10-01 | NW32 | URBAN | 324 | 0 | 49801.7347 |  | 0.076941 | 0.00050056 | 0 | MED | Equipment failure
2013-10-01 | DSH24 | URBAN | 161 | 0 | 128652.4113 |  | 0.19876 | 0.00024874 | 0 | MED | Weather
2013-10-01 | DN10 | URBAN | 162 | 0 | 28101.6054 |  | 0.043416 | 0.00025028 | 0 | MED | Vegetation
2013-10-01 | NW21 | URBAN | 3013 | 0 | 129267.2843 |  | 0.19971 | 0.0046549 | 0 | MED | Vegetation
2013-10-01 | EB21 | URBAN | 100 | 0 | 5043 |  | 0.0077912 | 0.00015449 | 0 | MED | Third party impacts
2013-10-01 | EW14 | URBAN | 1983 | 0 | 135818.2724 |  | 0.20983 | 0.0030636 | 0 | MED | Vegetation
2013-10-01 | NW32 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0.0006736 | MED | Vegetation
2013-10-01 | BR4 | URBAN | 1 | 0 | 412.6333 |  | 0.0006375 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | CDA24 | URBAN | 1 | 0 | 189.4667 |  | 0.00029272 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | NP14 | URBAN | 308 | 0 | 17545.7436 |  | 0.027107 | 0.00047584 | 0 | MED | Vegetation
2013-10-01 | NP12 | URBAN | 29.7 | 0 | 16070.67 |  | 0.024828 | 4.5885e-05 | 0 | MED | Equipment failure
2013-10-01 | HGS33 | RURAL SHORT | 1650 | 0 | 3684.945 |  | 0.0056931 | 0.0025492 | 0 | MED | Weather
2013-10-01 | CDA11 | URBAN | 5136 | 0 | 249284.7696 |  | 0.38513 | 0.0079349 | 0 | MED | Vegetation
2013-10-01 | SS12 | URBAN | 1 | 0 | 183.4833 |  | 0.00028347 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | DVY34 | URBAN | 1 | 0 | 1233 |  | 0.0019049 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | LWN33 | URBAN | 1 | 0 | 175.1167 |  | 0.00027055 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | CDA11 | URBAN | 1 | 0 | 239.7667 |  | 0.00037043 | 1.5449e-06 | 0 | MED | Inter-distributor connection failure
2013-10-01 | FSH13 | URBAN | 1955 | 0 | 319985.8985 |  | 0.49436 | 0.0030204 | 0 | MED | Vegetation
2013-10-01 | MC1 | URBAN | 4534 | 0 | 493902.877 |  | 0.76305 | 0.0070048 | 0 | MED | Vegetation
2013-10-01 | DSH24 | URBAN | 3634 | 0 | 705237.0518 |  | 1.0896 | 0.0056143 | 0 | MED | Vegetation
2013-10-01 | LD33 | URBAN | 3103 | 0 | 527028.9777 |  | 0.81423 | 0.004794 | 0 | MED | Vegetation
2013-10-01 | NW32 | URBAN | 722 | 0 | 41515 |  | 0.064139 | 0.0011155 | 0 | MED | Vegetation
2013-10-01 | NP24 | URBAN | 22.44 | 0 | 9769.6287 |  | 0.015094 | 3.4669e-05 | 0 | MED | Equipment failure
2013-10-01 | NB25 | URBAN | 38.86 | 0 | 11128.855 |  | 0.017194 | 6.0037e-05 | 0 | MED | Weather
2013-10-01 | DVY24 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0.0010181 | MED | Other
2013-10-01 | NP25 | URBAN | 76 | 0 | 22224.9308 |  | 0.034336 | 0.00011742 | 0 | MED | Other
2013-10-01 | BR4 | URBAN | 1 | 0 | 0 |  | 0 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | SS23 | URBAN | 14.85 | 0 | 6227.3475 |  | 0.0096209 | 2.2942e-05 | 0 | MED | Equipment failure
2013-10-01 | EW3 | URBAN | 6.93 | 0 | 3157.7702 |  | 0.0048786 | 1.0706e-05 | 0 | MED | Vegetation
2013-10-01 | NP14 | URBAN | 2 | 0 | 2177.1666 |  | 0.0033636 | 3.0899e-06 | 0 | MED | Vegetation
2013-10-01 | OE4 | URBAN | 34.98 | 0 | 7411.6778 |  | 0.011451 | 5.4042e-05 | 0 | MED | Equipment failure
2013-10-01 | SR19 | URBAN | 95.04 | 0 | 25166.592 |  | 0.038881 | 0.00014683 | 0 | MED | Vegetation
2013-10-01 | RWT18 | URBAN | 254 | 0 | 62136.8582 |  | 0.095998 | 0.00039242 | 0 | MED | Vegetation
2013-10-01 | OE4 | URBAN | 24.42 | 0 | 3743.1782 |  | 0.005783 | 3.7728e-05 | 0 | MED | Equipment failure
2013-10-01 | WD36 | URBAN | 1 | 0 | 117.85 |  | 0.00018207 | 1.5449e-06 | 0 | MED | Weather
2013-10-01 | BW34 | URBAN | 18.81 | 0 | 7472.8989 |  | 0.011545 | 2.906e-05 | 0 | MED | Equipment failure
2013-10-01 | NB11 | URBAN | 19.14 | 0 | 5295.081 |  | 0.0081806 | 2.957e-05 | 0 | MED | Weather
2013-10-01 | OR6 | URBAN | 1 | 0 | 95.55 |  | 0.00014762 | 1.5449e-06 | 0 | MED | Other
2013-10-01 | NP12 | URBAN | 49.6 | 0 | 18896.7717 |  | 0.029195 | 7.6629e-05 | 0 | MED | Weather
2013-10-01 | LWN31 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0 | MED | Vegetation
2013-10-01 | SVW55 | URBAN | 24.75 | 0 | 13190.9258 |  | 0.020379 | 3.8237e-05 | 0 | MED | Vegetation
2013-10-01 | OR13 | URBAN | 26.24 | 0 | 12404.0862 |  | 0.019164 | 4.0539e-05 | 0 | MED | Weather
2013-10-01 | NW21 | URBAN | 1 | 0 | 455.8167 |  | 0.00070421 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | BT4 | URBAN | 33.66 | 0 | 6709.5589 |  | 0.010366 | 5.2003e-05 | 0 | MED | Weather
2013-10-01 | BT5 | URBAN | 24.09 | 0 | 8700.5058 |  | 0.013442 | 3.7218e-05 | 0 | MED | Weather
2013-10-01 | BR15 | URBAN | 1 | 0 | 259.1 |  | 0.0004003 | 1.5449e-06 | 0 | MED | Other
2013-10-01 | EB31 | URBAN | 1 | 0 | 362.3833 |  | 0.00055986 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | NP12 | URBAN | 1 | 0 | 653.5833 |  | 0.0010098 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | NW33 | URBAN | 82 | 0 | 30536.732 |  | 0.047178 | 0.00012669 | 0 | MED | Weather
2013-10-01 | NP23 | URBAN | 1 | 0 | 363.7 |  | 0.0005619 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | SS13 | URBAN | 46 | 0 | 30510.2682 |  | 0.047137 | 7.1068e-05 | 0 | MED | Equipment failure
2013-10-01 | CRM35 | URBAN | 1 | 0 | 229.55 |  | 0.00035464 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | DSH24 | URBAN | 6.6 | 0 | 3292.1902 |  | 0.0050863 | 1.0197e-05 | 0 | MED | Vegetation
2013-10-01 | CDA21 | URBAN | 1 | 0 | 231.9167 |  | 0.0003583 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | SS13 | URBAN | 42.24 | 0 | 3368.64 |  | 0.0052044 | 6.5259e-05 | 0 | MED | Vegetation
2013-10-01 | OR4 | URBAN | 22 | 0 | 12298 |  | 0.019 | 3.3989e-05 | 0 | MED | Weather
2013-10-01 | HT13 | URBAN | 5.94 | 0 | 3623.7962 |  | 0.0055986 | 9.177e-06 | 0 | MED | Equipment failure
2013-10-01 | BU10 | URBAN | 26.4 | 0 | 4239.3991 |  | 0.0065497 | 4.0787e-05 | 0 | MED | Weather
2013-10-01 | LWN31 | RURAL SHORT | 1 | 0 | 294.9833 |  | 0.00045573 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | HT7 | URBAN | 3.96 | 0 | 2112.5281 |  | 0.0032637 | 6.118e-06 | 0 | MED | Weather
2013-10-01 | DC5 | URBAN | 8.91 | 0 | 1030.5903 |  | 0.0015922 | 1.3765e-05 | 0 | MED | Vegetation
2013-10-01 | M34 | URBAN | 3.63 | 0 | 1713.8439 |  | 0.0026478 | 5.6082e-06 | 0 | MED | Weather
2013-10-01 | FSH12 | URBAN | 1 | 0 | 0 |  | 0 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | EW9 | URBAN | 189 | 0 | 134952.2937 |  | 0.20849 | 0.000292 | 0 | MED | Vegetation
2013-10-01 | NW21 | URBAN | 394 | 0 | 124241.3202 |  | 0.19195 | 0.00060871 | 0 | MED | Vegetation
2013-10-01 | FSH11 | URBAN | 1 | 0 | 83 |  | 0.00012823 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | BT2 | URBAN | 1 | 0 | 449.2 |  | 0.00069399 | 1.5449e-06 | 0 | MED | Weather
2013-10-01 | FSH12 | URBAN | 1 | 0 | 192.25 |  | 0.00029702 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | DMA12 | URBAN | 1 | 0 | 533.6667 |  | 0.00082449 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | HGS22 | RURAL SHORT | 2811 | 0 | 59276.6847 |  | 0.091579 | 0.0043429 | 0 | MED | Vegetation
2013-10-01 | NB25 | URBAN | 164 | 0 | 5248 |  | 0.0081079 | 0.00025337 | 0 | MED | Vegetation
2013-10-01 | HGS22 | RURAL SHORT | 2541 | 0 | 262042.1512 |  | 0.40484 | 0.0039257 | 0 | MED | Vegetation
2013-10-01 | EB24 | URBAN | 63.65 | 0 | 27682.448 |  | 0.042768 | 9.8336e-05 | 0 | MED | Vegetation
2013-10-01 | CRM35 | URBAN | 1 | 0 | 765.0667 |  | 0.001182 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | DVY24 | RURAL SHORT | 0 | 0 | 0 |  | 0 | 0 | 0.00016685 | MED | Other
2013-10-01 | DC10 | URBAN | 20.77 | 0 | 8035.5661 |  | 0.012415 | 3.2089e-05 | 0 | MED | Equipment failure
2013-10-01 | NP14 | URBAN | 35.64 | 0 | 5381.0448 |  | 0.0083134 | 5.5062e-05 | 0 | MED | Equipment failure
2013-10-01 | HGS23 | RURAL SHORT | 1 | 0 | 447.5833 |  | 0.00069149 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | BR15 | URBAN | 21.12 | 0 | 5974.1447 |  | 0.0092297 | 3.2629e-05 | 0 | MED | Vegetation
2013-10-01 | MC6 | URBAN | 234 | 0 | 69958.2078 |  | 0.10808 | 0.00036152 | 0 | MED | Weather
2013-10-01 | RWT18 | URBAN | 1 | 0 | 117.6833 |  | 0.00018181 | 1.5449e-06 | 0 | MED | Other
2013-10-01 | CRM14 | URBAN | 68 | 0 | 19160.1356 |  | 0.029601 | 0.00010506 | 0 | MED | Vegetation
2013-10-01 | RBD21 | RURAL SHORT | 1 | 0 | 723.7333 |  | 0.0011181 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | MR12 | URBAN | 1 | 0 | 832.5667 |  | 0.0012863 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | HGS23 | RURAL SHORT | 34 | 0 | 14159.8678 |  | 0.021876 | 5.2528e-05 | 0 | MED | Weather
2013-10-01 | HT11 | URBAN | 4.62 | 0 | 2555.1682 |  | 0.0039476 | 7.1377e-06 | 0 | MED | Vegetation
2013-10-01 | DVY24 | RURAL SHORT | 1024 | 0 | 52789.3004 |  | 0.081557 | 0.001582 | 0 | MED | Equipment failure
2013-10-01 | NW21 | URBAN | 1 | 0 | 72.8667 |  | 0.00011258 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | BW23 | URBAN | 1.98 | 0 | 633.6 |  | 0.00097888 | 3.059e-06 | 0 | MED | Weather
2013-10-01 | SS12 | URBAN | 52.47 | 0 | 20286.3853 |  | 0.031341 | 8.1063e-05 | 0 | MED | Equipment failure
2013-10-01 | FSH22 | URBAN | 1 | 0 | 430.2333 |  | 0.00066469 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | SS23 | URBAN | 16.17 | 0 | 6345.6465 |  | 0.0098037 | 2.4982e-05 | 0 | MED | Equipment failure
2013-10-01 | NP14 | URBAN | 10 | 0 | 0 |  | 0 | 1.5449e-05 | 0 | MED | Inter-distributor connection failure
2013-10-01 | RBD14 | URBAN | 1 | 0 | 711.6833 |  | 0.0010995 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | NB25 | URBAN | 1 | 0 | 9.1833 |  | 1.4188e-05 | 1.5449e-06 | 0 | MED | Other
2013-10-01 | DSH32 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 0 | MED | Vegetation
2013-10-01 | DVY24 | RURAL SHORT | 1006 | 0 | 57117.5487 |  | 0.088244 | 0.0015542 | 0 | MED | Equipment failure
2013-10-01 | EL13 | URBAN | 1142 | 0 | 85027.5328 |  | 0.13136 | 0.0017643 | 0 | MED | Equipment failure
2013-10-01 | MR23 | URBAN | 1 | 0 | 353.75 |  | 0.00054653 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | BR13 | URBAN | 1 | 0 | 0 |  | 0 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | NB25 | URBAN | 38.28 | 0 | 27033.9753 |  | 0.041766 | 5.9141e-05 | 0 | MED | Equipment failure
2013-10-01 | MGE34 | URBAN | 1 | 0 | 177.6167 |  | 0.00027441 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | MR21 | URBAN | 1 | 0 | 1039.7667 |  | 0.0016064 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | WD36 | URBAN | 1 | 0 | 1740.15 |  | 0.0026884 | 1.5449e-06 | 0 | MED | Other
2013-10-01 | RWT24 | URBAN | 11.22 | 0 | 957.4396 |  | 0.0014792 | 1.7334e-05 | 0 | MED | Weather
2013-10-01 | DSH14 | URBAN | 2 | 0 | 2468.8666 |  | 0.0038143 | 3.0899e-06 | 0 | MED | Weather
2013-10-01 | DSH24 | URBAN | 0 | 0 | 0 |  | 0 | 0 | 1.5449e-06 | MED | Other
2013-10-01 | BW21 | URBAN | 1 | 0 | 112.2667 |  | 0.00017345 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | HGS22 | RURAL SHORT | 7 | 0 | 2238.6 |  | 0.0034585 | 1.0815e-05 | 0 | MED | Vegetation
2013-10-01 | NP12 | URBAN | 33.66 | 0 | 5094.441 |  | 0.0078707 | 5.2003e-05 | 0 | MED | Equipment failure
2013-10-01 | NP18 | URBAN | 1 | 0 | 230.8333 |  | 0.00035663 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | SS14 | URBAN | 1 | 0 | 329.35 |  | 0.00050883 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | DMA12 | URBAN | 1 | 0 | 113.0333 |  | 0.00017463 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | BU2 | URBAN | 1 | 0 | 178.9 |  | 0.00027639 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | MC6 | URBAN | 25.41 | 0 | 4198.1563 |  | 0.0064859 | 3.9257e-05 | 0 | MED | Operational error
2013-10-01 | FTN24 | URBAN | 1 | 0 | 382.3333 |  | 0.00059069 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | RBD22 | URBAN | 19.8 | 0 | 3328.38 |  | 0.0051422 | 3.059e-05 | 0 | MED | Equipment failure
2013-10-01 | GW11 | URBAN | 1 | 0 | 298.9833 |  | 0.00046191 | 1.5449e-06 | 0 | MED | Vegetation
2013-10-01 | EM10 | URBAN | 1 | 0 | 204.4 |  | 0.00031579 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | FGY21 | URBAN | 1 | 0 | 337.3667 |  | 0.00052121 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | DC2 | URBAN | 1 | 0 | 618.6667 |  | 0.00095581 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | DC6 | URBAN | 24.42 | 0 | 5630.4388 |  | 0.0086987 | 3.7728e-05 | 0 | MED | Weather
2013-10-01 | CDA22 | URBAN | 1 | 0 | 115.0667 |  | 0.00017777 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | HGS22 | RURAL SHORT | 1 | 0 | 824.2 |  | 0.0012733 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | NP23 | URBAN | 12.87 | 0 | 566.28 |  | 0.00087487 | 1.9883e-05 | 0 | MED | Equipment failure
2013-10-01 | NP36 | URBAN | 1 | 0 | 339.9 |  | 0.00052513 | 1.5449e-06 | 0 | MED | Equipment failure
2013-10-01 | MGE34 | URBAN | 2 | 0 | 42.2666 |  | 6.53e-05 | 3.0899e-06 | 0 | MED | Animals
2013-12-07 | DSH13 | URBAN | 0.99395 | 0 | 11.229 | 5 | 1.7348e-05 | 1.5356e-06 | 0 |  | Transmission failure
2013-12-07 | DSH22 | URBAN | 12.9213 | 0 | 145.9776 | 5 | 0.00022553 | 1.9963e-05 | 0 |  | Transmission failure
2013-12-07 | DSH31 | URBAN | 39.7579 | 0 | 449.1618 | 5 | 0.00069393 | 6.1424e-05 | 0 |  | Transmission failure
2013-12-07 | DN2 | URBAN | 71.5643 | 0 | 808.4913 | 5 | 0.0012491 | 0.00011056 | 0 |  | Transmission failure
2013-12-07 | DVY33 | URBAN | 72.5582 | 0 | 819.7203 | 5 | 0.0012664 | 0.0001121 | 0 |  | Transmission failure
2013-12-07 | DVY14 | URBAN | 78.5219 | 0 | 887.0946 | 5 | 0.0013705 | 0.00012131 | 0 |  | Transmission failure
2013-12-07 | DVY13 | URBAN | 82.4977 | 0 | 932.0108 | 5 | 0.0014399 | 0.00012745 | 0 |  | Transmission failure
2013-12-07 | DN9 | URBAN | 86.4735 | 0 | 976.927 | 5 | 0.0015093 | 0.0001336 | 0 |  | Transmission failure
2013-12-07 | DVY32 | URBAN | 137.1648 | 0 | 1549.6083 | 5 | 0.0023941 | 0.00021191 | 0 |  | Transmission failure
2013-12-07 | DSH14 | URBAN | 140.1467 | 0 | 1583.2955 | 5 | 0.0024461 | 0.00021652 | 0 |  | Transmission failure
2013-12-07 | DN4 | URBAN | 152.074 | 0 | 1718.044 | 5 | 0.0026543 | 0.00023495 | 0 |  | Transmission failure
2013-12-07 | DSH33 | URBAN | 156.0498 | 0 | 1762.9602 | 5 | 0.0027237 | 0.00024109 | 0 |  | Transmission failure
2013-12-07 | DVY22 | URBAN | 163.0075 | 0 | 1841.5635 | 5 | 0.0028451 | 0.00025184 | 0 |  | Transmission failure
2013-12-07 | DVY21 | URBAN | 163.0075 | 0 | 1841.5635 | 5 | 0.0028451 | 0.00025184 | 0 |  | Transmission failure
2013-12-07 | DVY23 | RURAL SHORT | 167.9772 | 0 | 1897.7087 | 5 | 0.0029319 | 0.00025952 | 0 |  | Transmission failure
2013-12-07 | DSH23 | URBAN | 172.9469 | 0 | 1953.854 | 5 | 0.0030186 | 0.00026719 | 0 |  | Transmission failure
2013-12-07 | DSH32 | URBAN | 187.8562 | 0 | 2122.2897 | 5 | 0.0032788 | 0.00029023 | 0 |  | Transmission failure
2013-12-07 | DVY31 | URBAN | 191.832 | 0 | 2167.2058 | 5 | 0.0033482 | 0.00029637 | 0 |  | Transmission failure
2013-12-07 | DN24 | URBAN | 194.8138 | 0 | 2200.893 | 5 | 0.0034003 | 0.00030098 | 0 |  | Transmission failure
2013-12-07 | DSH21 | URBAN | 213.6988 | 0 | 2414.2448 | 5 | 0.0037299 | 0.00033015 | 0 |  | Transmission failure
2013-12-07 | DN8 | URBAN | 266.3781 | 0 | 3009.3843 | 5 | 0.0046493 | 0.00041154 | 0 |  | Transmission failure
2013-12-07 | DSH34 | URBAN | 313.0936 | 0 | 3537.1494 | 5 | 0.0054647 | 0.00048371 | 0 |  | Transmission failure
2013-12-07 | DN21 | URBAN | 545.6774 | 0 | 6164.7461 | 5 | 0.0095242 | 0.00084304 | 0 |  | Transmission failure
2013-12-07 | DVY34 | URBAN | 705.7031 | 0 | 7972.6225 | 5 | 0.012317 | 0.0010903 | 0 |  | Transmission failure
2013-12-07 | DN7 | URBAN | 859.765 | 0 | 9713.1246 | 5 | 0.015006 | 0.0013283 | 0 |  | Transmission failure
2013-12-07 | DN25 | URBAN | 950.2143 | 0 | 10734.9678 | 5 | 0.016585 | 0.001468 | 0 |  | Transmission failure
2013-12-07 | DN6 | URBAN | 954.1901 | 0 | 10779.884 | 5 | 0.016654 | 0.0014742 | 0 |  | Transmission failure
2013-12-07 | DVY24 | RURAL SHORT | 1208.6407 | 0 | 13654.5197 | 5 | 0.021096 | 0.0018673 | 0 |  | Transmission failure
2013-12-07 | DN11 | URBAN | 2403.3662 | 0 | 27151.8327 | 5 | 0.041948 | 0.0037131 | 0 |  | Transmission failure
2013-12-07 | DN10 | URBAN | 3245.2402 | 0 | 36662.8345 | 5 | 0.056642 | 0.0050137 | 0 |  | Transmission failure
2013-12-07 | DSH24 | URBAN | 3488.7574 | 0 | 39413.9507 | 5 | 0.060893 | 0.00539 | 0 |  | Transmission failure
2013-12-07 | DN13 | URBAN | 4185.515 | 0 | 47285.5118 | 5 | 0.073054 | 0.0064664 | 0 |  | Transmission failure
2013-12-07 | DN22 | URBAN | 4336.5951 | 0 | 48992.3268 | 5 | 0.075691 | 0.0066998 | 0 |  | Transmission failure
Note:
The AER's Electricity distribution network service providers, Service target performance incentive scheme, November 2009, p. 22, defines SAIDI and SAIFI.
The AER will apply the ESCV's definition of MAIFI for transitional reasons. The ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30, defines MAIFI as follows:
MAIFI - The total number of momentary interruptions divided by the average number of distribution customers over the regulatory reporting period. (where the distribution customers are network or per feeder based, as appropriate).
Contents

## 2. Demand (hidden)
United Energy Distribution Pty Limited
Demand
CY 2013
Table 1 Customer Numbers by Voltage Level
Customer numbers by voltage level
Sub transmission
High Voltage
Low Voltage Residential
Low Voltage Non-Residential
Total - all customers | 0
Table 2 New Customer Connections
Note: 'Total customer numbers' is the total average of end of prior year customers and end of current year customers
New connections
Total new connections
New customer connections as a % of total customers | #DIV/0!
Table 3 Customer Disconnections
Note: 'Total customer numbers' is the total average of end of prior year customers and end of current year customers
Disconnections
Total disconnections
Disconnections as a % of total customers | #DIV/0!
Table 4 Electricity Consumption
Electricity consumption by voltage level (MWh)
Sub transmission
High Voltage
Low Voltage Residential
Low Voltage Non-Residential
Controlled load
Total consumption | 0
Table 5 Maximum Coincident Demand at the Network Level
Note: a) Maximum Coincident Demand at the Network Level is calculated as the sum of all maximum coincident demand for zone substations and all feeders from terminal stations.
b) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
c) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
d) The PoE level only applies to the forecasts
Network coincident maximum demand |  |  |  |  | t+1 forecast
| Forecast | Actual: raw | Actual: weather normalised | Variation %
90% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
50% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
10% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
Table 6 Summer or winter non-coincident maximum demand by zone substation
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
c) The PoE level only applies to the forecasts
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | Nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual: raw |  |  |  | Actual: weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
<ZS 1> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 1> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 2> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 2> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 3> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 3> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS n> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS n> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
Contents

## 3. Asset Installation (hidden)
United Energy Distribution Pty Limited
Asset Installation
CY 2013
Instructions
Insert rows for each of its asset types under each high level asset group. Additional groups may be added if a particular asset is not encompassed by the asset groups in the table.
Develop a set of asset types under the high level asset groups that represent its network asset base.
In determining whether a new asset type is required, whether asset types should be aggregated or whether asset types should be disaggregated, the DNSP should consider:
- the proportion of the overall replacement expenditure forecast for the assets
- the differentiation of unit replacement costs into clear and distinguishable distributions
- the differentiation of replacement lives into clear and distinguishable distributions
- multiple 'end of life' actions such as 'replacement' or 'life extension' (eg pole staking) - in the case of 'life extension', the DNSP should appropriately account for this in defining the replacement life and unit cost for the asset category.
Table 1 For each asset type, provide:
a) the mean replacement asset life (years)
b) the standard deviation of the mean replacement asset life
c) the replacement unit cost ($ nominal).
d) the total number of asset failures during the regulatory year
e) the total quantity (number) of each asset type that was commissioned in the relevant regulatory reporting year.
Table 1 Asset age profile for distribution system assets
Statutory Account code or reference to account code | Asset group | Replacement life (years) |  | Replacement unit cost | Number of asset failures | Total quantity replaced | Total quantity installed | Year Commissioned (number of assets commissioned in each year)
|  | Mean | Standard Deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012
Poles
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Pole top structures
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Conductors
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Underground cables
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Services (incl. LV pillars and LV service pits)
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution transformers
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution switchgear
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution 'other assets'
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone transformers
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone switchgear
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone 'other assets'
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
SCADA and protection
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Other
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Contents

## 4. Customer Service
United Energy Distribution Pty Limited
Customer Service
2013
Table 1 Quality of supply
Over voltage events - due to high voltage injection | 0
Customers receiving over-voltage - due to high voltage injection | 0
Over voltage events - due to lightning | 0
Customers receiving over-voltage - due to lightning | 0
Over voltage events - due to voltage regulation or other cause | 0
Customers receiving over-voltage - due to voltage regulation or other cause | 0
Voltage variations - steady state (zone sub) | 190
Voltage variations - one minute (zone sub) | 4
Voltage variations - 10 seconds (zone sub) Min<0.7 | 1485
Voltage variations - 10 seconds (zone sub) Min<0.8 | 530
Voltage variations - 10 seconds (zone sub) Min<0.9 | 2011
Voltage variations - steady state (feeder) | 1593
Voltage variations - % zone subs monitored | 1
Voltage variations - % feeders monitored | 1
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number | 451
Complaints by category (%)
Low voltage supply | 0.9167%
Voltage dips | 0.5%
Voltage swell | 0%
Voltage spike (impulsive transient) | 0.1667%
TV or radio interference | 0%
Noise from appliances | 0%
Other | 98.42%
Complaints by Likely Cause (%)
Network equipment faulty | 0.1667%
Network interference by NSP equipment | 0%
Network interference by another customer | 0%
Network limitation | 0.25%
Customer internal problem | 0%
No problem identified | 0.1667%
Environmental | 0.25%
Other | 99.17%
Table 3 Customer service
Timely provision of services
Connections made | 11696
Connections not made on agreed date | 258
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 3462
Streetlights - not repaired by "fix by" date | 364
Streetlights - average number of days to repair | 127.9
Total streetlights | 118739
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 234156
Calls to fault line not answered within 30 seconds | 56719
Calls to fault line - average waiting time before call answered | 78.91
Calls abandoned - percentage | 33
Call centre - number of overload events | 13
Customer complaints (number) | 1334
Complaint - reliability of supply | 264
Complaint - technical quality of supply | 36
Complaint - administrative process or customer service | 113
Complaint - connection or augmentation | 22
Complaint - other | 16
Total complaints | 451
Note: for Table 3 Calls to Call Centre Fault Line means the total number of calls to the fault line to be reported, including any answered by an automated response service and terminated without being answered by an operator. Excludes missed calls where the fault line is overloaded.
Contents

## 5. General Information
United Energy Distribution Pty Limited
General Information
2013
Table 1 General Information
Number of metered supply points | Total no. | By type of customer |  | By supply voltage
|  | Domestic | Non-Domestic | ST | HV | LV
CBD | 0 | 0 | 0 | 0 | 0 | 0
Urban | 614135.1943 | 557732.4575 | 56402.7368 | 1 | 79.7064 | 614054.5389
Rural Short | 33081.8057 | 30043.5425 | 3038.2632 |  | 4.2936 | 33077.4611
Rural Long | 0 | 0 | 0 | 0 | 0 | 0
Total number of metered supply points | 647217 | 587776 | 59441 | 1 | 84 | 647132
Number of unmetered supply points | CBD | Urban | Short Rural | Long Rural
Total no. | 0 | 8823.6915 | 475.3085 | 0
Energy delivered (GWh) | Total GWh | By type of customer |  | By supply voltage
|  | Domestic | Non-Domestic | ST | HV | LV
CBD | 0 | 0 | 0 | 0 | 0 | 0
Urban | 7454.7063 | 2600.8764 | 4853.8299 | 40.3478 | 974.1626 | 6440.2583
Rural Short | 401.5649 | 140.1022 | 261.4627 |  | 52.4755 | 349.0271
Rural Long | 0 | 0 | 0 | 0 | 0 | 0
Total energy | 7856.2712 | 2740.9786 | 5115.2926 | 40.3478 | 1026.6381 | 6789.2853
Line length (km) | Total km | Underground |  |  | Overhead
|  | ST | HV | LV | ST | HV | LV
CBD | 0 | 0 | 0 | 0 | 0 | 0 | 0
Urban | 10379.44 | 12 | 870.31 | 1435.11 | 635.72 | 2604.25 | 4822.05
Rural Short | 2455.18 | 0 | 117.87 | 255.42 | 0 | 1006.17 | 1075.72
Rural Long | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total line length | 12834.62 | 12 | 988.18 | 1690.53 | 635.72 | 3610.42 | 5897.77
Number and total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 12795 | 4619
Zone substations | 46 | 3258
Total | 12841 | 7877
Customer numbers
Subtransmission | 1
High voltage | 84
Low voltage - residential | 609263.2593
Low voltage - non-residential | 47167.7407
Total customer numbers | 656516
Number of poles
Subtransmission | 11325
Distribution | 203476
Total | 214801
Other information
Distribution losses (% of purchases) | 4.1%
Network Service area (sq.km) | 1472
Peak Coincident Demand (MW) | 1982
Note: Distribution Loss factors are to be reported on a financial year basis
Contents
Contents

## 6a. Planned Outages
United Energy Distribution Pty Limited
Planned Outages
2013
Table 1 Planned Outages
Date (DD/MM/YYYY) | Feeder ID / name | Feeder Classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (mins) | Total minutes off supply (planned) | Effect on planned SAIDI | Effect on planned SAIFI | Effect on planned MAIFI
2013-01-02 | SV33 | URBAN | Replace Overhead Assets | 101 | 210 | 21210 | 0.032829 | 0.00015633 | 0
2013-01-02 | STO21 | RURAL SHORT | Regular Maintenance | 2 | 0 | 0 | 0 | 3.0956e-06 | 0
2013-01-02 | WD15 | URBAN | Regular Maintenance | 9 | 330 | 2970 | 0.004597 | 1.393e-05 | 0
2013-01-02 | HGS33 | URBAN | Regular Maintenance | 41 | 410 | 16810 | 0.026019 | 6.3461e-05 | 0
2013-01-03 | HGS22 | URBAN | Regular Maintenance | 41 | 270 | 11070 | 0.017134 | 6.3461e-05 | 0
2013-01-03 | STO13 | URBAN | Replace Overhead Assets | 60 | 480 | 28800 | 0.044577 | 9.2869e-05 | 0
2013-01-04 | DMA13 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 262 | 270 | 70740 | 0.10949 | 0.00040553 | 0
2013-01-06 | SVW55 | RURAL SHORT | Replace Overhead Assets | 8 | 360 | 2880 | 0.0044577 | 1.2383e-05 | 0
2013-01-07 | DMA15 | URBAN | Tree Clearing/Bushfire Mitigation | 14 | 175 | 2450 | 0.0037922 | 2.1669e-05 | 0
2013-01-07 | MTN5 | URBAN | Replace Overhead Assets | 28 | 165 | 4620 | 0.0071509 | 4.3339e-05 | 0
2013-01-07 | SR20 | URBAN | Upgrade capacity - subs and LV | 100 | 335 | 33500 | 0.051852 | 0.00015478 | 0
2013-01-08 | BW21 | URBAN |  | 56 | 130 | 7280 | 0.011268 | 8.6678e-05 | 0
2013-01-08 | MGE12 | URBAN | Regular Maintenance | 1 | 250 | 250 | 0.00038695 | 1.5478e-06 | 0
2013-01-08 | GW12 | URBAN | Replace underground assets | 1 | 240 | 240 | 0.00037148 | 1.5478e-06 | 0
2013-01-08 | SR19 | URBAN | Replace Overhead Assets | 32 | 340 | 10880 | 0.01684 | 4.953e-05 | 0
2013-01-08 | CDA23 | URBAN | Replace Overhead Assets | 42 | 320 | 13440 | 0.020803 | 6.5008e-05 | 0
2013-01-08 | NP6 | URBAN | Regular Maintenance | 7 | 375 | 2625 | 0.004063 | 1.0835e-05 | 0
2013-01-08 | STO23 | RURAL SHORT | Replace Overhead Assets | 35 | 285 | 9975 | 0.01544 | 5.4174e-05 | 0
2013-01-08 | LWN34 | URBAN | Regular Maintenance | 27 | 320 | 8640 | 0.013373 | 4.1791e-05 | 0
2013-01-09 | FTN14 | URBAN | Replace Overhead Assets | 32 | 170 | 5440 | 0.0084201 | 4.953e-05 | 0
2013-01-09 | SV33 | URBAN | Extended Electricity Supply | 72 | 445 | 32040 | 0.049592 | 0.00011144 | 0
2013-01-09 | HGS22 | URBAN | Replace Overhead Assets | 21 | 265 | 5565 | 0.0086136 | 3.2504e-05 | 0
2013-01-09 | LD7 | URBAN | Replace Overhead Assets | 37 | 345 | 12765 | 0.019758 | 5.7269e-05 | 0
2013-01-09 | DC6 | RURAL SHORT | Replace Overhead Assets | 44 | 330 | 14520 | 0.022474 | 6.8104e-05 | 0
2013-01-09 | RBD13 | URBAN | Regular Maintenance | 25 | 90 | 2250 | 0.0034826 | 3.8695e-05 | 0
2013-01-09 | DC5 | URBAN | Upgrade capacity - subs and LV | 9 | 525 | 4725 | 0.0073134 | 1.393e-05 | 0
2013-01-09 | NB15 | URBAN | Replace plant and equipment | 54 | 510 | 27540 | 0.042627 | 8.3582e-05 | 0
2013-01-10 | CM25 | URBAN | Replace plant and equipment | 2 | 110 | 220 | 0.00034052 | 3.0956e-06 | 0
2013-01-10 | STO21 | URBAN | Regular Maintenance | 26 | 155 | 4030 | 0.0062377 | 4.0243e-05 | 0
2013-01-10 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 27 | 150 | 4050 | 0.0062687 | 4.1791e-05 | 0
2013-01-10 | CFD24 | URBAN | Replace Overhead Assets | 20 | 210 | 4200 | 0.0065008 | 3.0956e-05 | 0
2013-01-10 | M17 | URBAN | Replace Overhead Assets | 33 | 300 | 9900 | 0.015323 | 5.1078e-05 | 0
2013-01-10 | K10 | URBAN | Upgrade capacity - subs and LV | 0 | - | 0 | 0 | 0 | 0
2013-01-10 | STO23 | URBAN | Regular Maintenance | 78 | 375 | 29250 | 0.045274 | 0.00012073 | 0
2013-01-10 | MGE21 | URBAN | Extended Electricity Supply | 12 | 420 | 5040 | 0.007801 | 1.8574e-05 | 0
2013-01-11 | CRM12 | URBAN | Replace Overhead Assets | 16 | 210 | 3360 | 0.0052007 | 2.4765e-05 | 0
2013-01-11 | GW7 | URBAN | Replace Overhead Assets | 17 | 210 | 3570 | 0.0055257 | 2.6313e-05 | 0
2013-01-11 | NP6 | RURAL SHORT | Regular Maintenance | 41 | 284 | 11644 | 0.018023 | 6.3461e-05 | 0
2013-01-11 | FSH33 | URBAN | Regular Maintenance | 141 | 360 | 50760 | 0.078567 | 0.00021824 | 0
2013-01-11 | MTN8 | URBAN | Regular Maintenance | 33 | 390 | 12870 | 0.01992 | 5.1078e-05 | 0
2013-01-12 | DMA15 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 70 | 240 | 16800 | 0.026003 | 0.00010835 | 0
2013-01-12 | DSH32 | URBAN | Regular Maintenance | 5 | 50 | 250 | 0.00038695 | 7.7391e-06 | 0
2013-01-12 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 10 | 55 | 550 | 0.0008513 | 1.5478e-05 | 0
2013-01-12 | STO12 | URBAN | Replace Overhead Assets | 45 | 135 | 6075 | 0.009403 | 6.9652e-05 | 0
2013-01-12 | SVW55 | URBAN | Regular Maintenance | 2 | 420 | 840 | 0.0013002 | 3.0956e-06 | 0
2013-01-13 | MC4 | URBAN | Replace Overhead Assets | 29 | 249.1345 | 7224.9 | 0.011183 | 4.4887e-05 | 0
2013-01-13 | DSH24 | URBAN | Replace Overhead Assets | 88 | 298 | 26224 | 0.04059 | 0.00013621 | 0
2013-01-13 | NP5 | RURAL SHORT | Replace Overhead Assets | 94 | 510 | 47940 | 0.074202 | 0.0001455 | 0
2013-01-13 | SVW45 | RURAL SHORT | Regular Maintenance | 11 | 540 | 5940 | 0.0091941 | 1.7026e-05 | 0
2013-01-14 | FSH22 | RURAL SHORT | Replace Overhead Assets | 30 | 52.5833 | 1577.5 | 0.0024417 | 4.6435e-05 | 0
2013-01-14 | NO5 | URBAN | Replace Overhead Assets | 27 | 550 | 14850 | 0.022985 | 4.1791e-05 | 0
2013-01-15 | DMA12 | RURAL SHORT | Replace Overhead Assets | 16 | 205 | 3280 | 0.0050768 | 2.4765e-05 | 0
2013-01-15 | RBD12 | URBAN | Replace Overhead Assets | 48 | 230 | 11040 | 0.017088 | 7.4295e-05 | 0
2013-01-15 | FTN25 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 238 | 270 | 64260 | 0.099463 | 0.00036838 | 0
2013-01-15 | NW14 | RURAL SHORT | Regular Maintenance | 36 | 290 | 10440 | 0.016159 | 5.5722e-05 | 0
2013-01-15 | FSH13 | URBAN | Replace Overhead Assets | 76 | 320 | 24320 | 0.037643 | 0.00011763 | 0
2013-01-15 | NB12 | URBAN | Extended Electricity Supply | 53 | 345 | 18285 | 0.028302 | 8.2034e-05 | 0
2013-01-15 | LD6 | URBAN | Regular Maintenance | 403 | 490 | 197470 | 0.30565 | 0.00062377 | 0
2013-01-15 | HGS23 | URBAN | Regular Maintenance | 21 | 420 | 8820 | 0.013652 | 3.2504e-05 | 0
2013-01-15 | BH21 | URBAN | Upgrade capacity - lines and ZSS | 277 | 420 | 116340 | 0.18007 | 0.00042875 | 0
2013-01-15 | LD1 | URBAN | Replace Overhead Assets | 1 | 810 | 810 | 0.0012537 | 1.5478e-06 | 0
2013-01-16 | LWN32 | URBAN | Regular Maintenance | 6 | 55 | 330 | 0.00051078 | 9.2869e-06 | 0
2013-01-16 | LWN32 | URBAN | Replace Overhead Assets | 6 | 80 | 480 | 0.00074295 | 9.2869e-06 | 0
2013-01-16 | MTN3 | URBAN | Regular Maintenance | 5 | 230 | 1150 | 0.00178 | 7.7391e-06 | 0
2013-01-16 | SS23 | URBAN | Upgrade capacity - subs and LV | 40 | 160 | 6400 | 0.009906 | 6.1913e-05 | 0
2013-01-16 | MTN3 | URBAN | Regular Maintenance | 59 | 300 | 17700 | 0.027396 | 9.1321e-05 | 0
2013-01-16 | MTN3 | RURAL SHORT | Regular Maintenance | 38 | 70 | 2660 | 0.0041172 | 5.8817e-05 | 0
2013-01-16 | RWT18 | URBAN | Replace Overhead Assets | 77 | 405 | 31185 | 0.048269 | 0.00011918 | 0
2013-01-16 | MTN3 | URBAN | Extended Electricity Supply | 4 | 570 | 2280 | 0.003529 | 6.1913e-06 | 0
2013-01-17 | CFD24 | URBAN | Replace Overhead Assets | 60 | 195 | 11700 | 0.018109 | 9.2869e-05 | 0
2013-01-17 | HGS33 | URBAN | Regular Maintenance | 10 | 210 | 2100 | 0.0032504 | 1.5478e-05 | 0
2013-01-17 | LWN31 | URBAN | Replace Overhead Assets | 5 | 405 | 2025 | 0.0031343 | 7.7391e-06 | 0
2013-01-17 | HGS33 | URBAN | Regular Maintenance | 1 | 420 | 420 | 0.00065008 | 1.5478e-06 | 0
2013-01-18 | HGS33 | URBAN | Regular Maintenance | 2 | 120 | 240 | 0.00037148 | 3.0956e-06 | 0
2013-01-18 | FSH21 | RURAL SHORT | Regular Maintenance | 234 | 220 | 51480 | 0.079682 | 0.00036219 | 0
2013-01-18 | BU2 | URBAN | Replace Overhead Assets | 20 | 210 | 4200 | 0.0065008 | 3.0956e-05 | 0
2013-01-18 | LWN32 | URBAN | Regular Maintenance | 5 | 50 | 250 | 0.00038695 | 7.7391e-06 | 0
2013-01-18 | MTN5 | RURAL SHORT | Replace Overhead Assets | 5 | 275 | 1375 | 0.0021283 | 7.7391e-06 | 0
2013-01-18 | DC5 | RURAL SHORT | Replace Overhead Assets | 63 | 380 | 23940 | 0.037055 | 9.7513e-05 | 0
2013-01-18 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 3 | 380 | 1140 | 0.0017645 | 4.6435e-06 | 0
2013-01-18 | HGS22 | URBAN | Tree Clearing/Bushfire Mitigation | 137 | 425 | 58225 | 0.090122 | 0.00021205 | 0
2013-01-18 | HGS33 | URBAN | Replace Overhead Assets | 2 | 395 | 790 | 0.0012228 | 3.0956e-06 | 0
2013-01-18 | RBD13 | URBAN | Regular Maintenance | 25 | 390 | 9750 | 0.015091 | 3.8695e-05 | 0
2013-01-18 | STO21 | RURAL SHORT | Replace Overhead Assets | 11 | 435 | 4785 | 0.0074063 | 1.7026e-05 | 0
2013-01-18 | HGS33 | URBAN | Replace Overhead Assets | 1 | 420 | 420 | 0.00065008 | 1.5478e-06 | 0
2013-01-20 | LWN33 | URBAN | Replace Overhead Assets | 6 | 325 | 1950 | 0.0030182 | 9.2869e-06 | 0
2013-01-20 | GW6 | URBAN | Replace Overhead Assets | 78 | 375 | 29250 | 0.045274 | 0.00012073 | 0
2013-01-20 | HGS33 | RURAL SHORT | Regular Maintenance | 47 | 395 | 18565 | 0.028735 | 7.2748e-05 | 0
2013-01-20 | NO5 | URBAN | Upgrade capacity - subs and LV | 145 | 700 | 101500 | 0.1571 | 0.00022443 | 0
2013-01-20 | CRM34 | RURAL SHORT | Replace Overhead Assets | 2 | 735 | 1470 | 0.0022753 | 3.0956e-06 | 0
2013-01-21 | MGE23 | URBAN | Replace Overhead Assets | 50 | 180 | 9000 | 0.01393 | 7.7391e-05 | 0
2013-01-21 | FSH11 | URBAN | Regular Maintenance | 48 | 190 | 9120 | 0.014116 | 7.4295e-05 | 0
2013-01-21 | FSH22 | URBAN | Replace Overhead Assets | 14 | 210 | 2940 | 0.0045506 | 2.1669e-05 | 0
2013-01-21 | MGE23 | RURAL SHORT | Replace Overhead Assets | 40 | 120 | 4800 | 0.0074295 | 6.1913e-05 | 0
2013-01-21 | CFD14 | RURAL SHORT | Upgrade capacity - subs and LV | 30 | 465 | 13950 | 0.021592 | 4.6435e-05 | 0
2013-01-22 | EM9 | URBAN | Regular Maintenance | 100 | 210 | 21000 | 0.032504 | 0.00015478 | 0
2013-01-22 | RBD21 | RURAL SHORT | Replace Overhead Assets | 130 | 245 | 31850 | 0.049298 | 0.00020122 | 0
2013-01-22 | MTN5 | URBAN | Regular Maintenance | 70 | 370 | 25900 | 0.040089 | 0.00010835 | 0
2013-01-22 | NW23 | URBAN | Extended Electricity Supply | 72 | 390.1 | 28087.2 | 0.043474 | 0.00011144 | 0
2013-01-22 | CFD12 | URBAN | Extended Electricity Supply | 1 | 300 | 300 | 0.00046435 | 1.5478e-06 | 0
2013-01-22 | EB14 | URBAN | Upgrade capacity - subs and LV | 47 | 440 | 20680 | 0.032009 | 7.2748e-05 | 0
2013-01-23 | FSH34 | URBAN | Replace Overhead Assets | 37 | 180 | 6660 | 0.010308 | 5.7269e-05 | 0
2013-01-23 | FSH13 | URBAN | Regular Maintenance | 35 | 220 | 7700 | 0.011918 | 5.4174e-05 | 0
2013-01-23 | EW2 | URBAN | Upgrade capacity - subs and LV | 187 | 365 | 68255 | 0.10565 | 0.00028944 | 0
2013-01-24 | MTN3 | URBAN |  | 389 | 120 | 46680 | 0.072252 | 0.0006021 | 0
2013-01-24 | HGS31 | URBAN | Regular Maintenance | 570 | 344 | 196080 | 0.3035 | 0.00088226 | 0
2013-01-24 | HGS22 | URBAN | Tree Clearing/Bushfire Mitigation | 76 | 390 | 29640 | 0.045877 | 0.00011763 | 0
2013-01-24 | MR31 | URBAN | Upgrade capacity - subs and LV | 234 | 630 | 147420 | 0.22818 | 0.00036219 | 0
2013-01-25 | BU9 | RURAL SHORT | Regular Maintenance | 95 | 180 | 17100 | 0.026468 | 0.00014704 | 0
2013-01-25 | MTN3 | URBAN | Regular Maintenance | 3 | 180 | 540 | 0.00083582 | 4.6435e-06 | 0
2013-01-25 | LWN35 | RURAL SHORT | Replace Overhead Assets | 13 | 235 | 3055 | 0.0047286 | 2.0122e-05 | 0
2013-01-25 | EW12 | URBAN |  | 54 | 330 | 17820 | 0.027582 | 8.3582e-05 | 0
2013-01-25 | LD2 | URBAN | Replace Overhead Assets | 19 | 360 | 6840 | 0.010587 | 2.9409e-05 | 0
2013-01-25 | EB21 | URBAN | Upgrade capacity - subs and LV | 38 | 360 | 13680 | 0.021174 | 5.8817e-05 | 0
2013-01-25 | EB32 | URBAN | Upgrade capacity - subs and LV | 41 | 380 | 15580 | 0.024115 | 6.3461e-05 | 0
2013-01-25 | SVW53 | URBAN | Upgrade capacity - subs and LV | 91 | 465 | 42315 | 0.065496 | 0.00014085 | 0
2013-01-25 | MTN3 | URBAN | Replace Overhead Assets | 18 | 380 | 6840 | 0.010587 | 2.7861e-05 | 0
2013-01-27 | SVW41 | URBAN | Replace Overhead Assets | 40 | 205 | 8200 | 0.012692 | 6.1913e-05 | 0
2013-01-27 | STO21 | URBAN | Regular Maintenance | 11 | 330 | 3630 | 0.0056186 | 1.7026e-05 | 0
2013-01-27 | SVW45 | URBAN | Regular Maintenance | 11 | 540 | 5940 | 0.0091941 | 1.7026e-05 | 0
2013-01-27 | HT3 | URBAN | Extended Electricity Supply | 26 | 510 | 13260 | 0.020524 | 4.0243e-05 | 0
2013-01-29 | NB21 | URBAN | Replace Overhead Assets | 45 | 160 | 7200 | 0.011144 | 6.9652e-05 | 0
2013-01-29 | RWT31 | URBAN | Upgrade capacity - subs and LV | 41 | 360 | 14760 | 0.022846 | 6.3461e-05 | 0
2013-01-29 | HGS33 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 115 | 450 | 51750 | 0.0801 | 0.000178 | 0
2013-01-29 | FSH32 | URBAN | Tree Clearing/Bushfire Mitigation | 209 | 420 | 87780 | 0.13587 | 0.00032349 | 0
2013-01-29 | FSH21 | URBAN | Tree Clearing/Bushfire Mitigation | 89 | 420 | 37380 | 0.057858 | 0.00013776 | 0
2013-01-29 | CRM13 | RURAL SHORT | Replace Overhead Assets | 75 | 488 | 36600 | 0.05665 | 0.00011609 | 0
2013-01-30 | MTN3 | URBAN | Regular Maintenance | 1 | 240 | 240 | 0.00037148 | 1.5478e-06 | 0
2013-01-30 | EL11 | URBAN | Replace Overhead Assets | 17 | 270 | 4590 | 0.0071045 | 2.6313e-05 | 0
2013-01-30 | DC10 | RURAL SHORT | Upgrade capacity - subs and LV | 4 | 315 | 1260 | 0.0019503 | 6.1913e-06 | 0
2013-01-30 | DC6 | URBAN | Replace Overhead Assets | 75 | 405 | 30375 | 0.047015 | 0.00011609 | 0
2013-01-30 | DMA14 | RURAL SHORT | Regular Maintenance | 10 | 390 | 3900 | 0.0060365 | 1.5478e-05 | 0
2013-01-30 | M12 | URBAN | Replace Overhead Assets | 68 | 435 | 29580 | 0.045785 | 0.00010525 | 0
2013-01-31 | LWN33 | URBAN | Tree Clearing/Bushfire Mitigation | 84 | 250 | 21000 | 0.032504 | 0.00013002 | 0
2013-01-31 | NW31 | URBAN | Replace Overhead Assets | 57 | 210 | 11970 | 0.018527 | 8.8226e-05 | 0
2013-01-31 | BU10 | RURAL SHORT | Upgrade capacity - subs and LV | 93 | 240 | 22320 | 0.034547 | 0.00014395 | 0
2013-01-31 | MTN3 | URBAN | Replace Overhead Assets | 2 | 245 | 490 | 0.00075843 | 3.0956e-06 | 0
2013-01-31 | MGE12 | URBAN | Replace underground assets | 62 | 240 | 14880 | 0.023032 | 9.5965e-05 | 0
2013-01-31 | STO23 | URBAN | Regular Maintenance | 2 | 315 | 630 | 0.00097513 | 3.0956e-06 | 0
2013-01-31 | DSH24 | URBAN | Extended Electricity Supply | 3 | 351 | 1053 | 0.0016299 | 4.6435e-06 | 0
2013-01-31 | CRM33 | URBAN | Replace Overhead Assets | 315 | 79 | 24885 | 0.038517 | 0.00048756 | 0
2013-01-31 | EB32 | URBAN | Upgrade capacity - subs and LV | 74 | 395 | 29230 | 0.045243 | 0.00011454 | 0
2013-01-31 | HGS23 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 12 | 460 | 5520 | 0.008544 | 1.8574e-05 | 0
2013-02-01 | RBD13 | URBAN | Regular Maintenance | 48 | 210 | 10080 | 0.015577 | 7.4178e-05 | 0
2013-02-01 | WD3 | URBAN | Upgrade capacity - subs and LV | 2 | 345 | 690 | 0.0010663 | 3.0907e-06 | 0
2013-02-01 | LD2 | URBAN | Replace Overhead Assets | 22 | 296 | 6512 | 0.010063 | 3.3998e-05 | 0
2013-02-01 | SR23 | RURAL SHORT | Upgrade capacity - subs and LV | 98 | 415 | 40670 | 0.06285 | 0.00015145 | 0
2013-02-01 | EB31 | RURAL SHORT | Replace underground assets | 13 | 390 | 5070 | 0.007835 | 2.009e-05 | 0
2013-02-01 | HGS33 | URBAN | Replace Overhead Assets | 41 | 480 | 19680 | 0.030413 | 6.336e-05 | 0
2013-02-02 | MR15 | RURAL SHORT |  | 46 | 210 | 9660 | 0.014928 | 7.1087e-05 | 0
2013-02-03 | SV32 | URBAN |  | 7 | 210 | 1470 | 0.0022717 | 1.0818e-05 | 0
2013-02-03 | SV31 | URBAN | Upgrade capacity - subs and LV | 1 | 275 | 275 | 0.00042498 | 1.5454e-06 | 0
2013-02-03 | M17 | URBAN | Replace Overhead Assets | 13 | 405 | 5265 | 0.0081364 | 2.009e-05 | 0
2013-02-03 | GW6 | URBAN | Replace Overhead Assets | 68 | 480 | 32640 | 0.050441 | 0.00010509 | 0
2013-02-03 | DN4 | URBAN | Replace Overhead Assets | 25 | 480 | 12000 | 0.018544 | 3.8634e-05 | 0
2013-02-04 | CFD24 | URBAN | Replace Overhead Assets | 27 | 240 | 6480 | 0.010014 | 4.1725e-05 | 0
2013-02-04 | CRM12 | URBAN | Replace Overhead Assets | 17 | 270 | 4590 | 0.0070932 | 2.6271e-05 | 0
2013-02-05 | FSH34 | URBAN | Regular Maintenance | 25 | 120 | 3000 | 0.0046361 | 3.8634e-05 | 0
2013-02-05 | FSH31 | URBAN | Replace Overhead Assets | 13 | 200 | 2600 | 0.004018 | 2.009e-05 | 0
2013-02-05 | LWN34 | URBAN | Regular Maintenance | 14 | 240 | 3360 | 0.0051924 | 2.1635e-05 | 0
2013-02-05 | GW4 | URBAN | Upgrade capacity - subs and LV | 1 | 285 | 285 | 0.00044043 | 1.5454e-06 | 0
2013-02-05 | WD3 | URBAN | Replace Overhead Assets | 318 | 450 | 143100 | 0.22114 | 0.00049143 | 0
2013-02-05 | DC10 | URBAN | Replace underground assets | 34 | 455 | 15470 | 0.023907 | 5.2543e-05 | 0
2013-02-05 | FTN14 | URBAN | Regular Maintenance | 5 | 155 | 775 | 0.0011977 | 7.7268e-06 | 0
2013-02-06 | DC12 | URBAN | Regular Maintenance | 2 | 210 | 420 | 0.00064905 | 3.0907e-06 | 0
2013-02-06 | DC4 | URBAN | Upgrade capacity - subs and LV | 32 | 0 | 0 | 0 | 4.9452e-05 | 0
2013-02-06 | K10 | URBAN | Replace Overhead Assets | 5 | 150 | 750 | 0.001159 | 7.7268e-06 | 0
2013-02-06 | DC3 | URBAN | Replace plant and equipment | 30 | 240 | 7200 | 0.011127 | 4.6361e-05 | 0
2013-02-06 | MTN5 | URBAN | Replace Overhead Assets | 4 | 315 | 1260 | 0.0019472 | 6.1815e-06 | 0
2013-02-07 | DMA15 | URBAN | Tree Clearing/Bushfire Mitigation | 28 | 225 | 6300 | 0.0097358 | 4.327e-05 | 0
2013-02-07 | DMA15 | URBAN | Tree Clearing/Bushfire Mitigation | 59 | 300 | 17700 | 0.027353 | 9.1177e-05 | 0
2013-02-07 | MTN5 | URBAN | Replace Overhead Assets | 1 | 240 | 240 | 0.00037089 | 1.5454e-06 | 0
2013-02-07 | EM8 | URBAN | Replace Overhead Assets | 3 | 240 | 720 | 0.0011127 | 4.6361e-06 | 0
2013-02-07 | DC6 | URBAN | Improving Reliability | 238 | 285 | 67830 | 0.10482 | 0.0003678 | 0
2013-02-07 | DC1 | URBAN | Replace plant and equipment | 13 | 240 | 3120 | 0.0048215 | 2.009e-05 | 0
2013-02-07 | DMA13 | URBAN | Replace Overhead Assets | 30 | 295 | 8850 | 0.013677 | 4.6361e-05 | 0
2013-02-07 | SR20 | URBAN | Regular Maintenance | 35 | 320 | 11200 | 0.017308 | 5.4088e-05 | 0
2013-02-07 | RWT31 | URBAN | Replace Overhead Assets | 61 | 330 | 20130 | 0.031108 | 9.4267e-05 | 0
2013-02-07 | STO21 | URBAN | Regular Maintenance | 38 | 180 | 6840 | 0.01057 | 5.8724e-05 | 0
2013-02-07 | EL12 | URBAN | Replace underground assets | 1 | 450 | 450 | 0.00069542 | 1.5454e-06 | 0
2013-02-08 | DMA11 | URBAN | Regular Maintenance | 24 | 165 | 3960 | 0.0061197 | 3.7089e-05 | 0
2013-02-08 | CRM33 | URBAN | Road Works - VicRoads | 149 | 193 | 28757 | 0.04444 | 0.00023026 | 0
2013-02-08 | LWN32 | URBAN | Regular Maintenance | 22 | 330 | 7260 | 0.011219 | 3.3998e-05 | 0
2013-02-08 | RWT18 | URBAN | Replace Overhead Assets | 47 | 410 | 19270 | 0.029779 | 7.2632e-05 | 0
2013-02-08 | SV23 | URBAN | Regular Maintenance | 10 | 150 | 1500 | 0.0023181 | 1.5454e-05 | 0
2013-02-08 | SVW45 | URBAN | Replace Overhead Assets | 4 | 360 | 1440 | 0.0022253 | 6.1815e-06 | 0
2013-02-10 | GW4 | URBAN | Regular Maintenance | 29 | 270 | 7830 | 0.0121 | 4.4816e-05 | 0
2013-02-10 | EB11 | URBAN | Replace Overhead Assets | 157 | 270 | 42390 | 0.065508 | 0.00024262 | 0
2013-02-10 | LD7 | URBAN | Regular Maintenance | 30 | 333 | 9990 | 0.015438 | 4.6361e-05 | 0
2013-02-10 | NW32 | URBAN | Upgrade capacity - subs and LV | 7 | 320 | 2240 | 0.0034616 | 1.0818e-05 | 0
2013-02-10 | HT3 | URBAN | Regular Maintenance | 88 | 140 | 12320 | 0.019039 | 0.00013599 | 0
2013-02-10 | SS11 | URBAN | Replace Overhead Assets | 224 | 555 | 124320 | 0.19212 | 0.00034616 | 0
2013-02-11 | FSH11 | URBAN | Tree Clearing/Bushfire Mitigation | 15 | 210 | 3150 | 0.0048679 | 2.3181e-05 | 0
2013-02-11 | NB12 | URBAN | Replace Overhead Assets | 18 | 240 | 4320 | 0.006676 | 2.7817e-05 | 0
2013-02-11 | RBD23 | URBAN | Regular Maintenance | 1 | 424 | 424 | 0.00065524 | 1.5454e-06 | 0
2013-02-11 | CRM12 | URBAN | Regular Maintenance | 41 | 345 | 14145 | 0.021859 | 6.336e-05 | 0
2013-02-11 | MTN5 | URBAN | Replace underground assets | 67 | 390 | 26130 | 0.04038 | 0.00010354 | 0
2013-02-11 | EB32 | RURAL SHORT | Replace Overhead Assets | 67 | 370 | 24790 | 0.03831 | 0.00010354 | 0
2013-02-12 | FSH32 | URBAN | Replace Overhead Assets | 9 | 195 | 1755 | 0.0027121 | 1.3908e-05 | 0
2013-02-12 | DC2 | URBAN | Replace underground assets | 24 | 185 | 4440 | 0.0068614 | 3.7089e-05 | 0
2013-02-12 | RWT24 | URBAN | Replace Overhead Assets | 25 | 240 | 6000 | 0.0092722 | 3.8634e-05 | 0
2013-02-12 | FSH23 | URBAN | Regular Maintenance | 1 | 200 | 200 | 0.00030907 | 1.5454e-06 | 0
2013-02-12 | STO12 | URBAN | Regular Maintenance | 58 | 270 | 15660 | 0.0242 | 8.9631e-05 | 0
2013-02-12 | BH12 | URBAN | Replace Overhead Assets | 5 | 310 | 1550 | 0.0023953 | 7.7268e-06 | 0
2013-02-12 | MTN7 | URBAN | Replace Overhead Assets | 34 | 210 | 7140 | 0.011034 | 5.2543e-05 | 0
2013-02-12 | K6 | URBAN | Upgrade capacity - subs and LV | 22 | 390 | 8580 | 0.013259 | 3.3998e-05 | 0
2013-02-12 | DC2 | URBAN | Replace underground assets | 76 | 180 | 13680 | 0.021141 | 0.00011745 | 0
2013-02-12 | K2 | URBAN | Upgrade capacity - subs and LV | 27 | 370 | 9990 | 0.015438 | 4.1725e-05 | 0
2013-02-12 | SH80 | URBAN |  | 6 | 480 | 2880 | 0.0044507 | 9.2722e-06 | 0
2013-02-12 | LWN31 | URBAN | Replace Overhead Assets | 5 | 480 | 2400 | 0.0037089 | 7.7268e-06 | 0
2013-02-12 | SH80 | URBAN | Upgrade capacity - subs and LV | 101 | 600 | 60600 | 0.093649 | 0.00015608 | 0
2013-02-13 | DC2 | URBAN | Replace underground assets | 18 | 180 | 3240 | 0.005007 | 2.7817e-05 | 0
2013-02-13 | NB21 | URBAN | Replace Overhead Assets | 45 | 240 | 10800 | 0.01669 | 6.9542e-05 | 0
2013-02-13 | DMA13 | URBAN | Regular Maintenance | 14 | 240 | 3360 | 0.0051924 | 2.1635e-05 | 0
2013-02-13 | NO5 | URBAN | Upgrade capacity - subs and LV | 145 | 345 | 50025 | 0.077307 | 0.00022408 | 0
2013-02-13 | DC2 | URBAN | Replace underground assets | 23 | 210 | 4830 | 0.0074641 | 3.5543e-05 | 0
2013-02-13 | CFD22 | URBAN | Replace Overhead Assets | 109 | 420 | 45780 | 0.070747 | 0.00016845 | 0
2013-02-13 | EW3 | URBAN | Replace underground assets | 114 | 360 | 41040 | 0.063422 | 0.00017617 | 0
2013-02-14 | STO12 | URBAN | Regular Maintenance | 50 | 150 | 7500 | 0.01159 | 7.7268e-05 | 0
2013-02-14 | LWN31 | URBAN | Tree Clearing/Bushfire Mitigation | 81 | 502 | 40662 | 0.062838 | 0.00012517 | 0
2013-02-14 | DMA13 | URBAN | Extended Electricity Supply | 27 | 475 | 12825 | 0.019819 | 4.1725e-05 | 0
2013-02-15 | RBD13 | URBAN | Tree Clearing/Bushfire Mitigation | 123 | 210 | 25830 | 0.039917 | 0.00019008 | 0
2013-02-15 | NW31 | URBAN | Replace Overhead Assets | 64 | 240 | 15360 | 0.023737 | 9.8904e-05 | 0
2013-02-15 | STO21 | RURAL SHORT | Regular Maintenance | 2 | 360 | 720 | 0.0011127 | 3.0907e-06 | 0
2013-02-15 | STO21 | URBAN | Regular Maintenance | 10 | 150 | 1500 | 0.0023181 | 1.5454e-05 | 0
2013-02-15 | STO23 | URBAN | Replace Overhead Assets | 76 | 150 | 11400 | 0.017617 | 0.00011745 | 0
2013-02-15 | K10 | URBAN | Replace Overhead Assets | 19 | 405 | 7695 | 0.011892 | 2.9362e-05 | 0
2013-02-17 | CRM12 | URBAN | Replace Overhead Assets | 32 | 55 | 1760 | 0.0027198 | 4.9452e-05 | 0
2013-02-17 | HGS32 | URBAN | Replace Overhead Assets | 150 | 240 | 36000 | 0.055633 | 0.00023181 | 0
2013-02-17 | MGE12 | RURAL SHORT | Regular Maintenance | 4 | 180 | 720 | 0.0011127 | 6.1815e-06 | 0
2013-02-17 | CRM22 | URBAN | Replace Overhead Assets | 213 | 450 | 95850 | 0.14812 | 0.00032916 | 0
2013-02-17 | HT2 | URBAN | Upgrade capacity - subs and LV | 6 | 510 | 3060 | 0.0047288 | 9.2722e-06 | 0
2013-02-17 | HT2 | URBAN | Upgrade capacity - subs and LV | 6 | 540 | 3240 | 0.005007 | 9.2722e-06 | 0
2013-02-17 | DC2 | URBAN | Replace Overhead Assets | 17 | 545 | 9265 | 0.014318 | 2.6271e-05 | 0
2013-02-18 | MTN8 | RURAL SHORT | Regular Maintenance | 20 | 420 | 8400 | 0.012981 | 3.0907e-05 | 0
2013-02-18 | NP34 | URBAN | Regular Maintenance | 37 | 360 | 13320 | 0.020584 | 5.7179e-05 | 0
2013-02-19 | BH21 | URBAN | Replace Overhead Assets | 139 | 65 | 9035 | 0.013962 | 0.00021481 | 0
2013-02-19 | DMA13 | URBAN | Regular Maintenance | 99 | 190 | 18810 | 0.029068 | 0.00015299 | 0
2013-02-19 | DC2 | URBAN | Replace plant and equipment | 67 | 225 | 15075 | 0.023296 | 0.00010354 | 0
2013-02-19 | NP9 | URBAN | Replace Overhead Assets | 20 | 272 | 5440 | 0.0084068 | 3.0907e-05 | 0
2013-02-19 | FSH33 | URBAN | Replace Overhead Assets | 34 | 310 | 10540 | 0.016288 | 5.2543e-05 | 0
2013-02-19 | DMA14 | URBAN | Regular Maintenance | 306 | 390 | 119340 | 0.18442 | 0.00047288 | 0
2013-02-19 | OR4 | URBAN | Upgrade capacity - subs and LV | 57 | 400 | 22800 | 0.035234 | 8.8086e-05 | 0
2013-02-20 | DC3 | URBAN | Replace plant and equipment | 22 | 165 | 3630 | 0.0056097 | 3.3998e-05 | 0
2013-02-20 | HGS22 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 29 | 315 | 9135 | 0.014117 | 4.4816e-05 | 0
2013-02-20 | DMA12 | URBAN | Replace Overhead Assets | 40 | 188 | 7520 | 0.011621 | 6.1815e-05 | 0
2013-02-20 | HGS22 | URBAN | Replace Overhead Assets | 93 | 330 | 30690 | 0.047427 | 0.00014372 | 0
2013-02-20 | DC2 | URBAN | Improving Reliability | 35 | 125 | 4375 | 0.006761 | 5.4088e-05 | 0
2013-02-21 | BU10 | URBAN | Improving Reliability | 133 | 285 | 37905 | 0.058577 | 0.00020553 | 0
2013-02-21 | EL13 | URBAN | Replace Overhead Assets | 2 | 400 | 800 | 0.0012363 | 3.0907e-06 | 0
2013-02-22 | MTN3 | URBAN | Replace plant and equipment | 2 | 135 | 270 | 0.00041725 | 3.0907e-06 | 0
2013-02-22 | DN13 | URBAN | Replace Overhead Assets | 2 | 210 | 420 | 0.00064905 | 3.0907e-06 | 0
2013-02-22 | HGS33 | URBAN | Regular Maintenance | 2 | 266 | 532 | 0.00082214 | 3.0907e-06 | 0
2013-02-22 | DC3 | URBAN | Upgrade capacity - subs and LV | 39 | 360 | 14040 | 0.021697 | 6.0269e-05 | 0
2013-02-22 | DMA15 | URBAN | Replace plant and equipment | 4 | 195 | 780 | 0.0012054 | 6.1815e-06 | 0
2013-02-22 | K12 | URBAN | Replace Overhead Assets | 8 | 340 | 2720 | 0.0042034 | 1.2363e-05 | 0
2013-02-23 | DVY22 | URBAN | Extended Electricity Supply | 8 | 425 | 3400 | 0.0052543 | 1.2363e-05 | 0
2013-02-24 | DN24 | URBAN | Replace Overhead Assets | 7 | 200 | 1400 | 0.0021635 | 1.0818e-05 | 0
2013-02-24 | DVY14 | URBAN | Replace Overhead Assets | 4 | 420 | 1680 | 0.0025962 | 6.1815e-06 | 0
2013-02-24 | DN25 | URBAN | Regular Maintenance | 1 | 415 | 415 | 0.00064133 | 1.5454e-06 | 0
2013-02-24 | LWN31 | URBAN | Tree Clearing/Bushfire Mitigation | 84 | 465 | 39060 | 0.060362 | 0.00012981 | 0
2013-02-24 | DC8 | RURAL SHORT | Upgrade capacity - subs and LV | 18 | 600 | 10800 | 0.01669 | 2.7817e-05 | 0
2013-02-25 | DC2 | URBAN | Regular Maintenance | 11 | 185 | 2035 | 0.0031448 | 1.6999e-05 | 0
2013-02-25 | GW11 | URBAN |  | 2 | 225 | 450 | 0.00069542 | 3.0907e-06 | 0
2013-02-26 | RBD12 | URBAN | Regular Maintenance | 17 | 200 | 3400 | 0.0052543 | 2.6271e-05 | 0
2013-02-26 | BU2 | RURAL SHORT | Replace underground assets | 63 | 127 | 8001 | 0.012364 | 9.7358e-05 | 0
2013-02-26 | GW6 | URBAN | Extended Electricity Supply | 2 | 360 | 720 | 0.0011127 | 3.0907e-06 | 0
2013-02-26 | CFD22 | URBAN | Improving Reliability | 183 | 330 | 60390 | 0.093325 | 0.0002828 | 0
2013-02-27 | MTN3 | URBAN | Regular Maintenance | 3 | 10 | 30 | 4.6361e-05 | 4.6361e-06 | 0
2013-02-27 | RBD12 | URBAN | Regular Maintenance | 6 | 30 | 180 | 0.00027817 | 9.2722e-06 | 0
2013-02-27 | K10 | URBAN | Replace Overhead Assets | 34 | 345 | 11730 | 0.018127 | 5.2543e-05 | 0
2013-02-27 | SS14 | URBAN | Replace Overhead Assets | 1 | 370 | 370 | 0.00057179 | 1.5454e-06 | 0
2013-02-27 | NW13 | URBAN | Replace underground assets | 9 | 325 | 2925 | 0.0045202 | 1.3908e-05 | 0
2013-02-27 | DMA12 | URBAN | Replace Overhead Assets | 65 | 105 | 6825 | 0.010547 | 0.00010045 | 0
2013-02-27 | DC12 | URBAN | Replace Overhead Assets | 72 | 300 | 21600 | 0.03338 | 0.00011127 | 0
2013-02-27 | RD4 | RURAL SHORT | Improving Reliability | 71 | 395 | 28045 | 0.04334 | 0.00010972 | 0
2013-02-27 | BH11 | RURAL SHORT | Regular Maintenance | 8 | 480 | 3840 | 0.0059342 | 1.2363e-05 | 0
2013-02-28 | STO12 | URBAN | Replace Overhead Assets | 31 | 195 | 6045 | 0.0093418 | 4.7906e-05 | 0
2013-02-28 | CRM22 | URBAN | Regular Maintenance | 17 | 240 | 4080 | 0.0063051 | 2.6271e-05 | 0
2013-02-28 | LD33 | URBAN | Regular Maintenance | 192 | 262 | 50304 | 0.077738 | 0.00029671 | 0
2013-02-28 | EM8 | URBAN | Improving Reliability | 45 | 315 | 14175 | 0.021906 | 6.9542e-05 | 0
2013-02-28 | NB15 | RURAL SHORT | Replace Overhead Assets | 65 | 375 | 24375 | 0.037668 | 0.00010045 | 0
2013-02-28 | STO23 | RURAL SHORT | Replace Overhead Assets | 101 | 480 | 48480 | 0.074919 | 0.00015608 | 0
2013-03-01 | DMA13 | URBAN | Improving Reliability | 1 | 40 | 40 | 6.1969e-05 | 1.5492e-06 | 0
2013-03-01 | MTN3 | URBAN | Regular Maintenance | 2 | 95 | 190 | 0.00029435 | 3.0985e-06 | 0
2013-03-01 | MTN3 | URBAN | Replace Overhead Assets | 5 | 140 | 700 | 0.0010845 | 7.7462e-06 | 0
2013-03-01 | MTN6 | URBAN | Regular Maintenance | 61 | 240 | 14640 | 0.022681 | 9.4503e-05 | 0
2013-03-01 | BU1 | URBAN | Replace Overhead Assets | 23 | 420 | 9660 | 0.014966 | 3.5632e-05 | 0
2013-03-03 | NW11 | URBAN | Replace Overhead Assets | 36 | 360 | 12960 | 0.020078 | 5.5772e-05 | 0
2013-03-03 | BW22 | URBAN | Replace Overhead Assets | 5 | 370 | 1850 | 0.0028661 | 7.7462e-06 | 0
2013-03-01 | M16 | URBAN | Regular Maintenance | 120 | 3270 | 392400 | 0.60792 | 0.00018591 | 0
2013-03-03 | NW32 | URBAN |  | 43 | 620 | 26660 | 0.041303 | 6.6617e-05 | 0
2013-03-03 | HT2 | URBAN | Upgrade capacity - subs and LV | 4 | 660 | 2640 | 0.00409 | 6.1969e-06 | 0
2013-03-03 | SVW53 | URBAN | Regular Maintenance | 2 | 270 | 540 | 0.00083659 | 3.0985e-06 | 0
2013-03-04 | SS14 | RURAL SHORT | Upgrade capacity - subs and LV | 4 | 220 | 880 | 0.0013633 | 6.1969e-06 | 0
2013-03-04 | SS14 | URBAN | Replace Overhead Assets | 1 | 270 | 270 | 0.00041829 | 1.5492e-06 | 0
2013-03-05 | DC1 | URBAN | Replace underground assets | 14 | 240 | 3360 | 0.0052054 | 2.1689e-05 | 0
2013-03-05 | BU1 | URBAN | Replace Overhead Assets | 23 | 260 | 5980 | 0.0092644 | 3.5632e-05 | 0
2013-03-05 | EB13 | URBAN | Replace Overhead Assets | 35 | 290 | 10150 | 0.015725 | 5.4223e-05 | 0
2013-03-05 | SR23 | URBAN | Replace Overhead Assets | 45 | 285 | 12825 | 0.019869 | 6.9716e-05 | 0
2013-03-05 | FSH21 | URBAN | Replace Overhead Assets | 7 | 233 | 1631 | 0.0025268 | 1.0845e-05 | 0
2013-03-05 | FSH32 | URBAN | Replace Overhead Assets | 14 | 339 | 4746 | 0.0073527 | 2.1689e-05 | 0
2013-03-05 | EM11 | URBAN | Replace plant and equipment | 10 | 375 | 3750 | 0.0058096 | 1.5492e-05 | 0
2013-03-05 | DC1 | RURAL SHORT | Improving Reliability | 1 | 360 | 360 | 0.00055772 | 1.5492e-06 | 0
2013-03-05 | MTN5 | URBAN | Upgrade capacity - lines and ZSS | 5 | 840 | 4200 | 0.0065068 | 7.7462e-06 | 0
2013-03-05 | SS13 | URBAN | Regular Maintenance | 56 | 240 | 13440 | 0.020822 | 8.6757e-05 | 0
2013-03-06 | GW1 | URBAN | Regular Maintenance | 4 | 180 | 720 | 0.0011154 | 6.1969e-06 | 0
2013-03-05 | EB31 | URBAN | Regular Maintenance | 43 | 450 | 19350 | 0.029978 | 6.6617e-05 | 0
2013-03-06 | SR23 | URBAN | Replace Overhead Assets | 16 | 195 | 3120 | 0.0048336 | 2.4788e-05 | 0
2013-03-06 | CFD22 | URBAN | Improving Reliability | 69 | 360 | 24840 | 0.038483 | 0.0001069 | 0
2013-03-06 | MTN3 | URBAN | Replace Overhead Assets | 19 | 205 | 3895 | 0.0060343 | 2.9435e-05 | 0
2013-03-06 | DC3 | URBAN | Upgrade capacity - subs and LV | 3 | 390 | 1170 | 0.0018126 | 4.6477e-06 | 0
2013-03-06 | DMA15 | URBAN | Tree Clearing/Bushfire Mitigation | 14 | 470 | 6580 | 0.010194 | 2.1689e-05 | 0
2013-03-06 | OAK22 | URBAN | Improving Reliability | 60 | 360 | 21600 | 0.033463 | 9.2954e-05 | 0
2013-03-06 | SR23 | URBAN | Replace Overhead Assets | 13 | 335 | 4355 | 0.0067469 | 2.014e-05 | 0
2013-03-07 | DC4 | URBAN | Regular Maintenance | 46 | 210 | 9660 | 0.014966 | 7.1265e-05 | 0
2013-03-07 | DMA13 | RURAL SHORT | Regular Maintenance | 39 | 140 | 5460 | 0.0084588 | 6.042e-05 | 0
2013-03-07 | SV21 | URBAN | Replace Overhead Assets | 3 | 150 | 450 | 0.00069716 | 4.6477e-06 | 0
2013-03-07 | K10 | URBAN | Extended Electricity Supply | 65 | 270 | 17550 | 0.027189 | 0.0001007 | 0
2013-03-07 | DC6 | URBAN | Upgrade capacity - subs and LV | 28 | 140 | 3920 | 0.006073 | 4.3379e-05 | 0
2013-03-07 | NP34 | URBAN | Regular Maintenance | 69 | 139 | 9591 | 0.014859 | 0.0001069 | 0
2013-03-07 | MR14 | URBAN | Replace Overhead Assets | 128 | 263 | 33664 | 0.052153 | 0.0001983 | 0
2013-03-08 | DMA14 | URBAN | Replace Overhead Assets | 1 | 150 | 150 | 0.00023239 | 1.5492e-06 | 0
2013-03-08 | MTN7 | RURAL SHORT | Upgrade capacity - subs and LV | 34 | 375 | 12750 | 0.019753 | 5.2674e-05 | 0
2013-03-08 | CRM35 | URBAN | Regular Maintenance | 34 | 371 | 12614 | 0.019542 | 5.2674e-05 | 0
2013-03-08 | MR12 | RURAL SHORT | Replace Overhead Assets | 69 | 270 | 18630 | 0.028862 | 0.0001069 | 0
2013-03-10 | EB32 | URBAN | Regular Maintenance | 194 | 555 | 107670 | 0.16681 | 0.00030055 | 0
2013-03-10 | DN4 | URBAN | Replace Overhead Assets | 218 | 575 | 125350 | 0.1942 | 0.00033773 | 0
2013-03-10 | FSH33 | URBAN | Upgrade capacity - subs and LV | 43 | 550 | 23650 | 0.036639 | 6.6617e-05 | 0
2013-03-12 | STO12 | URBAN | Regular Maintenance | 394 | 345 | 135930 | 0.21059 | 0.0006104 | 0
2013-03-12 | DC4 | URBAN | Upgrade capacity - subs and LV | 34 | 710 | 24140 | 0.037399 | 5.2674e-05 | 0
2013-03-13 | SVW41 | URBAN | Upgrade capacity - subs and LV | 3 | 0 | 0 | 0 | 4.6477e-06 | 0
2013-03-13 | DC4 | URBAN | Upgrade capacity - subs and LV | 48 | 130 | 6240 | 0.0096672 | 7.4363e-05 | 0
2013-03-13 | DC3 | URBAN | Upgrade capacity - subs and LV | 2 | 105 | 210 | 0.00032534 | 3.0985e-06 | 0
2013-03-13 | RD4 | URBAN | Improving Reliability | 71 | 215 | 15265 | 0.023649 | 0.00011 | 0
2013-03-13 | SS23 | RURAL SHORT | Upgrade capacity - subs and LV | 1 | 160 | 160 | 0.00024788 | 1.5492e-06 | 0
2013-03-13 | MTN3 | RURAL SHORT | Replace plant and equipment | 6 | 425 | 2550 | 0.0039505 | 9.2954e-06 | 0
2013-03-14 | MR15 | URBAN | Replace Overhead Assets | 6 | 240 | 1440 | 0.0022309 | 9.2954e-06 | 0
2013-03-14 | FSH34 | URBAN | Replace Overhead Assets | 10 | 74 | 740 | 0.0011464 | 1.5492e-05 | 0
2013-03-14 | EL9 | URBAN | Replace Overhead Assets | 25 | 245 | 6125 | 0.0094891 | 3.8731e-05 | 0
2013-03-14 | DMA12 | URBAN | Replace Overhead Assets | 2 | 320 | 640 | 0.00099151 | 3.0985e-06 | 0
2013-03-14 | HGS23 | URBAN |  | 196 | 350 | 68600 | 0.10628 | 0.00030365 | 0
2013-03-14 | STO13 | URBAN | Replace underground assets | 63 | 150 | 9450 | 0.01464 | 9.7602e-05 | 0
2013-03-14 | CRM33 | RURAL SHORT | Regular Maintenance | 70 | 520 | 36400 | 0.056392 | 0.00010845 | 0
2013-03-15 | MTN5 | URBAN | Replace Overhead Assets | 239 | 30 | 7170 | 0.011108 | 0.00037027 | 0
2013-03-15 | LWN33 | URBAN | Regular Maintenance | 1 | 70 | 70 | 0.00010845 | 1.5492e-06 | 0
2013-03-15 | MGE24 | URBAN | Upgrade capacity - subs and LV | 46 | 260 | 11960 | 0.018529 | 7.1265e-05 | 0
2013-03-15 | STO22 | URBAN | Replace underground assets | 33 | 330 | 10890 | 0.016871 | 5.1125e-05 | 0
2013-03-15 | DC1 | RURAL SHORT | Upgrade capacity - subs and LV | 17 | 330 | 5610 | 0.0086912 | 2.6337e-05 | 0
2013-03-15 | DC2 | URBAN | Upgrade capacity - subs and LV | 36 | 320 | 11520 | 0.017847 | 5.5772e-05 | 0
2013-03-15 | STO12 | URBAN | Replace Overhead Assets | 46 | 435 | 20010 | 0.031 | 7.1265e-05 | 0
2013-03-16 | CDA11 | URBAN |  | 51 | 660 | 33660 | 0.052147 | 7.9011e-05 | 0
2013-03-17 | OAK35 | URBAN |  | 3 | 0 | 0 | 0 | 4.6477e-06 | 0
2013-03-17 | CM21 | URBAN | Upgrade capacity - subs and LV | 1 | 150 | 150 | 0.00023239 | 1.5492e-06 | 0
2013-03-17 | FTN14 | URBAN | Replace underground assets | 3 | 300 | 900 | 0.0013943 | 4.6477e-06 | 0
2013-03-17 | DN2 | URBAN | Replace Overhead Assets | 4 | 320 | 1280 | 0.001983 | 6.1969e-06 | 0
2013-03-17 | CDA11 | RURAL SHORT | Replace Overhead Assets | 13 | 310 | 4030 | 0.0062434 | 2.014e-05 | 0
2013-03-17 | CM21 | URBAN | Upgrade capacity - subs and LV | 4 | 720 | 2880 | 0.0044618 | 6.1969e-06 | 0
2013-03-18 | SVW53 | URBAN | Upgrade capacity - subs and LV | 3 | 225 | 675 | 0.0010457 | 4.6477e-06 | 0
2013-03-18 | CRM33 | URBAN | Replace Overhead Assets | 22 | 260 | 5720 | 0.0088616 | 3.4083e-05 | 0
2013-03-18 | MTN3 | URBAN | Tree Clearing/Bushfire Mitigation | 24 | 330 | 7920 | 0.01227 | 3.7182e-05 | 0
2013-03-18 | SVW54 | URBAN | Upgrade capacity - subs and LV | 56 | 150 | 8400 | 0.013014 | 8.6757e-05 | 0
2013-03-19 | CDA22 | URBAN | Regular Maintenance | 1 | 125 | 125 | 0.00019365 | 1.5492e-06 | 0
2013-03-19 | DC3 | URBAN | Replace underground assets | 14 | 390 | 5460 | 0.0084588 | 2.1689e-05 | 0
2013-03-19 | RWT18 | RURAL SHORT | Replace underground assets | 27 | 100 | 2700 | 0.0041829 | 4.1829e-05 | 0
2013-03-19 | CRM22 | URBAN | Regular Maintenance | 49 | 134 | 6566 | 0.010172 | 7.5912e-05 | 0
2013-03-19 | HGS33 | RURAL SHORT | Replace Overhead Assets | 14 | 190 | 2660 | 0.004121 | 2.1689e-05 | 0
2013-03-19 | SS13 | URBAN | Upgrade capacity - subs and LV | 7 | 250 | 1750 | 0.0027112 | 1.0845e-05 | 0
2013-03-19 | EM8 | URBAN | Improving Reliability | 23 | 275 | 6325 | 0.0097989 | 3.5632e-05 | 0
2013-03-19 | SS22 | URBAN | Upgrade capacity - subs and LV | 6 | 210 | 1260 | 0.001952 | 9.2954e-06 | 0
2013-03-19 | DC2 | URBAN | Upgrade capacity - subs and LV | 1 | 390 | 390 | 0.0006042 | 1.5492e-06 | 0
2013-03-19 | MGE31 | URBAN | Regular Maintenance | 22 | 390 | 8580 | 0.013292 | 3.4083e-05 | 0
2013-03-19 | CRM12 | URBAN | Regular Maintenance | 245 | 405 | 99225 | 0.15372 | 0.00037956 | 0
2013-03-20 | HT1 | URBAN | Regular Maintenance | 245 | 125 | 30625 | 0.047445 | 0.00037956 | 0
2013-03-20 | BT10 | RURAL SHORT | Replace Overhead Assets | 100 | 270 | 27000 | 0.041829 | 0.00015492 | 0
2013-03-20 | CRM22 | URBAN | Regular Maintenance | 57 | 271 | 15447 | 0.023931 | 8.8306e-05 | 0
2013-03-20 | MTN3 | URBAN | Tree Clearing/Bushfire Mitigation | 9 | 405 | 3645 | 0.005647 | 1.3943e-05 | 0
2013-03-20 | HT2 | RURAL SHORT | Regular Maintenance | 58 | 95 | 5510 | 0.0085363 | 8.9856e-05 | 0
2013-03-20 | DC5 | URBAN |  | 18 | 375 | 6750 | 0.010457 | 2.7886e-05 | 0
2013-03-20 | MTN6 | URBAN | Replace Overhead Assets | 86 | 455 | 39130 | 0.060622 | 0.00013323 | 0
2013-03-20 | DMA15 | URBAN | Tree Clearing/Bushfire Mitigation | 32 | 525 | 16800 | 0.026027 | 4.9576e-05 | 0
2013-03-20 | SVW53 | URBAN | Replace Overhead Assets | 179 | 585 | 104715 | 0.16223 | 0.00027731 | 0
2013-03-21 | SS12 | URBAN | Upgrade capacity - subs and LV | 14 | 165 | 2310 | 0.0035787 | 2.1689e-05 | 0
2013-03-21 | FSH13 | URBAN | Regular Maintenance | 18 | 150 | 2700 | 0.0041829 | 2.7886e-05 | 0
2013-03-21 | CRM33 | URBAN | Regular Maintenance | 34 | 155 | 5270 | 0.0081645 | 5.2674e-05 | 0
2013-03-21 | OR12 | URBAN | Upgrade capacity - subs and LV | 4 | 240 | 960 | 0.0014873 | 6.1969e-06 | 0
2013-03-21 | HGS23 | URBAN | Replace Overhead Assets | 2 | 240 | 480 | 0.00074363 | 3.0985e-06 | 0
2013-03-21 | MTN3 | URBAN | Replace Overhead Assets | 16 | 140 | 2240 | 0.0034703 | 2.4788e-05 | 0
2013-03-21 | SS11 | URBAN | Upgrade capacity - subs and LV | 5 | 190 | 950 | 0.0014718 | 7.7462e-06 | 0
2013-03-21 | STO23 | URBAN | Replace Overhead Assets | 10 | 405 | 4050 | 0.0062744 | 1.5492e-05 | 0
2013-03-21 | DC5 | URBAN |  | 18 | 480 | 8640 | 0.013385 | 2.7886e-05 | 0
2013-03-22 | OR5 | URBAN | Tree Clearing - Urban | 43 | 360 | 15480 | 0.023982 | 6.6617e-05 | 0
2013-03-23 | HT8 | URBAN | Regular Maintenance | 1 | 425 | 425 | 0.00065842 | 1.5492e-06 | 0
2013-03-24 | DN24 | URBAN | Regular Maintenance | 21 | 150 | 3150 | 0.0048801 | 3.2534e-05 | 0
2013-03-24 | DVY32 | URBAN | Regular Maintenance | 4 | 240 | 960 | 0.0014873 | 6.1969e-06 | 0
2013-03-24 | RWT18 | URBAN | Upgrade capacity - subs and LV | 6 | 305 | 1830 | 0.0028351 | 9.2954e-06 | 0
2013-03-24 | DN24 | URBAN | Replace Overhead Assets | 2 | 335 | 670 | 0.001038 | 3.0985e-06 | 0
2013-03-24 | DC12 | URBAN | Replace Overhead Assets | 159 | 385 | 61215 | 0.094836 | 0.00024633 | 0
2013-03-24 | DVY24 | URBAN | Regular Maintenance | 1 | 80 | 80 | 0.00012394 | 1.5492e-06 | 0
2013-03-25 | GW6 | URBAN | Upgrade capacity - subs and LV | 4 | 240 | 960 | 0.0014873 | 6.1969e-06 | 0
2013-03-25 | LWN35 | URBAN | Replace Overhead Assets | 43 | 151 | 6493 | 0.010059 | 6.6617e-05 | 0
2013-03-25 | FSH13 | URBAN | Replace Overhead Assets | 41 | 355 | 14555 | 0.022549 | 6.3519e-05 | 0
2013-03-26 | NB23 | URBAN | Upgrade capacity - subs and LV | 22 | 70 | 1540 | 0.0023858 | 3.4083e-05 | 0
2013-03-26 | MC3 | URBAN | Regular Maintenance | 10 | 80 | 800 | 0.0012394 | 1.5492e-05 | 0
2013-03-26 | MR21 | URBAN | Replace Overhead Assets | 18 | 120 | 2160 | 0.0033463 | 2.7886e-05 | 0
2013-03-26 | EB31 | URBAN | Replace underground assets | 9 | 215 | 1935 | 0.0029978 | 1.3943e-05 | 0
2013-03-26 | DN13 | URBAN | Regular Maintenance | 43 | 360 | 15480 | 0.023982 | 6.6617e-05 | 0
2013-03-26 | LD2 | URBAN | Replace Overhead Assets | 37 | 335 | 12395 | 0.019203 | 5.7322e-05 | 0
2013-03-26 | GW2 | URBAN | Replace Overhead Assets | 92 | 405 | 37260 | 0.057724 | 0.00014253 | 0
2013-03-26 | SVW54 | URBAN | Upgrade capacity - subs and LV | 42 | 300 | 12600 | 0.01952 | 6.5068e-05 | 0
2013-03-26 | STO22 | URBAN | Replace Overhead Assets | 32 | 480 | 15360 | 0.023796 | 4.9576e-05 | 0
2013-03-27 | DC2 | URBAN | Replace underground assets | 53 | 187 | 9911 | 0.015354 | 8.2109e-05 | 0
2013-03-27 | LD32 | URBAN | Replace Overhead Assets | 23 | 265 | 6095 | 0.0094426 | 3.5632e-05 | 0
2013-03-27 | MR22 | URBAN | Upgrade capacity - subs and LV | 1 | 150 | 150 | 0.00023239 | 1.5492e-06 | 0
2013-03-27 | RBD12 | URBAN | Replace Overhead Assets | 17 | 350 | 5950 | 0.0092179 | 2.6337e-05 | 0
2013-03-27 | DC5 | URBAN | Replace Overhead Assets | 320 | 330 | 105600 | 0.1636 | 0.00049576 | 0
2013-03-27 | DC3 | URBAN | Replace plant and equipment | 13 | 195 | 2535 | 0.0039273 | 2.014e-05 | 0
2013-03-28 | LD2 | URBAN | Regular Maintenance | 7 | 30 | 210 | 0.00032534 | 1.0845e-05 | 0
2013-03-28 | MTN23 | URBAN | Replace underground assets | 68 | 60 | 4080 | 0.0063209 | 0.00010535 | 0
2013-03-28 | DC12 | URBAN | Replace Overhead Assets | 85 | 325 | 27625 | 0.042798 | 0.00013168 | 0
2013-03-28 | DN13 | URBAN | Regular Maintenance | 22 | 120 | 2640 | 0.00409 | 3.4083e-05 | 0
2013-03-28 | STO22 | RURAL SHORT | Replace Overhead Assets | 49 | 330 | 16170 | 0.025051 | 7.5912e-05 | 0
2013-03-28 | SS22 | URBAN | Upgrade capacity - subs and LV | 2 | 700 | 1400 | 0.0021689 | 3.0985e-06 | 0
2013-04-02 | STO12 | URBAN | Replace Overhead Assets | 50 | 80 | 4000 | 0.0061971 | 7.7463e-05 | 0
2013-04-02 | SS14 | URBAN | Upgrade capacity - subs and LV | 1 | 240 | 240 | 0.00037182 | 1.5493e-06 | 0
2013-04-03 | EM7 | RURAL SHORT | Regular Maintenance | 1 | 85 | 85 | 0.00013169 | 1.5493e-06 | 0
2013-04-03 | CRM22 | URBAN | Regular Maintenance | 28 | 0 | 0 | 0 | 4.338e-05 | 0
2013-04-03 | DMA12 | URBAN | Replace Overhead Assets | 29 | 105 | 3045 | 0.0047175 | 4.4929e-05 | 0
2013-04-03 | DMA12 | URBAN | Replace Overhead Assets | 19 | 105 | 1995 | 0.0030908 | 2.9436e-05 | 0
2013-04-03 | LWN31 | RURAL SHORT | Replace Overhead Assets | 29 | 276 | 8004 | 0.0124 | 4.4929e-05 | 0
2013-04-03 | EM8 | URBAN | Improving Reliability | 68 | 320 | 21760 | 0.033712 | 0.00010535 | 0
2013-04-03 | HGS22 | URBAN | Replace Overhead Assets | 175 | 425 | 74375 | 0.11523 | 0.00027112 | 0
2013-04-03 | BC11 | URBAN |  | 1 | 480 | 480 | 0.00074365 | 1.5493e-06 | 0
2013-04-03 | DC6 | URBAN | Replace Overhead Assets | 109 | 450 | 49050 | 0.075992 | 0.00016887 | 0
2013-04-04 | NB13 | URBAN | Replace Overhead Assets | 35 | 270 | 9450 | 0.014641 | 5.4224e-05 | 0
2013-04-04 | RD4 | URBAN | Improving Reliability | 82 | 340 | 27880 | 0.043194 | 0.00012704 | 0
2013-04-04 | MTN1 | URBAN | Regular Maintenance | 266 | 510 | 135660 | 0.21017 | 0.00041211 | 0
2013-04-05 | DMA11 | URBAN | Replace underground assets | 14 | 135 | 1890 | 0.0029281 | 2.169e-05 | 0
2013-04-05 | CRM22 | URBAN | Replace Overhead Assets | 138 | 315 | 43470 | 0.067347 | 0.0002138 | 0
2013-04-07 | EM5 | URBAN |  | 93 | 0 | 0 | 0 | 0.00014408 | 0
2013-04-07 | K3 | RURAL SHORT | Regular Maintenance | 4 | 210 | 840 | 0.0013014 | 6.1971e-06 | 0
2013-04-07 | RD4 | URBAN | Upgrade capacity - subs and LV | 15 | 360 | 5400 | 0.008366 | 2.3239e-05 | 0
2013-04-07 | LD4 | URBAN | Regular Maintenance | 42 | 280 | 11760 | 0.018219 | 6.5069e-05 | 0
2013-04-07 | CRM12 | URBAN | Replace Overhead Assets | 29 | 322 | 9338 | 0.014467 | 4.4929e-05 | 0
2013-04-07 | DC8 | RURAL SHORT | Extended Electricity Supply | 152 | 450 | 68400 | 0.10597 | 0.00023549 | 0
2013-04-07 | DC8 | URBAN | Extended Electricity Supply | 101 | 465 | 46965 | 0.072761 | 0.00015648 | 0
2013-04-07 | CDA11 | URBAN | Replace Overhead Assets | 13 | 420 | 5460 | 0.008459 | 2.014e-05 | 0
2013-04-07 | K12 | URBAN | Regular Maintenance | 2 | 270 | 540 | 0.0008366 | 3.0985e-06 | 0
2013-04-07 | HT8 | URBAN |  | 15 | 639 | 9585 | 0.01485 | 2.3239e-05 | 0
2013-04-08 | SVW41 | URBAN | Replace Overhead Assets | 1 | 300 | 300 | 0.00046478 | 1.5493e-06 | 0
2013-04-08 | HGS23 | URBAN | Replace Overhead Assets | 1 | 330 | 330 | 0.00051126 | 1.5493e-06 | 0
2013-04-09 | HGS22 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 68 | 85 | 5780 | 0.0089548 | 0.00010535 | 0
2013-04-09 | OAK22 | URBAN | Replace underground assets | 21 | 195 | 4095 | 0.0063443 | 3.2535e-05 | 0
2013-04-09 | MTN35 | RURAL SHORT | Regular Maintenance | 19 | 255 | 4845 | 0.0075062 | 2.9436e-05 | 0
2013-04-09 | STO12 | URBAN | Replace Overhead Assets | 2 | 280 | 560 | 0.00086759 | 3.0985e-06 | 0
2013-04-09 | DC8 | URBAN | Replace Overhead Assets | 121 | 330 | 39930 | 0.061862 | 0.00018746 | 0
2013-04-09 | EB12 | URBAN | Replace Overhead Assets | 258 | 390 | 100620 | 0.15589 | 0.00039971 | 0
2013-04-09 | DMA15 | RURAL SHORT | Replace Overhead Assets | 3 | 270 | 810 | 0.0012549 | 4.6478e-06 | 0
2013-04-09 | MTN3 | URBAN | Replace Overhead Assets | 4 | 410 | 1640 | 0.0025408 | 6.1971e-06 | 0
2013-04-09 | FSH31 | URBAN | Replace Overhead Assets | 85 | 390 | 33150 | 0.051358 | 0.00013169 | 0
2013-04-09 | FTN23 | URBAN | Regular Maintenance | 62 | 465 | 28830 | 0.044665 | 9.6055e-05 | 0
2013-04-09 | FTN12 | URBAN | Regular Maintenance | 89 | 370 | 32930 | 0.051017 | 0.00013788 | 0
2013-04-09 | FTN23 | URBAN | Upgrade capacity - subs and LV | 62 | 455 | 28210 | 0.043705 | 9.6055e-05 | 0
2013-04-09 | FTN22 | URBAN | Regular Maintenance | 44 | 170 | 7480 | 0.011589 | 6.8168e-05 | 0
2013-04-10 | LD2 | URBAN | Regular Maintenance | 5 | 125 | 625 | 0.00096829 | 7.7463e-06 | 0
2013-04-10 | WD9 | URBAN | Upgrade capacity - subs and LV | 2 | 225 | 450 | 0.00069717 | 3.0985e-06 | 0
2013-04-10 | RBD21 | RURAL SHORT | Replace Overhead Assets | 130 | 300 | 39000 | 0.060421 | 0.0002014 | 0
2013-04-10 | DMA13 | RURAL SHORT | Extended Electricity Supply | 1 | 325 | 325 | 0.00050351 | 1.5493e-06 | 0
2013-04-10 | BH21 | URBAN | Replace Overhead Assets | 141 | 395 | 55695 | 0.086286 | 0.00021845 | 0
2013-04-10 | FSH31 | URBAN | Replace Overhead Assets | 74 | 405 | 29970 | 0.046432 | 0.00011465 | 0
2013-04-10 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 45 | 515 | 23175 | 0.035904 | 6.9717e-05 | 0
2013-04-11 | DMA15 | URBAN | Replace Overhead Assets | 4 | 175 | 700 | 0.0010845 | 6.1971e-06 | 0
2013-04-11 | GW8 | RURAL SHORT | Replace Overhead Assets | 47 | 270 | 12690 | 0.01966 | 7.2816e-05 | 0
2013-04-12 | CRM35 | URBAN | Regular Maintenance | 34 | 115 | 3910 | 0.0060576 | 5.2675e-05 | 0
2013-04-12 | HGS33 | URBAN | Replace Overhead Assets | 8 | 300 | 2400 | 0.0037182 | 1.2394e-05 | 0
2013-04-12 | OAK26 | RURAL SHORT | Replace Overhead Assets | 69 | 390 | 26910 | 0.041691 | 0.0001069 | 0
2013-04-12 | NW31 | URBAN | Replace Overhead Assets | 111 | 505 | 56055 | 0.086844 | 0.00017197 | 0
2013-04-13 | SVW45 | URBAN | Regular Maintenance | 10 | 0 | 0 | 0 | 1.5493e-05 | 0
2013-04-14 | K2 | URBAN | Regular Maintenance | 10 | 120 | 1200 | 0.0018591 | 1.5493e-05 | 0
2013-04-14 | K7 | URBAN | Regular Maintenance | 21 | 270 | 5670 | 0.0087844 | 3.2535e-05 | 0
2013-04-14 | MC6 | URBAN | Regular Maintenance | 44 | 547 | 24068 | 0.037288 | 6.8168e-05 | 0
2013-04-14 | BH12 | URBAN | Replace Overhead Assets | 81 | 650 | 52650 | 0.081569 | 0.00012549 | 0
2013-04-15 | SS21 | RURAL SHORT | Upgrade capacity - subs and LV | 6 | 150 | 900 | 0.0013943 | 9.2956e-06 | 0
2013-04-15 | RBD21 | URBAN | Replace Overhead Assets | 2 | 390 | 780 | 0.0012084 | 3.0985e-06 | 0
2013-04-15 | DMA13 | URBAN | Improving Reliability | 3 | 105 | 315 | 0.00048802 | 4.6478e-06 | 0
2013-04-15 | DSH24 | URBAN | Regular Maintenance | 11 | 420 | 4620 | 0.0071576 | 1.7042e-05 | 0
2013-04-16 | STO21 | URBAN | Replace Overhead Assets | 37 | 291 | 10767 | 0.016681 | 5.7323e-05 | 0
2013-04-16 | STO12 | URBAN | Replace Overhead Assets | 2 | 225 | 450 | 0.00069717 | 3.0985e-06 | 0
2013-04-16 | MGE14 | URBAN | Upgrade capacity - subs and LV | 6 | 351 | 2106 | 0.0032628 | 9.2956e-06 | 0
2013-04-16 | DC12 | URBAN | Upgrade capacity - subs and LV | 162 | 435 | 70470 | 0.10918 | 0.00025098 | 0
2013-04-16 | LWN31 | URBAN | Replace Overhead Assets | 208 | 485 | 100880 | 0.15629 | 0.00032225 | 0
2013-04-16 | EW14 | URBAN | Replace underground assets | 66 | 450 | 29700 | 0.046013 | 0.00010225 | 0
2013-04-16 | NW32 | URBAN | Replace underground assets | 64 | 655 | 41920 | 0.064945 | 9.9153e-05 | 0
2013-04-16 | FTN14 | URBAN | Regular Maintenance | 1 | 180 | 180 | 0.00027887 | 1.5493e-06 | 0
2013-04-17 | DN7 | URBAN | Regular Maintenance | 6 | 75 | 450 | 0.00069717 | 9.2956e-06 | 0
2013-04-17 | DMA13 | URBAN | Improving Reliability | 19 | 165 | 3135 | 0.004857 | 2.9436e-05 | 0
2013-04-17 | FTN21 | RURAL SHORT | Regular Maintenance | 1 | 220 | 220 | 0.00034084 | 1.5493e-06 | 0
2013-04-17 | DMA13 | RURAL SHORT | Replace Overhead Assets | 1 | 60 | 60 | 9.2956e-05 | 1.5493e-06 | 0
2013-04-17 | DC8 | URBAN | Replace Overhead Assets | 5 | 254 | 1270 | 0.0019676 | 7.7463e-06 | 0
2013-04-17 | DMA15 | RURAL SHORT | Replace Overhead Assets | 2 | 105 | 210 | 0.00032535 | 3.0985e-06 | 0
2013-04-17 | MR22 | URBAN | Replace Overhead Assets | 1 | 330 | 330 | 0.00051126 | 1.5493e-06 | 0
2013-04-17 | EW14 | URBAN | Upgrade capacity - subs and LV | 156 | 405 | 63180 | 0.097883 | 0.00024169 | 0
2013-04-17 | DC2 | URBAN | Replace underground assets | 84 | 405 | 34020 | 0.052706 | 0.00013014 | 0
2013-04-17 | EW9 | RURAL SHORT | Replace Overhead Assets | 63 | 340 | 21420 | 0.033185 | 9.7604e-05 | 0
2013-04-17 | RBD21 | RURAL SHORT | Replace Overhead Assets | 6 | 480 | 2880 | 0.0044619 | 9.2956e-06 | 0
2013-04-17 | BT10 | URBAN | Upgrade capacity - subs and LV | 286 | 510 | 145860 | 0.22598 | 0.00044309 | 0
2013-04-18 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 44 | 130 | 5720 | 0.0088618 | 6.8168e-05 | 0
2013-04-18 | RBD23 | URBAN | Replace Overhead Assets | 42 | 270 | 11340 | 0.017569 | 6.5069e-05 | 0
2013-04-18 | LD5 | URBAN | Regular Maintenance | 26 | 230 | 5980 | 0.0092646 | 4.0281e-05 | 0
2013-04-18 | M7 | URBAN | Replace Overhead Assets | 29 | 353 | 10237 | 0.01586 | 4.4929e-05 | 0
2013-04-18 | RBD21 | URBAN | Extended Electricity Supply | 91 | 320 | 29120 | 0.045115 | 0.00014098 | 0
2013-04-18 | DMA13 | URBAN | Extended Electricity Supply | 2 | 420 | 840 | 0.0013014 | 3.0985e-06 | 0
2013-04-18 | EB31 | URBAN | Replace underground assets | 39 | 390 | 15210 | 0.023564 | 6.0421e-05 | 0
2013-04-19 | EM7 | URBAN | Tree Clearing - Urban | 203 | 210 | 42630 | 0.066045 | 0.0003145 | 0
2013-04-19 | STO12 | URBAN | Replace Overhead Assets | 394 | 155 | 61070 | 0.094614 | 0.00061041 | 0
2013-04-19 | RWT31 | RURAL SHORT | Replace Overhead Assets | 7 | 280 | 1960 | 0.0030366 | 1.0845e-05 | 0
2013-04-19 | FSH31 | URBAN | Replace Overhead Assets | 58 | 305 | 17690 | 0.027407 | 8.9858e-05 | 0
2013-04-19 | EW3 | URBAN | Replace Overhead Assets | 21 | 390 | 8190 | 0.012689 | 3.2535e-05 | 0
2013-04-21 | NB15 | URBAN | Upgrade capacity - subs and LV | 68 | 328 | 22304 | 0.034555 | 0.00010535 | 0
2013-04-21 | SS22 | URBAN | Upgrade capacity - subs and LV | 52 | 488 | 25376 | 0.039314 | 8.0562e-05 | 0
2013-04-22 | CRM33 | URBAN | Replace Overhead Assets | 3 | 220 | 660 | 0.0010225 | 4.6478e-06 | 0
2013-04-22 | CRM22 | URBAN | Regular Maintenance | 25 | 300 | 7500 | 0.01162 | 3.8732e-05 | 0
2013-04-22 | DC12 | RURAL SHORT |  | 72 | 375 | 27000 | 0.04183 | 0.00011155 | 0
2013-04-22 | EB14 | URBAN | Upgrade capacity - subs and LV | 5 | 330 | 1650 | 0.0025563 | 7.7463e-06 | 0
2013-04-23 | MGE12 | URBAN | Replace Overhead Assets | 1 | 120 | 120 | 0.00018591 | 1.5493e-06 | 0
2013-04-23 | MGE12 | URBAN | Replace Overhead Assets | 14 | 0 | 0 | 0 | 2.169e-05 | 0
2013-04-23 | MGE12 | URBAN | Replace Overhead Assets | 11 | 180 | 1980 | 0.0030676 | 1.7042e-05 | 0
2013-04-23 | STO12 | URBAN | Replace Overhead Assets | 9 | 215 | 1935 | 0.0029978 | 1.3943e-05 | 0
2013-04-23 | FSH12 | URBAN | Replace Overhead Assets | 24 | 300 | 7200 | 0.011155 | 3.7182e-05 | 0
2013-04-23 | CFD22 | URBAN | Replace Overhead Assets | 183 | 330 | 60390 | 0.09356 | 0.00028352 | 0
2013-04-23 | DC3 | RURAL SHORT | Replace underground assets | 16 | 365 | 5840 | 0.0090477 | 2.4788e-05 | 0
2013-04-23 | BC23 | URBAN | Replace Overhead Assets | 29 | 405 | 11745 | 0.018196 | 4.4929e-05 | 0
2013-04-24 | STO12 | URBAN | Replace Overhead Assets | 3 | 200 | 600 | 0.00092956 | 4.6478e-06 | 0
2013-04-24 | HGS33 | URBAN | Regular Maintenance | 21 | 98 | 2058 | 0.0031884 | 3.2535e-05 | 0
2013-04-24 | OR13 | URBAN | Replace Overhead Assets | 33 | 330 | 10890 | 0.016872 | 5.1126e-05 | 0
2013-04-24 | DC6 | URBAN | Replace Overhead Assets | 127 | 271 | 34417 | 0.053321 | 0.00019676 | 0
2013-04-24 | DC1 | URBAN | Replace Overhead Assets | 32 | 390 | 12480 | 0.019335 | 4.9577e-05 | 0
2013-04-24 | BC23 | URBAN | Upgrade capacity - subs and LV | 39 | 436 | 17004 | 0.026344 | 6.0421e-05 | 0
2013-04-24 | DC2 | URBAN | Upgrade capacity - subs and LV | 175 | 570 | 99750 | 0.15454 | 0.00027112 | 0
2013-04-24 | FTN12 | RURAL SHORT | Replace Overhead Assets | 232 | 510 | 118320 | 0.18331 | 0.00035943 | 0
2013-04-26 | OAK26 | URBAN | Extended Electricity Supply | 86 | 370 | 31820 | 0.049298 | 0.00013324 | 0
2013-04-26 | HGS23 | URBAN | Regular Maintenance | 11 | 407 | 4477 | 0.0069361 | 1.7042e-05 | 0
2013-04-27 | SVW55 | URBAN | Replace Overhead Assets | 13 | 332 | 4316 | 0.0066866 | 2.014e-05 | 0
2013-04-28 | MC4 | URBAN | Regular Maintenance | 1 | 476 | 476 | 0.00073745 | 1.5493e-06 | 0
2013-04-28 | DC6 | RURAL SHORT | Replace Overhead Assets | 110 | 540 | 59400 | 0.092027 | 0.00017042 | 0
2013-04-28 | CRM12 | URBAN | Replace Overhead Assets | 34 | 485 | 16490 | 0.025547 | 5.2675e-05 | 0
2013-04-29 | SVW41 | URBAN | Upgrade capacity - subs and LV | 4 | 165 | 660 | 0.0010225 | 6.1971e-06 | 0
2013-04-29 | FTN12 | URBAN | Replace Overhead Assets | 50 | 290 | 14500 | 0.022464 | 7.7463e-05 | 0
2013-04-29 | RWT24 | RURAL SHORT | Replace Overhead Assets | 15 | 290 | 4350 | 0.0067393 | 2.3239e-05 | 0
2013-04-29 | EL14 | URBAN | Replace Overhead Assets | 80 | 290 | 23200 | 0.035943 | 0.00012394 | 0
2013-04-29 | RBD22 | URBAN | Regular Maintenance | 1 | 327 | 327 | 0.00050661 | 1.5493e-06 | 0
2013-04-30 | MC6 | URBAN | Regular Maintenance | 15 | 136 | 2040 | 0.0031605 | 2.3239e-05 | 0
2013-04-30 | DC12 | URBAN | Replace Overhead Assets | 83 | 229 | 19007 | 0.029447 | 0.00012859 | 0
2013-04-30 | FSH31 | URBAN | Replace Overhead Assets | 47 | 275 | 12925 | 0.020024 | 7.2816e-05 | 0
2013-04-30 | HGS33 | URBAN | Replace Overhead Assets | 20 | 270 | 5400 | 0.008366 | 3.0985e-05 | 0
2013-04-30 | MC6 | URBAN | Regular Maintenance | 46 | 230 | 10580 | 0.016391 | 7.1266e-05 | 0
2013-04-30 | DMA14 | URBAN | Replace Overhead Assets | 121 | 350 | 42350 | 0.065612 | 0.00018746 | 0
2013-04-30 | MC2 | URBAN | Regular Maintenance | 15 | 155 | 2325 | 0.003602 | 2.3239e-05 | 0
2013-04-30 | NW31 | URBAN | Replace Overhead Assets | 57 | 411 | 23427 | 0.036295 | 8.8308e-05 | 0
2013-05-01 | OAK23 | RURAL SHORT | Replace Overhead Assets | 82 | 0 | 0 | 0 | 0.00012709 | 0
2013-05-01 | DMA12 | URBAN | Extended Electricity Supply | 9 | 250 | 2250 | 0.0034873 | 1.3949e-05 | 0
2013-05-01 | SR11 | URBAN | Upgrade capacity - subs and LV | 14 | 297 | 4158 | 0.0064444 | 2.1698e-05 | 0
2013-05-01 | NB12 | URBAN | Replace Overhead Assets | 27 | 285 | 7695 | 0.011926 | 4.1847e-05 | 0
2013-05-01 | LWN35 | URBAN | Replace Overhead Assets | 4 | 365 | 1460 | 0.0022628 | 6.1996e-06 | 0
2013-04-30 | CFD23 | URBAN | Replace Overhead Assets | 86 | 1860 | 159960 | 0.24782 | 0.00013324 | 0
2013-05-01 | MTN35 | URBAN | Replace Overhead Assets | 6 | 330 | 1980 | 0.0030688 | 9.2993e-06 | 0
2013-05-01 | RBD12 | RURAL SHORT | Replace Overhead Assets | 3 | 360 | 1080 | 0.0016739 | 4.6497e-06 | 0
2013-05-01 | EW9 | URBAN | Replace Overhead Assets | 32 | 1040 | 33280 | 0.05158 | 4.9596e-05 | 0
2013-05-02 | DC4 | URBAN | Upgrade capacity - subs and LV | 1 | 0 | 0 | 0 | 1.5499e-06 | 0
2013-05-02 | EL6 | URBAN | Regular Maintenance | 5 | 210 | 1050 | 0.0016274 | 7.7495e-06 | 0
2013-05-02 | DC12 | URBAN | Replace Overhead Assets | 89 | 310 | 27590 | 0.042761 | 0.00013794 | 0
2013-05-02 | DC2 | RURAL SHORT | Upgrade capacity - subs and LV | 1 | 345 | 345 | 0.00053471 | 1.5499e-06 | 0
2013-05-02 | MGE23 | URBAN | Replace underground assets | 36 | 370 | 13320 | 0.020645 | 5.5796e-05 | 0
2013-05-02 | K10 | URBAN | Replace plant and equipment | 1 | 450 | 450 | 0.00069745 | 1.5499e-06 | 0
2013-05-02 | HGS23 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 44 | 440 | 19360 | 0.030006 | 6.8195e-05 | 0
2013-05-02 | NO3 | URBAN | Replace underground assets | 1 | 450 | 450 | 0.00069745 | 1.5499e-06 | 0
2013-05-02 | DN13 | URBAN | Regular Maintenance | 86 | 225 | 19350 | 0.02999 | 0.00013329 | 0
2013-05-02 | K6 | URBAN | Replace Overhead Assets | 18 | 240 | 4320 | 0.0066955 | 2.7898e-05 | 0
2013-05-03 | DC8 | URBAN | Replace Overhead Assets | 81 | 240 | 19440 | 0.03013 | 0.00012554 | 0
2013-05-03 | MC3 | URBAN | Regular Maintenance | 90 | 210 | 18900 | 0.029293 | 0.00013949 | 0
2013-05-03 | EW8 | URBAN | Replace Overhead Assets | 27 | 240 | 6480 | 0.010043 | 4.1847e-05 | 0
2013-05-03 | DMA15 | URBAN | Tree Clearing/Bushfire Mitigation | 36 | 340 | 12240 | 0.018971 | 5.5796e-05 | 0
2013-05-04 | MGE33 | URBAN | Upgrade capacity - subs and LV | 1 | 120 | 120 | 0.00018599 | 1.5499e-06 | 0
2013-05-04 | SVW55 | URBAN | Upgrade capacity - subs and LV | 3 | 120 | 360 | 0.00055796 | 4.6497e-06 | 0
2013-05-05 | HT1 | URBAN | Replace underground assets | 17 | 180 | 3060 | 0.0047427 | 2.6348e-05 | 0
2013-05-05 | BH23 | URBAN | Improving Reliability | 47 | 420 | 19740 | 0.030595 | 7.2845e-05 | 0
2013-05-05 | NB24 | URBAN | Replace Overhead Assets | 8 | 445 | 3560 | 0.0055176 | 1.2399e-05 | 0
2013-05-05 | LD7 | URBAN | Regular Maintenance | 33 | 660 | 21780 | 0.033757 | 5.1146e-05 | 0
2013-05-06 | SR19 | URBAN | Replace Overhead Assets | 17 | 255 | 4335 | 0.0067188 | 2.6348e-05 | 0
2013-05-07 | DC12 | URBAN | Replace Overhead Assets | 203 | 224 | 45472 | 0.070477 | 0.00031463 | 0
2013-05-07 | RBD14 | URBAN | Replace Overhead Assets | 54 | 285 | 15390 | 0.023853 | 8.3694e-05 | 0
2013-05-07 | RD4 | URBAN | Replace Overhead Assets | 65 | 253 | 16445 | 0.025488 | 0.00010074 | 0
2013-05-07 | MTN32 | URBAN | Replace Overhead Assets | 21 | 235 | 4935 | 0.0076487 | 3.2548e-05 | 0
2013-05-07 | MTN24 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 28 | 410 | 11480 | 0.017793 | 4.3397e-05 | 0
2013-05-07 | FSH32 | URBAN | Regular Maintenance | 36 | 455 | 16380 | 0.025387 | 5.5796e-05 | 0
2013-05-07 | BC23 | URBAN | Extended Electricity Supply | 150 | 462 | 69300 | 0.10741 | 0.00023248 | 0
2013-05-07 | GW7 | URBAN | Extended Electricity Supply | 69 | 495 | 34155 | 0.052936 | 0.00010694 | 0
2013-05-07 | DN7 | URBAN | Regular Maintenance | 1 | 570 | 570 | 0.00088344 | 1.5499e-06 | 0
2013-05-08 | HGS33 | URBAN | Upgrade capacity - subs and LV | 11 | 225 | 2475 | 0.003836 | 1.7049e-05 | 0
2013-05-08 | BH21 | RURAL SHORT | Replace Overhead Assets | 20 | 260 | 5200 | 0.0080594 | 3.0998e-05 | 0
2013-05-08 | LD3 | URBAN | Replace Overhead Assets | 56 | 235 | 13160 | 0.020397 | 8.6794e-05 | 0
2013-05-08 | NB23 | URBAN | Replace Overhead Assets | 24 | 345 | 8280 | 0.012833 | 3.7197e-05 | 0
2013-05-08 | HGS22 | URBAN | Upgrade capacity - subs and LV | 2 | 165 | 330 | 0.00051146 | 3.0998e-06 | 0
2013-05-08 | FSH13 | URBAN | Replace Overhead Assets | 62 | 435 | 26970 | 0.041801 | 9.6093e-05 | 0
2013-05-08 | RBD23 | URBAN | Extended Electricity Supply | 108 | 425 | 45900 | 0.07114 | 0.00016739 | 0
2013-05-08 | HGS22 | URBAN | Regular Maintenance | 2 | 519 | 1038 | 0.0016088 | 3.0998e-06 | 0
2013-05-08 | M22 | URBAN | Replace Overhead Assets | 38 | 700 | 26600 | 0.041227 | 5.8896e-05 | 0
2013-05-09 | SR19 | URBAN | Replace Overhead Assets | 23 | 220 | 5060 | 0.0078424 | 3.5647e-05 | 0
2013-05-09 | MTN35 | URBAN | Replace Overhead Assets | 31 | 275 | 8525 | 0.013213 | 4.8047e-05 | 0
2013-05-09 | STO21 | URBAN |  | 199 | 330 | 65670 | 0.10178 | 0.00030843 | 0
2013-05-09 | NW11 | URBAN | Replace Overhead Assets | 15 | 450 | 6750 | 0.010462 | 2.3248e-05 | 0
2013-05-10 | STO22 | URBAN | Extended Electricity Supply | 34 | 375 | 12750 | 0.019761 | 5.2696e-05 | 0
2013-05-10 | BC23 | URBAN | Replace Overhead Assets | 90 | 375 | 33750 | 0.052309 | 0.00013949 | 0
2013-05-10 | RBD12 | URBAN | Replace Overhead Assets | 33 | 95 | 3135 | 0.0048589 | 5.1146e-05 | 0
2013-05-10 | RBD13 | URBAN | Replace Overhead Assets | 96 | 400 | 38400 | 0.059516 | 0.00014879 | 0
2013-05-10 | K4 | URBAN | Tree Clearing - Urban | 43 | 340 | 14620 | 0.022659 | 6.6645e-05 | 0
2013-05-10 | CRM22 | URBAN | Regular Maintenance | 3 | 360 | 1080 | 0.0016739 | 4.6497e-06 | 0
2013-05-11 | CDA22 | URBAN | Regular Maintenance | 3 | 175 | 525 | 0.00081369 | 4.6497e-06 | 0
2013-05-11 | SV32 | URBAN | Upgrade capacity - subs and LV | 1 | 540 | 540 | 0.00083694 | 1.5499e-06 | 0
2013-05-12 | MGE32 | RURAL SHORT | Regular Maintenance | 1 | 240 | 240 | 0.00037197 | 1.5499e-06 | 0
2013-05-12 | DSH31 | URBAN | Replace Overhead Assets | 17 | 365 | 6205 | 0.0096171 | 2.6348e-05 | 0
2013-05-12 | M17 | URBAN | Regular Maintenance | 31 | 361 | 11191 | 0.017345 | 4.8047e-05 | 0
2013-05-13 | CDA21 | URBAN | Regular Maintenance | 1 | 105 | 105 | 0.00016274 | 1.5499e-06 | 0
2013-05-13 | CRM33 | URBAN | Replace Overhead Assets | 316 | 271 | 85636 | 0.13273 | 0.00048977 | 0
2013-05-13 | RWT24 | URBAN | Improving Reliability | 122 | 440 | 53680 | 0.083198 | 0.00018909 | 0
2013-05-13 | CFD15 | URBAN | Replace Overhead Assets | 47 | 60 | 2820 | 0.0043707 | 7.2845e-05 | 0
2013-05-13 | RBD22 | URBAN | Regular Maintenance | 17 | 216 | 3672 | 0.0056912 | 2.6348e-05 | 0
2013-05-14 | M23 | URBAN | Regular Maintenance | 106 | 0 | 0 | 0 | 0.00016429 | 0
2013-05-14 | EW14 | URBAN |  | 17 | 255 | 4335 | 0.0067188 | 2.6348e-05 | 0
2013-05-14 | LWN31 | URBAN | Replace underground assets | 12 | 75 | 900 | 0.0013949 | 1.8599e-05 | 0
2013-05-14 | BH21 | URBAN | Replace Overhead Assets | 69 | 330 | 22770 | 0.035291 | 0.00010694 | 0
2013-05-14 | MC6 | URBAN | Regular Maintenance | 109 | 375 | 40875 | 0.063352 | 0.00016894 | 0
2013-05-14 | MTN31 | URBAN | Extended Electricity Supply | 122 | 480 | 58560 | 0.090762 | 0.00018909 | 0
2013-05-14 | STO13 | URBAN | Extended Electricity Supply | 18 | 465 | 8370 | 0.012973 | 2.7898e-05 | 0
2013-05-14 | CRM21 | URBAN | Improving Reliability | 164 | 435 | 71340 | 0.11057 | 0.00025418 | 0
2013-05-14 | EL14 | URBAN | Replace Overhead Assets | 1 | 275 | 275 | 0.00042622 | 1.5499e-06 | 0
2013-05-15 | MTN31 | URBAN | Replace underground assets | 42 | 135 | 5670 | 0.0087879 | 6.5095e-05 | 0
2013-05-15 | BR13 | URBAN | Replace Overhead Assets | 21 | 320 | 6720 | 0.010415 | 3.2548e-05 | 0
2013-05-15 | DMA11 | URBAN | Replace Overhead Assets | 69 | 450 | 31050 | 0.048124 | 0.00010694 | 0
2013-05-15 | FTN24 | URBAN | Upgrade capacity - subs and LV | 58 | 490 | 28420 | 0.044048 | 8.9894e-05 | 0
2013-05-15 | MGE32 | URBAN | Regular Maintenance | 2 | 205 | 410 | 0.00063545 | 3.0998e-06 | 0
2013-05-15 | EL14 | RURAL SHORT | Replace Overhead Assets | 35 | 220.6171 | 7721.6 | 0.011968 | 5.4246e-05 | 0
2013-05-16 | M18 | URBAN | Replace Overhead Assets | 106 | 0 | 0 | 0 | 0.00016429 | 0
2013-05-16 | RBD23 | URBAN | Replace plant and equipment | 1 | 350 | 350 | 0.00054246 | 1.5499e-06 | 0
2013-05-16 | DC12 | URBAN | Replace Overhead Assets | 105 | 420 | 44100 | 0.06835 | 0.00016274 | 0
2013-05-16 | EW9 | URBAN | Replace Overhead Assets | 33 | 270 | 8910 | 0.01381 | 5.1146e-05 | 0
2013-05-17 | CRM35 | URBAN | Tree Clearing/Bushfire Mitigation | 345 | 270 | 93150 | 0.14437 | 0.00053471 | 0
2013-05-17 | BH11 | URBAN | Replace Overhead Assets | 95 | 390 | 37050 | 0.057423 | 0.00014724 | 0
2013-05-17 | MC7 | URBAN | Regular Maintenance | 4 | 389 | 1556 | 0.0024116 | 6.1996e-06 | 0
2013-05-19 | HGS23 | URBAN | Tree Clearing/Bushfire Mitigation | 36 | 240 | 8640 | 0.013391 | 5.5796e-05 | 0
2013-05-19 | MC9 | URBAN | Regular Maintenance | 2 | 240 | 480 | 0.00074395 | 3.0998e-06 | 0
2013-05-19 | NP24 | URBAN | Regular Maintenance | 28 | 450 | 12600 | 0.019529 | 4.3397e-05 | 0
2013-05-19 | OE6 | URBAN | Replace Overhead Assets | 4 | 450 | 1800 | 0.0027898 | 6.1996e-06 | 0
2013-05-19 | CRM12 | URBAN | Replace Overhead Assets | 29 | 420 | 12180 | 0.018878 | 4.4947e-05 | 0
2013-05-20 | NRN11 | URBAN | Regular Maintenance | 46 | 120 | 5520 | 0.0085554 | 7.1295e-05 | 0
2013-05-20 | SR24 | RURAL SHORT | Replace Overhead Assets | 106 | 210 | 22260 | 0.034501 | 0.00016429 | 0
2013-05-20 | CRM35 | RURAL SHORT | Replace Overhead Assets | 270 | 326 | 88020 | 0.13642 | 0.00041847 | 0
2013-05-21 | HGS23 | URBAN | Replace Overhead Assets | 4 | 120 | 480 | 0.00074395 | 6.1996e-06 | 0
2013-05-21 | FTN12 | RURAL SHORT | Replace Overhead Assets | 34 | 127 | 4318 | 0.0066924 | 5.2696e-05 | 0
2013-05-21 | LWN31 | URBAN | Replace Overhead Assets | 96 | 230 | 22080 | 0.034222 | 0.00014879 | 0
2013-05-21 | DC6 | URBAN | Replace Overhead Assets | 120 | 248 | 29760 | 0.046125 | 0.00018599 | 0
2013-05-21 | DMA13 | URBAN | Replace Overhead Assets | 28 | 180 | 5040 | 0.0078114 | 4.3397e-05 | 0
2013-05-21 | EW14 | RURAL SHORT | Replace Overhead Assets | 29 | 305 | 8845 | 0.013709 | 4.4947e-05 | 0
2013-05-21 | DC5 | URBAN | Replace Overhead Assets | 64 | 300 | 19200 | 0.029758 | 9.9193e-05 | 0
2013-05-21 | HGS22 | URBAN | Replace Overhead Assets | 1 | 120 | 120 | 0.00018599 | 1.5499e-06 | 0
2013-05-21 | FSH34 | RURAL SHORT | Replace Overhead Assets | 179 | 400 | 71600 | 0.11097 | 0.00027743 | 0
2013-05-22 | CRM33 | URBAN | Replace Overhead Assets | 9 | 195 | 1755 | 0.0027201 | 1.3949e-05 | 0
2013-05-22 | NW13 | URBAN | Regular Maintenance | 4 | 180 | 720 | 0.0011159 | 6.1996e-06 | 0
2013-05-22 | OR7 | RURAL SHORT | Upgrade capacity - subs and LV | 1 | 275 | 275 | 0.00042622 | 1.5499e-06 | 0
2013-05-22 | NW13 | URBAN | Regular Maintenance | 8 | 180 | 1440 | 0.0022318 | 1.2399e-05 | 0
2013-05-22 | MGE24 | URBAN | Replace Overhead Assets | 45 | 270 | 12150 | 0.018831 | 6.9745e-05 | 0
2013-05-22 | MTN31 | URBAN | Upgrade capacity - subs and LV | 194 | 255 | 49470 | 0.076673 | 0.00030068 | 0
2013-05-22 | DVY24 | URBAN | Replace Overhead Assets | 1 | 530 | 530 | 0.00082144 | 1.5499e-06 | 0
2013-05-23 | SS11 | RURAL SHORT | Replace Overhead Assets | 36 | 0 | 0 | 0 | 5.5796e-05 | 0
2013-05-23 | DN13 | URBAN | Replace Overhead Assets | 43 | 295 | 12685 | 0.01966 | 6.6645e-05 | 0
2013-05-23 | BU2 | RURAL SHORT | Replace Overhead Assets | 22 | 300 | 6600 | 0.010229 | 3.4098e-05 | 0
2013-05-23 | SR24 | URBAN | Replace Overhead Assets | 144 | 385 | 55440 | 0.085926 | 0.00022318 | 0
2013-05-23 | HGS23 | URBAN | Improving Reliability | 131 | 445 | 58295 | 0.090351 | 0.00020304 | 0
2013-05-23 | FSH31 | URBAN | Replace Overhead Assets | 257 | 560 | 143920 | 0.22306 | 0.00039832 | 0
2013-05-23 | BW22 | URBAN | Upgrade capacity - subs and LV | 4 | 245 | 980 | 0.0015189 | 6.1996e-06 | 0
2013-05-24 | HT6 | URBAN | Regular Maintenance | 1 | 180 | 180 | 0.00027898 | 1.5499e-06 | 0
2013-05-24 | MGE12 | URBAN | Replace Overhead Assets | 264 | 290 | 76560 | 0.11866 | 0.00040917 | 0
2013-05-24 | DC12 | URBAN | Replace Overhead Assets | 116 | 310 | 35960 | 0.055734 | 0.00017979 | 0
2013-05-24 | STO12 | URBAN | Replace Overhead Assets | 19 | 385 | 7315 | 0.011337 | 2.9448e-05 | 0
2013-05-24 | SR15 | URBAN | Replace Overhead Assets | 105 | 410 | 43050 | 0.066723 | 0.00016274 | 0
2013-05-24 | M23 | URBAN | Replace Overhead Assets | 2 | 540 | 1080 | 0.0016739 | 3.0998e-06 | 0
2013-05-25 | CRM35 | URBAN | Regular Maintenance | 24 | 103 | 2472 | 0.0038313 | 3.7197e-05 | 0
2013-05-26 | MC7 | URBAN | Regular Maintenance | 6 | 180 | 1080 | 0.0016739 | 9.2993e-06 | 0
2013-05-26 | NO5 | URBAN | Upgrade capacity - subs and LV | 13 | 225 | 2925 | 0.0045334 | 2.0149e-05 | 0
2013-05-26 | HT2 | URBAN | Regular Maintenance | 2 | 180 | 360 | 0.00055796 | 3.0998e-06 | 0
2013-05-26 | CM13 | URBAN | Regular Maintenance | 30 | 415 | 12450 | 0.019296 | 4.6497e-05 | 0
2013-05-26 | MC5 | URBAN | Upgrade capacity - subs and LV | 1 | 420 | 420 | 0.00065095 | 1.5499e-06 | 0
2013-05-26 | HGS32 | URBAN | Tree Clearing/Bushfire Mitigation | 15 | 480 | 7200 | 0.011159 | 2.3248e-05 | 0
2013-05-26 | NW32 | URBAN |  | 50 | 600 | 30000 | 0.046497 | 7.7495e-05 | 0
2013-05-26 | DVY14 | URBAN | Replace Overhead Assets | 12 | 870 | 10440 | 0.016181 | 1.8599e-05 | 0
2013-05-27 | CRM35 | URBAN | Replace Overhead Assets | 19 | 135 | 2565 | 0.0039755 | 2.9448e-05 | 0
2013-05-27 | FSH12 | RURAL SHORT | Replace Overhead Assets | 5 | 222 | 1110 | 0.0017204 | 7.7495e-06 | 0
2013-05-27 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 45 | 490 | 22050 | 0.034175 | 6.9745e-05 | 0
2013-05-27 | EL14 | URBAN | Replace Overhead Assets | 2 | 270 | 540 | 0.00083694 | 3.0998e-06 | 0
2013-05-28 | GW7 | URBAN | Replace Overhead Assets | 10 | 150 | 1500 | 0.0023248 | 1.5499e-05 | 0
2013-05-28 | DMA13 | RURAL SHORT | Replace Overhead Assets | 120 | 230 | 27600 | 0.042777 | 0.00018599 | 0
2013-05-28 | DC3 | URBAN | Replace underground assets | 29 | 313 | 9077 | 0.014068 | 4.4947e-05 | 0
2013-05-28 | EW14 | URBAN | Replace Overhead Assets | 15 | 360 | 5400 | 0.0083694 | 2.3248e-05 | 0
2013-05-28 | GW7 | URBAN | Replace Overhead Assets | 16 | 180 | 2880 | 0.0044637 | 2.4798e-05 | 0
2013-05-28 | DMA13 | URBAN | Replace Overhead Assets | 18 | 360 | 6480 | 0.010043 | 2.7898e-05 | 0
2013-05-28 | MTN24 | URBAN | Replace Overhead Assets | 6 | 435 | 2610 | 0.0040452 | 9.2993e-06 | 0
2013-05-28 | BW21 | URBAN | Replace Overhead Assets | 41 | 390 | 15990 | 0.024783 | 6.3545e-05 | 0
2013-05-29 | MTN34 | URBAN | Replace Overhead Assets | 33 | 125 | 4125 | 0.0063933 | 5.1146e-05 | 0
2013-05-29 | MGE32 | URBAN | Replace Overhead Assets | 41 | 240 | 9840 | 0.015251 | 6.3545e-05 | 0
2013-05-29 | STO22 | URBAN | Upgrade capacity - subs and LV | 2 | 270 | 540 | 0.00083694 | 3.0998e-06 | 0
2013-05-29 | HT10 | URBAN | Replace Overhead Assets | 22 | 270 | 5940 | 0.0092063 | 3.4098e-05 | 0
2013-05-29 | DC3 | URBAN | Replace underground assets | 21 | 285 | 5985 | 0.0092761 | 3.2548e-05 | 0
2013-05-29 | K3 | URBAN | Tree Clearing - Urban | 10 | 295 | 2950 | 0.0045722 | 1.5499e-05 | 0
2013-05-29 | OR13 | RURAL SHORT | Replace Overhead Assets | 173 | 360 | 62280 | 0.096527 | 0.00026813 | 0
2013-05-29 | NO7 | URBAN | Replace Overhead Assets | 28 | 360 | 10080 | 0.015623 | 4.3397e-05 | 0
2013-05-29 | DMA13 | URBAN | Replace Overhead Assets | 20 | 380 | 7600 | 0.011779 | 3.0998e-05 | 0
2013-05-29 | LWN31 | URBAN | Replace Overhead Assets | 82 | 410 | 33620 | 0.052107 | 0.00012709 | 0
2013-05-29 | FTN13 | URBAN | Upgrade capacity - subs and LV | 16 | 450 | 7200 | 0.011159 | 2.4798e-05 | 0
2013-05-29 | LWN33 | URBAN | Upgrade capacity - subs and LV | 38 | 465 | 17670 | 0.027387 | 5.8896e-05 | 0
2013-05-29 | NW22 | URBAN | Extended Electricity Supply | 358 | 465 | 166470 | 0.25801 | 0.00055486 | 0
2013-05-30 | DN13 | URBAN | Regular Maintenance | 15 | 145 | 2175 | 0.003371 | 2.3248e-05 | 0
2013-05-30 | CFD14 | URBAN | Replace Overhead Assets | 16 | 270 | 4320 | 0.0066955 | 2.4798e-05 | 0
2013-05-30 | HGS23 | URBAN | Tree Clearing/Bushfire Mitigation | 37 | 395 | 14615 | 0.022652 | 5.7346e-05 | 0
2013-05-30 | DC3 | URBAN | Replace underground assets | 13 | 375 | 4875 | 0.0075557 | 2.0149e-05 | 0
2013-05-30 | MTN31 | URBAN | Upgrade capacity - subs and LV | 66 | 465 | 30690 | 0.047566 | 0.00010229 | 0
2013-05-30 | SVW41 | RURAL SHORT |  | 53 | 505 | 26765 | 0.041483 | 8.2144e-05 | 0
2013-05-30 | DC10 | URBAN | Replace Overhead Assets | 178 | 1439 | 256142 | 0.39699 | 0.00027588 | 0
2013-05-31 | HGS23 | URBAN | Replace Overhead Assets | 124 | 105 | 13020 | 0.02018 | 0.00019219 | 0
2013-05-31 | HGS23 | URBAN | Replace Overhead Assets | 1 | 135 | 135 | 0.00020924 | 1.5499e-06 | 0
2013-05-31 | DC4 | URBAN | Replace Overhead Assets | 28 | 225 | 6300 | 0.0097643 | 4.3397e-05 | 0
2013-05-31 | SR19 | URBAN | Replace Overhead Assets | 25 | 270 | 6750 | 0.010462 | 3.8747e-05 | 0
2013-05-31 | BR6 | URBAN |  | 7 | 276 | 1932 | 0.0029944 | 1.0849e-05 | 0
2013-05-31 | EW12 | URBAN | Replace Overhead Assets | 52 | 270 | 14040 | 0.02176 | 8.0594e-05 | 0
2013-05-31 | NW14 | URBAN | Replace underground assets | 45 | 270 | 12150 | 0.018831 | 6.9745e-05 | 0
2013-05-31 | DC4 | URBAN | Upgrade capacity - subs and LV | 1 | 315 | 315 | 0.00048822 | 1.5499e-06 | 0
2013-05-31 | HT10 | URBAN | Replace Overhead Assets | 36 | 345 | 12420 | 0.01925 | 5.5796e-05 | 0
2013-05-31 | FSH21 | URBAN | Regular Maintenance | 3 | 378 | 1134 | 0.0017576 | 4.6497e-06 | 0
2013-05-31 | MC1 | URBAN | Replace Overhead Assets | 33 | 360 | 11880 | 0.018413 | 5.1146e-05 | 0
2013-06-01 | EM5 | URBAN | Replace Overhead Assets | 22 | 0 | 0 | 0 | 3.4086e-05 | 0
2013-06-02 | MTN23 | URBAN | Tree Clearing/Bushfire Mitigation | 10 | 230 | 2300 | 0.0035635 | 1.5494e-05 | 0
2013-06-02 | SR19 | URBAN | Replace Overhead Assets | 70 | 465 | 32550 | 0.050432 | 0.00010845 | 0
2013-06-02 | BH22 | URBAN | Replace Overhead Assets | 36 | 510 | 18360 | 0.028446 | 5.5777e-05 | 0
2013-06-02 | DSH14 | URBAN | Regular Maintenance | 32 | 575 | 18400 | 0.028508 | 4.9579e-05 | 0
2013-06-02 | DC6 | URBAN | Extended Electricity Supply | 182 | 685 | 124670 | 0.19316 | 0.00028198 | 0
2013-06-03 | BT15 | URBAN | Replace Overhead Assets | 67 | 270 | 18090 | 0.028028 | 0.00010381 | 0
2013-06-04 | MC3 | URBAN | Replace Overhead Assets | 141 | 241 | 33981 | 0.052649 | 0.00021846 | 0
2013-06-04 | OAK33 | RURAL SHORT | Replace plant and equipment | 676 | 330 | 223080 | 0.34563 | 0.0010474 | 0
2013-06-04 | EM1 | URBAN | Replace Overhead Assets | 153 | 420 | 64260 | 0.099562 | 0.00023705 | 0
2013-06-04 | DC3 | URBAN | Replace underground assets | 16 | 360 | 5760 | 0.0089243 | 2.479e-05 | 0
2013-06-04 | MGE22 | URBAN | Replace Overhead Assets | 42 | 410 | 17220 | 0.02668 | 6.5073e-05 | 0
2013-06-04 | BW34 | URBAN | Upgrade capacity - subs and LV | 124 | 470 | 58280 | 0.090297 | 0.00019212 | 0
2013-06-04 | M18 | URBAN | Replace Overhead Assets | 106 | 490 | 51940 | 0.080474 | 0.00016423 | 0
2013-06-05 | OAK23 | URBAN | Replace Overhead Assets | 442 | 300 | 132600 | 0.20544 | 0.00068482 | 0
2013-06-05 | DC3 | URBAN | Replace underground assets | 22 | 280 | 6160 | 0.009544 | 3.4086e-05 | 0
2013-06-05 | MTN31 | URBAN | Replace Overhead Assets | 87 | 295 | 25665 | 0.039764 | 0.00013479 | 0
2013-06-05 | NW13 | RURAL SHORT | Upgrade capacity - subs and LV | 55 | 370 | 20350 | 0.031529 | 8.5215e-05 | 0
2013-06-05 | CRM35 | URBAN | Replace Overhead Assets | 76 | 365 | 27740 | 0.042979 | 0.00011775 | 0
2013-06-05 | CRM35 | RURAL SHORT | Upgrade capacity - subs and LV | 288 | 540 | 155520 | 0.24096 | 0.00044621 | 0
2013-06-06 | HGS22 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 17 | 155.2 | 2638.4 | 0.0040878 | 2.6339e-05 | 0
2013-06-06 | MTN32 | RURAL SHORT | Replace Overhead Assets | 7 | 195 | 1365 | 0.0021149 | 1.0845e-05 | 0
2013-06-06 | SR25 | URBAN | Replace Overhead Assets | 33 | 240 | 7920 | 0.012271 | 5.1129e-05 | 0
2013-06-06 | MR14 | URBAN | Replace Overhead Assets | 61 | 255 | 15555 | 0.0241 | 9.4511e-05 | 0
2013-06-06 | DMA11 | RURAL SHORT | Replace Overhead Assets | 40 | 330 | 13200 | 0.020452 | 6.1974e-05 | 0
2013-06-06 | DMA13 | URBAN | Replace Overhead Assets | 6 | 50 | 300 | 0.00046481 | 9.2961e-06 | 0
2013-06-06 | LD6 | URBAN | Upgrade capacity - subs and LV | 77 | 345 | 26565 | 0.041159 | 0.0001193 | 0
2013-06-06 | CM13 | URBAN |  | 71 | 390 | 27690 | 0.042902 | 0.00011 | 0
2013-06-06 | NP25 | URBAN | Regular Maintenance | 1 | 390 | 390 | 0.00060425 | 1.5494e-06 | 0
2013-06-06 | DC3 | RURAL SHORT | Replace underground assets | 29 | 367 | 10643 | 0.01649 | 4.4931e-05 | 0
2013-06-06 | M12 | URBAN | Replace Overhead Assets | 133 | 470 | 62510 | 0.09685 | 0.00020606 | 0
2013-06-06 | CRM22 | URBAN | Regular Maintenance | 43 | 480 | 20640 | 0.031979 | 6.6622e-05 | 0
2013-06-07 | GW1 | URBAN | Replace underground assets | 4 | 75 | 300 | 0.00046481 | 6.1974e-06 | 0
2013-06-07 | EW14 | URBAN | Replace Overhead Assets | 27 | 150 | 4050 | 0.0062749 | 4.1833e-05 | 0
2013-06-07 | MGE12 | URBAN | Replace Overhead Assets | 24 | 300 | 7200 | 0.011155 | 3.7185e-05 | 0
2013-06-07 | NW13 | URBAN | Upgrade capacity - subs and LV | 8 | 390 | 3120 | 0.004834 | 1.2395e-05 | 0
2013-06-07 | FSH21 | URBAN | Regular Maintenance | 7 | 265 | 1855 | 0.0028741 | 1.0845e-05 | 0
2013-06-07 | HGS23 | URBAN | Upgrade capacity - subs and LV | 54 | 350 | 18900 | 0.029283 | 8.3665e-05 | 0
2013-06-09 | SV32 | URBAN | Replace Overhead Assets | 177 | 400 | 70800 | 0.10969 | 0.00027424 | 0
2013-06-09 | DSH14 | RURAL SHORT | Regular Maintenance | 1 | 420 | 420 | 0.00065073 | 1.5494e-06 | 0
2013-06-09 | BH12 | RURAL SHORT | Replace Overhead Assets | 9 | 360 | 3240 | 0.0050199 | 1.3944e-05 | 0
2013-06-09 | DSH34 | RURAL SHORT | Replace Overhead Assets | 4 | 560 | 2240 | 0.0034706 | 6.1974e-06 | 0
2013-06-11 | SR15 | URBAN | Extended Electricity Supply | 93 | 65 | 6045 | 0.0093659 | 0.00014409 | 0
2013-06-11 | SV32 | URBAN | Replace Overhead Assets | 30 | 180 | 5400 | 0.0083665 | 4.6481e-05 | 0
2013-06-11 | SR25 | URBAN | Replace Overhead Assets | 76 | 240 | 18240 | 0.02826 | 0.00011775 | 0
2013-06-11 | OAK33 | URBAN | Replace Overhead Assets | 99 | 250 | 24750 | 0.038347 | 0.00015339 | 0
2013-06-11 | DSH33 | URBAN | Upgrade capacity - subs and LV | 6 | 445 | 2670 | 0.0041368 | 9.2961e-06 | 0
2013-06-11 | MC1 | URBAN | Regular Maintenance | 115 | 450 | 51750 | 0.080179 | 0.00017818 | 0
2013-06-11 | NP33 | RURAL SHORT | Replace Overhead Assets | 89 | 405 | 36045 | 0.055847 | 0.00013789 | 0
2013-06-11 | BU2 | URBAN | Replace underground assets | 23 | 345 | 7935 | 0.012294 | 3.5635e-05 | 0
2013-06-12 | CRM24 | URBAN | Regular Maintenance | 79 | 120 | 9480 | 0.014688 | 0.0001224 | 0
2013-06-12 | CRM22 | URBAN | Upgrade capacity - subs and LV | 57 | 100 | 5700 | 0.0088313 | 8.8313e-05 | 0
2013-06-12 | RBD21 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 17 | 215 | 3655 | 0.0056629 | 2.6339e-05 | 0
2013-06-12 | OR4 | URBAN | Tree Clearing - Urban | 295 | 220 | 64900 | 0.10055 | 0.00045706 | 0
2013-06-12 | RWT18 | URBAN | Replace Overhead Assets | 43 | 345 | 14835 | 0.022985 | 6.6622e-05 | 0
2013-06-12 | OAK26 | URBAN | Replace Overhead Assets | 326 | 315 | 102690 | 0.1591 | 0.00050509 | 0
2013-06-12 | OAK21 | URBAN | Replace Overhead Assets | 61 | 240 | 14640 | 0.022683 | 9.4511e-05 | 0
2013-06-12 | DC3 | URBAN | Replace underground assets | 13 | 332 | 4316 | 0.006687 | 2.0142e-05 | 0
2013-06-12 | MC3 | URBAN | Regular Maintenance | 73 | 405 | 29565 | 0.045807 | 0.0001131 | 0
2013-06-12 | OAK21 | URBAN | Replace plant and equipment | 116 | 150 | 17400 | 0.026959 | 0.00017973 | 0
2013-06-13 | CDA11 | RURAL SHORT | Replace Overhead Assets | 48 | 71 | 3408 | 0.0052802 | 7.4369e-05 | 0
2013-06-13 | DVY34 | URBAN | Regular Maintenance | 13 | 218 | 2834 | 0.0043909 | 2.0142e-05 | 0
2013-06-13 | MTN31 | URBAN | Extended Electricity Supply | 45 | 135 | 6075 | 0.0094123 | 6.9721e-05 | 0
2013-06-13 | RD4 | URBAN | Replace plant and equipment | 284 | 240 | 68160 | 0.1056 | 0.00044002 | 0
2013-06-13 | LD5 | URBAN | Replace Overhead Assets | 101 | 220 | 22220 | 0.034427 | 0.00015649 | 0
2013-06-13 | DMA13 | URBAN | Tree Clearing/Bushfire Mitigation | 37 | 330 | 12210 | 0.018918 | 5.7326e-05 | 0
2013-06-13 | NW31 | URBAN | Upgrade capacity - subs and LV | 131 | 390 | 51090 | 0.079157 | 0.00020297 | 0
2013-06-13 | K7 | URBAN | Replace plant and equipment | 56 | 240 | 13440 | 0.020823 | 8.6764e-05 | 0
2013-06-13 | NB22 | URBAN | Replace Overhead Assets | 8 | 480 | 3840 | 0.0059495 | 1.2395e-05 | 0
2013-06-13 | DC3 | URBAN | Replace underground assets | 22 | 360 | 7920 | 0.012271 | 3.4086e-05 | 0
2013-06-14 | NB14 | URBAN | Replace Overhead Assets | 34 | 360 | 12240 | 0.018964 | 5.2678e-05 | 0
2013-06-14 | MC6 | URBAN | Regular Maintenance | 46 | 345 | 15870 | 0.024588 | 7.127e-05 | 0
2013-06-14 | GW3 | URBAN | Replace Overhead Assets | 14 | 420 | 5880 | 0.0091102 | 2.1691e-05 | 0
2013-06-14 | OAK26 | RURAL SHORT | Replace underground assets | 3 | 240 | 720 | 0.0011155 | 4.6481e-06 | 0
2013-06-14 | MGE24 | URBAN | Upgrade capacity - subs and LV | 131 | 480 | 62880 | 0.097424 | 0.00020297 | 0
2013-06-14 | RBD23 | RURAL SHORT | Upgrade capacity - subs and LV | 41 | 505 | 20705 | 0.032079 | 6.3524e-05 | 0
2013-06-15 | EM5 | URBAN | Replace Overhead Assets | 22 | 345 | 7590 | 0.01176 | 3.4086e-05 | 0
2013-06-15 | FSH33 | RURAL SHORT | Replace Overhead Assets | 15 | 345 | 5175 | 0.0080179 | 2.324e-05 | 0
2013-06-15 | FTN11 | URBAN | Replace Overhead Assets | 49 | 390 | 19110 | 0.029608 | 7.5918e-05 | 0
2013-06-16 | NO3 | URBAN | Replace plant and equipment | 2 | 295 | 590 | 0.00091412 | 3.0987e-06 | 0
2013-06-16 | FTN11 | URBAN | Replace Overhead Assets | 2 | 392 | 784 | 0.0012147 | 3.0987e-06 | 0
2013-06-16 | OAK35 | URBAN | Replace Overhead Assets | 330 | 475 | 156750 | 0.24286 | 0.00051129 | 0
2013-06-16 | SVW45 | URBAN | Upgrade capacity - subs and LV | 11 | 465 | 5115 | 0.007925 | 1.7043e-05 | 0
2013-06-16 | MC6 | URBAN | Regular Maintenance | 49 | 510 | 24990 | 0.038718 | 7.5918e-05 | 0
2013-06-16 | SH80 | URBAN | Replace Overhead Assets | 122 | 565 | 68930 | 0.1068 | 0.00018902 | 0
2013-06-16 | MGE22 | URBAN | Replace Overhead Assets | 36 | 520 | 18720 | 0.029004 | 5.5777e-05 | 0
2013-06-17 | EB32 | URBAN | Regular Maintenance | 1 | 75 | 75 | 0.0001162 | 1.5494e-06 | 0
2013-06-17 | CRM24 | URBAN | Regular Maintenance | 5 | 45 | 225 | 0.00034861 | 7.7468e-06 | 0
2013-06-18 | FSH11 | URBAN | Regular Maintenance | 2 | 90 | 180 | 0.00027888 | 3.0987e-06 | 0
2013-06-18 | FSH11 | URBAN | Regular Maintenance | 2 | 100 | 200 | 0.00030987 | 3.0987e-06 | 0
2013-06-18 | BH23 | URBAN | Regular Maintenance | 6 | 254 | 1524 | 0.0023612 | 9.2961e-06 | 0
2013-06-18 | MC1 | RURAL SHORT | Regular Maintenance | 59 | 75 | 4425 | 0.0068559 | 9.1412e-05 | 0
2013-06-18 | MC2 | RURAL SHORT | Replace Overhead Assets | 28 | 195 | 5460 | 0.0084595 | 4.3382e-05 | 0
2013-06-18 | CDA21 | URBAN | Replace plant and equipment | 355 | 270 | 95850 | 0.14851 | 0.00055002 | 0
2013-06-18 | DMA15 | URBAN | Replace Overhead Assets | 8 | 210 | 1680 | 0.0026029 | 1.2395e-05 | 0
2013-06-18 | HGS23 | URBAN | Replace Overhead Assets | 2 | 240 | 480 | 0.00074369 | 3.0987e-06 | 0
2013-06-18 | M14 | URBAN | Replace Overhead Assets | 13 | 235 | 3055 | 0.0047333 | 2.0142e-05 | 0
2013-06-18 | MGE34 | URBAN |  | 37 | 260 | 9620 | 0.014905 | 5.7326e-05 | 0
2013-06-18 | DC3 | RURAL SHORT | Replace underground assets | 17 | 310 | 5270 | 0.0081651 | 2.6339e-05 | 0
2013-06-18 | STO21 | URBAN | Replace Overhead Assets | 42 | 345 | 14490 | 0.02245 | 6.5073e-05 | 0
2013-06-18 | SS11 | URBAN | Replace plant and equipment | 265 | 175 | 46375 | 0.071851 | 0.00041058 | 0
2013-06-18 | SH80 | RURAL SHORT | Replace Overhead Assets | 38 | 425 | 16150 | 0.025022 | 5.8876e-05 | 0
2013-06-18 | FSH31 | URBAN | Replace Overhead Assets | 38 | 390 | 14820 | 0.022961 | 5.8876e-05 | 0
2013-06-18 | SS11 | URBAN | Upgrade capacity - subs and LV | 35 | 455 | 15925 | 0.024674 | 5.4227e-05 | 0
2013-06-18 | DMA15 | RURAL SHORT | Replace Overhead Assets | 3 | 210 | 630 | 0.00097609 | 4.6481e-06 | 0
2013-06-19 | DC3 | URBAN | Replace underground assets | 48 | 293 | 14064 | 0.02179 | 7.4369e-05 | 0
2013-06-19 | DN10 | URBAN | Replace Overhead Assets | 11 | 255 | 2805 | 0.0043459 | 1.7043e-05 | 0
2013-06-19 | DMA12 | URBAN | Replace Overhead Assets | 20 | 315 | 6300 | 0.0097609 | 3.0987e-05 | 0
2013-06-19 | CRM12 | URBAN | Replace Overhead Assets | 3 | 300 | 900 | 0.0013944 | 4.6481e-06 | 0
2013-06-19 | LD6 | URBAN | Replace Overhead Assets | 12 | 325 | 3900 | 0.0060425 | 1.8592e-05 | 0
2013-06-19 | DMA14 | URBAN | Replace Overhead Assets | 52 | 375 | 19500 | 0.030212 | 8.0567e-05 | 0
2013-06-19 | HGS22 | URBAN | Tree Clearing/Bushfire Mitigation | 82 | 460 | 37720 | 0.058442 | 0.00012705 | 0
2013-06-19 | CFD12 | URBAN | Extended Electricity Supply | 51 | 495 | 25245 | 0.039114 | 7.9017e-05 | 0
2013-06-20 | CFD13 | URBAN | Replace Overhead Assets | 37 | 210 | 7770 | 0.012039 | 5.7326e-05 | 0
2013-06-20 | STO12 | RURAL SHORT | Replace Overhead Assets | 81 | 240 | 19440 | 0.03012 | 0.0001255 | 0
2013-06-20 | MGE34 | URBAN | Replace Overhead Assets | 9 | 210 | 1890 | 0.0029283 | 1.3944e-05 | 0
2013-06-20 | DC3 | URBAN | Replace underground assets | 8 | 280 | 2240 | 0.0034706 | 1.2395e-05 | 0
2013-06-20 | DC8 | RURAL SHORT | Replace Overhead Assets | 43 | 240 | 10320 | 0.015989 | 6.6622e-05 | 0
2013-06-20 | LD6 | URBAN | Replace Overhead Assets | 20 | 300 | 6000 | 0.0092961 | 3.0987e-05 | 0
2013-06-20 | DN10 | RURAL SHORT | Regular Maintenance | 23 | 357 | 8211 | 0.012722 | 3.5635e-05 | 0
2013-06-20 | DMA12 | URBAN | Improving Reliability | 65 | 420 | 27300 | 0.042297 | 0.00010071 | 0
2013-06-20 | STO23 | URBAN | Replace Overhead Assets | 85 | 320 | 27200 | 0.042143 | 0.0001317 | 0
2013-06-20 | CFD22 | URBAN | Upgrade capacity - subs and LV | 234 | 420 | 98280 | 0.15227 | 0.00036255 | 0
2013-06-20 | MC1 | URBAN | Regular Maintenance | 352 | 475 | 167200 | 0.25905 | 0.00054537 | 0
2013-06-21 | BH23 | URBAN | Regular Maintenance | 1 | 265 | 265 | 0.00041058 | 1.5494e-06 | 0
2013-06-21 | BH23 | URBAN | Regular Maintenance | 2 | 265 | 530 | 0.00082116 | 3.0987e-06 | 0
2013-06-21 | CDA22 | URBAN | Replace Overhead Assets | 299 | 205 | 61295 | 0.094968 | 0.00046326 | 0
2013-06-21 | CDA11 | RURAL SHORT | Replace Overhead Assets | 36 | 150 | 5400 | 0.0083665 | 5.5777e-05 | 0
2013-06-21 | DC1 | URBAN | Replace Overhead Assets | 5 | 245 | 1225 | 0.001898 | 7.7468e-06 | 0
2013-06-21 | MGE23 | RURAL SHORT | Replace Overhead Assets | 36 | 240 | 8640 | 0.013386 | 5.5777e-05 | 0
2013-06-21 | CDA11 | URBAN | Replace Overhead Assets | 114 | 120 | 13680 | 0.021195 | 0.00017663 | 0
2013-06-21 | MTN23 | URBAN | Replace Overhead Assets | 50 | 135 | 6750 | 0.010458 | 7.7468e-05 | 0
2013-06-21 | FTN13 | URBAN | Tree Clearing/Bushfire Mitigation | 1 | 465 | 465 | 0.00072045 | 1.5494e-06 | 0
2013-06-23 | OAK24 | RURAL SHORT |  | 14 | 30 | 420 | 0.00065073 | 2.1691e-05 | 0
2013-06-23 | CRM22 | URBAN | Replace Overhead Assets | 114 | 265 | 30210 | 0.046806 | 0.00017663 | 0
2013-06-23 | LD5 | URBAN | Regular Maintenance | 6 | 310 | 1860 | 0.0028818 | 9.2961e-06 | 0
2013-06-23 | DSH33 | URBAN | Improving Reliability | 3 | 390 | 1170 | 0.0018127 | 4.6481e-06 | 0
2013-06-23 | CFD24 | RURAL SHORT | Extended Electricity Supply | 12 | 405 | 4860 | 0.0075299 | 1.8592e-05 | 0
2013-06-23 | CDA22 | URBAN | Replace Overhead Assets | 287 | 380 | 109060 | 0.16897 | 0.00044467 | 0
2013-06-23 | OAK23 | URBAN | Replace Overhead Assets | 412 | 240 | 98880 | 0.1532 | 0.00063834 | 0
2013-06-23 | SV32 | URBAN | Upgrade capacity - subs and LV | 4 | 405 | 1620 | 0.00251 | 6.1974e-06 | 0
2013-06-23 | AR12 | URBAN | Regular Maintenance | 1 | 345 | 345 | 0.00053453 | 1.5494e-06 | 0
2013-06-24 | DC1 | RURAL SHORT | Regular Maintenance | 2 | 155 | 310 | 0.0004803 | 3.0987e-06 | 0
2013-06-24 | HGS32 | RURAL SHORT | Regular Maintenance | 5 | 355 | 1775 | 0.0027501 | 7.7468e-06 | 0
2013-06-24 | SVW41 | URBAN | Replace Overhead Assets | 1 | 350 | 350 | 0.00054227 | 1.5494e-06 | 0
2013-06-24 | DSH24 | URBAN | Replace Overhead Assets | 16 | 365 | 5840 | 0.0090482 | 2.479e-05 | 0
2013-06-24 | RBD22 | URBAN | Regular Maintenance | 1 | 315 | 315 | 0.00048805 | 1.5494e-06 | 0
2013-06-25 | HGS32 | URBAN | Regular Maintenance | 5 | 160 | 800 | 0.0012395 | 7.7468e-06 | 0
2013-06-25 | DN13 | RURAL SHORT | Replace Overhead Assets | 51 | 220 | 11220 | 0.017384 | 7.9017e-05 | 0
2013-06-25 | MC1 | URBAN | Regular Maintenance | 120 | 300 | 36000 | 0.055777 | 0.00018592 | 0
2013-06-25 | CDA22 | URBAN | Replace Overhead Assets | 11 | 300 | 3300 | 0.0051129 | 1.7043e-05 | 0
2013-06-25 | CRM22 | URBAN | Replace Overhead Assets | 30 | 270 | 8100 | 0.01255 | 4.6481e-05 | 0
2013-06-25 | DC3 | URBAN | Replace underground assets | 34 | 295 | 10030 | 0.01554 | 5.2678e-05 | 0
2013-06-25 | NW22 | URBAN | Upgrade capacity - subs and LV | 46 | 330 | 15180 | 0.023519 | 7.127e-05 | 0
2013-06-25 | BH23 | URBAN | Replace Overhead Assets | 63 | 330 | 20790 | 0.032211 | 9.7609e-05 | 0
2013-06-25 | HGS23 | URBAN | Upgrade capacity - subs and LV | 17 | 405 | 6885 | 0.010667 | 2.6339e-05 | 0
2013-06-25 | CRM14 | RURAL SHORT | Replace Overhead Assets | 55 | 435 | 23925 | 0.037068 | 8.5215e-05 | 0
2013-06-25 | BC22 | RURAL SHORT | Replace Overhead Assets | 93 | 270 | 25110 | 0.038904 | 0.00014409 | 0
2013-06-26 | K7 | URBAN | Replace plant and equipment | 56 | 0 | 0 | 0 | 8.6764e-05 | 0
2013-06-26 | DC3 | URBAN | Replace underground assets | 23 | 325 | 7475 | 0.011581 | 3.5635e-05 | 0
2013-06-26 | CRM22 | RURAL SHORT | Upgrade capacity - subs and LV | 24 | 360 | 8640 | 0.013386 | 3.7185e-05 | 0
2013-06-26 | FSH11 | URBAN | Replace Overhead Assets | 38 | 375 | 14250 | 0.022078 | 5.8876e-05 | 0
2013-06-26 | CFD13 | URBAN | Replace Overhead Assets | 108 | 392 | 42336 | 0.065594 | 0.00016733 | 0
2013-06-26 | RWT16 | URBAN | Regular Maintenance | 59 | 420 | 24780 | 0.038393 | 9.1412e-05 | 0
2013-06-26 | CFD12 | URBAN | Extended Electricity Supply | 72 | 405 | 29160 | 0.045179 | 0.00011155 | 0
2013-06-26 | DMA12 | URBAN | Replace Overhead Assets | 140 | 465 | 65100 | 0.10086 | 0.00021691 | 0
2013-06-26 | MTN23 | URBAN | Regular Maintenance | 6 | 175 | 1050 | 0.0016268 | 9.2961e-06 | 0
2013-06-26 | MGE32 | URBAN | Replace Overhead Assets | 1 | 210 | 210 | 0.00032536 | 1.5494e-06 | 0
2013-06-27 | RBD12 | URBAN | Regular Maintenance | 3 | 120 | 360 | 0.00055777 | 4.6481e-06 | 0
2013-06-27 | HGS22 | RURAL SHORT | Replace Overhead Assets | 58 | 120 | 6960 | 0.010784 | 8.9863e-05 | 0
2013-06-27 | EW14 | URBAN | Regular Maintenance | 28 | 150 | 4200 | 0.0065073 | 4.3382e-05 | 0
2013-06-27 | DC3 | URBAN | Replace underground assets | 22 | 285 | 6270 | 0.0097145 | 3.4086e-05 | 0
2013-06-27 | CRM35 | URBAN | Regular Maintenance | 304 | 395 | 120080 | 0.18605 | 0.000471 | 0
2013-06-26 | EW9 | RURAL SHORT | Replace Overhead Assets | 13 | 1890 | 24570 | 0.038068 | 2.0142e-05 | 0
2013-06-27 | BR9 | URBAN | Replace Overhead Assets | 2 | 555 | 1110 | 0.0017198 | 3.0987e-06 | 0
2013-06-27 | FSH23 | RURAL SHORT | Replace Overhead Assets | 49 | 630 | 30870 | 0.047829 | 7.5918e-05 | 0
2013-06-27 | EW9 | URBAN | Replace Overhead Assets | 52 | 245 | 12740 | 0.019739 | 8.0567e-05 | 0
2013-06-28 | STO21 | URBAN | Replace Overhead Assets | 38 | 91.9 | 3492.2 | 0.0054107 | 5.8876e-05 | 0
2013-06-28 | CRM22 | URBAN | Regular Maintenance | 66 | 270 | 17820 | 0.02761 | 0.00010226 | 0
2013-06-28 | CDA22 | URBAN | Replace Overhead Assets | 18 | 360 | 6480 | 0.01004 | 2.7888e-05 | 0
2013-06-28 | LD4 | URBAN | Regular Maintenance | 103 | 375 | 38625 | 0.059844 | 0.00015958 | 0
2013-06-28 | DMA15 | URBAN | Replace Overhead Assets | 8 | 145 | 1160 | 0.0017973 | 1.2395e-05 | 0
2013-06-28 | RBD24 | URBAN | Upgrade capacity - subs and LV | 74 | 425 | 31450 | 0.048727 | 0.00011465 | 0
2013-06-29 | MTN22 | URBAN | Replace Overhead Assets | 91 | 420 | 38220 | 0.059216 | 0.00014099 | 0
2013-06-30 | DVY31 | URBAN | Regular Maintenance | 1 | 70 | 70 | 0.00010845 | 1.5494e-06 | 0
2013-06-30 | HT8 | URBAN | Regular Maintenance | 2 | 320 | 640 | 0.00099159 | 3.0987e-06 | 0
2013-06-30 | BW22 | URBAN | Replace Overhead Assets | 38 | 330 | 12540 | 0.019429 | 5.8876e-05 | 0
2013-06-30 | CDA11 | URBAN | Replace Overhead Assets | 131 | 420 | 55020 | 0.085246 | 0.00020297 | 0
2013-06-30 | RWT16 | URBAN | Replace Overhead Assets | 24 | 480 | 11520 | 0.017849 | 3.7185e-05 | 0
2013-06-30 | MC3 | URBAN | Regular Maintenance | 213 | 465 | 99045 | 0.15346 | 0.00033001 | 0
2013-06-30 | HGS33 | URBAN | Replace Overhead Assets | 65 | 490 | 31850 | 0.049347 | 0.00010071 | 0
2013-06-30 | DSH33 | URBAN | Extended Electricity Supply | 3 | 582 | 1746 | 0.0027052 | 4.6481e-06 | 0
2013-07-01 | GW2 | URBAN | Regular Maintenance | 21 | 145 | 3045 | 0.0047321 | 3.2635e-05 | 0
2013-07-01 | NB22 | RURAL SHORT | Replace Overhead Assets | 32 | 186 | 5952 | 0.0092497 | 4.9729e-05 | 0
2013-07-01 | OR6 | RURAL SHORT | Replace Overhead Assets | 14 | 275 | 3850 | 0.0059831 | 2.1757e-05 | 0
2013-07-01 | EM6 | URBAN | Replace Overhead Assets | 66 | 365 | 24090 | 0.037437 | 0.00010257 | 0
2013-07-01 | EB31 | URBAN | Extended Electricity Supply | 121 | 415 | 50215 | 0.078036 | 0.00018804 | 0
2013-07-02 | DC2 | URBAN | Replace underground assets | 20 | 155 | 3100 | 0.0048175 | 3.1081e-05 | 0
2013-07-02 | SR15 | URBAN | Replace Overhead Assets | 29 | 165 | 4785 | 0.0074361 | 4.5067e-05 | 0
2013-07-02 | LWN34 | URBAN | Replace Overhead Assets | 9 | 195 | 1755 | 0.0027273 | 1.3986e-05 | 0
2013-07-02 | LWN32 | URBAN | Replace Overhead Assets | 48 | 300 | 14400 | 0.022378 | 7.4594e-05 | 0
2013-07-02 | MEN11 | URBAN | Regular Maintenance | 2 | 180 | 360 | 0.00055946 | 3.1081e-06 | 0
2013-07-02 | CFD15 | URBAN | Replace Overhead Assets | 5 | 270 | 1350 | 0.002098 | 7.7702e-06 | 0
2013-07-02 | CRM22 | URBAN | Regular Maintenance | 231 | 320 | 73920 | 0.11487 | 0.00035898 | 0
2013-07-02 | DC2 | URBAN | Replace Overhead Assets | 5 | 330 | 1650 | 0.0025642 | 7.7702e-06 | 0
2013-07-02 | CDA11 | URBAN | Replace Overhead Assets | 45 | 455 | 20475 | 0.031819 | 6.9932e-05 | 0
2013-07-02 | OAK26 | URBAN | Improving Reliability | 113 | 485 | 54805 | 0.085169 | 0.00017561 | 0
2013-07-03 | SR25 | URBAN | Replace Overhead Assets | 76 | 240 | 18240 | 0.028346 | 0.00011811 | 0
2013-07-03 | LD6 | URBAN | Replace Overhead Assets | 6 | 200 | 1200 | 0.0018649 | 9.3243e-06 | 0
2013-07-03 | NW31 | URBAN | Replace Overhead Assets | 55 | 300 | 16500 | 0.025642 | 8.5472e-05 | 0
2013-07-03 | MTN32 | RURAL SHORT | Upgrade capacity - subs and LV | 9 | 350 | 3150 | 0.0048952 | 1.3986e-05 | 0
2013-07-03 | GW11 | URBAN | Replace Overhead Assets | 149 | 405 | 60345 | 0.093779 | 0.00023155 | 0
2013-07-03 | NW22 | URBAN | Extended Electricity Supply | 357 | 500 | 178500 | 0.2774 | 0.00055479 | 0
2013-07-04 | OAK23 | URBAN | Replace Overhead Assets | 81 | 170 | 13770 | 0.021399 | 0.00012588 | 0
2013-07-04 | DC10 | RURAL SHORT | Replace Overhead Assets | 24 | 255 | 6120 | 0.0095107 | 3.7297e-05 | 0
2013-07-04 | CM25 | URBAN | Replace Overhead Assets | 10 | 315 | 3150 | 0.0048952 | 1.554e-05 | 0
2013-07-04 | SR11 | RURAL SHORT | Replace Overhead Assets | 43 | 320 | 13760 | 0.021384 | 6.6824e-05 | 0
2013-07-04 | STO23 | URBAN | Replace Overhead Assets | 28 | 209 | 5852 | 0.0090943 | 4.3513e-05 | 0
2013-07-04 | CRM35 | URBAN | Replace Overhead Assets | 61 | 400 | 24400 | 0.037919 | 9.4797e-05 | 0
2013-07-04 | BW34 | URBAN | Replace Overhead Assets | 113 | 360 | 40680 | 0.063218 | 0.00017561 | 0
2013-07-05 | CRM33 | URBAN | Regular Maintenance | 43 | 130 | 5590 | 0.0086871 | 6.6824e-05 | 0
2013-07-05 | STO22 | URBAN | Replace underground assets | 2 | 150 | 300 | 0.00046621 | 3.1081e-06 | 0
2013-07-05 | M23 | URBAN | Regular Maintenance | 106 | 80 | 8480 | 0.013178 | 0.00016473 | 0
2013-07-05 | CRM22 | URBAN | Upgrade capacity - subs and LV | 61 | 340 | 20740 | 0.032231 | 9.4797e-05 | 0
2013-07-05 | HGS22 | URBAN | Replace Overhead Assets | 31 | 305 | 9455 | 0.014693 | 4.8175e-05 | 0
2013-07-05 | GW11 | URBAN | Replace Overhead Assets | 75 | 298 | 22350 | 0.034733 | 0.00011655 | 0
2013-07-05 | DC3 | URBAN | Replace underground assets | 23 | 450 | 10350 | 0.016084 | 3.5743e-05 | 0
2013-07-07 | DN21 | URBAN | Regular Maintenance | 5 | 180 | 900 | 0.0013986 | 7.7702e-06 | 0
2013-07-07 | DN2 | URBAN | Replace Overhead Assets | 12 | 380 | 4560 | 0.0070864 | 1.8649e-05 | 0
2013-07-07 | DC5 | URBAN | Regular Maintenance | 30 | 480 | 14400 | 0.022378 | 4.6621e-05 | 0
2013-07-07 | BH22 | URBAN | Replace Overhead Assets | 70 | 540 | 37800 | 0.058743 | 0.00010878 | 0
2013-07-07 | MC7 | URBAN | Replace Overhead Assets | 7 | 540 | 3780 | 0.0058743 | 1.0878e-05 | 0
2013-07-08 | NB22 | URBAN | Replace Overhead Assets | 18 | 280 | 5040 | 0.0078324 | 2.7973e-05 | 0
2013-07-08 | SR15 | RURAL SHORT | Replace Overhead Assets | 77 | 435 | 33495 | 0.052053 | 0.00011966 | 0
2013-07-09 | CDA11 | RURAL SHORT | Replace Overhead Assets | 154 | 247 | 38038 | 0.059113 | 0.00023932 | 0
2013-07-09 | MGE23 | URBAN | Replace underground assets | 36 | 268 | 9648 | 0.014993 | 5.5946e-05 | 0
2013-07-09 | LWN31 | URBAN | Regular Maintenance | 1 | 331 | 331 | 0.00051439 | 1.554e-06 | 0
2013-07-09 | LWN31 | URBAN | Replace Overhead Assets | 18 | 330 | 5940 | 0.009231 | 2.7973e-05 | 0
2013-07-09 | CRM33 | RURAL SHORT | Replace Overhead Assets | 19 | 307 | 5833 | 0.0090647 | 2.9527e-05 | 0
2013-07-09 | K12 | RURAL SHORT | Improving Reliability | 94 | 360 | 33840 | 0.052589 | 0.00014608 | 0
2013-07-09 | CFD12 | URBAN | Replace Overhead Assets | 23 | 360 | 8280 | 0.012867 | 3.5743e-05 | 0
2013-07-09 | DN10 | URBAN | Regular Maintenance | 28 | 405 | 11340 | 0.017623 | 4.3513e-05 | 0
2013-07-09 | DVY34 | RURAL SHORT | Regular Maintenance | 10 | 395 | 3950 | 0.0061385 | 1.554e-05 | 0
2013-07-09 | EB32 | URBAN | Replace Overhead Assets | 85 | 480 | 40800 | 0.063405 | 0.00013209 | 0
2013-07-10 | OR13 | RURAL SHORT | Replace Overhead Assets | 15 | 75 | 1125 | 0.0017483 | 2.3311e-05 | 0
2013-07-10 | EB12 | URBAN | Replace Overhead Assets | 12 | 150 | 1800 | 0.0027973 | 1.8649e-05 | 0
2013-07-10 | DC1 | URBAN | Replace underground assets | 10 | 247 | 2470 | 0.0038385 | 1.554e-05 | 0
2013-07-10 | EB12 | RURAL SHORT | Replace Overhead Assets | 47 | 145 | 6815 | 0.010591 | 7.304e-05 | 0
2013-07-10 | RWT18 | URBAN | Replace underground assets | 27 | 300 | 8100 | 0.012588 | 4.1959e-05 | 0
2013-07-10 | LD32 | URBAN | Replace Overhead Assets | 9 | 245 | 2205 | 0.0034267 | 1.3986e-05 | 0
2013-07-10 | MEN11 | URBAN | Upgrade capacity - subs and LV | 308 | 325 | 100100 | 0.15556 | 0.00047865 | 0
2013-07-10 | DMA14 | URBAN | Replace plant and equipment | 285 | 420 | 119700 | 0.18602 | 0.0004429 | 0
2013-07-11 | FSH22 | RURAL SHORT | Replace Overhead Assets | 69 | 300 | 20700 | 0.032169 | 0.00010723 | 0
2013-07-11 | BR9 | URBAN | Upgrade capacity - subs and LV | 22 | 290 | 6380 | 0.0099148 | 3.4189e-05 | 0
2013-07-11 | LD1 | URBAN | Regular Maintenance | 26 | 390 | 10140 | 0.015758 | 4.0405e-05 | 0
2013-07-12 | BH21 | RURAL SHORT | Replace Overhead Assets | 94 | 380 | 35720 | 0.05551 | 0.00014608 | 0
2013-07-12 | FSH32 | URBAN | Upgrade capacity - subs and LV | 27 | 355 | 9585 | 0.014895 | 4.1959e-05 | 0
2013-07-12 | FTN14 | URBAN | Replace Overhead Assets | 66 | 400 | 26400 | 0.041027 | 0.00010257 | 0
2013-07-13 | M17 | URBAN | Upgrade capacity - subs and LV | 83 | 450 | 37350 | 0.058043 | 0.00012899 | 0
2013-07-14 | DN21 | URBAN | Regular Maintenance | 1 | 105 | 105 | 0.00016317 | 1.554e-06 | 0
2013-07-14 | DMA12 | URBAN | Replace Overhead Assets | 37 | 95 | 3515 | 0.0054625 | 5.75e-05 | 0
2013-07-14 | FSH23 | URBAN | Regular Maintenance | 1 | 360 | 360 | 0.00055946 | 1.554e-06 | 0
2013-07-14 | CRM22 | URBAN | Upgrade capacity - subs and LV | 198 | 450 | 89100 | 0.13847 | 0.0003077 | 0
2013-07-14 | CM25 | URBAN | Improving Reliability | 185 | 420 | 77700 | 0.12075 | 0.0002875 | 0
2013-07-14 | SH80 | URBAN | Replace Overhead Assets | 121 | 540 | 65340 | 0.10154 | 0.00018804 | 0
2013-07-16 | NW11 | URBAN | Replace underground assets | 52 | 180 | 9360 | 0.014546 | 8.081e-05 | 0
2013-07-16 | FTN12 | URBAN | Replace Overhead Assets | 31 | 270 | 8370 | 0.013007 | 4.8175e-05 | 0
2013-07-16 | EL10 | URBAN | Replace Overhead Assets | 32 | 271 | 8672 | 0.013477 | 4.9729e-05 | 0
2013-07-16 | RWT18 | URBAN | Replace underground assets | 18 | 285 | 5130 | 0.0079722 | 2.7973e-05 | 0
2013-07-16 | NB22 | URBAN | Replace Overhead Assets | 8 | 320 | 2560 | 0.0039783 | 1.2432e-05 | 0
2013-07-16 | MTN32 | URBAN | Tree Clearing/Bushfire Mitigation | 40 | 355 | 14200 | 0.022067 | 6.2162e-05 | 0
2013-07-16 | FTN12 | URBAN | Replace Overhead Assets | 25 | 310 | 7750 | 0.012044 | 3.8851e-05 | 0
2013-07-16 | FTN12 | RURAL SHORT | Regular Maintenance | 1 | 329 | 329 | 0.00051128 | 1.554e-06 | 0
2013-07-16 | CRM12 | URBAN | Upgrade capacity - subs and LV | 190 | 405 | 76950 | 0.11958 | 0.00029527 | 0
2013-07-16 | CDA23 | URBAN | Replace Overhead Assets | 80 | 360 | 28800 | 0.044756 | 0.00012432 | 0
2013-07-17 | MGE24 | URBAN | Replace Overhead Assets | 2 | 200 | 400 | 0.00062162 | 3.1081e-06 | 0
2013-07-17 | DMA15 | URBAN | Replace Overhead Assets | 2 | 195 | 390 | 0.00060608 | 3.1081e-06 | 0
2013-07-17 | NP23 | URBAN | Replace Overhead Assets | 12 | 139 | 1668 | 0.0025921 | 1.8649e-05 | 0
2013-07-17 | OR4 | URBAN | Replace Overhead Assets | 20 | 180 | 3600 | 0.0055946 | 3.1081e-05 | 0
2013-07-17 | DVY34 | URBAN | Regular Maintenance | 8 | 180 | 1440 | 0.0022378 | 1.2432e-05 | 0
2013-07-17 | BR13 | URBAN | Replace Overhead Assets | 89 | 275 | 24475 | 0.038035 | 0.00013831 | 0
2013-07-17 | BU1 | URBAN | Replace underground assets | 32 | 240 | 7680 | 0.011935 | 4.9729e-05 | 0
2013-07-17 | BT10 | URBAN | Replace Overhead Assets | 71 | 300 | 21300 | 0.033101 | 0.00011034 | 0
2013-07-17 | RWT18 | URBAN | Replace underground assets | 19 | 285 | 5415 | 0.0084151 | 2.9527e-05 | 0
2013-07-17 | FSH21 | URBAN | Upgrade capacity - subs and LV | 28 | 255 | 7140 | 0.011096 | 4.3513e-05 | 0
2013-07-18 | NW13 | URBAN | Upgrade capacity - subs and LV | 13 | 60 | 780 | 0.0012122 | 2.0203e-05 | 0
2013-07-18 | RWT16 | RURAL SHORT | Replace Overhead Assets | 85 | 120 | 10200 | 0.015851 | 0.00013209 | 0
2013-07-18 | MEN11 | URBAN | Replace Overhead Assets | 56 | 185 | 10360 | 0.0161 | 8.7026e-05 | 0
2013-07-18 | HGS22 | URBAN | Replace Overhead Assets | 2 | 255 | 510 | 0.00079256 | 3.1081e-06 | 0
2013-07-18 | MTN32 | URBAN | Tree Clearing/Bushfire Mitigation | 38 | 420 | 15960 | 0.024803 | 5.9054e-05 | 0
2013-07-18 | CFD23 | URBAN | Replace Overhead Assets | 121 | 341 | 41261 | 0.064121 | 0.00018804 | 0
2013-07-19 | DC2 | URBAN | Replace underground assets | 10 | 130 | 1300 | 0.0020203 | 1.554e-05 | 0
2013-07-19 | CRM35 | URBAN | Regular Maintenance | 98 | 295 | 28910 | 0.044927 | 0.0001523 | 0
2013-07-19 | DC2 | URBAN | Replace underground assets | 19 | 115 | 2185 | 0.0033956 | 2.9527e-05 | 0
2013-07-19 | HGS22 | URBAN | Replace Overhead Assets | 85 | 375 | 31875 | 0.049535 | 0.00013209 | 0
2013-07-19 | OAK26 | URBAN | Replace Overhead Assets | 136 | 380 | 51680 | 0.080313 | 0.00021135 | 0
2013-07-19 | DMA14 | URBAN | Replace Overhead Assets | 17 | 380 | 6460 | 0.010039 | 2.6419e-05 | 0
2013-07-21 | SVW55 | URBAN | Regular Maintenance | 4 | 180 | 720 | 0.0011189 | 6.2162e-06 | 0
2013-07-21 | NO7 | URBAN | Upgrade capacity - subs and LV | 8 | 180 | 1440 | 0.0022378 | 1.2432e-05 | 0
2013-07-21 | DN10 | URBAN | Replace Overhead Assets | 75 | 150 | 11250 | 0.017483 | 0.00011655 | 0
2013-07-21 | HT2 | URBAN | Replace Overhead Assets | 14 | 360 | 5040 | 0.0078324 | 2.1757e-05 | 0
2013-07-21 | SH81 | URBAN | Replace Overhead Assets | 373 | 360 | 134280 | 0.20868 | 0.00057966 | 0
2013-07-21 | NO3 | URBAN | Upgrade capacity - subs and LV | 10 | 130 | 1300 | 0.0020203 | 1.554e-05 | 0
2013-07-21 | M32 | URBAN | Regular Maintenance | 158 | 480 | 75840 | 0.11786 | 0.00024554 | 0
2013-07-21 | DSH33 | URBAN | Improving Reliability | 72 | 470 | 33840 | 0.052589 | 0.00011189 | 0
2013-07-21 | RBD14 | URBAN | Replace Overhead Assets | 140 | 400 | 56000 | 0.087026 | 0.00021757 | 0
2013-07-21 | HT9 | URBAN | Replace Overhead Assets | 20 | 525 | 10500 | 0.016317 | 3.1081e-05 | 0
2013-07-21 | AR2 | URBAN | Upgrade capacity - subs and LV | 131 | 435 | 56985 | 0.088557 | 0.00020358 | 0
2013-07-22 | HGS22 | URBAN | Tree Clearing/Bushfire Mitigation | 32 | 255 | 8160 | 0.012681 | 4.9729e-05 | 0
2013-07-23 | EM11 | URBAN | Replace Overhead Assets | 49 | 180 | 8820 | 0.013707 | 7.6148e-05 | 0
2013-07-23 | BT10 | URBAN | Replace Overhead Assets | 24 | 250 | 6000 | 0.0093243 | 3.7297e-05 | 0
2013-07-23 | K13 | URBAN |  | 32 | 210 | 6720 | 0.010443 | 4.9729e-05 | 0
2013-07-23 | M35 | URBAN | Replace Overhead Assets | 13 | 245 | 3185 | 0.0049496 | 2.0203e-05 | 0
2013-07-23 | DC1 | URBAN | Replace underground assets | 3 | 150 | 450 | 0.00069932 | 4.6621e-06 | 0
2013-07-23 | DN22 | URBAN | Replace Overhead Assets | 86 | 250 | 21500 | 0.033412 | 0.00013365 | 0
2013-07-23 | BW34 | URBAN | Replace Overhead Assets | 14 | 290 | 4060 | 0.0063094 | 2.1757e-05 | 0
2013-07-23 | K13 | URBAN | Replace Overhead Assets | 50 | 75 | 3750 | 0.0058277 | 7.7702e-05 | 0
2013-07-23 | MTN34 | URBAN | Replace Overhead Assets | 33 | 420 | 13860 | 0.021539 | 5.1283e-05 | 0
2013-07-24 | DC3 | RURAL SHORT | Regular Maintenance | 13 | 105 | 1365 | 0.0021213 | 2.0203e-05 | 0
2013-07-24 | DMA12 | URBAN | Replace Overhead Assets | 7 | 220 | 1540 | 0.0023932 | 1.0878e-05 | 0
2013-07-24 | DN10 | URBAN | Replace Overhead Assets | 84 | 170 | 14280 | 0.022192 | 0.00013054 | 0
2013-07-24 | LD7 | URBAN | Replace Overhead Assets | 36 | 245 | 8820 | 0.013707 | 5.5946e-05 | 0
2013-07-24 | DC3 | URBAN | Regular Maintenance | 25 | 100 | 2500 | 0.0038851 | 3.8851e-05 | 0
2013-07-24 | HGS23 | URBAN | Replace Overhead Assets | 6 | 75 | 450 | 0.00069932 | 9.3243e-06 | 0
2013-07-24 | NW13 | RURAL SHORT | Replace Overhead Assets | 44 | 360 | 15840 | 0.024616 | 6.8378e-05 | 0
2013-07-24 | RWT16 | URBAN | Replace Overhead Assets | 29 | 405 | 11745 | 0.018252 | 4.5067e-05 | 0
2013-07-25 | BH21 | URBAN | Replace Overhead Assets | 33 | 195 | 6435 | 0.01 | 5.1283e-05 | 0
2013-07-25 | MTN35 | URBAN | Upgrade capacity - subs and LV | 126 | 360 | 45360 | 0.070491 | 0.00019581 | 0
2013-07-25 | DN11 | URBAN | Replace Overhead Assets | 21 | 420 | 8820 | 0.013707 | 3.2635e-05 | 0
2013-07-25 | M34 | URBAN | Replace plant and equipment | 26 | 435 | 11310 | 0.017576 | 4.0405e-05 | 0
2013-07-26 | LWN31 | URBAN | Replace Overhead Assets | 14 | 140 | 1960 | 0.0030459 | 2.1757e-05 | 0
2013-07-26 | BU14 | URBAN | Regular Maintenance | 1 | 180 | 180 | 0.00027973 | 1.554e-06 | 0
2013-07-26 | STO13 | URBAN | Replace Overhead Assets | 32 | 330 | 10560 | 0.016411 | 4.9729e-05 | 0
2013-07-26 | BU10 | URBAN | Replace Overhead Assets | 6 | 345 | 2070 | 0.0032169 | 9.3243e-06 | 0
2013-07-26 | STO12 | URBAN | Replace Overhead Assets | 394 | 405 | 159570 | 0.24798 | 0.00061229 | 0
2013-07-27 | FSH11 | URBAN | Replace Overhead Assets | 17 | 201 | 3417 | 0.0053102 | 2.6419e-05 | 0
2013-07-27 | DN8 | URBAN | Replace Overhead Assets | 19 | 407 | 7733 | 0.012017 | 2.9527e-05 | 0
2013-07-28 | FSH32 | URBAN | Regular Maintenance | 1 | 90 | 90 | 0.00013986 | 1.554e-06 | 0
2013-07-28 | M31 | URBAN | Replace Overhead Assets | 18 | 265 | 4770 | 0.0074128 | 2.7973e-05 | 0
2013-07-28 | DC3 | URBAN | Regular Maintenance | 1 | 240 | 240 | 0.00037297 | 1.554e-06 | 0
2013-07-28 | SR25 | URBAN | Replace Overhead Assets | 70 | 400 | 28000 | 0.043513 | 0.00010878 | 0
2013-07-28 | CM11 | URBAN | Replace Overhead Assets | 30 | 465 | 13950 | 0.021679 | 4.6621e-05 | 0
2013-07-28 | CFD15 | URBAN |  | 42 | 465 | 19530 | 0.03035 | 6.527e-05 | 0
2013-07-28 | HT10 | URBAN | Upgrade capacity - subs and LV | 388 | 520 | 201760 | 0.31354 | 0.00060297 | 0
2013-07-30 | HGS22 | RURAL SHORT | Replace Overhead Assets | 2 | 41 | 82 | 0.00012743 | 3.1081e-06 | 0
2013-07-30 | HGS22 | RURAL SHORT | Replace Overhead Assets | 1 | 45 | 45 | 6.9932e-05 | 1.554e-06 | 0
2013-07-30 | DN10 | URBAN | Replace Overhead Assets | 11 | 225 | 2475 | 0.0038463 | 1.7094e-05 | 0
2013-07-30 | LWN31 | URBAN | Replace Overhead Assets | 51 | 270 | 13770 | 0.021399 | 7.9256e-05 | 0
2013-07-30 | HGS22 | URBAN | Replace Overhead Assets | 8 | 75 | 600 | 0.00093243 | 1.2432e-05 | 0
2013-07-30 | HGS22 | URBAN | Replace Overhead Assets | 1 | 60 | 60 | 9.3243e-05 | 1.554e-06 | 0
2013-07-30 | BR9 | URBAN | Upgrade capacity - subs and LV | 10 | 285 | 2850 | 0.004429 | 1.554e-05 | 0
2013-07-30 | EB22 | URBAN | Replace Overhead Assets | 145 | 375 | 54375 | 0.084501 | 0.00022534 | 0
2013-07-30 | M22 | URBAN | Regular Maintenance | 1 | 392 | 392 | 0.00060918 | 1.554e-06 | 0
2013-07-31 | DC3 | URBAN | Regular Maintenance | 1 | 155 | 155 | 0.00024088 | 1.554e-06 | 0
2013-07-31 | GW7 | URBAN | Replace Overhead Assets | 196 | 270 | 52920 | 0.08224 | 0.00030459 | 0
2013-07-31 | OAK26 | URBAN | Replace Overhead Assets | 71 | 225 | 15975 | 0.024826 | 0.00011034 | 0
2013-07-31 | CRM35 | URBAN | Replace Overhead Assets | 90 | 345 | 31050 | 0.048253 | 0.00013986 | 0
2013-07-31 | K4 | URBAN | Replace Overhead Assets | 35 | 390 | 13650 | 0.021213 | 5.4391e-05 | 0
2013-07-31 | EB22 | URBAN | Replace Overhead Assets | 72 | 375 | 27000 | 0.041959 | 0.00011189 | 0
2013-07-31 | MTN32 | URBAN | Upgrade capacity - subs and LV | 23 | 435 | 10005 | 0.015548 | 3.5743e-05 | 0
2013-07-31 | DSH33 | URBAN | Regular Maintenance | 15 | 435 | 6525 | 0.01014 | 2.3311e-05 | 0
2013-08-01 | HGS23 | URBAN | Replace Overhead Assets | 49 | 305 | 14945 | 0.023179 | 7.5998e-05 | 0
2013-08-01 | NW13 | URBAN | Regular Maintenance | 4 | 105 | 420 | 0.00065141 | 6.2039e-06 | 0
2013-08-01 | HGS33 | URBAN | Replace Overhead Assets | 1 | 193 | 193 | 0.00029934 | 1.551e-06 | 0
2013-08-01 | K10 | URBAN | Replace Overhead Assets | 54 | 370 | 19980 | 0.030989 | 8.3753e-05 | 0
2013-08-02 | EL8 | URBAN | Replace Overhead Assets | 45 | 85 | 3825 | 0.0059325 | 6.9794e-05 | 0
2013-08-02 | HGS33 | RURAL SHORT | Replace Overhead Assets | 24 | 210 | 5040 | 0.0078169 | 3.7223e-05 | 0
2013-08-02 | MC7 | URBAN | Regular Maintenance | 5 | 260 | 1300 | 0.0020163 | 7.7549e-06 | 0
2013-08-02 | BU2 | RURAL SHORT | Regular Maintenance | 3 | 37 | 111 | 0.00017216 | 4.6529e-06 | 0
2013-08-02 | CRM35 | URBAN | Regular Maintenance | 40 | 352 | 14080 | 0.021838 | 6.2039e-05 | 0
2013-08-02 | OR13 | URBAN | Replace Overhead Assets | 15 | 390 | 5850 | 0.0090732 | 2.3265e-05 | 0
2013-08-04 | CFD12 | URBAN |  | 53 | 480 | 25440 | 0.039457 | 8.2202e-05 | 0
2013-08-04 | SH80 | RURAL SHORT | Improving Reliability | 168 | 630 | 105840 | 0.16416 | 0.00026056 | 0
2013-08-04 | SR15 | URBAN | Improving Reliability | 228 | 695 | 158460 | 0.24577 | 0.00035362 | 0
2013-08-06 | NO7 | URBAN | Upgrade capacity - subs and LV | 3 | 30 | 90 | 0.00013959 | 4.6529e-06 | 0
2013-08-06 | EW12 | URBAN | Replace Overhead Assets | 259 | 235 | 60865 | 0.0944 | 0.0004017 | 0
2013-08-06 | SH70 | URBAN | Replace Overhead Assets | 500 | 340 | 170000 | 0.26367 | 0.00077549 | 0
2013-08-06 | SS11 | URBAN | Replace Overhead Assets | 52 | 315 | 16380 | 0.025405 | 8.0651e-05 | 0
2013-08-06 | DN6 | URBAN | Replace Overhead Assets | 56 | 375 | 21000 | 0.032571 | 8.6855e-05 | 0
2013-08-06 | DC10 | RURAL SHORT | Replace underground assets | 6 | 180 | 1080 | 0.0016751 | 9.3059e-06 | 0
2013-08-06 | CRM13 | URBAN | Tree Clearing/Bushfire Mitigation | 59 | 405 | 23895 | 0.037061 | 9.1508e-05 | 0
2013-08-06 | MTN34 | URBAN | Replace Overhead Assets | 70 | 540 | 37800 | 0.058627 | 0.00010857 | 0
2013-08-07 | DC1 | URBAN | Replace underground assets | 2 | 120 | 240 | 0.00037223 | 3.102e-06 | 0
2013-08-07 | MGE24 | URBAN | Replace Overhead Assets | 191 | 210 | 40110 | 0.06221 | 0.00029624 | 0
2013-08-07 | OAK33 | RURAL SHORT | Replace Overhead Assets | 145 | 240 | 34800 | 0.053974 | 0.00022489 | 0
2013-08-07 | RWT24 | URBAN | Replace Overhead Assets | 33 | 270 | 8910 | 0.013819 | 5.1182e-05 | 0
2013-08-07 | LWN31 | URBAN | Replace Overhead Assets | 36 | 330 | 11880 | 0.018426 | 5.5835e-05 | 0
2013-08-07 | DN10 | URBAN | Replace Overhead Assets | 83 | 327 | 27141 | 0.042095 | 0.00012873 | 0
2013-08-07 | STO12 | URBAN | Replace Overhead Assets | 25 | 380 | 9500 | 0.014734 | 3.8774e-05 | 0
2013-08-07 | FTN11 | URBAN | Replace Overhead Assets | 30 | 347 | 10410 | 0.016146 | 4.6529e-05 | 0
2013-08-07 | DMA12 | URBAN | Replace Overhead Assets | 37 | 391 | 14467 | 0.022438 | 5.7386e-05 | 0
2013-08-07 | BC23 | RURAL SHORT | Improving Reliability | 86 | 480 | 41280 | 0.064024 | 0.00013338 | 0
2013-08-08 | NP33 | URBAN | Replace Overhead Assets | 22 | 164 | 3608 | 0.0055959 | 3.4121e-05 | 0
2013-08-08 | GW6 | URBAN | Replace Overhead Assets | 391 | 165 | 64515 | 0.10006 | 0.00060643 | 0
2013-08-08 | MGE32 | URBAN | Replace Overhead Assets | 31 | 265 | 8215 | 0.012741 | 4.808e-05 | 0
2013-08-08 | EM8 | URBAN | Replace Overhead Assets | 61 | 250 | 15250 | 0.023652 | 9.461e-05 | 0
2013-08-08 | LWN31 | URBAN | Regular Maintenance | 81 | 440 | 35640 | 0.055277 | 0.00012563 | 0
2013-08-08 | NW23 | URBAN | Replace Overhead Assets | 45 | 480 | 21600 | 0.033501 | 6.9794e-05 | 0
2013-08-09 | CFD23 | URBAN | Extended Electricity Supply | 83 | 20 | 1660 | 0.0025746 | 0.00012873 | 0
2013-08-09 | DC3 | URBAN | Regular Maintenance | 4 | 120 | 480 | 0.00074447 | 6.2039e-06 | 0
2013-08-09 | HGS22 | URBAN | Replace Overhead Assets | 15 | 300 | 4500 | 0.0069794 | 2.3265e-05 | 0
2013-08-09 | FTN12 | URBAN | Replace Overhead Assets | 170 | 308 | 52360 | 0.081209 | 0.00026367 | 0
2013-08-10 | DN13 | URBAN | Regular Maintenance | 17 | 361 | 6137 | 0.0095183 | 2.6367e-05 | 0
2013-08-10 | NP36 | URBAN |  | 111 | 470 | 52170 | 0.080914 | 0.00017216 | 0
2013-08-11 | CFD15 | URBAN |  | 50 | 265 | 13250 | 0.02055 | 7.7549e-05 | 0
2013-08-11 | BU13 | URBAN | Upgrade capacity - subs and LV | 22 | 420 | 9240 | 0.014331 | 3.4121e-05 | 0
2013-08-11 | MC9 | URBAN | Regular Maintenance | 151 | 435 | 65685 | 0.10188 | 0.0002342 | 0
2013-08-12 | LWN31 | RURAL SHORT | Replace Overhead Assets | 62 | 310 | 19220 | 0.02981 | 9.6161e-05 | 0
2013-08-12 | OAK33 | URBAN | Replace Overhead Assets | 59 | 285 | 16815 | 0.02608 | 9.1508e-05 | 0
2013-08-12 | LWN31 | URBAN | Replace Overhead Assets | 3 | 150 | 450 | 0.00069794 | 4.6529e-06 | 0
2013-08-12 | FTN14 | RURAL SHORT | Regular Maintenance | 35 | 458 | 16030 | 0.024862 | 5.4284e-05 | 0
2013-08-13 | MGE21 | URBAN | Replace underground assets | 20 | 0 | 0 | 0 | 3.102e-05 | 0
2013-08-13 | GW5 | URBAN | Regular Maintenance | 63 | 50 | 3150 | 0.0048856 | 9.7712e-05 | 0
2013-08-13 | SS23 | URBAN | Replace Overhead Assets | 57 | 0 | 0 | 0 | 8.8406e-05 | 0
2013-08-13 | FSH23 | URBAN | Replace Overhead Assets | 3 | 210 | 630 | 0.00097712 | 4.6529e-06 | 0
2013-08-13 | NP33 | URBAN | Replace Overhead Assets | 28 | 260 | 7280 | 0.011291 | 4.3427e-05 | 0
2013-08-13 | CRM12 | URBAN | Replace Overhead Assets | 123 | 285 | 35055 | 0.054369 | 0.00019077 | 0
2013-08-13 | CRM35 | URBAN | Regular Maintenance | 73 | 336 | 24528 | 0.038042 | 0.00011322 | 0
2013-08-13 | LWN31 | URBAN | Regular Maintenance | 29 | 360 | 10440 | 0.016192 | 4.4978e-05 | 0
2013-08-13 | NW13 | URBAN | Upgrade capacity - subs and LV | 13 | 405 | 5265 | 0.0081659 | 2.0163e-05 | 0
2013-08-14 | M32 | URBAN | Replace Overhead Assets | 86 | 190 | 16340 | 0.025343 | 0.00013338 | 0
2013-08-14 | MGE21 | URBAN | Replace underground assets | 20 | 213 | 4260 | 0.0066072 | 3.102e-05 | 0
2013-08-14 | MTN32 | URBAN | Upgrade capacity - subs and LV | 25 | 150 | 3750 | 0.0058162 | 3.8774e-05 | 0
2013-08-14 | EB12 | URBAN | Replace Overhead Assets | 88 | 345 | 30360 | 0.047088 | 0.00013649 | 0
2013-08-14 | BU9 | URBAN | Replace underground assets | 67 | 290 | 19430 | 0.030135 | 0.00010392 | 0
2013-08-14 | HGS23 | URBAN | Replace plant and equipment | 134 | 210 | 28140 | 0.043644 | 0.00020783 | 0
2013-08-15 | SVW42 | URBAN | Regular Maintenance | 3 | 135 | 405 | 0.00062815 | 4.6529e-06 | 0
2013-08-15 | EM8 | URBAN | Replace Overhead Assets | 68 | 195 | 13260 | 0.020566 | 0.00010547 | 0
2013-08-15 | M35 | URBAN | Replace Overhead Assets | 13 | 195 | 2535 | 0.0039317 | 2.0163e-05 | 0
2013-08-15 | EM8 | URBAN | Replace Overhead Assets | 68 | 290 | 19720 | 0.030585 | 0.00010547 | 0
2013-08-15 | DC2 | URBAN | Replace underground assets | 35 | 275 | 9625 | 0.014928 | 5.4284e-05 | 0
2013-08-15 | MR32 | URBAN | Upgrade capacity - subs and LV | 3 | 215 | 645 | 0.0010004 | 4.6529e-06 | 0
2013-08-15 | OR9 | URBAN | Improving Reliability | 6 | 300 | 1800 | 0.0027918 | 9.3059e-06 | 0
2013-08-15 | OAK26 | RURAL SHORT | Replace Overhead Assets | 84 | 90 | 7560 | 0.011725 | 0.00013028 | 0
2013-08-15 | LWN31 | URBAN | Regular Maintenance | 134 | 415 | 55610 | 0.08625 | 0.00020783 | 0
2013-08-15 | FTN13 | URBAN | Regular Maintenance | 79 | 390 | 30810 | 0.047786 | 0.00012253 | 0
2013-08-16 | DC3 | RURAL SHORT | Replace underground assets | 26 | 0 | 0 | 0 | 4.0325e-05 | 0
2013-08-16 | HGS33 | RURAL SHORT | Replace Overhead Assets | 11 | 160 | 1760 | 0.0027297 | 1.7061e-05 | 0
2013-08-16 | EB13 | URBAN | Replace underground assets | 31 | 120 | 3720 | 0.0057696 | 4.808e-05 | 0
2013-08-16 | CDA24 | URBAN | Replace Overhead Assets | 2 | 210 | 420 | 0.00065141 | 3.102e-06 | 0
2013-08-16 | FSH12 | URBAN | Improving Reliability | 16 | 210 | 3360 | 0.0052113 | 2.4816e-05 | 0
2013-08-16 | LWN31 | URBAN | Replace plant and equipment | 30 | 210 | 6300 | 0.0097712 | 4.6529e-05 | 0
2013-08-16 | CRM14 | URBAN | Regular Maintenance | 21 | 240 | 5040 | 0.0078169 | 3.2571e-05 | 0
2013-08-18 | RWT16 | URBAN | Replace Overhead Assets | 487 | 355 | 172885 | 0.26814 | 0.00075533 | 0
2013-08-18 | MC4 | RURAL SHORT | Regular Maintenance | 87 | 389 | 33843 | 0.05249 | 0.00013493 | 0
2013-08-18 | M11 | URBAN | Upgrade capacity - subs and LV | 182 | 368 | 66976 | 0.10388 | 0.00028228 | 0
2013-08-18 | BH21 | RURAL SHORT | Replace Overhead Assets | 161 | 480 | 77280 | 0.11986 | 0.00024971 | 0
2013-08-19 | NO5 | URBAN | Replace underground assets | 142 | 165 | 23430 | 0.036339 | 0.00022024 | 0
2013-08-19 | NP33 | URBAN | Replace Overhead Assets | 83 | 250 | 20750 | 0.032183 | 0.00012873 | 0
2013-08-20 | NP23 | URBAN | Replace Overhead Assets | 2 | 150 | 300 | 0.00046529 | 3.102e-06 | 0
2013-08-20 | EW12 | RURAL SHORT | Replace Overhead Assets | 6 | 220 | 1320 | 0.0020473 | 9.3059e-06 | 0
2013-08-20 | DC12 | URBAN | Replace Overhead Assets | 25 | 300 | 7500 | 0.011632 | 3.8774e-05 | 0
2013-08-20 | MGE23 | URBAN | Replace Overhead Assets | 58 | 330 | 19140 | 0.029686 | 8.9957e-05 | 0
2013-08-20 | LD1 | URBAN | Regular Maintenance | 20 | 270 | 5400 | 0.0083753 | 3.102e-05 | 0
2013-08-21 | CRM12 | URBAN | Regular Maintenance | 33 | 175 | 5775 | 0.0089569 | 5.1182e-05 | 0
2013-08-21 | BR10 | URBAN | Regular Maintenance | 34 | 363 | 12342 | 0.019142 | 5.2733e-05 | 0
2013-08-21 | MC7 | URBAN | Regular Maintenance | 3 | 480 | 1440 | 0.0022334 | 4.6529e-06 | 0
2013-08-22 | EM8 | URBAN | Replace Overhead Assets | 79 | 30 | 2370 | 0.0036758 | 0.00012253 | 0
2013-08-22 | M34 | RURAL SHORT | Regular Maintenance | 122 | 110 | 13420 | 0.020814 | 0.00018922 | 0
2013-08-22 | DC3 | URBAN | Replace underground assets | 10 | 185 | 1850 | 0.0028693 | 1.551e-05 | 0
2013-08-22 | NP23 | URBAN | Regular Maintenance | 27 | 225 | 6075 | 0.0094222 | 4.1876e-05 | 0
2013-08-22 | SS14 | URBAN | Upgrade capacity - subs and LV | 18 | 300 | 5400 | 0.0083753 | 2.7918e-05 | 0
2013-08-22 | RBD21 | URBAN | Replace plant and equipment | 11 | 360 | 3960 | 0.0061419 | 1.7061e-05 | 0
2013-08-22 | RBD23 | URBAN | Improving Reliability | 249 | 338 | 84162 | 0.13053 | 0.00038619 | 0
2013-08-22 | BR10 | URBAN | Regular Maintenance | 76 | 390 | 29640 | 0.045971 | 0.00011787 | 0
2013-08-23 | NB25 | URBAN | Tree Clearing - Urban | 2 | 180 | 360 | 0.00055835 | 3.102e-06 | 0
2013-08-23 | DC5 | URBAN | Replace Overhead Assets | 53 | 190 | 10070 | 0.015618 | 8.2202e-05 | 0
2013-08-23 | DC3 | URBAN | Replace underground assets | 15 | 180 | 2700 | 0.0041876 | 2.3265e-05 | 0
2013-08-23 | DMA13 | URBAN | Replace plant and equipment | 4 | 210 | 840 | 0.0013028 | 6.2039e-06 | 0
2013-08-23 | M11 | RURAL SHORT | Regular Maintenance | 24 | 315 | 7560 | 0.011725 | 3.7223e-05 | 0
2013-08-23 | M32 | URBAN | Regular Maintenance | 19 | 330 | 6270 | 0.0097246 | 2.9469e-05 | 0
2013-08-23 | DMA13 | RURAL SHORT | Replace plant and equipment | 3 | 165 | 495 | 0.00076773 | 4.6529e-06 | 0
2013-08-23 | MGE14 | URBAN | Replace plant and equipment | 4 | 225 | 900 | 0.0013959 | 6.2039e-06 | 0
2013-08-24 | FSH13 | URBAN | Replace plant and equipment | 8 | 440 | 3520 | 0.0054594 | 1.2408e-05 | 0
2013-08-25 | CRM12 | URBAN | Regular Maintenance | 89 | 280 | 24920 | 0.03865 | 0.00013804 | 0
2013-08-25 | MGE32 | RURAL SHORT | Extended Electricity Supply | 1 | 390 | 390 | 0.00060488 | 1.551e-06 | 0
2013-08-25 | DMA13 | URBAN | Extended Electricity Supply | 26 | 420 | 10920 | 0.016937 | 4.0325e-05 | 0
2013-08-25 | K13 | RURAL SHORT | Replace plant and equipment | 36 | 455 | 16380 | 0.025405 | 5.5835e-05 | 0
2013-08-27 | DC7 | RURAL SHORT | Replace underground assets | 7 | 265 | 1855 | 0.0028771 | 1.0857e-05 | 0
2013-08-27 | RBD24 | URBAN | Regular Maintenance | 22 | 135 | 2970 | 0.0046064 | 3.4121e-05 | 0
2013-08-27 | DC3 | URBAN | Upgrade capacity - subs and LV | 1 | 160 | 160 | 0.00024816 | 1.551e-06 | 0
2013-08-27 | DC3 | URBAN | Replace underground assets | 17 | 240 | 4080 | 0.006328 | 2.6367e-05 | 0
2013-08-27 | CFD26 | URBAN | Upgrade capacity - subs and LV | 64 | 370 | 23680 | 0.036727 | 9.9263e-05 | 0
2013-08-27 | WD36 | URBAN | Replace Overhead Assets | 187 | 460 | 86020 | 0.13342 | 0.00029003 | 0
2013-08-27 | NP23 | URBAN | Replace Overhead Assets | 21 | 450 | 9450 | 0.014657 | 3.2571e-05 | 0
2013-08-28 | HGS22 | URBAN | Replace Overhead Assets | 2 | 90 | 180 | 0.00027918 | 3.102e-06 | 0
2013-08-28 | EB12 | RURAL SHORT | Upgrade capacity - subs and LV | 72 | 210 | 15120 | 0.023451 | 0.00011167 | 0
2013-08-28 | DC10 | URBAN | Replace underground assets | 16 | 245 | 3920 | 0.0060798 | 2.4816e-05 | 0
2013-08-28 | LWN31 | URBAN | Regular Maintenance | 3 | 302 | 906 | 0.0014052 | 4.6529e-06 | 0
2013-08-28 | DMA15 | URBAN | Replace Overhead Assets | 4 | 210 | 840 | 0.0013028 | 6.2039e-06 | 0
2013-08-28 | OAK21 | URBAN | Replace Overhead Assets | 34 | 345 | 11730 | 0.018193 | 5.2733e-05 | 0
2013-08-28 | SV16 | RURAL SHORT | Upgrade capacity - subs and LV | 3 | 495 | 1485 | 0.0023032 | 4.6529e-06 | 0
2013-08-29 | CRM12 | URBAN | Regular Maintenance | 46 | 245 | 11270 | 0.01748 | 7.1345e-05 | 0
2013-08-29 | BH22 | URBAN | Upgrade capacity - subs and LV | 1 | 275 | 275 | 0.00042652 | 1.551e-06 | 0
2013-08-29 | WD36 | URBAN | Replace Overhead Assets | 115 | 405 | 46575 | 0.072237 | 0.00017836 | 0
2013-08-29 | MTN32 | URBAN | Upgrade capacity - subs and LV | 40 | 395 | 15800 | 0.024505 | 6.2039e-05 | 0
2013-08-29 | OR9 | URBAN | Replace plant and equipment | 6 | 390 | 2340 | 0.0036293 | 9.3059e-06 | 0
2013-08-29 | DC3 | URBAN | Replace underground assets | 29 | 375 | 10875 | 0.016867 | 4.4978e-05 | 0
2013-08-29 | CRM14 | URBAN | Regular Maintenance | 60 | 195 | 11700 | 0.018146 | 9.3059e-05 | 0
2013-08-30 | BU1 | URBAN | Replace Overhead Assets | 37 | 240 | 8880 | 0.013773 | 5.7386e-05 | 0
2013-08-30 | EB32 | URBAN | Upgrade capacity - subs and LV | 1 | 270 | 270 | 0.00041876 | 1.551e-06 | 0
2013-08-30 | DC10 | URBAN | Replace underground assets | 25 | 255 | 6375 | 0.0098875 | 3.8774e-05 | 0
2013-08-30 | NP23 | URBAN | Regular Maintenance | 21 | 386 | 8106 | 0.012572 | 3.2571e-05 | 0
2013-08-30 | FSH33 | URBAN | Replace Overhead Assets | 272 | 430 | 116960 | 0.1814 | 0.00042187 | 0
2013-09-01 | LD4 | URBAN | Tree Clearing - Urban | 33 | 300 | 9900 | 0.015365 | 5.1216e-05 | 0
2013-09-01 | DN10 | URBAN | Replace Overhead Assets | 79 | 315 | 24885 | 0.038622 | 0.00012261 | 0
2013-09-01 | DC6 | URBAN | Replace Overhead Assets | 108 | 610 | 65880 | 0.10225 | 0.00016762 | 0
2013-09-02 | MTN32 | URBAN | Replace Overhead Assets | 1 | 82 | 82 | 0.00012727 | 1.552e-06 | 0
2013-09-02 | SS23 | URBAN | Replace Overhead Assets | 57 | 305 | 17385 | 0.026982 | 8.8465e-05 | 0
2013-09-02 | HGS22 | URBAN | Replace Overhead Assets | 1 | 125 | 125 | 0.000194 | 1.552e-06 | 0
2013-09-02 | DN7 | URBAN | Replace Overhead Assets | 14 | 420 | 5880 | 0.0091258 | 2.1728e-05 | 0
2013-09-02 | HGS22 | URBAN | Replace Overhead Assets | 1 | 255 | 255 | 0.00039576 | 1.552e-06 | 0
2013-09-02 | DN10 | URBAN | Regular Maintenance | 56 | 400 | 22400 | 0.034765 | 8.6913e-05 | 0
2013-09-02 | MTN34 | URBAN | Regular Maintenance | 25 | 80 | 2000 | 0.003104 | 3.88e-05 | 0
2013-09-03 | DN6 | URBAN | Regular Maintenance | 1 | 225 | 225 | 0.0003492 | 1.552e-06 | 0
2013-09-03 | HT1 | URBAN | Upgrade capacity - subs and LV | 67 | 280 | 18760 | 0.029116 | 0.00010398 | 0
2013-09-03 | BU14 | URBAN | Replace Overhead Assets | 71 | 285 | 20235 | 0.031405 | 0.00011019 | 0
2013-09-03 | DC2 | URBAN | Replace underground assets | 34 | 252 | 8568 | 0.013298 | 5.2768e-05 | 0
2013-09-03 | FSH22 | URBAN | Replace Overhead Assets | 41 | 335 | 13735 | 0.021317 | 6.3633e-05 | 0
2013-09-03 | EM2 | URBAN | Upgrade capacity - subs and LV | 101 | 480 | 48480 | 0.075242 | 0.00015675 | 0
2013-09-04 | GW2 | URBAN | Replace Overhead Assets | 8 | 220 | 1760 | 0.0027315 | 1.2416e-05 | 0
2013-09-04 | NP23 | RURAL SHORT | Regular Maintenance | 47 | 220 | 10340 | 0.016048 | 7.2945e-05 | 0
2013-09-04 | MGE33 | URBAN | Replace underground assets | 38 | 285 | 10830 | 0.016808 | 5.8977e-05 | 0
2013-09-04 | EM8 | URBAN | Replace Overhead Assets | 137 | 330 | 45210 | 0.070167 | 0.00021263 | 0
2013-09-04 | HGS32 | URBAN | Replace Overhead Assets | 1 | 350 | 350 | 0.0005432 | 1.552e-06 | 0
2013-09-04 | RWT16 | URBAN | Replace Overhead Assets | 60 | 330 | 19800 | 0.03073 | 9.3121e-05 | 0
2013-09-04 | EW14 | RURAL SHORT | Replace Overhead Assets | 26 | 405 | 10530 | 0.016343 | 4.0352e-05 | 0
2013-09-04 | RBD22 | URBAN | Replace Overhead Assets | 58 | 300 | 17400 | 0.027005 | 9.0017e-05 | 0
2013-09-04 | OAK21 | URBAN | Upgrade capacity - subs and LV | 34 | 345 | 11730 | 0.018205 | 5.2768e-05 | 0
2013-09-04 | FSH11 | URBAN | Regular Maintenance | 57 | 370 | 21090 | 0.032732 | 8.8465e-05 | 0
2013-09-04 | GW2 | URBAN | Replace Overhead Assets | 13 | 275 | 3575 | 0.0055485 | 2.0176e-05 | 0
2013-09-05 | FTN13 | URBAN | Replace Overhead Assets | 55 | 137 | 7535 | 0.011694 | 8.5361e-05 | 0
2013-09-05 | FSH33 | URBAN | Replace Overhead Assets | 64 | 255 | 16320 | 0.025329 | 9.9329e-05 | 0
2013-09-05 | DC3 | URBAN | Replace underground assets | 43 | 300 | 12900 | 0.020021 | 6.6737e-05 | 0
2013-09-05 | MGE32 | URBAN | Extended Electricity Supply | 9 | 120 | 1080 | 0.0016762 | 1.3968e-05 | 0
2013-09-05 | MC7 | URBAN | Regular Maintenance | 119 | 345 | 41055 | 0.063718 | 0.00018469 | 0
2013-09-05 | HGS23 | URBAN | Replace Overhead Assets | 1 | 360 | 360 | 0.00055873 | 1.552e-06 | 0
2013-09-05 | DC1 | URBAN | Replace Overhead Assets | 3 | 300 | 900 | 0.0013968 | 4.656e-06 | 0
2013-09-05 | RD4 | URBAN | Replace Overhead Assets | 79 | 285 | 22515 | 0.034944 | 0.00012261 | 0
2013-09-05 | WD34 | URBAN | Upgrade capacity - lines and ZSS | 23 | 540 | 12420 | 0.019276 | 3.5696e-05 | 0
2013-09-06 | NP23 | URBAN | Regular Maintenance | 31 | 77 | 2387 | 0.0037047 | 4.8112e-05 | 0
2013-09-06 | FSH11 | URBAN | Replace plant and equipment | 55 | 260 | 14300 | 0.022194 | 8.5361e-05 | 0
2013-09-06 | FSH32 | URBAN | Regular Maintenance | 16 | 290 | 4640 | 0.0072013 | 2.4832e-05 | 0
2013-09-06 | FTN13 | RURAL SHORT | Regular Maintenance | 14 | 240 | 3360 | 0.0052148 | 2.1728e-05 | 0
2013-09-06 | BW21 | URBAN |  | 149 | 345 | 51405 | 0.079781 | 0.00023125 | 0
2013-09-06 | DN7 | RURAL SHORT | Regular Maintenance | 3 | 450 | 1350 | 0.0020952 | 4.656e-06 | 0
2013-09-07 | SVW45 | URBAN | Upgrade capacity - subs and LV | 1 | 500 | 500 | 0.00077601 | 1.552e-06 | 0
2013-09-08 | SVW53 | URBAN | Replace Overhead Assets | 16 | 390 | 6240 | 0.0096846 | 2.4832e-05 | 0
2013-09-08 | NP24 | URBAN | Replace Overhead Assets | 14 | 268 | 3752 | 0.0058232 | 2.1728e-05 | 0
2013-09-08 | HT6 | URBAN | Replace Overhead Assets | 2 | 175 | 350 | 0.0005432 | 3.104e-06 | 0
2013-09-08 | SVW41 | URBAN | Replace Overhead Assets | 44 | 140 | 6160 | 0.0095604 | 6.8289e-05 | 0
2013-09-08 | HGS22 | URBAN | Replace underground assets | 51 | 405 | 20655 | 0.032057 | 7.9153e-05 | 0
2013-09-08 | RWT16 | URBAN | Replace Overhead Assets | 132 | 570 | 75240 | 0.11677 | 0.00020487 | 0
2013-09-09 | NB22 | URBAN | Replace Overhead Assets | 35 | 180 | 6300 | 0.0097777 | 5.432e-05 | 0
2013-09-09 | MC7 | URBAN | Regular Maintenance | 2 | 345 | 690 | 0.0010709 | 3.104e-06 | 0
2013-09-09 | NW23 | RURAL SHORT | Upgrade capacity - subs and LV | 1 | 330 | 330 | 0.00051216 | 1.552e-06 | 0
2013-09-09 | NW13 | URBAN | Replace underground assets | 8 | 350 | 2800 | 0.0043456 | 1.2416e-05 | 0
2013-09-09 | RBD21 | RURAL SHORT | Regular Maintenance | 7 | 493 | 3451 | 0.005356 | 1.0864e-05 | 0
2013-09-10 | FSH13 | URBAN | Regular Maintenance | 7 | 240 | 1680 | 0.0026074 | 1.0864e-05 | 0
2013-09-10 | NW31 | RURAL SHORT | Replace Overhead Assets | 3 | 335 | 1005 | 0.0015598 | 4.656e-06 | 0
2013-09-10 | EM5 | URBAN |  | 53 | 330 | 17490 | 0.027145 | 8.2257e-05 | 0
2013-09-10 | DC2 | URBAN | Replace underground assets | 17 | 350 | 5950 | 0.0092345 | 2.6384e-05 | 0
2013-09-10 | MTN32 | URBAN | Regular Maintenance | 21 | 420 | 8820 | 0.013689 | 3.2592e-05 | 0
2013-09-10 | BR6 | URBAN | Regular Maintenance | 26 | 435 | 11310 | 0.017553 | 4.0352e-05 | 0
2013-09-11 | EM7 | URBAN | Replace Overhead Assets | 138 | 0 | 0 | 0 | 0.00021418 | 0
2013-09-11 | NP23 | URBAN | Regular Maintenance | 22 | 170 | 3740 | 0.0058045 | 3.4144e-05 | 0
2013-09-11 | SR20 | RURAL SHORT | Replace Overhead Assets | 16 | 315 | 5040 | 0.0078222 | 2.4832e-05 | 0
2013-09-11 | DC3 | URBAN | Replace underground assets | 30 | 300 | 9000 | 0.013968 | 4.656e-05 | 0
2013-09-11 | BR10 | URBAN | Regular Maintenance | 12 | 240 | 2880 | 0.0044698 | 1.8624e-05 | 0
2013-09-11 | NW21 | URBAN | Replace Overhead Assets | 38 | 330 | 12540 | 0.019462 | 5.8977e-05 | 0
2013-09-11 | MTN35 | URBAN | Replace Overhead Assets | 8 | 360 | 2880 | 0.0044698 | 1.2416e-05 | 0
2013-09-11 | BC11 | RURAL SHORT |  | 141 | 330 | 46530 | 0.072215 | 0.00021883 | 0
2013-09-11 | MC2 | URBAN | Regular Maintenance | 1 | 180 | 180 | 0.00027936 | 1.552e-06 | 0
2013-09-12 | CRM22 | URBAN | Regular Maintenance | 38 | 180 | 6840 | 0.010616 | 5.8977e-05 | 0
2013-09-12 | MR32 | RURAL SHORT | Upgrade capacity - subs and LV | 1 | 240 | 240 | 0.00037248 | 1.552e-06 | 0
2013-09-12 | FSH13 | URBAN | Regular Maintenance | 8 | 185 | 1480 | 0.002297 | 1.2416e-05 | 0
2013-09-12 | OAK23 | URBAN | Replace Overhead Assets | 135 | 345 | 46575 | 0.072285 | 0.00020952 | 0
2013-09-12 | NW33 | URBAN | Replace Overhead Assets | 35 | 365 | 12775 | 0.019827 | 5.432e-05 | 0
2013-09-12 | K10 | URBAN | Replace Overhead Assets | 54 | 430 | 23220 | 0.036038 | 8.3809e-05 | 0
2013-09-12 | CRM35 | URBAN | Regular Maintenance | 32 | 605 | 19360 | 0.030047 | 4.9664e-05 | 0
2013-09-13 | CRM14 | URBAN | Replace Overhead Assets | 41 | 210 | 8610 | 0.013363 | 6.3633e-05 | 0
2013-09-13 | LWN31 | URBAN | Improving Reliability | 110 | 245 | 26950 | 0.041827 | 0.00017072 | 0
2013-09-13 | M35 | URBAN | Regular Maintenance | 63 | 350 | 22050 | 0.034222 | 9.7777e-05 | 0
2013-09-13 | DC3 | URBAN | Replace underground assets | 49 | 360 | 17640 | 0.027378 | 7.6049e-05 | 0
2013-09-13 | FSH33 | URBAN | Replace Overhead Assets | 78 | 435 | 33930 | 0.05266 | 0.00012106 | 0
2013-09-14 | RBD24 | URBAN | Regular Maintenance | 41 | 150 | 6150 | 0.0095449 | 6.3633e-05 | 0
2013-09-15 | EB22 | URBAN | Replace Overhead Assets | 153 | 315 | 48195 | 0.074799 | 0.00023746 | 0
2013-09-15 | FSH23 | URBAN | Replace Overhead Assets | 28 | 315 | 8820 | 0.013689 | 4.3456e-05 | 0
2013-09-15 | DN4 | URBAN | Regular Maintenance | 46 | 335 | 15410 | 0.023917 | 7.1393e-05 | 0
2013-09-15 | SS14 | URBAN | Replace plant and equipment | 10 | 455 | 4550 | 0.0070617 | 1.552e-05 | 0
2013-09-15 | BT9 | URBAN | Upgrade capacity - subs and LV | 90 | 480 | 43200 | 0.067047 | 0.00013968 | 0
2013-09-16 | EW14 | URBAN | Replace Overhead Assets | 52 | 180 | 9360 | 0.014527 | 8.0705e-05 | 0
2013-09-16 | LD5 | URBAN | Regular Maintenance | 38 | 190 | 7220 | 0.011206 | 5.8977e-05 | 0
2013-09-16 | MC6 | URBAN | Regular Maintenance | 26 | 265 | 6890 | 0.010693 | 4.0352e-05 | 0
2013-09-16 | MC1 | URBAN | Regular Maintenance | 50 | 310 | 15500 | 0.024056 | 7.7601e-05 | 0
2013-09-16 | MC6 | URBAN | Regular Maintenance | 19 | 317 | 6023 | 0.0093478 | 2.9488e-05 | 0
2013-09-16 | BR4 | URBAN |  | 46 | 364 | 16744 | 0.025987 | 7.1393e-05 | 0
2013-09-17 | EB22 | URBAN | Replace Overhead Assets | 6 | 120 | 720 | 0.0011175 | 9.3121e-06 | 0
2013-09-17 | RBD23 | URBAN |  | 84 | 195 | 16380 | 0.025422 | 0.00013037 | 0
2013-09-17 | DC3 | URBAN | Replace underground assets | 12 | 235 | 2820 | 0.0043767 | 1.8624e-05 | 0
2013-09-17 | MTN24 | URBAN | Regular Maintenance | 98 | 300 | 29400 | 0.045629 | 0.0001521 | 0
2013-09-17 | DMA13 | URBAN | Replace Overhead Assets | 4 | 100 | 400 | 0.00062081 | 6.2081e-06 | 0
2013-09-17 | DC3 | RURAL SHORT | Replace underground assets | 29 | 300 | 8700 | 0.013503 | 4.5008e-05 | 0
2013-09-17 | NW33 | URBAN | Upgrade capacity - subs and LV | 5 | 315 | 1575 | 0.0024444 | 7.7601e-06 | 0
2013-09-17 | DVY24 | URBAN | Regular Maintenance | 2 | 255 | 510 | 0.00079153 | 3.104e-06 | 0
2013-09-17 | GW12 | URBAN | Regular Maintenance | 26 | 415 | 10790 | 0.016746 | 4.0352e-05 | 0
2013-09-18 | HGS22 | URBAN | Replace Overhead Assets | 1 | 90 | 90 | 0.00013968 | 1.552e-06 | 0
2013-09-18 | DC3 | URBAN | Replace underground assets | 9 | 300 | 2700 | 0.0041904 | 1.3968e-05 | 0
2013-09-18 | HGS33 | URBAN | Replace Overhead Assets | 11 | 60 | 660 | 0.0010243 | 1.7072e-05 | 0
2013-09-18 | GW7 | URBAN | Replace Overhead Assets | 2 | 175 | 350 | 0.0005432 | 3.104e-06 | 0
2013-09-18 | BR15 | URBAN |  | 29 | 360 | 10440 | 0.016203 | 4.5008e-05 | 0
2013-09-19 | DSH33 | URBAN | Replace Overhead Assets | 2 | 65 | 130 | 0.00020176 | 3.104e-06 | 0
2013-09-19 | BH23 | RURAL SHORT | Upgrade capacity - subs and LV | 87 | 315 | 27405 | 0.042533 | 0.00013503 | 0
2013-09-19 | DC3 | URBAN | Replace underground assets | 22 | 320 | 7040 | 0.010926 | 3.4144e-05 | 0
2013-09-19 | FSH32 | URBAN | Upgrade capacity - subs and LV | 4 | 80 | 320 | 0.00049664 | 6.2081e-06 | 0
2013-09-19 | CDA22 | URBAN | Extended Electricity Supply | 7 | 420 | 2940 | 0.0045629 | 1.0864e-05 | 0
2013-09-19 | EM8 | URBAN | Replace Overhead Assets | 79 | 425 | 33575 | 0.052109 | 0.00012261 | 0
2013-09-20 | HGS33 | URBAN | Improving Reliability | 1 | 70 | 70 | 0.00010864 | 1.552e-06 | 0
2013-09-20 | FSH33 | URBAN | Replace Overhead Assets | 54 | 135 | 7290 | 0.011314 | 8.3809e-05 | 0
2013-09-20 | HGS23 | URBAN | Improving Reliability | 2 | 125 | 250 | 0.000388 | 3.104e-06 | 0
2013-09-20 | DC3 | URBAN | Replace underground assets | 18 | 325 | 5850 | 0.0090793 | 2.7936e-05 | 0
2013-09-20 | HGS22 | URBAN | Replace Overhead Assets | 12 | 315 | 3780 | 0.0058666 | 1.8624e-05 | 0
2013-09-20 | HGS33 | URBAN | Regular Maintenance | 3 | 410 | 1230 | 0.001909 | 4.656e-06 | 0
2013-09-22 | RWT16 | RURAL SHORT | Extended Electricity Supply | 1 | 300 | 300 | 0.0004656 | 1.552e-06 | 0
2013-09-22 | MGE22 | URBAN | Replace Overhead Assets | 185 | 420 | 77700 | 0.12059 | 0.00028712 | 0
2013-09-22 | SV23 | RURAL SHORT | Upgrade capacity - subs and LV | 10 | 660 | 6600 | 0.010243 | 1.552e-05 | 0
2013-09-22 | CFD22 | URBAN | Replace plant and equipment | 3 | 705 | 2115 | 0.0032825 | 4.656e-06 | 0
2013-09-23 | LD33 | URBAN | Replace Overhead Assets | 271 | 285 | 77235 | 0.11987 | 0.0004206 | 0
2013-09-23 | EL6 | URBAN | Replace Overhead Assets | 221 | 365 | 80665 | 0.12519 | 0.000343 | 0
2013-09-24 | BH11 | URBAN | Replace Overhead Assets | 77 | 255 | 19635 | 0.030474 | 0.00011951 | 0
2013-09-24 | DMA15 | RURAL SHORT | Replace Overhead Assets | 70 | 330 | 23100 | 0.035852 | 0.00010864 | 0
2013-09-24 | DC3 | URBAN | Replace underground assets | 13 | 305 | 3965 | 0.0061537 | 2.0176e-05 | 0
2013-09-24 | M33 | URBAN | Regular Maintenance | 37 | 390 | 14430 | 0.022396 | 5.7425e-05 | 0
2013-09-24 | NP31 | URBAN | Regular Maintenance | 9 | 340 | 3060 | 0.0047492 | 1.3968e-05 | 0
2013-09-24 | HGS22 | URBAN | Tree Clearing/Bushfire Mitigation | 45 | 475 | 21375 | 0.033174 | 6.9841e-05 | 0
2013-09-24 | FSH31 | RURAL SHORT | Replace Overhead Assets | 89 | 410 | 36490 | 0.056633 | 0.00013813 | 0
2013-09-25 | LD1 | RURAL SHORT | Regular Maintenance | 52 | 90 | 4680 | 0.0072634 | 8.0705e-05 | 0
2013-09-25 | NP33 | RURAL SHORT | Replace Overhead Assets | 10 | 165 | 1650 | 0.0025608 | 1.552e-05 | 0
2013-09-25 | K3 | URBAN | Replace Overhead Assets | 49 | 240 | 11760 | 0.018252 | 7.6049e-05 | 0
2013-09-25 | DC3 | RURAL SHORT | Replace underground assets | 8 | 295 | 2360 | 0.0036628 | 1.2416e-05 | 0
2013-09-25 | EL14 | URBAN | Replace Overhead Assets | 56 | 270 | 15120 | 0.023466 | 8.6913e-05 | 0
2013-09-25 | BR15 | RURAL SHORT | Regular Maintenance | 23 | 440 | 10120 | 0.015706 | 3.5696e-05 | 0
2013-09-25 | NW22 | RURAL SHORT | Replace Overhead Assets | 63 | 510 | 32130 | 0.049866 | 9.7777e-05 | 0
2013-09-26 | BR9 | URBAN | Regular Maintenance | 13 | 95 | 1235 | 0.0019167 | 2.0176e-05 | 0
2013-09-26 | FTN13 | RURAL SHORT | Replace Overhead Assets | 55 | 220 | 12100 | 0.018779 | 8.5361e-05 | 0
2013-09-26 | DC3 | URBAN | Replace underground assets | 15 | 255 | 3825 | 0.0059365 | 2.328e-05 | 0
2013-09-26 | MC3 | URBAN |  | 13 | 210 | 2730 | 0.004237 | 2.0176e-05 | 0
2013-09-26 | MTN21 | URBAN | Replace underground assets | 97 | 315 | 30555 | 0.047422 | 0.00015055 | 0
2013-09-26 | MTN24 | URBAN | Upgrade capacity - subs and LV | 267 | 375 | 100125 | 0.1554 | 0.00041439 | 0
2013-09-26 | NP24 | URBAN | Replace Overhead Assets | 12 | 335 | 4020 | 0.0062391 | 1.8624e-05 | 0
2013-09-26 | NW14 | URBAN | Upgrade capacity - subs and LV | 41 | 360 | 14760 | 0.022908 | 6.3633e-05 | 0
2013-09-26 | EL6 | URBAN | Replace Overhead Assets | 257 | 395 | 101515 | 0.15755 | 0.00039887 | 0
2013-09-26 | BR9 | URBAN | Regular Maintenance | 37 | 390 | 14430 | 0.022396 | 5.7425e-05 | 0
2013-09-27 | FTN25 | RURAL SHORT | Regular Maintenance | 2 | 120 | 240 | 0.00037248 | 3.104e-06 | 0
2013-09-27 | DC3 | URBAN | Replace underground assets | 13 | 255 | 3315 | 0.0051449 | 2.0176e-05 | 0
2013-09-27 | NW14 | URBAN |  | 6 | 150 | 900 | 0.0013968 | 9.3121e-06 | 0
2013-09-27 | BR15 | URBAN | Regular Maintenance | 33 | 405 | 13365 | 0.020743 | 5.1216e-05 | 0
2013-09-27 | HGS22 | RURAL SHORT | Regular Maintenance | 56 | 495 | 27720 | 0.043022 | 8.6913e-05 | 0
2013-09-27 | HGS33 | URBAN | Regular Maintenance | 1 | 330 | 330 | 0.00051216 | 1.552e-06 | 0
2013-09-29 | BW21 | URBAN | Replace Overhead Assets | 22 | 330 | 7260 | 0.011268 | 3.4144e-05 | 0
2013-09-29 | GW7 | RURAL SHORT | Replace Overhead Assets | 2 | 375 | 750 | 0.001164 | 3.104e-06 | 0
2013-09-29 | CRM35 | URBAN | Regular Maintenance | 54 | 360 | 19440 | 0.030171 | 8.3809e-05 | 0
2013-09-29 | MC6 | URBAN | Replace Overhead Assets | 38 | 465 | 17670 | 0.027424 | 5.8977e-05 | 0
2013-09-29 | MGE12 | URBAN | Regular Maintenance | 1 | 635 | 635 | 0.00098553 | 1.552e-06 | 0
2013-09-30 | EM8 | URBAN | Upgrade capacity - subs and LV | 37 | 360 | 13320 | 0.020673 | 5.7425e-05 | 0
2013-09-30 | BR13 | URBAN | Regular Maintenance | 12 | 280 | 3360 | 0.0052148 | 1.8624e-05 | 0
2013-09-30 | FSH12 | RURAL SHORT | Replace Overhead Assets | 136 | 450 | 61200 | 0.094983 | 0.00021107 | 0
2013-10-01 | EW14 | URBAN | Extended Electricity Supply | 248 | 0 | 0 | 0 | 0.0003851 | 0
2013-10-01 | DC3 | URBAN | Replace underground assets | 3 | 245 | 735 | 0.0011413 | 4.6584e-06 | 0
2013-10-01 | DC3 | URBAN | Replace underground assets | 10 | 270 | 2700 | 0.0041926 | 1.5528e-05 | 0
2013-10-01 | SH70 | URBAN | Replace Overhead Assets | 538 | 310 | 166780 | 0.25898 | 0.00083541 | 0
2013-10-01 | DC3 | RURAL SHORT | Replace underground assets | 13 | 360 | 4680 | 0.0072671 | 2.0186e-05 | 0
2013-10-02 | NW22 | URBAN | Replace Overhead Assets | 85 | 0 | 0 | 0 | 0.00013199 | 0
2013-10-02 | NB21 | URBAN | Replace Overhead Assets | 34 | 300 | 10200 | 0.015839 | 5.2795e-05 | 0
2013-10-02 | DC3 | URBAN | Replace underground assets | 49 | 320 | 15680 | 0.024348 | 7.6087e-05 | 0
2013-10-02 | K13 | URBAN | Replace Overhead Assets | 157 | 420 | 65940 | 0.10239 | 0.00024379 | 0
2013-10-03 | RBD23 | URBAN | Replace Overhead Assets | 20 | 180 | 3600 | 0.0055901 | 3.1056e-05 | 0
2013-10-03 | MTN24 | URBAN | Upgrade capacity - subs and LV | 2 | 345 | 690 | 0.0010714 | 3.1056e-06 | 0
2013-10-03 | DC3 | RURAL SHORT | Replace underground assets | 18 | 330 | 5940 | 0.0092237 | 2.795e-05 | 0
2013-10-03 | EM2 | URBAN | Replace Overhead Assets | 40 | 240 | 9600 | 0.014907 | 6.2112e-05 | 0
2013-10-04 | DC3 | URBAN | Replace underground assets | 6 | 307 | 1842 | 0.0028603 | 9.3168e-06 | 0
2013-10-04 | CRM34 | URBAN | Regular Maintenance | 2 | 360 | 720 | 0.001118 | 3.1056e-06 | 0
2013-10-05 | EL14 | URBAN | Replace Overhead Assets | 26 | 25 | 650 | 0.0010093 | 4.0373e-05 | 0
2013-10-05 | EL14 | URBAN | Replace Overhead Assets | 77 | 25 | 1925 | 0.0029891 | 0.00011957 | 0
2013-10-06 | DN9 | URBAN | Regular Maintenance | 31 | 150 | 4650 | 0.0072205 | 4.8137e-05 | 0
2013-10-06 | DN24 | RURAL SHORT | Regular Maintenance | 14 | 160 | 2240 | 0.0034783 | 2.1739e-05 | 0
2013-10-06 | HT9 | RURAL SHORT | Replace Overhead Assets | 22 | 390 | 8580 | 0.013323 | 3.4162e-05 | 0
2013-10-06 | LD5 | URBAN | Regular Maintenance | 1 | 476 | 476 | 0.00073914 | 1.5528e-06 | 0
2013-10-06 | CM15 | URBAN | Upgrade capacity - subs and LV | 8 | 365 | 2920 | 0.0045342 | 1.2422e-05 | 0
2013-10-06 | EM8 | URBAN | Replace Overhead Assets | 237 | 500 | 118500 | 0.18401 | 0.00036801 | 0
2013-10-06 | M23 | URBAN | Extended Electricity Supply | 3 | 420 | 1260 | 0.0019565 | 4.6584e-06 | 0
2013-10-06 | HT2 | URBAN | Upgrade capacity - subs and LV | 25 | 720 | 18000 | 0.02795 | 3.882e-05 | 0
2013-10-06 | HT9 | URBAN | Upgrade capacity - subs and LV | 8 | 660 | 5280 | 0.0081988 | 1.2422e-05 | 0
2013-10-07 | HGS23 | URBAN | Improving Reliability | 26 | 210 | 5460 | 0.0084783 | 4.0373e-05 | 0
2013-10-07 | DMA15 | URBAN | Replace underground assets | 24 | 250 | 6000 | 0.0093168 | 3.7267e-05 | 0
2013-10-07 | DC3 | URBAN | Replace underground assets | 26 | 180 | 4680 | 0.0072671 | 4.0373e-05 | 0
2013-10-07 | OAK22 | URBAN | Extended Electricity Supply | 60 | 395 | 23700 | 0.036801 | 9.3168e-05 | 0
2013-10-08 | MTN32 | URBAN | Regular Maintenance | 1 | 150 | 150 | 0.00023292 | 1.5528e-06 | 0
2013-10-08 | MTN31 | URBAN | Replace underground assets | 32 | 80 | 2560 | 0.0039752 | 4.969e-05 | 0
2013-10-08 | HGS22 | URBAN | Regular Maintenance | 21 | 185 | 3885 | 0.0060326 | 3.2609e-05 | 0
2013-10-08 | RBD21 | URBAN | Replace Overhead Assets | 135 | 330 | 44550 | 0.069177 | 0.00020963 | 0
2013-10-08 | CRM12 | URBAN | Regular Maintenance | 51 | 315 | 16065 | 0.024946 | 7.9193e-05 | 0
2013-10-08 | HGS22 | URBAN | Improving Reliability | 15 | 325 | 4875 | 0.0075699 | 2.3292e-05 | 0
2013-10-08 | MTN23 | URBAN | Replace underground assets | 65 | 260 | 16900 | 0.026242 | 0.00010093 | 0
2013-10-08 | DC3 | URBAN | Replace underground assets | 36 | 317 | 11412 | 0.017721 | 5.5901e-05 | 0
2013-10-08 | GW2 | URBAN | Upgrade capacity - subs and LV | 73 | 346 | 25258 | 0.039221 | 0.00011335 | 0
2013-10-08 | NP24 | URBAN | Regular Maintenance | 76 | 615 | 46740 | 0.072578 | 0.00011801 | 0
2013-10-09 | HGS23 | URBAN | Improving Reliability | 6 | 165 | 990 | 0.0015373 | 9.3168e-06 | 0
2013-10-09 | HGS23 | URBAN | Improving Reliability | 8 | 210 | 1680 | 0.0026087 | 1.2422e-05 | 0
2013-10-09 | LD3 | URBAN | Regular Maintenance | 13 | 220 | 2860 | 0.004441 | 2.0186e-05 | 0
2013-10-09 | DC3 | URBAN | Replace underground assets | 11 | 248 | 2728 | 0.0042361 | 1.7081e-05 | 0
2013-10-09 | M25 | URBAN | Regular Maintenance | 10 | 270 | 2700 | 0.0041926 | 1.5528e-05 | 0
2013-10-09 | CRM21 | URBAN | Regular Maintenance | 1 | 300 | 300 | 0.00046584 | 1.5528e-06 | 0
2013-10-09 | BR6 | URBAN | Regular Maintenance | 39 | 315 | 12285 | 0.019076 | 6.0559e-05 | 0
2013-10-09 | BH11 | URBAN | Replace Overhead Assets | 153 | 420 | 64260 | 0.099783 | 0.00023758 | 0
2013-10-09 | CRM21 | URBAN | Regular Maintenance | 5 | 240 | 1200 | 0.0018634 | 7.764e-06 | 0
2013-10-09 | LD3 | URBAN | Regular Maintenance | 95 | 120 | 11400 | 0.017702 | 0.00014752 | 0
2013-10-10 | NP24 | URBAN | Regular Maintenance | 20 | 165 | 3300 | 0.0051243 | 3.1056e-05 | 0
2013-10-10 | FSH13 | RURAL SHORT | Replace underground assets | 21 | 165 | 3465 | 0.0053805 | 3.2609e-05 | 0
2013-10-10 | NP25 | URBAN | Replace Overhead Assets | 29 | 240 | 6960 | 0.010808 | 4.5031e-05 | 0
2013-10-10 | LWN31 | URBAN | Replace Overhead Assets | 96 | 305 | 29280 | 0.045466 | 0.00014907 | 0
2013-10-10 | BH22 | URBAN | Replace Overhead Assets | 50 | 345 | 17250 | 0.026786 | 7.764e-05 | 0
2013-10-11 | GW2 | URBAN | Replace Overhead Assets | 15 | 265 | 3975 | 0.0061724 | 2.3292e-05 | 0
2013-10-11 | DC3 | URBAN | Replace underground assets | 9 | 265 | 2385 | 0.0037034 | 1.3975e-05 | 0
2013-10-11 | HGS23 | URBAN | Replace Overhead Assets | 82 | 280 | 22960 | 0.035652 | 0.00012733 | 0
2013-10-11 | SH70 | URBAN | Replace Overhead Assets | 12 | 330 | 3960 | 0.0061491 | 1.8634e-05 | 0
2013-10-11 | CRM21 | URBAN | Regular Maintenance | 10 | 420 | 4200 | 0.0065218 | 1.5528e-05 | 0
2013-10-11 | NP36 | URBAN | Regular Maintenance | 12 | 390 | 4680 | 0.0072671 | 1.8634e-05 | 0
2013-10-12 | BH21 | URBAN | Short Interruption | 60 | 30 | 1800 | 0.002795 | 9.3168e-05 | 0
2013-10-12 | DN21 | URBAN | Regular Maintenance | 4 | 147 | 588 | 0.00091305 | 6.2112e-06 | 0
2013-10-13 | NP36 | URBAN | Regular Maintenance | 2 | 140 | 280 | 0.00043479 | 3.1056e-06 | 0
2013-10-13 | HGS32 | URBAN | Replace Overhead Assets | 15 | 300 | 4500 | 0.0069876 | 2.3292e-05 | 0
2013-10-13 | NP25 | URBAN | Regular Maintenance | 25 | 230 | 5750 | 0.0089286 | 3.882e-05 | 0
2013-10-13 | OR12 | URBAN | Replace Overhead Assets | 5 | 390 | 1950 | 0.003028 | 7.764e-06 | 0
2013-10-13 | CFD12 | URBAN | Upgrade capacity - subs and LV | 141 | 450 | 63450 | 0.098525 | 0.00021895 | 0
2013-10-13 | MC3 | URBAN | Regular Maintenance | 14 | 390 | 5460 | 0.0084783 | 2.1739e-05 | 0
2013-10-13 | RWT24 | URBAN | Replace Overhead Assets | 14 | 535 | 7490 | 0.011631 | 2.1739e-05 | 0
2013-10-13 | M33 | URBAN | Regular Maintenance | 28 | 465 | 13020 | 0.020218 | 4.3479e-05 | 0
2013-10-13 | GW10 | URBAN | Improving Reliability | 28 | 570 | 15960 | 0.024783 | 4.3479e-05 | 0
2013-10-14 | DMA12 | URBAN | Replace Overhead Assets | 33 | 170 | 5610 | 0.0087112 | 5.1243e-05 | 0
2013-10-15 | LWN32 | URBAN | Regular Maintenance | 64 | 120 | 7680 | 0.011926 | 9.9379e-05 | 0
2013-10-15 | HGS22 | RURAL SHORT | Replace Overhead Assets | 62 | 260 | 16120 | 0.025031 | 9.6274e-05 | 0
2013-10-15 | MC3 | URBAN | Regular Maintenance | 12 | 270 | 3240 | 0.0050311 | 1.8634e-05 | 0
2013-10-15 | DC5 | RURAL SHORT | Upgrade capacity - subs and LV | 220 | 330 | 72600 | 0.11273 | 0.00034162 | 0
2013-10-15 | DC3 | URBAN | Replace underground assets | 17 | 295 | 5015 | 0.0077873 | 2.6398e-05 | 0
2013-10-15 | NP36 | RURAL SHORT | Replace Overhead Assets | 27 | 330 | 8910 | 0.013835 | 4.1926e-05 | 0
2013-10-15 | DC3 | URBAN | Replace underground assets | 22 | 330 | 7260 | 0.011273 | 3.4162e-05 | 0
2013-10-15 | NP11 | URBAN | Regular Maintenance | 31 | 315 | 9765 | 0.015163 | 4.8137e-05 | 0
2013-10-15 | RBD12 | URBAN | Improving Reliability | 56 | 345 | 19320 | 0.03 | 8.6957e-05 | 0
2013-10-15 | K13 | RURAL SHORT | Replace Overhead Assets | 100 | 450 | 45000 | 0.069876 | 0.00015528 | 0
2013-10-16 | DVY24 | URBAN | Regular Maintenance | 2 | 40 | 80 | 0.00012422 | 3.1056e-06 | 0
2013-10-16 | FTN13 | URBAN | Regular Maintenance | 113 | 135 | 15255 | 0.023688 | 0.00017547 | 0
2013-10-16 | RBD21 | URBAN | Replace Overhead Assets | 18 | 165 | 2970 | 0.0046118 | 2.795e-05 | 0
2013-10-16 | DC3 | URBAN | Replace underground assets | 30 | 295 | 8850 | 0.013742 | 4.6584e-05 | 0
2013-10-16 | MTN35 | URBAN | Regular Maintenance | 2 | 225 | 450 | 0.00069876 | 3.1056e-06 | 0
2013-10-16 | LD33 | URBAN | Replace Overhead Assets | 128 | 470 | 60160 | 0.093417 | 0.00019876 | 0
2013-10-16 | GW4 | URBAN | Replace plant and equipment | 1 | 480 | 480 | 0.00074535 | 1.5528e-06 | 0
2013-10-17 | DC5 | URBAN | Upgrade capacity - subs and LV | 133 | 285 | 37905 | 0.058859 | 0.00020652 | 0
2013-10-17 | DC10 | RURAL SHORT | Replace underground assets | 16 | 300 | 4800 | 0.0074535 | 2.4845e-05 | 0
2013-10-17 | EB12 | URBAN | Replace Overhead Assets | 59 | 335 | 19765 | 0.030691 | 9.1615e-05 | 0
2013-10-17 | DC3 | URBAN | Replace underground assets | 39 | 297 | 11583 | 0.017986 | 6.0559e-05 | 0
2013-10-17 | HGS22 | URBAN | Improving Reliability | 82 | 370 | 30340 | 0.047112 | 0.00012733 | 0
2013-10-18 | DMA13 | URBAN | Extended Electricity Supply | 6 | 190 | 1140 | 0.0017702 | 9.3168e-06 | 0
2013-10-18 | NP25 | URBAN | Replace Overhead Assets | 1 | 150 | 150 | 0.00023292 | 1.5528e-06 | 0
2013-10-18 | DMA13 | URBAN | Replace Overhead Assets | 12 | 230 | 2760 | 0.0042857 | 1.8634e-05 | 0
2013-10-18 | NP36 | URBAN | Regular Maintenance | 25 | 300 | 7500 | 0.011646 | 3.882e-05 | 0
2013-10-18 | DC3 | RURAL SHORT | Replace underground assets | 8 | 243 | 1944 | 0.0030187 | 1.2422e-05 | 0
2013-10-18 | NP14 | RURAL SHORT | Regular Maintenance | 7 | 165 | 1155 | 0.0017935 | 1.087e-05 | 0
2013-10-19 | NP36 | URBAN | Replace Overhead Assets | 74 | 400 | 29600 | 0.045963 | 0.00011491 | 0
2013-10-20 | OAK23 | URBAN | Replace Overhead Assets | 34 | 270 | 9180 | 0.014255 | 5.2795e-05 | 0
2013-10-20 | SVW42 | URBAN |  | 203 | 420 | 85260 | 0.13239 | 0.00031522 | 0
2013-10-20 | OAK21 | RURAL SHORT | Upgrade capacity - subs and LV | 54 | 420 | 22680 | 0.035218 | 8.3851e-05 | 0
2013-10-20 | NP36 | URBAN | Regular Maintenance | 27 | 488 | 13176 | 0.02046 | 4.1926e-05 | 0
2013-10-20 | GW10 | RURAL SHORT | Improving Reliability | 38 | 240 | 9120 | 0.014162 | 5.9007e-05 | 0
2013-10-21 | NP23 | URBAN | Regular Maintenance | 72 | 120 | 8640 | 0.013416 | 0.0001118 | 0
2013-10-21 | NP36 | URBAN | Replace Overhead Assets | 10 | 205 | 2050 | 0.0031832 | 1.5528e-05 | 0
2013-10-21 | HGS22 | RURAL SHORT | Replace Overhead Assets | 57 | 285 | 16245 | 0.025225 | 8.851e-05 | 0
2013-10-21 | K2 | RURAL SHORT | Replace plant and equipment | 10 | 485 | 4850 | 0.0075311 | 1.5528e-05 | 0
2013-10-22 | DMA13 | URBAN | Improving Reliability | 4 | 180 | 720 | 0.001118 | 6.2112e-06 | 0
2013-10-22 | NB21 | URBAN | Replace Overhead Assets | 35 | 180 | 6300 | 0.0097827 | 5.4348e-05 | 0
2013-10-22 | HGS22 | URBAN | Improving Reliability | 6 | 255 | 1530 | 0.0023758 | 9.3168e-06 | 0
2013-10-22 | DN6 | URBAN | Regular Maintenance | 66 | 280 | 18480 | 0.028696 | 0.00010249 | 0
2013-10-22 | DMA13 | URBAN | Improving Reliability | 2 | 180 | 360 | 0.00055901 | 3.1056e-06 | 0
2013-10-22 | HGS22 | URBAN | Replace Overhead Assets | 9 | 180 | 1620 | 0.0025155 | 1.3975e-05 | 0
2013-10-22 | HGS22 | RURAL SHORT | Replace Overhead Assets | 1 | 150 | 150 | 0.00023292 | 1.5528e-06 | 0
2013-10-22 | HGS22 | URBAN | Regular Maintenance | 54 | 47.35 | 2556.9 | 0.0039704 | 8.3851e-05 | 0
2013-10-22 | DC1 | URBAN | Replace underground assets | 15 | 360 | 5400 | 0.0083851 | 2.3292e-05 | 0
2013-10-22 | SH81 | URBAN | Replace Overhead Assets | 22 | 390 | 8580 | 0.013323 | 3.4162e-05 | 0
2013-10-22 | FSH34 | RURAL SHORT | Regular Maintenance | 55 | 451 | 24805 | 0.038517 | 8.5404e-05 | 0
2013-10-23 | DC1 | URBAN | Replace underground assets | 32 | 80 | 2560 | 0.0039752 | 4.969e-05 | 0
2013-10-23 | BT9 | URBAN | Replace Overhead Assets | 66 | 210 | 13860 | 0.021522 | 0.00010249 | 0
2013-10-23 | MTN31 | URBAN | Replace underground assets | 43 | 345 | 14835 | 0.023036 | 6.6771e-05 | 0
2013-10-23 | NW21 | RURAL SHORT | Tree Clearing - Urban | 196 | 360 | 70560 | 0.10957 | 0.00030435 | 0
2013-10-23 | MTN32 | URBAN | Improving Reliability | 59 | 405 | 23895 | 0.037104 | 9.1615e-05 | 0
2013-10-24 | CRM21 | RURAL SHORT | Regular Maintenance | 5 | 115 | 575 | 0.00089286 | 7.764e-06 | 0
2013-10-24 | M11 | URBAN | Regular Maintenance | 2 | 150 | 300 | 0.00046584 | 3.1056e-06 | 0
2013-10-24 | MTN23 | RURAL SHORT | Replace underground assets | 50 | 329.95 | 16497.5 | 0.025617 | 7.764e-05 | 0
2013-10-24 | NP16 | RURAL SHORT | Regular Maintenance | 51 | 235 | 11985 | 0.01861 | 7.9193e-05 | 0
2013-10-25 | RBD21 | URBAN | Replace Overhead Assets | 63 | 185 | 11655 | 0.018098 | 9.7827e-05 | 0
2013-10-25 | EM8 | URBAN | Replace Overhead Assets | 36 | 180 | 6480 | 0.010062 | 5.5901e-05 | 0
2013-10-25 | EB22 | URBAN | Replace Overhead Assets | 77 | 285 | 21945 | 0.034076 | 0.00011957 | 0
2013-10-25 | DC1 | URBAN | Replace underground assets | 18 | 325 | 5850 | 0.0090839 | 2.795e-05 | 0
2013-10-25 | MTN31 | URBAN | Replace underground assets | 45 | 335 | 15075 | 0.023409 | 6.9876e-05 | 0
2013-10-25 | MGE24 | URBAN | Replace Overhead Assets | 26 | 360 | 9360 | 0.014534 | 4.0373e-05 | 0
2013-10-25 | MTN35 | URBAN | Replace Overhead Assets | 9 | 170 | 1530 | 0.0023758 | 1.3975e-05 | 0
2013-10-25 | CFD23 | URBAN | Extended Electricity Supply | 82 | 343 | 28126 | 0.043674 | 0.00012733 | 0
2013-10-26 | MTN35 | URBAN | Replace Overhead Assets | 25 | 185 | 4625 | 0.0071817 | 3.882e-05 | 0
2013-10-26 | MC10 | URBAN | Regular Maintenance | 1 | 270 | 270 | 0.00041926 | 1.5528e-06 | 0
2013-10-26 | DC3 | URBAN | Replace underground assets | 11 | 360 | 3960 | 0.0061491 | 1.7081e-05 | 0
2013-10-26 | NW22 | URBAN | Tree Clearing - Urban | 1 | 465 | 465 | 0.00072205 | 1.5528e-06 | 0
2013-10-27 | DVY14 | URBAN | Extended Electricity Supply | 12 | 180 | 2160 | 0.0033541 | 1.8634e-05 | 0
2013-10-27 | DN2 | URBAN | Replace Overhead Assets | 11 | 100 | 1100 | 0.0017081 | 1.7081e-05 | 0
2013-10-27 | DSH33 | URBAN |  | 1 | 435 | 435 | 0.00067547 | 1.5528e-06 | 0
2013-10-27 | RWT24 | URBAN | Replace Overhead Assets | 16 | 495 | 7920 | 0.012298 | 2.4845e-05 | 0
2013-10-27 | DSH32 | URBAN | Extended Electricity Supply | 5 | 540 | 2700 | 0.0041926 | 7.764e-06 | 0
2013-10-27 | DN8 | URBAN | Replace Overhead Assets | 4 | 185 | 740 | 0.0011491 | 6.2112e-06 | 0
2013-10-27 | FTN12 | URBAN | Regular Maintenance | 38 | 690 | 26220 | 0.040715 | 5.9007e-05 | 0
2013-10-28 | EW14 | URBAN | Extended Electricity Supply | 189 | 60 | 11340 | 0.017609 | 0.00029348 | 0
2013-10-28 | MTN24 | URBAN | Replace underground assets | 48 | 240 | 11520 | 0.017888 | 7.4535e-05 | 0
2013-10-28 | DMA13 | URBAN | Replace Overhead Assets | 1 | 150 | 150 | 0.00023292 | 1.5528e-06 | 0
2013-10-28 | EW14 | URBAN | Short Interruption | 189 | 60 | 11340 | 0.017609 | 0.00029348 | 0
2013-10-28 | HGS22 | URBAN | Replace Overhead Assets | 90 | 695 | 62550 | 0.097128 | 0.00013975 | 0
2013-10-29 | FSH23 | URBAN | Replace Overhead Assets | 2 | 120 | 240 | 0.00037267 | 3.1056e-06 | 0
2013-10-29 | BW33 | RURAL SHORT | Replace Overhead Assets | 42 | 120 | 5040 | 0.0078261 | 6.5218e-05 | 0
2013-10-29 | DMA13 | RURAL SHORT | Improving Reliability | 3 | 150 | 450 | 0.00069876 | 4.6584e-06 | 0
2013-10-29 | EB13 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 1920 | 0.0029814 | 0 | 0
2013-10-29 | DVY34 | URBAN | Regular Maintenance | 1 | 40 | 40 | 6.2112e-05 | 1.5528e-06 | 0
2013-10-29 | FSH23 | URBAN | Replace Overhead Assets | 1 | 210 | 210 | 0.00032609 | 1.5528e-06 | 0
2013-10-29 | DC1 | URBAN | Replace underground assets | 13 | 292 | 3796 | 0.0058944 | 2.0186e-05 | 0
2013-10-29 | FSH23 | URBAN | Replace Overhead Assets | 2 | 150 | 300 | 0.00046584 | 3.1056e-06 | 0
2013-10-29 | DVY34 | URBAN | Regular Maintenance | 9 | 255 | 2295 | 0.0035637 | 1.3975e-05 | 0
2013-10-29 | DMA13 | URBAN | Improving Reliability | 1 | 140 | 140 | 0.00021739 | 1.5528e-06 | 0
2013-10-29 | HGS33 | URBAN | Replace Overhead Assets | 3 | 345 | 1035 | 0.0016072 | 4.6584e-06 | 0
2013-10-29 | RBD12 | URBAN | Improving Reliability | 18 | 360 | 6480 | 0.010062 | 2.795e-05 | 0
2013-10-29 | MGE34 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 3360 | 0.0052174 | 0 | 0
2013-10-29 | FSH23 | URBAN | Replace Overhead Assets | 2 | 135 | 270 | 0.00041926 | 3.1056e-06 | 0
2013-10-30 | DSH33 | URBAN | Regular Maintenance | 1 | 270 | 270 | 0.00041926 | 1.5528e-06 | 0
2013-10-30 | MTN22 | URBAN | Improving Reliability | 2 | 255 | 510 | 0.00079193 | 3.1056e-06 | 0
2013-10-30 | M11 | URBAN | Replace Overhead Assets | 39 | 255 | 9945 | 0.015443 | 6.0559e-05 | 0
2013-10-30 | EW14 | URBAN | Replace Overhead Assets | 40 | 165 | 6600 | 0.010249 | 6.2112e-05 | 0
2013-10-31 | SH70 | URBAN | Replace Overhead Assets | 538 | 0 | 0 | 0 | 0.00083541 | 0
2013-10-31 | DMA13 | URBAN | Improving Reliability | 99 | 285 | 28215 | 0.043812 | 0.00015373 | 0
2013-10-31 | HGS33 | URBAN | Replace Overhead Assets | 8 | 270 | 2160 | 0.0033541 | 1.2422e-05 | 0
2013-10-31 | HGS32 | URBAN | Road Works Council | 29 | 315 | 9135 | 0.014185 | 4.5031e-05 | 0
2013-11-01 | EM10 | URBAN | Replace Overhead Assets | 40 | 165 | 6600 | 0.010267 | 6.2222e-05 | 0
2013-11-01 | K4 | URBAN | Replace Overhead Assets | 42 | 245 | 10290 | 0.016007 | 6.5333e-05 | 0
2013-11-01 | RD10 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 10620 | 0.01652 | 0 | 0
2013-11-01 | DC1 | URBAN | Replace underground assets | 16 | 345 | 5520 | 0.0085866 | 2.4889e-05 | 0
2013-11-01 | HGS31 | URBAN | Improving Reliability | 133 | 405 | 53865 | 0.083789 | 0.00020689 | 0
2013-11-01 | DVY24 | URBAN | Regular Maintenance | 7 | 305 | 2135 | 0.0033211 | 1.0889e-05 | 0
2013-11-03 | NP36 | URBAN | Extended Electricity Supply | 87 | 280 | 24360 | 0.037893 | 0.00013533 | 0
2013-11-03 | K7 | URBAN | Upgrade capacity - subs and LV | 97 | 430 | 41710 | 0.064882 | 0.00015089 | 0
2013-11-06 | K10 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 23250 | 0.036166 | 0 | 0
2013-11-06 | DC3 | URBAN | Replace underground assets | 0 | #DIV/0! | 10440 | 0.01624 | 0 | 0
2013-11-06 | SV16 | URBAN | Replace plant and equipment | 0 | #DIV/0! | 600 | 0.00093333 | 0 | 0
2013-11-06 | HGS32 | URBAN | Replace underground assets | 0 | #DIV/0! | 20235 | 0.031476 | 0 | 0
2013-11-06 | HGS22 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 9620 | 0.014964 | 0 | 0
2013-11-06 | HGS33 | URBAN | Extended Electricity Supply | 3 | 355 | 1065 | 0.0016567 | 4.6666e-06 | 0
2013-11-06 | GW5 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 64350 | 0.1001 | 0 | 0
2013-11-06 | MTN32 | URBAN | Tree Clearing/Bushfire Mitigation | 123 | 415 | 51045 | 0.079403 | 0.00019133 | 0
2013-11-06 | RBD12 | URBAN | Replace Overhead Assets | 0 | #DIV/0! | 140 | 0.00021778 | 0 | 0
2013-11-06 | NP23 | URBAN | Regular Maintenance | 20 | 570 | 11400 | 0.017733 | 3.1111e-05 | 0
2013-11-07 | GW2 | URBAN | Replace Overhead Assets | 61 | 120 | 7320 | 0.011387 | 9.4888e-05 | 0
2013-11-07 | MGE21 | URBAN | Replace underground assets | 19 | 185 | 3515 | 0.0054677 | 2.9555e-05 | 0
2013-11-07 | DC3 | URBAN | Replace underground assets | 31 | 250 | 7750 | 0.012055 | 4.8222e-05 | 0
2013-11-07 | NW13 | URBAN | Tree Clearing - Urban | 16 | 255 | 4080 | 0.0063466 | 2.4889e-05 | 0
2013-11-07 | CDA11 | URBAN | Replace Overhead Assets | 41 | 260 | 10660 | 0.016582 | 6.3777e-05 | 0
2013-11-07 | GW4 | URBAN | Replace Overhead Assets | 52 | 105 | 5460 | 0.0084933 | 8.0888e-05 | 0
2013-11-07 | RBD22 | URBAN | Replace Overhead Assets | 51 | 380 | 19380 | 0.030146 | 7.9333e-05 | 0
2013-11-07 | CRM35 | URBAN | Regular Maintenance | 134 | 457 | 61238 | 0.095258 | 0.00020844 | 0
2013-11-07 | HT11 | URBAN | Regular Maintenance | 60 | 465 | 27900 | 0.0434 | 9.3333e-05 | 0
2013-11-08 | DC2 | URBAN | Replace Overhead Assets | 137 | 85 | 11645 | 0.018114 | 0.00021311 | 0
2013-11-08 | MGE13 | URBAN | Replace plant and equipment | 234 | 145 | 33930 | 0.05278 | 0.000364 | 0
2013-11-08 | DMA13 | URBAN | Replace Overhead Assets | 105 | 255 | 26775 | 0.04165 | 0.00016333 | 0
2013-11-08 | CFD15 | URBAN | Replace Overhead Assets | 91 | 240 | 21840 | 0.033973 | 0.00014155 | 0
2013-11-08 | DC3 | URBAN | Replace underground assets | 30 | 275 | 8250 | 0.012833 | 4.6666e-05 | 0
2013-11-08 | M35 | URBAN | Regular Maintenance | 99 | 450 | 44550 | 0.069299 | 0.000154 | 0
2013-11-09 | DVY21 | URBAN | Regular Maintenance | 1 | 257 | 257 | 0.00039977 | 1.5555e-06 | 0
2013-11-09 | DVY24 | URBAN | Regular Maintenance | 19 | 315 | 5985 | 0.0093099 | 2.9555e-05 | 0
2013-11-10 | BC6 | URBAN | Replace underground assets | 1 | 330 | 330 | 0.00051333 | 1.5555e-06 | 0
2013-11-10 | DSH21 | RURAL SHORT | Extended Electricity Supply | 2 | 375 | 750 | 0.0011667 | 3.1111e-06 | 0
2013-11-10 | FTN24 | URBAN | Regular Maintenance | 9 | 445 | 4005 | 0.00623 | 1.4e-05 | 0
2013-11-10 | FTN11 | URBAN | Extended Electricity Supply | 15 | 360 | 5400 | 0.0083999 | 2.3333e-05 | 0
2013-11-10 | LD7 | URBAN | Extended Electricity Supply | 133 | 440 | 58520 | 0.09103 | 0.00020689 | 0
2013-11-10 | EM10 | URBAN | Upgrade capacity - subs and LV | 102 | 465 | 47430 | 0.073779 | 0.00015867 | 0
2013-11-10 | M21 | URBAN | Regular Maintenance | 9 | 570 | 5130 | 0.0079799 | 1.4e-05 | 0
2013-11-10 | HT9 | RURAL SHORT | Extended Electricity Supply | 2 | 540 | 1080 | 0.00168 | 3.1111e-06 | 0
2013-11-11 | EB12 | URBAN | Replace Overhead Assets | 58 | 180 | 10440 | 0.01624 | 9.0222e-05 | 0
2013-11-11 | RBD22 | URBAN | Replace Overhead Assets | 29 | 280 | 8120 | 0.012631 | 4.5111e-05 | 0
2013-11-11 | EM8 | URBAN | Upgrade capacity - subs and LV | 71 | 330 | 23430 | 0.036446 | 0.00011044 | 0
2013-11-11 | GW4 | URBAN | Replace Overhead Assets | 41 | 450 | 18450 | 0.0287 | 6.3777e-05 | 0
2013-11-12 | DC3 | URBAN | Replace underground assets | 25 | 280 | 7000 | 0.010889 | 3.8889e-05 | 0
2013-11-13 | RBD22 | URBAN | Replace Overhead Assets | 176 | 70 | 12320 | 0.019164 | 0.00027378 | 0
2013-11-13 | K2 | URBAN | Replace plant and equipment | 10 | 540 | 5400 | 0.0083999 | 1.5555e-05 | 0
2013-11-14 | NP25 | URBAN | Replace Overhead Assets | 36 | 120 | 4320 | 0.0067199 | 5.6e-05 | 0
2013-11-14 | FSH32 | URBAN | Road Works - VicRoads | 140 | 309 | 43260 | 0.067293 | 0.00021778 | 0
2013-11-14 | SH70 | URBAN | Replace Overhead Assets | 497 | 510 | 253470 | 0.39428 | 0.00077311 | 0
2013-11-15 | NP36 | URBAN | Replace Overhead Assets | 22 | 180 | 3960 | 0.00616 | 3.4222e-05 | 0
2013-11-15 | HGS23 | URBAN | Replace Overhead Assets | 40 | 190 | 7600 | 0.011822 | 6.2222e-05 | 0
2013-11-15 | OE4 | URBAN | Replace Overhead Assets | 34 | 270 | 9180 | 0.01428 | 5.2888e-05 | 0
2013-11-15 | NW23 | URBAN | Replace Overhead Assets | 64 | 360 | 23040 | 0.03584 | 9.9555e-05 | 0
2013-11-16 | GW2 | URBAN | Tree Clearing/Bushfire Mitigation | 15 | 300 | 4500 | 0.0069999 | 2.3333e-05 | 0
2013-11-16 | MGE31 | URBAN | Tree Clearing - Urban | 50 | 110 | 5500 | 0.0085555 | 7.7777e-05 | 0
2013-11-17 | MGE32 | URBAN | Regular Maintenance | 23 | 180 | 4140 | 0.00644 | 3.5778e-05 | 0
2013-11-17 | MGE32 | RURAL SHORT | Regular Maintenance | 7 | 360 | 2520 | 0.00392 | 1.0889e-05 | 0
2013-11-17 | NP11 | URBAN | Replace Overhead Assets | 75 | 270 | 20250 | 0.0315 | 0.00011667 | 0
2013-11-17 | DN4 | URBAN | Upgrade capacity - subs and LV | 1 | 300 | 300 | 0.00046666 | 1.5555e-06 | 0
2013-11-18 | DC2 | URBAN | Replace underground assets | 6 | 180 | 1080 | 0.00168 | 9.3333e-06 | 0
2013-11-18 | BT6 | URBAN | Replace Overhead Assets | 87 | 270 | 23490 | 0.03654 | 0.00013533 | 0
2013-11-18 | RD4 | RURAL SHORT | Replace Overhead Assets | 174 | 270 | 46980 | 0.073079 | 0.00027066 | 0
2013-11-18 | HGS23 | URBAN | Replace Overhead Assets | 2 | 260 | 520 | 0.00080888 | 3.1111e-06 | 0
2013-11-18 | M32 | URBAN | Replace Overhead Assets | 57 | 210 | 11970 | 0.01862 | 8.8666e-05 | 0
2013-11-18 | BC23 | URBAN | Replace Overhead Assets | 32 | 300 | 9600 | 0.014933 | 4.9777e-05 | 0
2013-11-18 | DMA13 | URBAN | Replace Overhead Assets | 4 | 80 | 320 | 0.00049777 | 6.2222e-06 | 0
2013-11-18 | NP23 | URBAN | Regular Maintenance | 80 | 485 | 38800 | 0.060355 | 0.00012444 | 0
2013-11-19 | DMA12 | URBAN | Replace Overhead Assets | 40 | 225 | 9000 | 0.014 | 6.2222e-05 | 0
2013-11-19 | MR13 | URBAN | Replace Overhead Assets | 56 | 180 | 10080 | 0.01568 | 8.711e-05 | 0
2013-11-19 | LD5 | URBAN | Replace Overhead Assets | 3 | 200 | 600 | 0.00093333 | 4.6666e-06 | 0
2013-11-19 | CRM14 | URBAN | Replace Overhead Assets | 7 | 205 | 1435 | 0.0022322 | 1.0889e-05 | 0
2013-11-19 | EM2 | URBAN | Replace Overhead Assets | 19 | 270 | 5130 | 0.0079799 | 2.9555e-05 | 0
2013-11-19 | HGS22 | URBAN | Replace Overhead Assets | 82 | 365 | 29930 | 0.046557 | 0.00012755 | 0
2013-11-19 | NW31 | URBAN | Replace Overhead Assets | 61 | 360 | 21960 | 0.03416 | 9.4888e-05 | 0
2013-11-19 | DC1 | URBAN | Replace underground assets | 20 | 345 | 6900 | 0.010733 | 3.1111e-05 | 0
2013-11-19 | K13 | URBAN | Replace Overhead Assets | 156 | 405 | 63180 | 0.098279 | 0.00024266 | 0
2013-11-19 | CRM35 | URBAN | Replace Overhead Assets | 36 | 525 | 18900 | 0.0294 | 5.6e-05 | 0
2013-11-20 | BU14 | URBAN | Replace underground assets | 2 | 75 | 150 | 0.00023333 | 3.1111e-06 | 0
2013-11-20 | RBD22 | URBAN | Replace Overhead Assets | 428 | 135 | 57780 | 0.089879 | 0.00066577 | 0
2013-11-20 | RBD14 | URBAN | Replace Overhead Assets | 35 | 135 | 4725 | 0.0073499 | 5.4444e-05 | 0
2013-11-20 | RBD23 | URBAN | Replace Overhead Assets | 36 | 150 | 5400 | 0.0083999 | 5.6e-05 | 0
2013-11-20 | GW4 | URBAN | Replace Overhead Assets | 114 | 270 | 30780 | 0.04788 | 0.00017733 | 0
2013-11-20 | DC1 | URBAN | Replace underground assets | 8 | 90 | 720 | 0.00112 | 1.2444e-05 | 0
2013-11-20 | NP12 | URBAN | Replace Overhead Assets | 72 | 245 | 17640 | 0.02744 | 0.000112 | 0
2013-11-20 | DC3 | URBAN | Replace underground assets | 37 | 330 | 12210 | 0.018993 | 5.7555e-05 | 0
2013-11-20 | MTN31 | URBAN | Replace underground assets | 135 | 375 | 50625 | 0.078749 | 0.00021 | 0
2013-11-21 | DC3 | URBAN |  | 14 | 90 | 1260 | 0.00196 | 2.1778e-05 | 0
2013-11-21 | OAK22 | RURAL SHORT | Replace Overhead Assets | 98 | 150 | 14700 | 0.022866 | 0.00015244 | 0
2013-11-21 | RBD13 | RURAL SHORT | Replace Overhead Assets | 1 | 205 | 205 | 0.00031889 | 1.5555e-06 | 0
2013-11-21 | DMA13 | URBAN | Replace Overhead Assets | 4 | 120 | 480 | 0.00074666 | 6.2222e-06 | 0
2013-11-21 | GW12 | URBAN | Replace Overhead Assets | 53 | 340 | 18020 | 0.028031 | 8.2444e-05 | 0
2013-11-21 | RBD22 | URBAN | Replace Overhead Assets | 141 | 345 | 48645 | 0.075669 | 0.00021933 | 0
2013-11-21 | LWN31 | URBAN | Replace Overhead Assets | 9 | 285 | 2565 | 0.00399 | 1.4e-05 | 0
2013-11-21 | DC5 | URBAN | Replace Overhead Assets | 30 | 415 | 12450 | 0.019367 | 4.6666e-05 | 0
2013-11-21 | DC3 | URBAN | Replace underground assets | 55 | 450 | 24750 | 0.0385 | 8.5555e-05 | 0
2013-11-21 | K13 | URBAN | Replace Overhead Assets | 48 | 480 | 23040 | 0.03584 | 7.4666e-05 | 0
2013-11-22 | HGS31 | URBAN | Replace Overhead Assets | 3 | 121 | 363 | 0.00056466 | 4.6666e-06 | 0
2013-11-22 | DC1 | URBAN | Replace underground assets | 11 | 295 | 3245 | 0.0050477 | 1.7111e-05 | 0
2013-11-22 | DC2 | URBAN | Replace underground assets | 19 | 300 | 5700 | 0.0088666 | 2.9555e-05 | 0
2013-11-22 | HGS33 | URBAN | Replace Overhead Assets | 6 | 130 | 780 | 0.0012133 | 9.3333e-06 | 0
2013-11-22 | NP36 | URBAN | Regular Maintenance | 43 | 418 | 17974 | 0.027959 | 6.6888e-05 | 0
2013-11-24 | MGE33 | URBAN | Regular Maintenance | 16 | 200 | 3200 | 0.0049777 | 2.4889e-05 | 0
2013-11-24 | NP23 | URBAN | Regular Maintenance | 1 | 450 | 450 | 0.00069999 | 1.5555e-06 | 0
2013-11-24 | LD7 | URBAN | Extended Electricity Supply | 138 | 370 | 51060 | 0.079426 | 0.00021467 | 0
2013-11-24 | MGE12 | URBAN | Regular Maintenance | 6 | 270 | 1620 | 0.00252 | 9.3333e-06 | 0
2013-11-24 | MC4 | URBAN | Replace Overhead Assets | 6 | 440 | 2640 | 0.0041066 | 9.3333e-06 | 0
2013-11-24 | DN6 | RURAL SHORT | Regular Maintenance | 62 | 662 | 41044 | 0.063846 | 9.6444e-05 | 0
2013-11-26 | DMA13 | URBAN | Replace Overhead Assets | 33 | 120 | 3960 | 0.00616 | 5.1333e-05 | 0
2013-11-26 | MTN32 | URBAN | Tree Clearing/Bushfire Mitigation | 41 | 330 | 13530 | 0.021047 | 6.3777e-05 | 0
2013-11-27 | RBD13 | URBAN | Short Interruption | 21 | 35 | 735 | 0.0011433 | 3.2666e-05 | 0
2013-11-27 | RBD22 | URBAN | Short Interruption | 25 | 60 | 1500 | 0.0023333 | 3.8889e-05 | 0
2013-11-27 | BR15 | URBAN | Replace Overhead Assets | 24 | 215 | 5160 | 0.0080266 | 3.7333e-05 | 0
2013-11-27 | BR1 | URBAN | Regular Maintenance | 26 | 390 | 10140 | 0.015773 | 4.0444e-05 | 0
2013-11-27 | SH70 | URBAN | Replace Overhead Assets | 539 | 450 | 242550 | 0.3773 | 0.00083844 | 0
2013-11-27 | HGS33 | URBAN | Replace Overhead Assets | 4 | 870 | 3480 | 0.0054133 | 6.2222e-06 | 0
2013-11-28 | DMA15 | URBAN | Replace Overhead Assets | 15 | 75 | 1125 | 0.00175 | 2.3333e-05 | 0
2013-11-28 | MTN32 | URBAN | Replace Overhead Assets | 234 | 90 | 21060 | 0.03276 | 0.000364 | 0
2013-11-28 | GW4 | URBAN | Replace Overhead Assets | 24 | 270 | 6480 | 0.01008 | 3.7333e-05 | 0
2013-11-28 | FSH12 | URBAN | Replace Overhead Assets | 9 | 69 | 621 | 0.00096599 | 1.4e-05 | 0
2013-11-28 | RBD21 | RURAL SHORT | Extended Electricity Supply | 49 | 380 | 18620 | 0.028964 | 7.6222e-05 | 0
2013-11-28 | NP33 | URBAN | Replace Overhead Assets | 126 | 405 | 51030 | 0.079379 | 0.000196 | 0
2013-11-28 | CRM33 | URBAN | Replace Overhead Assets | 46 | 480 | 22080 | 0.034346 | 7.1555e-05 | 0
2013-11-29 | BW33 | URBAN | Replace Overhead Assets | 42 | 195 | 8190 | 0.01274 | 6.5333e-05 | 0
2013-11-29 | NP23 | URBAN | Regular Maintenance | 74 | 75 | 5550 | 0.0086333 | 0.00011511 | 0
2013-11-29 | DMA13 | URBAN | Replace Overhead Assets | 10 | 180 | 1800 | 0.0028 | 1.5555e-05 | 0
2013-11-29 | BR15 | URBAN | Replace Overhead Assets | 15 | 290 | 4350 | 0.0067666 | 2.3333e-05 | 0
2013-12-01 | MC5 | URBAN | Extended Electricity Supply | 2 | 607 | 1214 | 0.0018909 | 3.1152e-06 | 0
2013-12-02 | NP36 | URBAN | Replace Overhead Assets | 25 | 215 | 5375 | 0.008372 | 3.894e-05 | 0
2013-12-02 | BR6 | URBAN | Regular Maintenance | 27 | 165 | 4455 | 0.006939 | 4.2055e-05 | 0
2013-12-02 | DN25 | URBAN | Road Works - VicRoads | 30 | 50 | 1500 | 0.0023364 | 4.6727e-05 | 0
2013-12-03 | MTN34 | URBAN | Replace Overhead Assets | 55 | 180 | 9900 | 0.01542 | 8.5667e-05 | 0
2013-12-03 | HGS33 | URBAN | Replace Overhead Assets | 33 | 230 | 7590 | 0.011822 | 5.14e-05 | 0
2013-12-03 | NP33 | URBAN | Regular Maintenance | 11 | 240 | 2640 | 0.004112 | 1.7133e-05 | 0
2013-12-03 | NP23 | URBAN | Regular Maintenance | 27 | 380 | 10260 | 0.015981 | 4.2055e-05 | 0
2013-12-03 | NP11 | URBAN | Replace Overhead Assets | 63 | 360 | 22680 | 0.035326 | 9.8128e-05 | 0
2013-12-03 | DC2 | RURAL SHORT | Replace underground assets | 30 | 390 | 11700 | 0.018224 | 4.6727e-05 | 0
2013-12-03 | MTN31 | URBAN | Replace Overhead Assets | 46 | 225 | 10350 | 0.016121 | 7.1649e-05 | 0
2013-12-03 | M25 | URBAN | Regular Maintenance | 97 | 410 | 39770 | 0.061945 | 0.00015109 | 0
2013-12-04 | EB32 | URBAN | Replace Overhead Assets | 125 | 180 | 22500 | 0.035046 | 0.0001947 | 0
2013-12-04 | LWN32 | URBAN | Regular Maintenance | 100 | 250 | 25000 | 0.03894 | 0.00015576 | 0
2013-12-04 | CRM22 | URBAN | Regular Maintenance | 27 | 255 | 6885 | 0.010724 | 4.2055e-05 | 0
2013-12-04 | OR12 | URBAN | Extended Electricity Supply | 84 | 320 | 26880 | 0.041868 | 0.00013084 | 0
2013-12-04 | CRM33 | URBAN | Regular Maintenance | 54 | 305 | 16470 | 0.025653 | 8.4109e-05 | 0
2013-12-04 | DC2 | URBAN | Replace underground assets | 20 | 350 | 7000 | 0.010903 | 3.1152e-05 | 0
2013-12-04 | NP23 | URBAN | Replace Overhead Assets | 20 | 570 | 11400 | 0.017756 | 3.1152e-05 | 0
2013-12-04 | DSH33 | URBAN | Extended Electricity Supply | 5 | 105 | 525 | 0.00081773 | 7.7879e-06 | 0
2013-12-05 | DMA12 | RURAL SHORT | Regular Maintenance | 1 | 152 | 152 | 0.00023675 | 1.5576e-06 | 0
2013-12-05 | GW3 | URBAN | Replace Overhead Assets | 83 | 195 | 16185 | 0.025209 | 0.00012928 | 0
2013-12-05 | MC3 | URBAN | Replace Overhead Assets | 30 | 190 | 5700 | 0.0088782 | 4.6727e-05 | 0
2013-12-05 | HGS32 | URBAN | Extended Electricity Supply | 13 | 285 | 3705 | 0.0057708 | 2.0249e-05 | 0
2013-12-05 | RBD21 | URBAN | Regular Maintenance | 20 | 155 | 3100 | 0.0048285 | 3.1152e-05 | 0
2013-12-05 | DC1 | RURAL SHORT | Replace underground assets | 22 | 310 | 6820 | 0.010623 | 3.4267e-05 | 0
2013-12-05 | SH70 | RURAL SHORT | Replace Overhead Assets | 184 | 480 | 88320 | 0.13757 | 0.00028659 | 0
2013-12-05 | CRM33 | URBAN | Regular Maintenance | 40 | 650 | 26000 | 0.040497 | 6.2303e-05 | 0
2013-12-05 | CRM22 | URBAN | Regular Maintenance | 54 | 650 | 35100 | 0.054671 | 8.4109e-05 | 0
2013-12-06 | MR32 | RURAL SHORT | Extended Electricity Supply | 12 | 195 | 2340 | 0.0036447 | 1.8691e-05 | 0
2013-12-06 | DC1 | RURAL SHORT | Replace underground assets | 26 | 240 | 6240 | 0.0097193 | 4.0497e-05 | 0
2013-12-06 | NP36 | URBAN | Regular Maintenance | 13 | 240 | 3120 | 0.0048597 | 2.0249e-05 | 0
2013-12-06 | DC1 | URBAN | Replace Overhead Assets | 22 | 270 | 5940 | 0.009252 | 3.4267e-05 | 0
2013-12-06 | MTN31 | RURAL SHORT | Replace underground assets | 137 | 300 | 41100 | 0.064017 | 0.00021339 | 0
2013-12-06 | FTN22 | RURAL SHORT | Regular Maintenance | 8 | 231 | 1848 | 0.0028784 | 1.2461e-05 | 0
2013-12-06 | MTN34 | RURAL SHORT | Replace Overhead Assets | 10 | 670 | 6700 | 0.010436 | 1.5576e-05 | 0
2013-12-07 | OE15 | URBAN | Regular Maintenance | 1 | 0 | 0 | 0 | 1.5576e-06 | 0
2013-12-07 | OE15 | URBAN | Regular Maintenance | 1 | 0 | 0 | 0 | 1.5576e-06 | 0
2013-12-08 | HGS31 | URBAN | Extended Electricity Supply | 24 | 80 | 1920 | 0.0029906 | 3.7382e-05 | 0
2013-12-08 | SVW41 | RURAL SHORT | Replace Overhead Assets | 26 | 210 | 5460 | 0.0085044 | 4.0497e-05 | 0
2013-12-08 | SS12 | URBAN | Replace Overhead Assets | 17 | 360 | 6120 | 0.0095324 | 2.6479e-05 | 0
2013-12-08 | GW1 | URBAN | Replace Overhead Assets | 14 | 285 | 3990 | 0.0062147 | 2.1806e-05 | 0
2013-12-08 | DVY22 | URBAN | Regular Maintenance | 3 | 410 | 1230 | 0.0019158 | 4.6727e-06 | 0
2013-12-08 | LD32 | URBAN | Regular Maintenance | 109 | 390 | 42510 | 0.066213 | 0.00016978 | 0
2013-12-08 | CRM22 | URBAN | Regular Maintenance | 30 | 461 | 13830 | 0.021541 | 4.6727e-05 | 0
2013-12-09 | HGS22 | URBAN | Tree Clearing/Bushfire Mitigation | 26 | 260 | 6760 | 0.010529 | 4.0497e-05 | 0
2013-12-09 | SS12 | URBAN | Replace Overhead Assets | 13 | 255 | 3315 | 0.0051634 | 2.0249e-05 | 0
2013-12-09 | NP12 | RURAL SHORT | Regular Maintenance | 38 | 300 | 11400 | 0.017756 | 5.9188e-05 | 0
2013-12-09 | DN10 | URBAN | Regular Maintenance | 17 | 165 | 2805 | 0.004369 | 2.6479e-05 | 0
2013-12-09 | CDA11 | URBAN | Replace plant and equipment | 2 | 630 | 1260 | 0.0019626 | 3.1152e-06 | 0
2013-12-10 | DN22 | RURAL SHORT | Replace Overhead Assets | 3 | 165 | 495 | 0.000771 | 4.6727e-06 | 0
2013-12-10 | FSH11 | URBAN | Upgrade capacity - subs and LV | 6 | 345 | 2070 | 0.0032242 | 9.3455e-06 | 0
2013-12-10 | K13 | URBAN | Replace Overhead Assets | 74 | 450 | 33300 | 0.051867 | 0.00011526 | 0
2013-12-10 | BU9 | URBAN | Replace underground assets | 31 | 420 | 13020 | 0.02028 | 4.8285e-05 | 0
2013-12-10 | NP36 | RURAL SHORT | Regular Maintenance | 16 | 461 | 7376 | 0.011489 | 2.4921e-05 | 0
2013-12-10 | M11 | URBAN | Regular Maintenance | 19 | 360 | 6840 | 0.010654 | 2.9594e-05 | 0
2013-12-10 | NP24 | URBAN | Improving Reliability | 37 | 420 | 15540 | 0.024205 | 5.7631e-05 | 0
2013-12-11 | NP31 | URBAN | Replace Overhead Assets | 83 | 130 | 10790 | 0.016806 | 0.00012928 | 0
2013-12-11 | BT10 | URBAN | Replace Overhead Assets | 11 | 225 | 2475 | 0.003855 | 1.7133e-05 | 0
2013-12-11 | DC3 | URBAN | Replace Overhead Assets | 67 | 300 | 20100 | 0.031307 | 0.00010436 | 0
2013-12-11 | MGE21 | URBAN | Replace underground assets | 30 | 327 | 9810 | 0.01528 | 4.6727e-05 | 0
2013-12-11 | RWT31 | URBAN |  | 2 | 365 | 730 | 0.001137 | 3.1152e-06 | 0
2013-12-11 | HGS23 | URBAN | Tree Clearing/Bushfire Mitigation | 48 | 390 | 18720 | 0.029158 | 7.4764e-05 | 0
2013-12-11 | K10 | URBAN | Upgrade capacity - subs and LV | 65 | 420 | 27300 | 0.042522 | 0.00010124 | 0
2013-12-11 | CFD22 | URBAN | Upgrade capacity - subs and LV | 54 | 420 | 22680 | 0.035326 | 8.4109e-05 | 0
2013-12-11 | MTN34 | URBAN | Improving Reliability | 42 | 450 | 18900 | 0.029438 | 6.5418e-05 | 0
2013-12-11 | NP24 | URBAN | Regular Maintenance | 79 | 345 | 27255 | 0.042452 | 0.00012305 | 0
2013-12-11 | DSH21 | RURAL SHORT | Regular Maintenance | 1 | 400 | 400 | 0.00062303 | 1.5576e-06 | 0
2013-12-11 | M25 | URBAN | Regular Maintenance | 102 | 510 | 52020 | 0.081025 | 0.00015887 | 0
2013-12-12 | GW3 | URBAN | Replace Overhead Assets | 17 | 300 | 5100 | 0.0079437 | 2.6479e-05 | 0
2013-12-12 | FSH32 | RURAL SHORT | Road Works - VicRoads | 141 | 345 | 48645 | 0.075769 | 0.00021962 | 0
2013-12-12 | NP11 | RURAL SHORT | Regular Maintenance | 1 | 345 | 345 | 0.00053737 | 1.5576e-06 | 0
2013-12-12 | DMA13 | RURAL SHORT | Tree Clearing/Bushfire Mitigation | 9 | 395 | 3555 | 0.0055372 | 1.4018e-05 | 0
2013-12-12 | RBD23 | URBAN | Upgrade capacity - subs and LV | 1 | 270 | 270 | 0.00042055 | 1.5576e-06 | 0
2013-12-12 | NP36 | URBAN | Regular Maintenance | 22 | 365 | 8030 | 0.012507 | 3.4267e-05 | 0
2013-12-13 | OAK23 | RURAL SHORT | Replace Overhead Assets | 36 | 130 | 4680 | 0.0072895 | 5.6073e-05 | 0
2013-12-13 | HGS23 | URBAN | Replace Overhead Assets | 43 | 90 | 3870 | 0.0060278 | 6.6976e-05 | 0
2013-12-13 | M32 | URBAN | Tree Clearing/Bushfire Mitigation | 777 | 230 | 178710 | 0.27836 | 0.0012102 | 0
2013-12-13 | NP24 | URBAN | Regular Maintenance | 25 | 370 | 9250 | 0.014408 | 3.894e-05 | 0
2013-12-13 | CRM21 | URBAN | Extended Electricity Supply | 1 | 90 | 90 | 0.00014018 | 1.5576e-06 | 0
2013-12-13 | GW7 | URBAN | Replace Overhead Assets | 2 | 150 | 300 | 0.00046727 | 3.1152e-06 | 0
2013-12-14 | NW21 | URBAN | Tree Clearing/Bushfire Mitigation | 436 | 195 | 85020 | 0.13243 | 0.00067911 | 0
2013-12-14 | NW21 | URBAN | Tree Clearing - Urban | 220 | 240 | 52800 | 0.08224 | 0.00034267 | 0
2013-12-15 | SV33 | URBAN | Replace Overhead Assets | 1 | 150 | 150 | 0.00023364 | 1.5576e-06 | 0
2013-12-15 | CM11 | URBAN | Replace Overhead Assets | 7 | 365 | 2555 | 0.0039796 | 1.0903e-05 | 0
2013-12-15 | NP36 | URBAN | Regular Maintenance | 49 | 415 | 20335 | 0.031673 | 7.6321e-05 | 0
2013-12-15 | EB22 | URBAN | Replace Overhead Assets | 353 | 510 | 180030 | 0.28041 | 0.00054983 | 0
2013-12-15 | FSH33 | URBAN | Regular Maintenance | 49 | 371 | 18179 | 0.028315 | 7.6321e-05 | 0
2013-12-16 | DC2 | RURAL SHORT |  | 17 | 200 | 3400 | 0.0052958 | 2.6479e-05 | 0
2013-12-16 | EW14 | URBAN | Replace Overhead Assets | 39 | 420 | 16380 | 0.025513 | 6.0746e-05 | 0
2013-12-16 | SS23 | URBAN | Replace Overhead Assets | 9 | 420 | 3780 | 0.0058877 | 1.4018e-05 | 0
2013-12-17 | EM9 | URBAN | Replace Overhead Assets | 157 | 210 | 32970 | 0.051353 | 0.00024454 | 0
2013-12-17 | CFD14 | URBAN | Replace Overhead Assets | 51 | 315 | 16065 | 0.025023 | 7.9437e-05 | 0
2013-12-17 | OR12 | URBAN | Extended Electricity Supply | 7 | 360 | 2520 | 0.0039251 | 1.0903e-05 | 0
2013-12-17 | FSH33 | URBAN | Regular Maintenance | 17 | 145 | 2465 | 0.0038394 | 2.6479e-05 | 0
2013-12-18 | CFD15 | URBAN | Replace plant and equipment | 11 | 0 | 0 | 0 | 1.7133e-05 | 0
2013-12-18 | BH23 | URBAN | Replace Overhead Assets | 81 | 0 | 0 | 0 | 0.00012616 | 0
2013-12-18 | M32 | URBAN | Tree Clearing/Bushfire Mitigation | 547 | 260 | 142220 | 0.22152 | 0.000852 | 0
2013-12-18 | BR6 | URBAN | Regular Maintenance | 14 | 165 | 2310 | 0.003598 | 2.1806e-05 | 0
2013-12-18 | RBD23 | URBAN | Replace Overhead Assets | 35 | 300 | 10500 | 0.016355 | 5.4515e-05 | 0
2013-12-18 | DMA13 | URBAN | Replace Overhead Assets | 3 | 53 | 159 | 0.00024766 | 4.6727e-06 | 0
2013-12-18 | BR4 | URBAN |  | 49 | 300 | 14700 | 0.022896 | 7.6321e-05 | 0
2013-12-18 | EW9 | URBAN | Replace Overhead Assets | 123 | 420 | 51660 | 0.080465 | 0.00019158 | 0
2013-12-18 | HGS22 | URBAN | Replace Overhead Assets | 63 | 480 | 30240 | 0.047101 | 9.8128e-05 | 0
2013-12-19 | NW13 | URBAN | Replace Overhead Assets | 11 | 0 | 0 | 0 | 1.7133e-05 | 0
2013-12-19 | FSH21 | URBAN | Tree Clearing/Bushfire Mitigation | 94 | 160 | 15040 | 0.023426 | 0.00014641 | 0
2013-12-19 | EM11 | RURAL SHORT | Replace Overhead Assets | 47 | 130 | 6110 | 0.0095168 | 7.3206e-05 | 0
2013-12-19 | EM11 | URBAN | Replace Overhead Assets | 30 | 155 | 4650 | 0.0072428 | 4.6727e-05 | 0
2013-12-19 | CFD26 | URBAN | Replace Overhead Assets | 55 | 240 | 13200 | 0.02056 | 8.5667e-05 | 0
2013-12-19 | DC3 | URBAN | Replace underground assets | 19 | 270 | 5130 | 0.0079904 | 2.9594e-05 | 0
2013-12-19 | MGE32 | URBAN | Upgrade capacity - subs and LV | 21 | 420 | 8820 | 0.013738 | 3.2709e-05 | 0
2013-12-19 | EW14 | URBAN | Replace Overhead Assets | 84 | 450 | 37800 | 0.058877 | 0.00013084 | 0
2013-12-19 | DC3 | URBAN | Replace underground assets | 11 | 300 | 3300 | 0.00514 | 1.7133e-05 | 0
2013-12-20 | MTN32 | URBAN | Improving Reliability | 1 | 180 | 180 | 0.00028036 | 1.5576e-06 | 0
2013-12-20 | GW5 | URBAN | Replace Overhead Assets | 107 | 330 | 35310 | 0.054998 | 0.00016666 | 0
2013-12-20 | GW4 | URBAN | Replace Overhead Assets | 113 | 395 | 44635 | 0.069523 | 0.00017601 | 0
2013-12-22 | NW22 | URBAN | Replace underground assets | 41 | 300 | 12300 | 0.019158 | 6.3861e-05 | 0
2013-12-22 | HT3 | URBAN | Replace plant and equipment | 1 | 300 | 300 | 0.00046727 | 1.5576e-06 | 0
2013-12-22 | DVY24 | URBAN | Extended Electricity Supply | 3 | 375 | 1125 | 0.0017523 | 4.6727e-06 | 0
2013-12-22 | GW6 | URBAN | Replace Overhead Assets | 18 | 285 | 5130 | 0.0079904 | 2.8036e-05 | 0
2013-12-22 | DC6 | URBAN |  | 25 | 540 | 13500 | 0.021027 | 3.894e-05 | 0
2013-12-23 | NP24 | RURAL SHORT | Regular Maintenance | 4 | 295 | 1180 | 0.0018379 | 6.2303e-06 | 0
2013-12-23 | MR15 | URBAN | Regular Maintenance | 1 | 120 | 120 | 0.00018691 | 1.5576e-06 | 0
2013-12-23 | NP16 | URBAN | Regular Maintenance | 1 | 675 | 675 | 0.0010514 | 1.5576e-06 | 0
2013-12-30 | CFD22 | RURAL SHORT | Replace Overhead Assets | 87 | 360 | 31320 | 0.048783 | 0.00013551 | 0
2013-12-31 | CRM33 | URBAN | Replace Overhead Assets | 219 | 300 | 65700 | 0.10233 | 0.00034111 | 0
2013-12-31 | LD5 | RURAL SHORT | Regular Maintenance | 18 | 425 | 7650 | 0.011915 | 2.8036e-05 | 0
Contents

## 6b. Annual Feeder Reliability
United Energy Distribution Pty Limited
Annual Feeder Reliability
2013
Table 1 Annual Feeder Reliability Data
| Feeder ID / name | Description of the service area for the feeder | Feeder classification | Number of distribution customers | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Total Length | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Total unplanned minutes off-supply | Unplanned minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) | Unplanned interruptions (SAIFI) (after removing excluded events) | Total number of planned outages | Total planned minutes off-supply | Planned interruptions (SAIFI) | Total number of momentary feeder outages | Total number of momentary feeder section outages | Momentary interruptions due to feeder outages (MAIFI) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events) | Momentary interruptions due to feeder section outages (MAIFI) | Monetary interruptions due to feeder section outages (MAIFI) (after removing excluded events) | Low Reliability Feeder (SAIDI) | Low Reliability Feeder (MAIFI) | Average Demand | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh)
| AR11 | Citipower Feeder | URBAN | 294 | 0.45 | 0.37 | 0.82 | 0 | 0 | 0 | 1 | 13684.6732 | 13684.6732 | 0.00047275 | 0.00047275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| AR12 | Citipower Feeder | URBAN | 122 | 0.07 | 0 | 0.07 | 0 | 0 | 0 | 3 | 30597.352 | 30597.352 | 0.00080821 | 0.00080821 | 1 | 345 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| AR2 | Citipower Feeder | URBAN | 117 | 0 | 0.11 | 0.11 | 0 | 0 | 0 | 1 | 7443.161 | 7443.161 | 0.00026264 | 0.00026264 | 1 | 56985 | 0.00020239 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0 | 0 | 0
| AR3 | Citipower Feeder | URBAN | 81 | 0.05 | 0.18 | 0.23 | 0 | 0 | 0 | 2 | 18661.0974 | 18661.0974 | 0.00023947 | 0.00023947 | 0 | 0 | 0 | 1 | 0 | 0.00011587 | 0.00011587 | 0 | 0 | no | no | 0 | 0 | 0
| AR6 | Citipower Feeder | URBAN | 278.5 | 0.54 | 0.87 | 1.41 | 0 | 0 | 0 | 3 | 31425.8059 | 31425.8059 | 0.00091242 | 0.00091242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| AR7 | Citipower Feeder | URBAN | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 175.1332 | 175.1332 | 6.1798e-06 | 6.1798e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| AR99 | Citipower Feeder | URBAN | 30.5 | 147.56 | 0.42 | 147.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BC11 | Citipower Feeder | URBAN | 1255 | 1.16 | 1.34 | 2.5 | 0 | 0 | 0 | 3 | 10107.2124 | 10107.2124 | 0.0020077 | 0.0020077 | 0 | 47010 | 0.00021938 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BC12 | Citipower Feeder | URBAN | 202 | 0.2 | 0.13 | 0.33 | 0 | 0 | 0 | 1 | 701.8226 | 701.8226 | 0.00031721 | 0.00031721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BC22 | Citipower Feeder | URBAN | 395 | 0 | 1.72 | 1.72 | 0 | 0 | 0 | 2 | 3086.1802 | 3086.1802 | 0.00061815 | 0.00061815 | 2 | 25110 | 0.00014368 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BC23 | Citipower Feeder | URBAN | 1313 | 3.08 | 1.04 | 4.12 | 0 | 0 | 0 | 7 | 41434.7389 | 41434.7389 | 0.0024317 | 0.0024317 | 0 | 182679 | 0.00065815 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BC6 | Citipower Feeder | URBAN | 19 | 0 | 0.65 | 0.65 | 0 | 0 | 0 | 1 | 48.3338 | 48.3338 | 2.6306e-05 | 2.6306e-05 | 1 | 330 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BH11 | United Energy Feeder | URBAN | 2840.5 | 9.45 | 0.83 | 10.28 | 8.6565 | 9.4457 | 2.1613 | 12 | 545357.7871 | 545357.7871 | 0.015442 | 0.015442 | 6 | 124785 | 0.00051447 | 3 | 1 | 0.020333 | 0.020333 | 0.0022216 | 0.0022216 | no | yes | 2.9519 | 9.4457 | 2.1613
| BH12 | United Energy Feeder | URBAN | 943 | 4.87 | 1.26 | 6.13 | 2.7011 | 0.66693 | 0.55589 | 4 | 68913.4454 | 68913.4454 | 0.0029911 | 0.0029911 | 1 | 57440 | 0.00014677 | 1 | 0 | 0.0014198 | 0.0014198 | 0 | 0 | no | no | 0.54757 | 0.66693 | 0.55589
| BH14 | United Energy Feeder | URBAN | 1 | 0 | 1.24 | 1.24 | 6.3663 | 0.75427 | 0 | 1 | 7.007 | 7.007 | 1.5392e-06 | 1.5392e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 6.4588 | 0.75427 | 0
| BH21 | United Energy Feeder | URBAN | 3500 | 12.98 | 2.26 | 15.24 | 7.4782 | 0.75492 | 3.9969 | 7 | 62381.3078 | 62381.3078 | 0.0058921 | 0.0058921 | 3 | 330275 | 0.0015357 | 1 | 0 | 0.0046009 | 0.0046009 | 0 | 0 | no | no | 2.5413 | 0.75492 | 3.9969
| BH22 | United Energy Feeder | URBAN | 1468 | 6.01 | 0.99 | 7 | 4.3518 | 2.9534 | 1.4434 | 8 | 150767.41 | 116544.81 | 0.0044778 | 0.0029421 | 0 | 73685 | 0.00024256 | 1 | 0 | 0.0022649 | 0 | 0 | 0 | no | no | 1.7254 | 2.9534 | 1.4434
| BH23 | United Energy Feeder | URBAN | 2846.5 | 7.2 | 1.88 | 9.08 | 12.4147 | 6.4074 | 1.9574 | 7 | 229974.8965 | 229974.8965 | 0.006413 | 0.006413 | 9 | 70254 | 0.0004434 | 1 | 0 | 0.0057843 | 0.0057843 | 0 | 0 | no | no | 4.7585 | 6.4074 | 1.9574
| BH24 | United Energy Feeder | URBAN | 1 | 0 | 1.19 | 1.19 | 13.4969 | 0.96003 | 0 | 1 | 7.007 | 7.007 | 1.5392e-06 | 1.5392e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 8.2206 | 0.96003 | 0
| BR1 | United Energy Feeder | URBAN | 1461 | 5.75 | 0.48 | 6.23 | 4.6531 | 3.6004 | 0.16823 | 7 | 217016.8824 | 18029.0014 | 0.0047062 | 0.00020769 | 7 | 10140 | 4.0169e-05 | 1 | 0 | 0.0022541 | 0.0022541 | 0 | 0 | no | no | 1.4543 | 3.6004 | 0.16823
| BR10 | United Energy Feeder | URBAN | 1048.5 | 3.59 | 3.39 | 6.98 | 3.1753 | 0.79049 | 0.67951 | 6 | 52189.0338 | 24551.6114 | 0.0017811 | 0.00018919 | 0 | 44862 | 0.00018848 | 0 | 1 | 0 | 0 | 0.0010197 | 0 | no | no | 0.95287 | 0.79049 | 0.67951
| BR13 | United Energy Feeder | URBAN | 1391.5 | 4.63 | 0.2 | 4.83 | 3.7937 | 6.4048 | 0.47874 | 4 | 462287.9384 | 424549.6644 | 0.0065761 | 0.0044008 | 1 | 34555 | 0.00018848 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.1567 | 6.4048 | 0.47874
| BR15 | United Energy Feeder | URBAN | 1291.5 | 3.71 | 0.19 | 3.9 | 3.7754 | 10.4017 | 0.5938 | 5 | 760858.5132 | 81556.0043 | 0.0060667 | 0.0020854 | 3 | 43435 | 0.00019157 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.0594 | 10.4017 | 0.5938
| BR4 | United Energy Feeder | URBAN | 1443.5 | 4.2 | 0.2 | 4.4 | 4.2889 | 0.6448 | 0.41746 | 4 | 48567.8795 | 9458.099 | 0.0024823 | 0.00030361 | 3 | 31444 | 0.00014677 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1499 | 0.6448 | 0.41746
| BR6 | United Energy Feeder | URBAN | 1240 | 6.97 | 0.88 | 7.85 | 3.6911 | 1.0092 | 0.56454 | 2 | 57729.2386 | 25401.1832 | 0.0020058 | 0.00014368 | 5 | 32292 | 0.00017458 | 1 | 0 | 0.001908 | 0.001908 | 0 | 0 | no | no | 1.3007 | 1.0092 | 0.56454
| BR9 | United Energy Feeder | URBAN | 1475.5 | 5.22 | 0.26 | 5.48 | 5.0568 | 1.4582 | 0.45606 | 10 | 83148.5061 | 44210.9225 | 0.0026081 | 0.00036526 | 2 | 26005 | 0.00012978 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 1.5526 | 1.4582 | 0.45606
| BRA23 | SPAusnet Feeder | URBAN | 17 | 0.13 | 0.09 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BRA32 | SPAusnet Feeder | URBAN | 288 | 3.11 | 0.08 | 3.19 | 0 | 0 | 0 | 1 | 1481.8645 | 1481.8645 | 2.4487e-05 | 2.4487e-05 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| BT10 | United Energy Feeder | URBAN | 1990.5 | 5.48 | 0.39 | 5.87 | 5.7816 | 3.9245 | 2.7299 | 4 | 291306.78 | 238777.0215 | 0.0073491 | 0.0043233 | 5 | 202635 | 0.00076011 | 1 | 0 | 0.0030497 | 0.0030497 | 0 | 0 | no | no | 1.609 | 3.9245 | 2.7299
| BT14 | United Energy Feeder | URBAN | 1125.5 | 2.84 | 0.38 | 3.22 | 5.2053 | 0.43726 | 0 | 2 | 34112.3884 | 4609.3733 | 0.00175 | 5.0613e-05 | 0 | 0 | 0 | 1 | 0 | 0.0023746 | 0.0023746 | 0 | 0 | no | no | 0.86561 | 0.43726 | 0
| BT15 | United Energy Feeder | URBAN | 1027.5 | 2.23 | 0.68 | 2.91 | 2.3715 | 0.46036 | 0.26083 | 2 | 31928.006 | 4583.7481 | 0.0016221 | 4.7059e-05 | 0 | 18090 | 0.00010351 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.88891 | 0.46036 | 0.26083
| BT2 | United Energy Feeder | URBAN | 1448 | 2.93 | 0.62 | 3.55 | 4.015 | 0.66676 | 0 | 1 | 42034.703 | 2446.8835 | 0.0022691 | 2.0084e-05 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3781 | 0.66676 | 0
| BT4 | United Energy Feeder | URBAN | 1937.5 | 4.95 | 1.46 | 6.41 | 4.7843 | 3.2718 | 0 | 5 | 205394.6261 | 145761.3573 | 0.0062538 | 0.0031729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.8518 | 3.2718 | 0
| BT5 | United Energy Feeder | URBAN | 744 | 2.05 | 0.41 | 2.46 | 1.8898 | 2.5354 | 0 | 5 | 165626.5064 | 137577.1398 | 0.0042912 | 0.0031395 | 1 | 0 | 0 | 1 | 0 | 0.0010135 | 0.0010135 | 0 | 0 | no | no | 0.68335 | 2.5354 | 0
| BT6 | United Energy Feeder | URBAN | 940.5 | 2.8 | 0.32 | 3.12 | 2.7841 | 0.63103 | 0.40097 | 2 | 36967.213 | 12128.1795 | 0.001627 | 0.00019621 | 0 | 23490 | 0.00013441 | 3 | 0 | 0.004332 | 0.004332 | 0 | 0 | no | no | 0.96326 | 0.63103 | 0.40097
| BT9 | United Energy Feeder | URBAN | 1991 | 4.17 | 0.49 | 4.66 | 4.1356 | 0.74953 | 0.71998 | 2 | 59401.6523 | 6445.4726 | 0.003108 | 5.7719e-05 | 0 | 57060 | 0.00024101 | 1 | 0 | 0.0030652 | 0.0030652 | 0 | 0 | no | no | 1.5073 | 0.74953 | 0.71998
| BU1 | United Energy Feeder | URBAN | 1283 | 6.9 | 0.35 | 7.25 | 3.6796 | 0.029791 | 0.44917 | 2 | 2135.62 | 2135.62 | 3.3201e-05 | 3.3201e-05 | 0 | 32200 | 0.00017767 | 1 | 0 | 0.0019806 | 0.0019806 | 0 | 0 | no | no | 1.0738 | 0.029791 | 0.44917
| BU10 | United Energy Feeder | URBAN | 1599 | 7.76 | 0.24 | 8 | 4.208 | 0.16577 | 0.90321 | 4 | 11433.5285 | 7194.1294 | 0.00013935 | 9.8568e-05 | 1 | 62295 | 0.00035843 | 2 | 0 | 0.0048898 | 0.0048898 | 0 | 0 | no | no | 1.391 | 0.16577 | 0.90321
| BU13 | United Energy Feeder | URBAN | 702 | 5.58 | 0.84 | 6.42 | 2.2508 | 0.53559 | 0.20862 | 6 | 23722.1947 | 23722.1947 | 0.00015762 | 0.00015762 | 2 | 9240 | 3.3989e-05 | 1 | 0 | 0.0010861 | 0.0010861 | 0 | 0 | no | no | 0.95097 | 0.53559 | 0.20862
| BU14 | United Energy Feeder | URBAN | 1579 | 9.84 | 0.72 | 10.56 | 4.3059 | 6.4441 | 0.33454 | 6 | 396141.1369 | 396141.1369 | 0.005309 | 0.005309 | 4 | 20565 | 0.00011433 | 4 | 0 | 0.0097394 | 0.0097394 | 0 | 0 | no | no | 1.5412 | 6.4441 | 0.33454
| BU2 | United Energy Feeder | URBAN | 1538 | 9.08 | 1.85 | 10.93 | 4.5016 | 1.5066 | 0.42201 | 6 | 95845.9033 | 93079.1756 | 0.0028822 | 0.002847 | 3 | 26847 | 0.00020239 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4505 | 1.5066 | 0.42201
| BU4 | United Energy Feeder | URBAN | 1362.5 | 6.07 | 0.2 | 6.27 | 3.8557 | 0.16794 | 0 | 2 | 11366.1772 | 11366.1772 | 0.00015743 | 0.00015743 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2079 | 0.16794 | 0
| BU6 | United Energy Feeder | URBAN | 1413 | 5.45 | 0.88 | 6.33 | 3.7579 | 0.28469 | 0 | 6 | 24187.9263 | 17727.2309 | 0.00017442 | 0.00013313 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.99787 | 0.28469 | 0
| BU9 | United Energy Feeder | URBAN | 1497.5 | 7.87 | 1.84 | 9.71 | 4.0319 | 2.1211 | 0.70766 | 7 | 148517.0846 | 148517.0846 | 0.002451 | 0.002451 | 5 | 49550 | 0.00029818 | 2 | 0 | 0.0046364 | 0.0046364 | 0 | 0 | no | no | 1.2832 | 2.1211 | 0.70766
| BW21 | United Energy Feeder | URBAN | 1775.5 | 6.62 | 0.86 | 7.48 | 4.4109 | 0.29992 | 1.2003 | 3 | 20472.4748 | 8012.7201 | 0.00026028 | 0.00010781 | 0 | 81935 | 0.00041405 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5607 | 0.29992 | 1.2003
| BW22 | United Energy Feeder | URBAN | 615 | 3.65 | 1.4 | 5.05 | 3.6469 | 0.020246 | 0.46721 | 0 | 666.0333 | 666.0333 | 4.6348e-06 | 4.6348e-06 | 0 | 15370 | 7.2613e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1217 | 0.020246 | 0.46721
| BW23 | United Energy Feeder | URBAN | 726 | 2.92 | 1.25 | 4.17 | 3.1724 | 0.026642 | 0 | 1 | 1266.15 | 632.55 | 7.6938e-06 | 4.6348e-06 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.91659 | 0.026642 | 0
| BW32 | United Energy Feeder | URBAN | 897 | 2.63 | 0.5 | 3.13 | 2.5097 | 0.007162 | 0 | 0 | 429 | 429 | 3.0899e-06 | 3.0899e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.8985 | 0.007162 | 0
| BW33 | United Energy Feeder | URBAN | 1536 | 8.07 | 0.2 | 8.27 | 3.6128 | 3.0389 | 0.19674 | 5 | 204358.6691 | 204358.6691 | 0.006875 | 0.006875 | 3 | 13230 | 0.00012978 | 1 | 0 | 0.0023251 | 0.0023251 | 0 | 0 | no | no | 1.3705 | 3.0389 | 0.19674
| BW34 | United Energy Feeder | URBAN | 1466 | 6 | 0.24 | 6.24 | 3.5394 | 0.11036 | 1.2856 | 1 | 8843.3988 | 1370.4999 | 4.2965e-05 | 1.3905e-05 | 0 | 103020 | 0.00038778 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0977 | 0.11036 | 1.2856
| BW35 | United Energy Feeder | URBAN | 1828.5 | 6.65 | 0.33 | 6.98 | 4.2995 | 0.67699 | 0 | 4 | 50634.171 | 50634.171 | 0.0015807 | 0.0015807 | 0 | 0 | 0 | 1 | 0 | 0.0028041 | 0.0028041 | 0 | 0 | no | no | 1.4668 | 0.67699 | 0
BW22 | BW8 | United Energy Feeder | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1217 | 0 | 0
| CDA11 | United Energy Feeder | URBAN | 2894.5 | 19.35 | 1.83 | 21.18 | 9.912 | 10.9443 | 4.2705 | 10 | 489717.9672 | 123958.5272 | 0.021283 | 0.0051708 | 2 | 191091 | 0.0010011 | 0 | 3 | 0 | 0 | 0.014059 | 0.014059 | no | no | 3.8812 | 10.9443 | 4.2705
| CDA21 | United Energy Feeder | URBAN | 609 | 4.37 | 0.57 | 4.94 | 2.2105 | 4.0599 | 2.5837 | 4 | 150776.1572 | 98054.1053 | 0.0031089 | 0.0017968 | 3 | 95955 | 0.00055 | 3 | 0 | 0.0027407 | 0.0018648 | 0 | 0 | yes | no | 0.98389 | 4.0599 | 2.5837
| CDA22 | United Energy Feeder | URBAN | 2005 | 14.07 | 1.1 | 15.17 | 6.1281 | 16.2554 | 4.4629 | 7 | 669189.5876 | 142079.3987 | 0.011126 | 0.004904 | 0 | 183725 | 0.00096714 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 2.9222 | 16.2554 | 4.4629
| CDA23 | United Energy Feeder | URBAN | 3220.5 | 5.01 | 1.04 | 6.05 | 3.4908 | 1.2804 | 0.30893 | 4 | 175072.7724 | 3549.9311 | 0.0045121 | 4.4618e-05 | 0 | 42240 | 0.00018848 | 4 | 0 | 0.0087877 | 0.0065892 | 0 | 0 | no | no | 1.4132 | 1.2804 | 0.30893
| CDA24 | United Energy Feeder | URBAN | 3493.5 | 13.05 | 2.04 | 15.09 | 10.6287 | 1.6324 | 0.0080251 | 2 | 85434.6386 | 6139.2893 | 0.0056352 | 6.9353e-05 | 11 | 420 | 3.0899e-06 | 1 | 2 | 0.0053965 | 0 | 0.0070604 | 0.0070604 | no | no | 4.0051 | 1.6324 | 0.0080251
| CFD11 | United Energy Feeder | URBAN | 182.5 | 0 | 2.61 | 2.61 | 4.438 | 0.012542 | 0 | 0 | 93.45 | 93.45 | 1.5449e-06 | 1.5449e-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4696 | 0.012542 | 0
| CFD12 | United Energy Feeder | URBAN | 1192 | 2.24 | 4.19 | 6.43 | 4.9638 | 0.29675 | 4.1066 | 2 | 10975.032 | 10975.032 | 6.5444e-05 | 6.5444e-05 | 7 | 151875 | 0.00052683 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.9338 | 0.29675 | 4.1066
| CFD13 | United Energy Feeder | URBAN | 1638.5 | 4.7 | 0.66 | 5.36 | 4.6932 | 0.17556 | 0.68123 | 2 | 12912.6787 | 12912.6787 | 0.00016244 | 0.00016244 | 2 | 50106 | 0.00022402 | 3 | 2 | 0.0076027 | 0.0076027 | 0.0010985 | 0.0010985 | no | no | 1.3366 | 0.17556 | 0.68123
| CFD14 | United Energy Feeder | URBAN | 3427 | 9.05 | 2.49 | 11.54 | 8.4455 | 0.1055 | 0.45473 | 2 | 7965.8504 | 6348.6171 | 0.00011464 | 0.00011309 | 1 | 34335 | 0.00014986 | 1 | 0 | 0.0053486 | 0.0053486 | 0 | 0 | no | no | 2.7232 | 0.1055 | 0.45473
| CFD15 | United Energy Feeder | URBAN | 2672.5 | 4.14 | 1.38 | 5.52 | 3.3423 | 0.019058 | 0.51629 | 1 | 2170.169 | 2170.169 | 4.7059e-05 | 4.7059e-05 | 0 | 58790 | 0.00038006 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4082 | 0.019058 | 0.51629
| CFD16 | United Energy Feeder | URBAN | 150 | 0 | 1.5 | 1.5 | 0.37845 | 0.00043488 | 0 | 0 | 83.3667 | 83.3667 | 1.5449e-06 | 1.5449e-06 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.046948 | 0.00043488 | 0
| CFD21 | United Energy Feeder | URBAN | 130.5 | 0 | 1.52 | 1.52 | 0.28284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.069576 | 0 | 0
| CFD22 | United Energy Feeder | URBAN | 2123.5 | 6.56 | 1.3 | 7.86 | 5.7764 | 0.18473 | 6.384 | 3 | 10006.3197 | 10006.3197 | 0.00019442 | 0.00019442 | 2 | 345795 | 0.0014244 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.3522 | 0.18473 | 6.384
| CFD23 | United Energy Feeder | URBAN | 1686 | 3.9 | 1.54 | 5.44 | 5.6174 | 0.42579 | 3.9898 | 6 | 24652.9691 | 24652.9691 | 0.00034545 | 0.00034545 | 3 | 231007 | 0.00057472 | 1 | 0 | 0.0026249 | 0.0026249 | 0 | 0 | no | no | 1.7472 | 0.42579 | 3.9898
| CFD24 | United Energy Feeder | URBAN | 829 | 3.11 | 0.56 | 3.67 | 6.844 | 1.3666 | 1.109 | 3 | 33567.7465 | 33567.7465 | 0.00023253 | 0.00023253 | 6 | 27240 | 0.00018385 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.025 | 1.3666 | 1.109
| CFD25 | United Energy Feeder | URBAN | 1299 | 2.88 | 0.23 | 3.11 | 2.8762 | 0.046756 | 0 | 1 | 4507.7695 | 4507.7695 | 0.00014677 | 0.00014677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.80841 | 0.046756 | 0
| CFD26 | United Energy Feeder | URBAN | 2341.5 | 4.18 | 0.86 | 5.04 | 3.9122 | 0.76017 | 0.38612 | 3 | 72606.5271 | 72241.4771 | 0.00034533 | 0.00034378 | 0 | 36880 | 0.00018385 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4709 | 0.76017 | 0.38612
| CM11 | United Energy Feeder | URBAN | 47.5 | 1.62 | 0.45 | 2.07 | 2.691 | 3.0322 | 8.0657 | 2 | 6204.8472 | 4925.5837 | 9.0681e-05 | 1.6994e-05 | 8 | 16505 | 5.7163e-05 | 1 | 0 | 7.5703e-05 | 7.5703e-05 | 0 | 0 | yes | no | 1.3927 | 3.0322 | 8.0657
| CM12 | United Energy Feeder | URBAN | 218 | 0 | 2.57 | 2.57 | 3.0511 | 7.8054 | 0 | 3 | 62936.9761 | 58113.0866 | 0.00071044 | 0.00043259 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.6222 | 7.8054 | 0
| CM13 | United Energy Feeder | URBAN | 895.5 | 3.7 | 0.35 | 4.05 | 2.4583 | 2.6935 | 0.67217 | 4 | 160847.3476 | 137047.7157 | 0.0029359 | 0.001565 | 4 | 40140 | 0.00015604 | 2 | 0 | 0.002767 | 0.002767 | 0 | 0 | no | no | 0.89974 | 2.6935 | 0.67217
| CM14 | United Energy Feeder | URBAN | 28.5 | 0 | 1.67 | 1.67 | 2.655 | 0.14612 | 0 | 1 | 239.8619 | 0 | 1.3816e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0417 | 0.14612 | 0
| CM15 | United Energy Feeder | URBAN | 66.5 | 0.73 | 0.57 | 1.3 | 2.1984 | 0.29212 | 0.45723 | 1 | 1865.5926 | 0 | 0.00010746 | 0 | 2 | 2920 | 1.236e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.62477 | 0.29212 | 0.45723
| CM21 | United Energy Feeder | URBAN | 52.5 | 1.01 | 0.52 | 1.53 | 4.3529 | 1.1378 | 1.9778 | 1 | 1743.1961 | 144.1167 | 9.3653e-05 | 1.5449e-06 | 2 | 3030 | 7.7247e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.0561 | 1.1378 | 1.9778
| CM22 | United Energy Feeder | URBAN | 399.5 | 1.59 | 0.13 | 1.72 | 1.3244 | 0.22795 | 0 | 1 | 11361.9728 | 834.7 | 0.00061256 | 6.1798e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.48089 | 0.22795 | 0
| CM23 | United Energy Feeder | URBAN | 46.5 | 0.04 | 1.58 | 1.62 | 3.108 | 1.0728 | 0 | 1 | 2531.8757 | 0 | 0.00014584 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1822 | 1.0728 | 0
| CM24 | United Energy Feeder | URBAN | 257.5 | 1.07 | 1.07 | 2.14 | 4.0883 | 0.89831 | 0 | 1 | 8235.259 | 0 | 0.00047436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.6853 | 0.89831 | 0
| CM25 | United Energy Feeder | URBAN | 1198 | 3.81 | 1.06 | 4.87 | 3.619 | 0.77953 | 1.9569 | 2 | 32294.8682 | 979.5631 | 0.0018182 | 1.4414e-05 | 1 | 81070 | 0.00030435 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.735 | 0.77953 | 1.9569
| CRM11 | United Energy Feeder | URBAN | 4.5 | 2.31 | 0.87 | 3.18 | 15.6816 | 82.2696 | 0 | 3 | 3521.7332 | 3521.7332 | 1.8539e-05 | 1.8539e-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 6.3073 | 82.2696 | 0
| CRM12 | United Energy Feeder | URBAN | 3184 | 9.43 | 3.19 | 12.62 | 6.5648 | 6.9349 | 4.1632 | 7 | 553066.8106 | 553066.8106 | 0.0036865 | 0.0036865 | 0 | 332023 | 0.001511 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 2.3954 | 6.9349 | 4.1632
| CRM13 | United Energy Feeder | URBAN | 755 | 13.28 | 2.21 | 15.49 | 8.6243 | 1.0152 | 3.4734 | 6 | 17681.0606 | 17681.0606 | 0.00024067 | 0.00024067 | 0 | 60495 | 0.00020702 | 2 | 0 | 0.0027933 | 0.0027933 | 0 | 0 | no | no | 2.601 | 1.0152 | 3.4734
| CRM14 | United Energy Feeder | URBAN | 4050.5 | 17.72 | 8.23 | 25.95 | 9.7334 | 5.3211 | 0.70574 | 8 | 382339.4789 | 363179.3433 | 0.0068028 | 0.0066978 | 0 | 50710 | 0.00028427 | 1 | 0 | 0.0062972 | 0.0062972 | 4.6348e-06 | 4.6348e-06 | no | no | 3.3823 | 5.3211 | 0.70574
| CRM21 | United Energy Feeder | URBAN | 4746 | 19.77 | 11.91 | 31.68 | 12.358 | 5.381 | 0.97725 | 7 | 427864.412 | 427864.412 | 0.013344 | 0.013344 | 3 | 77705 | 0.00028736 | 1 | 0 | 0.0062617 | 0.0062617 | 0 | 0 | no | no | 3.5813 | 5.381 | 0.97725
| CRM22 | United Energy Feeder | URBAN | 4033.5 | 10.19 | 3.59 | 13.78 | 11.0061 | 8.9028 | 6.2626 | 18 | 727164.9187 | 726956.852 | 0.012484 | 0.012482 | 0 | 511518 | 0.0023221 | 1 | 0 | 0.0061628 | 0.0061628 | 0 | 0 | yes | no | 2.963 | 8.9028 | 6.2626
| CRM24 | United Energy Feeder | URBAN | 1829 | 3.74 | 3.82 | 7.56 | 4.9155 | 6.2417 | 0.14337 | 5 | 422520.4746 | 422520.4746 | 0.010609 | 0.010609 | 15 | 9705 | 0.00012978 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.6211 | 6.2417 | 0.14337
| CRM32 | United Energy Feeder | URBAN | 0.5 | 0.09 | 2.92 | 3.01 | 7.582 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.9323 | 0 | 0
| CRM33 | United Energy Feeder | URBAN | 2566.5 | 10.51 | 1.86 | 12.37 | 8.1378 | 10.6698 | 4.8218 | 8 | 731897.8672 | 730424.2839 | 0.0098567 | 0.0098551 | 2 | 330756 | 0.0020687 | 0 | 1 | 0 | 0 | 0.0016562 | 0.0016562 | yes | no | 2.2449 | 10.6698 | 4.8218
| CRM34 | United Energy Feeder | URBAN | 337.5 | 4.73 | 9.32 | 14.05 | 4.635 | 0 | 0.21264 | 0 | 0 | 0 | 0 | 0 | 1 | 2190 | 6.1798e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.9661 | 0 | 0.21264
| CRM35 | United Energy Feeder | URBAN | 3726.5 | 28.78 | 5.1 | 33.88 | 11.5203 | 11.95 | 16.2821 | 19 | 548968.0611 | 547973.4444 | 0.0089526 | 0.0089496 | 5 | 747977 | 0.0031084 | 1 | 2 | 0.0057951 | 0.0057951 | 0.0029957 | 0.0029957 | yes | no | 4.8671 | 11.95 | 16.2821
| DC1 | United Energy Feeder | URBAN | 2285 | 18.3 | 6.15 | 24.45 | 10.0663 | 5.1286 | 2.1857 | 12 | 195969.8262 | 195862.6595 | 0.0024792 | 0.0024777 | 6 | 83516 | 0.00047121 | 1 | 6 | 0.0035055 | 0.0035055 | 0.0085667 | 0.0085667 | no | no | 3.588 | 5.1286 | 2.1857
| DC10 | United Energy Feeder | URBAN | 3682.5 | 14.21 | 4.32 | 18.53 | 8.296 | 3.955 | 3.2692 | 12 | 357081.6159 | 349046.0498 | 0.0060395 | 0.0060074 | 21 | 295167 | 0.00046812 | 1 | 0 | 0.0055788 | 0.0055788 | 0 | 0 | no | no | 2.4472 | 3.955 | 3.2692
| DC12 | United Energy Feeder | URBAN | 1435 | 4.07 | 1.61 | 5.68 | 7.0713 | 6.3864 | 14.1217 | 2 | 175450.4403 | 174476.7236 | 0.0076276 | 0.0076261 | 2 | 387959 | 0.0018122 | 2 | 0 | 0.0045545 | 0.0045545 | 0 | 0 | yes | no | 3.134 | 6.3864 | 14.1217
| DC2 | United Energy Feeder | URBAN | 3963 | 13.88 | 10.77 | 24.65 | 10.5971 | 7.2902 | 3.8958 | 16 | 534770.0213 | 534151.3546 | 0.019003 | 0.019002 | 0 | 285779 | 0.0015295 | 1 | 2 | 0.0060717 | 0.0060717 | 0.0052281 | 0.0052281 | no | no | 3.2415 | 7.2902 | 3.8958
| DC3 | United Energy Feeder | URBAN | 3902.5 | 13.82 | 10.74 | 24.56 | 10.3707 | 8.9839 | 6.3969 | 18 | 627244.0554 | 627244.0554 | 0.0211 | 0.0211 | 14 | 446624 | 0.002285 | 0 | 4 | 0 | 0 | 0.0087738 | 0.0087738 | yes | no | 3.3537 | 8.9839 | 6.3969
| DC4 | United Energy Feeder | URBAN | 3130 | 11.17 | 2.62 | 13.79 | 8.5226 | 8.2975 | 0.82579 | 7 | 468786.316 | 468786.316 | 0.0099282 | 0.0099282 | 2 | 46655 | 0.00029354 | 1 | 1 | 0.0046503 | 0.0046503 | 0.0030575 | 0.0030575 | no | no | 3.3241 | 8.2975 | 0.82579
| DC5 | United Energy Feeder | URBAN | 4471 | 13.79 | 2.58 | 16.37 | 11.0069 | 5.7281 | 4.3223 | 15 | 419153.2128 | 417757.6558 | 0.0071109 | 0.0070956 | 18 | 316280 | 0.0014801 | 2 | 0 | 0.013698 | 0.013698 | 0 | 0 | no | no | 3.666 | 5.7281 | 4.3223
| DC6 | United Energy Feeder | URBAN | 2322 | 4.47 | 2.46 | 6.93 | 5.8976 | 3.2132 | 7.7967 | 4 | 203311.8225 | 197681.3837 | 0.0037325 | 0.0036947 | 22 | 493322 | 0.0018014 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 2.2019 | 3.2132 | 7.7967
| DC7 | United Energy Feeder | URBAN | 1443 | 5.52 | 1.98 | 7.5 | 6.6442 | 0.28525 | 0.054099 | 4 | 9781.0746 | 9781.0746 | 8.6239e-05 | 8.6239e-05 | 8 | 1855 | 1.0815e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.525 | 0.28525 | 0.054099
| DC8 | United Energy Feeder | URBAN | 2309 | 11.15 | 1.02 | 12.17 | 5.7786 | 9.014 | 3.3701 | 6 | 527245.9383 | 250500.9383 | 0.0088054 | 0.006199 | 12 | 197125 | 0.00080492 | 2 | 1 | 0.0071284 | 0.0071284 | 0.0028767 | 0.0028767 | yes | no | 2.3685 | 9.014 | 3.3701
| DMA11 | United Energy Feeder | URBAN | 3194.5 | 13.9 | 1.64 | 15.54 | 5.5601 | 1.6901 | 0.37222 | 7 | 227489.3802 | 72537.6372 | 0.01048 | 0.0003304 | 27 | 50100 | 0.00022711 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.424 | 1.6901 | 0.37222
| DMA12 | United Energy Feeder | URBAN | 4513 | 21.78 | 10.52 | 32.3 | 12.361 | 3.4506 | 1.8077 | 19 | 302629.7939 | 58290.7171 | 0.016145 | 0.000629 | 72 | 158539 | 0.00086517 | 5 | 2 | 0.03729 | 0.03729 | 0.003524 | 0.003524 | no | yes | 3.0875 | 3.4506 | 1.8077
| DMA13 | United Energy Feeder | RURAL SHORT | 3158 | 168.28 | 7.16 | 175.44 | 7.1135 | 31.0738 | 6.1075 | 63 | 1650037.7803 | 1386737.2144 | 0.039669 | 0.029267 | 7 | 324314 | 0.0019065 | 4 | 26 | 0.021575 | 0.021575 | 0.045411 | 0.044073 | yes | yes | 3.5683 | 31.0738 | 6.1075
| DMA14 | United Energy Feeder | URBAN | 2818 | 15.93 | 1.41 | 17.34 | 7.0855 | 20.2175 | 4.2752 | 15 | 1472632.8915 | 1350901.0561 | 0.015344 | 0.0074834 | 11 | 311400 | 0.0012236 | 9 | 3 | 0.037 | 0.037 | 0.0063111 | 0.0063111 | yes | yes | 2.3213 | 20.2175 | 4.2752
| DMA15 | United Energy Feeder | RURAL SHORT | 1742.5 | 41.46 | 7.67 | 49.13 | 5.2701 | 1.712 | 1.7608 | 21 | 113076.4099 | 30392.5346 | 0.005762 | 0.00035174 | 11 | 116295 | 0.00061798 | 4 | 1 | 0.010526 | 0.010526 | 0.0083597 | 0.0083597 | no | no | 1.5829 | 1.712 | 1.7608
| DN10 | United Energy Feeder | URBAN | 3349.5 | 5.89 | 10.82 | 16.71 | 5.6468 | 0.92436 | 1.093 | 7 | 107906.943 | 43142.5031 | 0.0057848 | 0.00052074 | 1 | 127592 | 0.00072149 | 2 | 0 | 0.0097424 | 0.0048697 | 0 | 0 | no | no | 1.7216 | 0.92436 | 1.093
| DN11 | United Energy Feeder | URBAN | 2432.5 | 9.06 | 0.7 | 9.76 | 9.172 | 4.233 | 0.067967 | 5 | 549309.326 | 522157.4933 | 0.011083 | 0.00737 | 7 | 8820 | 3.2444e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1247 | 4.233 | 0.067967
| DN13 | United Energy Feeder | URBAN | 4277.5 | 7.77 | 17.7 | 25.47 | 8.3928 | 0.57387 | 0.41101 | 8 | 97886.2621 | 50232.3836 | 0.0067072 | 0.00023922 | 4 | 70107 | 0.00043104 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5046 | 0.57387 | 0.41101
| DN2 | United Energy Feeder | URBAN | 70.5 | 4.31 | 0.55 | 4.86 | 10.9294 | 0.7861 | 5.7273 | 2 | 952.5413 | 144.05 | 0.00011211 | 1.5449e-06 | 16 | 6940 | 4.1714e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.4909 | 0.7861 | 5.7273
| DN21 | United Energy Feeder | URBAN | 479.5 | 5.8 | 3.21 | 9.01 | 8.167 | 0.59435 | 0.13452 | 3 | 7038.4033 | 873.6572 | 0.00087811 | 3.507e-05 | 43 | 1593 | 1.5449e-05 | 3 | 0 | 0.0025353 | 0.0025353 | 0 | 0 | no | no | 2.4295 | 0.59435 | 0.13452
| DN22 | United Energy Feeder | URBAN | 4410 | 8.18 | 13.57 | 21.75 | 9.8856 | 4.9918 | 0.26706 | 9 | 411120.5711 | 362128.2443 | 0.013906 | 0.0072066 | 7 | 21995 | 0.0001375 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.2128 | 4.9918 | 0.26706
| DN24 | United Energy Feeder | URBAN | 192.5 | 6.78 | 3.47 | 10.25 | 6.524 | 2.6275 | 0.80445 | 4 | 24366.2134 | 3948.3184 | 0.00049101 | 9.7332e-05 | 19 | 7460 | 6.7978e-05 | 2 | 0 | 0.00037851 | 0.00037851 | 1.5449e-06 | 0 | no | no | 1.2455 | 2.6275 | 0.80445
| DN25 | United Energy Feeder | URBAN | 933 | 8.07 | 1.77 | 9.84 | 6.8606 | 17.8056 | 0.078575 | 9 | 433952.7738 | 416032.0559 | 0.0045821 | 0.0030376 | 10 | 1915 | 4.7893e-05 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 2.2969 | 17.8056 | 0.078575
| DN4 | United Energy Feeder | URBAN | 373.5 | 6.71 | 1.23 | 7.94 | 6.838 | 0.25652 | 13.2446 | 5 | 2964.4372 | 1246.3932 | 0.00024618 | 1.1232e-05 | 1 | 153060 | 0.00044804 | 1 | 0 | 0.00086826 | 0.00086826 | 0 | 0 | yes | no | 1.9392 | 0.25652 | 13.2446
| DN6 | United Energy Feeder | URBAN | 1010 | 5.88 | 0.99 | 6.87 | 5.9949 | 2.2914 | 2.8102 | 2 | 65841.0679 | 55061.1839 | 0.0030516 | 0.0015774 | 8 | 80749 | 0.00028582 | 1 | 0 | 0.0015434 | 0.0015434 | 0 | 0 | no | no | 2.109 | 2.2914 | 2.8102
| DN7 | United Energy Feeder | URBAN | 838 | 4.44 | 3.32 | 7.76 | 9.8239 | 8.4743 | 0.48972 | 3 | 142760.2322 | 133047.1076 | 0.0035098 | 0.0021815 | 3 | 8250 | 3.7079e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.9846 | 8.4743 | 0.48972
| DN8 | United Energy Feeder | URBAN | 189.5 | 2.12 | 6.18 | 8.3 | 6.1496 | 0.75375 | 1.6338 | 2 | 3909.075 | 899.6907 | 0.0004192 | 7.6629e-06 | 3 | 8473 | 3.5534e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.1924 | 0.75375 | 1.6338
| DN9 | United Energy Feeder | URBAN | 91.5 | 5.37 | 1.96 | 7.33 | 6.9463 | 4.5562 | 3.1167 | 4 | 6797.6436 | 5820.7166 | 0.00027519 | 0.00014159 | 2 | 4650 | 4.7893e-05 | 2 | 0 | 0.00026419 | 0.00026419 | 0 | 0 | no | no | 3.6797 | 4.5562 | 3.1167
| DSH13 | United Energy Feeder | URBAN | 1 | 0 | 0.53 | 0.53 | 11.4278 | 1.1849 | 0 | 1 | 11.229 | 0 | 1.5356e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 6.3312 | 1.1849 | 0
| DSH14 | United Energy Feeder | URBAN | 143 | 2.87 | 2.11 | 4.98 | 6.3699 | 2.5687 | 5.2988 | 4 | 9123.3288 | 4887.8667 | 0.00045599 | 1.8539e-05 | 4 | 18820 | 5.0983e-05 | 1 | 0 | 0.00021938 | 0.00021938 | 0 | 0 | no | no | 2.4157 | 2.5687 | 5.2988
| DSH21 | United Energy Feeder | URBAN | 216 | 4.2 | 2.29 | 6.49 | 10.2662 | 20.1965 | 0.48556 | 4 | 47833.2974 | 45419.0526 | 0.00045375 | 0.0001236 | 2 | 1150 | 4.6348e-06 | 1 | 0 | 0.0003059 | 0.0003059 | 0 | 0 | no | no | -5.4721 | 20.1965 | 0.48556
| DSH22 | United Energy Feeder | URBAN | 12 | 1.8 | 0.42 | 2.22 | 6.0602 | 6.4234 | 0 | 2 | 1382.7105 | 1236.7329 | 4.0047e-05 | 2.0084e-05 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | -3.3448 | 6.4234 | 0
| DSH23 | United Energy Feeder | URBAN | 164.5 | 2.78 | 0.11 | 2.89 | 3.4173 | 0.29896 | 0 | 1 | 2042.7373 | 88.8833 | 0.00026874 | 1.5449e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | -1.4445 | 0.29896 | 0
| DSH24 | United Energy Feeder | URBAN | 3546.5 | 11.74 | 5.12 | 16.86 | 7.4832 | 28.0869 | 0.5641 | 15 | 1878961.3526 | 671153.838 | 0.028517 | 0.011805 | 4 | 37737 | 0.0001823 | 1 | 2 | 0.0059511 | 0.0059511 | 0.0046704 | 0.0046688 | yes | no | 3.1808 | 28.0869 | 0.5641
| DSH31 | United Energy Feeder | URBAN | 41 | 2.93 | 0.71 | 3.64 | 5.5285 | 1.3242 | 5.4831 | 3 | 1498.5436 | 1049.3818 | 6.9659e-05 | 8.2346e-06 | 2 | 6205 | 2.6264e-05 | 1 | 0 | 5.8708e-05 | 5.8708e-05 | 0 | 0 | no | no | 2.1738 | 1.3242 | 5.4831
| DSH32 | United Energy Feeder | URBAN | 182 | 4.6 | 1.07 | 5.67 | 8.1458 | 31.5098 | 0.92848 | 4 | 100113.9689 | 22921.3167 | 0.0006054 | 2.7809e-05 | 1 | 2950 | 1.5449e-05 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 3.437 | 31.5098 | 0.92848
| DSH33 | United Energy Feeder | URBAN | 174.5 | 3.46 | 8.64 | 12.1 | 14.5332 | 12.2393 | 29.325 | 3 | 19746.1525 | 17983.1923 | 0.00032388 | 8.2794e-05 | 0 | 47311 | 0.00016685 | 3 | 0 | 0.00081264 | 0.00081264 | 0 | 0 | yes | no | -6.4897 | 12.2393 | 29.325
| DSH34 | United Energy Feeder | URBAN | 318 | 3.92 | 2.59 | 6.51 | 3.0616 | 0.4345 | 0.18972 | 3 | 5129.9501 | 1592.8007 | 0.00053488 | 5.1169e-05 | 2 | 2240 | 6.1798e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.616 | 0.4345 | 0.18972
| DVY13 | United Energy Feeder | URBAN | 80.5 | 2.79 | 1.56 | 4.35 | 10.2418 | 0.97885 | 0 | 1 | 932.0108 | 0 | 0.00012745 | 0 | 2 | 0 | 0 | 1 | 0 | 0.00012823 | 0.00012823 | 0 | 0 | no | no | 5.0727 | 0.97885 | 0
| DVY14 | United Energy Feeder | URBAN | 103.5 | 2.12 | 2.01 | 4.13 | 9.2727 | 0.79258 | 10.0485 | 2 | 1126.3412 | 239.2466 | 0.00012657 | 5.2528e-06 | 0 | 14280 | 4.3259e-05 | 1 | 0 | 0.00012205 | 0.00012205 | 0 | 0 | no | no | 4.3698 | 0.79258 | 10.0485
| DVY21 | United Energy Feeder | URBAN | 157.5 | 4.54 | 4.12 | 8.66 | 10.4231 | 10.6611 | 0.11356 | 4 | 24127.3635 | 22285.8 | 0.00069524 | 0.0004434 | 0 | 257 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.1756 | 10.6611 | 0.11356
| DVY22 | United Energy Feeder | URBAN | 167 | 3.54 | 1.82 | 5.36 | 9.5858 | 0.87829 | 2.2082 | 1 | 1841.5635 | 0 | 0.00025184 | 0 | 5 | 4630 | 1.6994e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.7788 | 0.87829 | 2.2082
| DVY23 | United Energy Feeder | RURAL SHORT | 84 | 2.8 | 1.69 | 4.49 | 0 | 0.58602 | 0 | 3 | 2654.9205 | 757.2118 | 0.00027126 | 1.1742e-05 | 4 | 0 | 0 | 1 | 0 | 0.00025955 | 0.00025955 | 0 | 0 | no | no | 1.1125 | 0.58602 | 0
| DVY24 | United Energy Feeder | RURAL SHORT | 1250 | 24.82 | 13.47 | 38.29 | 9.0263 | 37.2592 | 0.64816 | 12 | 600427.8942 | 119535.0739 | 0.010868 | 0.0039565 | 1 | 10445 | 5.4073e-05 | 2 | 3 | 0.0038145 | 0.0038145 | 0.0027562 | 0.0015712 | no | no | 4.6541 | 37.2592 | 0.64816
| DVY31 | United Energy Feeder | URBAN | 266.5 | 2.14 | 2.25 | 4.39 | 11.0823 | 0.86274 | 0.016112 | 2 | 3748.2643 | 1581.0585 | 0.00030658 | 1.0212e-05 | 2 | 70 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.6804 | 0.86274 | 0.016112
| DVY32 | United Energy Feeder | URBAN | 143 | 3.56 | 2.33 | 5.89 | 6.6834 | 1.6283 | 0.23242 | 3 | 6725.6242 | 5176.0159 | 0.00026444 | 5.2528e-05 | 9 | 960 | 6.1798e-06 | 2 | 0 | 0.00041714 | 0.00041714 | 0 | 0 | no | no | 2.0772 | 1.6283 | 0.23242
| DVY33 | United Energy Feeder | URBAN | 94.5 | 1.98 | 3.03 | 5.01 | 9.1292 | 10.9189 | 0 | 4 | 18457.97 | 17638.2497 | 0.00042881 | 0.00031671 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.3541 | 10.9189 | 0
| DVY34 | United Energy Feeder | URBAN | 662 | 19.52 | 5.93 | 25.45 | 9.8954 | 42.991 | 1.0596 | 9 | 428421.5986 | 191991.8451 | 0.003041 | 0.00084767 | 0 | 10559 | 6.3343e-05 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 3.9858 | 42.991 | 1.0596
| EB11 | United Energy Feeder | URBAN | 1241 | 4.26 | 1.8 | 6.06 | 8.0281 | 1.1532 | 1.7427 | 2 | 28050.4924 | 821.0334 | 0.0019292 | 1.3905e-05 | 3 | 42390 | 0.00024256 | 0 | 1 | 0 | 0 | 0.00060871 | 0.00060871 | no | no | 3.0611 | 1.1532 | 1.7427
| EB12 | United Energy Feeder | URBAN | 1783.5 | 8.31 | 0.34 | 8.65 | 3.8971 | 3.7501 | 1.9701 | 2 | 352000.9834 | 1292.3167 | 0.0056206 | 1.3905e-05 | 1 | 184920 | 0.0009177 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.1401 | 3.7501 | 1.9701
| EB13 | United Energy Feeder | URBAN | 516.5 | 3.55 | 2.33 | 5.88 | 5.4874 | 3.3017 | 1.4314 | 3 | 36421.3932 | 25049.3562 | 0.0016046 | 0.0008047 | 2 | 15790 | 0.00010197 | 1 | 0 | 0.00077247 | 0.00077247 | 0 | 0 | no | no | 2.8094 | 3.3017 | 1.4314
| EB14 | United Energy Feeder | URBAN | 2064 | 6.88 | 1.41 | 8.29 | 4.092 | 1.1452 | 0.21605 | 3 | 118362.5744 | 72081.5554 | 0.006451 | 0.0031956 | 0 | 22330 | 8.0337e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1982 | 1.1452 | 0.21605
| EB21 | United Energy Feeder | URBAN | 1281 | 6.53 | 0.83 | 7.36 | 4.1309 | 1.1308 | 0.31765 | 3 | 48700.0647 | 15408.2 | 0.0024381 | 0.00029663 | 7 | 13680 | 5.8708e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.7847 | 1.1308 | 0.31765
| EB22 | United Energy Feeder | URBAN | 1910 | 8.23 | 0.39 | 8.62 | 7.5268 | 2.6144 | 6.9131 | 5 | 125655.5356 | 82274.1595 | 0.0063048 | 0.0032534 | 1 | 332265 | 0.0012452 | 1 | 0 | 0.002957 | 0.002957 | 0 | 0 | no | no | 2.3844 | 2.6144 | 6.9131
| EB23 | United Energy Feeder | URBAN | 441.5 | 2.65 | 2.17 | 4.82 | 7.5837 | 22.8151 | 0 | 2 | 138213.2819 | 0 | 0.0013982 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | yes | no | 4.3727 | 22.8151 | 0
| EB24 | United Energy Feeder | URBAN | 1038.5 | 2.98 | 0.81 | 3.79 | 2.5331 | 0.92255 | 0 | 6 | 71020.7789 | 19597.5047 | 0.0020304 | 0.0002621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.8094 | 0.92255 | 0
| EB31 | United Energy Feeder | URBAN | 1956 | 6.35 | 3.58 | 9.93 | 6.7496 | 1.5598 | 2.4431 | 4 | 58598.4799 | 13540.8198 | 0.0033266 | 0.00018116 | 5 | 91780 | 0.00034761 | 1 | 2 | 0.0030497 | 0 | 0.0039829 | 0.0039829 | no | no | 3.124 | 1.5598 | 2.4431
| EB32 | United Energy Feeder | URBAN | 3737.5 | 19.12 | 1.97 | 21.09 | 8.2619 | 7.3176 | 2.7347 | 15 | 644646.9798 | 560217.534 | 0.030649 | 0.024711 | 1 | 240915 | 0.00090843 | 1 | 0 | 0.0057534 | 0.0057534 | 0 | 0 | no | no | 2.5455 | 7.3176 | 2.7347
| EB33 | United Energy Feeder | URBAN | 2468 | 7.95 | 1.7 | 9.65 | 7.7865 | 2.5905 | 0 | 7 | 141132.0689 | 85631.0917 | 0.0083556 | 0.0044517 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.7181 | 2.5905 | 0
| EL10 | United Energy Feeder | URBAN | 1307.5 | 2.37 | 1 | 3.37 | 3.7383 | 6.7746 | 0.17087 | 2 | 343827.1769 | 343827.1769 | 0.0021034 | 0.0021034 | 3 | 8672 | 4.9438e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5457 | 6.7746 | 0.17087
| EL11 | United Energy Feeder | URBAN | 209 | 2.6 | 0.05 | 2.65 | 4.346 | 1.2917 | 0.40256 | 3 | 14727.4709 | 14727.4709 | 5.2049e-05 | 5.2049e-05 | 2 | 4590 | 2.6264e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0998 | 1.2917 | 0.40256
| EL12 | United Energy Feeder | URBAN | 283 | 0.53 | 0.82 | 1.35 | 2.9256 | 0.47369 | 0.02466 | 1 | 8644.1433 | 8644.1433 | 6.9399e-05 | 6.9399e-05 | 1 | 450 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.93049 | 0.47369 | 0.02466
| EL13 | United Energy Feeder | URBAN | 1105.5 | 3.39 | 0.42 | 3.81 | 3.3237 | 1.9114 | 0.015884 | 2 | 96268.7094 | 612.8666 | 0.0018077 | 7.7247e-06 | 6 | 800 | 3.0899e-06 | 1 | 0 | 0.0017643 | 0 | 0 | 0 | no | no | 1.317 | 1.9114 | 0.015884
| EL14 | United Energy Feeder | URBAN | 1150.5 | 2.92 | 0.96 | 3.88 | 3.7706 | 0.49296 | 0.85532 | 4 | 28489.5763 | 28489.5763 | 0.00045907 | 0.00045907 | 0 | 49431.6 | 0.00042795 | 1 | 0 | 0.0015048 | 0.0015048 | 0 | 0 | no | no | 1.1944 | 0.49296 | 0.85532
| EL5 | United Energy Feeder | URBAN | 838 | 1.09 | 3.44 | 4.53 | 2.5043 | 0.015158 | 0 | 0 | 865.3334 | 865.3334 | 7.7247e-06 | 7.7247e-06 | 0 | 0 | 0 | 1 | 0 | 0.0013534 | 0.0013534 | 0 | 0 | no | no | 0.88078 | 0.015158 | 0
| EL6 | United Energy Feeder | URBAN | 1514 | 3.67 | 0.25 | 3.92 | 3.6013 | 0.12624 | 2.0031 | 3 | 11547.2809 | 11547.2809 | 0.00018317 | 0.00018317 | 5 | 183230 | 0.00074621 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.99307 | 0.12624 | 2.0031
| EL7 | United Energy Feeder | URBAN | 327.5 | 1.2 | 1.34 | 2.54 | 2.0849 | 0.28815 | 0 | 2 | 10384.1158 | 10384.1158 | 8.2624e-05 | 8.2624e-05 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.54528 | 0.28815 | 0
| EL8 | United Energy Feeder | URBAN | 1339 | 3.46 | 0.21 | 3.67 | 3.386 | 0.0679 | 0.052407 | 1 | 4955.7925 | 4333.1425 | 3.6337e-05 | 3.4792e-05 | 0 | 3825 | 6.9523e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1007 | 0.0679 | 0.052407
| EL9 | United Energy Feeder | URBAN | 809.5 | 2.3 | 1.3 | 3.6 | 3.6404 | 0.1489 | 0.12779 | 2 | 7136.8549 | 5161.4316 | 6.8379e-05 | 3.728e-05 | 1 | 6125 | 3.8624e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0133 | 0.1489 | 0.12779
| EM1 | United Energy Feeder | URBAN | 1860 | 3.88 | 0.55 | 4.43 | 3.0026 | 0.065805 | 0.7256 | 1 | 5827.7334 | 5827.7334 | 0.00055 | 0.00055 | 1 | 64260 | 0.00023638 | 1 | 0 | 0.0028891 | 0.0028891 | 0 | 0 | no | no | 1.2601 | 0.065805 | 0.7256
| EM10 | United Energy Feeder | URBAN | 1966.5 | 4.52 | 0.49 | 5.01 | 3.5153 | 0.025639 | 0.70841 | 0 | 1955.4833 | 1751.0833 | 2.0084e-05 | 1.8539e-05 | 1 | 54030 | 0.00021938 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.547 | 0.025639 | 0.70841
| EM11 | United Energy Feeder | URBAN | 948.5 | 3.71 | 1.25 | 4.96 | 3.1056 | 0.069369 | 0.50371 | 1 | 3212.9199 | 3212.9199 | 0.00011141 | 0.00011141 | 1 | 23330 | 0.00021011 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2287 | 0.069369 | 0.50371
| EM2 | United Energy Feeder | URBAN | 598 | 3.44 | 1.09 | 4.53 | 4.9623 | 2.319 | 3.5806 | 2 | 40937.5301 | 40937.5301 | 0.00018107 | 0.00018107 | 7 | 63210 | 0.00024719 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.0325 | 2.319 | 3.5806
| EM3 | United Energy Feeder | URBAN | 364 | 1.51 | 0.76 | 2.27 | 4.0182 | 4.3193 | 0 | 1 | 63603.7 | 157.15 | 0.00055618 | 3.0899e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4831 | 4.3193 | 0
| EM5 | United Energy Feeder | URBAN | 1299 | 3.86 | 0.55 | 4.41 | 3.747 | 0.78517 | 0.40882 | 2 | 48168.2258 | 48168.2258 | 0.0020704 | 0.0020704 | 3 | 25080 | 0.00029354 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2705 | 0.78517 | 0.40882
| EM6 | United Energy Feeder | URBAN | 1531 | 2.99 | 0.63 | 3.62 | 4.8019 | 1.9333 | 0.32632 | 12 | 142724.828 | 134755.2078 | 0.0026116 | 0.002475 | 0 | 24090 | 0.00010197 | 1 | 0 | 0.0020084 | 0.0020084 | 0 | 0 | no | no | 1.2443 | 1.9333 | 0.32632
| EM7 | United Energy Feeder | URBAN | 1251 | 5.57 | 1.11 | 6.68 | 3.8763 | 0.10228 | 0.81244 | 2 | 5377.6873 | 5377.6873 | 0.0001036 | 0.0001036 | 1 | 42715 | 0.00052837 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4277 | 0.10228 | 0.81244
| EM8 | United Energy Feeder | URBAN | 1443 | 4.96 | 0.71 | 5.67 | 4.0636 | 0.24969 | 4.6141 | 3 | 18079.3987 | 18079.3987 | 0.0022816 | 0.0022816 | 1 | 334095 | 0.0015635 | 2 | 0 | 0.0042301 | 0.0042301 | 0 | 0 | no | no | 1.1957 | 0.24969 | 4.6141
| EM9 | United Energy Feeder | URBAN | 1141 | 3.28 | 0.83 | 4.11 | 3.0647 | 0.021048 | 0.81765 | 0 | 1389.3001 | 1389.3001 | 9.2697e-06 | 9.2697e-06 | 1 | 53970 | 0.00039705 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0372 | 0.021048 | 0.81765
| EW1 | United Energy Feeder | URBAN | 2954 | 3.23 | 2.69 | 5.92 | 4.6262 | 1.7084 | 0 | 8 | 129082.194 | 128819.3773 | 0.0019193 | 0.0019177 | 2 | 0 | 0 | 0 | 3 | 0 | 0 | 0.006977 | 0.006977 | no | no | 2.3458 | 1.7084 | 0
| EW12 | United Energy Feeder | URBAN | 2796.5 | 3.91 | 1.05 | 4.96 | 4.1348 | 3.886 | 0.91185 | 6 | 400784.4178 | 400784.4178 | 0.0049221 | 0.0049221 | 4 | 94045 | 0.00057318 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.6269 | 3.886 | 0.91185
| EW14 | United Energy Feeder | URBAN | 1722 | 4.29 | 2.98 | 7.27 | 4.742 | 2.4549 | 2.9949 | 6 | 182841.6309 | 46320.6752 | 0.0038383 | 0.00077312 | 3 | 223060 | 0.0018617 | 1 | 0 | 0.0025631 | 0.0025631 | 0 | 0 | no | no | 1.3872 | 2.4549 | 2.9949
| EW2 | United Energy Feeder | URBAN | 2291.5 | 2.94 | 0.85 | 3.79 | 3.7288 | 4.4741 | 0.65667 | 16 | 465044.3678 | 238574.2572 | 0.0080462 | 0.0044063 | 0 | 68255 | 0.00028891 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3228 | 4.4741 | 0.65667
| EW3 | United Energy Feeder | URBAN | 1088.5 | 2.15 | 0.99 | 3.14 | 2.5534 | 0.28246 | 0.77673 | 4 | 17902.9538 | 14745.1836 | 0.00013056 | 0.00011986 | 4 | 49230 | 0.00020857 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0304 | 0.28246 | 0.77673
| EW8 | United Energy Feeder | URBAN | 1647 | 1.62 | 2.08 | 3.7 | 1.9252 | 0.82794 | 0.051653 | 1 | 103867.8168 | 103867.8168 | 0.000292 | 0.000292 | 1 | 6480 | 4.1714e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.7877 | 0.82794 | 0.051653
| EW9 | United Energy Feeder | URBAN | 2629.5 | 2.32 | 1.55 | 3.87 | 3.5058 | 2.0885 | 1.6664 | 11 | 191236.754 | 56284.4603 | 0.0011455 | 0.00085349 | 3 | 152580 | 0.0004882 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.723 | 2.0885 | 1.6664
| FGY21 | SPAusnet Feeder | URBAN | 127.5 | 0.13 | 1.43 | 1.56 | 0 | 0 | 0 | 0 | 337.3667 | 0 | 1.5449e-06 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| FGY31 | SPAusnet Feeder | URBAN | 26 | 0.52 | 0.05 | 0.57 | 0 | 0 | 0 | 1 | 1177.7842 | 1177.7842 | 4.3259e-05 | 4.3259e-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| FSH11 | United Energy Feeder | URBAN | 2443.5 | 10.19 | 2.25 | 12.44 | 8.5251 | 11.0793 | 1.8212 | 8 | 412318.696 | 406593.3215 | 0.012894 | 0.0091561 | 0 | 67777 | 0.00037079 | 1 | 0 | 0.0037195 | 0.0037195 | 0 | 0 | no | no | 3.9395 | 11.0793 | 1.8212
| FSH12 | United Energy Feeder | URBAN | 1893 | 20.12 | 4.44 | 24.56 | 9.0453 | 0.58945 | 1.1659 | 5 | 37155.0314 | 33332.5254 | 0.0050332 | 0.0026264 | 4 | 73491 | 0.00029354 | 1 | 1 | 0.0023931 | 0.0023931 | 0.00096096 | 0.00096096 | no | no | 1.8019 | 0.58945 | 1.1659
| FSH13 | United Energy Feeder | URBAN | 3263 | 25.14 | 2.2 | 27.34 | 8.8961 | 13.2329 | 1.3148 | 14 | 869445.506 | 541950.5122 | 0.017446 | 0.0094535 | 15 | 86390 | 0.00042641 | 2 | 1 | 0.0099047 | 0.0099047 | 0.0030235 | 0.0030219 | yes | no | 2.9798 | 13.2329 | 1.3148
| FSH21 | United Energy Feeder | RURAL SHORT | 2018.5 | 20.21 | 3.01 | 23.22 | 4.5112 | 2.1801 | 1.4127 | 8 | 178491.4135 | 173848.0628 | 0.0092273 | 0.0061528 | 1 | 115660 | 0.00071377 | 5 | 0 | 0.016661 | 0.016661 | 0 | 0 | no | no | 1.4792 | 2.1801 | 1.4127
| FSH22 | United Energy Feeder | URBAN | 2359.5 | 8.71 | 3.15 | 11.86 | 8.6086 | 5.9132 | 0.78421 | 8 | 293712.5707 | 287855.7145 | 0.011806 | 0.0082109 | 2 | 38952.5 | 0.00023792 | 1 | 0 | 0.0035773 | 0.0035773 | 0 | 0 | no | no | 2.8502 | 5.9132 | 0.78421
| FSH23 | United Energy Feeder | URBAN | 1198 | 16.75 | 3.94 | 20.69 | 8.8464 | 1.3348 | 2.3402 | 5 | 23899.5084 | 21111.1529 | 0.0037184 | 0.0018722 | 1 | 41900 | 0.0001375 | 2 | 0 | 0.0036333 | 0.0036333 | 0 | 0 | no | no | 4.0146 | 1.3348 | 2.3402
| FSH31 | United Energy Feeder | URBAN | 3807 | 15.7 | 1.59 | 17.29 | 8.1707 | 1.4408 | 3.0548 | 8 | 137519.6266 | 101550.514 | 0.012299 | 0.0064164 | 6 | 291565 | 0.0010212 | 2 | 1 | 0.011619 | 0.011619 | 0.0031811 | 0 | no | no | 2.3932 | 1.4408 | 3.0548
| FSH32 | United Energy Feeder | RURAL SHORT | 961.5 | 32.73 | 1.98 | 34.71 | 3.4393 | 3.0114 | 5.9178 | 18 | 110528.5834 | 108328.8546 | 0.0034203 | 0.0019638 | 0 | 217201 | 0.00092233 | 4 | 1 | 0.0091501 | 0.004404 | 0.00026728 | 0.00026728 | no | no | 1.5718 | 3.0114 | 5.9178
| FSH33 | United Energy Feeder | URBAN | 3524.5 | 21.51 | 5.44 | 26.95 | 10.5971 | 12.8071 | 5.0962 | 19 | 716898.9283 | 344386.9449 | 0.022092 | 0.01031 | 0 | 285269 | 0.001185 | 4 | 3 | 0.023552 | 0.023552 | 0.011258 | 0.011258 | yes | yes | 3.7778 | 12.8071 | 5.0962
| FSH34 | United Energy Feeder | URBAN | 3278.5 | 7.68 | 7.94 | 15.62 | 6.595 | 2.1008 | 0.98753 | 7 | 227205.2143 | 212812.2508 | 0.015068 | 0.010031 | 9 | 106805 | 0.00047275 | 1 | 0 | 0.0049547 | 0.0049547 | 0 | 0 | no | no | 1.8188 | 2.1008 | 0.98753
| FTN11 | United Energy Feeder | URBAN | 2093.5 | 7.6 | 1.57 | 9.17 | 6.7701 | 7.1552 | 0.7035 | 6 | 363141.4222 | 51157.217 | 0.0071299 | 0.0038392 | 5 | 35704 | 0.00014832 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 2.475 | 7.1552 | 0.7035
| FTN12 | United Energy Feeder | URBAN | 2563 | 11.67 | 1.93 | 13.6 | 6.6024 | 0.78881 | 4.5928 | 4 | 45530.0375 | 45243.1542 | 0.00032319 | 0.00032164 | 9 | 265097 | 0.0010351 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.6642 | 0.78881 | 4.5928
| FTN13 | United Energy Feeder | RURAL SHORT | 1812 | 11.16 | 0.22 | 11.38 | 3.3515 | 1.1562 | 0.74181 | 6 | 119586.5301 | 119586.5301 | 0.0036106 | 0.0036106 | 7 | 76725 | 0.00051447 | 1 | 0 | 0.0026388 | 0.0026388 | 0 | 0 | no | no | 1.0512 | 1.1562 | 0.74181
| FTN14 | United Energy Feeder | URBAN | 1674 | 5.77 | 2.84 | 8.61 | 6.6555 | 2.6376 | 1.2038 | 11 | 108946.9696 | 108946.9696 | 0.0012289 | 0.0012289 | 4 | 49725 | 0.00021938 | 1 | 0 | 0.0026264 | 0.0026264 | 0 | 0 | no | no | 2.4316 | 2.6376 | 1.2038
| FTN21 | United Energy Feeder | URBAN | 1651.5 | 8.72 | 0.52 | 9.24 | 3.5853 | 4.585 | 0.0039372 | 4 | 256193.536 | 256193.536 | 0.00083932 | 0.00083932 | 9 | 220 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.7734 | 4.585 | 0.0039372
| FTN22 | United Energy Feeder | URBAN | 918 | 3.25 | 2.55 | 5.8 | 9.212 | 1.0902 | 0.6283 | 2 | 16184.8649 | 16184.8649 | 6.9028e-05 | 6.9028e-05 | 8 | 9328 | 8.0337e-05 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 3.71 | 1.0902 | 0.6283
| FTN23 | United Energy Feeder | URBAN | 2784.5 | 14.52 | 6.11 | 20.63 | 7.0195 | 9.3805 | 1.054 | 9 | 507647.418 | 42258.7847 | 0.0050433 | 0.0009754 | 10 | 57040 | 0.00019157 | 1 | 2 | 0.0030791 | 0.0030791 | 0.00457 | 0.00457 | no | no | 3.0872 | 9.3805 | 1.054
| FTN24 | United Energy Feeder | URBAN | 2505 | 8.67 | 3.07 | 11.74 | 5.5231 | 0.53742 | 0.41007 | 7 | 42494.5934 | 42112.2601 | 0.00055788 | 0.00055634 | 10 | 32425 | 0.00010351 | 0 | 1 | 0 | 0 | 0.0021537 | 0.0021537 | no | no | 1.9008 | 0.53742 | 0.41007
| FTN25 | United Energy Feeder | URBAN | 2704.5 | 13.49 | 3.59 | 17.08 | 5.4241 | 0.98637 | 0.7854 | 3 | 81004.2506 | 80699.4173 | 0.0038716 | 0.0038701 | 5 | 64500 | 0.00037079 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.9759 | 0.98637 | 0.7854
| GW1 | United Energy Feeder | URBAN | 695 | 3.42 | 1.06 | 4.48 | 10.2543 | 6.206 | 0.4384 | 5 | 70921.1011 | 54905.1048 | 0.0024324 | 0.0013058 | 4 | 5010 | 3.3989e-05 | 1 | 0 | 0.0010753 | 0.0010753 | 0 | 0 | no | no | 3.649 | 6.206 | 0.4384
| GW10 | United Energy Feeder | URBAN | 953.5 | 4 | 0.96 | 4.96 | 6.043 | 3.7474 | 0.8358 | 6 | 112449.8921 | 89592.5509 | 0.0048027 | 0.003195 | 9 | 25080 | 0.00010197 | 2 | 0 | 0.0031332 | 0.0031332 | 0 | 0 | no | no | 1.9065 | 3.7474 | 0.8358
| GW11 | United Energy Feeder | URBAN | 2397.5 | 10.75 | 1.42 | 12.17 | 8.3902 | 3.7465 | 1.5171 | 6 | 205323.5386 | 113751.6807 | 0.0092973 | 0.0038025 | 7 | 83145 | 0.00034916 | 1 | 1 | 0.0036909 | 0.0036909 | 0.0017087 | 0.0017087 | no | no | 2.6248 | 3.7465 | 1.5171
| GW12 | United Energy Feeder | URBAN | 2250.5 | 10.66 | 1.14 | 11.8 | 6.6012 | 4.3386 | 0.45119 | 6 | 279341.6891 | 228869.78 | 0.0071335 | 0.0035833 | 6 | 29050 | 0.0001236 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 2.0972 | 4.3386 | 0.45119
| GW2 | United Energy Feeder | URBAN | 2561.5 | 13.45 | 4.46 | 17.91 | 7.571 | 1.0904 | 1.489 | 2 | 63486.8231 | 5154.1634 | 0.0041782 | 7.5085e-05 | 1 | 86693 | 0.00046039 | 1 | 0 | 0.0038268 | 0.0038268 | 0 | 0 | no | no | 2.6397 | 1.0904 | 1.489
| GW3 | United Energy Feeder | URBAN | 1665 | 8.9 | 1.36 | 10.26 | 5.8073 | 6.286 | 0.64307 | 6 | 265537.5361 | 228181.9804 | 0.0076894 | 0.0050618 | 2 | 27165 | 0.00017612 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.3649 | 6.286 | 0.64307
| GW4 | United Energy Feeder | URBAN | 1103.5 | 5.08 | 1.32 | 6.4 | 7.0781 | 1.2588 | 5.0539 | 3 | 28493.8402 | 3484.4203 | 0.0018185 | 5.9357e-05 | 2 | 114400 | 0.00057936 | 1 | 0 | 0.0017087 | 0.0017087 | 0 | 0 | no | no | 2.925 | 1.2588 | 5.0539
| GW5 | United Energy Feeder | URBAN | 1460.5 | 7.03 | 2.23 | 9.26 | 4.4458 | 0.9891 | 1.7643 | 3 | 57637.319 | 24450 | 0.0026882 | 0.00035379 | 2 | 102810 | 0.00026264 | 1 | 0 | 0.0022634 | 0.0022634 | 0 | 0 | no | no | 1.5038 | 0.9891 | 1.7643
| GW6 | United Energy Feeder | URBAN | 1154 | 8.35 | 1.04 | 9.39 | 6.7732 | 1.9998 | 6.529 | 4 | 40803.0229 | 14615.623 | 0.0020494 | 0.00020742 | 2 | 133215 | 0.00086672 | 2 | 0 | 0.0035657 | 0.0035657 | 0 | 0 | no | no | 3.3935 | 1.9998 | 6.529
| GW7 | United Energy Feeder | URBAN | 2453 | 15.86 | 6.52 | 22.38 | 5.6612 | 2.1177 | 1.2458 | 7 | 163908.1866 | 109245.3874 | 0.0095142 | 0.0056692 | 3 | 96425 | 0.00048511 | 4 | 0 | 0.015293 | 0.011439 | 0 | 0 | no | no | 1.9015 | 2.1177 | 1.2458
| GW8 | United Energy Feeder | URBAN | 2216.5 | 7.04 | 1.19 | 8.23 | 5.1263 | 2.7084 | 0.16515 | 3 | 208114.2711 | 158389.9262 | 0.0069314 | 0.0034338 | 2 | 12690 | 7.2613e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.7308 | 2.7084 | 0.16515
| HGS21 | United Energy Feeder | URBAN | 2 | 4.32 | 0.45 | 4.77 | 4.0381 | 0.37877 | 0 | 1 | 17.8341 | 0 | 3.0389e-06 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.5486 | 0.37877 | 0
| HGS22 | United Energy Feeder | RURAL SHORT | 2894 | 69.71 | 2.92 | 72.63 | 8.3646 | 25.2972 | 10.7765 | 42 | 1453472.6932 | 1102625.2966 | 0.030175 | 0.017384 | 3 | 619175.3 | 0.0026511 | 0 | 6 | 0 | 0 | 0.024002 | 0.024002 | yes | no | 3.0221 | 25.2972 | 10.7765
| HGS23 | United Energy Feeder | RURAL SHORT | 5014.5 | 117.07 | 3.16 | 120.23 | 11.9391 | 9.8321 | 5.1613 | 72 | 638124.8644 | 570729.6613 | 0.017662 | 0.0099978 | 8 | 334982 | 0.0017612 | 0 | 1 | 0 | 0 | 0.0006566 | 0.0006566 | no | no | 4.6357 | 9.8321 | 5.1613
| HGS31 | United Energy Feeder | RURAL SHORT | 2064.5 | 32.73 | 4.79 | 37.52 | 5.9089 | 0.70039 | 5.5109 | 11 | 32056.1581 | 13802.9869 | 0.0032863 | 0.00017602 | 3 | 252228 | 0.0011278 | 2 | 4 | 0.0062725 | 0.0062725 | 0.0061875 | 0.0061875 | no | no | 2.7064 | 0.70039 | 5.5109
| HGS32 | United Energy Feeder | URBAN | 3183 | 17.71 | 6.19 | 23.9 | 10.0615 | 2.5467 | 2.3617 | 10 | 90256.1423 | 62042.6427 | 0.0054633 | 0.00065572 | 8 | 83700 | 0.00035997 | 2 | 4 | 0.0097023 | 0.0097023 | 0.010662 | 0.010662 | no | no | 5.3887 | 2.5467 | 2.3617
| HGS33 | United Energy Feeder | RURAL SHORT | 3907 | 108.42 | 5.19 | 113.61 | 10.6005 | 22.4259 | 3.2513 | 41 | 1265983.9409 | 849772.9344 | 0.027275 | 0.014168 | 3 | 183543 | 0.00078792 | 0 | 8 | 0 | 0 | 0.019961 | 0.019707 | no | no | 4.1526 | 22.4259 | 3.2513
| HT1 | United Energy Feeder | URBAN | 2004.5 | 9.04 | 3.44 | 12.48 | 6.3042 | 16.1319 | 0.85277 | 13 | 992103.8843 | 661832.6399 | 0.018475 | 0.013554 | 6 | 52445 | 0.00050829 | 1 | 0 | 0.0031502 | 0.0031502 | 0 | 0 | yes | no | 1.9556 | 16.1319 | 0.85277
| HT10 | United Energy Feeder | URBAN | 563 | 3.53 | 1.76 | 5.29 | 3.4814 | 0.86029 | 8.6417 | 3 | 21913.2556 | 3506.1958 | 0.00095429 | 4.7028e-05 | 8 | 220120 | 0.00068905 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.3262 | 0.86029 | 8.6417
| HT11 | United Energy Feeder | URBAN | 2206 | 7.41 | 0.96 | 8.37 | 6.419 | 10.8477 | 0.54132 | 9 | 559103.0935 | 353449.9259 | 0.011225 | 0.0048843 | 1 | 27900 | 9.2697e-05 | 1 | 1 | 0.0024287 | 0.0024287 | 0.0027778 | 0.0027778 | no | no | 2.568 | 10.8477 | 0.54132
| HT13 | United Energy Feeder | URBAN | 289.5 | 3.29 | 1.33 | 4.62 | 6.3823 | 6.3209 | 0 | 6 | 47701.6659 | 34827.6214 | 0.0013684 | 0.00090327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.3017 | 6.3209 | 0
| HT2 | United Energy Feeder | URBAN | 1224.5 | 6.39 | 2.08 | 8.47 | 5.7307 | 1.4647 | 1.1721 | 2 | 47298.1013 | 9051.2834 | 0.0019361 | 5.0983e-05 | 45 | 37850 | 0.00017767 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.2752 | 1.4647 | 1.1721
| HT3 | United Energy Feeder | URBAN | 371 | 4.72 | 0.9 | 5.62 | 4.5388 | 5.6787 | 1.532 | 6 | 95929.1554 | 84311.8402 | 0.0023747 | 0.0018021 | 29 | 25880 | 0.00017767 | 3 | 0 | 0.0017334 | 0.0011572 | 0 | 0 | yes | no | 1.3177 | 5.6787 | 1.532
| HT4 | United Energy Feeder | URBAN | 322 | 3.89 | 0.22 | 4.11 | 1.096 | 0.49745 | 0 | 6 | 30132.2801 | 19729.644 | 0.00079429 | 0.00028155 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.31895 | 0.49745 | 0
| HT6 | United Energy Feeder | URBAN | 144 | 2.5 | 1.05 | 3.55 | 5.8814 | 5.0317 | 0.1931 | 4 | 13810.8874 | 8921.0255 | 0.00048972 | 0.00024871 | 9 | 530 | 4.6348e-06 | 1 | 0 | 0.00024256 | 0.00024256 | 0 | 0 | no | no | 3.1478 | 5.0317 | 0.1931
| HT7 | United Energy Feeder | URBAN | 344 | 3.64 | 1.29 | 4.93 | 4.5212 | 4.3824 | 0 | 4 | 46730.2957 | 33747.9472 | 0.0015677 | 0.0010259 | 29 | 0 | 0 | 1 | 0 | 0.00048666 | 0.00048666 | 0 | 0 | no | no | 1.9356 | 4.3824 | 0
| HT8 | United Energy Feeder | URBAN | 362 | 5.96 | 1.11 | 7.07 | 6.0608 | 1.4587 | 1.2275 | 2 | 12655.5082 | 1225.0667 | 0.00057112 | 7.7247e-06 | 3 | 10650 | 2.7809e-05 | 1 | 0 | 0.00056854 | 0.00056854 | 0 | 0 | no | no | 2.5034 | 1.4587 | 1.2275
| HT9 | United Energy Feeder | URBAN | 292.5 | 4.75 | 3.49 | 8.24 | 7.8791 | 6.9078 | 5.9158 | 3 | 29706.1386 | 21016.5114 | 0.0011382 | 0.00070992 | 3 | 25440 | 8.0337e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.0811 | 6.9078 | 5.9158
| K10 | United Energy Feeder | URBAN | 1861 | 3.41 | 2.11 | 5.52 | 3.924 | 0.95804 | 1.7266 | 7 | 73199.9379 | 73114.8379 | 0.00055436 | 0.00055281 | 1 | 131925 | 0.00045885 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4614 | 0.95804 | 1.7266
| K11 | United Energy Feeder | URBAN | 2 | 0 | 1.14 | 1.14 | 4.0298 | 1.0746 | 0 | 1 | 189.5666 | 189.5666 | 3.0899e-06 | 3.0899e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.68026 | 1.0746 | 0
| K12 | United Energy Feeder | URBAN | 1251.5 | 0.33 | 4.56 | 4.89 | 3.5365 | 0.20842 | 0.68228 | 2 | 11332.9632 | 11332.9632 | 0.00039205 | 0.00039205 | 7 | 37100 | 0.00016067 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3809 | 0.20842 | 0.68228
| K13 | United Energy Feeder | URBAN | 1018 | 4.34 | 0.78 | 5.12 | 1.6931 | 1.4119 | 4.0573 | 6 | 89542.713 | 89542.713 | 0.0014372 | 0.0014372 | 3 | 257310 | 0.0010089 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0.96313 | 1.4119 | 4.0573
| K2 | United Energy Feeder | URBAN | 1264 | 2.53 | 1.39 | 3.92 | 3.4459 | 0.30282 | 0.357 | 9 | 18186.1821 | 18186.1821 | 0.00040323 | 0.00040323 | 0 | 21440 | 8.8062e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2628 | 0.30282 | 0.357
| K3 | United Energy Feeder | URBAN | 819 | 2.93 | 1.77 | 4.7 | 3.7218 | 0.53235 | 0.40172 | 2 | 20606.6557 | 20606.6557 | 0.00011321 | 0.00011321 | 2 | 15550 | 9.7332e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2695 | 0.53235 | 0.40172
| K4 | United Energy Feeder | URBAN | 816.5 | 2.16 | 1.1 | 3.26 | 3.5489 | 0.052305 | 0.84062 | 2 | 2399.2748 | 2399.2748 | 3.3695e-05 | 3.3695e-05 | 0 | 38560 | 0.00018539 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.068 | 0.052305 | 0.84062
| K5 | United Energy Feeder | URBAN | 69 | 0.9 | 0.78 | 1.68 | 4.0036 | 6.9486 | 0 | 1 | 13488.4167 | 13488.4167 | 6.6433e-05 | 6.6433e-05 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.1327 | 6.9486 | 0
| K6 | United Energy Feeder | URBAN | 1738 | 4.99 | 2.91 | 7.9 | 4.1829 | 0.14794 | 0.25785 | 2 | 7401.3249 | 7401.3249 | 0.00011893 | 0.00011893 | 4 | 12900 | 6.1798e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.0844 | 0.14794 | 0.25785
| K7 | United Energy Feeder | URBAN | 1121 | 3.3 | 3.17 | 6.47 | 5.8162 | 0.023231 | 1.7008 | 1 | 830.7333 | 830.7333 | 2.6264e-05 | 2.6264e-05 | 10 | 60820 | 0.00035534 | 2 | 0 | 0.0035364 | 0.0035364 | 0 | 0 | no | no | 1.8809 | 0.023231 | 1.7008
| K8 | United Energy Feeder | URBAN | 1134.5 | 2.94 | 2.76 | 5.7 | 3.5256 | 0.33498 | 0 | 2 | 23452.9986 | 23452.9986 | 0.0001605 | 0.0001605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.97225 | 0.33498 | 0
| K9 | United Energy Feeder | URBAN | 393 | 0 | 0.97 | 0.97 | 2.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.97164 | 0 | 0
| LD1 | United Energy Feeder | URBAN | 996.5 | 3.82 | 1.25 | 5.07 | 6.9153 | 0.36902 | 1.2532 | 1 | 6192.6021 | 6192.6021 | 6.7931e-05 | 6.7931e-05 | 3 | 21030 | 0.00015295 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.5629 | 0.36902 | 1.2532
| LD2 | United Energy Feeder | URBAN | 2737.5 | 11.52 | 3.33 | 14.85 | 9.5479 | 7.1145 | 0.74088 | 13 | 255263.8511 | 226661.7222 | 0.0025318 | 0.0024558 | 8 | 26582 | 0.00013905 | 2 | 1 | 0.012882 | 0.012882 | 0.00010969 | 0.00010969 | no | no | 4.5779 | 7.1145 | 0.74088
| LD3 | United Energy Feeder | URBAN | 1679.5 | 6.64 | 1.25 | 7.89 | 3.5074 | 0.18733 | 0.28188 | 2 | 18222.6819 | 18064.6986 | 7.1068e-05 | 6.9523e-05 | 4 | 27420 | 0.00025337 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0359 | 0.18733 | 0.28188
| LD32 | United Energy Feeder | URBAN | 403 | 4.38 | 2.01 | 6.39 | 3.1177 | 0.23176 | 2.6091 | 2 | 4513.4167 | 4513.4167 | 3.986e-05 | 3.986e-05 | 3 | 50810 | 0.00021784 | 1 | 0 | 0.0013256 | 0.0013256 | 0 | 0 | no | no | 1.2416 | 0.23176 | 2.6091
| LD33 | United Energy Feeder | URBAN | 1852 | 14.86 | 11.91 | 26.77 | 10.0546 | 18.8261 | 5.6266 | 6 | 628021.2465 | 100992.2688 | 0.0098429 | 0.0050489 | 3 | 187699 | 0.00091306 | 1 | 0 | 0.0058677 | 0.0058677 | 0 | 0 | yes | no | 3.331 | 18.8261 | 5.6266
| LD4 | United Energy Feeder | URBAN | 3893 | 13.77 | 0.86 | 14.63 | 8.106 | 6.6453 | 0.83732 | 6 | 478449.1749 | 478449.1749 | 0.014166 | 0.014166 | 0 | 60285 | 0.000275 | 0 | 3 | 0 | 0 | 0.011972 | 0.011972 | no | no | 3.2443 | 6.6453 | 0.83732
| LD5 | United Energy Feeder | URBAN | 1002 | 7.12 | 2 | 9.12 | 7.615 | 2.531 | 4.3928 | 3 | 26507.8167 | 26507.8167 | 0.00042641 | 0.00042641 | 2 | 46006 | 0.00029818 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 5.7404 | 2.531 | 4.3928
| LD6 | United Energy Feeder | URBAN | 3423.5 | 11.23 | 1.99 | 13.22 | 10.0156 | 0.40812 | 2.532 | 5 | 37900.9445 | 28837.6218 | 0.00020517 | 0.00016591 | 4 | 235135 | 0.00080028 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.2119 | 0.40812 | 2.532
| LD7 | United Energy Feeder | URBAN | 2373.5 | 8.07 | 2.62 | 10.69 | 6.1964 | 3.8321 | 3.9292 | 9 | 158906.224 | 158906.224 | 0.0036674 | 0.0036674 | 0 | 162935 | 0.00062879 | 1 | 0 | 0.0039443 | 0.0039443 | 0 | 0 | no | no | 3.4343 | 3.8321 | 3.9292
| LWN31 | United Energy Feeder | RURAL SHORT | 3364.5 | 73.59 | 16.29 | 89.88 | 8.8542 | 7.1676 | 7.134 | 32 | 473092.3048 | 203807.0597 | 0.011659 | 0.0040872 | 0 | 470873 | 0.001976 | 2 | 0 | 0.0099974 | 0.0099974 | 4.6348e-06 | 4.6348e-06 | no | no | 3.0585 | 7.1676 | 7.134
| LWN32 | United Energy Feeder | URBAN | 3993.5 | 14.53 | 16.81 | 31.34 | 10.2336 | 1.682 | 0.83357 | 12 | 111788.0664 | 111788.0664 | 0.0065588 | 0.0065588 | 4 | 55400 | 0.00038778 | 2 | 4 | 0.012324 | 0.012324 | 0.014801 | 0.014801 | no | no | 3.6053 | 1.682 | 0.83357
| LWN33 | United Energy Feeder | URBAN | 1867 | 11.01 | 0.58 | 11.59 | 6.054 | 0.68306 | 0.80421 | 5 | 34560.2883 | 34385.1716 | 0.0030549 | 0.0030533 | 5 | 40690 | 0.0001993 | 1 | 0 | 0.0027933 | 0.0027933 | 0 | 0 | no | no | 2.214 | 0.68306 | 0.80421
| LWN34 | United Energy Feeder | URBAN | 3801.5 | 15.6 | 2.06 | 17.66 | 10.6991 | 2.8106 | 0.20836 | 11 | 185545.8198 | 181640.1607 | 0.0014298 | 0.001388 | 3 | 13755 | 7.7247e-05 | 2 | 1 | 0.010998 | 0.010998 | 0.0015449 | 0.0015449 | no | no | 3.4551 | 2.8106 | 0.20836
| LWN35 | United Energy Feeder | URBAN | 1768.5 | 7.58 | 3.78 | 11.36 | 5.6392 | 3.737 | 0.14116 | 4 | 291413.9864 | 3837.9284 | 0.0029039 | 0.00012412 | 3 | 11008 | 9.2697e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3607 | 3.737 | 0.14116
| M11 | United Energy Feeder | URBAN | 755.5 | 5.13 | 0.31 | 5.44 | 4.0813 | 2.5773 | 2.4651 | 2 | 95790.8411 | 54321.3818 | 0.0047802 | 0.0023916 | 3 | 91621 | 0.00041096 | 1 | 0 | 0.0023885 | 0.0023885 | 0 | 0 | no | no | 1.2196 | 2.5773 | 2.4651
| M12 | United Energy Feeder | URBAN | 1298.5 | 4.12 | 0.96 | 5.08 | 3.3456 | 0.0073227 | 1.533 | 0 | 439.9001 | 439.9001 | 9.2697e-06 | 9.2697e-06 | 3 | 92090 | 0.00031053 | 2 | 0 | 0.0033088 | 0.0033088 | 0 | 0 | no | no | 1.2969 | 0.0073227 | 1.533
| M13 | United Energy Feeder | URBAN | 1686.5 | 5.56 | 2.95 | 8.51 | 4.6373 | 0.74217 | 0 | 2 | 49516.2393 | 5408.2989 | 0.0051438 | 0.0026031 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5167 | 0.74217 | 0
| M14 | United Energy Feeder | URBAN | 867 | 0 | 0.01 | 0.01 | 0 | 3.0947e-05 | 4.7847e-07 | 3 | 197593.9574 | 197593.9574 | 0.0040873 | 0.0040873 | 5 | 3055 | 2.0084e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 8.1473e-06 | 3.0947e-05 | 4.7847e-07
M33 | M16 | United Energy Feeder | URBAN | 831.5 | 0 | 0.01 | 0.01 | 0 | 0.049621 | 8.8713 | 1 | 2194.8751 | 2194.8751 | 0.0012796 | 0.0012796 | 6 | 392400 | 0.00018539 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.1279 | 0.049621 | 8.8713
M34 | M17 | United Energy Feeder | URBAN | 518.5 | 0 | 0 | 0 | 0 | 1.8557 | 2.544 | 8 | 46470.8095 | 46470.8095 | 0.002688 | 0.002688 | 24 | 63706 | 0.00024719 | 2 | 0 | 0.0032119 | 0.0016067 | 0 | 0 | no | no | 1.2423 | 1.8557 | 2.544
M35 | M18 | United Energy Feeder | URBAN | 708.5 | 0 | 0 | 0 | 0 | 3.4685 | 1.3574 | 3 | 132718.0337 | 132718.0337 | 0.0033398 | 0.0033398 | 7 | 51940 | 0.00032753 | 1 | 0 | 0.0021907 | 0.0021907 | 0 | 0 | no | no | 1.111 | 3.4685 | 1.3574
| M21 | United Energy Feeder | URBAN | 222.5 | 2.77 | 0.71 | 3.48 | 4.6463 | 1.3984 | 0.54034 | 1 | 13276.5073 | 377.2667 | 0.00074918 | 6.1798e-06 | 4 | 5130 | 1.3905e-05 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 1.4061 | 1.3984 | 0.54034
| M22 | United Energy Feeder | URBAN | 662.5 | 3.21 | 0.59 | 3.8 | 1.0429 | 6.0091 | 0.54065 | 2 | 300001.701 | 264662.0461 | 0.0040935 | 0.0020579 | 3 | 26992 | 6.0253e-05 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0.7962 | 6.0091 | 0.54065
| M23 | United Energy Feeder | URBAN | 445.5 | 3.74 | 0.57 | 4.31 | 5.0481 | 1.2573 | 0.5873 | 2 | 23162.7109 | 1148.7177 | 0.0012773 | 9.2388e-06 | 3 | 10820 | 0.00033525 | 2 | 0 | 0.0032475 | 0.0016392 | 0 | 0 | no | no | 1.4509 | 1.2573 | 0.5873
| M25 | United Energy Feeder | URBAN | 666 | 4.16 | 0.49 | 4.65 | 3.8127 | 1.6839 | 2.2289 | 2 | 71383.1689 | 36043.514 | 0.0021607 | 0.00012514 | 5 | 94490 | 0.00032289 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.94262 | 1.6839 | 2.2289
| M31 | United Energy Feeder | URBAN | 292.5 | 3.01 | 0.43 | 3.44 | 0.85389 | 0.68167 | 0.19822 | 2 | 16403.6475 | 679.3667 | 0.0015345 | 0.00062879 | 2 | 4770 | 2.7809e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.7293 | 0.68167 | 0.19822
| M32 | United Energy Feeder | URBAN | 1011 | 4.91 | 1.72 | 6.63 | 3.2567 | 4.5682 | 8.1533 | 4 | 241680.5572 | 188431.2129 | 0.005988 | 0.0029208 | 0 | 431350 | 0.0025399 | 3 | 0 | 0.0093284 | 0.0093284 | 0 | 0 | yes | yes | 1.1466 | 4.5682 | 8.1533
| M33 | United Energy Feeder | URBAN | 414 | 3.73 | 0.46 | 4.19 | 4.6463 | 4.0667 | 1.2464 | 4 | 89562.5721 | 68641.2832 | 0.0015156 | 0.00031053 | 1 | 27450 | 0.00010042 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 1.1279 | 4.0667 | 1.2464
| M34 | United Energy Feeder | URBAN | 386.5 | 3.02 | 0.37 | 3.39 | 4.6438 | 1.2157 | 1.3248 | 3 | 22692.4249 | 217.2 | 0.0012129 | 1.1433e-05 | 1 | 24730 | 0.00022865 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2423 | 1.2157 | 1.3248
| M35 | United Energy Feeder | URBAN | 547.5 | 3.29 | 0.94 | 4.23 | 3.7335 | 2.1352 | 2.4458 | 5 | 63137.3093 | 34940.2091 | 0.0039986 | 0.0023744 | 4 | 72320 | 0.00029045 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.111 | 2.1352 | 2.4458
M23 | M7 | United Energy Feeder | URBAN | 954 | 0 | 0 | 0 | 0 | 0.12606 | 0.25948 | 1 | 4973.2119 | 4973.2119 | 5.7673e-05 | 5.7673e-05 | 0 | 10237 | 4.4804e-05 | 1 | 0 | 0.0031043 | 0.0031043 | 1.5449e-06 | 1.5449e-06 | no | no | 1.4509 | 0.12606 | 0.25948
M22 | M8 | United Energy Feeder | URBAN | 904 | 0 | 0 | 0 | 0 | 0.01341 | 0 | 1 | 913.539 | 913.539 | 1.9374e-05 | 1.9374e-05 | 2 | 0 | 0 | 1 | 0 | 0.0029359 | 0.0029359 | 0 | 0 | no | no | 0.7962 | 0.01341 | 0
M25 | M9 | United Energy Feeder | URBAN | 880.5 | 0 | 0 | 0 | 0 | 0.0054452 | 0 | 0 | 305.1833 | 305.1833 | 4.6348e-06 | 4.6348e-06 | 0 | 0 | 0 | 1 | 0 | 0.0028237 | 0.0028237 | 0 | 0 | no | no | 0.94262 | 0.0054452 | 0
| MC1 | United Energy Feeder | URBAN | 2032.5 | 7.54 | 0.58 | 8.12 | 5.3791 | 35.0078 | 8.1289 | 14 | 1234934.886 | 686287.1305 | 0.021984 | 0.011832 | 1 | 286755 | 0.0011263 | 2 | 0 | 0.0063559 | 0.003178 | 0 | 0 | yes | no | 3.457 | 35.0078 | 8.1289
| MC10 | United Energy Feeder | URBAN | 329.5 | 3.01 | 2.11 | 5.12 | 11.0604 | 1.841 | 0.054388 | 2 | 9139.3867 | 1437.1542 | 0.0004549 | 1.1247e-05 | 2 | 270 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.9824 | 1.841 | 0.054388
| MC2 | United Energy Feeder | URBAN | 2471.5 | 9.56 | 3.61 | 13.17 | 8.6553 | 10.0139 | 0.14254 | 11 | 559576.3382 | 284496.5966 | 0.010849 | 0.0058044 | 4 | 7965 | 6.7978e-05 | 2 | 0 | 0.007649 | 0.007649 | 0 | 0 | no | no | 2.6537 | 10.0139 | 0.14254
| MC3 | United Energy Feeder | URBAN | 2600 | 9.93 | 1.08 | 11.01 | 5.8415 | 1.5921 | 2.452 | 10 | 129489.1662 | 60432.8276 | 0.0045282 | 0.00057678 | 3 | 199421 | 0.00092079 | 2 | 0 | 0.0078391 | 0.0078391 | 0 | 0 | no | no | 1.9181 | 1.5921 | 2.452
| MC4 | United Energy Feeder | URBAN | 337.5 | 4.89 | 4.57 | 9.46 | 8.9745 | 22.1193 | 8.1122 | 6 | 120474.4733 | 111732.8392 | 0.0024115 | 0.001908 | 1 | 44183.9 | 0.00019003 | 1 | 0 | 0.00055927 | 0.00055927 | 0 | 0 | yes | no | 3.7179 | 22.1193 | 8.1122
| MC5 | United Energy Feeder | URBAN | 343.5 | 3.46 | 2.84 | 6.3 | 8.6828 | 1.506 | 0.26675 | 1 | 9225.2306 | 217.0833 | 0.00052042 | 1.5449e-06 | 6 | 1634 | 4.6348e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.3645 | 1.506 | 0.26675
| MC6 | United Energy Feeder | URBAN | 2669 | 8.95 | 1.6 | 10.55 | 9.5323 | 15.205 | 4.0549 | 11 | 558742.4264 | 22444.1 | 0.009137 | 0.00048314 | 2 | 149006 | 0.00060562 | 1 | 1 | 0.0041204 | 0.0041204 | 0.00030435 | 0.00030435 | no | no | 4.3579 | 15.205 | 4.0549
| MC7 | United Energy Feeder | URBAN | 1653 | 11.13 | 7.46 | 18.59 | 6.4228 | 6.837 | 1.3315 | 5 | 261366.8485 | 212914.7424 | 0.0054386 | 0.0026477 | 2 | 50901 | 0.00022556 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.5944 | 6.837 | 1.3315
| MC9 | United Energy Feeder | URBAN | 354 | 5.18 | 2.69 | 7.87 | 8.3719 | 14.6783 | 16.1821 | 5 | 60016.3406 | 50661.7261 | 0.0012386 | 0.0006998 | 4 | 66165 | 0.00023638 | 1 | 0 | 0.00083582 | 0.00083582 | 0 | 0 | yes | no | 5.1947 | 14.6783 | 16.1821
M11 | MEN11 | United Energy Feeder | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33333.5708 | 33333.5708 | 0.0028674 | 0.0028674 | 1 | 110820 | 0.00056545 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 1.2196 | #DIV/0! | #DIV/0!
M12 | MEN12 | United Energy Feeder | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 60719.8927 | 18850.6635 | 0.0069013 | 0.0044896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2969 | #DIV/0! | #DIV/0!
M13 | MEN13 | United Energy Feeder | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 246517.5381 | 246517.5381 | 0.0032013 | 0.0032013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5167 | #DIV/0! | #DIV/0!
| MGE11 | United Energy Feeder | URBAN | 837.5 | 0 | 2.34 | 2.34 | 3.068 | 0.55071 | 0 | 8 | 41081.5154 | 36939.2611 | 0.00027026 | 0.000231 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.67362 | 0.55071 | 0
| MGE12 | United Energy Feeder | URBAN | 1088 | 6.61 | 6.42 | 13.03 | 7.3494 | 1.642 | 4.7617 | 10 | 35850.6649 | 35850.6649 | 0.0002719 | 0.0002719 | 1 | 103965 | 0.00059944 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.9899 | 1.642 | 4.7617
| MGE13 | United Energy Feeder | URBAN | 919.5 | 4.35 | 8.92 | 13.27 | 9.7574 | 0.18356 | 2.7709 | 1 | 2247.7044 | 2247.7044 | 2.6048e-05 | 2.6048e-05 | 3 | 33930 | 0.00036152 | 4 | 0 | 0.0057379 | 0.0057379 | 0 | 0 | no | no | 4.5054 | 0.18356 | 2.7709
| MGE14 | United Energy Feeder | URBAN | 375 | 3.4 | 3.69 | 7.09 | 7.419 | 0.054352 | 0.40389 | 0 | 404.5167 | 404.5167 | 4.6348e-06 | 4.6348e-06 | 9 | 3006 | 1.5449e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.0232 | 0.054352 | 0.40389
| MGE21 | United Energy Feeder | URBAN | 2120 | 8.24 | 9.3 | 17.54 | 7.8782 | 6.5151 | 0.52171 | 15 | 282539.9269 | 259616.2769 | 0.0042028 | 0.0039726 | 4 | 22625 | 0.00015604 | 0 | 1 | 0 | 0 | 9.2697e-06 | 9.2697e-06 | no | no | 2.9331 | 6.5151 | 0.52171
| MGE22 | United Energy Feeder | URBAN | 1057 | 7.48 | 2.22 | 9.7 | 7.0818 | 4.2071 | 5.5499 | 3 | 86144.4301 | 84304.3232 | 0.0022389 | 0.0022108 | 2 | 113640 | 0.00040632 | 2 | 0 | 0.0032753 | 0.0032753 | 0 | 0 | no | no | 3.0973 | 4.2071 | 5.5499
| MGE23 | United Energy Feeder | URBAN | 2285.5 | 11.01 | 2.61 | 13.62 | 6.5756 | 0.55477 | 0.86859 | 7 | 41227.221 | 41227.221 | 0.0002484 | 0.0002484 | 9 | 64548 | 0.00039551 | 0 | 1 | 0 | 0 | 0.0025523 | 0.0025523 | no | no | 1.8453 | 0.55477 | 0.86859
| MGE24 | United Energy Feeder | URBAN | 1786 | 8.84 | 1.72 | 10.56 | 9.3857 | 0.82045 | 5.8002 | 4 | 19359.1255 | 18647.6255 | 0.00027977 | 0.00027823 | 7 | 136860 | 0.00068132 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.5415 | 0.82045 | 5.8002
| MGE31 | United Energy Feeder | URBAN | 2138 | 8.66 | 6.89 | 15.55 | 8.2363 | 8.7215 | 0.33358 | 6 | 368127.8372 | 26588.0025 | 0.0034603 | 9.9309e-05 | 2 | 14080 | 0.00011124 | 1 | 0 | 0.003283 | 0.003283 | 0 | 0 | no | no | 3.0391 | 8.7215 | 0.33358
| MGE32 | United Energy Feeder | URBAN | 1057.5 | 5.81 | 6.68 | 12.49 | 8.667 | 20.1131 | 2.2889 | 7 | 315151.0735 | 173952.1167 | 0.0049548 | 0.0035211 | 3 | 35865 | 0.00021166 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 4.0494 | 20.1131 | 2.2889
| MGE33 | United Energy Feeder | URBAN | 2268.5 | 2.78 | 4.05 | 6.83 | 8.1825 | 1.0508 | 0.10077 | 1 | 147550.8235 | 147550.8235 | 0.0052884 | 0.0052884 | 0 | 14150 | 8.4972e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.96931 | 1.0508 | 0.10077
| MGE34 | United Energy Feeder | URBAN | 2342.5 | 12.57 | 1.07 | 13.64 | 5.8677 | 3.204 | 0.18568 | 8 | 256581.8563 | 256361.973 | 0.0097387 | 0.009734 | 0 | 14870 | 7.1068e-05 | 2 | 0 | 0.0073107 | 0.0073107 | 0 | 0 | no | no | 1.7551 | 3.204 | 0.18568
| MR11 | United Energy Feeder | URBAN | 1007 | 3.93 | 0.19 | 4.12 | 2.7048 | 0.43913 | 0 | 1 | 28083.7074 | 1085.9167 | 0.0015644 | 9.2697e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.94476 | 0.43913 | 0
| MR12 | United Energy Feeder | URBAN | 1236 | 4.7 | 0.46 | 5.16 | 2.8537 | 0.50886 | 0.21373 | 4 | 44354.8172 | 11007.6359 | 0.0020437 | 0.00016933 | 10 | 18630 | 0.0001066 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.85081 | 0.50886 | 0.21373
MTN31 | MR13 | United Energy Feeder | URBAN | 992.5 | 3.34 | 1.07 | 4.41 | 4.5414 | 0.86207 | 0.15493 | 10 | 56088.9147 | 36446.8893 | 0.0015394 | 0.00040804 | 1 | 10080 | 8.6517e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.91527 | 0.86207 | 0.15493
| MR14 | United Energy Feeder | URBAN | 2304 | 7.18 | 0.56 | 7.74 | 5.6264 | 0.94377 | 0.54093 | 5 | 85873.4156 | 25454.8653 | 0.0037078 | 0.00022765 | 2 | 49219 | 0.000292 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5193 | 0.94377 | 0.54093
| MR15 | United Energy Feeder | URBAN | 1731.5 | 8.05 | 0.82 | 8.87 | 6.978 | 1.734 | 0.28726 | 6 | 67728.5506 | 10106.2478 | 0.0081185 | 0.0029646 | 5 | 11220 | 8.1882e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.6599 | 1.734 | 0.28726
| MR21 | United Energy Feeder | URBAN | 1333.5 | 4.47 | 0.47 | 4.94 | 5.7654 | 1.9297 | 0.040653 | 9 | 102527.9381 | 73930.7029 | 0.0042181 | 0.0026292 | 3 | 2160 | 2.7809e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5059 | 1.9297 | 0.040653
| MR22 | United Energy Feeder | URBAN | 1901 | 5.95 | 1.16 | 7.11 | 4.6194 | 2.5519 | 0.0060616 | 12 | 202075.1311 | 145614.6772 | 0.0093675 | 0.0063839 | 6 | 480 | 3.0899e-06 | 2 | 0 | 0.00586 | 0.00586 | 0 | 0 | no | no | 1.4404 | 2.5519 | 0.0060616
MTN24 | MR23 | United Energy Feeder | URBAN | 661.5 | 0.49 | 1.5 | 1.99 | 3.9246 | 0.72433 | 0 | 2 | 20566.9957 | 1681.7834 | 0.001026 | 1.6994e-05 | 6 | 0 | 0 | 1 | 0 | 0.00099958 | 0.00099958 | 0 | 0 | no | no | 1.3978 | 0.72433 | 0
| MR24 | United Energy Feeder | URBAN | 1091.5 | 4.8 | 1.27 | 6.07 | 4.0873 | 1.4334 | 0 | 2 | 57527.5411 | 28104.48 | 0.0034236 | 0.0017288 | 2 | 0 | 0 | 1 | 0 | 0.0017736 | 0.0017736 | 0 | 0 | no | no | 1.6318 | 1.4334 | 0
| MR31 | United Energy Feeder | URBAN | 1136 | 4.04 | 1.65 | 5.69 | 3.9471 | 1.9843 | 2.5708 | 6 | 113788.2171 | 72548.6791 | 0.0036862 | 0.0018627 | 10 | 147420 | 0.00036152 | 1 | 0 | 0.0017612 | 0.0017612 | 0 | 0 | no | no | 1.1886 | 1.9843 | 2.5708
| MR32 | United Energy Feeder | URBAN | 646 | 4.46 | 3.46 | 7.92 | 0 | 1.8874 | 0.12528 | 6 | 48586.7084 | 11627.0448 | 0.0022302 | 0.00022973 | 3 | 3225 | 2.4719e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5056 | 1.8874 | 0.12528
MTN31 | MTN1 | United Energy Feeder | URBAN | 2786 | 0 | 0 | 0 | 0 | 4.7554 | 3.1759 | 2 | 203127.9945 | 203127.9945 | 0.0087877 | 0.0087862 | 3 | 135660 | 0.00041096 | 1 | 1 | 0.0087537 | 0.0087537 | 0.0016763 | 0.0016763 | no | no | 3.9134 | 4.7554 | 3.1759
MTN22 | MTN21 | United Energy Feeder | URBAN | 1380 | 13.32 | 5.84 | 19.16 | 10.2499 | 3.5989 | 1.4367 | 5 | 76537.3172 | 57855.8713 | 0.0050065 | 0.00077865 | 0 | 30555 | 0.00014986 | 3 | 2 | 0.013337 | 0.013337 | 0.0048743 | 0.0048743 | no | yes | 3.8934 | 3.5989 | 1.4367
| MTN22 | United Energy Feeder | RURAL SHORT | 583 | 42.09 | 1.69 | 43.78 | 3.0518 | 3.4219 | 1.7447 | 7 | 75961.9814 | 69012.9769 | 0.0034776 | 0.0019049 | 1 | 38730 | 0.00014368 | 1 | 0 | 0.0015676 | 0.0015676 | 0 | 0 | no | no | 1.5758 | 3.4219 | 1.7447
| MTN23 | United Energy Feeder | URBAN | 1088 | 11.21 | 3.99 | 15.2 | 8.2609 | 10.0913 | 2.0569 | 10 | 233417.5804 | 218580.702 | 0.010143 | 0.0067853 | 1 | 47577.5 | 0.00038469 | 1 | 0 | 0.0033469 | 0.0033469 | 0 | 0 | no | no | 2.8222 | 10.0913 | 2.0569
| MTN24 | United Energy Feeder | RURAL SHORT | 1053 | 31.47 | 12.8 | 44.27 | 2.7401 | 1.9441 | 4.6391 | 7 | 65301.4164 | 54226.8689 | 0.0036928 | 0.0011865 | 2 | 155825 | 0.00069368 | 2 | 0 | 0.0042363 | 0.0042363 | 0 | 0 | no | no | 1.881 | 1.9441 | 4.6391
| MTN3 | United Energy Feeder | RURAL SHORT | 780.5 | 0 | 0 | 0 | 0 | 3.0014 | 5.5357 | 12 | 55118.7238 | 55118.7238 | 0.0014259 | 0.0014259 | 3 | 101660 | 0.00094087 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.55 | 3.0014 | 5.5357
| MTN31 | United Energy Feeder | URBAN | 2730.5 | 12.9 | 15.69 | 28.59 | 11.4073 | 5.0791 | 7.421 | 7 | 212631.2999 | 172253.0609 | 0.017804 | 0.0086662 | 1 | 310675 | 0.0015357 | 1 | 0 | 0.0091085 | 0.0091085 | 0 | 0 | no | no | 3.9134 | 5.0791 | 7.421
MTN34 | MTN32 | United Energy Feeder | RURAL SHORT | 386.5 | 97.33 | 3.43 | 100.76 | 1.096 | 6.8321 | 7.2881 | 17 | 176170.1225 | 170879.5589 | 0.0044266 | 0.0032293 | 2 | 187927 | 0.0010567 | 1 | 2 | 0.0011934 | 0.0011934 | 0.0018957 | 0.0018957 | yes | no | 0.89934 | 6.8321 | 7.2881
MTN35 | MTN34 | United Energy Feeder | URBAN | 1915 | 13.46 | 4.05 | 17.51 | 7.318 | 0.69939 | 2.182 | 2 | 29900.0259 | 4002.3061 | 0.0059162 | 5.5247e-05 | 0 | 93285 | 0.00041405 | 1 | 0 | 0.005842 | 0.005842 | 0 | 0 | no | no | 2.6876 | 0.69939 | 2.182
MTN21 | MTN35 | United Energy Feeder | RURAL SHORT | 1236.5 | 28.74 | 3.91 | 32.65 | 8.7664 | 14.0125 | 3.078 | 8 | 319557.9758 | 302692.5912 | 0.010869 | 0.0070521 | 0 | 70195 | 0.00034916 | 1 | 2 | 0.0038045 | 0.0038045 | 0.0069646 | 0.0069646 | no | no | 3.2532 | 14.0125 | 3.078
| MTN5 | United Energy Feeder | RURAL SHORT | 2048.5 | 0 | 0 | 0 | 0 | 1.9994 | 2.1139 | 12 | 67054.0715 | 66772.0715 | 0.00038976 | 0.00038821 | 1 | 70895 | 0.00064733 | 0 | 1 | 0 | 0 | 0.0015882 | 0.0015882 | no | no | 3.6649 | 1.9994 | 2.1139
MTN34 | MTN6 | United Energy Feeder | URBAN | 1748 | 0 | 0 | 0 | 0 | 0.86311 | 1.3779 | 3 | 33681.325 | 33681.325 | 0.00036367 | 0.00036367 | 3 | 53770 | 0.00022711 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.6876 | 0.86311 | 1.3779
MTN35 | MTN7 | United Energy Feeder | RURAL SHORT | 1317.5 | 0 | 0 | 0 | 0 | 12.5032 | 0.81855 | 6 | 303817.19 | 303817.19 | 0.0025334 | 0.0025334 | 1 | 19890 | 0.00010506 | 0 | 1 | 0 | 0 | 0.0036291 | 0.0036291 | no | no | 3.2532 | 12.5032 | 0.81855
MTN21 | MTN8 | United Energy Feeder | URBAN | 1597.5 | 0 | 0 | 0 | 0 | 0.51353 | 0.86398 | 2 | 12642.4873 | 12447.6206 | 0.00022921 | 0.00022612 | 1 | 21270 | 8.1882e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.8934 | 0.51353 | 0.86398
| NB11 | United Energy Feeder | URBAN | 806.5 | 2.46 | 0.62 | 3.08 | 2.6492 | 0.97361 | 0 | 6 | 70574.4462 | 43691.7932 | 0.0025936 | 0.0013206 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.66757 | 0.97361 | 0
| NB12 | United Energy Feeder | URBAN | 1916.5 | 5.1 | 0.56 | 5.66 | 5.4378 | 2.7752 | 0.41399 | 10 | 203118.69 | 150988.7013 | 0.0071644 | 0.0041617 | 6 | 30300 | 0.00015141 | 3 | 0 | 0.0089901 | 0.0089901 | 0 | 0 | no | no | 1.5711 | 2.7752 | 0.41399
| NB13 | United Energy Feeder | URBAN | 882 | 2.64 | 1.21 | 3.85 | 3.0874 | 0.81726 | 0.14603 | 3 | 52886.3136 | 31751.8141 | 0.00249 | 0.0012726 | 6 | 9450 | 5.4073e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.81778 | 0.81726 | 0.14603
| NB14 | United Energy Feeder | URBAN | 1103.5 | 1.83 | 1.85 | 3.68 | 4.6211 | 2.1361 | 0.32518 | 5 | 80404.2332 | 50314.889 | 0.0035364 | 0.0018032 | 19 | 12240 | 5.2528e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.759 | 2.1361 | 0.32518
| NB15 | United Energy Feeder | URBAN | 636 | 2.86 | 0.25 | 3.11 | 5.7863 | 2.7313 | 2.7551 | 6 | 73578.7634 | 57214.8508 | 0.0029717 | 0.0020291 | 12 | 74219 | 0.00028891 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4165 | 2.7313 | 2.7551
| NB21 | United Energy Feeder | URBAN | 1823 | 5.09 | 1.32 | 6.41 | 4.4618 | 6.7901 | 0.53372 | 6 | 438914.3954 | 37889.9993 | 0.0068954 | 0.00029031 | 16 | 34500 | 0.00024565 | 1 | 0 | 0.002852 | 0.002852 | 0 | 0 | no | no | 1.6921 | 6.7901 | 0.53372
| NB22 | United Energy Feeder | URBAN | 1569 | 4.34 | 1.84 | 6.18 | 5.9955 | 2.8947 | 0.52597 | 8 | 130390.2874 | 86655.4656 | 0.0054167 | 0.0028975 | 7 | 23692 | 0.00015604 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.09 | 2.8947 | 0.52597
| NB23 | United Energy Feeder | URBAN | 1180 | 3.41 | 1.89 | 5.3 | 6.0552 | 1.2858 | 0.30411 | 5 | 41519.1368 | 3448.1392 | 0.0023773 | 0.00051756 | 8 | 9820 | 7.1068e-05 | 1 | 0 | 0.0017906 | 0.0017906 | 0 | 0 | no | no | 2.1926 | 1.2858 | 0.30411
| NB24 | United Energy Feeder | URBAN | 1374 | 4.81 | 2.08 | 6.89 | 5.4179 | 1.2679 | 0.071439 | 6 | 63181.417 | 29200.9796 | 0.0022144 | 0.00025709 | 8 | 3560 | 1.236e-05 | 1 | 0 | 0.0019714 | 0.0019714 | 0 | 0 | no | no | 1.6543 | 1.2679 | 0.071439
| NB25 | United Energy Feeder | URBAN | 1276.5 | 4.25 | 0.85 | 5.1 | 4.641 | 3.9733 | 0.0074136 | 11 | 192940.8833 | 116633.1365 | 0.0046755 | 0.002407 | 2 | 360 | 3.0899e-06 | 1 | 0 | 0.0031548 | 0 | 0 | 0 | no | no | 1.5772 | 3.9733 | 0.0074136
| NO126 | United Energy Feeder | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| NO2 | United Energy Feeder | URBAN | 225 | 4.16 | 2.37 | 6.53 | 9.0952 | 1.1219 | 0 | 1 | 5658.92 | 290.05 | 0.00038074 | 3.0899e-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.6764 | 1.1219 | 0
| NO22 | United Energy Feeder | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| NO3 | United Energy Feeder | URBAN | 190 | 3.72 | 2.13 | 5.85 | 10.5651 | 2.2163 | 1.1986 | 1 | 4326.8109 | 0 | 0.00030435 | 0 | 2 | 2340 | 2.0084e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 5.8393 | 2.2163 | 1.1986
| NO38 | United Energy Feeder | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| NO4 | United Energy Feeder | URBAN | 275 | 2.65 | 1.85 | 4.5 | 7.6821 | 2.101 | 0 | 3 | 10436.2973 | 4659.665 | 0.00048512 | 7.8792e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.3217 | 2.101 | 0
| NO5 | United Energy Feeder | URBAN | 615 | 4.31 | 2.37 | 6.68 | 10.7358 | 1.7499 | 21.669 | 1 | 15564.3365 | 703.6667 | 0.001053 | 7.7247e-06 | 3 | 192730 | 0.00072922 | 1 | 0 | 0.0012143 | 0.0012143 | 0 | 0 | yes | no | 4.1487 | 1.7499 | 21.669
| NO6 | United Energy Feeder | URBAN | 643.5 | 3.94 | 0.35 | 4.29 | 6.006 | 0.76553 | 0 | 1 | 14920.461 | 444.9 | 0.0010244 | 6.1798e-06 | 1 | 0 | 0 | 1 | 0 | 0.00098413 | 0.00098413 | 0 | 0 | no | no | 1.981 | 0.76553 | 0
| NO7 | United Energy Feeder | URBAN | 2071.5 | 6.11 | 0.91 | 7.02 | 6.8444 | 1.1019 | 0.18668 | 7 | 68531.2813 | 33441.0716 | 0.0028524 | 0.00038418 | 1 | 11610 | 6.0253e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.9985 | 1.1019 | 0.18668
| NP11 | United Energy Feeder | URBAN | 2913 | 13.12 | 1.03 | 14.15 | 9.8801 | 5.7078 | 1.212 | 3 | 249785.0889 | 249785.0889 | 0.0048012 | 0.0048012 | 3 | 53040 | 0.00026264 | 1 | 1 | 0.0035277 | 0 | 0.0010367 | 0.0010367 | no | no | 3.9939 | 5.7078 | 1.212
| NP12 | United Energy Feeder | URBAN | 766 | 8.26 | 2.57 | 10.83 | 0 | 2.2747 | 1.6224 | 3 | 40715.466 | 0 | 0.00017606 | 0 | 4 | 29040 | 0.00016994 | 1 | 0 | 0.0025296 | 0 | 0 | 0 | no | no | 2.5677 | 2.2747 | 1.6224
| NP13 | United Energy Feeder | URBAN | 1466 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2193 | 0 | 0
| NP14 | United Energy Feeder | URBAN | 2004.5 | 19.68 | 16.51 | 36.19 | 8.2862 | 3.249 | 0.025955 | 8 | 144578.6713 | 119474.7163 | 0.0061886 | 0.0056392 | 5 | 1155 | 1.0815e-05 | 1 | 1 | 0.0053991 | 0 | 0.0027346 | 0.0027346 | no | no | 2.7027 | 3.249 | 0.025955
NP34 | NP15 | United Energy Feeder | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1496.7435 | 0 | 0.00011745 | 0 | 2 | 0 | 0 | 1 | 0 | 0.00013132 | 0 | 0 | 0 | no | no | 2.91 | #DIV/0! | #DIV/0!
| NP16 | United Energy Feeder | URBAN | 1985.5 | 12.44 | 0.55 | 12.99 | 3.7189 | 1.6703 | 0.42593 | 2 | 49647.8378 | 49647.8378 | 0.00048555 | 0.00048555 | 1 | 12660 | 8.0337e-05 | 1 | 0 | 0.0064562 | 0 | 0 | 0 | no | no | 4.008 | 1.6703 | 0.42593
NP25 | NP18 | United Energy Feeder | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9669.8682 | 477.2833 | 0.00071096 | 6.1798e-06 | 1 | 0 | 0 | 1 | 0 | 0.00077645 | 0 | 0 | 0 | no | no | 2.9673 | #DIV/0! | #DIV/0!
NP33 | NP2 | United Energy Feeder | URBAN | 1628 | 0 | 0 | 0 | 0 | 1.7888 | 0 | 1 | 50815.6833 | 50815.6833 | 0.00019312 | 0.00019312 | 0 | 0 | 0 | 1 | 0 | 0.0051138 | 0.0051138 | 0 | 0 | no | no | 3.4385 | 1.7888 | 0
| NP23 | United Energy Feeder | URBAN | 1624.5 | 12.83 | 0.78 | 13.61 | 10.6785 | 41.6937 | 4.2874 | 11 | 1250265.0689 | 126147.9196 | 0.014048 | 0.0055913 | 0 | 128566 | 0.00073694 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 3.2504 | 41.6937 | 4.2874
| NP24 | United Energy Feeder | URBAN | 2000 | 10.56 | 1.22 | 11.78 | 8.6689 | 7.1338 | 4.1258 | 8 | 213778.1822 | 159798.4931 | 0.0077779 | 0.004274 | 0 | 123637 | 0.00045576 | 2 | 2 | 0.0062285 | 0.0029339 | 0.0011402 | 0.0011402 | no | no | 4.0044 | 7.1338 | 4.1258
| NP25 | United Energy Feeder | URBAN | 2466.5 | 6.26 | 0.66 | 6.92 | 3.7828 | 3.6481 | 0.35229 | 7 | 181948.2039 | 72668.9307 | 0.0087311 | 0.0017824 | 3 | 17570 | 0.00014214 | 7 | 1 | 0.027589 | 0.02479 | 0.0013704 | 0.0013704 | no | yes | 2.9673 | 3.6481 | 0.35229
| NP31 | United Energy Feeder | URBAN | 431.5 | 6.93 | 1.07 | 8 | 8.3547 | 2.7901 | 2.1069 | 1 | 18341.2813 | 193.2667 | 0.0014256 | 1.5449e-06 | 0 | 13850 | 0.00014214 | 2 | 0 | 0.003199 | 0.0016083 | 0 | 0 | no | no | 3.9384 | 2.7901 | 2.1069
| NP33 | United Energy Feeder | URBAN | 1336 | 10.05 | 2.11 | 12.16 | 8.5527 | 2.6821 | 5.2763 | 1 | 62526.2265 | 467.5001 | 0.0048791 | 9.2697e-06 | 0 | 123003 | 0.00057009 | 2 | 0 | 0.0095644 | 0.0051076 | 0 | 0 | no | no | 3.4385 | 2.6821 | 5.2763
| NP34 | United Energy Feeder | URBAN | 1486 | 8.83 | 4.91 | 13.74 | 5.5944 | 2.2222 | 0.74777 | 4 | 68086.2119 | 7328.1615 | 0.0044376 | 4.8496e-05 | 5 | 22911 | 0.00016376 | 2 | 1 | 0.0069065 | 0.0046132 | 9.5787e-05 | 9.5787e-05 | no | no | 2.91 | 2.2222 | 0.74777
| NP36 | United Energy Feeder | URBAN | 1888.5 | 17.64 | 0.49 | 18.13 | 6.823 | 3.1446 | 6.6629 | 5 | 98590.5469 | 14489.1401 | 0.0068116 | 0.00023724 | 0 | 208896 | 0.0008729 | 2 | 1 | 0.013153 | 0.0069229 | 0.0015079 | 0.0015079 | no | yes | 3.6141 | 3.1446 | 6.6629
NP31 | NP4 | United Energy Feeder | URBAN | 478.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.9384 | 0 | 0
NP11 | NP5 | United Energy Feeder | URBAN | 1053 | 0 | 0 | 0 | 0 | 1.6564 | 3.0305 | 2 | 26202.8936 | 26202.8936 | 0.00030127 | 0.00030127 | 3 | 47940 | 0.00014523 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.9939 | 1.6564 | 3.0305
NP14 | NP6 | United Energy Feeder | URBAN | 1640.5 | 0 | 0 | 0 | 0 | 7.3994 | 0.3918 | 9 | 269476.3571 | 269369.0404 | 0.0041604 | 0.0041588 | 4 | 14269 | 7.4158e-05 | 0 | 1 | 0 | 0 | 0.0027299 | 0.0027299 | no | no | 2.7027 | 7.3994 | 0.3918
NP16 | NP8 | United Energy Feeder | URBAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 157378.4297 | 157378.4297 | 0.009763 | 0.009763 | 2 | 0 | 0 | 0 | 1 | 0 | 0 | 0.0026419 | 0.0026419 | no | no | 4.008 | #DIV/0! | #DIV/0!
NP23 | NP9 | United Energy Feeder | URBAN | 1743 | 0 | 0 | 0 | 0 | 0.23676 | 0.16908 | 1 | 7617.5819 | 7617.5819 | 3.3232e-05 | 3.3232e-05 | 0 | 5440 | 3.0899e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.2504 | 0.23676 | 0.16908
| NRN11 | SPAusnet Feeder | URBAN | 2.5 | 2.4 | 1.5 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5520 | 7.1068e-05 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0 | 0 | 0
| NW11 | United Energy Feeder | URBAN | 1536 | 4.98 | 1.88 | 6.86 | 4.6223 | 1.2708 | 0.52371 | 2 | 70540.6869 | 70540.6869 | 0.00025113 | 0.00025113 | 1 | 29070 | 0.00015913 | 2 | 0 | 0.0046673 | 0.0046673 | 0 | 0 | no | no | 1.6603 | 1.2708 | 0.52371
| NW13 | United Energy Feeder | URBAN | 3121 | 16.2 | 7.75 | 23.95 | 8.2497 | 6.7269 | 0.83091 | 16 | 467458.6204 | 467458.6204 | 0.011229 | 0.011229 | 0 | 57740 | 0.00029818 | 5 | 2 | 0.024195 | 0.024195 | 0.0045128 | 0.0045128 | no | yes | 2.6948 | 6.7269 | 0.83091
| NW14 | United Energy Feeder | URBAN | 2492 | 10.14 | 3.48 | 13.62 | 7.9513 | 0.5073 | 0.84657 | 8 | 22920.8026 | 22920.8026 | 0.00032818 | 0.00032818 | 2 | 38250 | 0.00019775 | 3 | 2 | 0.011522 | 0.011522 | 0.0031625 | 0.0031625 | no | no | 3.3093 | 0.5073 | 0.84657
| NW21 | United Energy Feeder | URBAN | 3033 | 11.29 | 3.03 | 14.32 | 8.9909 | 5.8267 | 3.8224 | 12 | 336762.2479 | 82724.96 | 0.0094609 | 0.0041942 | 0 | 220920 | 0.001375 | 1 | 0 | 0.0015202 | 0.0015202 | 0 | 0 | no | no | 3.1486 | 5.8267 | 3.8224
| NW22 | United Energy Feeder | URBAN | 2708 | 11.47 | 1.47 | 12.94 | 7.0674 | 3.8031 | 6.5373 | 8 | 235635.3691 | 234314.2191 | 0.0071108 | 0.0071093 | 0 | 405045 | 0.0014692 | 0 | 1 | 0 | 0 | 0.0019204 | 0.0019204 | no | no | 2.6224 | 3.8031 | 6.5373
| NW23 | United Energy Feeder | URBAN | 3135 | 12.38 | 1.59 | 13.97 | 7.4806 | 0.47146 | 1.0568 | 4 | 32592.9907 | 32592.9907 | 0.00061084 | 0.00061084 | 15 | 73057.2 | 0.00028118 | 3 | 0 | 0.014502 | 0.014502 | 0 | 0 | no | no | 2.7209 | 0.47146 | 1.0568
| NW31 | United Energy Feeder | URBAN | 3569.5 | 9.12 | 2.47 | 11.59 | 7.5304 | 6.9822 | 2.498 | 9 | 551657.0818 | 551657.0818 | 0.004782 | 0.004782 | 9 | 197367 | 0.00083273 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.7107 | 6.9822 | 2.498
| NW32 | United Energy Feeder | URBAN | 762 | 2.84 | 3.84 | 6.68 | 6.0009 | 10.1279 | 4.5103 | 5 | 226389.8231 | 7811.0884 | 0.002897 | 0.00010685 | 5 | 100820 | 0.00025337 | 2 | 0 | 0.0018478 | 0.0011742 | 0 | 0 | yes | no | 2.0453 | 10.1279 | 4.5103
| NW33 | United Energy Feeder | URBAN | 2531 | 8.86 | 2.25 | 11.11 | 8.5791 | 7.2287 | 0.29567 | 10 | 350830.0473 | 84217.2936 | 0.011604 | 0.0042158 | 2 | 14350 | 6.1798e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.129 | 7.2287 | 0.29567
| NW34 | United Energy Feeder | URBAN | 1 | 0 | 2.64 | 2.64 | 2.0137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.62632 | 0 | 0
| OAK21 | United Energy Feeder | URBAN | 1364 | 5.62 | 0.71 | 6.33 | 3.5155 | 0.035193 | 0.92493 | 1 | 2974.6961 | 2974.6961 | 4.091e-05 | 4.091e-05 | 7 | 78180 | 0.00046194 | 1 | 0 | 0.0020888 | 0.0020888 | 0 | 0 | no | no | 0.96823 | 0.035193 | 0.92493
| OAK22 | United Energy Feeder | URBAN | 1191 | 3.27 | 1.64 | 4.91 | 4.4884 | 0.068321 | 1.5773 | 2 | 2776.3342 | 2776.3342 | 5.4228e-05 | 5.4228e-05 | 2 | 64095 | 0.00036924 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.7585 | 0.068321 | 1.5773
| OAK23 | United Energy Feeder | URBAN | 2006 | 5.54 | 1.28 | 6.82 | 5.1464 | 0.060957 | 4.7976 | 0 | 3883.8998 | 3883.8998 | 3.3989e-05 | 3.3989e-05 | 16 | 305685 | 0.0018879 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.889 | 0.060957 | 4.7976
| OAK24 | United Energy Feeder | URBAN | 376 | 1.93 | 0.52 | 2.45 | 2.8919 | 0.072037 | 0.023988 | 0 | 1261.2667 | 1261.2667 | 1.236e-05 | 1.236e-05 | 0 | 420 | 2.1629e-05 | 1 | 0 | 0.00043413 | 0.00043413 | 0 | 0 | no | no | 1.2885 | 0.072037 | 0.023988
| OAK25 | United Energy Feeder | URBAN | 162.5 | 0.9 | 0.53 | 1.43 | 2.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.99157 | 0 | 0
| OAK26 | United Energy Feeder | URBAN | 2403 | 8.17 | 0.82 | 8.99 | 4.3213 | 0.066121 | 2.6463 | 2 | 7300.0748 | 7300.0748 | 8.437e-05 | 8.437e-05 | 1 | 292160 | 0.0013719 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3059 | 0.066121 | 2.6463
| OAK31 | United Energy Feeder | URBAN | 379.5 | 0.45 | 1.54 | 1.99 | 4.1599 | 0.015812 | 0 | 0 | 231.3667 | 231.3667 | 1.5449e-06 | 1.5449e-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5562 | 0.015812 | 0
| OAK32 | United Energy Feeder | URBAN | 738 | 2.27 | 0.64 | 2.91 | 1.5884 | 0.25107 | 0 | 4 | 20974.4808 | 13234.0668 | 0.00039798 | 0.0003368 | 0 | 0 | 0 | 1 | 0 | 0.0011618 | 0.0011618 | 0 | 0 | no | no | 0.53004 | 0.25107 | 0
| OAK33 | United Energy Feeder | URBAN | 2042.5 | 7.78 | 1.31 | 9.09 | 4.2825 | 0.017724 | 3.082 | 0 | 1722.0499 | 1722.0499 | 2.3174e-05 | 2.3174e-05 | 1 | 299445 | 0.0015125 | 0 | 1 | 0 | 0 | 0.0019621 | 0.0019621 | no | no | 1.2614 | 0.017724 | 3.082
| OAK34 | United Energy Feeder | URBAN | 796.5 | 3.14 | 0.61 | 3.75 | 6.0582 | 0.040055 | 0 | 0 | 1185.65 | 1185.65 | 9.2697e-06 | 9.2697e-06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.6145 | 0.040055 | 0
| OAK35 | United Energy Feeder | URBAN | 376 | 2.79 | 0.38 | 3.17 | 2.4879 | 1.0716 | 6.3191 | 2 | 26582.4584 | 26582.4584 | 0.00024753 | 0.00024753 | 3 | 156750 | 0.00051447 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0.90946 | 1.0716 | 6.3191
| OE1 | United Energy Feeder | URBAN | 86 | 0.3 | 0.88 | 1.18 | 1.2681 | 0.17093 | 0 | 1 | 2016.1579 | 0 | 0.00014182 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.43747 | 0.17093 | 0
| OE10 | United Energy Feeder | URBAN | 224 | 2.17 | 0.96 | 3.13 | 2.0607 | 0.28296 | 0 | 1 | 5242.9279 | 259.1667 | 0.00035365 | 3.0899e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.72535 | 0.28296 | 0
| OE14 | United Energy Feeder | URBAN | 178 | 1.93 | 0.6 | 2.53 | 2.2212 | 0.41763 | 0 | 1 | 4197.8728 | 120.25 | 0.00028836 | 1.5449e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0625 | 0.41763 | 0
| OE15 | United Energy Feeder | URBAN | 506 | 2.62 | 0.99 | 3.61 | 2.1301 | 0.62775 | 0 | 2 | 25519.4179 | 673.7834 | 0.00094228 | 1.236e-05 | 7 | 0 | 3.0899e-06 | 1 | 0 | 0.00079101 | 0.00079101 | 0 | 0 | no | no | 0.74682 | 0.62775 | 0
| OE2 | United Energy Feeder | URBAN | 299 | 1.58 | 1.24 | 2.82 | 0.63407 | 0.10286 | 0 | 1 | 7179.6674 | 519.5501 | 0.00047465 | 6.1798e-06 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.25703 | 0.10286 | 0
| OE4 | United Energy Feeder | URBAN | 1616 | 5.28 | 0.61 | 5.89 | 3.4081 | 0.65302 | 0.11959 | 4 | 50129.145 | 1075.0503 | 0.0027766 | 1.8987e-05 | 8 | 9180 | 5.2528e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2631 | 0.65302 | 0.11959
| OE5 | United Energy Feeder | URBAN | 343.5 | 2.64 | 0.74 | 3.38 | 1.605 | 0.32374 | 0 | 2 | 11603.9439 | 3652.5794 | 0.00059758 | 3.8284e-05 | 4 | 0 | 0 | 2 | 0 | 0.0010861 | 0.0010861 | 0 | 0 | no | no | 0.57501 | 0.32374 | 0
| OE6 | United Energy Feeder | URBAN | 25.5 | 0.72 | 0.29 | 1.01 | 1.7041 | 0.47487 | 1.1547 | 1 | 740.2698 | 173.9333 | 4.1381e-05 | 1.5449e-06 | 2 | 1800 | 6.1798e-06 | 2 | 0 | 7.7247e-05 | 7.7247e-05 | 0 | 0 | no | no | 0.98147 | 0.47487 | 1.1547
| OE9 | United Energy Feeder | URBAN | 615.5 | 1.89 | 0.68 | 2.57 | 1.3474 | 0.19754 | 0 | 1 | 15301.3049 | 1301.4666 | 0.0010002 | 1.5449e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.47677 | 0.19754 | 0
OR33 | OR11 | United Energy Feeder | URBAN | 846 | 3.94 | 0.2 | 4.14 | 2.8484 | 0.027394 | 0 | 0 | 1485.7834 | 1485.7834 | 1.3905e-05 | 1.3905e-05 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.93587 | 0.027394 | 0
OR34 | OR12 | United Energy Feeder | URBAN | 1093.5 | 6.36 | 0.48 | 6.84 | 4.9796 | 0.24004 | 0.70037 | 1 | 11073.8706 | 11073.8706 | 7.7804e-05 | 7.7804e-05 | 4 | 32310 | 0.00015449 | 1 | 1 | 0.0035178 | 0.0035178 | 0.0020919 | 0.0020919 | no | no | 1.4222 | 0.24004 | 0.70037
OR35 | OR13 | United Energy Feeder | URBAN | 1173.5 | 0 | 0 | 0 | 4.8939 | 5.2178 | 1.5364 | 7 | 272177.6578 | 250519.0516 | 0.0020235 | 0.0019524 | 7 | 80145 | 0.00036461 | 1 | 1 | 0.0036214 | 0.0036214 | 0.0017211 | 0 | yes | no | 1.3498 | 5.2178 | 1.5364
| OR3 | United Energy Feeder | URBAN | 8 | 0.01 | 1.18 | 1.19 | 2.1691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.0869 | 0 | 0
| OR31 | United Energy Feeder | URBAN | 4 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.96101 | 0 | 0
| OR32 | United Energy Feeder | URBAN | 787.5 | 0 | 0.02 | 0.02 | 0 | 0.0027381 | 0 | 0 | 108.85 | 108.85 | 1.5449e-06 | 1.5449e-06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1886 | 0.0027381 | 0
| OR33 | United Energy Feeder | URBAN | 1523 | 0 | 0.03 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.93587 | 0 | 0
| OR34 | United Energy Feeder | URBAN | 1171.5 | 0 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.4222 | 0 | 0
| OR35 | United Energy Feeder | URBAN | 1175 | 5.29 | 0.78 | 6.07 | 0 | 0.0032695 | 0 | 0 | 170.7666 | 170.7666 | 3.0899e-06 | 3.0899e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3498 | 0.0032695 | 0
| OR4 | United Energy Feeder | URBAN | 2259 | 6.17 | 0.49 | 6.66 | 4.641 | 0.38675 | 1.053 | 4 | 33532.5497 | 21234.5497 | 0.00045442 | 0.00042043 | 8 | 91300 | 0.00057472 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5633 | 0.38675 | 1.053
| OR5 | United Energy Feeder | URBAN | 1699.5 | 4.31 | 1.09 | 5.4 | 5.1589 | 0.3709 | 0.3453 | 2 | 16627.4612 | 16627.4612 | 0.00012313 | 0.00012313 | 0 | 15480 | 6.6433e-05 | 1 | 0 | 0.0026295 | 0.0026295 | 0 | 0 | no | no | 2.2746 | 0.3709 | 0.3453
| OR6 | United Energy Feeder | URBAN | 2636.5 | 5.78 | 0.28 | 6.06 | 4.1231 | 0.42032 | 0.033261 | 7 | 48652.7091 | 48557.1591 | 0.00044153 | 0.00043999 | 0 | 3850 | 2.1629e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.3666 | 0.42032 | 0.033261
| OR7 | United Energy Feeder | URBAN | 677.5 | 4.9 | 0.53 | 5.43 | 4.0236 | 0.078067 | 0.008507 | 1 | 2523.6167 | 2523.6167 | 4.0895e-05 | 4.0895e-05 | 4 | 275 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2575 | 0.078067 | 0.008507
OR31 | OR8 | United Energy Feeder | URBAN | 3 | 0 | 0.59 | 0.59 | 2.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.96101 | 0 | 0
OR32 | OR9 | United Energy Feeder | URBAN | 784.5 | 5.1 | 0.73 | 5.83 | 3.9837 | 2.5514 | 0.10454 | 6 | 101038.026 | 18230.3323 | 0.0010882 | 0.0004332 | 0 | 4140 | 1.8539e-05 | 3 | 0 | 0.0071778 | 0.0047909 | 0 | 0 | no | yes | 1.1886 | 2.5514 | 0.10454
RBD13 | RBD05 | United Energy Feeder | URBAN | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.0926 | 0 | 0
| RBD11 | United Energy Feeder | RURAL SHORT | 532 | 3.56 | 3.43 | 6.99 | 0 | 0.017972 | 0 | 1 | 467.4228 | 467.4228 | 1.1216e-05 | 1.1216e-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2273 | 0.017972 | 0
| RBD12 | United Energy Feeder | RURAL SHORT | 2282.5 | 57.63 | 6.05 | 63.68 | 5.2377 | 14.257 | 0.73907 | 29 | 985456.1848 | 957681.3596 | 0.014098 | 0.010636 | 0 | 51085 | 0.00031053 | 4 | 2 | 0.01695 | 0.01695 | 0.00097795 | 0.00097795 | no | no | 1.9813 | 14.257 | 0.73907
| RBD13 | United Energy Feeder | URBAN | 3492 | 18.14 | 1.71 | 19.85 | 7.5656 | 9.1563 | 1.2878 | 7 | 620336.2988 | 539746.5556 | 0.011422 | 0.0057132 | 0 | 87250 | 0.00052374 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.0926 | 9.1563 | 1.2878
| RBD14 | United Energy Feeder | URBAN | 1543 | 7.93 | 0.52 | 8.45 | 4.3454 | 23.1774 | 2.3829 | 12 | 740335.4661 | 657752.528 | 0.015496 | 0.0041504 | 0 | 76115 | 0.00035379 | 2 | 0 | 0.014567 | 0.011924 | 0 | 0 | yes | yes | 2.8984 | 23.1774 | 2.3829
| RBD21 | United Energy Feeder | RURAL SHORT | 1486 | 93.78 | 21.99 | 115.77 | 7.8372 | 20.7353 | 9.3239 | 32 | 434969.6632 | 345117.6467 | 0.016404 | 0.0083875 | 2 | 195591 | 0.001049 | 1 | 5 | 0.004573 | 0.004573 | 0.011776 | 0.011776 | no | no | 4.2503 | 20.7353 | 9.3239
| RBD22 | United Energy Feeder | URBAN | 965.5 | 0.36 | 0.08 | 0.44 | 3.9574 | 24.2275 | 6.5294 | 15 | 628781.9045 | 517045.6895 | 0.027429 | 0.012378 | 0 | 169459 | 0.0014322 | 0 | 1 | 0 | 0 | 0.0001236 | 0.0001236 | yes | no | 2.2321 | 24.2275 | 6.5294
| RBD23 | United Energy Feeder | URBAN | 4276.5 | 27.72 | 2.29 | 30.01 | 9.704 | 12.5624 | 2.116 | 13 | 1181619.3778 | 1124139.4693 | 0.024867 | 0.017434 | 1 | 199031 | 0.00095478 | 0 | 5 | 0 | 0 | 0.026891 | 0.026891 | yes | no | 2.7279 | 12.5624 | 2.116
| RBD24 | United Energy Feeder | URBAN | 3116.5 | 13.82 | 0.82 | 14.64 | 6.2099 | 5.1093 | 0.35283 | 15 | 587497.7401 | 553207.3983 | 0.012114 | 0.0073626 | 0 | 40570 | 0.00021166 | 5 | 0 | 0.023585 | 0.023585 | 0 | 0 | no | no | 1.6262 | 5.1093 | 0.35283
| RD10 | Citipower Feeder | URBAN | 936.5 | 5.05 | 0 | 5.05 | 0 | 0 | 0 | 3 | 88714.4158 | 67624.0445 | 0.0029511 | 0.0014676 | 1 | 10620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| RD2 | Citipower Feeder | URBAN | 148 | 1.14 | 0.78 | 1.92 | 0 | 0 | 0 | 1 | 3422.2712 | 228.1333 | 0.00022776 | 3.0899e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| RD4 | Citipower Feeder | URBAN | 1966.5 | 5.3 | 0.12 | 5.42 | 0 | 0 | 0 | 4 | 587016.7577 | 44264.4672 | 0.0064529 | 0.00028282 | 0 | 230690 | 0.0012993 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0 | 0 | 0
| RWT13 | United Energy Feeder | URBAN | 1 | 0 | 0 | 0 | 1.4705 | 0.1871 | 0 | 1 | 40.0248 | 0 | 1.5456e-06 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.28048 | 0.1871 | 0
| RWT16 | United Energy Feeder | URBAN | 1683 | 6.12 | 1.2 | 7.32 | 4.9123 | 1.5439 | 5.1093 | 4 | 98648.4161 | 31246.5882 | 0.0028375 | 0.00023477 | 4 | 326470 | 0.0013549 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5803 | 1.5439 | 5.1093
| RWT18 | United Energy Feeder | URBAN | 3337.5 | 14.09 | 1.86 | 15.95 | 9.7292 | 4.6465 | 0.93633 | 10 | 438999.0714 | 242722.6995 | 0.014803 | 0.0092763 | 0 | 88465 | 0.00040787 | 0 | 1 | 0 | 0 | 0.002234 | 0.002234 | no | no | 2.1195 | 4.6465 | 0.93633
| RWT24 | United Energy Feeder | URBAN | 3078 | 11.53 | 1.93 | 13.46 | 7.5835 | 4.3851 | 1.3833 | 8 | 280076.1074 | 224808.4549 | 0.012502 | 0.0078003 | 0 | 88350 | 0.00034761 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.8915 | 4.3851 | 1.3833
| RWT28 | United Energy Feeder | URBAN | 2530.5 | 6.91 | 4.93 | 11.84 | 7.3445 | 6.306 | 0 | 11 | 355355.343 | 298732.3006 | 0.013452 | 0.0091583 | 0 | 0 | 0 | 2 | 0 | 0.0081666 | 0.0081666 | 0 | 0 | no | no | 2.6943 | 6.306 | 0
| RWT31 | United Energy Feeder | URBAN | 2472.5 | 13 | 0.51 | 13.51 | 6.1254 | 0.66672 | 0.44455 | 4 | 56360.4393 | 32946.6881 | 0.0057175 | 0.0019107 | 0 | 37580 | 0.00017149 | 0 | 1 | 0 | 0 | 0.0017736 | 0.0017736 | no | no | 1.7549 | 0.66672 | 0.44455
| SH70 | United Energy Feeder | URBAN | 1046.5 | 3.47 | 0.49 | 3.96 | 2.1366 | 1.3497 | 11.1336 | 4 | 112144.8273 | 112144.8273 | 0.0019159 | 0.0019159 | 0 | 925080 | 0.0043382 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0.7557 | 1.3497 | 11.1336
| SH72 | United Energy Feeder | URBAN | 210 | 2.1 | 0.2 | 2.3 | 0 | 0.032227 | 0 | 1 | 1052.9572 | 1052.9572 | 3.9288e-05 | 3.9288e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.38564 | 0.032227 | 0
| SH75 | United Energy Feeder | URBAN | 212 | 0 | 0 | 0 | 1.1135 | 0.0081318 | 0 | 0 | 268.2167 | 268.2167 | 4.6348e-06 | 4.6348e-06 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.38564 | 0.0081318 | 0
| SH77 | United Energy Feeder | URBAN | 283 | 0 | 0 | 0 | 1.2845 | 0.29925 | 0 | 1 | 11596.7333 | 11596.7333 | 0.00013287 | 0.00013287 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.43816 | 0.29925 | 0
| SH80 | United Energy Feeder | URBAN | 1121.5 | 3.46 | 0.15 | 3.61 | 2.2962 | 0.033655 | 3.4934 | 1 | 3080.3023 | 3080.3023 | 4.8063e-05 | 4.8063e-05 | 1 | 319740 | 0.00085899 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | yes | no | 0.7352 | 0.033655 | 3.4934
| SH81 | United Energy Feeder | URBAN | 283.5 | 2.54 | 0.17 | 2.71 | 0 | 0.049308 | 3.6799 | 0 | 1914.1834 | 1914.1834 | 3.0899e-06 | 3.0899e-06 | 1 | 142860 | 0.00061025 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0.43816 | 0.049308 | 3.6799
| SK1 | Citipower Feeder | URBAN | 326 | 0 | 2.2 | 2.2 | 0 | 0 | 0 | 0 | 190.2834 | 190.2834 | 3.0899e-06 | 3.0899e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0 | 0 | 0
| SR11 | United Energy Feeder | URBAN | 1175 | 4.01 | 0.75 | 4.76 | 2.8866 | 2.7688 | 0.20629 | 5 | 240497.9627 | 209848.9407 | 0.0037126 | 0.0019472 | 2 | 17918 | 8.8062e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.81166 | 2.7688 | 0.20629
| SR12 | United Energy Feeder | URBAN | 275.5 | 1.68 | 0.13 | 1.81 | 0.94546 | 0.46387 | 0 | 4 | 24666.1506 | 17390.3393 | 0.0013383 | 0.00091924 | 0 | 0 | 0 | 1 | 0 | 0.00042177 | 0.00042177 | 0 | 0 | no | no | 0.31086 | 0.46387 | 0
| SR13 | United Energy Feeder | URBAN | 1733.5 | 3.65 | 0.88 | 4.53 | 6.8691 | 0.9999 | 0 | 2 | 58134.4535 | 11947.7099 | 0.0027336 | 7.3184e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.7889 | 0.9999 | 0
| SR14 | United Energy Feeder | URBAN | 736.5 | 2.23 | 0.32 | 2.55 | 1.6855 | 0.25725 | 0 | 2 | 21506.4807 | 1731.1987 | 0.0012013 | 6.2231e-05 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.52857 | 0.25725 | 0
| SR15 | United Energy Feeder | URBAN | 2046 | 4.96 | 0.73 | 5.69 | 4.2175 | 0.94453 | 3.0995 | 3 | 74914.3482 | 20474.8216 | 0.0033486 | 0.00022306 | 7 | 245835 | 0.00082191 | 0 | 2 | 0 | 0 | 0.001976 | 0.001976 | no | no | 1.5478 | 0.94453 | 3.0995
| SR19 | United Energy Feeder | URBAN | 820.5 | 3 | 0.25 | 3.25 | 2.7299 | 0.90666 | 0.9909 | 5 | 54509.9908 | 7569.2675 | 0.0015444 | 0.00014336 | 3 | 59575 | 0.00025801 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.81884 | 0.90666 | 0.9909
| SR20 | United Energy Feeder | URBAN | 1157.5 | 4.21 | 0.94 | 5.15 | 3.8045 | 2.798 | 1.1026 | 4 | 126224.8002 | 94882.8438 | 0.0037794 | 0.0019741 | 13 | 49740 | 0.00023329 | 1 | 0 | 0.0016191 | 0.0016191 | 0 | 0 | no | no | 1.5395 | 2.798 | 1.1026
| SR23 | United Energy Feeder | URBAN | 2012 | 5.49 | 1.24 | 6.73 | 5.6828 | 1.6883 | 1.009 | 14 | 102022.0769 | 53063.5957 | 0.0034082 | 0.00058813 | 10 | 60970 | 0.00026573 | 1 | 0 | 0.0030961 | 0.0030961 | 0 | 0 | no | no | 1.9977 | 1.6883 | 1.009
| SR24 | United Energy Feeder | URBAN | 1796 | 5.53 | 0.31 | 5.84 | 3.4741 | 0.67077 | 0.79539 | 2 | 65525.9208 | 17340.328 | 0.0029281 | 0.00015258 | 11 | 77700 | 0.00038624 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.1031 | 0.67077 | 0.79539
| SR25 | United Energy Feeder | URBAN | 908.5 | 4.44 | 0.39 | 4.83 | 3.3706 | 0.63068 | 1.7742 | 2 | 25736.3164 | 1243.7501 | 0.0014247 | 1.3905e-05 | 3 | 72400 | 0.00039396 | 3 | 0 | 0.004278 | 0.004278 | 0 | 0 | no | no | 1.3358 | 0.63068 | 1.7742
| SS11 | United Energy Feeder | URBAN | 2080 | 12.16 | 0.22 | 12.38 | 6.8707 | 5.9748 | 9.6007 | 5 | 126924.0541 | 87784.2122 | 0.0067806 | 0.0037093 | 1 | 203950 | 0.00095323 | 1 | 1 | 0.0032336 | 0.0032336 | 0.00035997 | 0.00035997 | no | no | -5.8748 | 5.9748 | 9.6007
| SS12 | United Energy Feeder | URBAN | 1081 | 8.19 | 1.38 | 9.57 | 4.5339 | 1.616 | 0.32556 | 8 | 58297.5744 | 17415.8666 | 0.001997 | 0.00031264 | 0 | 11745 | 6.7978e-05 | 6 | 0 | 0.0098614 | 0.0098614 | 0 | 0 | no | yes | 1.7979 | 1.616 | 0.32556
| SS13 | United Energy Feeder | URBAN | 1919.5 | 6.92 | 1.26 | 8.18 | 4.7333 | 2.7213 | 0.25445 | 6 | 162457.9642 | 92582.3754 | 0.0036132 | 0.00065222 | 8 | 15190 | 9.7332e-05 | 1 | 0 | 0.0029802 | 0.0029802 | 0 | 0 | no | no | 1.9292 | 2.7213 | 0.25445
| SS14 | United Energy Feeder | URBAN | 627.5 | 3.79 | 3.62 | 7.41 | 5.0287 | 11.4035 | 0.52525 | 6 | 254233.3101 | 39069.8832 | 0.0035622 | 0.00098568 | 0 | 11710 | 5.4073e-05 | 1 | 0 | 0.0009625 | 0 | 0 | 0 | yes | no | 1.6888 | 11.4035 | 0.52525
| SS21 | United Energy Feeder | URBAN | 381.5 | 7.11 | 0.69 | 7.8 | 4.2844 | 2.7205 | 0.07314 | 6 | 33476.5306 | 19483.7433 | 0.0015338 | 0.00079563 | 8 | 900 | 9.2697e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.8602 | 2.7205 | 0.07314
| SS22 | United Energy Feeder | URBAN | 1248 | 6.49 | 1.09 | 7.58 | 4.3395 | 1.3309 | 0.88921 | 6 | 41961.8885 | 2665.4884 | 0.0018931 | 4.4726e-05 | 8 | 28036 | 9.2697e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.3749 | 1.3309 | 0.88921
| SS23 | United Energy Feeder | URBAN | 3521 | 14.6 | 4.14 | 18.74 | 8.9391 | 0.30901 | 0.071727 | 11 | 119441.9131 | 40843.8225 | 0.011006 | 0.0057771 | 6 | 27725 | 0.00025337 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.54655 | 0.30901 | 0.071727
| SS24 | United Energy Feeder | URBAN | 109 | 3.23 | 8.28 | 11.51 | 9.4138 | 2.3268 | 0 | 2 | 3573.363 | 1534.05 | 0.00018166 | 2.1629e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.2585 | 2.3268 | 0
| STO12 | United Energy Feeder | URBAN | 2681 | 0 | 0 | 0 | 0 | 14.827 | 6.0809 | 26 | 1111031.7751 | 329890.6945 | 0.011328 | 0.0023751 | 4 | 455660 | 0.0024766 | 0 | 1 | 0 | 0 | 0.0013997 | 0.0013997 | yes | no | 2.1467 | 14.827 | 6.0809
| STO13 | United Energy Feeder | RURAL SHORT | 3301.5 | 36.59 | 7.7 | 44.29 | 9.1409 | 12.9038 | 0.73236 | 17 | 1007489.6877 | 374588.519 | 0.013353 | 0.006782 | 7 | 57180 | 0.00026728 | 2 | 0 | 0.010126 | 0.0050597 | 1.5449e-06 | 0 | no | no | 2.5371 | 12.9038 | 0.73236
| STO14 | United Energy Feeder | URBAN | 2696 | 27.93 | 0.4 | 28.33 | 11.3112 | 0.46714 | 0 | 2 | 35199.9318 | 35199.9318 | 0.0065457 | 0.0065457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.1467 | 0.46714 | 0
| STO21 | United Energy Feeder | URBAN | 3520 | 0 | 0.23 | 0.23 | 6.9896 | 5.7043 | 0.83096 | 15 | 795783.7819 | 435522.3852 | 0.011904 | 0.0067413 | 0 | 115924.2 | 0.0006427 | 1 | 1 | 0.005412 | 0.005412 | 0.00024256 | 0.00024256 | no | no | 1.5139 | 5.7043 | 0.83096
| STO22 | United Energy Feeder | URBAN | 1744.5 | 0 | 0.16 | 0.16 | 5.6422 | 4.1244 | 0.94751 | 9 | 243801.8778 | 33096.2151 | 0.0051867 | 0.002581 | 0 | 56010 | 0.00023483 | 1 | 0 | 0.0026542 | 0.0026542 | 0 | 0 | no | no | 1.7707 | 4.1244 | 0.94751
| STO23 | United Energy Feeder | URBAN | 3678 | 0 | 0.07 | 0.07 | 6.8327 | 1.8339 | 0.5162 | 11 | 486131.1639 | 77346.2364 | 0.0095138 | 0.0040016 | 6 | 136837 | 0.00064115 | 0 | 0 | 0 | 0 | 1.5449e-06 | 1.5449e-06 | no | no | 0.83249 | 1.8339 | 0.5162
| SV14 | United Energy Feeder | URBAN | 17 | 1.88 | 0.85 | 2.73 | 4.9375 | 1.1583 | 0 | 2 | 426.5527 | 127.204 | 2.5529e-05 | 2.0393e-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.7699 | 1.1583 | 0
| SV16 | United Energy Feeder | URBAN | 1076.5 | 6.79 | 1.27 | 8.06 | 6.1063 | 1.0395 | 0.079286 | 3 | 27336.7869 | 7224.2964 | 0.0016298 | 5.1509e-05 | 0 | 2085 | 4.6348e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.4562 | 1.0395 | 0.079286
| SV20 | United Energy Feeder | URBAN | 83 | 5.67 | 1.11 | 6.78 | 6.7159 | 1.202 | 0 | 1 | 1711.1566 | 120.8667 | 0.00012634 | 1.5449e-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.4981 | 1.202 | 0
| SV21 | United Energy Feeder | URBAN | 1061.5 | 4.73 | 2.59 | 7.32 | 6.5558 | 0.92901 | 0.02089 | 1 | 20012.5376 | 442.6166 | 0.0015434 | 7.7247e-06 | 0 | 450 | 4.6348e-06 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.9566 | 0.92901 | 0.02089
| SV22 | United Energy Feeder | URBAN | 35 | 0 | 0.57 | 0.57 | 3.2904 | 0.36373 | 0 | 1 | 636.116 | 0 | 4.9917e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.2008 | 0.36373 | 0
| SV23 | United Energy Feeder | URBAN | 172.5 | 3.45 | 0.78 | 4.23 | 7.3907 | 5.6851 | 2.128 | 3 | 21639.5665 | 18589.9517 | 0.00050658 | 0.00026728 | 0 | 8100 | 3.0899e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.7191 | 5.6851 | 2.128
| SV31 | United Energy Feeder | URBAN | 90.5 | 3.8 | 0.65 | 4.45 | 2.9307 | 0.43045 | 0.082169 | 1 | 1440.6156 | 0 | 0.00011305 | 0 | 5 | 275 | 1.5449e-06 | 1 | 0 | 0.00011896 | 0.00011896 | 0 | 0 | no | no | 1.6225 | 0.43045 | 0.082169
| SV32 | United Energy Feeder | URBAN | 1803 | 7.41 | 0.89 | 8.3 | 9.2786 | 2.0497 | 2.0255 | 6 | 80785.7442 | 42300.7276 | 0.0062651 | 0.0032451 | 5 | 79830 | 0.00033834 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.7448 | 2.0497 | 2.0255
| SV33 | United Energy Feeder | URBAN | 1480 | 8.47 | 1.09 | 9.56 | 5.5757 | 2.4399 | 1.835 | 4 | 71003.7 | 43220.3992 | 0.0022952 | 0.00011502 | 3 | 53400 | 0.00026882 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.0514 | 2.4399 | 1.835
| SV34 | United Energy Feeder | URBAN | 10 | 1 | 1.1 | 2.1 | 2.0007 | 0.24512 | 0 | 1 | 187.0929 | 0 | 1.4681e-05 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.7861 | 0.24512 | 0
| SVW41 | United Energy Feeder | URBAN | 985 | 6.23 | 1.15 | 7.38 | 4.1891 | 0.93259 | 1.6456 | 3 | 27142.8095 | 8508.3532 | 0.0015726 | 0.00011032 | 2 | 47895 | 0.00026573 | 2 | 0 | 0.0031177 | 0.0031177 | 0 | 0 | no | no | 2.0306 | 0.93259 | 1.6456
| SVW42 | United Energy Feeder | URBAN | 548 | 3.16 | 2.4 | 5.56 | 7.4025 | 4.6042 | 10.667 | 2 | 36975.9994 | 26105.8999 | 0.0017521 | 0.00089916 | 4 | 85665 | 0.00031826 | 1 | 0 | 0.00088835 | 0.00088835 | 0 | 0 | no | no | 4.0942 | 4.6042 | 10.667
| SVW43 | United Energy Feeder | URBAN | 1.5 | 0.08 | 2.24 | 2.32 | 5.1551 | 0.65918 | 0 | 1 | 18.7093 | 0 | 1.4681e-06 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 3.171 | 0.65918 | 0
| SVW44 | United Energy Feeder | URBAN | 1 | 0.05 | 2.61 | 2.66 | 4.2982 | 0.91632 | 0 | 1 | 18.7093 | 0 | 1.4681e-06 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.9386 | 0.91632 | 0
| SVW45 | United Energy Feeder | URBAN | 411.5 | 4.27 | 2.12 | 6.39 | 10.6269 | 1.7119 | 3.2962 | 1 | 9833.9467 | 479.3 | 0.00074025 | 6.1798e-06 | 2 | 18935 | 7.4158e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 4.298 | 1.7119 | 3.2962
| SVW52 | United Energy Feeder | URBAN | 15.5 | 0 | 0.79 | 0.79 | 4.7294 | 0.54549 | 0 | 1 | 280.6394 | 0 | 2.2022e-05 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.8077 | 0.54549 | 0
| SVW53 | United Energy Feeder | URBAN | 2041.5 | 11.16 | 1.03 | 12.19 | 6.933 | 3.6022 | 4.0167 | 9 | 138542.9791 | 101723.0896 | 0.0063134 | 0.0034241 | 1 | 154485 | 0.00044958 | 1 | 0 | 0.0044077 | 0.0044077 | 0 | 0 | no | no | 3.1848 | 3.6022 | 4.0167
| SVW54 | United Energy Feeder | URBAN | 627.5 | 4.95 | 0.72 | 5.67 | 3.494 | 6.8481 | 1.233 | 2 | 116636.6127 | 591 | 0.0012075 | 7.7247e-06 | 3 | 21000 | 0.00015141 | 1 | 0 | 0.00096868 | 0.00096868 | 0 | 0 | no | no | 2.2105 | 6.8481 | 1.233
| SVW55 | United Energy Feeder | URBAN | 1064 | 8.17 | 2.32 | 10.49 | 4.7458 | 0.98631 | 0.28156 | 5 | 31933.2298 | 3232.2997 | 0.0013382 | 8.2887e-05 | 5 | 9116 | 4.6348e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.9718 | 0.98631 | 0.28156
WD15 | WD1 | United Energy Feeder | URBAN | 323 | 0 | 0 | 0 | 0 | 0.0246 | 0 | 0 | 307.1833 | 307.1833 | 3.0899e-06 | 3.0899e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.552 | 0.0246 | 0
| WD13 | United Energy Feeder | URBAN | 548.5 | 0 | 0 | 0 | 4.8601 | 0.2531 | 0 | 1 | 5945.499 | 5945.499 | 5.5587e-05 | 5.5587e-05 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.401 | 0.2531 | 0
| WD14 | United Energy Feeder | URBAN | 579 | 5.4 | 1.41 | 6.81 | 3.6451 | 0.011465 | 0 | 0 | 329.5833 | 329.5833 | 4.6348e-06 | 4.6348e-06 | 4 | 0 | 0 | 1 | 0 | 0.0017906 | 0.0017906 | 0 | 0 | no | no | 1.2085 | 0.011465 | 0
| WD15 | United Energy Feeder | URBAN | 1049.5 | 4.55 | 0.79 | 5.34 | 3.4459 | 0.017713 | 0.0732 | 0 | 718.6667 | 718.6667 | 6.1798e-06 | 6.1798e-06 | 0 | 2970 | 1.3905e-05 | 2 | 0 | 0.0028149 | 0.0028149 | 0 | 0 | no | no | 1.552 | 0.017713 | 0.0732
| WD16 | United Energy Feeder | URBAN | 345 | 3.45 | 0.21 | 3.66 | 1.3545 | 0.045681 | 0 | 1 | 2772.3903 | 2772.3903 | 2.8072e-05 | 2.8072e-05 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.34108 | 0.045681 | 0
WD23 | WD17 | United Energy Feeder | URBAN | 479 | 0 | 0 | 0 | 0 | 9.3717 | 0 | 8 | 250542.6248 | 250542.6248 | 0.0059877 | 0.0059877 | 6 | 0 | 0 | 1 | 0 | 0.0015357 | 0.0015357 | 0 | 0 | yes | no | 1.075 | 9.3717 | 0
| WD23 | United Energy Feeder | URBAN | 479.5 | 4.71 | 1.13 | 5.84 | 3.9439 | 0.87426 | 0 | 1 | 23396.7017 | 23396.7017 | 8.9267e-05 | 8.9267e-05 | 8 | 0 | 0 | 2 | 0 | 0.0029478 | 0.0029478 | 0 | 0 | no | no | 1.075 | 0.87426 | 0
| WD24 | United Energy Feeder | URBAN | 17 | 0 | 2.31 | 2.31 | 3.9185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5701 | 0 | 0
M34 | WD26 | United Energy Feeder | URBAN | 299.5 | 4.18 | 0.17 | 4.35 | 1.4142 | 0.12617 | 0 | 2 | 6690.778 | 6690.778 | 0.0009448 | 0.0009448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.33887 | 0.12617 | 0
WD26 | WD3 | United Energy Feeder | URBAN | 300 | 0 | 0 | 0 | 0 | 0.15808 | 2.707 | 2 | 8397.1178 | 8397.1178 | 9.812e-05 | 9.812e-05 | 2 | 143790 | 0.00049438 | 0 | 0 | 0 | 0 | 0 | 0 | yes | no | 0.33887 | 0.15808 | 2.707
| WD33 | United Energy Feeder | URBAN | 17.5 | 0 | 3.38 | 3.38 | 5.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 2.103 | 0 | 0
| WD34 | United Energy Feeder | URBAN | 552.5 | 5.1 | 0.11 | 5.21 | 2.7687 | 0.1462 | 0.26868 | 2 | 6758.2042 | 6758.2042 | 9.2836e-05 | 9.2836e-05 | 0 | 12420 | 3.5534e-05 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.71713 | 0.1462 | 0.26868
| WD36 | United Energy Feeder | URBAN | 729.5 | 10.09 | 1.19 | 11.28 | 4.5404 | 4.7874 | 4.6078 | 4 | 137761.7153 | 135903.7153 | 0.0022938 | 0.0022907 | 1 | 132595 | 0.00046657 | 1 | 0 | 0.0022263 | 0.0022263 | 0 | 0 | yes | no | 1.521 | 4.7874 | 4.6078
WD24 | WD5 | United Energy Feeder | URBAN | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 1.5701 | 0 | 0
WD16 | WD8 | United Energy Feeder | URBAN | 324 | 0 | 0 | 0 | 0 | 0.0025432 | 0 | 0 | 144.95 | 144.95 | 1.5449e-06 | 1.5449e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | no | no | 0.34108 | 0.0025432 | 0
WD14 | WD9 | United Energy Feeder | URBAN | 579 | 0 | 0 | 0 | 0 | 7.1766 | 0.015654 | 1 | 206302.9641 | 206064.6974 | 0.0018107 | 0.0018091 | 2 | 450 | 3.0899e-06 | 1 | 0 | 0.001806 | 0.001806 | 0 | 0 | yes | no | 1.2085 | 7.1766 | 0.015654
Contents
Contents

## 6c. Causes of Outages and Worst
United Energy Distribution Pty Limited
Cause of Outages and Worst Served 15 per cent customers
2013
Table 1 Causes of Unplanned Sustained Outages
Cause of outage | Number of outages
Weather | 101
Equipment failure | 1188
Operational error | 27
Vegetation | 306
Animals | 236
Third party impacts | 93
Transmission failure | 241
Load shedding | 6
Inter-distributor connection failure | 20
Other | 210
Table 2 Minutes off Supply for Worst Served 15 per cent customers
Minutes off supply (worst 15%) | 339.4509
The AER will use the ESCV's definition of minutes of supply for worst served 15% of customers. This is defined as the total annual minutes off supply (SAIDI for planned and unplanned sustained interruptions) experienced by the 15% of customers in the distribution business area connected by those feeders experiencing the longest time off supply.
Contents